## Slide 1: Building Ventilation What Everyone Should Know
Walter Sobkiw
May 2022
https://www.cassbeth.com/cleanairbuildings/presentations/Ventilation-Education-handouts.pdf

## Slide 2: Introductions
Are there any
Licensed doctors or pharmacists with an infection disease background where they needed to maintain certified facilities
HVAC staff that work with airborne contagion mitigation ventilation systems
Ceiling Level / Upper Room UV-C or FAR UV specialists that work with airborne contagion mitigation systems
Engineers or scientists performing research on airborne contagion mitigation systems
HVAC staff or facility managers

## Slide 3: Introductions
Collaborated and shared COVID-19 systems research with others at Drexel University and the MITRE healthcare coalition starting in 2020
Research was about determining probability of infection using common operational living scenarios
Changed the dialogue to admit that the COVID-19 virus is airborne, and that ventilation is critical
Wrote a book: COVID-19 A Systems Perspective

## Slide 4: Our Parents and Grandparents
Swarthmore Public School Classroom
circa 1937 - 1943
Open windows Public School cafeteria circa 1908
First US fresh-air school for tubercular children opened in Providence in 1908 and by 1910 there were 65 fresh-air schools in the country.
UPENN study with Ceiling Level UV lights.

## Slide 5: Why is Ventilation Suddenly a Problem
COVID-19 is endemic, it is like tuberculosis, measles, and other airborne contagions from the previous century
It has been a leading cause of death for 2 years
To eventually eliminate tuberculosis and other airborne contagions, it took vaccines and modern forced air heat and cooling systems
Our building ventilation systems have been ignored during the time of great health when our parents and grandparents understood building ventilation

## Slide 6: Professor Edward A. Nardell Harvard Medical School
From Time Magazine February 1, 2022: If We're Going to Live With COVID-19, It's Time to Clean Our Indoor Air Properly, Edward A. Nardell is Professor of Global Health and Social Medicine, Harvard Medical School.
COVID-variants may be with us for years to come, and this will certainly not be the last respiratory virus pandemic. We have long suffered from annual contagious respiratory infections, but exceptionally low rates of influenza and common colds during COVID-precautions have demonstrated that not all of this suffering need happen. So, we need to think clearly and scientifically about how better we can reduce the spread of viruses indoors especially when and where masks will no longer be in common use.
Are there effective engineering controls that can help make indoor environments truly safer?

## Slide 7: A Paradigm Shift to Combat Indoor Respiratory Infection
In May of 2021, 39 scientists published "A Paradigm Shift to Combat Indoor Respiratory Infection"
There is great disparity in the way we think about and address different sources of environmental infection. Governments have for decades promulgated a large amount of legislation and invested heavily in food safety, sanitation, and drinking water for public health purposes. By contrast, airborne pathogens and respiratory infections, whether seasonal influenza or COVID-19, are addressed weakly, if at all, in terms of regulations, standards, and building design and operation, pertaining to the air we breathe.

## Slide 8: Ventilation
Ventilation what is it?
We hear that we need ventilation in small indoor spaces, But why?
We hear we need to increase ventilation but what does that mean?

## Slide 9: Ventilation what is it?
It is about Ventilation performance levels
Ventilation performance is measured as Air Changes Per Hour (ACH)
ACH is a measure of how often air changes in a room
  1 ACH changes the room air 1 time per hour
  20 ACH changes the room air 20 times per hour
  or every 3 minutes (60 min / 3 min = 20 ACH)
Disease specialists address ventilation only in ACH
ACH = Fan Cubic-feet per Hour / Room Cubic-feet

## Slide 10: Ventilation what is it?
It is not about measuring and maintaining CO2 levels
Maintaining CO2 levels leads to a system with ACH levels that are too low such as 1 ACH or less
It is not about liters/min or cubic-feet/min per person, this will never provide visibility into the actual ACH level in a room and when scenarios are run the ACH levels are too low such as 1 ACH or less
Ventilation performance when dealing with airborne contagions is always in terms of ACH in a real room setting, not a lab or test fixture
Example: 60 min / air changed every 3 min = 20 ACH

## Slide 11: Scenarios Analyzed Key Research Findings
Small indoor space - problem is massive
Large indoor space - problematic
Outside - extremely rare
Mask on / off
Exposure time of 1, 4 , 8 hours
Various ventilation rates - key to reduce risk
Used Well-Riley equation to develop scenarios
Scenarios show probability of infection
99% to .0003%

## Slide 12: What should be the ACH Level?
0 leads to infection
1 leads to infection we know from data
CDC recommends 12 ACH for a hospital room with airborne contagion
The number must be greater than 1
As ACH increases the risk of infection drops

## Slide 13: Mental Models to Understand ACH
Many address ACH levels as a percent of remaining contagions after 1 ACH
  One air change removes approximately 63% of room air contaminants, and a second air change removes about 63% of what remains, and so on
Systems engineering safety and reliability analysis is about probabilities, relative probabilities and time before failure
Applying systems engineering safety and reliability concepts to ACH provides a quick view on the effectiveness of ACH levels and how one can behave

## Slide 14: ACH Various Analysis Perspectives
ACH | Remaining Virus * 63% / AC | Time (mins.) removal: 99% efficiency * | Time (mins.) removal: 99.9% efficiency * | Infection Risk (1/ACH) Safety world | Time to Infection (hours) Reliability world
0 | 100% | - | - | 100% | 1 or .5 or .25
1 | 63% | - | - | 100% or 50% | 1 or 4 or 6
2 | 40% | 138 | 207 | 50% | 2
4 | 16% | 69 | 104 | 25% | 4
6 | 6% | 46 | 69 | 17% | 6
8 | 2% | 35 | 52 | 13% | 8
10 | 1% | 28 | 41 | 10% | 10
12 | 0.39% | 23 | 35 | 8% | 12
15 | 0.10% | 18 | 28 | 7% | 15
20 | 0.01% | 14 | 21 | 5% | 20
50 | - | 6 | 8 | 2% | 50
* CDC Appendix B. Air Guidelines for Environmental Infection Control in Health-Care Facilities (2003), Medical world

## Slide 15: Where do ACH standards and guidelines come from?
ASHRAE American Society of Heating, Refrigerating and Air-Conditioning Engineers
CDC Centers for Disease Control and Prevention
DOD Department of Defense Standards
ISO International Organization for Standardization
Others
Most of the ACH levels are based on comfort except for when airborne contagion mitigation is required in hospitals

## Slide 16: ACH Standards & Guidelines
Area | ACH min | ACH max | Source | Area | ACH min | ACH max | Source
Hospital Trauma room | 15 | - | CDC | Classroom (Art) | 16 | 20 | EPA
Hospital room airborne precautions | 12 | - | CDC | Malls | 6 | 10 | EPA
Hospital operating room | 25 | - |  | Office | 8 | 30 | Greenheck
Hospital rooms | 6 | 10 | EPA | Engine Room | 20 | 60 | Greenheck
Restaurants | 8 | 12 | EPA | Kitchen | 12 | 60 | Greenheck
Restaurants | 8 | 20 | NCI | Kitchen | 7 | 8 | NCI

## Slide 17: ACH Standards & Guidelines
Area | ACH min | ACH max | Source | Area | ACH min | ACH max | Source
Restaurants | 15 | 20 | wiki | Kitchen | 14 | 18 | NCI
Bar | 15 | 30 | Greenheck | Kitchens | 15 | 30 | EPA
Bar | 15 | 20 | NCI | Retail | 6 | 10 | NCI, wiki, EPA
Bar | 15 | 20 | wiki | Laboratory | 12 | 30 | Greenheck
School Classroom | 4 | 12 | EPA | Laboratory | 6 | 12 | wiki
Auditorium | 8 | 15 | EPA | Club Houses | 20 | 30 | EPA
Assembly Hall | 6 | 8 | EPA | Theatres | 8 | 15 | EPA
Swimming Pool | 20 | 30 | EPA |  |  |  | 

## Slide 18: What have facility managers done?
Hawaiian airlines ventilation performance level is 20 ACH and they posted it for all passengers to see on their entertainment screens
Philadelphia restaurant program is 15 ACH and 106 restaurants participated
There is a public database with hundreds of facilities showing what they have done
https://www.cassbeth.com/cleanairbuildings/index.html

## Slide 19: Facility Types Research Findings
Facility Type | ACH Levels | Maintenance | Operations
Elite Facilities | Excellent | Excellent | Excellent
Medium Facilities | Lower | Excellent | Excellent
Low End Facilities | Lower | Poor | Excellent
Low End Facilities | Lower | Excellent | Poor
Low End Facilities | None | Poor | Poor
Where does your facility fall?

## Slide 20: Ventilation Approaches Research Findings
Approach | ACH / e ACH Levels | Comments
Natural Ventilation | 35+ | Open windows & Doors
HVAC | 4 to 6 typical | 12+ ACH are elite settings
Exhaust Fans | 60+ | Old bars, auto & machine shops…
Ceiling Level UV Lights | 24+ eACH | Well established 80+ years
Far UV 222 Lights | 24+ eACH | No need for surface cleaning
Room sanitizers | 1-2 | too small for public rooms, may be okay for small 1 person office
Will revisit the technologies at the end

## Slide 21: Home Ventilation Actions & Costs
Turn on the HVAC fan when guests arrive and turn it off when they leave
What about costs?
Typical home fan motor takes the equivalent power of 1 to 3, 100-watt lightbulbs

## Slide 22: Public Buildings Ventilation Actions & Costs
Must turn on ventilation system 1 hour before and after the public arrives and leaves
Most commercial facilities are not on demand systems and the fans run all the time, no cost impacts
  However, there are serious maintenance issues
  That is why the ACH levels must be determined and posted
Facilities using on demand systems, some cost impacts
  They are negligible because the fans take little power once compared to heating and cooling
  Instead of using the HVAC or exhaust fans they can install ceiling level UV or far UV 222 systems, which will run at about 10% of the mechanical motors

## Slide 23: Commercial Building Challenges
It is more about proper maintenance and operation because this will lead to ACH = 0 or ACH = 1
Are vents blocked
Are dampers partially closed by someone
Are timers working properly
Are sensors, fans, and dampers working properly
Do vents have streamers so people can see system is working
Periodic inspections with documented evidence using certificates that are posted will ensure effective maintenance

## Slide 24: What Can We Do Operations
Turn on the HVAC FANs 1 hour before people enter and 1 hour after people leave the facility
When you enter the facility, make sure the fans are turned on, if not turn them on
Place a sign at each thermostat stating to turn on the fan and show how to turn on the fan
If the fans fail to operate or you are unable to see the thermostat display report it immediately
Setup a training session to show people how to turn on the fans

## Slide 25: What Can We Do Maintenance
Make sure all the HVAC FANS work
Make sure the vents are not blocked or closed
Place streamers on all the vents so people can see they work
Replace the batteries in all the thermostats so that the displays are visible, and people can see what they are doing
Ensure that the filters are replaced every 3 months

## Slide 26: What Can We Do Disclosure
Completed
Using anemometers, measure the air flow from each vent and calculate the measured ACH levels
Suggested
Gather design data from the HVAC vendor or maintenance committee to determine design ACH levels
Disclose ACH levels for each room via email and on website
Post room certificates showing the measured ACH levels
Update the certificates every 3 months to show the system is being monitored and maintained

## Slide 27: Tools to Measure ACH Levels
Tape measure to determine room size
Anemometer
https://www.amazon.com/Anemometer-Handheld-Detector-Temperature-Windsurfing/dp/B07ZJ38ZMX
ACH = Vents cu-ft per hour / room cubic feet

## Slide 28: Measured ACH Level House
Num | Room Name | Num of Vents | ACH | System On yes, no, fail
0. | Living Room | 2 | 2.3 | Yes
1. | Dining Room | 1 | 2.8 | Yes
2. | Family Room | 1 | 1.7 | Yes
3. | Kitchen | 1 | 3.8 | Yes
4. | Breakfast Room | 1 | 4.9 | Yes
5. | Sunroom | 1 | 3.3 | Yes
6. | Bedroom 1 Master | 2 | 3.6 | Yes
7. | Office | 1 | 2.9 | Yes
8. | Bathroom 1 | 1 | 3.4 | Yes
9. | Powder Room | 1 | 6.2 | Yes
Note: Open spaces share ACH with adjacent spaces. All values are approximate because of ceiling height and vent size approximations.

## Slide 29: Measured ACH Level House
Num | Room Name | Num of Vents | ACH | System On yes, no, fail
10. | Foyer (open space) | 0 | 0 | Yes
11. | Loft | 2 | 4.1 | Yes
12. | Bedroom 2 | 2 | 6 | Yes
13. | Bathroom 2 | 1 | 3.8 | Yes
14. | Laundry Room | 1 | 8.2 | Yes
15. | Stairs (open space) | 0 | 0 | Yes
16. | Hall 1 (open space) | 0 | 0 | Yes
17. | Hall 2 (open space) | 0 | 0 | Yes
Note: Open spaces share ACH with adjacent spaces. All values are approximate because of ceiling height and vent size approximations.

## Slide 30: Measured ACH Level House
Room Name | Num of Vents | ACH
Aggregate | 18 | 3.2
Max | - | 8.2
Min (includes 0) | - | 0
Lowest (excludes 0) | - | 1.7
Average ACH (affected by room sizes) | - | 3.3
Note: Open spaces share ACH with adjacent spaces. All values are approximate because of ceiling height and vent size approximations.
HVAC Design ACH = 4
Difference between measured and design is reductions caused by air resistance from filter and ducts

## Slide 31: How was this done
Anemometer
Dollar store broom sticks (2)
Selfie stick to hold Anemometer
ACH = Vents cu-ft per hour / room cubic feet

## Slide 32: Clean Air Buildings Database
https://www.cassbeth.com/cleanairbuildings/index.html
Search examples
  Philadelphia Schools (ACH site survey data)
  Philadelphia Restaurant Program (ACH site survey data)
  School
  Restaurant
  Airport
  Airplane

## Slide 33: Measured ACH Levels Scenario: Generic Example Possible Findings
Num | Room Name | ACH Measured | Control Zone # | System ON yes, no, fail
1. | Ballroom Ceiling Vents | 5.7 | 1, 2 | No
2. | Kitchen | 11 | 1 | No
3. | Library | 6.3 | 3 | No
4. | Sitting Room | 5.2 | 3 | No
5. | Conference Room | 0 | 3 ? | Fail
6. | Office | ? | ? | ?
7. | Exercise Room | 3.2 | 5 | No
8. | Pool Room | 3.6 | 6 | Yes
9. | Game Room 1 | 0 | 4 | Fail
10. | Game Room 2 | 0 | 4 | Fail
Note: Open spaces share ACH with adjacent spaces. All values are approximate because of ceiling height and vent size approximations.

## Slide 34: Measured ACH Levels Scenario: Generic Example Possible Findings
Num | Room Name | ACH Measured | Control Zone # | System ON yes, no, fail
11. | Arts and Crafts Room | 0 | 4 | Fail
12. | Women's Room | ? | ? | ?
13. | Men's Room | 0 | ? | Fail
14. | Lobby | 3.2 | 3 | No
15. | Reception and Hall | 7.6 | 3 | No
16. | Hall 1 Ballroom | 0 | 3 ? | No
17. | Hall 2 Pool Exercise | 0 | 4 | Fail
18. | Hall 3 Game Area | 0 | 4 | Fail
19. | Women’s Pool Area | ? | ? | ?
20. | Men’s Pool Area | 6.5 | ? | Partial Yes
21. | Swimming Pool Floor Vents | 9.9 | ? | Yes
Note: Open spaces share ACH with adjacent spaces. All values are approximate because of ceiling height and vent size approximations.

## Slide 35: Suggested Short Term Action Plan
Fix Zone 3 fan so that it operates
Fix areas that have zero ventilation readings
Open any closed dampers and vents because of previous complaints of hot or cold air
Adjust or change vent types so that there are no complaints but keep the vents open (ball room, perhaps game rooms, library)
Post signs to turn on the fans and provide simple instructions
Post certificates at each thermostat with a date showing last maintenance date and average ACH level
Place streamers on all vents
Do this until the COVID-19 disaster is over in about 10 years

## Slide 36: HVAC Inspection Certificate
Zone (1, 2, 3, 4, 5, 6, pool): example A
HVAC Vendor Name & Visit date: HVAC 05/21/22
Filter Change Date & MERV Rating: 5/21/22 MERV 13
Fan Mode Operational (yes/no): Yes
All Vents Operational (yes/no): Yes
Thermostat Display Visible: (yes/no): Yes
Timers Working & Set: (yes/no): Yes
Thermostat Instructions: (yes/no): Yes
Staff Turn On Fans On Entry (yes/no): Yes
Fan CFM: 1,600

## Slide 37: Room Certificate Key Elements
Room Name & Zone:
Square feet:
Cubic feet:
CFM:
ACH Level:
Vents Unblocked: yes/no
Dampers Open: yes/no
Timers Working: yes/no
Inspection Authority and Date:
Comments:

## Slide 38: Building Certificate Key Elements
Building Name & Address:
Square feet:
Cubic feet:
CFM:
Min ACH Level:
Max ACH Level:
Average ACH Level:
Inspection Authority and Date:
Comments:

## Slide 39: Suggested Long Term Action Plan
Consider replacing existing string lights in the Ball Room and Lobby with ceiling level / upper room UV-C lights
  Proven technology, massive science & engineering going back to 1937
  Used in commercial & industrial settings and public buildings like hospitals, elite schools, elite restaurants, elite condominiums, etc.
  This will add an additional 24 eACH to the Ball Room & Lobby
Consider adding FAR UV-222 lights to other areas
  Relatively new based on LED technology
  Science & engineering based on ceiling level UV-C lights
  This will add an additional 24 eACH to all other rooms
  Will eliminate surface cleaning need
  See next slide for references and presentations

## Slide 40: What Can We Do Suggested Long Term Action Plan
Ceiling level / upper room UV-C and FAR UV-222
The Second Gilbert W. Beebe Webinar: Safety and Efficacy of UVC to Fight Covid-19, National Academies of Sciences, Engineering, and Medicine, Sep 16, 2020.
https://www.nationalacademies.org/event/09-16-2020/the-second-gilbert-w-beebe-webinar-safety-and-efficacy-of-uvc-to-fight-covid-19
The National Academy of Sciences (NAS) is a private, non-profit society of distinguished scholars. Established by an Act of Congress, signed by President Abraham Lincoln in 1863, the NAS is charged with providing independent, objective advice to the nation on matters related to science and technology.

## Slide 41: Ceiling Level UV-C Examples

## Slide 42: FAR UV-222 Examples Surface Cleaning NOT Required!

## Slide 43: Ceiling Level UV-C and FAR UV-222 Characteristics eACH = 24
FAR UV-222
Ceiling Level UV-C

## Slide 44: Closing Comments
In the last century, our parents and grandparents had to deal with tuberculosis and other deadly infections
Vaccines did a great deal to eliminate those contagions, but they would not have worked without the introduction of forced air HVAC systems and ceiling level UV systems
Unlike in the last century no new technology is needed, we just need to use what our parents and grandparents developed
There always will be unvaccinated people
The system solution must use vaccines + ventilation
The analysis clearly shows why; large numbers of people will continue to get sick and die – see this research findings

## Slide 45: ACH Impact on Lives Saved
Naturally Immune % | Vaccine Effectiveness % | Vaccinated % | Deaths @ 3.5% * | UV-C or FAR UV-222 | Deaths @ 3.5% (With UV) | Ventilation Effectiveness 4 AUC | Deaths @ 3.5% (With UV + Ventilation)
10% | 70% | 70% | 5,269,320 | 90% | 526,932 | 28% | 379,391
10% | 90% | 90% | 1,963,080 | 90% | 196,308 | 28% | 141,342
0% | 70% | 70% | 5,854,800 | 90% | 585,480 | 28% | 421,546
0% | 90% | 90% | 2,181,200 | 90% | 218,120 | 28% | 157,046
. |  |  |  |  |  |  | 
0% | 0% | 0% | 11,480,000 | 90% | 1,148,000 | 28% | 826,560
10% | 0% | 0% | 10,332,000 | 90% | 1,033,200 | 28% | 743,904
2020 Analysis: impact of each of the mitigation subsystem on lives saved
* For less than 3.5% just divide all the numbers by 3 and they are still massive

## Slide 46: Closing Comments
It will take years for the building codes to change to include contagion mitigation, so what can we do?
As responsible managers of our children’s future
Stop using the phrase - increase ventilation
We must talk in terms of ventilation performance levels using the decades old ACH levels
We must post ACH levels throughout our buildings

## Slide 47: Closing Comments
We are not here to determine the future minimum ACH levels that will become part of future building certificates of occupancy
We are here to measure and document the building ventilation levels and post the resulting ACH performance levels throughout the building
This approach of building assessment and disclosure was inspired by a 2021 Drexel Faculty Meeting

## Slide 48: Facility Types
Facility Type | ACH Levels | Maintenance | Operations
Elite Facilities | Excellent | Excellent | Excellent
Medium Facilities | Lower | Excellent | Excellent
Low End Facilities | Lower | Poor | Excellent
Low End Facilities | Lower | Excellent | Poor
Low End Facilities | None | Poor | Poor
Where do you want to live and work?

## Slide 49: How to Proceed Grass Roots Level
Fill out and submit the form
Building Ventilation Performance Levels Disclosure Request
https://www.cassbeth.com/cleanairbuildings/info-sheet.html
Click on PDF or .docx links
Print pages 1 - 5 and drop off at clubhouses, work, school, house of worship, restaurants, bars, store customer service desks, etc.

## Slide 50: Links & Contact
This Presentation & All Research
https://www.cassbeth.com/cleanairbuildings/presentations/Ventilation-Education-handouts.pdf
https://www.cassbeth.com/covid-19/index.html (massive)
ACH Assessment Tools
https://www.cassbeth.com/cleanairbuildings/index.html
https://www.cassbeth.com/covid-19/faq.html
Contact
walt@cassbeth.com
walter.sobkiw@drexel.edu

## Slide 51: References CDC ACH Guidelines
[1] CDC Appendix B. Air Guidelines for Environmental Infection Control in Health-Care Facilities (2003) https://www.cdc.gov/infectioncontrol/guidelines/environmental/appendix/air.html
[1.2] CDC Guidelines for Environmental Infection Control in Health-Care Facilities, July 2019. https://www.cdc.gov/infectioncontrol/pdf/guidelines/environmental-guidelines-P.pdf

## Slide 52: References Philadelphia Restaurant Program
[2.1] Enhanced Ventilation Standards for Indoor Dining and Application Form for Increased Dining Capacity, City of Philadelphia, February 14, 2021. webpage https://www.phila.gov/media/20210216105327/Enhanced-Ventilation-Standards-for-Indoor-Dining_2_16_21.pdf
[2.2] Food Establishments That Have Met Enhanced Ventilation Standards to Allow for Increased Indoor Dining Capacity, City of Philadelphia, March 09, 2021. webpage https://www.phila.gov/media/20210311122403/50CapacityRestaurants_030921.pdf
[2.3] EHS Enhanced Ventilation Standards for Indoor Dining, February 16, 2021. webpage https://www.youtube.com/watch?v=HlneLDi9r54
[2.4] EHS TIPS Enhanced Ventilation Standards for Indoor Dining, February 16, 2021. webpage https://www.youtube.com/watch?v=58uRfAxh6Cw

## Slide 53: References School Case History
[3.1] 8 Classmates, 2 Fully Vaccinated Family Members, Test Positive for COVID in Lower Merion, NBC 10 Philadelphia, April 25, 2021. webpage https://www.nbcphiladelphia.com/news/coronavirus/8-classmates-2-fully-vaccinated-family-members-test-positive-for-covid-in-lower-merion/2791754
[3.2] Lower Merion School District says a ventilation flaw could have fueled a COVID-19 outbreak in second-grade classroom, The Philadelphia Inquirer, April 26, 2021. webpage https://www.inquirer.com/education/lower-merion-school-district-penn-valley-covid-outbreak-hvac-20210426.html
[3.3] Drexel Faculty Meeting. The Lower Merion School District staff evaluated the classroom HVAC system and found that a part within the ductwork above the ceiling was mostly closed allowing only about 30% of the maximum amount of fresh air into the room where the 2d grade children were infected. The design requirement for the school HVAC system is 375 CFM and the measured rate was 120 CFM for the affected classroom.

## Slide 54: References Building Codes and Standards
[4.1] International Building Code (IBC), webpage, https://codes.iccsafe.org/content/IBC2018P3/chapter-12-interior-environment#IBC2018P3_Ch12_Sec1202, https://codes.iccsafe.org/content/IBC2021P2/index
[4.2] International Mechanical Code (IMC), webpage https://codes.iccsafe.org/content/IMC2015/chapter-4-ventilation
[4.3] American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE), webpage https://www.ashrae.org

## Slide 55: References Philadelphia Schools Site Surveys
[5] Philadelphia School District, Ventilation and Air Balance Reports, City of Philadelphia. March 22, 2021. webpage https://docs.google.com/spreadsheets/d/18Kn2h5zS6ivX27-msM2Pdy10HUUWaUAomAaXJJ2FK7w/edit#gid=999445241

## Slide 56: References Flu Season Costs
[6.1] Flu Season to Cost Business $17B in Lost Productivity, New Jersey Business & Industry Association NJBIA, January17,2019. webpage https://njbia.org/flu-season-to-cost-business-17b-in-lost-productivity
[6.2] Past Seasons Estimated Influenza Disease Burden, Centers for Disease Control and Prevention, October 01, 2020, webpage https://www.cdc.gov/flu/about/burden/past-seasons.html
[6.3] Inpatient Hospital Stays and Emergency Department Visits Involving Influenza, 2006-2016, Agency for Healthcare Research and Quality, October 2019. webpage https://www.hcup-us.ahrq.gov/reports/statbriefs/sb253-Influenza-Hospitalizations-ED-Visits-2006-2016.jsp