## Instructions
Ventilation Carbon Footprint Model
By Walter Sobkiw
2023-12-01
This analysis comes from COVID-19 Research from a Systems Perspective started in 2020.
Background
We know we need to reduce facility ventilation carbon footprints but not at the cost of lost health or epidemics.
Facility ventilation rates have been dropping since the first energy crisis in the last century.
With sustainability goals, ventilation rates are being forced to drop even further.
The challenge is to actually increase existing poor ventilation rates while reducing carbon footprints.
A systems perspective must be applied to the sustainability (carbon footprint) and ventilation challenges in facilities.
The CAP should include the carbon footprint impacts on ventilation performance levels and help establish a sustainable and healthy ventilation future.
Approach
Establish the ventilation performance levels baseline, a possible approach to gather the data is:
1. Prepare a Ventilation Quality Improvement Indicator (QII) to independently gather data. (one currently exists)
2. Have room attendants (staff, professor, student, or IT staff, etc.) gather the data per the QII.
3. The data feeds into spreadsheets / database / online portal (software exists for online entries)
Example site survey of all classrooms in all schools - Philadelphia 234 schools, 12,000+ rooms
https://docs.google.com/spreadsheets/d/18Kn2h5zS6ivX27-msM2Pdy10HUUWaUAomAaXJJ2FK7w/edit
Proposed CAP Ventilation Goals
1. Establish existing baseline ventilation performance levels and ventilation power needs for each room in all buildings by year 1.
2. Establish ventilation requirement targets across a 5 year period.
3. All buildings should have a ventilation rate of greater than 5 Total ACH in all occupied rooms by year 2. (1)
4. All buildings should have a ventilation rate of greater than 6 Total ACH in all occupied rooms by year 3. (2)
5. All buildings should have a ventilation rate of greater than 12 Total ACH in all occupied rooms by year 5. (3)
6. Total ACH = Mechanical ACH + UV eACH + Other oACH; ACH: Air Changes per Hour
(1) CDC Guidelines for all facilities is 5 ACH
(2) Harvard T.H. Chan 5-step guide to checking ventilation rates in classrooms is 6 ACH (Excellent level selected)
(3) CDC Guidelines for room airborne infections is 12 ACH
General Observations
While climate action solutions are complex and difficult to implement, fixing the ventilation in facilities is relatively easy.
The ventilation challenge is a social challenge. Everyone just assumes everything is okay, but it is not okay.
Research suggests that there are operational and maintenance problems with most facilities that must be corrected.
Once the operational and maintenance problems are corrected then some systems may be too small and plans for upgrades are needed.
For facilities needing upgrades, data is needed for sustainable (low carbon footprint) solutions that also meet ventilation requirements.
This research suggests that an independent Ventilation QII should be used to gather operational, maintenance, and system performance levels.
A QII is documented evidence that is not easily refuted by outsourced energy companies or staff that place all their faith in automated sensors.
Because facility ventilation has a large carbon footprint it should be an integral part of any climate action plan.
To ignore ventilation runs the risks of:
1. unhealthy infrastructure that will make people sick and may lead to future epidemics
2. poor carbon footprint management if poor solutions are selected
Ventilation awareness must be developed just like there is now awareness of sustainability and climate change.
This Spreadsheet - 2 models are offered
This Spreadsheet is an example analysis for potential CAP.
The Buildings tab has summary data of all the buildings. The focus is ventilation data and power consumption including green power.
Each tab (Bld 1) contains survey data for each room in the building. This data is sourced from the QIIs rather than the HVAC staff.
If the HVAC staff provide room ventilation level data then validations can be performed against the QII data.
The Source tab has power estimates for mechanical and other ventilation systems. It is expected that the source tab will change and grow.
This analysis shows the ventilation power levels for a baseline with poor ventilation and other architecture approaches with fixed and improved ventilation.
The Buildings and Building Summary tabs shows the results of the fine grain analysis.
This model is a fine grain model because it is based on room data that is then summed up for a building.
If the data is captured for each room then the model represents the actual results of a building.
The CG tab is a coarse grain model. It can never represent the actual situation unlike the fine grain model, but it can be useful for quick analysis of technology alternatives.
Carbon footprint is determined using the CO2 kWh tab. Model reports power because carbon footprint will change with energy mix.

## CO2 kWh
https://www.quora.com/Whats-the-carbon-footprint-of-1-kWh-of-electricity
Type of Powerplant
Fuel | Efficiency | Percentage Used in United States | Total Energy (Billion kWh) | CO2 per kWh Created by Powerplant (lbs.)
Natural Gas | 38% | 38.6% | 1.575 | 0.9
Coal | 29% | 21.8% | 899 | 2.34
Oil | 31% | 0.5% | 19 | 1.78
Fossil Fuel Total |  | 60 9% | 2.493 | 1.42 Weighted Avg
Nuclear | 290% | 18.9% | 778 | 0.03
Wind | 1164% | 9.2% | 380 | 0.02
Hydro | 317% | 6.3% | 260 | 0.05
Solar | 207% | 2.8% | 115 | 0.11
Biomass | 52% | 1.3% | 55 | 0.51
Geothermal | 514% | 0 4% | 16 | 0.08
Renewable Fuel Total |  | 38.5% | 1588 | 0.05 Weighted Avg
Total |  | 99 4% | 4081 | 0.89 Weighted Avg
What's the carbon footprint of 1 kWh of electricity?
This is information compiled from the US Dept. of Energy for various types of powerplants.
In the US, the weighted average for all types of powerplants is 0.89 lbs CO2 per kWh.
The average EV gets 3.6 miles per kWh. If this energy is used to charge an EV, the EV contributes 0.25 lbs CO2 per mile.
Burning a gallon of gasoline contributes 19.7 lbs CO2. The average ICE in the US gets 25 MPG, which would contribute 0.79 lbs, more than three times more than an average EV.
Alternate source check
Country | g CO2/kWh | US Dept of Energy | Comments
In USA | 460 | 404.06 | 454 g/lb. close enough.
China around | 600
Germany | 560
Sweden | 7
Norway | 9
In Sweden
Solar cells about | 27
Windpower around | 15–20
Nuclear | 4
Hydropower | 9

## Results
Scenario | Fine Grain Power | Coarse Grain Power | Fine Grain ACH | Course Grain ACH | Rating
Baseline | 28179 | 29276.7345 | 3.4179 | 4 | Poor
Arch A | 39351.2874 | 36595.9181 | 5.0513 | 5 | CDC LVL
Arch B | 30027.8285 | 30498.467 | 5.0883 | 5 | CDC LVL
Arch C | 38074.1885 | 39050.5943 | 12.0203 | 12 | CDC Airborne LVL
Assumptions |  |  |  |  | Givens
Room Height |  |  |  |  | Square Feet
Room CFM
Mech Watts / CFM |  |  |  |  | Givens shown in spreadsheet
UV Watts / Cu-Ft |  |  |  |  | Bld Avg kWh/Mon actual
Fine Grain baseline has failed rooms |  |  |  |  | Green Bld Avg kWh/Mon actual

## Buildings CG
ACH = CFM * 60 / cuft
CFM = ACH*cuft/60
Watts = CuFt*CFM* W/CFM
This sheet models buildings as a whole rather than as a summation of the individual rooms.
The issue with this approach is that there is no visibility into problem rooms within buildings.
Model Type | Coarse Grain | [9 empty] | (1) Total ACH = room ACH + room eACH; ACH: Air Changes per Hour
Mech Watts / CFM 2023 | 0.5175 | [9 empty] | (2) CDC Guidelines for all facilities
Mech Watts / CFM 2025 | 0.5175 | [9 empty] | (3) Harvard T.H. Chan 5-step guide to checking ventilation rates in classrooms; Excellent Level selected
UV Watts / Cu-Ft 2023 | 0.017276 | [9 empty] | (4) CDC Guidelines for room airborne infections
Far UV Watts / Cu-Ft 2023 | 0.017276
[6 empty] | Totals | 81853 | [6 empty] | 29276.7345 | 0 | 29276.7345 |  |  |  |  | 36595.9181 | 0 | 36595.9181 |  |  |  |  | 29276.7345 | 1221.7325 | 30498.467 |  |  |  |  | 29276.7345 | 9773.8598 | 39050.5943
[14 empty] | Baseline 2023 | [6 empty] | Arch A 2023 | [6 empty] | Arch B 2023 | [6 empty] | Arch C 2026
Property Name | Portfolio Manager ID | Street Address | Year Built | Property Type - Self-Selected | Occupancy (%) | # of Buildings? | Sq-Ft actual | Ht-ft avg assumed | Cu-Ft est | Bld Avg Usage kWh/Mon actual 2023 | Bld Avg Watts actual 2022 | Greenb Bld Avg Usage kWh/Mon actual 2022 | Green Bld Avg Watts actual 2022 | Ventilation Mech Watts est | Ventilation eACH Watts est | Ventilation Total Watts est | eACH assumed | ACH assumed | Total ACH Avg est (1) | Ventilation Rating | Ventilation Mech Watts est | Ventilation eACH Watts est | Ventilation Total Watts est | eACH assumed | ACH assumed | Total ACH Avg est (1) | Ventilation Rating | Ventilation Mech Watts est | Ventilation eACH Watts est | Ventilation Total Watts est | eACH assumed | ACH assumed | Total ACH Avg est (1) | Ventilation Rating | Ventilation Mech Watts est | Ventilation eACH Watts est | Ventilation Total Watts est | eACH assumed | ACH assumed | Total ACH Avg est (1) | Ventilation Rating | Total ACH Goal 2024 (2) | Total ACH Goal 2025 (3) | Total ACH Goal 2026 (4)
Example |  |  |  |  | 100 | 1 | 81853 | 10.3674 | 848601 | 108485 | 150673.6111 | 43394 | 60269.4444 | 29276.7345 | 0 | 29276.7345 | 0 | 4 | 4 | Low | 36595.9181 | 0 | 36595.9181 | 0 | 5 | 5 | CDC LVL | 29276.7345 | 1221.7325 | 30498.467 | 1 | 4 | 5 | CDC LVL | 29276.7345 | 9773.8598 | 39050.5943 | 8 | 4 | 12 | CDC Airborne LVL | #REF! | #REF! | #REF!

## Buildings Summary
(1) Total ACH = room ACH + room eACH; ACH: Air Changes per Hour
(2) CDC Guidelines for all facilities
(3) Harvard T.H. Chan 5-step guide to checking ventilation rates in classrooms; Excellent Level selected
This sheet compares the ventilation power needs with the the baseline and various architecture approaches. | [11 empty] | (4) CDC Guidelines for room airborne infections
This approach shows that there may be problem rooms (ACH min). Detail sheet shows which rooms have problems.
Model Type | Fine Grain
[6 empty] | Totals | 81853 | 28179 |  |  |  | 39351.2874 |  |  |  | 30027.8285 |  |  |  | 38074.1885
[8 empty] | Baseline est 2023 |  |  |  | Arch A est 2023 |  |  |  | Arch B est 2023 |  |  |  | Arch C est 2026
Property Name | Portfolio Manager ID | Street Address | Year Built | Property Type - Self-Selected | Occupancy (%) | # of Buildings? | Sq-Ft actual | Ventilation Total Watts est | Total ACH Min est (1) | Total ACH Avg est (1) | Ventilation Rating | Ventilation Total Watts est | Total ACH Min est (1) | Total ACH Avg est (1) | Ventilation Rating | Ventilation Total Watts est | Total ACH Min est (1) | Total ACH Avg est (1) | Ventilation Rating | Ventilation Total Watts est | Total ACH Min est (1) | Total ACH Avg est (1) | Ventilation Rating | Total ACH Goal 2024 (2) | Total ACH Goal 2025 (3) | Total ACH Goal 2026 (4)
Example |  |  |  |  | 100 | 1 | 81853 | 28179 | 0.3 | 3.4179 | Poor | 39351.2874 | 5 | 5.0513 | CDC LVL | 30027.8285 | 5 | 5.0883 | CDC LVL | 38074.1885 | 12 | 12.0203 | CDC Airborne LVL | 5 | 6 | 12

## Buildings Baseline
(1) Total ACH = room ACH + room eACH; ACH: Air Changes per Hour
(2) CDC Guidelines for all facilities
(3) Harvard T.H. Chan 5-step guide to checking ventilation rates in classrooms; Excellent Level selected
This sheet summarizes the ventilation performance levels for all the buildings and captures the power required to achieve the ventilation levels. | [12 empty] | (4) CDC Guidelines for room airborne infections
Model Type | Fine Grain
[6 empty] | Totals | 81853 | 848601 | 27349.875 | 829.2683 | 28179.1433 | 108485 | 150673.6111 | 43394 | 60269.4444 | Room CFM est 2023 |  |  | Room ACH est 2023 |  |  | Room eACH est 2023
Property Name | Portfolio Manager ID | Street Address | Year Built | Property Type - Self-Selected | Occupancy (%) | # of Buildings? | Sq-Ft actual | Cu-Ft est | Mech Ventilation Watts est | UV Ventilation Watts est | Ventilation Total Watts est | Bld Avg Usage kWh/Mon actual 2023 | Bld Avg Watts actual 2022 | Greenb Bld Avg Usage kWh/Mon actual 2022 | Green Bld Avg Watts actual 2022 | CFM Min (worst case room) | CFM Max (best case room) | CFM Avg (blding avg) | ACH Min (worst case room) | ACH Max (best case room) | ACH Avg (blding avg) | eACH min (worst case room) | eACH max (best case room) | eACH avg (blding avg) | Total ACH Min est (1) | Total ACH Avg est (1) | Ventilation Rating | Total ACH Goal 2024 (2) | Total ACH Goal 2025 (3) | Total ACH Goal 2026 (4)
Example |  |  |  |  | 100 | 1 | 81853 | 848601 | 27349.875 | 829.2683 | 28179.1433 | 108485 | 150673.6111 | 43394 | 60269.4444 | 5 | 6650 | 210.985 | 0.31847 | 7.1698 | 3.3666 | 0 | 12 | 0.051282 | 0.31847 | 3.4179 | Poor | 5 | 6 | 12

## Buildings Arch A
(1) Total ACH = room ACH + room eACH; ACH: Air Changes per Hour
(2) CDC Guidelines for all facilities
(3) Harvard T.H. Chan 5-step guide to checking ventilation rates in classrooms; Excellent Level selected
This sheet summarizes the ventilation performance levels for all the buildings and captures the power required to achieve the ventilation levels. | [12 empty] | (4) CDC Guidelines for room airborne infections
Model Type | Fine Grain
[6 empty] | Totals | 81853 | 848601 | 38522.0191 | 829.2683 | 39351.2874 | 108485 | 150673.6111 | 43394 | 60269.4444 | Room CFM est 2023 |  |  | Room ACH est 2023 |  |  | Room eACH est 2023
Property Name | Portfolio Manager ID | Street Address | Year Built | Property Type - Self-Selected | Occupancy (%) | # of Buildings? | Sq-Ft actual | Cu-Ft est | Mech Ventilation Watts est | UV Ventilation Watts est | Ventilation Total Watts est | Bld Avg Usage kWh/Mon actual 2023 | Bld Avg Watts actual 2022 | Greenb Bld Avg Usage kWh/Mon actual 2022 | Green Bld Avg Watts actual 2022 | CFM Min (worst case room) | CFM Max (best case room) | CFM Avg (blding avg) | ACH Min (worst case room) | ACH Max (best case room) | ACH Avg (blding avg) | eACH min (worst case room) | eACH max (best case room) | eACH avg (blding avg) | Total ACH Min est (1) | Total ACH Avg est (1) | Ventilation Rating | Total ACH Goal 2024 (2) | Total ACH Goal 2025 (3) | Total ACH Goal 2026 (4)
Example |  |  |  |  | 100 | 1 | 81853 | 848601 | 38522.0191 | 829.2683 | 39351.2874 | 108485 | 150673.6111 | 43394 | 60269.4444 | 24.75 | 8666.6667 | 302.2083 | 5 | 5 | 5 | 0 | 12 | 0.051282 | 5 | 5.0513 | CDC LVL | 5 | 6 | 12

## All Blds Arch B
(1) Total ACH = room ACH + room eACH; ACH: Air Changes per Hour
(2) CDC Guidelines for all facilities
(3) Harvard T.H. Chan 5-step guide to checking ventilation rates in classrooms; Excellent Level selected
This sheet summarizes the ventilation performance levels for all the buildings and captures the power required to achieve the ventilation levels. | [12 empty] | (4) CDC Guidelines for room airborne infections
Model Type | Fine Grain
[6 empty] | Totals | 81853 | 848601 | 27349.875 | 2677.9535 | 30027.8285 | 108485 | 150673.6111 | 43394 | 60269.4444 | Room CFM est 2023 |  |  | Room ACH est 2023 |  |  | Room eACH est 2023
Property Name | Portfolio Manager ID | Street Address | Year Built | Property Type - Self-Selected | Occupancy (%) | # of Buildings? | Sq-Ft actual | Cu-Ft est | Mech Ventilation Watts est | UV Ventilation Watts est | Ventilation Total Watts est | Bld Avg Usage kWh/Mon actual 2023 | Bld Avg Watts actual 2022 | Greenb Bld Avg Usage kWh/Mon actual 2022 | Green Bld Avg Watts actual 2022 | CFM Min (worst case room) | CFM Max (best case room) | CFM Avg (blding avg) | ACH Min (worst case room) | ACH Max (best case room) | ACH Avg (blding avg) | eACH min (worst case room) | eACH max (best case room) | eACH avg (blding avg) | Total ACH Min est (1) | Total ACH Avg est (1) | Ventilation Rating | Total ACH Goal 2024 (2) | Total ACH Goal 2025 (3) | Total ACH Goal 2026 (4)
Example |  |  |  |  | 100 | 1 | 81853 | 848601 | 27349.875 | 2677.9535 | 30027.8285 | 108485 | 150673.6111 | 43394 | 60269.4444 | 5 | 6650 | 210.985 | 0.31847 | 7.1698 | 3.3666 | 0.066667 | 12 | 1.7217 | 5 | 5.0883 | CDC LVL | 5 | 6 | 12

## Bld 1 Baseline
Building | Example
Survey Team | TBD | [21 empty] | ACH = CFM * 60 / cuft
Survey Date | TBD | [21 empty] | CFM = ACH*cuft/60
Purpose | This sheet captures the ventilation performance level in each room and the power required for the ventilation level achieved. | [23 empty] | cuft | CFM |  |  | ACH
Note | Once a survey is performed these values will be updated. | [23 empty] | 31500 | 2362.5 |  |  | 4.5
Ventilation Type | DCV: occupancy, timers, temperature, humidity | [21 empty] | 2100 | 15 | 31500 | 2375 | 2500 | 0.95 | 4.5238
Sensors | Particle, CO2
Control | Outsourced to Energy Company XYZ
Model Type | Fine Grain
Mech Watts / CFM 2023 | 0.5175
Mech Watts / CFM 2025 | 0.5175 |  |  | Min | 33 | 800 | 9127 | 9 | 297 | 5 | 25 | 0.1 | 0.31847 | 0 | 0.31847 | Min | 12.9375 | 0 | 0 | 12.9375
UV Watts / Cu-Ft 2023 | 0.017276 |  |  | Max | 5200 | 24627 | 24627 | 20 | 104000 | 6650 | 7000 | 0.95 | 7.1698 | 12 | 16.75 | Max | 3622.5 | 829.2683 | 0.40061 | 3622.5
Far UV Watts / Cu-Ft 2023 | 0.017276 |  |  | Avg | 339.2692 | 2560.9355 | 11341.2857 | 9.1453 | 3626.5 | 210.985 | 225.8547 | 0.80209 | 3.3666 | 0.051282 | 3.4179 | Avg | 116.8798 | 3.5439 | 0.001712 | 120.4237
Totals |  |  |  |  | 79389 | 79389 | 79389 | 9 | 848601 | 49370.5 | 52850 | [5 empty] | 27349.875 | 829.2683 | 0.40061 | 28179.1433
Room Name | Number | Flr | Area | Zone | Sq-Ft | Area Sq-Ft | Floor Sq-Ft | Ht Ft | Cu-Ft | Actual CFM | Design CFM | Actual / Design | ACH | eACH | Total ACH | Ventilation Rating | Mech Watts 2023 | UV-C Watts | UV Watts / Mech Watts | Total Watts | ACH | Scale Setings
Cafe | 100 | 1 | 1 |  | 3200 |  |  | 15 | 48000 | 3800 | 4000 | 0.95 | 4.75 | 12 | 16.75 | CDC Airborne LVL | 2070 | 829.2683 | 0.40061 | 2899.2683 | 0 | Fail
Transit Lounge | 101 | 1 | 2 |  | 2100 |  |  | 15 | 31500 | 2375 | 2500 | 0.95 | 4.5238 | 0 | 4.5238 | Low | 1293.75 | 0 | 0 | 1293.75 | 0.9 | Fail
Lobby | 102 | 1 | 3 |  | 4100 |  |  | 20 | 82000 | 4750 | 5000 | 0.95 | 3.4756 | 0 | 3.4756 | Poor | 2587.5 | 0 | 0 | 2587.5 | 1 | Very Bad
Lecture Hall | 103 | 1 | 4 |  | 5200 |  |  | 20 | 104000 | 6650 | 7000 | 0.95 | 3.8365 | 0 | 3.8365 | Poor | 3622.5 | 0 | 0 | 3622.5 | 2 | Bad
Space 1 | 104 | 1 | 5 |  | 3042.3333 |  |  | 9 | 27381 | 2000 | 600 | 0.95 | 4.3826 | 0 | 4.3826 | Low | 310.5 | 0 | 0 | 310.5 | 3 | Poor
Space 2 | 105 | 1 | 5 |  | 3042.3333 |  |  | 9 | 27381 | 2000 | 600 | 0.95 | 4.3826 | 0 | 4.3826 | Low | 310.5 | 0 | 0 | 310.5 | 4 | Low
Space 3 | 106 | 1 | 5 |  | 3042.3333 |  |  | 9 | 27381 | 2000 | 600 | 0.95 | 4.3826 | 0 | 4.3826 | Low | 310.5 | 0 | 0 | 310.5 | 5 | CDC LVL
Restrooms | 107 | 1 | 6 |  | 900 | 24627 | 24627 | 9 | 8100 | 570 | 600 | 0.95 | 4.2222 | 0 | 4.2222 | Low | 310.5 | 0 | 0 | 310.5 | 6 | CDC & Harvard LVL
Conference Room | 200 | 2 | 1 |  | 354 |  |  | 9 | 3186 | 213.75 | 225 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 116.4375 | 0 | 0 | 116.4375 | 7 | CDC & Harvard LVL
Office | 201 | 2 | 1 |  | 264 |  |  | 9 | 2376 | 142.5 | 150 | 0.95 | 3.5985 | 0 | 3.5985 | Poor | 77.625 | 0 | 0 | 77.625 | 8 | CDC & Harvard LVL
Office | 202 | 2 | 1 |  | 168 |  |  | 9 | 1512 | 25 | 100 | 0.25 | 0.99206 | 0 | 0.99206 | Fail | 51.75 | 0 | 0 | 51.75 | 9 | CDC & Harvard LVL
Office | 203 | 2 | 1 |  | 171 |  |  | 9 | 1539 | 25 | 100 | 0.25 | 0.97466 | 0 | 0.97466 | Fail | 51.75 | 0 | 0 | 51.75 | 10 | CDC & Harvard LVL
Office | 204 | 2 | 1 |  | 169 |  |  | 9 | 1521 | 95 | 100 | 0.95 | 3.7475 | 0 | 3.7475 | Poor | 51.75 | 0 | 0 | 51.75 | 11 | CDC & Harvard LVL
Office | 205 | 2 | 1 |  | 171 |  |  | 9 | 1539 | 95 | 100 | 0.95 | 3.7037 | 0 | 3.7037 | Poor | 51.75 | 0 | 0 | 51.75 | 12 | CDC Airborne LVL
Bull Penns | 206 | 2 | 1 |  | 600 |  |  | 9 | 5400 | 200 | 400 | 0.5 | 2.2222 | 0 | 2.2222 | Bad | 207 | 0 | 0 | 207
Copy | 207 | 2 | 1 |  | 97 |  |  | 9 | 873 | 47.5 | 50 | 0.95 | 3.2646 | 0 | 3.2646 | Poor | 25.875 | 0 | 0 | 25.875
Break Room | 208 | 2 | 1 |  | 99 | 2093 |  | 9 | 891 | 47.5 | 50 | 0.95 | 3.1987 | 0 | 3.1987 | Poor | 25.875 | 0 | 0 | 25.875
Common Area | 209 | 2 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 0 | 3.8704 | Poor | 284.625 | 0 | 0 | 284.625
Office | 210 | 2 | 2 |  | 136 |  |  | 9 | 1224 | 95 | 100 | 0.95 | 4.6569 | 0 | 4.6569 | Low | 51.75 | 0 | 0 | 51.75
Office | 211 | 2 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 0 | 1.0101 | Very Bad | 51.75 | 0 | 0 | 51.75
Office | 212 | 2 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 213 | 2 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 214 | 2 | 2 |  | 154 |  |  | 9 | 1386 | 95 | 100 | 0.95 | 4.1126 | 0 | 4.1126 | Low | 51.75 | 0 | 0 | 51.75
Bull Penns | 215 | 2 | 2 |  | 905 |  |  | 9 | 8145 | 50 | 200 | 0.25 | 0.36832 | 0 | 0.36832 | Fail | 103.5 | 0 | 0 | 103.5
Copy Workroom | 216 | 2 | 2 |  | 92 |  |  | 9 | 828 | 47.5 | 50 | 0.95 | 3.442 | 0 | 3.442 | Poor | 25.875 | 0 | 0 | 25.875
Storage | 217 | 2 | 2 |  | 40 | 2632 |  | 9 | 360 | 23.75 | 25 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 12.9375 | 0 | 0 | 12.9375
Conference Room | 218 | 2 | 3 |  | 156 |  |  | 9 | 1404 | 95 | 100 | 0.95 | 4.0598 | 0 | 4.0598 | Low | 51.75 | 0 | 0 | 51.75
Interview Room | 219 | 2 | 3 |  | 70 |  |  | 9 | 630 | 47.5 | 50 | 0.95 | 4.5238 | 0 | 4.5238 | Low | 25.875 | 0 | 0 | 25.875
Storage | 220 | 2 | 3 |  | 33 |  |  | 9 | 297 | 23.75 | 25 | 0.95 | 4.798 | 0 | 4.798 | Low | 12.9375 | 0 | 0 | 12.9375
File Storage | 221 | 2 | 3 |  | 136 |  |  | 9 | 1224 | 71.25 | 75 | 0.95 | 3.4926 | 0 | 3.4926 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 222 | 2 | 3 |  | 169 |  |  | 9 | 1521 | 95 | 100 | 0.95 | 3.7475 | 0 | 3.7475 | Poor | 51.75 | 0 | 0 | 51.75
Office | 223 | 2 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0 | 4.0948 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 224 | 2 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 225 | 2 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 226 | 2 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0 | 4.0948 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 227 | 2 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 0 | 3.9916 | Poor | 38.8125 | 0 | 0 | 38.8125
Reception | 228 | 2 | 3 |  | 772 |  |  | 9 | 6948 | 100 | 400 | 0.25 | 0.86356 | 0 | 0.86356 | Fail | 207 | 0 | 0 | 207
Restroom Men | 229 | 2 | 3 |  | 172 | 2095 |  | 9 | 1548 | 95 | 100 | 0.95 | 3.6822 | 0 | 3.6822 | Poor | 51.75 | 0 | 0 | 51.75
Restroom Womens | 230 | 2 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 0 | 3.0596 | Poor | 51.75 | 0 | 0 | 51.75
Hall | 231 | 2 | 4 |  | 600 |  |  | 9 | 5400 | 285 | 300 | 0.95 | 3.1667 | 0 | 3.1667 | Poor | 155.25 | 0 | 0 | 155.25
Mechanical Shaft | 232 | 2 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 0 | 3.1667 | Poor | 103.5 | 0 | 0 | 103.5
Elevators | 233 | 2 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 0 | 4.2222 | Low | 103.5 | 0 | 0 | 103.5
Stairs | 233 | 2 | 5 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 0 | 3.1667 | Poor | 103.5 | 0 | 0 | 103.5
Stairs | 234 | 2 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 0 | 3.1667 | Poor | 103.5 | 0 | 0 | 103.5
Office | 300 | 3 | 1 |  | 121 |  |  | 9 | 1089 | 71.25 | 75 | 0.95 | 3.9256 | 0 | 3.9256 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 301 | 3 | 1 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 0 | 3.9916 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 302 | 3 | 1 |  | 119 |  |  | 9 | 1071 | 19.5 | 75 | 0.26 | 1.0924 | 0 | 1.0924 | Very Bad | 38.8125 | 0 | 0 | 38.8125
Office | 303 | 3 | 1 |  | 189 |  |  | 9 | 1701 | 95 | 100 | 0.95 | 3.351 | 0 | 3.351 | Poor | 51.75 | 0 | 0 | 51.75
Office | 304 | 3 | 1 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 305 | 3 | 1 |  | 117 |  |  | 9 | 1053 | 71.25 | 75 | 0.95 | 4.0598 | 0 | 4.0598 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 306 | 3 | 1 |  | 113 |  |  | 9 | 1017 | 71.25 | 75 | 0.95 | 4.2035 | 0 | 4.2035 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 306 | 3 | 1 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 38.8125 | 0 | 0 | 38.8125
Collaboration | 305 | 3 | 1 |  | 290 |  |  | 9 | 2610 | 190 | 200 | 0.95 | 4.3678 | 0 | 4.3678 | Low | 103.5 | 0 | 0 | 103.5
Admin | 305 | 3 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 0 | 1.1905 | Very Bad | 103.5 | 0 | 0 | 103.5
Reception | 306 | 3 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 0 | 1.1905 | Very Bad | 103.5 | 0 | 0 | 103.5
Copy | 307 | 3 | 1 |  | 82 |  |  | 9 | 738 | 47.5 | 50 | 0.95 | 3.8618 | 0 | 3.8618 | Poor | 25.875 | 0 | 0 | 25.875
Break Room | 307 | 3 | 1 |  | 72 |  |  | 9 | 648 | 47.5 | 50 | 0.95 | 4.3981 | 0 | 4.3981 | Low | 25.875 | 0 | 0 | 25.875
IT | 308 | 3 | 1 |  | 73 | 2093 |  | 9 | 657 | 47.5 | 50 | 0.95 | 4.3379 | 0 | 4.3379 | Low | 25.875 | 0 | 0 | 25.875
Common Area | 309 | 3 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 0 | 3.8704 | Poor | 284.625 | 0 | 0 | 284.625
Office | 310 | 3 | 2 |  | 131 |  |  | 9 | 1179 | 7.5 | 75 | 0.1 | 0.38168 | 0 | 0.38168 | Fail | 38.8125 | 0 | 0 | 38.8125
Office | 311 | 3 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 0 | 1.0101 | Very Bad | 51.75 | 0 | 0 | 51.75
Office | 312 | 3 | 2 |  | 120 |  |  | 9 | 1080 | 7.5 | 75 | 0.1 | 0.41667 | 0 | 0.41667 | Fail | 38.8125 | 0 | 0 | 38.8125
Office | 313 | 3 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 313 | 3 | 2 |  | 165 |  |  | 9 | 1485 | 95 | 100 | 0.95 | 3.8384 | 0 | 3.8384 | Poor | 51.75 | 0 | 0 | 51.75
Office | 314 | 3 | 2 |  | 131 |  |  | 9 | 1179 | 95 | 100 | 0.95 | 4.8346 | 0 | 4.8346 | Low | 51.75 | 0 | 0 | 51.75
Bull Penns | 315 | 3 | 2 |  | 900 | 2632 |  | 9 | 8100 | 50 | 200 | 0.25 | 0.37037 | 0 | 0.37037 | Fail | 103.5 | 0 | 0 | 103.5
Meeting Room | 316 | 3 | 3 |  | 417 |  |  | 9 | 3753 | 285 | 300 | 0.95 | 4.5564 | 0 | 4.5564 | Low | 155.25 | 0 | 0 | 155.25
Research Room | 317 | 3 | 3 |  | 201 |  |  | 9 | 1809 | 118.75 | 125 | 0.95 | 3.9386 | 0 | 3.9386 | Poor | 64.6875 | 0 | 0 | 64.6875
Office | 318 | 3 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 319 | 3 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0 | 4.0948 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 320 | 3 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 321 | 3 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 322 | 3 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0 | 4.0948 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 323 | 3 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 0 | 3.9916 | Poor | 38.8125 | 0 | 0 | 38.8125
Hall | 324 | 3 | 3 |  | 600 |  |  | 9 | 5400 | 30 | 300 | 0.1 | 0.33333 | 0 | 0.33333 | Fail | 155.25 | 0 | 0 | 155.25
Restroom Men | 325 | 3 | 3 |  | 172 | 2095 |  | 9 | 1548 | 10 | 100 | 0.1 | 0.3876 | 0 | 0.3876 | Fail | 51.75 | 0 | 0 | 51.75
Restroom Womens | 326 | 3 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 0 | 3.0596 | Poor | 51.75 | 0 | 0 | 51.75
Hall | 327 | 3 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 0 | 3.6944 | Poor | 181.125 | 0 | 0 | 181.125
Mechanical Shaft | 328 | 3 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 0 | 3.1667 | Poor | 103.5 | 0 | 0 | 103.5
Elevators | 329 | 3 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 0 | 4.2222 | Low | 103.5 | 0 | 0 | 103.5
Stairs | 329 | 3 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 129.375 | 0 | 0 | 129.375
Stairs | 330 | 3 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 129.375 | 0 | 0 | 129.375
Office | 300 | 4 | 1 |  | 121 |  |  | 9 | 1089 | 71.25 | 75 | 0.95 | 3.9256 | 0 | 3.9256 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 301 | 4 | 1 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 0 | 3.9916 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 302 | 4 | 1 |  | 119 |  |  | 9 | 1071 | 19.5 | 75 | 0.26 | 1.0924 | 0 | 1.0924 | Very Bad | 38.8125 | 0 | 0 | 38.8125
Office | 303 | 4 | 1 |  | 189 |  |  | 9 | 1701 | 95 | 100 | 0.95 | 3.351 | 0 | 3.351 | Poor | 51.75 | 0 | 0 | 51.75
Office | 304 | 4 | 1 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 305 | 4 | 1 |  | 117 |  |  | 9 | 1053 | 71.25 | 75 | 0.95 | 4.0598 | 0 | 4.0598 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 306 | 4 | 1 |  | 113 |  |  | 9 | 1017 | 71.25 | 75 | 0.95 | 4.2035 | 0 | 4.2035 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 306 | 4 | 1 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 38.8125 | 0 | 0 | 38.8125
Collaboration | 305 | 4 | 1 |  | 290 |  |  | 9 | 2610 | 190 | 200 | 0.95 | 4.3678 | 0 | 4.3678 | Low | 103.5 | 0 | 0 | 103.5
Admin | 305 | 4 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 0 | 1.1905 | Very Bad | 103.5 | 0 | 0 | 103.5
Reception | 306 | 4 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 0 | 1.1905 | Very Bad | 103.5 | 0 | 0 | 103.5
Copy | 307 | 4 | 1 |  | 82 |  |  | 9 | 738 | 47.5 | 50 | 0.95 | 3.8618 | 0 | 3.8618 | Poor | 25.875 | 0 | 0 | 25.875
Break Room | 307 | 4 | 1 |  | 72 |  |  | 9 | 648 | 47.5 | 50 | 0.95 | 4.3981 | 0 | 4.3981 | Low | 25.875 | 0 | 0 | 25.875
IT | 308 | 4 | 1 |  | 73 | 2093 |  | 9 | 657 | 47.5 | 50 | 0.95 | 4.3379 | 0 | 4.3379 | Low | 25.875 | 0 | 0 | 25.875
Common Area | 309 | 4 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 0 | 3.8704 | Poor | 284.625 | 0 | 0 | 284.625
Office | 310 | 4 | 2 |  | 131 |  |  | 9 | 1179 | 7.5 | 75 | 0.1 | 0.38168 | 0 | 0.38168 | Fail | 38.8125 | 0 | 0 | 38.8125
Office | 311 | 4 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 0 | 1.0101 | Very Bad | 51.75 | 0 | 0 | 51.75
Office | 312 | 4 | 2 |  | 120 |  |  | 9 | 1080 | 7.5 | 75 | 0.1 | 0.41667 | 0 | 0.41667 | Fail | 38.8125 | 0 | 0 | 38.8125
Office | 313 | 4 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 313 | 4 | 2 |  | 165 |  |  | 9 | 1485 | 95 | 100 | 0.95 | 3.8384 | 0 | 3.8384 | Poor | 51.75 | 0 | 0 | 51.75
Office | 314 | 4 | 2 |  | 131 |  |  | 9 | 1179 | 95 | 100 | 0.95 | 4.8346 | 0 | 4.8346 | Low | 51.75 | 0 | 0 | 51.75
Bull Penns | 315 | 4 | 2 |  | 900 | 2632 |  | 9 | 8100 | 50 | 200 | 0.25 | 0.37037 | 0 | 0.37037 | Fail | 103.5 | 0 | 0 | 103.5
Meeting Room | 316 | 4 | 3 |  | 265 |  |  | 9 | 2385 | 285 | 300 | 0.95 | 7.1698 | 0 | 7.1698 | CDC & Harvard LVL | 155.25 | 0 | 0 | 155.25
Research Room | 317 | 4 | 3 |  | 128 |  |  | 9 | 1152 | 118.75 | 125 | 0.95 | 6.1849 | 0 | 6.1849 | CDC & Harvard LVL | 64.6875 | 0 | 0 | 64.6875
Office | 318 | 4 | 3 |  | 92 |  |  | 9 | 828 | 71.25 | 75 | 0.95 | 5.163 | 0 | 5.163 | CDC LVL | 38.8125 | 0 | 0 | 38.8125
Office | 319 | 4 | 3 |  | 105 |  |  | 9 | 945 | 71.25 | 75 | 0.95 | 4.5238 | 0 | 4.5238 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 320 | 4 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 321 | 4 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0 | 4.0948 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 322 | 4 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 322 | 4 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 322 | 4 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0 | 4.0948 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 323 | 4 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 0 | 3.9916 | Poor | 38.8125 | 0 | 0 | 38.8125
Hall | 324 | 4 | 3 |  | 628 |  |  | 9 | 5652 | 30 | 300 | 0.1 | 0.31847 | 0 | 0.31847 | Fail | 155.25 | 0 | 0 | 155.25
Restroom Men | 325 | 4 | 3 |  | 172 | 2095 |  | 9 | 1548 | 10 | 100 | 0.1 | 0.3876 | 0 | 0.3876 | Fail | 51.75 | 0 | 0 | 51.75
Restroom Womens | 326 | 4 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 0 | 3.0596 | Poor | 51.75 | 0 | 0 | 51.75
Hall | 327 | 4 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 0 | 3.6944 | Poor | 181.125 | 0 | 0 | 181.125
Mechanical Shaft | 328 | 4 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 0 | 3.1667 | Poor | 103.5 | 0 | 0 | 103.5
Elevators | 329 | 4 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 0 | 4.2222 | Low | 103.5 | 0 | 0 | 103.5
Stairs | 329 | 4 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 129.375 | 0 | 0 | 129.375
Stairs | 330 | 4 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 129.375 | 0 | 0 | 129.375
Office | 300 | 5 | 1 |  | 121 |  |  | 9 | 1089 | 71.25 | 75 | 0.95 | 3.9256 | 0 | 3.9256 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 301 | 5 | 1 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 0 | 3.9916 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 302 | 5 | 1 |  | 119 |  |  | 9 | 1071 | 19.5 | 75 | 0.26 | 1.0924 | 0 | 1.0924 | Very Bad | 38.8125 | 0 | 0 | 38.8125
Office | 303 | 5 | 1 |  | 189 |  |  | 9 | 1701 | 95 | 100 | 0.95 | 3.351 | 0 | 3.351 | Poor | 51.75 | 0 | 0 | 51.75
Office | 304 | 5 | 1 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 305 | 5 | 1 |  | 117 |  |  | 9 | 1053 | 71.25 | 75 | 0.95 | 4.0598 | 0 | 4.0598 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 306 | 5 | 1 |  | 113 |  |  | 9 | 1017 | 71.25 | 75 | 0.95 | 4.2035 | 0 | 4.2035 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 306 | 5 | 1 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 38.8125 | 0 | 0 | 38.8125
Collaboration | 305 | 5 | 1 |  | 290 |  |  | 9 | 2610 | 190 | 200 | 0.95 | 4.3678 | 0 | 4.3678 | Low | 103.5 | 0 | 0 | 103.5
Admin | 305 | 5 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 0 | 1.1905 | Very Bad | 103.5 | 0 | 0 | 103.5
Reception | 306 | 5 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 0 | 1.1905 | Very Bad | 103.5 | 0 | 0 | 103.5
Copy | 307 | 5 | 1 |  | 82 |  |  | 9 | 738 | 47.5 | 50 | 0.95 | 3.8618 | 0 | 3.8618 | Poor | 25.875 | 0 | 0 | 25.875
Break Room | 307 | 5 | 1 |  | 72 |  |  | 9 | 648 | 47.5 | 50 | 0.95 | 4.3981 | 0 | 4.3981 | Low | 25.875 | 0 | 0 | 25.875
Storage | 308 | 5 | 1 |  | 73 | 2093 |  | 9 | 657 | 47.5 | 50 | 0.95 | 4.3379 | 0 | 4.3379 | Low | 25.875 | 0 | 0 | 25.875
Common Area | 309 | 5 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 0 | 3.8704 | Poor | 284.625 | 0 | 0 | 284.625
Office | 310 | 5 | 2 |  | 131 |  |  | 9 | 1179 | 7.5 | 75 | 0.1 | 0.38168 | 0 | 0.38168 | Fail | 38.8125 | 0 | 0 | 38.8125
Office | 311 | 5 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 0 | 1.0101 | Very Bad | 51.75 | 0 | 0 | 51.75
Office | 312 | 5 | 2 |  | 120 |  |  | 9 | 1080 | 7.5 | 75 | 0.1 | 0.41667 | 0 | 0.41667 | Fail | 38.8125 | 0 | 0 | 38.8125
Office | 313 | 5 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 313 | 5 | 2 |  | 165 |  |  | 9 | 1485 | 95 | 100 | 0.95 | 3.8384 | 0 | 3.8384 | Poor | 51.75 | 0 | 0 | 51.75
Office | 314 | 5 | 2 |  | 131 |  |  | 9 | 1179 | 95 | 100 | 0.95 | 4.8346 | 0 | 4.8346 | Low | 51.75 | 0 | 0 | 51.75
Bull Penns | 315 | 5 | 2 |  | 900 | 2632 |  | 9 | 8100 | 50 | 200 | 0.25 | 0.37037 | 0 | 0.37037 | Fail | 103.5 | 0 | 0 | 103.5
Idea Room | 316 | 5 | 3 |  | 423 |  |  | 9 | 3807 | 285 | 300 | 0.95 | 4.4917 | 0 | 4.4917 | Low | 155.25 | 0 | 0 | 155.25
Office | 317 | 5 | 3 |  | 92 |  |  | 9 | 828 | 71.25 | 75 | 0.95 | 5.163 | 0 | 5.163 | CDC LVL | 38.8125 | 0 | 0 | 38.8125
Office | 318 | 5 | 3 |  | 105 |  |  | 9 | 945 | 71.25 | 75 | 0.95 | 4.5238 | 0 | 4.5238 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 319 | 5 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 320 | 5 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0 | 4.0948 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 321 | 5 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 321 | 5 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 321 | 5 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0 | 4.0948 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 322 | 5 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 0 | 3.9916 | Poor | 38.8125 | 0 | 0 | 38.8125
Hall | 323 | 5 | 3 |  | 598 |  |  | 9 | 5382 | 30 | 300 | 0.1 | 0.33445 | 0 | 0.33445 | Fail | 155.25 | 0 | 0 | 155.25
Restroom Men | 324 | 5 | 3 |  | 172 | 2095 |  | 9 | 1548 | 10 | 100 | 0.1 | 0.3876 | 0 | 0.3876 | Fail | 51.75 | 0 | 0 | 51.75
Restroom Womens | 325 | 5 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 0 | 3.0596 | Poor | 51.75 | 0 | 0 | 51.75
Hall | 326 | 5 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 0 | 3.6944 | Poor | 181.125 | 0 | 0 | 181.125
Mechanical Shaft | 327 | 5 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 0 | 3.1667 | Poor | 103.5 | 0 | 0 | 103.5
Elevators | 328 | 5 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 0 | 4.2222 | Low | 103.5 | 0 | 0 | 103.5
Stairs | 328 | 5 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 129.375 | 0 | 0 | 129.375
Stairs | 329 | 5 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 129.375 | 0 | 0 | 129.375
Office | 300 | 6 | 1 |  | 121 |  |  | 9 | 1089 | 71.25 | 75 | 0.95 | 3.9256 | 0 | 3.9256 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 301 | 6 | 1 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 0 | 3.9916 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 302 | 6 | 1 |  | 119 |  |  | 9 | 1071 | 19.5 | 75 | 0.26 | 1.0924 | 0 | 1.0924 | Very Bad | 38.8125 | 0 | 0 | 38.8125
Office | 303 | 6 | 1 |  | 189 |  |  | 9 | 1701 | 95 | 100 | 0.95 | 3.351 | 0 | 3.351 | Poor | 51.75 | 0 | 0 | 51.75
Office | 304 | 6 | 1 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 305 | 6 | 1 |  | 117 |  |  | 9 | 1053 | 71.25 | 75 | 0.95 | 4.0598 | 0 | 4.0598 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 306 | 6 | 1 |  | 113 |  |  | 9 | 1017 | 71.25 | 75 | 0.95 | 4.2035 | 0 | 4.2035 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 306 | 6 | 1 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 38.8125 | 0 | 0 | 38.8125
Collaboration | 305 | 6 | 1 |  | 290 |  |  | 9 | 2610 | 190 | 200 | 0.95 | 4.3678 | 0 | 4.3678 | Low | 103.5 | 0 | 0 | 103.5
Admin | 305 | 6 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 0 | 1.1905 | Very Bad | 103.5 | 0 | 0 | 103.5
Reception | 306 | 6 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 0 | 1.1905 | Very Bad | 103.5 | 0 | 0 | 103.5
Copy | 307 | 6 | 1 |  | 82 |  |  | 9 | 738 | 47.5 | 50 | 0.95 | 3.8618 | 0 | 3.8618 | Poor | 25.875 | 0 | 0 | 25.875
Break Room | 307 | 6 | 1 |  | 72 |  |  | 9 | 648 | 47.5 | 50 | 0.95 | 4.3981 | 0 | 4.3981 | Low | 25.875 | 0 | 0 | 25.875
IT | 308 | 6 | 1 |  | 73 | 2093 |  | 9 | 657 | 47.5 | 50 | 0.95 | 4.3379 | 0 | 4.3379 | Low | 25.875 | 0 | 0 | 25.875
Common Area | 309 | 6 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 0 | 3.8704 | Poor | 284.625 | 0 | 0 | 284.625
Office | 310 | 6 | 2 |  | 131 |  |  | 9 | 1179 | 7.5 | 75 | 0.1 | 0.38168 | 0 | 0.38168 | Fail | 38.8125 | 0 | 0 | 38.8125
Office | 311 | 6 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 0 | 1.0101 | Very Bad | 51.75 | 0 | 0 | 51.75
Office | 312 | 6 | 2 |  | 120 |  |  | 9 | 1080 | 7.5 | 75 | 0.1 | 0.41667 | 0 | 0.41667 | Fail | 38.8125 | 0 | 0 | 38.8125
Office | 313 | 6 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 38.8125 | 0 | 0 | 38.8125
Office | 313 | 6 | 2 |  | 165 |  |  | 9 | 1485 | 95 | 100 | 0.95 | 3.8384 | 0 | 3.8384 | Poor | 51.75 | 0 | 0 | 51.75
Office | 314 | 6 | 2 |  | 131 |  |  | 9 | 1179 | 95 | 100 | 0.95 | 4.8346 | 0 | 4.8346 | Low | 51.75 | 0 | 0 | 51.75
Bull Penns | 315 | 6 | 2 |  | 900 | 2632 |  | 9 | 8100 | 50 | 200 | 0.25 | 0.37037 | 0 | 0.37037 | Fail | 103.5 | 0 | 0 | 103.5
Conference Room | 316 | 6 | 3 |  | 423 |  |  | 9 | 3807 | 285 | 300 | 0.95 | 4.4917 | 0 | 4.4917 | Low | 155.25 | 0 | 0 | 155.25
Office | 317 | 6 | 3 |  | 92 |  |  | 9 | 828 | 71.25 | 75 | 0.95 | 5.163 | 0 | 5.163 | CDC LVL | 38.8125 | 0 | 0 | 38.8125
Office | 318 | 6 | 3 |  | 105 |  |  | 9 | 945 | 71.25 | 75 | 0.95 | 4.5238 | 0 | 4.5238 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 319 | 6 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 320 | 6 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0 | 4.0948 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 321 | 6 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 321 | 6 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 321 | 6 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0 | 4.0948 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 322 | 6 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 0 | 3.9916 | Poor | 38.8125 | 0 | 0 | 38.8125
Hall | 323 | 6 | 3 |  | 598 |  |  | 9 | 5382 | 30 | 300 | 0.1 | 0.33445 | 0 | 0.33445 | Fail | 155.25 | 0 | 0 | 155.25
Restroom Men | 324 | 6 | 3 |  | 172 | 2095 |  | 9 | 1548 | 10 | 100 | 0.1 | 0.3876 | 0 | 0.3876 | Fail | 51.75 | 0 | 0 | 51.75
Restroom Womens | 325 | 6 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 0 | 3.0596 | Poor | 51.75 | 0 | 0 | 51.75
Hall | 326 | 6 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 0 | 3.6944 | Poor | 181.125 | 0 | 0 | 181.125
Mechanical Shaft | 327 | 6 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 0 | 3.1667 | Poor | 103.5 | 0 | 0 | 103.5
Elevators | 328 | 6 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 0 | 4.2222 | Low | 103.5 | 0 | 0 | 103.5
Stairs | 328 | 6 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 129.375 | 0 | 0 | 129.375
Stairs | 329 | 6 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 129.375 | 0 | 0 | 129.375
Conference | 300 | 7 | 1 |  | 215 |  |  | 9 | 1935 | 71.25 | 75 | 0.95 | 2.2093 | 0 | 2.2093 | Bad | 38.8125 | 0 | 0 | 38.8125
Staff | 301 | 7 | 1 |  | 109 |  |  | 9 | 981 | 71.25 | 75 | 0.95 | 4.3578 | 0 | 4.3578 | Low | 38.8125 | 0 | 0 | 38.8125
Workroom | 302 | 7 | 1 |  | 242 |  |  | 9 | 2178 | 71.25 | 75 | 0.95 | 1.9628 | 0 | 1.9628 | Very Bad | 38.8125 | 0 | 0 | 38.8125
Lab | 303 | 7 | 1 |  | 1220 |  |  | 9 | 10980 | 855 | 900 | 0.95 | 4.6721 | 0 | 4.6721 | Low | 465.75 | 0 | 0 | 465.75
Lab Storage | 304 | 7 | 1 |  | 151 |  |  | 9 | 1359 | 71.25 | 75 | 0.95 | 3.1457 | 0 | 3.1457 | Poor | 38.8125 | 0 | 0 | 38.8125
Hall | 305 | 7 | 1 |  | 92 |  |  | 9 | 828 | 71.25 | 75 | 0.95 | 5.163 | 0 | 5.163 | CDC LVL | 38.8125 | 0 | 0 | 38.8125
Break Room | 306 | 7 | 1 |  | 64 | 2093 |  | 9 | 576 | 5 | 50 | 0.1 | 0.52083 | 0 | 0.52083 | Fail | 25.875 | 0 | 0 | 25.875
Common Area | 307 | 7 | 2 |  | 1279 |  |  | 9 | 11511 | 760 | 800 | 0.95 | 3.9614 | 0 | 3.9614 | Poor | 414 | 0 | 0 | 414
IT Office | 308 | 7 | 2 |  | 122 |  |  | 9 | 1098 | 95 | 100 | 0.95 | 5.1913 | 0 | 5.1913 | CDC LVL | 51.75 | 0 | 0 | 51.75
Office | 309 | 7 | 2 |  | 122 |  |  | 9 | 1098 | 95 | 100 | 0.95 | 5.1913 | 0 | 5.1913 | CDC LVL | 51.75 | 0 | 0 | 51.75
Staff | 310 | 7 | 2 |  | 179 |  |  | 9 | 1611 | 95 | 100 | 0.95 | 3.5382 | 0 | 3.5382 | Poor | 51.75 | 0 | 0 | 51.75
Workroom | 311 | 7 | 2 |  | 250 |  |  | 9 | 2250 | 190 | 200 | 0.95 | 5.0667 | 0 | 5.0667 | CDC LVL | 103.5 | 0 | 0 | 103.5
File Storage | 311 | 7 | 2 |  | 162 |  |  | 9 | 1458 | 95 | 100 | 0.95 | 3.9095 | 0 | 3.9095 | Poor | 51.75 | 0 | 0 | 51.75
Doctoral Student Lounge | 312 | 7 | 2 |  | 274 |  |  | 9 | 2466 | 190 | 200 | 0.95 | 4.6229 | 0 | 4.6229 | Low | 103.5 | 0 | 0 | 103.5
Reception | 313 | 7 | 2 |  | 244 | 2632 |  | 9 | 2196 | 80 | 200 | 0.4 | 2.1858 | 0 | 2.1858 | Bad | 103.5 | 0 | 0 | 103.5
Copy | 314 | 7 | 3 |  | 85 |  |  | 9 | 765 | 47.5 | 50 | 0.95 | 3.7255 | 0 | 3.7255 | Poor | 25.875 | 0 | 0 | 25.875
Consult | 315 | 7 | 3 |  | 84 |  |  | 9 | 756 | 47.5 | 50 | 0.95 | 3.7698 | 0 | 3.7698 | Poor | 25.875 | 0 | 0 | 25.875
Consult | 316 | 7 | 3 |  | 92 |  |  | 9 | 828 | 47.5 | 50 | 0.95 | 3.442 | 0 | 3.442 | Poor | 25.875 | 0 | 0 | 25.875
Part Time Faculty | 317 | 7 | 3 |  | 88 |  |  | 9 | 792 | 47.5 | 50 | 0.95 | 3.5985 | 0 | 3.5985 | Poor | 25.875 | 0 | 0 | 25.875
Part Time Faculty | 318 | 7 | 3 |  | 88 |  |  | 9 | 792 | 47.5 | 50 | 0.95 | 3.5985 | 0 | 3.5985 | Poor | 25.875 | 0 | 0 | 25.875
Office | 319 | 7 | 3 |  | 119 |  |  | 9 | 1071 | 7.5 | 75 | 0.1 | 0.42017 | 0 | 0.42017 | Fail | 38.8125 | 0 | 0 | 38.8125
Office | 320 | 7 | 3 |  | 116 |  |  | 9 | 1044 | 7.5 | 75 | 0.1 | 0.43103 | 0 | 0.43103 | Fail | 38.8125 | 0 | 0 | 38.8125
Office | 320 | 7 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 320 | 7 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0 | 4.0254 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 320 | 7 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0 | 4.0948 | Low | 38.8125 | 0 | 0 | 38.8125
Office | 321 | 7 | 3 |  | 169 |  |  | 9 | 1521 | 71.25 | 75 | 0.95 | 2.8107 | 0 | 2.8107 | Bad | 38.8125 | 0 | 0 | 38.8125
Admin & Hall | 322 | 7 | 3 |  | 730 |  |  | 9 | 6570 | 380 | 400 | 0.95 | 3.4703 | 0 | 3.4703 | Poor | 207 | 0 | 0 | 207
Restroom Men | 323 | 7 | 3 |  | 172 | 2095 |  | 9 | 1548 | 95 | 100 | 0.95 | 3.6822 | 0 | 3.6822 | Poor | 51.75 | 0 | 0 | 51.75
Restroom Womens | 324 | 7 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 0 | 3.0596 | Poor | 51.75 | 0 | 0 | 51.75
Hall | 325 | 7 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 0 | 3.6944 | Poor | 181.125 | 0 | 0 | 181.125
Mechanical Shaft | 326 | 7 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 0 | 3.1667 | Poor | 103.5 | 0 | 0 | 103.5
Elevators | 327 | 7 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 0 | 4.2222 | Low | 103.5 | 0 | 0 | 103.5
Stairs | 327 | 7 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 129.375 | 0 | 0 | 129.375
Stairs | 328 | 7 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 0 | 3.9583 | Poor | 129.375 | 0 | 0 | 129.375

## Bld 1 Arch A
Building | Example
Survey Team | TBD | [21 empty] | ACH = CFM * 60 / cuft
Survey Date | TBD | [21 empty] | CFM = ACH*cuft/60
Purpose | This sheet captures the ventilation performance level in each room and the power required for the ventilation level achieved. | [23 empty] | cuft | CFM |  |  | ACH
Note | Once a survey is performed these values will be updated. | [23 empty] | 31500 | 2362.5 |  |  | 4.5
Ventilation Type | DCV: occupancy, timers, temperature, humidity | [21 empty] | 2100 | 15 | 31500 | 2375 | 2500 | 0.95 | 4.5238
Sensors | Particle, CO2
Control | Outsourced to Energy Company XYZ
Model Type | Fine Grain
Mech Watts / CFM 2023 | 0.5175
Mech Watts / CFM 2025 | 0.5175 |  |  | Min | 33 | 800 | 9127 | 9 | 297 | 24.75 | 26.0526 | 0.95 | 5 | 0 | 5 | Min | 13.4822 | 0 | 0 | 13.4822
UV Watts / Cu-Ft 2023 | 0.017276 |  |  | Max | 5200 | 24627 | 24627 | 20 | 104000 | 8666.6667 | 9122.807 | 0.95 | 5 | 12 | 17 | Max | 4721.0526 | 829.2683 | 0.38058 | 4721.0526
Far UV Watts / Cu-Ft 2023 | 0.017276 |  |  | Avg | 339.2692 | 2560.9355 | 11341.2857 | 9.1453 | 3626.5 | 302.2083 | 318.114 | 0.95 | 5 | 0.051282 | 5.0513 | Avg | 164.624 | 3.5439 | 0.0016264 | 168.1679
Totals |  |  |  |  | 79389 | 79389 | 79389 | 9 | 848601 | 70716.75 | 74438.6842 | [5 empty] | 38522.0191 | 829.2683 | 0.38058 | 39351.2874
Room Name | Number | Flr | Area | Zone | Sq-Ft | Area Sq-Ft | Floor Sq-Ft | Ht Ft | Cu-Ft | Actual CFM | Design CFM | Actual / Design | ACH | eACH | Total ACH | Ventilation Rating | Mech Watts 2023 | UV-C Watts | UV Watts / Mech Watts | Total Watts | ACH | Scale Setings
Cafe | 100 | 1 | 1 |  | 3200 |  |  | 15 | 48000 | 4000 | 4210.5263 | 0.95 | 5 | 12 | 17 | CDC Airborne LVL | 2178.9474 | 829.2683 | 0.38058 | 3008.2157 | 0 | Fail
Transit Lounge | 101 | 1 | 2 |  | 2100 |  |  | 15 | 31500 | 2625 | 2763.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 1429.9342 | 0 | 0 | 1429.9342 | 0.9 | Fail
Lobby | 102 | 1 | 3 |  | 4100 |  |  | 20 | 82000 | 6833.3333 | 7192.9825 | 0.95 | 5 | 0 | 5 | CDC LVL | 3722.3684 | 0 | 0 | 3722.3684 | 1 | Very Bad
Lecture Hall | 103 | 1 | 4 |  | 5200 |  |  | 20 | 104000 | 8666.6667 | 9122.807 | 0.95 | 5 | 0 | 5 | CDC LVL | 4721.0526 | 0 | 0 | 4721.0526 | 2 | Bad
Space 1 | 104 | 1 | 5 |  | 3042.3333 |  |  | 9 | 27381 | 2281.75 | 2401.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 1242.9533 | 0 | 0 | 1242.9533 | 3 | Poor
Space 2 | 105 | 1 | 5 |  | 3042.3333 |  |  | 9 | 27381 | 2281.75 | 2401.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 1242.9533 | 0 | 0 | 1242.9533 | 4 | Low
Space 3 | 106 | 1 | 5 |  | 3042.3333 |  |  | 9 | 27381 | 2281.75 | 2401.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 1242.9533 | 0 | 0 | 1242.9533 | 5 | CDC LVL
Restrooms | 107 | 1 | 6 |  | 900 | 24627 | 24627 | 9 | 8100 | 675 | 710.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 367.6974 | 0 | 0 | 367.6974 | 6 | CDC & Harvard LVL
Conference Room | 200 | 2 | 1 |  | 354 |  |  | 9 | 3186 | 265.5 | 279.4737 | 0.95 | 5 | 0 | 5 | CDC LVL | 144.6276 | 0 | 0 | 144.6276 | 7 | CDC & Harvard LVL
Office | 201 | 2 | 1 |  | 264 |  |  | 9 | 2376 | 198 | 208.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 107.8579 | 0 | 0 | 107.8579 | 8 | CDC & Harvard LVL
Office | 202 | 2 | 1 |  | 168 |  |  | 9 | 1512 | 126 | 132.6316 | 0.95 | 5 | 0 | 5 | CDC LVL | 68.6368 | 0 | 0 | 68.6368 | 9 | CDC & Harvard LVL
Office | 203 | 2 | 1 |  | 171 |  |  | 9 | 1539 | 128.25 | 135 | 0.95 | 5 | 0 | 5 | CDC LVL | 69.8625 | 0 | 0 | 69.8625 | 10 | CDC & Harvard LVL
Office | 204 | 2 | 1 |  | 169 |  |  | 9 | 1521 | 126.75 | 133.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 69.0454 | 0 | 0 | 69.0454 | 11 | CDC & Harvard LVL
Office | 205 | 2 | 1 |  | 171 |  |  | 9 | 1539 | 128.25 | 135 | 0.95 | 5 | 0 | 5 | CDC LVL | 69.8625 | 0 | 0 | 69.8625 | 12 | CDC Airborne LVL
Bull Penns | 206 | 2 | 1 |  | 600 |  |  | 9 | 5400 | 450 | 473.6842 | 0.95 | 5 | 0 | 5 | CDC LVL | 245.1316 | 0 | 0 | 245.1316
Copy | 207 | 2 | 1 |  | 97 |  |  | 9 | 873 | 72.75 | 76.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 39.6296 | 0 | 0 | 39.6296
Break Room | 208 | 2 | 1 |  | 99 | 2093 |  | 9 | 891 | 74.25 | 78.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 40.4467 | 0 | 0 | 40.4467
Common Area | 209 | 2 | 2 |  | 900 |  |  | 9 | 8100 | 675 | 710.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 367.6974 | 0 | 0 | 367.6974
Office | 210 | 2 | 2 |  | 136 |  |  | 9 | 1224 | 102 | 107.3684 | 0.95 | 5 | 0 | 5 | CDC LVL | 55.5632 | 0 | 0 | 55.5632
Office | 211 | 2 | 2 |  | 165 |  |  | 9 | 1485 | 123.75 | 130.2632 | 0.95 | 5 | 0 | 5 | CDC LVL | 67.4112 | 0 | 0 | 67.4112
Office | 212 | 2 | 2 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Office | 213 | 2 | 2 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Office | 214 | 2 | 2 |  | 154 |  |  | 9 | 1386 | 115.5 | 121.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 62.9171 | 0 | 0 | 62.9171
Bull Penns | 215 | 2 | 2 |  | 905 |  |  | 9 | 8145 | 678.75 | 714.4737 | 0.95 | 5 | 0 | 5 | CDC LVL | 369.7401 | 0 | 0 | 369.7401
Copy Workroom | 216 | 2 | 2 |  | 92 |  |  | 9 | 828 | 69 | 72.6316 | 0.95 | 5 | 0 | 5 | CDC LVL | 37.5868 | 0 | 0 | 37.5868
Storage | 217 | 2 | 2 |  | 40 | 2632 |  | 9 | 360 | 30 | 31.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 16.3421 | 0 | 0 | 16.3421
Conference Room | 218 | 2 | 3 |  | 156 |  |  | 9 | 1404 | 117 | 123.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 63.7342 | 0 | 0 | 63.7342
Interview Room | 219 | 2 | 3 |  | 70 |  |  | 9 | 630 | 52.5 | 55.2632 | 0.95 | 5 | 0 | 5 | CDC LVL | 28.5987 | 0 | 0 | 28.5987
Storage | 220 | 2 | 3 |  | 33 |  |  | 9 | 297 | 24.75 | 26.0526 | 0.95 | 5 | 0 | 5 | CDC LVL | 13.4822 | 0 | 0 | 13.4822
File Storage | 221 | 2 | 3 |  | 136 |  |  | 9 | 1224 | 102 | 107.3684 | 0.95 | 5 | 0 | 5 | CDC LVL | 55.5632 | 0 | 0 | 55.5632
Office | 222 | 2 | 3 |  | 169 |  |  | 9 | 1521 | 126.75 | 133.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 69.0454 | 0 | 0 | 69.0454
Office | 223 | 2 | 3 |  | 116 |  |  | 9 | 1044 | 87 | 91.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.3921 | 0 | 0 | 47.3921
Office | 224 | 2 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 225 | 2 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 226 | 2 | 3 |  | 116 |  |  | 9 | 1044 | 87 | 91.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.3921 | 0 | 0 | 47.3921
Office | 227 | 2 | 3 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Reception | 228 | 2 | 3 |  | 772 |  |  | 9 | 6948 | 579 | 609.4737 | 0.95 | 5 | 0 | 5 | CDC LVL | 315.4026 | 0 | 0 | 315.4026
Restroom Men | 229 | 2 | 3 |  | 172 | 2095 |  | 9 | 1548 | 129 | 135.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 70.2711 | 0 | 0 | 70.2711
Restroom Womens | 230 | 2 | 4 |  | 207 |  |  | 9 | 1863 | 155.25 | 163.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 84.5704 | 0 | 0 | 84.5704
Hall | 231 | 2 | 4 |  | 600 |  |  | 9 | 5400 | 450 | 473.6842 | 0.95 | 5 | 0 | 5 | CDC LVL | 245.1316 | 0 | 0 | 245.1316
Mechanical Shaft | 232 | 2 | 4 |  | 400 |  |  | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Elevators | 233 | 2 | 4 |  | 300 | 1507 |  | 9 | 2700 | 225 | 236.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 122.5658 | 0 | 0 | 122.5658
Stairs | 233 | 2 | 5 |  | 400 |  |  | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Stairs | 234 | 2 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Office | 300 | 3 | 1 |  | 121 |  |  | 9 | 1089 | 90.75 | 95.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.4349 | 0 | 0 | 49.4349
Office | 301 | 3 | 1 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Office | 302 | 3 | 1 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Office | 303 | 3 | 1 |  | 189 |  |  | 9 | 1701 | 141.75 | 149.2105 | 0.95 | 5 | 0 | 5 | CDC LVL | 77.2164 | 0 | 0 | 77.2164
Office | 304 | 3 | 1 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 305 | 3 | 1 |  | 117 |  |  | 9 | 1053 | 87.75 | 92.3684 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.8007 | 0 | 0 | 47.8007
Office | 306 | 3 | 1 |  | 113 |  |  | 9 | 1017 | 84.75 | 89.2105 | 0.95 | 5 | 0 | 5 | CDC LVL | 46.1664 | 0 | 0 | 46.1664
Office | 306 | 3 | 1 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Collaboration | 305 | 3 | 1 |  | 290 |  |  | 9 | 2610 | 217.5 | 228.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 118.4803 | 0 | 0 | 118.4803
Admin | 305 | 3 | 1 |  | 280 |  |  | 9 | 2520 | 210 | 221.0526 | 0.95 | 5 | 0 | 5 | CDC LVL | 114.3947 | 0 | 0 | 114.3947
Reception | 306 | 3 | 1 |  | 280 |  |  | 9 | 2520 | 210 | 221.0526 | 0.95 | 5 | 0 | 5 | CDC LVL | 114.3947 | 0 | 0 | 114.3947
Copy | 307 | 3 | 1 |  | 82 |  |  | 9 | 738 | 61.5 | 64.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 33.5013 | 0 | 0 | 33.5013
Break Room | 307 | 3 | 1 |  | 72 |  |  | 9 | 648 | 54 | 56.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 29.4158 | 0 | 0 | 29.4158
IT | 308 | 3 | 1 |  | 73 | 2093 |  | 9 | 657 | 54.75 | 57.6316 | 0.95 | 5 | 0 | 5 | CDC LVL | 29.8243 | 0 | 0 | 29.8243
Common Area | 309 | 3 | 2 |  | 900 |  |  | 9 | 8100 | 675 | 710.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 367.6974 | 0 | 0 | 367.6974
Office | 310 | 3 | 2 |  | 131 |  |  | 9 | 1179 | 98.25 | 103.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 53.5204 | 0 | 0 | 53.5204
Office | 311 | 3 | 2 |  | 165 |  |  | 9 | 1485 | 123.75 | 130.2632 | 0.95 | 5 | 0 | 5 | CDC LVL | 67.4112 | 0 | 0 | 67.4112
Office | 312 | 3 | 2 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Office | 313 | 3 | 2 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Office | 313 | 3 | 2 |  | 165 |  |  | 9 | 1485 | 123.75 | 130.2632 | 0.95 | 5 | 0 | 5 | CDC LVL | 67.4112 | 0 | 0 | 67.4112
Office | 314 | 3 | 2 |  | 131 |  |  | 9 | 1179 | 98.25 | 103.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 53.5204 | 0 | 0 | 53.5204
Bull Penns | 315 | 3 | 2 |  | 900 | 2632 |  | 9 | 8100 | 675 | 710.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 367.6974 | 0 | 0 | 367.6974
Meeting Room | 316 | 3 | 3 |  | 417 |  |  | 9 | 3753 | 312.75 | 329.2105 | 0.95 | 5 | 0 | 5 | CDC LVL | 170.3664 | 0 | 0 | 170.3664
Research Room | 317 | 3 | 3 |  | 201 |  |  | 9 | 1809 | 150.75 | 158.6842 | 0.95 | 5 | 0 | 5 | CDC LVL | 82.1191 | 0 | 0 | 82.1191
Office | 318 | 3 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 319 | 3 | 3 |  | 116 |  |  | 9 | 1044 | 87 | 91.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.3921 | 0 | 0 | 47.3921
Office | 320 | 3 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 321 | 3 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 322 | 3 | 3 |  | 116 |  |  | 9 | 1044 | 87 | 91.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.3921 | 0 | 0 | 47.3921
Office | 323 | 3 | 3 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Hall | 324 | 3 | 3 |  | 600 |  |  | 9 | 5400 | 450 | 473.6842 | 0.95 | 5 | 0 | 5 | CDC LVL | 245.1316 | 0 | 0 | 245.1316
Restroom Men | 325 | 3 | 3 |  | 172 | 2095 |  | 9 | 1548 | 129 | 135.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 70.2711 | 0 | 0 | 70.2711
Restroom Womens | 326 | 3 | 4 |  | 207 |  |  | 9 | 1863 | 155.25 | 163.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 84.5704 | 0 | 0 | 84.5704
Hall | 327 | 3 | 4 |  | 600 |  |  | 9 | 5400 | 450 | 473.6842 | 0.95 | 5 | 0 | 5 | CDC LVL | 245.1316 | 0 | 0 | 245.1316
Mechanical Shaft | 328 | 3 | 4 |  | 400 |  |  | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Elevators | 329 | 3 | 4 |  | 300 | 1507 |  | 9 | 2700 | 225 | 236.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 122.5658 | 0 | 0 | 122.5658
Stairs | 329 | 3 | 5 |  | 400 |  |  | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Stairs | 330 | 3 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Office | 300 | 4 | 1 |  | 121 |  |  | 9 | 1089 | 90.75 | 95.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.4349 | 0 | 0 | 49.4349
Office | 301 | 4 | 1 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Office | 302 | 4 | 1 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Office | 303 | 4 | 1 |  | 189 |  |  | 9 | 1701 | 141.75 | 149.2105 | 0.95 | 5 | 0 | 5 | CDC LVL | 77.2164 | 0 | 0 | 77.2164
Office | 304 | 4 | 1 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 305 | 4 | 1 |  | 117 |  |  | 9 | 1053 | 87.75 | 92.3684 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.8007 | 0 | 0 | 47.8007
Office | 306 | 4 | 1 |  | 113 |  |  | 9 | 1017 | 84.75 | 89.2105 | 0.95 | 5 | 0 | 5 | CDC LVL | 46.1664 | 0 | 0 | 46.1664
Office | 306 | 4 | 1 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Collaboration | 305 | 4 | 1 |  | 290 |  |  | 9 | 2610 | 217.5 | 228.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 118.4803 | 0 | 0 | 118.4803
Admin | 305 | 4 | 1 |  | 280 |  |  | 9 | 2520 | 210 | 221.0526 | 0.95 | 5 | 0 | 5 | CDC LVL | 114.3947 | 0 | 0 | 114.3947
Reception | 306 | 4 | 1 |  | 280 |  |  | 9 | 2520 | 210 | 221.0526 | 0.95 | 5 | 0 | 5 | CDC LVL | 114.3947 | 0 | 0 | 114.3947
Copy | 307 | 4 | 1 |  | 82 |  |  | 9 | 738 | 61.5 | 64.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 33.5013 | 0 | 0 | 33.5013
Break Room | 307 | 4 | 1 |  | 72 |  |  | 9 | 648 | 54 | 56.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 29.4158 | 0 | 0 | 29.4158
IT | 308 | 4 | 1 |  | 73 | 2093 |  | 9 | 657 | 54.75 | 57.6316 | 0.95 | 5 | 0 | 5 | CDC LVL | 29.8243 | 0 | 0 | 29.8243
Common Area | 309 | 4 | 2 |  | 900 |  |  | 9 | 8100 | 675 | 710.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 367.6974 | 0 | 0 | 367.6974
Office | 310 | 4 | 2 |  | 131 |  |  | 9 | 1179 | 98.25 | 103.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 53.5204 | 0 | 0 | 53.5204
Office | 311 | 4 | 2 |  | 165 |  |  | 9 | 1485 | 123.75 | 130.2632 | 0.95 | 5 | 0 | 5 | CDC LVL | 67.4112 | 0 | 0 | 67.4112
Office | 312 | 4 | 2 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Office | 313 | 4 | 2 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Office | 313 | 4 | 2 |  | 165 |  |  | 9 | 1485 | 123.75 | 130.2632 | 0.95 | 5 | 0 | 5 | CDC LVL | 67.4112 | 0 | 0 | 67.4112
Office | 314 | 4 | 2 |  | 131 |  |  | 9 | 1179 | 98.25 | 103.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 53.5204 | 0 | 0 | 53.5204
Bull Penns | 315 | 4 | 2 |  | 900 | 2632 |  | 9 | 8100 | 675 | 710.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 367.6974 | 0 | 0 | 367.6974
Meeting Room | 316 | 4 | 3 |  | 265 |  |  | 9 | 2385 | 198.75 | 209.2105 | 0.95 | 5 | 0 | 5 | CDC LVL | 108.2664 | 0 | 0 | 108.2664
Research Room | 317 | 4 | 3 |  | 128 |  |  | 9 | 1152 | 96 | 101.0526 | 0.95 | 5 | 0 | 5 | CDC LVL | 52.2947 | 0 | 0 | 52.2947
Office | 318 | 4 | 3 |  | 92 |  |  | 9 | 828 | 69 | 72.6316 | 0.95 | 5 | 0 | 5 | CDC LVL | 37.5868 | 0 | 0 | 37.5868
Office | 319 | 4 | 3 |  | 105 |  |  | 9 | 945 | 78.75 | 82.8947 | 0.95 | 5 | 0 | 5 | CDC LVL | 42.898 | 0 | 0 | 42.898
Office | 320 | 4 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 321 | 4 | 3 |  | 116 |  |  | 9 | 1044 | 87 | 91.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.3921 | 0 | 0 | 47.3921
Office | 322 | 4 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 322 | 4 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 322 | 4 | 3 |  | 116 |  |  | 9 | 1044 | 87 | 91.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.3921 | 0 | 0 | 47.3921
Office | 323 | 4 | 3 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Hall | 324 | 4 | 3 |  | 628 |  |  | 9 | 5652 | 471 | 495.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 256.5711 | 0 | 0 | 256.5711
Restroom Men | 325 | 4 | 3 |  | 172 | 2095 |  | 9 | 1548 | 129 | 135.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 70.2711 | 0 | 0 | 70.2711
Restroom Womens | 326 | 4 | 4 |  | 207 |  |  | 9 | 1863 | 155.25 | 163.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 84.5704 | 0 | 0 | 84.5704
Hall | 327 | 4 | 4 |  | 600 |  |  | 9 | 5400 | 450 | 473.6842 | 0.95 | 5 | 0 | 5 | CDC LVL | 245.1316 | 0 | 0 | 245.1316
Mechanical Shaft | 328 | 4 | 4 |  | 400 |  |  | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Elevators | 329 | 4 | 4 |  | 300 | 1507 |  | 9 | 2700 | 225 | 236.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 122.5658 | 0 | 0 | 122.5658
Stairs | 329 | 4 | 5 |  | 400 |  |  | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Stairs | 330 | 4 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Office | 300 | 5 | 1 |  | 121 |  |  | 9 | 1089 | 90.75 | 95.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.4349 | 0 | 0 | 49.4349
Office | 301 | 5 | 1 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Office | 302 | 5 | 1 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Office | 303 | 5 | 1 |  | 189 |  |  | 9 | 1701 | 141.75 | 149.2105 | 0.95 | 5 | 0 | 5 | CDC LVL | 77.2164 | 0 | 0 | 77.2164
Office | 304 | 5 | 1 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 305 | 5 | 1 |  | 117 |  |  | 9 | 1053 | 87.75 | 92.3684 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.8007 | 0 | 0 | 47.8007
Office | 306 | 5 | 1 |  | 113 |  |  | 9 | 1017 | 84.75 | 89.2105 | 0.95 | 5 | 0 | 5 | CDC LVL | 46.1664 | 0 | 0 | 46.1664
Office | 306 | 5 | 1 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Collaboration | 305 | 5 | 1 |  | 290 |  |  | 9 | 2610 | 217.5 | 228.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 118.4803 | 0 | 0 | 118.4803
Admin | 305 | 5 | 1 |  | 280 |  |  | 9 | 2520 | 210 | 221.0526 | 0.95 | 5 | 0 | 5 | CDC LVL | 114.3947 | 0 | 0 | 114.3947
Reception | 306 | 5 | 1 |  | 280 |  |  | 9 | 2520 | 210 | 221.0526 | 0.95 | 5 | 0 | 5 | CDC LVL | 114.3947 | 0 | 0 | 114.3947
Copy | 307 | 5 | 1 |  | 82 |  |  | 9 | 738 | 61.5 | 64.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 33.5013 | 0 | 0 | 33.5013
Break Room | 307 | 5 | 1 |  | 72 |  |  | 9 | 648 | 54 | 56.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 29.4158 | 0 | 0 | 29.4158
Storage | 308 | 5 | 1 |  | 73 | 2093 |  | 9 | 657 | 54.75 | 57.6316 | 0.95 | 5 | 0 | 5 | CDC LVL | 29.8243 | 0 | 0 | 29.8243
Common Area | 309 | 5 | 2 |  | 900 |  |  | 9 | 8100 | 675 | 710.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 367.6974 | 0 | 0 | 367.6974
Office | 310 | 5 | 2 |  | 131 |  |  | 9 | 1179 | 98.25 | 103.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 53.5204 | 0 | 0 | 53.5204
Office | 311 | 5 | 2 |  | 165 |  |  | 9 | 1485 | 123.75 | 130.2632 | 0.95 | 5 | 0 | 5 | CDC LVL | 67.4112 | 0 | 0 | 67.4112
Office | 312 | 5 | 2 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Office | 313 | 5 | 2 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Office | 313 | 5 | 2 |  | 165 |  |  | 9 | 1485 | 123.75 | 130.2632 | 0.95 | 5 | 0 | 5 | CDC LVL | 67.4112 | 0 | 0 | 67.4112
Office | 314 | 5 | 2 |  | 131 |  |  | 9 | 1179 | 98.25 | 103.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 53.5204 | 0 | 0 | 53.5204
Bull Penns | 315 | 5 | 2 |  | 900 | 2632 |  | 9 | 8100 | 675 | 710.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 367.6974 | 0 | 0 | 367.6974
Idea Room | 316 | 5 | 3 |  | 423 |  |  | 9 | 3807 | 317.25 | 333.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 172.8178 | 0 | 0 | 172.8178
Office | 317 | 5 | 3 |  | 92 |  |  | 9 | 828 | 69 | 72.6316 | 0.95 | 5 | 0 | 5 | CDC LVL | 37.5868 | 0 | 0 | 37.5868
Office | 318 | 5 | 3 |  | 105 |  |  | 9 | 945 | 78.75 | 82.8947 | 0.95 | 5 | 0 | 5 | CDC LVL | 42.898 | 0 | 0 | 42.898
Office | 319 | 5 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 320 | 5 | 3 |  | 116 |  |  | 9 | 1044 | 87 | 91.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.3921 | 0 | 0 | 47.3921
Office | 321 | 5 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 321 | 5 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 321 | 5 | 3 |  | 116 |  |  | 9 | 1044 | 87 | 91.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.3921 | 0 | 0 | 47.3921
Office | 322 | 5 | 3 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Hall | 323 | 5 | 3 |  | 598 |  |  | 9 | 5382 | 448.5 | 472.1053 | 0.95 | 5 | 0 | 5 | CDC LVL | 244.3145 | 0 | 0 | 244.3145
Restroom Men | 324 | 5 | 3 |  | 172 | 2095 |  | 9 | 1548 | 129 | 135.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 70.2711 | 0 | 0 | 70.2711
Restroom Womens | 325 | 5 | 4 |  | 207 |  |  | 9 | 1863 | 155.25 | 163.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 84.5704 | 0 | 0 | 84.5704
Hall | 326 | 5 | 4 |  | 600 |  |  | 9 | 5400 | 450 | 473.6842 | 0.95 | 5 | 0 | 5 | CDC LVL | 245.1316 | 0 | 0 | 245.1316
Mechanical Shaft | 327 | 5 | 4 |  | 400 |  |  | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Elevators | 328 | 5 | 4 |  | 300 | 1507 |  | 9 | 2700 | 225 | 236.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 122.5658 | 0 | 0 | 122.5658
Stairs | 328 | 5 | 5 |  | 400 |  |  | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Stairs | 329 | 5 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Office | 300 | 6 | 1 |  | 121 |  |  | 9 | 1089 | 90.75 | 95.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.4349 | 0 | 0 | 49.4349
Office | 301 | 6 | 1 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Office | 302 | 6 | 1 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Office | 303 | 6 | 1 |  | 189 |  |  | 9 | 1701 | 141.75 | 149.2105 | 0.95 | 5 | 0 | 5 | CDC LVL | 77.2164 | 0 | 0 | 77.2164
Office | 304 | 6 | 1 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 305 | 6 | 1 |  | 117 |  |  | 9 | 1053 | 87.75 | 92.3684 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.8007 | 0 | 0 | 47.8007
Office | 306 | 6 | 1 |  | 113 |  |  | 9 | 1017 | 84.75 | 89.2105 | 0.95 | 5 | 0 | 5 | CDC LVL | 46.1664 | 0 | 0 | 46.1664
Office | 306 | 6 | 1 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Collaboration | 305 | 6 | 1 |  | 290 |  |  | 9 | 2610 | 217.5 | 228.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 118.4803 | 0 | 0 | 118.4803
Admin | 305 | 6 | 1 |  | 280 |  |  | 9 | 2520 | 210 | 221.0526 | 0.95 | 5 | 0 | 5 | CDC LVL | 114.3947 | 0 | 0 | 114.3947
Reception | 306 | 6 | 1 |  | 280 |  |  | 9 | 2520 | 210 | 221.0526 | 0.95 | 5 | 0 | 5 | CDC LVL | 114.3947 | 0 | 0 | 114.3947
Copy | 307 | 6 | 1 |  | 82 |  |  | 9 | 738 | 61.5 | 64.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 33.5013 | 0 | 0 | 33.5013
Break Room | 307 | 6 | 1 |  | 72 |  |  | 9 | 648 | 54 | 56.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 29.4158 | 0 | 0 | 29.4158
IT | 308 | 6 | 1 |  | 73 | 2093 |  | 9 | 657 | 54.75 | 57.6316 | 0.95 | 5 | 0 | 5 | CDC LVL | 29.8243 | 0 | 0 | 29.8243
Common Area | 309 | 6 | 2 |  | 900 |  |  | 9 | 8100 | 675 | 710.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 367.6974 | 0 | 0 | 367.6974
Office | 310 | 6 | 2 |  | 131 |  |  | 9 | 1179 | 98.25 | 103.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 53.5204 | 0 | 0 | 53.5204
Office | 311 | 6 | 2 |  | 165 |  |  | 9 | 1485 | 123.75 | 130.2632 | 0.95 | 5 | 0 | 5 | CDC LVL | 67.4112 | 0 | 0 | 67.4112
Office | 312 | 6 | 2 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Office | 313 | 6 | 2 |  | 120 |  |  | 9 | 1080 | 90 | 94.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.0263 | 0 | 0 | 49.0263
Office | 313 | 6 | 2 |  | 165 |  |  | 9 | 1485 | 123.75 | 130.2632 | 0.95 | 5 | 0 | 5 | CDC LVL | 67.4112 | 0 | 0 | 67.4112
Office | 314 | 6 | 2 |  | 131 |  |  | 9 | 1179 | 98.25 | 103.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 53.5204 | 0 | 0 | 53.5204
Bull Penns | 315 | 6 | 2 |  | 900 | 2632 |  | 9 | 8100 | 675 | 710.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 367.6974 | 0 | 0 | 367.6974
Conference Room | 316 | 6 | 3 |  | 423 |  |  | 9 | 3807 | 317.25 | 333.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 172.8178 | 0 | 0 | 172.8178
Office | 317 | 6 | 3 |  | 92 |  |  | 9 | 828 | 69 | 72.6316 | 0.95 | 5 | 0 | 5 | CDC LVL | 37.5868 | 0 | 0 | 37.5868
Office | 318 | 6 | 3 |  | 105 |  |  | 9 | 945 | 78.75 | 82.8947 | 0.95 | 5 | 0 | 5 | CDC LVL | 42.898 | 0 | 0 | 42.898
Office | 319 | 6 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 320 | 6 | 3 |  | 116 |  |  | 9 | 1044 | 87 | 91.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.3921 | 0 | 0 | 47.3921
Office | 321 | 6 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 321 | 6 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 321 | 6 | 3 |  | 116 |  |  | 9 | 1044 | 87 | 91.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.3921 | 0 | 0 | 47.3921
Office | 322 | 6 | 3 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Hall | 323 | 6 | 3 |  | 598 |  |  | 9 | 5382 | 448.5 | 472.1053 | 0.95 | 5 | 0 | 5 | CDC LVL | 244.3145 | 0 | 0 | 244.3145
Restroom Men | 324 | 6 | 3 |  | 172 | 2095 |  | 9 | 1548 | 129 | 135.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 70.2711 | 0 | 0 | 70.2711
Restroom Womens | 325 | 6 | 4 |  | 207 |  |  | 9 | 1863 | 155.25 | 163.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 84.5704 | 0 | 0 | 84.5704
Hall | 326 | 6 | 4 |  | 600 |  |  | 9 | 5400 | 450 | 473.6842 | 0.95 | 5 | 0 | 5 | CDC LVL | 245.1316 | 0 | 0 | 245.1316
Mechanical Shaft | 327 | 6 | 4 |  | 400 |  |  | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Elevators | 328 | 6 | 4 |  | 300 | 1507 |  | 9 | 2700 | 225 | 236.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 122.5658 | 0 | 0 | 122.5658
Stairs | 328 | 6 | 5 |  | 400 |  |  | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Stairs | 329 | 6 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Conference | 300 | 7 | 1 |  | 215 |  |  | 9 | 1935 | 161.25 | 169.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 87.8388 | 0 | 0 | 87.8388
Staff | 301 | 7 | 1 |  | 109 |  |  | 9 | 981 | 81.75 | 86.0526 | 0.95 | 5 | 0 | 5 | CDC LVL | 44.5322 | 0 | 0 | 44.5322
Workroom | 302 | 7 | 1 |  | 242 |  |  | 9 | 2178 | 181.5 | 191.0526 | 0.95 | 5 | 0 | 5 | CDC LVL | 98.8697 | 0 | 0 | 98.8697
Lab | 303 | 7 | 1 |  | 1220 |  |  | 9 | 10980 | 915 | 963.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 498.4342 | 0 | 0 | 498.4342
Lab Storage | 304 | 7 | 1 |  | 151 |  |  | 9 | 1359 | 113.25 | 119.2105 | 0.95 | 5 | 0 | 5 | CDC LVL | 61.6914 | 0 | 0 | 61.6914
Hall | 305 | 7 | 1 |  | 92 |  |  | 9 | 828 | 69 | 72.6316 | 0.95 | 5 | 0 | 5 | CDC LVL | 37.5868 | 0 | 0 | 37.5868
Break Room | 306 | 7 | 1 |  | 64 | 2093 |  | 9 | 576 | 48 | 50.5263 | 0.95 | 5 | 0 | 5 | CDC LVL | 26.1474 | 0 | 0 | 26.1474
Common Area | 307 | 7 | 2 |  | 1279 |  |  | 9 | 11511 | 959.25 | 1009.7368 | 0.95 | 5 | 0 | 5 | CDC LVL | 522.5388 | 0 | 0 | 522.5388
IT Office | 308 | 7 | 2 |  | 122 |  |  | 9 | 1098 | 91.5 | 96.3158 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.8434 | 0 | 0 | 49.8434
Office | 309 | 7 | 2 |  | 122 |  |  | 9 | 1098 | 91.5 | 96.3158 | 0.95 | 5 | 0 | 5 | CDC LVL | 49.8434 | 0 | 0 | 49.8434
Staff | 310 | 7 | 2 |  | 179 |  |  | 9 | 1611 | 134.25 | 141.3158 | 0.95 | 5 | 0 | 5 | CDC LVL | 73.1309 | 0 | 0 | 73.1309
Workroom | 311 | 7 | 2 |  | 250 |  |  | 9 | 2250 | 187.5 | 197.3684 | 0.95 | 5 | 0 | 5 | CDC LVL | 102.1382 | 0 | 0 | 102.1382
File Storage | 311 | 7 | 2 |  | 162 |  |  | 9 | 1458 | 121.5 | 127.8947 | 0.95 | 5 | 0 | 5 | CDC LVL | 66.1855 | 0 | 0 | 66.1855
Doctoral Student Lounge | 312 | 7 | 2 |  | 274 |  |  | 9 | 2466 | 205.5 | 216.3158 | 0.95 | 5 | 0 | 5 | CDC LVL | 111.9434 | 0 | 0 | 111.9434
Reception | 313 | 7 | 2 |  | 244 | 2632 |  | 9 | 2196 | 183 | 192.6316 | 0.95 | 5 | 0 | 5 | CDC LVL | 99.6868 | 0 | 0 | 99.6868
Copy | 314 | 7 | 3 |  | 85 |  |  | 9 | 765 | 63.75 | 67.1053 | 0.95 | 5 | 0 | 5 | CDC LVL | 34.727 | 0 | 0 | 34.727
Consult | 315 | 7 | 3 |  | 84 |  |  | 9 | 756 | 63 | 66.3158 | 0.95 | 5 | 0 | 5 | CDC LVL | 34.3184 | 0 | 0 | 34.3184
Consult | 316 | 7 | 3 |  | 92 |  |  | 9 | 828 | 69 | 72.6316 | 0.95 | 5 | 0 | 5 | CDC LVL | 37.5868 | 0 | 0 | 37.5868
Part Time Faculty | 317 | 7 | 3 |  | 88 |  |  | 9 | 792 | 66 | 69.4737 | 0.95 | 5 | 0 | 5 | CDC LVL | 35.9526 | 0 | 0 | 35.9526
Part Time Faculty | 318 | 7 | 3 |  | 88 |  |  | 9 | 792 | 66 | 69.4737 | 0.95 | 5 | 0 | 5 | CDC LVL | 35.9526 | 0 | 0 | 35.9526
Office | 319 | 7 | 3 |  | 119 |  |  | 9 | 1071 | 89.25 | 93.9474 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.6178 | 0 | 0 | 48.6178
Office | 320 | 7 | 3 |  | 116 |  |  | 9 | 1044 | 87 | 91.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.3921 | 0 | 0 | 47.3921
Office | 320 | 7 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 320 | 7 | 3 |  | 118 |  |  | 9 | 1062 | 88.5 | 93.1579 | 0.95 | 5 | 0 | 5 | CDC LVL | 48.2092 | 0 | 0 | 48.2092
Office | 320 | 7 | 3 |  | 116 |  |  | 9 | 1044 | 87 | 91.5789 | 0.95 | 5 | 0 | 5 | CDC LVL | 47.3921 | 0 | 0 | 47.3921
Office | 321 | 7 | 3 |  | 169 |  |  | 9 | 1521 | 126.75 | 133.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 69.0454 | 0 | 0 | 69.0454
Admin & Hall | 322 | 7 | 3 |  | 730 |  |  | 9 | 6570 | 547.5 | 576.3158 | 0.95 | 5 | 0 | 5 | CDC LVL | 298.2434 | 0 | 0 | 298.2434
Restroom Men | 323 | 7 | 3 |  | 172 | 2095 |  | 9 | 1548 | 129 | 135.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 70.2711 | 0 | 0 | 70.2711
Restroom Womens | 324 | 7 | 4 |  | 207 |  |  | 9 | 1863 | 155.25 | 163.4211 | 0.95 | 5 | 0 | 5 | CDC LVL | 84.5704 | 0 | 0 | 84.5704
Hall | 325 | 7 | 4 |  | 600 |  |  | 9 | 5400 | 450 | 473.6842 | 0.95 | 5 | 0 | 5 | CDC LVL | 245.1316 | 0 | 0 | 245.1316
Mechanical Shaft | 326 | 7 | 4 |  | 400 |  |  | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Elevators | 327 | 7 | 4 |  | 300 | 1507 |  | 9 | 2700 | 225 | 236.8421 | 0.95 | 5 | 0 | 5 | CDC LVL | 122.5658 | 0 | 0 | 122.5658
Stairs | 327 | 7 | 5 |  | 400 |  |  | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211
Stairs | 328 | 7 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 300 | 315.7895 | 0.95 | 5 | 0 | 5 | CDC LVL | 163.4211 | 0 | 0 | 163.4211

## Bld 1 Arch B
Building | Example
Survey Team | TBD | [21 empty] | ACH = CFM * 60 / cuft
Survey Date | TBD | [21 empty] | CFM = ACH*cuft/60
Purpose | This sheet captures the ventilation performance level in each room and the power required for the ventilation level achieved. | [23 empty] | cuft | CFM |  |  | ACH
Note | Once a survey is performed these values will be updated. | [23 empty] | 31500 | 2362.5 |  |  | 4.5
Ventilation Type | DCV: occupancy, timers, temperature, humidity | [21 empty] | 2100 | 15 | 31500 | 2375 | 2500 | 0.95 | 4.5238
Sensors | Particle, CO2
Control | Outsourced to Energy Company XYZ
Model Type | Fine Grain
Mech Watts / CFM 2023 | 0.5175
Mech Watts / CFM 2025 | 0.5175 |  |  | Min | 33 | 800 | 9127 | 9 | 297 | 5 | 25 | 0.1 | 0.31847 | 0.066667 | 5 | Min | 12.9375 | 0.086382 | 0.0020865 | 13.0239
UV Watts / Cu-Ft 2023 | 0.017276 |  |  | Max | 5200 | 24627 | 24627 | 20 | 104000 | 6650 | 7000 | 0.95 | 7.1698 | 12 | 16.75 | Max | 3622.5 | 829.2683 | 0.52476 | 3796.7039
Far UV Watts / Cu-Ft 2023 | 0.017276 |  |  | Avg | 339.2692 | 2560.9355 | 11341.2857 | 9.1453 | 3626.5 | 210.985 | 225.8547 | 0.80209 | 3.3666 | 1.7217 | 5.0883 | Avg | 116.8798 | 11.4442 | 0.079739 | 128.3241
Totals |  |  |  |  | 79389 | 79389 | 79389 | 9 | 848601 | 49370.5 | 52850 | [5 empty] | 27349.875 | 2677.9535 | 18.6589 | 30027.8285
Room Name | Number | Flr | Area | Zone | Sq-Ft | Area Sq-Ft | Floor Sq-Ft | Ht Ft | Cu-Ft | Actual CFM | Design CFM | Actual / Design | ACH | eACH | Total ACH | Ventilation Rating | Mech Watts 2023 | UV-C Watts | UV Watts / Mech Watts | Total Watts | ACH | Scale Setings
Cafe | 100 | 1 | 1 |  | 3200 |  |  | 15 | 48000 | 3800 | 4000 | 0.95 | 4.75 | 12 | 16.75 | CDC Airborne LVL | 2070 | 829.2683 | 0.40061 | 2899.2683 | 0 | Fail
Transit Lounge | 101 | 1 | 2 |  | 2100 |  |  | 15 | 31500 | 2375 | 2500 | 0.95 | 4.5238 | 0.47619 | 5 | CDC LVL | 1293.75 | 21.5955 | 0.016692 | 1315.3455 | 0.9 | Fail
Lobby | 102 | 1 | 3 |  | 4100 |  |  | 20 | 82000 | 4750 | 5000 | 0.95 | 3.4756 | 1.5244 | 5 | CDC LVL | 2587.5 | 179.9627 | 0.069551 | 2767.4627 | 1 | Very Bad
Lecture Hall | 103 | 1 | 4 |  | 5200 |  |  | 20 | 104000 | 6650 | 7000 | 0.95 | 3.8365 | 1.1635 | 5 | CDC LVL | 3622.5 | 174.2039 | 0.048089 | 3796.7039 | 2 | Bad
Space 1 | 104 | 1 | 5 |  | 3042.3333 |  |  | 9 | 27381 | 2000 | 600 | 0.95 | 4.3826 | 0.6174 | 5 | CDC LVL | 310.5 | 24.3382 | 0.078384 | 334.8382 | 3 | Poor
Space 2 | 105 | 1 | 5 |  | 3042.3333 |  |  | 9 | 27381 | 2000 | 600 | 0.95 | 4.3826 | 0.6174 | 5 | CDC LVL | 310.5 | 24.3382 | 0.078384 | 334.8382 | 4 | Low
Space 3 | 106 | 1 | 5 |  | 3042.3333 |  |  | 9 | 27381 | 2000 | 600 | 0.95 | 4.3826 | 0.6174 | 5 | CDC LVL | 310.5 | 24.3382 | 0.078384 | 334.8382 | 5 | CDC LVL
Restrooms | 107 | 1 | 6 |  | 900 | 24627 | 24627 | 9 | 8100 | 570 | 600 | 0.95 | 4.2222 | 0.77778 | 5 | CDC LVL | 310.5 | 9.0701 | 0.029211 | 319.5701 | 6 | CDC & Harvard LVL
Conference Room | 200 | 2 | 1 |  | 354 |  |  | 9 | 3186 | 213.75 | 225 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 116.4375 | 4.4703 | 0.038392 | 120.9078 | 7 | CDC & Harvard LVL
Office | 201 | 2 | 1 |  | 264 |  |  | 9 | 2376 | 142.5 | 150 | 0.95 | 3.5985 | 1.4015 | 5 | CDC LVL | 77.625 | 4.7942 | 0.061761 | 82.4192 | 8 | CDC & Harvard LVL
Office | 202 | 2 | 1 |  | 168 |  |  | 9 | 1512 | 25 | 100 | 0.25 | 0.99206 | 4.0079 | 5 | CDC LVL | 51.75 | 8.7246 | 0.16859 | 60.4746 | 9 | CDC & Harvard LVL
Office | 203 | 2 | 1 |  | 171 |  |  | 9 | 1539 | 25 | 100 | 0.25 | 0.97466 | 4.0253 | 5 | CDC LVL | 51.75 | 8.919 | 0.17235 | 60.669 | 10 | CDC & Harvard LVL
Office | 204 | 2 | 1 |  | 169 |  |  | 9 | 1521 | 95 | 100 | 0.95 | 3.7475 | 1.2525 | 5 | CDC LVL | 51.75 | 2.7426 | 0.052998 | 54.4926 | 11 | CDC & Harvard LVL
Office | 205 | 2 | 1 |  | 171 |  |  | 9 | 1539 | 95 | 100 | 0.95 | 3.7037 | 1.2963 | 5 | CDC LVL | 51.75 | 2.8722 | 0.055502 | 54.6222 | 12 | CDC Airborne LVL
Bull Penns | 206 | 2 | 1 |  | 600 |  |  | 9 | 5400 | 200 | 400 | 0.5 | 2.2222 | 2.7778 | 5 | CDC LVL | 207 | 21.5955 | 0.10433 | 228.5955
Copy | 207 | 2 | 1 |  | 97 |  |  | 9 | 873 | 47.5 | 50 | 0.95 | 3.2646 | 1.7354 | 5 | CDC LVL | 25.875 | 2.1811 | 0.084296 | 28.0561
Break Room | 208 | 2 | 1 |  | 99 | 2093 |  | 9 | 891 | 47.5 | 50 | 0.95 | 3.1987 | 1.8013 | 5 | CDC LVL | 25.875 | 2.3107 | 0.089303 | 28.1857
Common Area | 209 | 2 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 1.1296 | 5 | CDC LVL | 284.625 | 13.1733 | 0.046283 | 297.7983
Office | 210 | 2 | 2 |  | 136 |  |  | 9 | 1224 | 95 | 100 | 0.95 | 4.6569 | 0.34314 | 5 | CDC LVL | 51.75 | 0.60467 | 0.011685 | 52.3547
Office | 211 | 2 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 3.9899 | 5 | CDC LVL | 51.75 | 8.5302 | 0.16484 | 60.2802
Office | 212 | 2 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 38.8125 | 1.6197 | 0.04173 | 40.4322
Office | 213 | 2 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 38.8125 | 1.6197 | 0.04173 | 40.4322
Office | 214 | 2 | 2 |  | 154 |  |  | 9 | 1386 | 95 | 100 | 0.95 | 4.1126 | 0.88745 | 5 | CDC LVL | 51.75 | 1.7708 | 0.034219 | 53.5208
Bull Penns | 215 | 2 | 2 |  | 905 |  |  | 9 | 8145 | 50 | 200 | 0.25 | 0.36832 | 4.6317 | 5 | CDC LVL | 103.5 | 54.3128 | 0.52476 | 157.8128
Copy Workroom | 216 | 2 | 2 |  | 92 |  |  | 9 | 828 | 47.5 | 50 | 0.95 | 3.442 | 1.558 | 5 | CDC LVL | 25.875 | 1.8572 | 0.071776 | 27.7322
Storage | 217 | 2 | 2 |  | 40 | 2632 |  | 9 | 360 | 23.75 | 25 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 12.9375 | 0.53989 | 0.04173 | 13.4774
Conference Room | 218 | 2 | 3 |  | 156 |  |  | 9 | 1404 | 95 | 100 | 0.95 | 4.0598 | 0.94017 | 5 | CDC LVL | 51.75 | 1.9004 | 0.036723 | 53.6504
Interview Room | 219 | 2 | 3 |  | 70 |  |  | 9 | 630 | 47.5 | 50 | 0.95 | 4.5238 | 0.47619 | 5 | CDC LVL | 25.875 | 0.43191 | 0.016692 | 26.3069
Storage | 220 | 2 | 3 |  | 33 |  |  | 9 | 297 | 23.75 | 25 | 0.95 | 4.798 | 0.20202 | 5 | CDC LVL | 12.9375 | 0.086382 | 0.0066769 | 13.0239
File Storage | 221 | 2 | 3 |  | 136 |  |  | 9 | 1224 | 71.25 | 75 | 0.95 | 3.4926 | 1.5074 | 5 | CDC LVL | 38.8125 | 2.6562 | 0.068438 | 41.4688
Office | 222 | 2 | 3 |  | 169 |  |  | 9 | 1521 | 95 | 100 | 0.95 | 3.7475 | 1.2525 | 5 | CDC LVL | 51.75 | 2.7426 | 0.052998 | 54.4926
Office | 223 | 2 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0.90517 | 5 | CDC LVL | 38.8125 | 1.3605 | 0.035054 | 40.173
Office | 224 | 2 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 225 | 2 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 226 | 2 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0.90517 | 5 | CDC LVL | 38.8125 | 1.3605 | 0.035054 | 40.173
Office | 227 | 2 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 1.0084 | 5 | CDC LVL | 38.8125 | 1.5549 | 0.040061 | 40.3674
Reception | 228 | 2 | 3 |  | 772 |  |  | 9 | 6948 | 100 | 400 | 0.25 | 0.86356 | 4.1364 | 5 | CDC LVL | 207 | 41.377 | 0.19989 | 248.377
Restroom Men | 229 | 2 | 3 |  | 172 | 2095 |  | 9 | 1548 | 95 | 100 | 0.95 | 3.6822 | 1.3178 | 5 | CDC LVL | 51.75 | 2.937 | 0.056753 | 54.687
Restroom Womens | 230 | 2 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 1.9404 | 5 | CDC LVL | 51.75 | 5.2045 | 0.10057 | 56.9545
Hall | 231 | 2 | 4 |  | 600 |  |  | 9 | 5400 | 285 | 300 | 0.95 | 3.1667 | 1.8333 | 5 | CDC LVL | 155.25 | 14.253 | 0.091807 | 169.503
Mechanical Shaft | 232 | 2 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 1.8333 | 5 | CDC LVL | 103.5 | 9.502 | 0.091807 | 113.002
Elevators | 233 | 2 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 0.77778 | 5 | CDC LVL | 103.5 | 3.0234 | 0.029211 | 106.5234
Stairs | 233 | 2 | 5 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 1.8333 | 5 | CDC LVL | 103.5 | 9.502 | 0.091807 | 113.002
Stairs | 234 | 2 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 1.8333 | 5 | CDC LVL | 103.5 | 9.502 | 0.091807 | 113.002
Office | 300 | 3 | 1 |  | 121 |  |  | 9 | 1089 | 71.25 | 75 | 0.95 | 3.9256 | 1.0744 | 5 | CDC LVL | 38.8125 | 1.6845 | 0.0434 | 40.497
Office | 301 | 3 | 1 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 1.0084 | 5 | CDC LVL | 38.8125 | 1.5549 | 0.040061 | 40.3674
Office | 302 | 3 | 1 |  | 119 |  |  | 9 | 1071 | 19.5 | 75 | 0.26 | 1.0924 | 3.9076 | 5 | CDC LVL | 38.8125 | 6.0252 | 0.15524 | 44.8377
Office | 303 | 3 | 1 |  | 189 |  |  | 9 | 1701 | 95 | 100 | 0.95 | 3.351 | 1.649 | 5 | CDC LVL | 51.75 | 4.0384 | 0.078036 | 55.7884
Office | 304 | 3 | 1 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 305 | 3 | 1 |  | 117 |  |  | 9 | 1053 | 71.25 | 75 | 0.95 | 4.0598 | 0.94017 | 5 | CDC LVL | 38.8125 | 1.4253 | 0.036723 | 40.2378
Office | 306 | 3 | 1 |  | 113 |  |  | 9 | 1017 | 71.25 | 75 | 0.95 | 4.2035 | 0.79646 | 5 | CDC LVL | 38.8125 | 1.1662 | 0.030046 | 39.9787
Office | 306 | 3 | 1 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 38.8125 | 1.6197 | 0.04173 | 40.4322
Collaboration | 305 | 3 | 1 |  | 290 |  |  | 9 | 2610 | 190 | 200 | 0.95 | 4.3678 | 0.63218 | 5 | CDC LVL | 103.5 | 2.3755 | 0.022952 | 105.8755
Admin | 305 | 3 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 3.8095 | 5 | CDC LVL | 103.5 | 13.8211 | 0.13354 | 117.3211
Reception | 306 | 3 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 3.8095 | 5 | CDC LVL | 103.5 | 13.8211 | 0.13354 | 117.3211
Copy | 307 | 3 | 1 |  | 82 |  |  | 9 | 738 | 47.5 | 50 | 0.95 | 3.8618 | 1.1382 | 5 | CDC LVL | 25.875 | 1.2093 | 0.046738 | 27.0843
Break Room | 307 | 3 | 1 |  | 72 |  |  | 9 | 648 | 47.5 | 50 | 0.95 | 4.3981 | 0.60185 | 5 | CDC LVL | 25.875 | 0.56148 | 0.0217 | 26.4365
IT | 308 | 3 | 1 |  | 73 | 2093 |  | 9 | 657 | 47.5 | 50 | 0.95 | 4.3379 | 0.6621 | 5 | CDC LVL | 25.875 | 0.62627 | 0.024204 | 26.5013
Common Area | 309 | 3 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 1.1296 | 5 | CDC LVL | 284.625 | 13.1733 | 0.046283 | 297.7983
Office | 310 | 3 | 2 |  | 131 |  |  | 9 | 1179 | 7.5 | 75 | 0.1 | 0.38168 | 4.6183 | 5 | CDC LVL | 38.8125 | 7.8392 | 0.20198 | 46.6517
Office | 311 | 3 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 3.9899 | 5 | CDC LVL | 51.75 | 8.5302 | 0.16484 | 60.2802
Office | 312 | 3 | 2 |  | 120 |  |  | 9 | 1080 | 7.5 | 75 | 0.1 | 0.41667 | 4.5833 | 5 | CDC LVL | 38.8125 | 7.1265 | 0.18361 | 45.939
Office | 313 | 3 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 38.8125 | 1.6197 | 0.04173 | 40.4322
Office | 313 | 3 | 2 |  | 165 |  |  | 9 | 1485 | 95 | 100 | 0.95 | 3.8384 | 1.1616 | 5 | CDC LVL | 51.75 | 2.4835 | 0.04799 | 54.2335
Office | 314 | 3 | 2 |  | 131 |  |  | 9 | 1179 | 95 | 100 | 0.95 | 4.8346 | 0.16539 | 5 | CDC LVL | 51.75 | 0.28074 | 0.005425 | 52.0307
Bull Penns | 315 | 3 | 2 |  | 900 | 2632 |  | 9 | 8100 | 50 | 200 | 0.25 | 0.37037 | 4.6296 | 5 | CDC LVL | 103.5 | 53.9888 | 0.52163 | 157.4888
Meeting Room | 316 | 3 | 3 |  | 417 |  |  | 9 | 3753 | 285 | 300 | 0.95 | 4.5564 | 0.44365 | 5 | CDC LVL | 155.25 | 2.3971 | 0.01544 | 157.6471
Research Room | 317 | 3 | 3 |  | 201 |  |  | 9 | 1809 | 118.75 | 125 | 0.95 | 3.9386 | 1.0614 | 5 | CDC LVL | 64.6875 | 2.7642 | 0.042732 | 67.4517
Office | 318 | 3 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 319 | 3 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0.90517 | 5 | CDC LVL | 38.8125 | 1.3605 | 0.035054 | 40.173
Office | 320 | 3 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 321 | 3 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 322 | 3 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0.90517 | 5 | CDC LVL | 38.8125 | 1.3605 | 0.035054 | 40.173
Office | 323 | 3 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 1.0084 | 5 | CDC LVL | 38.8125 | 1.5549 | 0.040061 | 40.3674
Hall | 324 | 3 | 3 |  | 600 |  |  | 9 | 5400 | 30 | 300 | 0.1 | 0.33333 | 4.6667 | 5 | CDC LVL | 155.25 | 36.2805 | 0.23369 | 191.5305
Restroom Men | 325 | 3 | 3 |  | 172 | 2095 |  | 9 | 1548 | 10 | 100 | 0.1 | 0.3876 | 4.6124 | 5 | CDC LVL | 51.75 | 10.2795 | 0.19864 | 62.0295
Restroom Womens | 326 | 3 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 1.9404 | 5 | CDC LVL | 51.75 | 5.2045 | 0.10057 | 56.9545
Hall | 327 | 3 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 1.3056 | 5 | CDC LVL | 181.125 | 10.1499 | 0.056038 | 191.2749
Mechanical Shaft | 328 | 3 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 1.8333 | 5 | CDC LVL | 103.5 | 9.502 | 0.091807 | 113.002
Elevators | 329 | 3 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 0.77778 | 5 | CDC LVL | 103.5 | 3.0234 | 0.029211 | 106.5234
Stairs | 329 | 3 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 129.375 | 5.3989 | 0.04173 | 134.7739
Stairs | 330 | 3 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 129.375 | 5.3989 | 0.04173 | 134.7739
Office | 300 | 4 | 1 |  | 121 |  |  | 9 | 1089 | 71.25 | 75 | 0.95 | 3.9256 | 1.0744 | 5 | CDC LVL | 38.8125 | 1.6845 | 0.0434 | 40.497
Office | 301 | 4 | 1 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 1.0084 | 5 | CDC LVL | 38.8125 | 1.5549 | 0.040061 | 40.3674
Office | 302 | 4 | 1 |  | 119 |  |  | 9 | 1071 | 19.5 | 75 | 0.26 | 1.0924 | 3.9076 | 5 | CDC LVL | 38.8125 | 6.0252 | 0.15524 | 44.8377
Office | 303 | 4 | 1 |  | 189 |  |  | 9 | 1701 | 95 | 100 | 0.95 | 3.351 | 1.649 | 5 | CDC LVL | 51.75 | 4.0384 | 0.078036 | 55.7884
Office | 304 | 4 | 1 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 305 | 4 | 1 |  | 117 |  |  | 9 | 1053 | 71.25 | 75 | 0.95 | 4.0598 | 0.94017 | 5 | CDC LVL | 38.8125 | 1.4253 | 0.036723 | 40.2378
Office | 306 | 4 | 1 |  | 113 |  |  | 9 | 1017 | 71.25 | 75 | 0.95 | 4.2035 | 0.79646 | 5 | CDC LVL | 38.8125 | 1.1662 | 0.030046 | 39.9787
Office | 306 | 4 | 1 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 38.8125 | 1.6197 | 0.04173 | 40.4322
Collaboration | 305 | 4 | 1 |  | 290 |  |  | 9 | 2610 | 190 | 200 | 0.95 | 4.3678 | 0.63218 | 5 | CDC LVL | 103.5 | 2.3755 | 0.022952 | 105.8755
Admin | 305 | 4 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 3.8095 | 5 | CDC LVL | 103.5 | 13.8211 | 0.13354 | 117.3211
Reception | 306 | 4 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 3.8095 | 5 | CDC LVL | 103.5 | 13.8211 | 0.13354 | 117.3211
Copy | 307 | 4 | 1 |  | 82 |  |  | 9 | 738 | 47.5 | 50 | 0.95 | 3.8618 | 1.1382 | 5 | CDC LVL | 25.875 | 1.2093 | 0.046738 | 27.0843
Break Room | 307 | 4 | 1 |  | 72 |  |  | 9 | 648 | 47.5 | 50 | 0.95 | 4.3981 | 0.60185 | 5 | CDC LVL | 25.875 | 0.56148 | 0.0217 | 26.4365
IT | 308 | 4 | 1 |  | 73 | 2093 |  | 9 | 657 | 47.5 | 50 | 0.95 | 4.3379 | 0.6621 | 5 | CDC LVL | 25.875 | 0.62627 | 0.024204 | 26.5013
Common Area | 309 | 4 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 1.1296 | 5 | CDC LVL | 284.625 | 13.1733 | 0.046283 | 297.7983
Office | 310 | 4 | 2 |  | 131 |  |  | 9 | 1179 | 7.5 | 75 | 0.1 | 0.38168 | 4.6183 | 5 | CDC LVL | 38.8125 | 7.8392 | 0.20198 | 46.6517
Office | 311 | 4 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 3.9899 | 5 | CDC LVL | 51.75 | 8.5302 | 0.16484 | 60.2802
Office | 312 | 4 | 2 |  | 120 |  |  | 9 | 1080 | 7.5 | 75 | 0.1 | 0.41667 | 4.5833 | 5 | CDC LVL | 38.8125 | 7.1265 | 0.18361 | 45.939
Office | 313 | 4 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 38.8125 | 1.6197 | 0.04173 | 40.4322
Office | 313 | 4 | 2 |  | 165 |  |  | 9 | 1485 | 95 | 100 | 0.95 | 3.8384 | 1.1616 | 5 | CDC LVL | 51.75 | 2.4835 | 0.04799 | 54.2335
Office | 314 | 4 | 2 |  | 131 |  |  | 9 | 1179 | 95 | 100 | 0.95 | 4.8346 | 0.16539 | 5 | CDC LVL | 51.75 | 0.28074 | 0.005425 | 52.0307
Bull Penns | 315 | 4 | 2 |  | 900 | 2632 |  | 9 | 8100 | 50 | 200 | 0.25 | 0.37037 | 4.6296 | 5 | CDC LVL | 103.5 | 53.9888 | 0.52163 | 157.4888
Meeting Room | 316 | 4 | 3 |  | 265 |  |  | 9 | 2385 | 285 | 300 | 0.95 | 7.1698 | 2.1698 | 9.3396 | CDC & Harvard LVL | 155.25 | 7.4505 | 0.04799 | 162.7005
Research Room | 317 | 4 | 3 |  | 128 |  |  | 9 | 1152 | 118.75 | 125 | 0.95 | 6.1849 | 1.1849 | 7.3698 | CDC & Harvard LVL | 64.6875 | 1.9652 | 0.03038 | 66.6527
Office | 318 | 4 | 3 |  | 92 |  |  | 9 | 828 | 71.25 | 75 | 0.95 | 5.163 | 0.16304 | 5.3261 | CDC LVL | 38.8125 | 0.19436 | 0.0050077 | 39.0069
Office | 319 | 4 | 3 |  | 105 |  |  | 9 | 945 | 71.25 | 75 | 0.95 | 4.5238 | 0.47619 | 5 | CDC LVL | 38.8125 | 0.64787 | 0.016692 | 39.4604
Office | 320 | 4 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 321 | 4 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0.90517 | 5 | CDC LVL | 38.8125 | 1.3605 | 0.035054 | 40.173
Office | 322 | 4 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 322 | 4 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 322 | 4 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0.90517 | 5 | CDC LVL | 38.8125 | 1.3605 | 0.035054 | 40.173
Office | 323 | 4 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 1.0084 | 5 | CDC LVL | 38.8125 | 1.5549 | 0.040061 | 40.3674
Hall | 324 | 4 | 3 |  | 628 |  |  | 9 | 5652 | 30 | 300 | 0.1 | 0.31847 | 4.6815 | 5 | CDC LVL | 155.25 | 38.0945 | 0.24538 | 193.3445
Restroom Men | 325 | 4 | 3 |  | 172 | 2095 |  | 9 | 1548 | 10 | 100 | 0.1 | 0.3876 | 4.6124 | 5 | CDC LVL | 51.75 | 10.2795 | 0.19864 | 62.0295
Restroom Womens | 326 | 4 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 1.9404 | 5 | CDC LVL | 51.75 | 5.2045 | 0.10057 | 56.9545
Hall | 327 | 4 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 1.3056 | 5 | CDC LVL | 181.125 | 10.1499 | 0.056038 | 191.2749
Mechanical Shaft | 328 | 4 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 1.8333 | 5 | CDC LVL | 103.5 | 9.502 | 0.091807 | 113.002
Elevators | 329 | 4 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 0.77778 | 5 | CDC LVL | 103.5 | 3.0234 | 0.029211 | 106.5234
Stairs | 329 | 4 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 129.375 | 5.3989 | 0.04173 | 134.7739
Stairs | 330 | 4 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 129.375 | 5.3989 | 0.04173 | 134.7739
Office | 300 | 5 | 1 |  | 121 |  |  | 9 | 1089 | 71.25 | 75 | 0.95 | 3.9256 | 1.0744 | 5 | CDC LVL | 38.8125 | 1.6845 | 0.0434 | 40.497
Office | 301 | 5 | 1 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 1.0084 | 5 | CDC LVL | 38.8125 | 1.5549 | 0.040061 | 40.3674
Office | 302 | 5 | 1 |  | 119 |  |  | 9 | 1071 | 19.5 | 75 | 0.26 | 1.0924 | 3.9076 | 5 | CDC LVL | 38.8125 | 6.0252 | 0.15524 | 44.8377
Office | 303 | 5 | 1 |  | 189 |  |  | 9 | 1701 | 95 | 100 | 0.95 | 3.351 | 1.649 | 5 | CDC LVL | 51.75 | 4.0384 | 0.078036 | 55.7884
Office | 304 | 5 | 1 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 305 | 5 | 1 |  | 117 |  |  | 9 | 1053 | 71.25 | 75 | 0.95 | 4.0598 | 0.94017 | 5 | CDC LVL | 38.8125 | 1.4253 | 0.036723 | 40.2378
Office | 306 | 5 | 1 |  | 113 |  |  | 9 | 1017 | 71.25 | 75 | 0.95 | 4.2035 | 0.79646 | 5 | CDC LVL | 38.8125 | 1.1662 | 0.030046 | 39.9787
Office | 306 | 5 | 1 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 38.8125 | 1.6197 | 0.04173 | 40.4322
Collaboration | 305 | 5 | 1 |  | 290 |  |  | 9 | 2610 | 190 | 200 | 0.95 | 4.3678 | 0.63218 | 5 | CDC LVL | 103.5 | 2.3755 | 0.022952 | 105.8755
Admin | 305 | 5 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 3.8095 | 5 | CDC LVL | 103.5 | 13.8211 | 0.13354 | 117.3211
Reception | 306 | 5 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 3.8095 | 5 | CDC LVL | 103.5 | 13.8211 | 0.13354 | 117.3211
Copy | 307 | 5 | 1 |  | 82 |  |  | 9 | 738 | 47.5 | 50 | 0.95 | 3.8618 | 1.1382 | 5 | CDC LVL | 25.875 | 1.2093 | 0.046738 | 27.0843
Break Room | 307 | 5 | 1 |  | 72 |  |  | 9 | 648 | 47.5 | 50 | 0.95 | 4.3981 | 0.60185 | 5 | CDC LVL | 25.875 | 0.56148 | 0.0217 | 26.4365
Storage | 308 | 5 | 1 |  | 73 | 2093 |  | 9 | 657 | 47.5 | 50 | 0.95 | 4.3379 | 0.6621 | 5 | CDC LVL | 25.875 | 0.62627 | 0.024204 | 26.5013
Common Area | 309 | 5 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 1.1296 | 5 | CDC LVL | 284.625 | 13.1733 | 0.046283 | 297.7983
Office | 310 | 5 | 2 |  | 131 |  |  | 9 | 1179 | 7.5 | 75 | 0.1 | 0.38168 | 4.6183 | 5 | CDC LVL | 38.8125 | 7.8392 | 0.20198 | 46.6517
Office | 311 | 5 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 3.9899 | 5 | CDC LVL | 51.75 | 8.5302 | 0.16484 | 60.2802
Office | 312 | 5 | 2 |  | 120 |  |  | 9 | 1080 | 7.5 | 75 | 0.1 | 0.41667 | 4.5833 | 5 | CDC LVL | 38.8125 | 7.1265 | 0.18361 | 45.939
Office | 313 | 5 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 38.8125 | 1.6197 | 0.04173 | 40.4322
Office | 313 | 5 | 2 |  | 165 |  |  | 9 | 1485 | 95 | 100 | 0.95 | 3.8384 | 1.1616 | 5 | CDC LVL | 51.75 | 2.4835 | 0.04799 | 54.2335
Office | 314 | 5 | 2 |  | 131 |  |  | 9 | 1179 | 95 | 100 | 0.95 | 4.8346 | 0.16539 | 5 | CDC LVL | 51.75 | 0.28074 | 0.005425 | 52.0307
Bull Penns | 315 | 5 | 2 |  | 900 | 2632 |  | 9 | 8100 | 50 | 200 | 0.25 | 0.37037 | 4.6296 | 5 | CDC LVL | 103.5 | 53.9888 | 0.52163 | 157.4888
Idea Room | 316 | 5 | 3 |  | 423 |  |  | 9 | 3807 | 285 | 300 | 0.95 | 4.4917 | 0.50827 | 5 | CDC LVL | 155.25 | 2.7858 | 0.017944 | 158.0358
Office | 317 | 5 | 3 |  | 92 |  |  | 9 | 828 | 71.25 | 75 | 0.95 | 5.163 | 0.16304 | 5.3261 | CDC LVL | 38.8125 | 0.19436 | 0.0050077 | 39.0069
Office | 318 | 5 | 3 |  | 105 |  |  | 9 | 945 | 71.25 | 75 | 0.95 | 4.5238 | 0.47619 | 5 | CDC LVL | 38.8125 | 0.64787 | 0.016692 | 39.4604
Office | 319 | 5 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 320 | 5 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0.90517 | 5 | CDC LVL | 38.8125 | 1.3605 | 0.035054 | 40.173
Office | 321 | 5 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 321 | 5 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 321 | 5 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0.90517 | 5 | CDC LVL | 38.8125 | 1.3605 | 0.035054 | 40.173
Office | 322 | 5 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 1.0084 | 5 | CDC LVL | 38.8125 | 1.5549 | 0.040061 | 40.3674
Hall | 323 | 5 | 3 |  | 598 |  |  | 9 | 5382 | 30 | 300 | 0.1 | 0.33445 | 4.6656 | 5 | CDC LVL | 155.25 | 36.1509 | 0.23286 | 191.4009
Restroom Men | 324 | 5 | 3 |  | 172 | 2095 |  | 9 | 1548 | 10 | 100 | 0.1 | 0.3876 | 4.6124 | 5 | CDC LVL | 51.75 | 10.2795 | 0.19864 | 62.0295
Restroom Womens | 325 | 5 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 1.9404 | 5 | CDC LVL | 51.75 | 5.2045 | 0.10057 | 56.9545
Hall | 326 | 5 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 1.3056 | 5 | CDC LVL | 181.125 | 10.1499 | 0.056038 | 191.2749
Mechanical Shaft | 327 | 5 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 1.8333 | 5 | CDC LVL | 103.5 | 9.502 | 0.091807 | 113.002
Elevators | 328 | 5 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 0.77778 | 5 | CDC LVL | 103.5 | 3.0234 | 0.029211 | 106.5234
Stairs | 328 | 5 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 129.375 | 5.3989 | 0.04173 | 134.7739
Stairs | 329 | 5 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 129.375 | 5.3989 | 0.04173 | 134.7739
Office | 300 | 6 | 1 |  | 121 |  |  | 9 | 1089 | 71.25 | 75 | 0.95 | 3.9256 | 1.0744 | 5 | CDC LVL | 38.8125 | 1.6845 | 0.0434 | 40.497
Office | 301 | 6 | 1 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 1.0084 | 5 | CDC LVL | 38.8125 | 1.5549 | 0.040061 | 40.3674
Office | 302 | 6 | 1 |  | 119 |  |  | 9 | 1071 | 19.5 | 75 | 0.26 | 1.0924 | 3.9076 | 5 | CDC LVL | 38.8125 | 6.0252 | 0.15524 | 44.8377
Office | 303 | 6 | 1 |  | 189 |  |  | 9 | 1701 | 95 | 100 | 0.95 | 3.351 | 1.649 | 5 | CDC LVL | 51.75 | 4.0384 | 0.078036 | 55.7884
Office | 304 | 6 | 1 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 305 | 6 | 1 |  | 117 |  |  | 9 | 1053 | 71.25 | 75 | 0.95 | 4.0598 | 0.94017 | 5 | CDC LVL | 38.8125 | 1.4253 | 0.036723 | 40.2378
Office | 306 | 6 | 1 |  | 113 |  |  | 9 | 1017 | 71.25 | 75 | 0.95 | 4.2035 | 0.79646 | 5 | CDC LVL | 38.8125 | 1.1662 | 0.030046 | 39.9787
Office | 306 | 6 | 1 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 38.8125 | 1.6197 | 0.04173 | 40.4322
Collaboration | 305 | 6 | 1 |  | 290 |  |  | 9 | 2610 | 190 | 200 | 0.95 | 4.3678 | 0.63218 | 5 | CDC LVL | 103.5 | 2.3755 | 0.022952 | 105.8755
Admin | 305 | 6 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 3.8095 | 5 | CDC LVL | 103.5 | 13.8211 | 0.13354 | 117.3211
Reception | 306 | 6 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 3.8095 | 5 | CDC LVL | 103.5 | 13.8211 | 0.13354 | 117.3211
Copy | 307 | 6 | 1 |  | 82 |  |  | 9 | 738 | 47.5 | 50 | 0.95 | 3.8618 | 1.1382 | 5 | CDC LVL | 25.875 | 1.2093 | 0.046738 | 27.0843
Break Room | 307 | 6 | 1 |  | 72 |  |  | 9 | 648 | 47.5 | 50 | 0.95 | 4.3981 | 0.60185 | 5 | CDC LVL | 25.875 | 0.56148 | 0.0217 | 26.4365
IT | 308 | 6 | 1 |  | 73 | 2093 |  | 9 | 657 | 47.5 | 50 | 0.95 | 4.3379 | 0.6621 | 5 | CDC LVL | 25.875 | 0.62627 | 0.024204 | 26.5013
Common Area | 309 | 6 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 1.1296 | 5 | CDC LVL | 284.625 | 13.1733 | 0.046283 | 297.7983
Office | 310 | 6 | 2 |  | 131 |  |  | 9 | 1179 | 7.5 | 75 | 0.1 | 0.38168 | 4.6183 | 5 | CDC LVL | 38.8125 | 7.8392 | 0.20198 | 46.6517
Office | 311 | 6 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 3.9899 | 5 | CDC LVL | 51.75 | 8.5302 | 0.16484 | 60.2802
Office | 312 | 6 | 2 |  | 120 |  |  | 9 | 1080 | 7.5 | 75 | 0.1 | 0.41667 | 4.5833 | 5 | CDC LVL | 38.8125 | 7.1265 | 0.18361 | 45.939
Office | 313 | 6 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 38.8125 | 1.6197 | 0.04173 | 40.4322
Office | 313 | 6 | 2 |  | 165 |  |  | 9 | 1485 | 95 | 100 | 0.95 | 3.8384 | 1.1616 | 5 | CDC LVL | 51.75 | 2.4835 | 0.04799 | 54.2335
Office | 314 | 6 | 2 |  | 131 |  |  | 9 | 1179 | 95 | 100 | 0.95 | 4.8346 | 0.16539 | 5 | CDC LVL | 51.75 | 0.28074 | 0.005425 | 52.0307
Bull Penns | 315 | 6 | 2 |  | 900 | 2632 |  | 9 | 8100 | 50 | 200 | 0.25 | 0.37037 | 4.6296 | 5 | CDC LVL | 103.5 | 53.9888 | 0.52163 | 157.4888
Conference Room | 316 | 6 | 3 |  | 423 |  |  | 9 | 3807 | 285 | 300 | 0.95 | 4.4917 | 0.50827 | 5 | CDC LVL | 155.25 | 2.7858 | 0.017944 | 158.0358
Office | 317 | 6 | 3 |  | 92 |  |  | 9 | 828 | 71.25 | 75 | 0.95 | 5.163 | 0.16304 | 5.3261 | CDC LVL | 38.8125 | 0.19436 | 0.0050077 | 39.0069
Office | 318 | 6 | 3 |  | 105 |  |  | 9 | 945 | 71.25 | 75 | 0.95 | 4.5238 | 0.47619 | 5 | CDC LVL | 38.8125 | 0.64787 | 0.016692 | 39.4604
Office | 319 | 6 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 320 | 6 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0.90517 | 5 | CDC LVL | 38.8125 | 1.3605 | 0.035054 | 40.173
Office | 321 | 6 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 321 | 6 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 321 | 6 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0.90517 | 5 | CDC LVL | 38.8125 | 1.3605 | 0.035054 | 40.173
Office | 322 | 6 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 1.0084 | 5 | CDC LVL | 38.8125 | 1.5549 | 0.040061 | 40.3674
Hall | 323 | 6 | 3 |  | 598 |  |  | 9 | 5382 | 30 | 300 | 0.1 | 0.33445 | 4.6656 | 5 | CDC LVL | 155.25 | 36.1509 | 0.23286 | 191.4009
Restroom Men | 324 | 6 | 3 |  | 172 | 2095 |  | 9 | 1548 | 10 | 100 | 0.1 | 0.3876 | 4.6124 | 5 | CDC LVL | 51.75 | 10.2795 | 0.19864 | 62.0295
Restroom Womens | 325 | 6 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 1.9404 | 5 | CDC LVL | 51.75 | 5.2045 | 0.10057 | 56.9545
Hall | 326 | 6 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 1.3056 | 5 | CDC LVL | 181.125 | 10.1499 | 0.056038 | 191.2749
Mechanical Shaft | 327 | 6 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 1.8333 | 5 | CDC LVL | 103.5 | 9.502 | 0.091807 | 113.002
Elevators | 328 | 6 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 0.77778 | 5 | CDC LVL | 103.5 | 3.0234 | 0.029211 | 106.5234
Stairs | 328 | 6 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 129.375 | 5.3989 | 0.04173 | 134.7739
Stairs | 329 | 6 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 129.375 | 5.3989 | 0.04173 | 134.7739
Conference | 300 | 7 | 1 |  | 215 |  |  | 9 | 1935 | 71.25 | 75 | 0.95 | 2.2093 | 2.7907 | 5 | CDC LVL | 38.8125 | 7.7744 | 0.20031 | 46.5869
Staff | 301 | 7 | 1 |  | 109 |  |  | 9 | 981 | 71.25 | 75 | 0.95 | 4.3578 | 0.6422 | 5 | CDC LVL | 38.8125 | 0.90701 | 0.023369 | 39.7195
Workroom | 302 | 7 | 1 |  | 242 |  |  | 9 | 2178 | 71.25 | 75 | 0.95 | 1.9628 | 3.0372 | 5 | CDC LVL | 38.8125 | 9.5236 | 0.24538 | 48.3361
Lab | 303 | 7 | 1 |  | 1220 |  |  | 9 | 10980 | 855 | 900 | 0.95 | 4.6721 | 0.32787 | 5 | CDC LVL | 465.75 | 5.1829 | 0.011128 | 470.9329
Lab Storage | 304 | 7 | 1 |  | 151 |  |  | 9 | 1359 | 71.25 | 75 | 0.95 | 3.1457 | 1.8543 | 5 | CDC LVL | 38.8125 | 3.628 | 0.093476 | 42.4405
Hall | 305 | 7 | 1 |  | 92 |  |  | 9 | 828 | 71.25 | 75 | 0.95 | 5.163 | 0.16304 | 5.3261 | CDC LVL | 38.8125 | 0.19436 | 0.0050077 | 39.0069
Break Room | 306 | 7 | 1 |  | 64 | 2093 |  | 9 | 576 | 5 | 50 | 0.1 | 0.52083 | 4.4792 | 5 | CDC LVL | 25.875 | 3.7144 | 0.14355 | 29.5894
Common Area | 307 | 7 | 2 |  | 1279 |  |  | 9 | 11511 | 760 | 800 | 0.95 | 3.9614 | 1.0386 | 5 | CDC LVL | 414 | 17.2116 | 0.041574 | 431.2116
IT Office | 308 | 7 | 2 |  | 122 |  |  | 9 | 1098 | 95 | 100 | 0.95 | 5.1913 | 0.19126 | 5.3825 | CDC LVL | 51.75 | 0.30234 | 0.0058423 | 52.0523
Office | 309 | 7 | 2 |  | 122 |  |  | 9 | 1098 | 95 | 100 | 0.95 | 5.1913 | 0.19126 | 5.3825 | CDC LVL | 51.75 | 0.30234 | 0.0058423 | 52.0523
Staff | 310 | 7 | 2 |  | 179 |  |  | 9 | 1611 | 95 | 100 | 0.95 | 3.5382 | 1.4618 | 5 | CDC LVL | 51.75 | 3.3905 | 0.065517 | 55.1405
Workroom | 311 | 7 | 2 |  | 250 |  |  | 9 | 2250 | 190 | 200 | 0.95 | 5.0667 | 0.066667 | 5.1333 | CDC LVL | 103.5 | 0.21596 | 0.0020865 | 103.716
File Storage | 311 | 7 | 2 |  | 162 |  |  | 9 | 1458 | 95 | 100 | 0.95 | 3.9095 | 1.0905 | 5 | CDC LVL | 51.75 | 2.2891 | 0.044234 | 54.0391
Doctoral Student Lounge | 312 | 7 | 2 |  | 274 |  |  | 9 | 2466 | 190 | 200 | 0.95 | 4.6229 | 0.37713 | 5 | CDC LVL | 103.5 | 1.3389 | 0.012936 | 104.8389
Reception | 313 | 7 | 2 |  | 244 | 2632 |  | 9 | 2196 | 80 | 200 | 0.4 | 2.1858 | 2.8142 | 5 | CDC LVL | 103.5 | 8.8974 | 0.085965 | 112.3974
Copy | 314 | 7 | 3 |  | 85 |  |  | 9 | 765 | 47.5 | 50 | 0.95 | 3.7255 | 1.2745 | 5 | CDC LVL | 25.875 | 1.4037 | 0.05425 | 27.2787
Consult | 315 | 7 | 3 |  | 84 |  |  | 9 | 756 | 47.5 | 50 | 0.95 | 3.7698 | 1.2302 | 5 | CDC LVL | 25.875 | 1.3389 | 0.051746 | 27.2139
Consult | 316 | 7 | 3 |  | 92 |  |  | 9 | 828 | 47.5 | 50 | 0.95 | 3.442 | 1.558 | 5 | CDC LVL | 25.875 | 1.8572 | 0.071776 | 27.7322
Part Time Faculty | 317 | 7 | 3 |  | 88 |  |  | 9 | 792 | 47.5 | 50 | 0.95 | 3.5985 | 1.4015 | 5 | CDC LVL | 25.875 | 1.5981 | 0.061761 | 27.4731
Part Time Faculty | 318 | 7 | 3 |  | 88 |  |  | 9 | 792 | 47.5 | 50 | 0.95 | 3.5985 | 1.4015 | 5 | CDC LVL | 25.875 | 1.5981 | 0.061761 | 27.4731
Office | 319 | 7 | 3 |  | 119 |  |  | 9 | 1071 | 7.5 | 75 | 0.1 | 0.42017 | 4.5798 | 5 | CDC LVL | 38.8125 | 7.0617 | 0.18194 | 45.8742
Office | 320 | 7 | 3 |  | 116 |  |  | 9 | 1044 | 7.5 | 75 | 0.1 | 0.43103 | 4.569 | 5 | CDC LVL | 38.8125 | 6.8674 | 0.17694 | 45.6799
Office | 320 | 7 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 320 | 7 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 0.97458 | 5 | CDC LVL | 38.8125 | 1.4901 | 0.038392 | 40.3026
Office | 320 | 7 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 0.90517 | 5 | CDC LVL | 38.8125 | 1.3605 | 0.035054 | 40.173
Office | 321 | 7 | 3 |  | 169 |  |  | 9 | 1521 | 71.25 | 75 | 0.95 | 2.8107 | 2.1893 | 5 | CDC LVL | 38.8125 | 4.7942 | 0.12352 | 43.6067
Admin & Hall | 322 | 7 | 3 |  | 730 |  |  | 9 | 6570 | 380 | 400 | 0.95 | 3.4703 | 1.5297 | 5 | CDC LVL | 207 | 14.469 | 0.069899 | 221.469
Restroom Men | 323 | 7 | 3 |  | 172 | 2095 |  | 9 | 1548 | 95 | 100 | 0.95 | 3.6822 | 1.3178 | 5 | CDC LVL | 51.75 | 2.937 | 0.056753 | 54.687
Restroom Womens | 324 | 7 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 1.9404 | 5 | CDC LVL | 51.75 | 5.2045 | 0.10057 | 56.9545
Hall | 325 | 7 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 1.3056 | 5 | CDC LVL | 181.125 | 10.1499 | 0.056038 | 191.2749
Mechanical Shaft | 326 | 7 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 1.8333 | 5 | CDC LVL | 103.5 | 9.502 | 0.091807 | 113.002
Elevators | 327 | 7 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 0.77778 | 5 | CDC LVL | 103.5 | 3.0234 | 0.029211 | 106.5234
Stairs | 327 | 7 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 129.375 | 5.3989 | 0.04173 | 134.7739
Stairs | 328 | 7 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 1.0417 | 5 | CDC LVL | 129.375 | 5.3989 | 0.04173 | 134.7739

## Bld 1 Arch C
Building | Example
Survey Team | TBD | [21 empty] | ACH = CFM * 60 / cuft
Survey Date | TBD | [21 empty] | CFM = ACH*cuft/60
Purpose | This sheet captures the ventilation performance level in each room and the power required for the ventilation level achieved. | [23 empty] | cuft | CFM |  |  | ACH
Note | Once a survey is performed these values will be updated. | [23 empty] | 31500 | 2362.5 |  |  | 4.5
Ventilation Type | DCV: occupancy, timers, temperature, humidity | [21 empty] | 2100 | 15 | 31500 | 2375 | 2500 | 0.95 | 4.5238
Sensors | Particle, CO2
Control | Outsourced to Energy Company XYZ
Model Type | Fine Grain
Mech Watts / CFM 2023 | 0.5175
Mech Watts / CFM 2025 | 0.5175 |  |  | Min | 33 | 800 | 9127 | 9 | 297 | 5 | 25 | 0.1 | 0.31847 | 4.8302 | 12 | Min | 12.9375 | 3.0795 | 0.10683 | 16.017
UV Watts / Cu-Ft 2023 | 0.017276 |  |  | Max | 5200 | 24627 | 24627 | 20 | 104000 | 6650 | 7000 | 0.95 | 7.1698 | 12 | 16.75 | Max | 3622.5 | 1222.3069 | 1.3178 | 4844.8069
Far UV Watts / Cu-Ft 2023 | 0.017276 |  |  | Avg | 339.2692 | 2560.9355 | 11341.2857 | 9.1453 | 3626.5 | 210.985 | 225.8547 | 0.80209 | 3.3666 | 8.6537 | 12.0203 | Avg | 116.8798 | 45.8304 | 0.38031 | 162.7102
Totals |  |  |  |  | 79389 | 79389 | 79389 | 9 | 848601 | 49370.5 | 52850 | [5 empty] | 27349.875 | 10724.3135 | 88.9924 | 38074.1885
Room Name | Number | Flr | Area | Zone | Sq-Ft | Area Sq-Ft | Floor Sq-Ft | Ht Ft | Cu-Ft | Actual CFM | Design CFM | Actual / Design | ACH | eACH | Total ACH | Ventilation Rating | Mech Watts 2023 | UV-C Watts | UV Watts / Mech Watts | Total Watts | ACH | Scale Setings
Cafe | 100 | 1 | 1 |  | 3200 |  |  | 15 | 48000 | 3800 | 4000 | 0.95 | 4.75 | 12 | 16.75 | CDC Airborne LVL | 2070 | 829.2683 | 0.40061 | 2899.2683 | 0 | Fail
Transit Lounge | 101 | 1 | 2 |  | 2100 |  |  | 15 | 31500 | 2375 | 2500 | 0.95 | 4.5238 | 7.4762 | 12 | CDC Airborne LVL | 1293.75 | 339.0498 | 0.26207 | 1632.7998 | 0.9 | Fail
Lobby | 102 | 1 | 3 |  | 4100 |  |  | 20 | 82000 | 4750 | 5000 | 0.95 | 3.4756 | 8.5244 | 12 | CDC Airborne LVL | 2587.5 | 1006.3516 | 0.38893 | 3593.8516 | 1 | Very Bad
Lecture Hall | 103 | 1 | 4 |  | 5200 |  |  | 20 | 104000 | 6650 | 7000 | 0.95 | 3.8365 | 8.1635 | 12 | CDC Airborne LVL | 3622.5 | 1222.3069 | 0.33742 | 4844.8069 | 2 | Bad
Space 1 | 104 | 1 | 5 |  | 3042.3333 |  |  | 9 | 27381 | 2000 | 600 | 0.95 | 4.3826 | 7.6174 | 12 | CDC Airborne LVL | 310.5 | 300.2815 | 0.96709 | 610.7815 | 3 | Poor
Space 2 | 105 | 1 | 5 |  | 3042.3333 |  |  | 9 | 27381 | 2000 | 600 | 0.95 | 4.3826 | 7.6174 | 12 | CDC Airborne LVL | 310.5 | 300.2815 | 0.96709 | 610.7815 | 4 | Low
Space 3 | 106 | 1 | 5 |  | 3042.3333 |  |  | 9 | 27381 | 2000 | 600 | 0.95 | 4.3826 | 7.6174 | 12 | CDC Airborne LVL | 310.5 | 300.2815 | 0.96709 | 610.7815 | 5 | CDC LVL
Restrooms | 107 | 1 | 6 |  | 900 | 24627 | 24627 | 9 | 8100 | 570 | 600 | 0.95 | 4.2222 | 7.7778 | 12 | CDC Airborne LVL | 310.5 | 90.7012 | 0.29211 | 401.2012 | 6 | CDC & Harvard LVL
Conference Room | 200 | 2 | 1 |  | 354 |  |  | 9 | 3186 | 213.75 | 225 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 116.4375 | 36.5785 | 0.31415 | 153.016 | 7 | CDC & Harvard LVL
Office | 201 | 2 | 1 |  | 264 |  |  | 9 | 2376 | 142.5 | 150 | 0.95 | 3.5985 | 8.4015 | 12 | CDC Airborne LVL | 77.625 | 28.7393 | 0.37023 | 106.3643 | 8 | CDC & Harvard LVL
Office | 202 | 2 | 1 |  | 168 |  |  | 9 | 1512 | 25 | 100 | 0.25 | 0.99206 | 11.0079 | 12 | CDC Airborne LVL | 51.75 | 23.9624 | 0.46304 | 75.7124 | 9 | CDC & Harvard LVL
Office | 203 | 2 | 1 |  | 171 |  |  | 9 | 1539 | 25 | 100 | 0.25 | 0.97466 | 11.0253 | 12 | CDC Airborne LVL | 51.75 | 24.4289 | 0.47206 | 76.1789 | 10 | CDC & Harvard LVL
Office | 204 | 2 | 1 |  | 169 |  |  | 9 | 1521 | 95 | 100 | 0.95 | 3.7475 | 8.2525 | 12 | CDC Airborne LVL | 51.75 | 18.0711 | 0.3492 | 69.8211 | 11 | CDC & Harvard LVL
Office | 205 | 2 | 1 |  | 171 |  |  | 9 | 1539 | 95 | 100 | 0.95 | 3.7037 | 8.2963 | 12 | CDC Airborne LVL | 51.75 | 18.3821 | 0.35521 | 70.1321 | 12 | CDC Airborne LVL
Bull Penns | 206 | 2 | 1 |  | 600 |  |  | 9 | 5400 | 200 | 400 | 0.5 | 2.2222 | 9.7778 | 12 | CDC Airborne LVL | 207 | 76.0163 | 0.36723 | 283.0163
Copy | 207 | 2 | 1 |  | 97 |  |  | 9 | 873 | 47.5 | 50 | 0.95 | 3.2646 | 8.7354 | 12 | CDC Airborne LVL | 25.875 | 10.9792 | 0.42432 | 36.8542
Break Room | 208 | 2 | 1 |  | 99 | 2093 |  | 9 | 891 | 47.5 | 50 | 0.95 | 3.1987 | 8.8013 | 12 | CDC Airborne LVL | 25.875 | 11.2901 | 0.43633 | 37.1651
Common Area | 209 | 2 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 8.1296 | 12 | CDC Airborne LVL | 284.625 | 94.8044 | 0.33309 | 379.4294
Office | 210 | 2 | 2 |  | 136 |  |  | 9 | 1224 | 95 | 100 | 0.95 | 4.6569 | 7.3431 | 12 | CDC Airborne LVL | 51.75 | 12.94 | 0.25005 | 64.69
Office | 211 | 2 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 10.9899 | 12 | CDC Airborne LVL | 51.75 | 23.4959 | 0.45403 | 75.2459
Office | 212 | 2 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 38.8125 | 12.5038 | 0.32216 | 51.3163
Office | 213 | 2 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 38.8125 | 12.5038 | 0.32216 | 51.3163
Office | 214 | 2 | 2 |  | 154 |  |  | 9 | 1386 | 95 | 100 | 0.95 | 4.1126 | 7.8874 | 12 | CDC Airborne LVL | 51.75 | 15.7388 | 0.30413 | 67.4888
Bull Penns | 215 | 2 | 2 |  | 905 |  |  | 9 | 8145 | 50 | 200 | 0.25 | 0.36832 | 11.6317 | 12 | CDC Airborne LVL | 103.5 | 136.3974 | 1.3178 | 239.8974
Copy Workroom | 216 | 2 | 2 |  | 92 |  |  | 9 | 828 | 47.5 | 50 | 0.95 | 3.442 | 8.558 | 12 | CDC Airborne LVL | 25.875 | 10.2017 | 0.39427 | 36.0767
Storage | 217 | 2 | 2 |  | 40 | 2632 |  | 9 | 360 | 23.75 | 25 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 12.9375 | 4.1679 | 0.32216 | 17.1054
Conference Room | 218 | 2 | 3 |  | 156 |  |  | 9 | 1404 | 95 | 100 | 0.95 | 4.0598 | 7.9402 | 12 | CDC Airborne LVL | 51.75 | 16.0498 | 0.31014 | 67.7998
Interview Room | 219 | 2 | 3 |  | 70 |  |  | 9 | 630 | 47.5 | 50 | 0.95 | 4.5238 | 7.4762 | 12 | CDC Airborne LVL | 25.875 | 6.781 | 0.26207 | 32.656
Storage | 220 | 2 | 3 |  | 33 |  |  | 9 | 297 | 23.75 | 25 | 0.95 | 4.798 | 7.202 | 12 | CDC Airborne LVL | 12.9375 | 3.0795 | 0.23803 | 16.017
File Storage | 221 | 2 | 3 |  | 136 |  |  | 9 | 1224 | 71.25 | 75 | 0.95 | 3.4926 | 8.5074 | 12 | CDC Airborne LVL | 38.8125 | 14.9916 | 0.38626 | 53.8041
Office | 222 | 2 | 3 |  | 169 |  |  | 9 | 1521 | 95 | 100 | 0.95 | 3.7475 | 8.2525 | 12 | CDC Airborne LVL | 51.75 | 18.0711 | 0.3492 | 69.8211
Office | 223 | 2 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 7.9052 | 12 | CDC Airborne LVL | 38.8125 | 11.8819 | 0.30613 | 50.6944
Office | 224 | 2 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 225 | 2 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 226 | 2 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 7.9052 | 12 | CDC Airborne LVL | 38.8125 | 11.8819 | 0.30613 | 50.6944
Office | 227 | 2 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 8.0084 | 12 | CDC Airborne LVL | 38.8125 | 12.3483 | 0.31815 | 51.1608
Reception | 228 | 2 | 3 |  | 772 |  |  | 9 | 6948 | 100 | 400 | 0.25 | 0.86356 | 11.1364 | 12 | CDC Airborne LVL | 207 | 111.3984 | 0.53816 | 318.3984
Restroom Men | 229 | 2 | 3 |  | 172 | 2095 |  | 9 | 1548 | 95 | 100 | 0.95 | 3.6822 | 8.3178 | 12 | CDC Airborne LVL | 51.75 | 18.5376 | 0.35821 | 70.2876
Restroom Womens | 230 | 2 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 8.9404 | 12 | CDC Airborne LVL | 51.75 | 23.9797 | 0.46338 | 75.7297
Hall | 231 | 2 | 4 |  | 600 |  |  | 9 | 5400 | 285 | 300 | 0.95 | 3.1667 | 8.8333 | 12 | CDC Airborne LVL | 155.25 | 68.6738 | 0.44234 | 223.9238
Mechanical Shaft | 232 | 2 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 8.8333 | 12 | CDC Airborne LVL | 103.5 | 45.7825 | 0.44234 | 149.2825
Elevators | 233 | 2 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 7.7778 | 12 | CDC Airborne LVL | 103.5 | 30.2337 | 0.29211 | 133.7337
Stairs | 233 | 2 | 5 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 8.8333 | 12 | CDC Airborne LVL | 103.5 | 45.7825 | 0.44234 | 149.2825
Stairs | 234 | 2 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 8.8333 | 12 | CDC Airborne LVL | 103.5 | 45.7825 | 0.44234 | 149.2825
Office | 300 | 3 | 1 |  | 121 |  |  | 9 | 1089 | 71.25 | 75 | 0.95 | 3.9256 | 8.0744 | 12 | CDC Airborne LVL | 38.8125 | 12.6593 | 0.32617 | 51.4718
Office | 301 | 3 | 1 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 8.0084 | 12 | CDC Airborne LVL | 38.8125 | 12.3483 | 0.31815 | 51.1608
Office | 302 | 3 | 1 |  | 119 |  |  | 9 | 1071 | 19.5 | 75 | 0.26 | 1.0924 | 10.9076 | 12 | CDC Airborne LVL | 38.8125 | 16.8186 | 0.43333 | 55.6311
Office | 303 | 3 | 1 |  | 189 |  |  | 9 | 1701 | 95 | 100 | 0.95 | 3.351 | 8.649 | 12 | CDC Airborne LVL | 51.75 | 21.1809 | 0.40929 | 72.9309
Office | 304 | 3 | 1 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 305 | 3 | 1 |  | 117 |  |  | 9 | 1053 | 71.25 | 75 | 0.95 | 4.0598 | 7.9402 | 12 | CDC Airborne LVL | 38.8125 | 12.0373 | 0.31014 | 50.8498
Office | 306 | 3 | 1 |  | 113 |  |  | 9 | 1017 | 71.25 | 75 | 0.95 | 4.2035 | 7.7965 | 12 | CDC Airborne LVL | 38.8125 | 11.4154 | 0.29412 | 50.2279
Office | 306 | 3 | 1 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 38.8125 | 12.5038 | 0.32216 | 51.3163
Collaboration | 305 | 3 | 1 |  | 290 |  |  | 9 | 2610 | 190 | 200 | 0.95 | 4.3678 | 7.6322 | 12 | CDC Airborne LVL | 103.5 | 28.6789 | 0.27709 | 132.1789
Admin | 305 | 3 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 10.8095 | 12 | CDC Airborne LVL | 103.5 | 39.2175 | 0.37891 | 142.7175
Reception | 306 | 3 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 10.8095 | 12 | CDC Airborne LVL | 103.5 | 39.2175 | 0.37891 | 142.7175
Copy | 307 | 3 | 1 |  | 82 |  |  | 9 | 738 | 47.5 | 50 | 0.95 | 3.8618 | 8.1382 | 12 | CDC Airborne LVL | 25.875 | 8.6468 | 0.33418 | 34.5218
Break Room | 307 | 3 | 1 |  | 72 |  |  | 9 | 648 | 47.5 | 50 | 0.95 | 4.3981 | 7.6019 | 12 | CDC Airborne LVL | 25.875 | 7.092 | 0.27409 | 32.967
IT | 308 | 3 | 1 |  | 73 | 2093 |  | 9 | 657 | 47.5 | 50 | 0.95 | 4.3379 | 7.6621 | 12 | CDC Airborne LVL | 25.875 | 7.2475 | 0.2801 | 33.1225
Common Area | 309 | 3 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 8.1296 | 12 | CDC Airborne LVL | 284.625 | 94.8044 | 0.33309 | 379.4294
Office | 310 | 3 | 2 |  | 131 |  |  | 9 | 1179 | 7.5 | 75 | 0.1 | 0.38168 | 11.6183 | 12 | CDC Airborne LVL | 38.8125 | 19.721 | 0.50811 | 58.5335
Office | 311 | 3 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 10.9899 | 12 | CDC Airborne LVL | 51.75 | 23.4959 | 0.45403 | 75.2459
Office | 312 | 3 | 2 |  | 120 |  |  | 9 | 1080 | 7.5 | 75 | 0.1 | 0.41667 | 11.5833 | 12 | CDC Airborne LVL | 38.8125 | 18.0107 | 0.46404 | 56.8232
Office | 313 | 3 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 38.8125 | 12.5038 | 0.32216 | 51.3163
Office | 313 | 3 | 2 |  | 165 |  |  | 9 | 1485 | 95 | 100 | 0.95 | 3.8384 | 8.1616 | 12 | CDC Airborne LVL | 51.75 | 17.4492 | 0.33718 | 69.1992
Office | 314 | 3 | 2 |  | 131 |  |  | 9 | 1179 | 95 | 100 | 0.95 | 4.8346 | 7.1654 | 12 | CDC Airborne LVL | 51.75 | 12.1626 | 0.23503 | 63.9126
Bull Penns | 315 | 3 | 2 |  | 900 | 2632 |  | 9 | 8100 | 50 | 200 | 0.25 | 0.37037 | 11.6296 | 12 | CDC Airborne LVL | 103.5 | 135.6199 | 1.3103 | 239.1199
Meeting Room | 316 | 3 | 3 |  | 417 |  |  | 9 | 3753 | 285 | 300 | 0.95 | 4.5564 | 7.4436 | 12 | CDC Airborne LVL | 155.25 | 40.2195 | 0.25906 | 195.4695
Research Room | 317 | 3 | 3 |  | 201 |  |  | 9 | 1809 | 118.75 | 125 | 0.95 | 3.9386 | 8.0614 | 12 | CDC Airborne LVL | 64.6875 | 20.9952 | 0.32456 | 85.6827
Office | 318 | 3 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 319 | 3 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 7.9052 | 12 | CDC Airborne LVL | 38.8125 | 11.8819 | 0.30613 | 50.6944
Office | 320 | 3 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 321 | 3 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 322 | 3 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 7.9052 | 12 | CDC Airborne LVL | 38.8125 | 11.8819 | 0.30613 | 50.6944
Office | 323 | 3 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 8.0084 | 12 | CDC Airborne LVL | 38.8125 | 12.3483 | 0.31815 | 51.1608
Hall | 324 | 3 | 3 |  | 600 |  |  | 9 | 5400 | 30 | 300 | 0.1 | 0.33333 | 11.6667 | 12 | CDC Airborne LVL | 155.25 | 90.7012 | 0.58423 | 245.9512
Restroom Men | 325 | 3 | 3 |  | 172 | 2095 |  | 9 | 1548 | 10 | 100 | 0.1 | 0.3876 | 11.6124 | 12 | CDC Airborne LVL | 51.75 | 25.8801 | 0.5001 | 77.6301
Restroom Womens | 326 | 3 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 8.9404 | 12 | CDC Airborne LVL | 51.75 | 23.9797 | 0.46338 | 75.7297
Hall | 327 | 3 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 8.3056 | 12 | CDC Airborne LVL | 181.125 | 64.5706 | 0.3565 | 245.6956
Mechanical Shaft | 328 | 3 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 8.8333 | 12 | CDC Airborne LVL | 103.5 | 45.7825 | 0.44234 | 149.2825
Elevators | 329 | 3 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 7.7778 | 12 | CDC Airborne LVL | 103.5 | 30.2337 | 0.29211 | 133.7337
Stairs | 329 | 3 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 129.375 | 41.6794 | 0.32216 | 171.0544
Stairs | 330 | 3 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 129.375 | 41.6794 | 0.32216 | 171.0544
Office | 300 | 4 | 1 |  | 121 |  |  | 9 | 1089 | 71.25 | 75 | 0.95 | 3.9256 | 8.0744 | 12 | CDC Airborne LVL | 38.8125 | 12.6593 | 0.32617 | 51.4718
Office | 301 | 4 | 1 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 8.0084 | 12 | CDC Airborne LVL | 38.8125 | 12.3483 | 0.31815 | 51.1608
Office | 302 | 4 | 1 |  | 119 |  |  | 9 | 1071 | 19.5 | 75 | 0.26 | 1.0924 | 10.9076 | 12 | CDC Airborne LVL | 38.8125 | 16.8186 | 0.43333 | 55.6311
Office | 303 | 4 | 1 |  | 189 |  |  | 9 | 1701 | 95 | 100 | 0.95 | 3.351 | 8.649 | 12 | CDC Airborne LVL | 51.75 | 21.1809 | 0.40929 | 72.9309
Office | 304 | 4 | 1 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 305 | 4 | 1 |  | 117 |  |  | 9 | 1053 | 71.25 | 75 | 0.95 | 4.0598 | 7.9402 | 12 | CDC Airborne LVL | 38.8125 | 12.0373 | 0.31014 | 50.8498
Office | 306 | 4 | 1 |  | 113 |  |  | 9 | 1017 | 71.25 | 75 | 0.95 | 4.2035 | 7.7965 | 12 | CDC Airborne LVL | 38.8125 | 11.4154 | 0.29412 | 50.2279
Office | 306 | 4 | 1 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 38.8125 | 12.5038 | 0.32216 | 51.3163
Collaboration | 305 | 4 | 1 |  | 290 |  |  | 9 | 2610 | 190 | 200 | 0.95 | 4.3678 | 7.6322 | 12 | CDC Airborne LVL | 103.5 | 28.6789 | 0.27709 | 132.1789
Admin | 305 | 4 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 10.8095 | 12 | CDC Airborne LVL | 103.5 | 39.2175 | 0.37891 | 142.7175
Reception | 306 | 4 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 10.8095 | 12 | CDC Airborne LVL | 103.5 | 39.2175 | 0.37891 | 142.7175
Copy | 307 | 4 | 1 |  | 82 |  |  | 9 | 738 | 47.5 | 50 | 0.95 | 3.8618 | 8.1382 | 12 | CDC Airborne LVL | 25.875 | 8.6468 | 0.33418 | 34.5218
Break Room | 307 | 4 | 1 |  | 72 |  |  | 9 | 648 | 47.5 | 50 | 0.95 | 4.3981 | 7.6019 | 12 | CDC Airborne LVL | 25.875 | 7.092 | 0.27409 | 32.967
IT | 308 | 4 | 1 |  | 73 | 2093 |  | 9 | 657 | 47.5 | 50 | 0.95 | 4.3379 | 7.6621 | 12 | CDC Airborne LVL | 25.875 | 7.2475 | 0.2801 | 33.1225
Common Area | 309 | 4 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 8.1296 | 12 | CDC Airborne LVL | 284.625 | 94.8044 | 0.33309 | 379.4294
Office | 310 | 4 | 2 |  | 131 |  |  | 9 | 1179 | 7.5 | 75 | 0.1 | 0.38168 | 11.6183 | 12 | CDC Airborne LVL | 38.8125 | 19.721 | 0.50811 | 58.5335
Office | 311 | 4 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 10.9899 | 12 | CDC Airborne LVL | 51.75 | 23.4959 | 0.45403 | 75.2459
Office | 312 | 4 | 2 |  | 120 |  |  | 9 | 1080 | 7.5 | 75 | 0.1 | 0.41667 | 11.5833 | 12 | CDC Airborne LVL | 38.8125 | 18.0107 | 0.46404 | 56.8232
Office | 313 | 4 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 38.8125 | 12.5038 | 0.32216 | 51.3163
Office | 313 | 4 | 2 |  | 165 |  |  | 9 | 1485 | 95 | 100 | 0.95 | 3.8384 | 8.1616 | 12 | CDC Airborne LVL | 51.75 | 17.4492 | 0.33718 | 69.1992
Office | 314 | 4 | 2 |  | 131 |  |  | 9 | 1179 | 95 | 100 | 0.95 | 4.8346 | 7.1654 | 12 | CDC Airborne LVL | 51.75 | 12.1626 | 0.23503 | 63.9126
Bull Penns | 315 | 4 | 2 |  | 900 | 2632 |  | 9 | 8100 | 50 | 200 | 0.25 | 0.37037 | 11.6296 | 12 | CDC Airborne LVL | 103.5 | 135.6199 | 1.3103 | 239.1199
Meeting Room | 316 | 4 | 3 |  | 265 |  |  | 9 | 2385 | 285 | 300 | 0.95 | 7.1698 | 4.8302 | 12 | CDC Airborne LVL | 155.25 | 16.5854 | 0.10683 | 171.8354
Research Room | 317 | 4 | 3 |  | 128 |  |  | 9 | 1152 | 118.75 | 125 | 0.95 | 6.1849 | 5.8151 | 12 | CDC Airborne LVL | 64.6875 | 9.6446 | 0.14909 | 74.3321
Office | 318 | 4 | 3 |  | 92 |  |  | 9 | 828 | 71.25 | 75 | 0.95 | 5.163 | 6.837 | 12 | CDC Airborne LVL | 38.8125 | 8.1502 | 0.20999 | 46.9627
Office | 319 | 4 | 3 |  | 105 |  |  | 9 | 945 | 71.25 | 75 | 0.95 | 4.5238 | 7.4762 | 12 | CDC Airborne LVL | 38.8125 | 10.1715 | 0.26207 | 48.984
Office | 320 | 4 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 321 | 4 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 7.9052 | 12 | CDC Airborne LVL | 38.8125 | 11.8819 | 0.30613 | 50.6944
Office | 322 | 4 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 322 | 4 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 322 | 4 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 7.9052 | 12 | CDC Airborne LVL | 38.8125 | 11.8819 | 0.30613 | 50.6944
Office | 323 | 4 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 8.0084 | 12 | CDC Airborne LVL | 38.8125 | 12.3483 | 0.31815 | 51.1608
Hall | 324 | 4 | 3 |  | 628 |  |  | 9 | 5652 | 30 | 300 | 0.1 | 0.31847 | 11.6815 | 12 | CDC Airborne LVL | 155.25 | 95.0549 | 0.61227 | 250.3049
Restroom Men | 325 | 4 | 3 |  | 172 | 2095 |  | 9 | 1548 | 10 | 100 | 0.1 | 0.3876 | 11.6124 | 12 | CDC Airborne LVL | 51.75 | 25.8801 | 0.5001 | 77.6301
Restroom Womens | 326 | 4 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 8.9404 | 12 | CDC Airborne LVL | 51.75 | 23.9797 | 0.46338 | 75.7297
Hall | 327 | 4 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 8.3056 | 12 | CDC Airborne LVL | 181.125 | 64.5706 | 0.3565 | 245.6956
Mechanical Shaft | 328 | 4 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 8.8333 | 12 | CDC Airborne LVL | 103.5 | 45.7825 | 0.44234 | 149.2825
Elevators | 329 | 4 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 7.7778 | 12 | CDC Airborne LVL | 103.5 | 30.2337 | 0.29211 | 133.7337
Stairs | 329 | 4 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 129.375 | 41.6794 | 0.32216 | 171.0544
Stairs | 330 | 4 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 129.375 | 41.6794 | 0.32216 | 171.0544
Office | 300 | 5 | 1 |  | 121 |  |  | 9 | 1089 | 71.25 | 75 | 0.95 | 3.9256 | 8.0744 | 12 | CDC Airborne LVL | 38.8125 | 12.6593 | 0.32617 | 51.4718
Office | 301 | 5 | 1 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 8.0084 | 12 | CDC Airborne LVL | 38.8125 | 12.3483 | 0.31815 | 51.1608
Office | 302 | 5 | 1 |  | 119 |  |  | 9 | 1071 | 19.5 | 75 | 0.26 | 1.0924 | 10.9076 | 12 | CDC Airborne LVL | 38.8125 | 16.8186 | 0.43333 | 55.6311
Office | 303 | 5 | 1 |  | 189 |  |  | 9 | 1701 | 95 | 100 | 0.95 | 3.351 | 8.649 | 12 | CDC Airborne LVL | 51.75 | 21.1809 | 0.40929 | 72.9309
Office | 304 | 5 | 1 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 305 | 5 | 1 |  | 117 |  |  | 9 | 1053 | 71.25 | 75 | 0.95 | 4.0598 | 7.9402 | 12 | CDC Airborne LVL | 38.8125 | 12.0373 | 0.31014 | 50.8498
Office | 306 | 5 | 1 |  | 113 |  |  | 9 | 1017 | 71.25 | 75 | 0.95 | 4.2035 | 7.7965 | 12 | CDC Airborne LVL | 38.8125 | 11.4154 | 0.29412 | 50.2279
Office | 306 | 5 | 1 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 38.8125 | 12.5038 | 0.32216 | 51.3163
Collaboration | 305 | 5 | 1 |  | 290 |  |  | 9 | 2610 | 190 | 200 | 0.95 | 4.3678 | 7.6322 | 12 | CDC Airborne LVL | 103.5 | 28.6789 | 0.27709 | 132.1789
Admin | 305 | 5 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 10.8095 | 12 | CDC Airborne LVL | 103.5 | 39.2175 | 0.37891 | 142.7175
Reception | 306 | 5 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 10.8095 | 12 | CDC Airborne LVL | 103.5 | 39.2175 | 0.37891 | 142.7175
Copy | 307 | 5 | 1 |  | 82 |  |  | 9 | 738 | 47.5 | 50 | 0.95 | 3.8618 | 8.1382 | 12 | CDC Airborne LVL | 25.875 | 8.6468 | 0.33418 | 34.5218
Break Room | 307 | 5 | 1 |  | 72 |  |  | 9 | 648 | 47.5 | 50 | 0.95 | 4.3981 | 7.6019 | 12 | CDC Airborne LVL | 25.875 | 7.092 | 0.27409 | 32.967
Storage | 308 | 5 | 1 |  | 73 | 2093 |  | 9 | 657 | 47.5 | 50 | 0.95 | 4.3379 | 7.6621 | 12 | CDC Airborne LVL | 25.875 | 7.2475 | 0.2801 | 33.1225
Common Area | 309 | 5 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 8.1296 | 12 | CDC Airborne LVL | 284.625 | 94.8044 | 0.33309 | 379.4294
Office | 310 | 5 | 2 |  | 131 |  |  | 9 | 1179 | 7.5 | 75 | 0.1 | 0.38168 | 11.6183 | 12 | CDC Airborne LVL | 38.8125 | 19.721 | 0.50811 | 58.5335
Office | 311 | 5 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 10.9899 | 12 | CDC Airborne LVL | 51.75 | 23.4959 | 0.45403 | 75.2459
Office | 312 | 5 | 2 |  | 120 |  |  | 9 | 1080 | 7.5 | 75 | 0.1 | 0.41667 | 11.5833 | 12 | CDC Airborne LVL | 38.8125 | 18.0107 | 0.46404 | 56.8232
Office | 313 | 5 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 38.8125 | 12.5038 | 0.32216 | 51.3163
Office | 313 | 5 | 2 |  | 165 |  |  | 9 | 1485 | 95 | 100 | 0.95 | 3.8384 | 8.1616 | 12 | CDC Airborne LVL | 51.75 | 17.4492 | 0.33718 | 69.1992
Office | 314 | 5 | 2 |  | 131 |  |  | 9 | 1179 | 95 | 100 | 0.95 | 4.8346 | 7.1654 | 12 | CDC Airborne LVL | 51.75 | 12.1626 | 0.23503 | 63.9126
Bull Penns | 315 | 5 | 2 |  | 900 | 2632 |  | 9 | 8100 | 50 | 200 | 0.25 | 0.37037 | 11.6296 | 12 | CDC Airborne LVL | 103.5 | 135.6199 | 1.3103 | 239.1199
Idea Room | 316 | 5 | 3 |  | 423 |  |  | 9 | 3807 | 285 | 300 | 0.95 | 4.4917 | 7.5083 | 12 | CDC Airborne LVL | 155.25 | 41.1524 | 0.26507 | 196.4024
Office | 317 | 5 | 3 |  | 92 |  |  | 9 | 828 | 71.25 | 75 | 0.95 | 5.163 | 6.837 | 12 | CDC Airborne LVL | 38.8125 | 8.1502 | 0.20999 | 46.9627
Office | 318 | 5 | 3 |  | 105 |  |  | 9 | 945 | 71.25 | 75 | 0.95 | 4.5238 | 7.4762 | 12 | CDC Airborne LVL | 38.8125 | 10.1715 | 0.26207 | 48.984
Office | 319 | 5 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 320 | 5 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 7.9052 | 12 | CDC Airborne LVL | 38.8125 | 11.8819 | 0.30613 | 50.6944
Office | 321 | 5 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 321 | 5 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 321 | 5 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 7.9052 | 12 | CDC Airborne LVL | 38.8125 | 11.8819 | 0.30613 | 50.6944
Office | 322 | 5 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 8.0084 | 12 | CDC Airborne LVL | 38.8125 | 12.3483 | 0.31815 | 51.1608
Hall | 323 | 5 | 3 |  | 598 |  |  | 9 | 5382 | 30 | 300 | 0.1 | 0.33445 | 11.6656 | 12 | CDC Airborne LVL | 155.25 | 90.3902 | 0.58222 | 245.6402
Restroom Men | 324 | 5 | 3 |  | 172 | 2095 |  | 9 | 1548 | 10 | 100 | 0.1 | 0.3876 | 11.6124 | 12 | CDC Airborne LVL | 51.75 | 25.8801 | 0.5001 | 77.6301
Restroom Womens | 325 | 5 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 8.9404 | 12 | CDC Airborne LVL | 51.75 | 23.9797 | 0.46338 | 75.7297
Hall | 326 | 5 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 8.3056 | 12 | CDC Airborne LVL | 181.125 | 64.5706 | 0.3565 | 245.6956
Mechanical Shaft | 327 | 5 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 8.8333 | 12 | CDC Airborne LVL | 103.5 | 45.7825 | 0.44234 | 149.2825
Elevators | 328 | 5 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 7.7778 | 12 | CDC Airborne LVL | 103.5 | 30.2337 | 0.29211 | 133.7337
Stairs | 328 | 5 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 129.375 | 41.6794 | 0.32216 | 171.0544
Stairs | 329 | 5 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 129.375 | 41.6794 | 0.32216 | 171.0544
Office | 300 | 6 | 1 |  | 121 |  |  | 9 | 1089 | 71.25 | 75 | 0.95 | 3.9256 | 8.0744 | 12 | CDC Airborne LVL | 38.8125 | 12.6593 | 0.32617 | 51.4718
Office | 301 | 6 | 1 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 8.0084 | 12 | CDC Airborne LVL | 38.8125 | 12.3483 | 0.31815 | 51.1608
Office | 302 | 6 | 1 |  | 119 |  |  | 9 | 1071 | 19.5 | 75 | 0.26 | 1.0924 | 10.9076 | 12 | CDC Airborne LVL | 38.8125 | 16.8186 | 0.43333 | 55.6311
Office | 303 | 6 | 1 |  | 189 |  |  | 9 | 1701 | 95 | 100 | 0.95 | 3.351 | 8.649 | 12 | CDC Airborne LVL | 51.75 | 21.1809 | 0.40929 | 72.9309
Office | 304 | 6 | 1 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 305 | 6 | 1 |  | 117 |  |  | 9 | 1053 | 71.25 | 75 | 0.95 | 4.0598 | 7.9402 | 12 | CDC Airborne LVL | 38.8125 | 12.0373 | 0.31014 | 50.8498
Office | 306 | 6 | 1 |  | 113 |  |  | 9 | 1017 | 71.25 | 75 | 0.95 | 4.2035 | 7.7965 | 12 | CDC Airborne LVL | 38.8125 | 11.4154 | 0.29412 | 50.2279
Office | 306 | 6 | 1 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 38.8125 | 12.5038 | 0.32216 | 51.3163
Collaboration | 305 | 6 | 1 |  | 290 |  |  | 9 | 2610 | 190 | 200 | 0.95 | 4.3678 | 7.6322 | 12 | CDC Airborne LVL | 103.5 | 28.6789 | 0.27709 | 132.1789
Admin | 305 | 6 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 10.8095 | 12 | CDC Airborne LVL | 103.5 | 39.2175 | 0.37891 | 142.7175
Reception | 306 | 6 | 1 |  | 280 |  |  | 9 | 2520 | 50 | 200 | 0.25 | 1.1905 | 10.8095 | 12 | CDC Airborne LVL | 103.5 | 39.2175 | 0.37891 | 142.7175
Copy | 307 | 6 | 1 |  | 82 |  |  | 9 | 738 | 47.5 | 50 | 0.95 | 3.8618 | 8.1382 | 12 | CDC Airborne LVL | 25.875 | 8.6468 | 0.33418 | 34.5218
Break Room | 307 | 6 | 1 |  | 72 |  |  | 9 | 648 | 47.5 | 50 | 0.95 | 4.3981 | 7.6019 | 12 | CDC Airborne LVL | 25.875 | 7.092 | 0.27409 | 32.967
IT | 308 | 6 | 1 |  | 73 | 2093 |  | 9 | 657 | 47.5 | 50 | 0.95 | 4.3379 | 7.6621 | 12 | CDC Airborne LVL | 25.875 | 7.2475 | 0.2801 | 33.1225
Common Area | 309 | 6 | 2 |  | 900 |  |  | 9 | 8100 | 522.5 | 550 | 0.95 | 3.8704 | 8.1296 | 12 | CDC Airborne LVL | 284.625 | 94.8044 | 0.33309 | 379.4294
Office | 310 | 6 | 2 |  | 131 |  |  | 9 | 1179 | 7.5 | 75 | 0.1 | 0.38168 | 11.6183 | 12 | CDC Airborne LVL | 38.8125 | 19.721 | 0.50811 | 58.5335
Office | 311 | 6 | 2 |  | 165 |  |  | 9 | 1485 | 25 | 100 | 0.25 | 1.0101 | 10.9899 | 12 | CDC Airborne LVL | 51.75 | 23.4959 | 0.45403 | 75.2459
Office | 312 | 6 | 2 |  | 120 |  |  | 9 | 1080 | 7.5 | 75 | 0.1 | 0.41667 | 11.5833 | 12 | CDC Airborne LVL | 38.8125 | 18.0107 | 0.46404 | 56.8232
Office | 313 | 6 | 2 |  | 120 |  |  | 9 | 1080 | 71.25 | 75 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 38.8125 | 12.5038 | 0.32216 | 51.3163
Office | 313 | 6 | 2 |  | 165 |  |  | 9 | 1485 | 95 | 100 | 0.95 | 3.8384 | 8.1616 | 12 | CDC Airborne LVL | 51.75 | 17.4492 | 0.33718 | 69.1992
Office | 314 | 6 | 2 |  | 131 |  |  | 9 | 1179 | 95 | 100 | 0.95 | 4.8346 | 7.1654 | 12 | CDC Airborne LVL | 51.75 | 12.1626 | 0.23503 | 63.9126
Bull Penns | 315 | 6 | 2 |  | 900 | 2632 |  | 9 | 8100 | 50 | 200 | 0.25 | 0.37037 | 11.6296 | 12 | CDC Airborne LVL | 103.5 | 135.6199 | 1.3103 | 239.1199
Conference Room | 316 | 6 | 3 |  | 423 |  |  | 9 | 3807 | 285 | 300 | 0.95 | 4.4917 | 7.5083 | 12 | CDC Airborne LVL | 155.25 | 41.1524 | 0.26507 | 196.4024
Office | 317 | 6 | 3 |  | 92 |  |  | 9 | 828 | 71.25 | 75 | 0.95 | 5.163 | 6.837 | 12 | CDC Airborne LVL | 38.8125 | 8.1502 | 0.20999 | 46.9627
Office | 318 | 6 | 3 |  | 105 |  |  | 9 | 945 | 71.25 | 75 | 0.95 | 4.5238 | 7.4762 | 12 | CDC Airborne LVL | 38.8125 | 10.1715 | 0.26207 | 48.984
Office | 319 | 6 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 320 | 6 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 7.9052 | 12 | CDC Airborne LVL | 38.8125 | 11.8819 | 0.30613 | 50.6944
Office | 321 | 6 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 321 | 6 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 321 | 6 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 7.9052 | 12 | CDC Airborne LVL | 38.8125 | 11.8819 | 0.30613 | 50.6944
Office | 322 | 6 | 3 |  | 119 |  |  | 9 | 1071 | 71.25 | 75 | 0.95 | 3.9916 | 8.0084 | 12 | CDC Airborne LVL | 38.8125 | 12.3483 | 0.31815 | 51.1608
Hall | 323 | 6 | 3 |  | 598 |  |  | 9 | 5382 | 30 | 300 | 0.1 | 0.33445 | 11.6656 | 12 | CDC Airborne LVL | 155.25 | 90.3902 | 0.58222 | 245.6402
Restroom Men | 324 | 6 | 3 |  | 172 | 2095 |  | 9 | 1548 | 10 | 100 | 0.1 | 0.3876 | 11.6124 | 12 | CDC Airborne LVL | 51.75 | 25.8801 | 0.5001 | 77.6301
Restroom Womens | 325 | 6 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 8.9404 | 12 | CDC Airborne LVL | 51.75 | 23.9797 | 0.46338 | 75.7297
Hall | 326 | 6 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 8.3056 | 12 | CDC Airborne LVL | 181.125 | 64.5706 | 0.3565 | 245.6956
Mechanical Shaft | 327 | 6 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 8.8333 | 12 | CDC Airborne LVL | 103.5 | 45.7825 | 0.44234 | 149.2825
Elevators | 328 | 6 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 7.7778 | 12 | CDC Airborne LVL | 103.5 | 30.2337 | 0.29211 | 133.7337
Stairs | 328 | 6 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 129.375 | 41.6794 | 0.32216 | 171.0544
Stairs | 329 | 6 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 129.375 | 41.6794 | 0.32216 | 171.0544
Conference | 300 | 7 | 1 |  | 215 |  |  | 9 | 1935 | 71.25 | 75 | 0.95 | 2.2093 | 9.7907 | 12 | CDC Airborne LVL | 38.8125 | 27.2752 | 0.70274 | 66.0877
Staff | 301 | 7 | 1 |  | 109 |  |  | 9 | 981 | 71.25 | 75 | 0.95 | 4.3578 | 7.6422 | 12 | CDC Airborne LVL | 38.8125 | 10.7934 | 0.27809 | 49.6059
Workroom | 302 | 7 | 1 |  | 242 |  |  | 9 | 2178 | 71.25 | 75 | 0.95 | 1.9628 | 10.0372 | 12 | CDC Airborne LVL | 38.8125 | 31.4733 | 0.81091 | 70.2858
Lab | 303 | 7 | 1 |  | 1220 |  |  | 9 | 10980 | 855 | 900 | 0.95 | 4.6721 | 7.3279 | 12 | CDC Airborne LVL | 465.75 | 115.8384 | 0.24871 | 581.5884
Lab Storage | 304 | 7 | 1 |  | 151 |  |  | 9 | 1359 | 71.25 | 75 | 0.95 | 3.1457 | 8.8543 | 12 | CDC Airborne LVL | 38.8125 | 17.3239 | 0.44635 | 56.1364
Hall | 305 | 7 | 1 |  | 92 |  |  | 9 | 828 | 71.25 | 75 | 0.95 | 5.163 | 6.837 | 12 | CDC Airborne LVL | 38.8125 | 8.1502 | 0.20999 | 46.9627
Break Room | 306 | 7 | 1 |  | 64 | 2093 |  | 9 | 576 | 5 | 50 | 0.1 | 0.52083 | 11.4792 | 12 | CDC Airborne LVL | 25.875 | 9.5193 | 0.3679 | 35.3943
Common Area | 307 | 7 | 2 |  | 1279 |  |  | 9 | 11511 | 760 | 800 | 0.95 | 3.9614 | 8.0386 | 12 | CDC Airborne LVL | 414 | 133.2185 | 0.32178 | 547.2185
IT Office | 308 | 7 | 2 |  | 122 |  |  | 9 | 1098 | 95 | 100 | 0.95 | 5.1913 | 6.8087 | 12 | CDC Airborne LVL | 51.75 | 10.7632 | 0.20798 | 62.5132
Office | 309 | 7 | 2 |  | 122 |  |  | 9 | 1098 | 95 | 100 | 0.95 | 5.1913 | 6.8087 | 12 | CDC Airborne LVL | 51.75 | 10.7632 | 0.20798 | 62.5132
Staff | 310 | 7 | 2 |  | 179 |  |  | 9 | 1611 | 95 | 100 | 0.95 | 3.5382 | 8.4618 | 12 | CDC Airborne LVL | 51.75 | 19.626 | 0.37925 | 71.376
Workroom | 311 | 7 | 2 |  | 250 |  |  | 9 | 2250 | 190 | 200 | 0.95 | 5.0667 | 6.9333 | 12 | CDC Airborne LVL | 103.5 | 22.4593 | 0.217 | 125.9593
File Storage | 311 | 7 | 2 |  | 162 |  |  | 9 | 1458 | 95 | 100 | 0.95 | 3.9095 | 8.0905 | 12 | CDC Airborne LVL | 51.75 | 16.9827 | 0.32817 | 68.7327
Doctoral Student Lounge | 312 | 7 | 2 |  | 274 |  |  | 9 | 2466 | 190 | 200 | 0.95 | 4.6229 | 7.3771 | 12 | CDC Airborne LVL | 103.5 | 26.1911 | 0.25305 | 129.6911
Reception | 313 | 7 | 2 |  | 244 | 2632 |  | 9 | 2196 | 80 | 200 | 0.4 | 2.1858 | 9.8142 | 12 | CDC Airborne LVL | 103.5 | 31.0285 | 0.29979 | 134.5285
Copy | 314 | 7 | 3 |  | 85 |  |  | 9 | 765 | 47.5 | 50 | 0.95 | 3.7255 | 8.2745 | 12 | CDC Airborne LVL | 25.875 | 9.1133 | 0.35221 | 34.9883
Consult | 315 | 7 | 3 |  | 84 |  |  | 9 | 756 | 47.5 | 50 | 0.95 | 3.7698 | 8.2302 | 12 | CDC Airborne LVL | 25.875 | 8.9578 | 0.3462 | 34.8328
Consult | 316 | 7 | 3 |  | 92 |  |  | 9 | 828 | 47.5 | 50 | 0.95 | 3.442 | 8.558 | 12 | CDC Airborne LVL | 25.875 | 10.2017 | 0.39427 | 36.0767
Part Time Faculty | 317 | 7 | 3 |  | 88 |  |  | 9 | 792 | 47.5 | 50 | 0.95 | 3.5985 | 8.4015 | 12 | CDC Airborne LVL | 25.875 | 9.5798 | 0.37023 | 35.4548
Part Time Faculty | 318 | 7 | 3 |  | 88 |  |  | 9 | 792 | 47.5 | 50 | 0.95 | 3.5985 | 8.4015 | 12 | CDC Airborne LVL | 25.875 | 9.5798 | 0.37023 | 35.4548
Office | 319 | 7 | 3 |  | 119 |  |  | 9 | 1071 | 7.5 | 75 | 0.1 | 0.42017 | 11.5798 | 12 | CDC Airborne LVL | 38.8125 | 17.8552 | 0.46004 | 56.6677
Office | 320 | 7 | 3 |  | 116 |  |  | 9 | 1044 | 7.5 | 75 | 0.1 | 0.43103 | 11.569 | 12 | CDC Airborne LVL | 38.8125 | 17.3887 | 0.44802 | 56.2012
Office | 320 | 7 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 320 | 7 | 3 |  | 118 |  |  | 9 | 1062 | 71.25 | 75 | 0.95 | 4.0254 | 7.9746 | 12 | CDC Airborne LVL | 38.8125 | 12.1928 | 0.31415 | 51.0053
Office | 320 | 7 | 3 |  | 116 |  |  | 9 | 1044 | 71.25 | 75 | 0.95 | 4.0948 | 7.9052 | 12 | CDC Airborne LVL | 38.8125 | 11.8819 | 0.30613 | 50.6944
Office | 321 | 7 | 3 |  | 169 |  |  | 9 | 1521 | 71.25 | 75 | 0.95 | 2.8107 | 9.1893 | 12 | CDC Airborne LVL | 38.8125 | 20.1227 | 0.51846 | 58.9352
Admin & Hall | 322 | 7 | 3 |  | 730 |  |  | 9 | 6570 | 380 | 400 | 0.95 | 3.4703 | 8.5297 | 12 | CDC Airborne LVL | 207 | 80.6809 | 0.38976 | 287.6809
Restroom Men | 323 | 7 | 3 |  | 172 | 2095 |  | 9 | 1548 | 95 | 100 | 0.95 | 3.6822 | 8.3178 | 12 | CDC Airborne LVL | 51.75 | 18.5376 | 0.35821 | 70.2876
Restroom Womens | 324 | 7 | 4 |  | 207 |  |  | 9 | 1863 | 95 | 100 | 0.95 | 3.0596 | 8.9404 | 12 | CDC Airborne LVL | 51.75 | 23.9797 | 0.46338 | 75.7297
Hall | 325 | 7 | 4 |  | 600 |  |  | 9 | 5400 | 332.5 | 350 | 0.95 | 3.6944 | 8.3056 | 12 | CDC Airborne LVL | 181.125 | 64.5706 | 0.3565 | 245.6956
Mechanical Shaft | 326 | 7 | 4 |  | 400 |  |  | 9 | 3600 | 190 | 200 | 0.95 | 3.1667 | 8.8333 | 12 | CDC Airborne LVL | 103.5 | 45.7825 | 0.44234 | 149.2825
Elevators | 327 | 7 | 4 |  | 300 | 1507 |  | 9 | 2700 | 190 | 200 | 0.95 | 4.2222 | 7.7778 | 12 | CDC Airborne LVL | 103.5 | 30.2337 | 0.29211 | 133.7337
Stairs | 327 | 7 | 5 |  | 400 |  |  | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 129.375 | 41.6794 | 0.32216 | 171.0544
Stairs | 328 | 7 | 5 |  | 400 | 800 | 9127 | 9 | 3600 | 237.5 | 250 | 0.95 | 3.9583 | 8.0417 | 12 | CDC Airborne LVL | 129.375 | 41.6794 | 0.32216 | 171.0544

## Source
Purpose | This sheet captures the power assumptions used in the model. Once the survey is completed the power levels will be replaced with actual data.
The following table shows the Ventilation Alternatives Cost Analysis.
Mechanical | Units | CFM | sq-ft | ceiling | cu-ft | ACH | Amps | Watts | Watts / CFM | Watts / ACH | Initial Cost | Comments
Dayton Furnace Blower possible | 1 | 1600 | 900 | 12 | 10800 | 8.89 | 6.9 | 828 | 0.52 | 93.15 | 350 | https://www.electricmotorwarehouse.com/content/PDF/1XJX7_spec.pdf
Dayton Furnace Blower Selected | 1 | 2700 | 900 | 12 | 10800 | 15 | 15.3 | 1836 | 0.68 | 122.4 | 700 | https://www.grainger.com/product/DAYTON-1-hpHP-115V-Double-Inlet-Forward-1XJY3
Derived / check | 1 | 2700 | 900 | 12 | 10800 | 15 | 15.3 | 1836 | 0.68 | 122.4 | na | used to check derived design from the selected approach
Baseline Approach | 0.8 | 2160 | 900 | 12 | 10800 | 12 | 12.24 | 1469 | 0.68 | 122.4 | na | Derived design
.
Ceiling Level UV-C | Units | eCFM | sq-ft | ceiling | cu-ft | eACH | Amps | Watts | Watts/eCFM | Watts / eACH | Initial Cost
GC-295 (2x95W bulbs) | 1 | 2200 | 550 | 12 | 6600 | 20 | 1.58 | 190 | 0.09 | 9.5 | na | https://www.lumalier.com/upper-air-disinfection/ceiling-mounted/gc-cieling-mount
GC-295 (2x95W bulbs) Selected | 1.64 | 3608 | 902 | 12 | 10824 | 20 | 2.6 | 312 | 0.09 | 15.58 | na | https://www.lumalier.com/upper-air-disinfection/ceiling-mounted/gc-cieling-mount
Derived / Check | 1.64 | 3608 | 902 | 12 | 10824 | 20 | 2.6 | 312 | 0.09 | 15.58 | na | used to check derived design from the selected approach
Baseline Approach | 0.984 | 2164.8 | 902 | 12 | 10824 | 12 | 1.56 | 187 | 0.09 | 15.58 | na | Derived design
.
Cost Difference | [6 empty] | 8 | 8 | 8 | 8 |  | Mechanical ventilation costs 8 times more than ceiling level UV-C ventilation
Notes: ACH = CFM*60/cu-ft, CFM = ACH*cu-ft/60, Cost Difference = Mechanical Baseline Approach / Ceiling Level UV-C Baseline Approach
A key finding is that the costs associated with mechanical ventilation are not linear. As more air needs to be pushed there is greater air resistance. This is shown by the 2 different mechanical fan models (possible & selected). For this analysis a fan was selected that is close to satisfying the need for a classroom (30 X 30 X 12 ft) and the desired 12 ACH level.
Mechanical ventilation costs 8 times more than ceiling level UV-C ventilation. However when making a final architecture solution it may be better to stay with mechanical ventilation because of other unique conditions including an existing system that is operating at the 12 ACH level.
The following table shows a list of possible products and technologies that can be subjected to a test and evaluation effort and the possible operational costs with each approach.
Product / Technology to be Tested | Products | ACH or eACH | Watts | Watts/ACH or eACH | Comments
Mechanical (old fan design) | Existing | 12 | 1469 | 122 | Data is from analysis.
Mechanical (Inverter 360 Cassette) | Existing | 12 | 240 | 20 | New technology. Displaces in room unit ventilators
Ceiling Level UV-C | Existing | 12 | 187 | 16 | Data is from analysis.
FAR UV-22 | New | 12 |  |  | New technology.