## Sheet1
Sheet Last Modified: | 2021-03-22
School: | Alexander Adaire Elementary School | House Fan Abated/Final Report | [7 empty] | #VALUE! | #VALUE! | Min
Vendor: | Chadwick | Devine | Devine Retest | [6 empty] | #VALUE! | #VALUE! | Max
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | #VALUE! | #VALUE! | Average
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | cu-ft | AUC | Cert Level
8 ft ceiling
- | Auditorium | 2417 | 161 |  | 3234 | 73 | 73 | Air Handling Unit | 25872 | 5.6053 | 2
- | Gym/Cafeteria | 322 | 21 |  | 3432 | 78 | 21 | Air Handling Unit | 27456 | 0.70367 | 0
- | Main Ofiice | 161 | 10 |  | 468 | 10 | 10 | Unit Ventilator | 3744 | 2.5801 | 1
100 | Classroom | 452 | 30 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.5312 | 1
101 | Classroom | 480 | 32 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.75 | 1
102 | Classroom | 509 | 33 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.9766 | 1
103 | Classroom | 409 | 27 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.1953 | 1
104 | Classroom | 514 | 34 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.0156 | 2
105 | Classroom | 523 | 34 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.0859 | 2
106 | Classroom | 125 | 8 | Yes | 782 | 17 | 17 | Unit Ventilator | 6256 | 1.1988 | 1
107 | Classroom | 272 | 18 |  | 380 | 8 | 8 | Unit Ventilator | 3040 | 5.3684 | 2
108 | Faculty Room | 0 | 0 |  | 104 | 2 | 0 | Unit Ventilator | 832 | 0 | 0
109 | Classroom | 485 | 32 |  | 1470 | 33 | 32 | Unit Ventilator | 11760 | 2.4745 | 1
200 | Classroom | 546 | 36 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 4.4901 | 2
201 | Classroom | 607 | 40 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 4.9918 | 2
202 | Classroom | 613 | 40 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 4.9119 | 2
203 | Library | 593 | 39 |  | 1080 | 24 | 24 | Unit Ventilator | 8640 | 4.1181 | 2
204 | Classroom | 480 | 32 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 3.9474 | 1
205 | Classroom | 182 | 12 | Yes | 960 | 21 | 21 | Unit Ventilator | 7680 | 1.4219 | 1
206 | Classroom | 317 | 21 |  | 984 | 22 | 21 | Unit Ventilator | 7872 | 2.4162 | 1
207 | Classroom | 798 | 53 |  | 456 | 10 | 10 | Unit Ventilator | 3648 | 13.125 | 3
208 | Classroom | 577 | 38 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.5078 | 2
209 | Classroom | 458 | 30 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.5781 | 1
210 | Classroom | 519 | 34 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.0547 | 2
211 | Classroom | 534 | 35 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 3.9732 | 1
212 | Classroom | 1568 | 104 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 12.25 | 3
214 | Classroom | 340 | 22 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 2.6562 | 1
216 | Classroom | 617 | 41 |  | 456 | 10 | 10 | Unit Ventilator | 3648 | 10.148 | 3
218 | Classroom | 424 | 28 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 4.0665 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-24 | [7 empty] | 0 | 0 | 0
School: | Ethan Allen Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
[9 empty] | 0 | 0 | 0
B1 | Classroom | 545 | 36 |  | 736 | 16 | 16 | House Fan | 5888 | 5.5537 | 2
B2 | Classroom | 708 | 47 |  | 352 | 8 | 8 | House Fan | 2816 | 15.0852 | 3
B3 | Classroom | 421 | 28 |  | 506 | 11 | 11 | House Fan | 4048 | 6.2401 | 2
B4 | Classroom | 453 | 30 |  | 452 | 10 | 10 | House Fan | 3616 | 7.5166 | 2
- | Auditorium | 2183 | 145 |  | 3432 | 78 | 78 | House Fan | 27456 | 4.7705 | 2
- | Boys Basement Restroom | 130 | 8 |  | 383 | 8 | 8 | AC Bathroom | 3064 | 2.5457 | 1
- | Girls Basement Restroom | 787 | 52 |  | 524 | 11 | 11 | AC Bathroom | 4192 | 11.2643 | 3
101 | Classroom | 600 | 40 |  | 920 | 20 | 20 | House Fan | 7360 | 4.8913 | 2
102 | Classroom | 405 | 27 |  | 690 | 15 | 15 | House Fan | 5520 | 4.4022 | 2
103 | Classroom | 190 | 12 | Yes | 736 | 16 | 16 | House Fan | 5888 | 1.9361 | 1
104 | Classroom | 505 | 33 |  | 690 | 15 | 15 | House Fan | 5520 | 5.4891 | 2
105 | Classroom | 1216 | 81 |  | 690 | 15 | 15 | House Fan | 5520 | 13.2174 | 3
106 | Classroom | 1055 | 70 |  | 690 | 15 | 15 | House Fan | 5520 | 11.4674 | 3
107 | Classroom | 1312 | 87 |  | 690 | 15 | 15 | House Fan | 5520 | 14.2609 | 3
108 | Classroom | 1307 | 87 |  | 736 | 16 | 16 | House Fan | 5888 | 13.3186 | 3
109 | Classroom | 874 | 58 |  | 690 | 15 | 15 | House Fan | 5520 | 9.5 | 2
110 | Classroom | 1349 | 89 |  | 736 | 16 | 16 | House Fan | 5888 | 13.7466 | 3
210 | Classroom | 1375 | 91 |  | 736 | 16 | 16 | House Fan | 5888 | 14.0115 | 3
202 | Classroom | 298 | 19 |  | 690 | 15 | 15 | House Fan | 5520 | 3.2391 | 1
203 | Classroom | 209 | 13 |  | 736 | 16 | 13 | House Fan | 5888 | 2.1298 | 1
204 | Classroom | 373 | 24 |  | 690 | 15 | 15 | House Fan | 5520 | 4.0543 | 2
205 | Classroom | 574 | 38 |  | 690 | 15 | 15 | House Fan | 5520 | 6.2391 | 2
206 | Classroom | 580 | 38 |  | 690 | 15 | 15 | House Fan | 5520 | 6.3043 | 2
207 | Classroom | 919 | 61 |  | 690 | 15 | 15 | House Fan | 5520 | 9.9891 | 2
208 | Classroom | 1175 | 78 |  | 736 | 16 | 16 | House Fan | 5888 | 11.9735 | 3
209 | Classroom | 753 | 50 |  | 690 | 15 | 15 | House Fan | 5520 | 8.1848 | 2
210 | Classroom | 1638 | 109 |  | 736 | 16 | 16 | House Fan | 5888 | 16.6916 | 3
214 | Classroom |  | 0 | Yes | 341 | 7 | 7 | House Fan | 2728 | 0 | 0
301 | Classroom | 880 | 58 |  | 736 | 16 | 16 | House Fan | 5888 | 8.9674 | 2
302 | Classroom | 319 | 21 |  | 690 | 15 | 15 | House Fan | 5520 | 3.4674 | 1
303 | Classroom | 74 | 4 |  | 736 | 16 | 4 | House Fan | 5888 | 0.75408 | 0
304 | Classroom | 141 | 9 |  | 690 | 15 | 9 | House Fan | 5520 | 1.5326 | 1
305 | Classroom | 151 | 10 |  | 690 | 15 | 10 | House Fan | 5520 | 1.6413 | 1
306 | Classroom | 268 | 17 |  | 690 | 15 | 15 | House Fan | 5520 | 2.913 | 1
307 | Classroom | 921 | 61 |  | 690 | 15 | 15 | House Fan | 5520 | 10.0109 | 3
308 | Classroom | 520 | 34 |  | 736 | 16 | 16 | House Fan | 5888 | 5.2989 | 2
309 | Classroom | 121 | 8 |  | 690 | 15 | 8 | House Fan | 5520 | 1.3152 | 1
310 | Classroom | 290 | 19 |  | 736 | 16 | 16 | House Fan | 5888 | 2.9552 | 1
314 | Classroom | 421 | 28 |  | 720 | 16 | 16 | House Fan | 5760 | 4.3854 | 2
- | Main Office |  | 0 | Yes | 309 | 7 | 7 | House Fan | 2472 | 0 | 0
- | Prinicipal Office |  | 0 | Yes | 177 | 4 | 4 | House Fan | 1416 | 0 | 0
- | Nurse Office |  | 0 | Yes | 186 | 4 | 4 | House Fan | 1488 | 0 | 0
- | Conselor Office |  | 0 | Yes | 177 | 4 | 4 | House Fan | 1416 | 0 | 0
- | Pyschologist Office |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | 0 | 0
- | Gym |  | 0 | Yes | 3422 | 77 | 77 | Hydroxyl Unit | 27376 | 0 | 0
Sheet Last Modified: | 2021-03-16 | [7 empty] | 0 | 0 | 0
School: | Dr. Ethel Allen Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Chadwick Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
[9 empty] | 0 | 0 | 0
101-A | Classroom | 528 | 35 |  | 896 | 20 | 20 | Unit Ventilator | 7168 | 4.4196 | 2
101-B | Classroom | 100 | 6 |  | 1036 | 23 | 6 | Unit Ventilator | 8288 | 0.72394 | 0
102-A | Classroom | 70 | 4 |  | 1110 | 25 | 4 | Unit Ventilator | 8880 | 0.47297 | 0
102-B | Classroom | 485 | 32 |  | 1110 | 25 | 25 | Unit Ventilator | 8880 | 3.277 | 1
102-C | Classroom | 0 | 0 |  | 1110 | 25 | 0 | Unit Ventilator | 8880 | 0 | 0
102-D | Classroom |  | 0 |  | 1110 | 25 | 0 | Unit Ventilator | 8880 | 0 | 0
103 | Classroom | 1233 | 82 | Yes | 2277 | 51 | 51 | Unit Ventilator | 18216 | 4.0613 | 2
103-A | Classroom | 76 | 5 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
104 | Classroom | 419 | 27 |  | 1260 | 28 | 27 | Unit Ventilator | 10080 | 2.494 | 1
105 | Classroom | 472 | 31 |  | 1260 | 28 | 28 | Unit Ventilator | 10080 | 2.8095 | 1
106 | Classroom | 152 | 10 |  | 1184 | 26 | 10 | Unit Ventilator | 9472 | 0.96284 | 0
107 | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | 0 | 0
109 | Classroom | 172 | 11 | Yes | 1260 | 28 | 28 | Unit Ventilator | 10080 | 1.0238 | 1
110 | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | 0 | 0
112 | Classroom | 29 | 1 |  | 1056 | 24 | 1 | Unit Ventilator | 8448 | 0.20597 | 0
113 | Classroom | 26 | 1 |  | 1056 | 24 | 1 | Unit Ventilator | 8448 | 0.18466 | 0
114 | Classroom | 380 | 25 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.6989 | 1
200 | Classroom | 511 | 34 |  | 1500 | 34 | 34 | Unit Ventilator | 12000 | 2.555 | 1
200C | Classroom | 0 | 0 | Yes | 784 | 17 | 17 | Unit Ventilator | 6272 | 0 | 0
201B | Classroom |  | 0 |  | 840 | 19 | 0 | Unit Ventilator | 6720 | 0 | 0
202 | Classroom | 367 | 24 |  | 983 | 22 | 22 | Unit Ventilator | 7864 | 2.8001 | 1
202 | Classroom |  | 0 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
203A | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | 0 | 0
203B | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | 0 | 0
203C | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | 0 | 0
203D | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | 0 | 0
204 | Classroom | 525 | 35 |  | 980 | 22 | 22 | Unit Ventilator | 7840 | 4.0179 | 2
206 | Classroom | 194 | 12 |  | 1200 | 27 | 12 | Unit Ventilator | 9600 | 1.2125 | 1
206 | Classroom | 170 | 11 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
207A | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | 0 | 0
207B | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | 0 | 0
208A | Classroom | 108 | 7 |  | 1260 | 28 | 7 | Unit Ventilator | 10080 | 0.64286 | 0
208B | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | 0 | 0
208C | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | 0 | 0
209 | Classroom | 907 | 60 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Add B. Anderson Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Part 2 | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
[9 empty] | 0 | 0 | 0
- | Auditorium | 5840 | 389 |  | 2589 | 58 | 58 | Air Handling Unit | 20712 | 16.9177 | 3
- | Gym | 2392 | 159 |  | 2200 | 50 | 50 | Air Handling Unit | 17600 | 8.1545 | 2
- | Main Office | 84 | 5 | Yes | 451 | 10 | 10 | Unit Ventilator | 3608 | 1.3969 | 1
- | Principal's Office |  | 0 | Yes | 350 | 7 | 7 | Convector | 2800 | 0 | 0
- | Nurse's Office |  | 0 | Yes | 350 | 7 | 7 | Convector | 2800 | 0 | 0
- | Stage | 2534 | 168 |  | 1008 | 22 | 22 | Air Handling Unit | 8064 | 18.8542 | 3
100 | Classroom | 281 | 18 |  | 467 | 10 | 10 | Unit Ventilator | 3736 | 4.5128 | 2
101 | Classroom | 32 | 2 |  | 355 | 8 | 2 | Unit Ventilator | 2840 | 0.67606 | 0
102 | Classroom | 102 | 6 | Yes | 540 | 12 | 12 | Unit Ventilator | 4320 | 1.4167 | 1
103 | Classroom | 40 | 2 | Yes | 628 | 14 | 14 | Unit Ventilator | 5024 | 0.47771 | 0
104 | Classroom | 287 | 19 |  | 395 | 8 | 8 | Unit Ventilator | 3160 | 5.4494 | 2
105 | Classroom | 295 | 19 |  | 521 | 11 | 11 | Unit Ventilator | 4168 | 4.2466 | 2
106 | Classroom | 290 | 19 |  | 446 | 10 | 10 | Unit Ventilator | 3568 | 4.8767 | 2
108 | Classroom | 283 | 18 |  | 405 | 9 | 9 | Unit Ventilator | 3240 | 5.2407 | 2
200 | Classroom | 82 | 5 | Yes | 476 | 10 | 10 | Unit Ventilator | 3808 | 1.292 | 1
201 | Classroom | 128 | 8 | Yes | 627 | 14 | 14 | Unit Ventilator | 5016 | 1.5311 | 1
202 | Classroom | 408 | 27 |  | 576 | 13 | 13 | Unit Ventilator | 4608 | 5.3125 | 2
204 | Classroom | 323 | 21 |  | 683 | 15 | 15 | Unit Ventilator | 5464 | 3.5469 | 1
205 | Classroom | 80 | 5 | Yes | 658 | 14 | 14 | Unit Ventilator | 5264 | 0.91185 | 0
206 | Classroom | 329 | 21 |  | 637 | 14 | 14 | Unit Ventilator | 5096 | 3.8736 | 1
207 | Classroom | 82 | 5 | Yes | 587 | 13 | 13 | Unit Ventilator | 4696 | 1.0477 | 1
208 | Classroom | 129 | 8 | Yes | 720 | 16 | 16 | Unit Ventilator | 5760 | 1.3438 | 1
209 | Classroom | 305 | 20 |  | 629 | 14 | 14 | Unit Ventilator | 5032 | 3.6367 | 1
210 | Classroom | 41 | 2 |  | 241 | 5 | 2 | Unit Ventilator | 1928 | 1.2759 | 1
211 | Classroom | 56 | 3 |  | 385 | 8 | 3 | Unit Ventilator | 3080 | 1.0909 | 1
212 | Classroom | 319 | 21 |  | 603 | 13 | 13 | Unit Ventilator | 4824 | 3.9677 | 1
213 | Classroom | 49 | 3 | Yes | 290 | 6 | 6 | Unit Ventilator | 2320 | 1.2672 | 1
214 | Classroom | 112 | 7 | Yes | 741 | 16 | 16 | Unit Ventilator | 5928 | 1.1336 | 1
300 | Classroom | 35 | 2 | Yes | 947 | 21 | 21 | Unit Ventilator | 7576 | 0.27719 | 0
301 | Classroom | 63 | 4 | Yes | 900 | 20 | 20 | Unit Ventilator | 7200 | 0.525 | 0
302 | Classroom | 87 | 5 | Yes | 588 | 13 | 13 | Unit Ventilator | 4704 | 1.1097 | 1
303 | Classroom | 85 | 5 | Yes | 571 | 12 | 12 | Unit Ventilator | 4568 | 1.1165 | 1
304 | Classroom | 293 | 19 |  | 431 | 9 | 9 | Unit Ventilator | 3448 | 5.0986 | 2
305 | Classroom | 58 | 3 | Yes | 504 | 11 | 11 | Unit Ventilator | 4032 | 0.8631 | 0
306 | Classroom | 286 | 19 |  | 415 | 9 | 9 | Unit Ventilator | 3320 | 5.1687 | 2
307 | Classroom | 97 | 6 | Yes | 501 | 11 | 11 | Unit Ventilator | 4008 | 1.4521 | 1
308 | Classroom | 79 | 5 | Yes | 686 | 15 | 15 | Unit Ventilator | 5488 | 0.8637 | 0
310 | Classroom | 106 | 7 | Yes | 592 | 13 | 13 | Unit Ventilator | 4736 | 1.3429 | 1
311 | Classroom | 53 | 3 | Yes | 441 | 10 | 10 | Unit Ventilator | 3528 | 0.90136 | 0
312 | Classroom | 18 | 1 | Yes | 465 | 10 | 10 | Unit Ventilator | 3720 | 0.29032 | 0
313 | Classroom | 72 | 4 | Yes | 463 | 10 | 10 | Unit Ventilator | 3704 | 1.1663 | 1
314 | Classroom | 61 | 4 | Yes | 533 | 12 | 12 | Unit Ventilator | 4264 | 0.85835 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | Chester A. Arthur Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Retest | Devine 3rd Retest | [6 empty] | 0 | 0 | 0
| Devine 4th Retest | Devine 5th Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
[9 empty] | 0 | 0 | 0
B001 | Classroom | 380 | 25 |  | 551 | 12 | 12 | Unit Ventilator | 4408 | 5.1724 | 2
B002 | Classroom | 0 | 0 |  | 100 | 2 | 0 | N/A | 800 | 0 | 0
100 | Classroom | 309 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.9261 | 1
102 | Classroom | 335 | 22 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.1723 | 1
104 | Classroom | 295 | 19 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.7936 | 1
106 | Classroom | 346 | 23 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.2765 | 1
107A | Teacher's Lounge |  | 0 | Yes | 448 | 10 | 10 | Unit Ventilator | 3584 | 0 | 0
200 | Classroom | 335 | 22 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.1723 | 1
201 | Classroom | 304 | 20 |  | 364 | 8 | 8 | Unit Ventilator | 2912 | 6.2637 | 2
202 | Classroom | 320 | 21 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.0303 | 1
203 | Classroom | 299 | 19 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.5955 | 1
204 | Classroom | 333 | 22 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.1534 | 1
205 | Classroom | 374 | 24 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.2465 | 1
206 | Classroom | 280 | 18 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.6515 | 1
207 | Classroom | 341 | 22 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.9601 | 1
207A | Classroom |  | 0 | Yes | 425 | 9 | 9 | Unit Ventilator | 3400 | 0 | 0
209 | Classroom | 311 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.9451 | 1
300 | Classroom | 293 | 19 |  | 857 | 19 | 19 | Unit Ventilator | 6856 | 2.5642 | 1
301 | Classroom | 273 | 18 |  | 364 | 8 | 8 | Unit Ventilator | 2912 | 5.625 | 2
302 | Classroom | 355 | 23 |  | 857 | 19 | 19 | Unit Ventilator | 6856 | 3.1068 | 1
303 | Classroom | 328 | 21 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.8472 | 1
304 | Classroom | 350 | 23 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.3144 | 1
305 | Classroom | 274 | 18 |  | 900 | 20 | 18 | Unit Ventilator | 7200 | 2.2833 | 1
306 | Classroom | 304 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.8788 | 1
307 | Classroom | 350 | 23 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.0382 | 1
307A | Classroom |  | 0 | Yes | 425 | 9 | 9 | Unit Ventilator | 3400 | 0 | 0
309 | Classroom | 331 | 22 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.1345 | 1
- | Auditorium | 753 | 50 |  | 4335 | 98 | 50 | HV Unit | 34680 | 1.3028 | 1
- | Gym | 2466 | 164 |  | 3055 | 69 | 69 | HV Unit | 24440 | 6.054 | 2
- | IMC | 383 | 25 |  | 1472 | 33 | 25 | Unit Ventilator | 11776 | 1.9514 | 1
- | Resource Room/Storage | 0 | 0 | Yes | 300 | 6 | 6 | Unit Ventilator | 2400 | 0 | 0
- | Main Office | 401 | 26 |  | 1104 | 25 | 25 | Unit Ventilator | 8832 | 2.7242 | 1
- | BE Office | 63 | 4 |  | 240 | 5 | 4 | Unit Ventilator | 1920 | 1.9688 | 1
- | Nurse Office | 0 | 0 | Yes | 276 | 6 | 6 |  | 2208 | 0 | 0
- | Principal's Office |  | 0 | Yes | 240 | 5 | 5 |  | 1920 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | Alexander D. Bache Elementary School | Bache Part 2 | [6 empty] | 0 | 0 | 0
School: | W.E. Martin Building | Martin Part 2 | [6 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
[9 empty] | 0 | 0 | 0
Bache Building | [8 empty] | 0 | 0 | 0
1 | Classroom | 274 | 18 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.6758 | 1
2 | Classroom | 295 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8809 | 1
3 | Classroom | 305 | 20 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.9785 | 1
4 | Classroom | 289 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8223 | 1
5 | Classroom | 330 | 22 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.2227 | 1
6 | Classroom | 273 | 18 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.666 | 1
7 | Classroom | 312 | 20 |  | 528 | 12 | 12 | Unit Ventilator | 4224 | 4.4318 | 2
8 | Classroom | 406 | 27 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.9648 | 1
9 | Classroom | 455 | 30 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 4.4434 | 2
10 | Classroom | 400 | 26 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.9062 | 1
11 | Classroom | 346 | 23 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.3789 | 1
12 | Classroom | 388 | 25 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.7891 | 1
13 | Teacher's Lounge | 339 | 22 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.3105 | 1
14 | Classroom | 288 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8125 | 1
15 | Classroom | 424 | 28 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 4.1406 | 2
16 | Library | 296 | 19 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 3.0833 | 1
17 | Library | 294 | 19 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 3.0625 | 1
18 | Classroom | 338 | 22 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.3008 | 1
19 | Classroom | 114 | 7 | Yes | 768 | 17 | 17 | Unit Ventilator | 6144 | 1.1133 | 1
20 | Classroom | 302 | 20 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 3.1458 | 1
21 | Classroom | 278 | 18 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 2.9616 | 1
22 | Classroom | 328 | 21 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.7273 | 1
23 | Classroom | 360 | 24 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 3.8352 | 1
24 | Classroom | 347 | 23 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.9432 | 1
25 | Classroom | 377 | 25 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.6816 | 1
26 | Classroom | 381 | 25 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 3.9688 | 1
27 | Classroom | 436 | 29 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 4.2578 | 2
- | Cafeteria | 0 | 0 | Yes | 1891 | 42 | 42 | Unit Ventilator | 15128 | 0 | 0
Martin Building | 0 | [7 empty] | 0 | 0 | 0
101 | Classroom | 405 | 27 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 4.2602 | 2
102 | Classroom | 415 | 27 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 4.3654 | 2
103 | Classroom | 308 | 20 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.5 | 1
104 | Classroom | 289 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8223 | 1
105 | Classroom | 355 | 23 |  | 570 | 12 | 12 | Unit Ventilator | 4560 | 4.6711 | 2
106 | Classroom | 339 | 22 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 3.9851 | 1
107A | Classroom | 317 | 21 |  | 900 | 20 | 20 | Unit Ventilator | 7200 | 2.6417 | 1
107B | Classroom | 0 | 0 | Yes | 736 | 16 | 16 | Unit Ventilator | 5888 | 0 | 0
108 | Classroom |  | 0 | Yes | 420 | 9 | 9 |  | 3360 | 0 | 0
110 | Classroom | 518 | 34 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 4.968 | 2
111 | Classroom | 354 | 23 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 3.9805 | 1
112 | Classroom | 328 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5652 | 1
113 | Classroom | 389 | 25 |  | 1092 | 24 | 24 | Unit Ventilator | 8736 | 2.6717 | 1
114 | Classroom | 663 | 44 |  | 1036 | 23 | 23 | Unit Ventilator | 8288 | 4.7997 | 2
115 | Classroom | 422 | 28 |  | 814 | 18 | 18 | Unit Ventilator | 6512 | 3.8882 | 1
117 | Classroom | 536 | 35 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 5.1407 | 2
119 | Classroom | 480 | 32 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 5.0491 | 2
120 | Classroom | 277 | 18 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.0109 | 1
121 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | Unit Ventilator | 5760 | 0 | 0
122 | Classroom | 0 | 0 |  | 744 | 16 | 0 | Unit Ventilator | 5952 | 0 | 0
124 | Classroom | 273 | 18 |  | 759 | 17 | 17 | Unit Ventilator | 6072 | 2.6976 | 1
127 | Classroom |  | 0 | Yes | 690 | 15 | 15 | N/A | 5520 | 0 | 0
128 | Homemaking | 288 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8125 | 1
129 | Classroom | 280 | 18 |  | 500 | 11 | 11 | Unit Ventilator | 4000 | 4.2 | 2
130 | Classroom | 321 | 21 |  | 644 | 14 | 14 | Unit Ventilator | 5152 | 3.7384 | 1
131 | Classroom | 283 | 18 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 3.3268 | 1
133 | Classroom | 337 | 22 |  | 403 | 9 | 9 | Unit Ventilator | 3224 | 6.2717 | 2
134 | Counselor office | 279 | 18 |  | 512 | 11 | 11 | Unit Ventilator | 4096 | 4.0869 | 2
135 | Custodial supply room | 0 | 0 |  | 512 | 11 | 0 | Unit Ventilator | 4096 | 0 | 0
136 | Classroom | 276 | 18 |  | 403 | 9 | 9 | Unit Ventilator | 3224 | 5.1365 | 2
- | Main Office |  | 0 | Yes | 529 | 12 | 12 |  | 4232 | 0 | 0
- | Principals Office |  | 0 | Yes | 221 | 5 | 5 |  | 1768 | 0 | 0
- | Nurses Office |  | 0 | Yes | 308 | 7 | 7 |  | 2464 | 0 | 0
- | Auditorium | 109 | 7 |  | 1702 | 38 | 7 | Unit Ventilator | 13616 | 0.48032 | 0
- | Cafe | 642 | 42 |  | 2451 | 55 | 42 | Unit Ventilator | 19608 | 1.9645 | 1
- | Gym | 364 | 24 |  | 1914 | 43 | 24 | Unit Ventilator | 15312 | 1.4263 | 1
- | Hallway | 157 | 10 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
- | Staff Lounge |  | 0 |  | 525 | 11 | 0 |  | 4200 | 0 | 0
Sheet Last Modified: | 2021-04-28 | [7 empty] | 0 | 0 | 0
School: | Charles Carmine Antonio Baldi Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
[9 empty] | 0 | 0 | 0
22 | Classroom | 903 | 60 |  | 799 | 18 | 18 | Air Handling Unit | 6392 | 8.4762 | 2
23 | Classroom | 552 | 36 |  | 844 | 19 | 19 | Unit Ventilator | 6752 | 4.9052 | 2
24 | Classroom | 670 | 44 |  | 853 | 19 | 19 | Unit Ventilator | 6824 | 5.891 | 2
26B | Classroom | 383 | 25 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 3.5116 | 1
27A | Classroom | 444 | 29 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 4.0709 | 2
28 | Science Lab | 1347 | 89 |  | 1213 | 27 | 27 | Unit Ventilator | 9704 | 8.3285 | 2
29 | Room | 733 | 48 |  | 1280 | 29 | 29 | Unit Ventilator | 10240 | 4.2949 | 2
30 | Science Lab | 1295 | 86 |  | 1213 | 27 | 27 | Unit Ventilator | 9704 | 8.007 | 2
31A | Classroom | 696 | 46 |  | 831 | 18 | 18 | Unit Ventilator | 6648 | 6.2816 | 2
31B | Classroom | 772 | 51 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 7.0782 | 2
32A | Classroom | 1064 | 70 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 9.3662 | 2
32B | Classroom | 395 | 26 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 3.6216 | 1
33A | Classroom | 1195 | 79 |  | 853 | 19 | 19 | Unit Ventilator | 6824 | 10.507 | 3
34a | Classroom | 310 | 20 |  | 844 | 19 | 19 | Unit Ventilator | 6752 | 2.7547 | 1
34b | Classroom | 232 | 15 |  | 799 | 18 | 15 | Unit Ventilator | 6392 | 2.1777 | 1
35 | Science Lab | 433 | 28 |  | 1227 | 27 | 27 | Unit Ventilator | 9816 | 2.6467 | 1
35 | Lounge | 133 | 8 |  | 435 | 9 | 8 | Unit Ventilator | 3480 | 2.2931 | 1
38 | Lounge | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0
39 | Lounge | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0
40 | Seminar Room | 1766 | 117 |  | 411 | 9 | 9 | Unit Ventilator | 3288 | 32.2263 | 4
40 | Classroom | 353 | 23 |  | 411 | 9 | 9 | Unit Ventilator | 3288 | 6.4416 | 2
42 | SGI Room | 205 | 13 |  | 435 | 9 | 9 | Unit Ventilator | 3480 | 3.5345 | 1
43 | SGI Room | 226 | 15 |  | 485 | 11 | 11 | Unit Ventilator | 3880 | 3.4948 | 1
44A | Classroom | 243 | 16 |  | 854 | 19 | 16 | Unit Ventilator | 6832 | 2.1341 | 1
44B | Classroom | 194 | 12 |  | 847 | 19 | 12 | Unit Ventilator | 6776 | 1.7178 | 1
45 | Teachers IPO Room | 0 | 0 |  | 980 | 22 | 0 | Unit Ventilator | 7840 | 0 | 0
46 | Conf. Room | 56 | 3 |  | 980 | 22 | 3 | Unit Ventilator | 7840 | 0.42857 | 0
46 | IPO Materials Room | 76 | 5 |  | 980 | 22 | 5 | Unit Ventilator | 7840 | 0.58163 | 0
47 | Faculty Lounge Room | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0
47a | Classroom | 195 | 13 |  | 841 | 19 | 13 | Air Handling Unit | 6728 | 1.739 | 1
47b | Classroom | 191 | 12 |  | 844 | 19 | 12 | Air Handling Unit | 6752 | 1.6973 | 1
48 | Science Lab | 858 | 57 |  | 1227 | 27 | 27 | Unit Ventilator | 9816 | 5.2445 | 2
B4 | Room |  | 0 |  | 853 | 19 | 0 |  | 6824 | 0 | 0
G5 | Room |  | 0 |  | 853 | 19 | 0 |  | 6824 | 0 | 0
G100 | Classroom |  | 0 | Yes | 565 | 12 | 12 |  | 4520 | 0 | 0
G101 | Classroom |  | 0 |  | 1227 | 27 | 0 |  | 9816 | 0 | 0
G102 | Classroom |  | 0 |  | 799 | 18 | 0 |  | 6392 | 0 | 0
G103 | Classroom |  | 0 |  | 844 | 19 | 0 |  | 6752 | 0 | 0
G104 | Classroom |  | 0 |  | 853 | 19 | 0 |  | 6824 | 0 | 0
G105 | Classroom |  | 0 |  | 853 | 19 | 0 |  | 6824 | 0 | 0
Y3 | Room |  | 0 |  | 818 | 18 | 0 |  | 6544 | 0 | 0
Y5 | Room |  | 0 |  | 852 | 19 | 0 |  | 6816 | 0 | 0
Y104 | Room |  | 0 |  | 818 | 18 | 0 |  | 6544 | 0 | 0
Y105 | Room |  | 0 |  | 852 | 19 | 0 |  | 6816 | 0 | 0
100 | Common Area | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
127 | Art Lab | 0 | 0 | Yes | 2279 | 51 | 51 | Unit Ventilator | 18232 | 0 | 0
128 | Art Lab | 0 | 0 | Yes | 2184 | 49 | 49 | Unit Ventilator | 17472 | 0 | 0
129 | Faculty Dining Room | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0
137 | Classroom | 1440 | 96 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 13.2029 | 3
138 | Classroom | 1218 | 81 |  | 831 | 18 | 18 | Unit Ventilator | 6648 | 10.9928 | 3
139 | Lab | 2473 | 164 |  | 1213 | 27 | 27 | Unit Ventilator | 9704 | 15.2906 | 3
140 | Large Group Room | 1508 | 100 |  | 1280 | 29 | 29 | Unit Ventilator | 10240 | 8.8359 | 2
141 | Science Lab | 1291 | 86 |  | 1213 | 27 | 27 | Unit Ventilator | 9704 | 7.9823 | 2
142 | Classroom | 1844 | 122 |  | 831 | 18 | 18 | Unit Ventilator | 6648 | 16.6426 | 3
143 | Classroom | 1560 | 104 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 14.3032 | 3
144 | Classroom | 391 | 26 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 3.585 | 1
145 | Classroom | 619 | 41 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 5.4489 | 2
146 | Classroom | 265 | 17 |  | 853 | 19 | 17 | Unit Ventilator | 6824 | 2.33 | 1
147 | Classroom | 562 | 37 |  | 853 | 19 | 19 | Unit Ventilator | 6824 | 4.9414 | 2
148 | Classroom | 592 | 39 |  | 844 | 19 | 19 | Unit Ventilator | 6752 | 5.2607 | 2
149 | Classroom | 385 | 25 |  | 799 | 18 | 18 | Unit Ventilator | 6392 | 3.6139 | 1
150 | Science Lab | 611 | 40 |  | 1233 | 28 | 28 | Unit Ventilator | 9864 | 3.7165 | 1
200 | Classroom |  | 0 | Yes | 566 | 12 | 12 |  | 4528 | 0 | 0
200 Office | Office |  | 0 | Yes | 374 | 8 | 8 |  | 2992 | 0 | 0
201 | Classroom |  | 0 | Yes | 1085 | 24 | 24 |  | 8680 | 0 | 0
202 | Classroom |  | 0 | Yes | 893 | 20 | 20 |  | 7144 | 0 | 0
203 | Classroom |  | 0 |  | 1029 | 23 | 0 |  | 8232 | 0 | 0
205 | Classroom |  | 0 | Yes | 1575 | 35 | 35 |  | 12600 | 0 | 0
211 | Classroom |  | 0 | Yes | 930 | 21 | 21 |  | 7440 | 0 | 0
212 | Classroom |  | 0 | Yes | 600 | 13 | 13 |  | 4800 | 0 | 0
213 | Classroom |  | 0 | Yes | 870 | 19 | 19 |  | 6960 | 0 | 0
214 | Classroom |  | 0 | Yes | 1326 | 30 | 30 |  | 10608 | 0 | 0
215 | Classroom |  | 0 |  | 980 | 22 | 0 |  | 7840 | 0 | 0
225 | Library | 0 | 0 |  | 1230 | 27 | 0 | Unit Ventilator | 9840 | 0 | 0
226 | Study Area | 0 | 0 |  | 3510 | 79 | 0 | Unit Ventilator | 28080 | 0 | 0
227 | Computer Lab | 0 | 0 |  | 980 | 22 | 0 | Unit Ventilator | 7840 | 0 | 0
228 | Mech. Room | 0 | 0 |  | 411 | 9 | 0 | Unit Ventilator | 3288 | 0 | 0
155A | Teachers Office | 0 | 0 |  | 948 | 21 | 0 | Unit Ventilator | 7584 | 0 | 0
156A | Teachers Office | 0 | 0 |  | 948 | 21 | 0 | Unit Ventilator | 7584 | 0 | 0
225A | Office | 0 | 0 |  | 948 | 21 | 0 | Unit Ventilator | 7584 | 0 | 0
225B | Office | 0 | 0 |  | 1029 | 23 | 0 | Unit Ventilator | 8232 | 0 | 0
225C | Storage | 0 | 0 |  | 1000 | 22 | 0 | Unit Ventilator | 8000 | 0 | 0
225D | Office | 0 | 0 |  | 299 | 6 | 0 | Unit Ventilator | 2392 | 0 | 0
Computer Lab A | Lab |  | 0 |  | 2640 | 60 | 0 |  | 21120 | 0 | 0
Computer Lab B | Lab |  | 0 |  | 2067 | 46 | 0 |  | 16536 | 0 | 0
Computer Lab C | Lab |  | 0 |  | 2262 | 51 | 0 |  | 18096 | 0 | 0
Main Office | Office |  | 0 | Yes | 875 | 19 | 19 |  | 7000 | 0 | 0
Principal | Office |  | 0 | Yes | 270 | 6 | 6 | Mobile Mini | 2160 | 0 | 0
Vice Principal | Office |  | 0 | Yes | 144 | 3 | 3 | Mobile Mini | 1152 | 0 | 0
Vice Principal | Office |  | 0 | Yes | 144 | 3 | 3 | Mobile Mini | 1152 | 0 | 0
Vice Principal | Office |  | 0 | Yes | 153 | 3 | 3 | Mobile Mini | 1224 | 0 | 0
- | Boys Gym | 0 | 0 |  | 5418 | 123 | 0 | Unit Ventilator | 43344 | 0 | 0
- | Boys Locker Room | 0 | 0 |  | 1824 | 41 | 0 | Unit Ventilator | 14592 | 0 | 0
- | Corridor/Hall | 1107 | 73 |  | 435 | 9 | 9 | Unit Ventilator | 3480 | 19.0862 | 3
Cafeteria 1 | Dining | 0 | 0 |  | 2179 | 49 | 0 | Unit Ventilator | 17432 | 0 | 0
Cafeteria 2 | Dining |  | 0 |  | 2179 | 49 | 0 |  | 17432 | 0 | 0
Cafeteria 3 | Dining |  | 0 |  | 2179 | 49 | 0 |  | 17432 | 0 | 0
Cafeteria 4 | Dining |  | 0 |  | 2179 | 49 | 0 |  | 17432 | 0 | 0
- | Girls Gym | 4087 | 272 | Yes | 5418 | 123 | 123 | Air Handling Unit | 43344 | 5.6575 | 2
- | IPO Bathrooms | 129 | 8 |  | 411 | 9 | 8 | Unit Ventilator | 3288 | 2.354 | 1
- | IPO Office 1 |  | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0
- | IPO Office 1 | 40 | 2 |  | 435 | 9 | 2 | Unit Ventilator | 3480 | 0.68966 | 0
- | IPO Office 3 | 46 | 3 |  | 435 | 9 | 3 | Unit Ventilator | 3480 | 0.7931 | 0
- | Lounge | 104 | 6 |  | 485 | 11 | 6 | Unit Ventilator | 3880 | 1.6082 | 1
Sheet Last Modified: | 2021-03-12 | [7 empty] | 0 | 0 | 0
School: | New Commodore John Barry Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | Exhaust | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Room |  | 0 | Yes | 425 | 9 | 9 | Rooftop Unit | 3400 | 0 | 0
104 | Room | 116 | 7 | Yes | 1008 | 22 | 22 | Rooftop Unit | 8064 | 0.8631 | 0
105 | Room | 133 | 8 | Yes | 1134 | 25 | 25 | Rooftop Unit | 9072 | 0.87963 | 0
106 | Room |  | 0 | Yes | 1140 | 25 | 25 | Rooftop Unit | 9120 | 0 | 0
107 | Room | 308 | 20 |  | 1118 | 25 | 20 | Rooftop Unit | 8944 | 2.0662 | 1
108 | Room | 303 | 20 |  | 1140 | 25 | 20 | Rooftop Unit | 9120 | 1.9934 | 1
109 | Room | 1254 | 83 |  | 2100 | 47 | 47 | Rooftop Unit | 16800 | 4.4786 | 2
116 | Room | 125 | 8 |  |  | 0 | 0 | Rooftop Unit | 0 | 0 | 0
202 | Room | 147 | 9 | Yes | 551 | 12 | 12 | Rooftop Unit | 4408 | 2.0009 | 1
203 | Room | 148 | 9 | Yes | 551 | 12 | 12 | Rooftop Unit | 4408 | 2.0145 | 1
204 | Room | 139 | 9 | Yes | 418 | 9 | 9 | Rooftop Unit | 3344 | 2.494 | 1
205 | Room | 202 | 13 | Yes | 551 | 12 | 12 | Rooftop Unit | 4408 | 2.7495 | 1
206 | Room | 145 | 9 | Yes | 728 | 16 | 16 | Rooftop Unit | 5824 | 1.4938 | 1
207 | Room | 185 | 12 | Yes | 728 | 16 | 16 | Rooftop Unit | 5824 | 1.9059 | 1
208 | Room | 139 | 9 | Yes | 728 | 16 | 16 | Rooftop Unit | 5824 | 1.432 | 1
209 | Room | 313 | 20 |  | 728 | 16 | 16 | Rooftop Unit | 5824 | 3.2246 | 1
210 | Room | 272 | 18 |  | 630 | 14 | 14 | Rooftop Unit | 5040 | 3.2381 | 1
211 | Room | 192 | 12 |  | 756 | 17 | 12 | Rooftop Unit | 6048 | 1.9048 | 1
212 | Room | 154 | 10 | Yes | 900 | 20 | 20 | Rooftop Unit | 7200 | 1.2833 | 1
213 | Room | 130 | 8 | Yes | 900 | 20 | 20 | Rooftop Unit | 7200 | 1.0833 | 1
214 | Room | 268 | 17 |  | 812 | 18 | 17 | Rooftop Unit | 6496 | 2.4754 | 1
215 | Room | 219 | 14 | Yes | 756 | 17 | 17 | Rooftop Unit | 6048 | 2.1726 | 1
216 | Room | 223 | 14 | Yes | 756 | 17 | 17 | Rooftop Unit | 6048 | 2.2123 | 1
301 | Room | 210 | 14 |  | 630 | 14 | 14 | Rooftop Unit | 5040 | 2.5 | 1
302A | Room |  | 0 |  | 104 | 2 | 0 | Rooftop Unit | 832 | 0 | 0
302B | Room |  | 0 |  | 117 | 2 | 0 | Rooftop Unit | 936 | 0 | 0
302C | Room |  | 0 |  | 104 | 2 | 0 | Rooftop Unit | 832 | 0 | 0
303 | Room | 99 | 6 |  | 651 | 14 | 6 | Rooftop Unit | 5208 | 1.1406 | 1
304 | Room |  | 0 |  | 110 | 2 | 0 | Rooftop Unit | 880 | 0 | 0
305 | Room | 237 | 15 |  | 756 | 17 | 15 | Rooftop Unit | 6048 | 2.3512 | 1
306 | Room | 156 | 10 |  | 756 | 17 | 10 | Rooftop Unit | 6048 | 1.5476 | 1
307 | Room | 265 | 17 |  | 784 | 17 | 17 | Rooftop Unit | 6272 | 2.5351 | 1
308 | Room | 192 | 12 | Yes | 864 | 19 | 19 | Rooftop Unit | 6912 | 1.6667 | 1
309 | Room | 208 | 13 |  | 810 | 18 | 13 | Rooftop Unit | 6480 | 1.9259 | 1
310 | Room | 296 | 19 |  | 810 | 18 | 18 | Rooftop Unit | 6480 | 2.7407 | 1
311 | Room | 249 | 16 |  | 812 | 18 | 16 | Rooftop Unit | 6496 | 2.2999 | 1
312 | Room | 210 | 14 |  | 840 | 19 | 14 | Rooftop Unit | 6720 | 1.875 | 1
313 | Room | 96 | 6 |  | 810 | 18 | 6 | Rooftop Unit | 6480 | 0.88889 | 0
314 | Room | 219 | 14 |  | 810 | 18 | 14 | Rooftop Unit | 6480 | 2.0278 | 1
315 | Room | 105 | 7 |  | 812 | 18 | 7 | Rooftop Unit | 6496 | 0.96983 | 0
316 | Room | 143 | 9 |  | 812 | 18 | 9 | Rooftop Unit | 6496 | 1.3208 | 1
320 | Room | 212 | 14 |  | 620 | 14 | 14 | Rooftop Unit | 4960 | 2.5645 | 1
323 | Room | 230 | 15 |  | 620 | 14 | 14 | Rooftop Unit | 4960 | 2.7823 | 1
401 | Room | 215 | 14 | Yes | 1260 | 28 | 28 | Rooftop Unit | 10080 | 1.2798 | 1
403A | Room |  | 0 |  | 240 | 5 | 0 | Rooftop Unit | 1920 | 0 | 0
403B | Room |  | 0 |  | 210 | 4 | 0 | Rooftop Unit | 1680 | 0 | 0
403C | Room |  | 0 |  | 240 | 5 | 0 | Rooftop Unit | 1920 | 0 | 0
404 | Room |  | 0 | Yes | 1024 | 23 | 23 | Rooftop Unit | 8192 | 0 | 0
405 | Room | 382 | 25 |  | 1476 | 33 | 25 | Rooftop Unit | 11808 | 1.9411 | 1
406 | Room |  | 0 |  | 1462 | 33 | 0 | Rooftop Unit | 11696 | 0 | 0
407 | Room |  | 0 |  | 1054 | 23 | 0 | Rooftop Unit | 8432 | 0 | 0
408 | Room | 561 | 37 |  | 1280 | 29 | 29 | Rooftop Unit | 10240 | 3.2871 | 1
409 | Room | 213 | 14 |  | 1160 | 26 | 14 | Rooftop Unit | 9280 | 1.3772 | 1
- | Café | 593 | 39 |  | 4800 | 109 | 39 | Rooftop Unit | 38400 | 0.92656 | 0
- | Gym |  | 0 | Yes | 6240 | 141 | 141 | Rooftop Unit | 49920 | 0 | 0
- | Library |  | 0 | Yes | 1961 | 44 | 44 | Rooftop Unit | 15688 | 0 | 0
- | Main Office |  | 0 |  | 924 | 21 | 0 | Rooftop Unit | 7392 | 0 | 0
- | Nurse's Office |  | 0 |  | 143 | 3 | 0 | Rooftop Unit | 1144 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-16 | [7 empty] | 0 | 0 | 0
School: | Clara Barton | [7 empty] | 0 | 0 | 0
Vendor: | [8 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B7 | Classroom | 0 | 0 | Yes | 601 | 13 | 13 | House Fan | 4808 | 0 | 0
B8 | Classroom | 0 | 0 | Yes | 848 | 19 | 19 | House Fan | 6784 | 0 | 0
B10 | Classroom | 0 | 0 |  | 686 | 15 | 0 | House Fan | 5488 | 0 | 0
B11 | Classroom | 0 | 0 |  | 806 | 18 | 0 | House Fan | 6448 | 0 | 0
100 | Classroom | 0 | 0 | Yes | 742 | 16 | 16 | House Fan | 5936 | 0 | 0
101 | Classroom | 0 | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | 0 | 0
102 | Office | 0 | 0 | Yes | 452 | 10 | 10 | House Fan | 3616 | 0 | 0
102 A | Classroom | 0 | 0 |  | 70 | 1 | 0 | House Fan | 560 | 0 | 0
102 B | Office | 0 | 0 |  | 122 | 2 | 0 | House Fan | 976 | 0 | 0
103 C | Office | 0 | 0 |  | 90 | 2 | 0 | House Fan | 720 | 0 | 0
103 | Classroom | 0 | 0 | Yes | 627 | 14 | 14 | House Fan | 5016 | 0 | 0
104 | Library | 0 | 0 | Yes | 645 | 14 | 14 | House Fan | 5160 | 0 | 0
105 | Library | 0 | 0 | Yes | 658 | 14 | 14 | House Fan | 5264 | 0 | 0
106 | Library | 0 | 0 | Yes | 653 | 14 | 14 | House Fan | 5224 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 632 | 14 | 14 | House Fan | 5056 | 0 | 0
108 | Classroom | 0 | 0 | Yes | 640 | 14 | 14 | House Fan | 5120 | 0 | 0
109 | Classroom | 0 | 0 | Yes | 694 | 15 | 15 | House Fan | 5552 | 0 | 0
110 | Classroom | 0 | 0 | Yes | 683 | 15 | 15 | House Fan | 5464 | 0 | 0
111 | Classroom | 0 | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | 0 | 0
112 | Nurse's Office | 0 | 0 | Yes | 118 | 2 | 2 | House Fan | 944 | 0 | 0
- | Main Office | 0 | 0 | Yes | 297 | 6 | 6 | House Fan | 2376 | 0 | 0
- | Principal's Office | 0 | 0 | Yes | 159 | 3 | 3 | House Fan | 1272 | 0 | 0
200 | Classroom | 0 | 0 | Yes | 663 | 15 | 15 | House Fan | 5304 | 0 | 0
200 A | Office | 0 | 0 | Yes | 226 | 5 | 5 | House Fan | 1808 | 0 | 0
200 B | Classroom | 0 | 0 | Yes | 158 | 3 | 3 | House Fan | 1264 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 635 | 14 | 14 | House Fan | 5080 | 0 | 0
202 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0
203 | Classroom | 0 | 0 | Yes | 645 | 14 | 14 | House Fan | 5160 | 0 | 0
204 | Classroom | 0 | 0 | Yes | 624 | 14 | 14 | House Fan | 4992 | 0 | 0
205 | Classroom | 0 | 0 | Yes | 624 | 14 | 14 | House Fan | 4992 | 0 | 0
206 | Classroom | 0 | 0 | Yes | 653 | 14 | 14 | House Fan | 5224 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 664 | 15 | 15 | House Fan | 5312 | 0 | 0
208 | Classroom | 0 | 0 | Yes | 638 | 14 | 14 | House Fan | 5104 | 0 | 0
209 | Classroom | 0 | 0 | Yes | 662 | 15 | 15 | House Fan | 5296 | 0 | 0
210 | Classroom | 0 | 0 | Yes | 694 | 15 | 15 | House Fan | 5552 | 0 | 0
211 | Classroom | 0 | 0 | Yes | 616 | 14 | 14 | House Fan | 4928 | 0 | 0
211 A | Office | 0 | 0 |  | 115 | 2 | 0 | House Fan | 920 | 0 | 0
- | Teacher Lounge | 0 | 0 | Yes | 340 | 7 | 7 | House Fan | 2720 | 0 | 0
215 | Classroom |  | 0 | Yes | 345 | 7 | 7 | house Fan | 2760 | 0 | 0
300 | Classroom | 0 | 0 | Yes | 640 | 14 | 14 | House Fan | 5120 | 0 | 0
300A | Office |  | 0 | Yes | 264 | 6 | 6 | House Fan | 2112 | 0 | 0
301 | Classroom | 0 | 0 | Yes | 668 | 15 | 15 | House Fan | 5344 | 0 | 0
301 A | Office | 0 | 0 |  | 203 | 4 | 0 | House Fan | 1624 | 0 | 0
302 | Classroom | 0 | 0 | Yes | 639 | 14 | 14 | House Fan | 5112 | 0 | 0
303 | Classroom | 0 | 0 | Yes | 692 | 15 | 15 | House Fan | 5536 | 0 | 0
304 | Classroom | 0 | 0 | Yes | 627 | 14 | 14 | House Fan | 5016 | 0 | 0
305 | Classroom | 0 | 0 | Yes | 655 | 14 | 14 | House Fan | 5240 | 0 | 0
306 | Classroom | 0 | 0 | Yes | 664 | 15 | 15 | House Fan | 5312 | 0 | 0
307 | Classroom | 0 | 0 | Yes | 642 | 14 | 14 | House Fan | 5136 | 0 | 0
308 | Classroom | 0 | 0 | Yes | 663 | 15 | 15 | House Fan | 5304 | 0 | 0
309 | Classroom | 0 | 0 | Yes | 605 | 13 | 13 | House Fan | 4840 | 0 | 0
310 | Classroom | 0 | 0 | Yes | 673 | 15 | 15 | House Fan | 5384 | 0 | 0
311 | Classroom | 0 | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
312 | Classroom | 0 | 0 |  | 634 | 14 | 0 | House Fan | 5072 | 0 | 0
312 A | Office | 0 | 0 |  | 112 | 2 | 0 | House Fan | 896 | 0 | 0
- | Counselor Office |  | 0 | Yes | 152 | 3 | 3 | House Fan | 1216 | 0 | 0
- | Gym | 0 | 0 | Yes | 3436 | 78 | 78 | N/A | 27488 | 0 | 0
- | Kitchen | 0 | 0 | Yes | 1140 | 25 | 25 | House Fan | 9120 | 0 | 0
- | Cafeteria | 0 | 0 | Yes | 1478 | 33 | 33 | House Fan | 11824 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | John Bartram High School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Part 2 | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 590 | 39 |  | 1196 | 27 | 27 | Unit Ventilator | 9568 | 3.6998 | 1
102 | Classroom | 359 | 23 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 3.1639 | 1
103 | Classroom | 759 | 50 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 6.875 | 2
104 | Classroom | 646 | 43 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.2663 | 2
105 | Classroom | 582 | 38 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 5.1293 | 2
106 | Classroom | 696 | 46 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 5.2781 | 2
107 | Classroom | 980 | 65 |  | 946 | 21 | 21 | Unit Ventilator | 7568 | 7.7696 | 2
108 | Classroom | 575 | 38 |  | 1012 | 23 | 23 | Unit Ventilator | 8096 | 4.2614 | 2
110 | Office | 0 | 0 |  | 238 | 5 | 0 | Unit Ventilator | 1904 | 0 | 0
111 | Classroom | 418 | 27 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 3.8944 | 1
112 | Room | 416 | 27 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 3.3913 | 1
113 | Classroom | 416 | 27 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.5217 | 2
115 | Classroom | 343 | 22 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.7283 | 1
116 | Classroom | 467 | 31 |  | 1357 | 30 | 30 | Unit Ventilator | 10856 | 2.5811 | 1
117 | Classroom | 352 | 23 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.8261 | 1
118 | Classroom | 325 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5326 | 1
119 | Classroom | 346 | 23 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.7609 | 1
120 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Unit Ventilator | 5520 | 0 | 0
121 | Office | 0 | 0 | Yes | 227 | 5 | 5 | Unit Ventilator | 1816 | 0 | 0
123 | Room | 498 | 33 |  | 1242 | 28 | 28 | Unit Ventilator | 9936 | 3.0072 | 1
124 | Office | 0 | 0 | Yes | 309 | 7 | 7 | Unit Ventilator | 2472 | 0 | 0
124A | Office | 0 | 0 | Yes | 218 | 4 | 4 | Unit Ventilator | 1744 | 0 | 0
125 | Room | 356 | 23 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.8696 | 1
126 | Room | 339 | 22 |  | 276 | 6 | 6 | Unit Ventilator | 2208 | 9.212 | 2
127 | Room | 349 | 23 |  | 644 | 14 | 14 | Unit Ventilator | 5152 | 4.0644 | 2
127a | Room | 331 | 22 |  | 345 | 7 | 7 | Unit Ventilator | 2760 | 7.1957 | 2
128 | Office | 0 | 0 |  | 230 | 5 | 0 | Unit Ventilator | 1840 | 0 | 0
130 | Room | 288 | 19 |  | 375 | 8 | 8 | Unit Ventilator | 3000 | 5.76 | 2
130A | Office | 0 | 0 |  | 236 | 5 | 0 | Unit Ventilator | 1888 | 0 | 0
131 | Office | 0 | 0 | Yes | 237 | 5 | 5 | Unit Ventilator | 1896 | 0 | 0
133 | Office | 0 | 0 | Yes | 333 | 7 | 7 | Unit Ventilator | 2664 | 0 | 0
134 | Main Office | 593 | 39 |  | 1656 | 37 | 37 | Unit Ventilator | 13248 | 2.6857 | 1
201 | Classroom | 617 | 41 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 4.679 | 2
202 | Classroom | 282 | 18 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 2.6273 | 1
203 | Classroom | 632 | 42 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 4.7927 | 2
204 | Classroom | 309 | 20 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.3587 | 1
205 | Classroom | 516 | 34 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 3.913 | 1
206 | Classroom | 324 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5217 | 1
207 | Classroom | 363 | 24 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 2.7528 | 1
208 | Classroom | 291 | 19 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.163 | 1
209 | Classroom | 0 | 0 | Yes | 309 | 7 | 7 | Unit Ventilator | 2472 | 0 | 0
210 | Classroom | 297 | 19 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.2283 | 1
211 | Room | 0 | 0 | Yes | 321 | 7 | 7 | Unit Ventilator | 2568 | 0 | 0
211A | copy Room | 0 | 0 |  | 227 | 5 | 0 | Unit Ventilator | 1816 | 0 | 0
214 | Classroom | 370 | 24 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.0217 | 2
215 | Classroom | 337 | 22 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.663 | 1
216 | Classroom | 327 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5543 | 1
217 | Classroom | 282 | 18 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.0652 | 1
218 | Classroom | 563 | 37 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 6.1196 | 2
219 | Office | 0 | 0 | Yes | 272 | 6 | 6 | Unit Ventilator | 2176 | 0 | 0
220A | Office | 0 | 0 | Yes | 169 | 3 | 3 | Unit Ventilator | 1352 | 0 | 0
221 | Classroom | 97 | 6 | Yes | 851 | 19 | 19 | Unit Ventilator | 6808 | 0.85488 | 0
222 | Classroom | 320 | 21 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 2.8202 | 1
223 | Classroom | 329 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5761 | 1
224 | Classroom | 302 | 20 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.2826 | 1
225 | Classroom | 437 | 29 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.75 | 2
226 | Classroom | 315 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.4239 | 1
227 | Classroom | 299 | 19 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.25 | 1
228 | Classroom | 302 | 20 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.2826 | 1
229 | Classroom | 407 | 27 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.4239 | 2
230 | Classroom | 290 | 19 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.1522 | 1
231 | Classroom | 331 | 22 |  | 322 | 7 | 7 | Unit Ventilator | 2576 | 7.7096 | 2
232 | Classroom | 0 | 0 | Yes | 690 | 15 | 15 | Unit Ventilator | 5520 | 0 | 0
234 | Office | 0 | 0 | Yes | 298 | 6 | 6 | Unit Ventilator | 2384 | 0 | 0
236 | Office | 0 | 0 | Yes | 299 | 6 | 6 | Unit Ventilator | 2392 | 0 | 0
236A | Copy room | 0 | 0 |  | 203 | 4 | 0 | Unit Ventilator | 1624 | 0 | 0
301 | Classroom |  | 0 |  | 816 | 18 | 0 | Air Handling Unit | 6528 | 0 | 0
302 | Classroom |  | 0 |  | 816 | 18 | 0 | Air Handling Unit | 6528 | 0 | 0
305 | Classroom |  | 0 |  | 1000 | 22 | 0 | Air Handling Unit | 8000 | 0 | 0
306 | Classroom |  | 0 |  | 136 | 3 | 0 | Air Handling Unit | 1088 | 0 | 0
307 | Classroom |  | 0 |  | 696 | 15 | 0 | Air Handling Unit | 5568 | 0 | 0
309 | Classroom |  | 0 |  | 225 | 5 | 0 | Air Handling Unit | 1800 | 0 | 0
313 | Faculty | 309 | 20 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.7855 | 1
320 | Classroom | 618 | 41 |  | 1080 | 24 | 24 | Unit Ventilator | 8640 | 4.2917 | 2
321 | Classroom | 574 | 38 |  | 1100 | 25 | 25 | Unit Ventilator | 8800 | 3.9136 | 1
324 | Classroom | 553 | 36 |  | 945 | 21 | 21 | Unit Ventilator | 7560 | 4.3889 | 2
325 | Classroom | 394 | 26 |  | 1080 | 24 | 24 | Unit Ventilator | 8640 | 2.7361 | 1
328 | Room | 0 | 0 | Yes | 169 | 3 | 3 | Unit Ventilator | 1352 | 0 | 0
331 | Classroom | 351 | 23 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 3.2702 | 1
332 | Classroom | 361 | 24 |  | 1081 | 24 | 24 | Unit Ventilator | 8648 | 2.5046 | 1
333 | Classroom | 321 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.4891 | 1
334 | Classroom | 284 | 18 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.087 | 1
335 | Classroom | 286 | 19 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 3.2159 | 1
336 | Classroom | 295 | 19 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.2065 | 1
337 | Classroom | 86 | 5 | Yes | 690 | 15 | 15 | Unit Ventilator | 5520 | 0.93478 | 0
338 | Classroom | 280 | 18 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 3.1484 | 1
339 | Classroom | 366 | 24 |  | 506 | 11 | 11 | Unit Ventilator | 4048 | 5.4249 | 2
340 | Classroom | 274 | 18 |  | 484 | 11 | 11 | Unit Ventilator | 3872 | 4.2459 | 2
341 | Classroom | 356 | 23 |  | 484 | 11 | 11 | Unit Ventilator | 3872 | 5.5165 | 2
342 | Classroom | 289 | 19 |  | 529 | 12 | 12 | Unit Ventilator | 4232 | 4.0974 | 2
344 | Room | 0 | 0 | Yes | 233 | 5 | 5 | Unit Ventilator | 1864 | 0 | 0
346 | Classroom | 291 | 19 |  | 675 | 15 | 15 | Unit Ventilator | 5400 | 3.2333 | 1
B12 | Room | 0 | 0 |  | 383 | 8 | 0 | Unit Ventilator | 3064 | 0 | 0
B13 | BE Office | 0 | 0 |  | 238 | 5 | 0 | Unit Ventilator | 1904 | 0 | 0
B17 | Room | 0 | 0 |  | 209 | 4 | 0 | Unit Ventilator | 1672 | 0 | 0
Bc | Room | 0 | 0 | Yes | 244 | 5 | 5 | Unit Ventilator | 1952 | 0 | 0
C1 | Classroom | 398 | 26 |  | 1000 | 22 | 22 | Unit Ventilator | 8000 | 2.985 | 1
C2 | Classroom | 0 | 0 |  | 1000 | 22 | 0 | Unit Ventilator | 8000 | 0 | 0
C3 | Classroom | 1212 | 80 |  | 1000 | 22 | 22 | Unit Ventilator | 8000 | 9.09 | 2
C4 | Classroom | 0 | 0 |  | 1000 | 22 | 0 | Unit Ventilator | 8000 | 0 | 0
C5 | Classroom | 0 | 0 |  | 1000 | 22 | 0 | Unit Ventilator | 8000 | 0 | 0
C7 | Classroom | 881 | 58 |  | 968 | 22 | 22 | Unit Ventilator | 7744 | 6.8259 | 2
C7A | Classroom | 0 | 0 |  | 909 | 20 | 0 | Unit Ventilator | 7272 | 0 | 0
- | School police | 0 | 0 | Yes | 192 | 4 | 4 | Unit Ventilator | 1536 | 0 | 0
- | 3rd Floor C Wing | 0 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Auditorium | 0 | 0 |  | 11625 | 264 | 0 | Air Handling Unit | 93000 | 0 | 0
- | Boys Gym | 5931 | 395 |  | 5280 | 120 | 120 | Air Handling Unit | 42240 | 8.4247 | 2
- | Library | 866 | 57 |  | 4526 | 102 | 57 | Unit Ventilator | 36208 | 1.435 | 1
- | Corridor | 0 | 0 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
- | Girls Gym | 6806 | 453 |  | 5280 | 120 | 120 | Air Handling Unit | 42240 | 9.6676 | 2
- | Nurse Area | 255 | 17 |  | 936 | 21 | 17 | Unit Ventilator | 7488 | 2.0433 | 1
- | Cafeteria | 0 | 0 | Yes | 6262 | 142 | 142 | Unit Ventilator | 50096 | 0 | 0
Sheet Last Modified: | 2021-04-05 | [7 empty] | 0 | 0 | 0
School: | Mary McLeod Bethune School | [7 empty] | 0 | 0 | 0
Vendor: | Capital | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Classroom | 300 | 20 |  | 1350 | 30 | 20 | Unit Ventilator | 10800 | 1.6667 | 1
2 | Classroom | 278 | 18 |  | 1350 | 30 | 18 | Unit Ventilator | 10800 | 1.5444 | 1
3 | Classroom | 395 | 26 |  | 1350 | 30 | 26 | Unit Ventilator | 10800 | 2.1944 | 1
4 | Classroom | 425 | 28 |  | 1296 | 29 | 28 | Unit Ventilator | 10368 | 2.4595 | 1
5 | Classroom | 314 | 20 |  | 1296 | 29 | 20 | Unit Ventilator | 10368 | 1.8171 | 1
100 | Classroom | 614 | 40 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.7969 | 2
101 | Classroom | 597 | 39 |  | 1024 | 23 | 23 | Unit Ventilator | 8192 | 4.3726 | 2
101A | Instructional Storage | 0 | 0 |  |  | 0 | 0 | HUV | 0 | 0 | 0
102 | Classroom | 560 | 37 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 6.087 | 2
103 | Classroom | 555 | 37 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 6.0326 | 2
104 | Classroom | 575 | 38 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 6.25 | 2
105 | Classroom | 618 | 41 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 6.7174 | 2
106 | Class Area | 163 | 10 |  | 625 | 14 | 10 | Unit Ventilator | 5000 | 1.956 | 1
106A | IT room | 280 | 18 |  | 304 | 6 | 6 | Unit Ventilator | 2432 | 6.9079 | 2
107 | Class Area | 155 | 10 |  | 1050 | 23 | 10 | Unit Ventilator | 8400 | 1.1071 | 1
108 | Class Area | 141 | 9 |  | 1050 | 23 | 9 | Unit Ventilator | 8400 | 1.0071 | 1
109 | Class Area | 143 | 9 |  | 625 | 14 | 9 | Unit Ventilator | 5000 | 1.716 | 1
110 | Class Area | 159 | 10 |  | 690 | 15 | 10 | Unit Ventilator | 5520 | 1.7283 | 1
111 | Class Area | 164 | 10 |  | 690 | 15 | 10 | Unit Ventilator | 5520 | 1.7826 | 1
112 | Class Area | 142 | 9 |  | 690 | 15 | 9 | Unit Ventilator | 5520 | 1.5435 | 1
113 | Class Area | 149 | 9 |  | 690 | 15 | 9 | Unit Ventilator | 5520 | 1.6196 | 1
114 | Class Area | 137 | 9 |  | 690 | 15 | 9 | Unit Ventilator | 5520 | 1.4891 | 1
114A | Team Planning | 0 | 0 |  | 360 | 8 | 0 | HUV | 2880 | 0 | 0
115 | Class | 141 | 9 |  | 690 | 15 | 9 | Unit Ventilator | 5520 | 1.5326 | 1
118D | Main Office | 0 | 0 |  | 150 | 3 | 0 | Unit Ventilator | 1200 | 0 | 0
119A | Instructional Storage | 0 | 0 |  |  | 0 | 0 | HUV | 0 | 0 | 0
119B | Building Engineer's Office | 305 | 20 |  | 450 | 10 | 10 | Unit Ventilator | 3600 | 5.0833 | 2
120 | Instructional Materials Center | 303 | 20 |  | 2520 | 57 | 20 | Unit Ventilator | 20160 | 0.90179 | 0
122 | Main Office | 394 | 26 |  | 600 | 13 | 13 | Unit Ventilator | 4800 | 4.925 | 2
122C | Main Office | 301 | 20 |  | 130 | 2 | 2 | Unit Ventilator | 1040 | 17.3654 | 3
122D | Principal's Office | 383 | 25 |  | 216 | 4 | 4 | Unit Ventilator | 1728 | 13.2986 | 3
123 | Teacher's Dining | 355 | 23 |  | 594 | 13 | 13 | Unit Ventilator | 4752 | 4.4823 | 2
123A | Teacher's Lounge | 298 | 19 |  | 270 | 6 | 6 | Unit Ventilator | 2160 | 8.2778 | 2
127 | Corridor | 0 | 0 |  |  | 0 | 0 | HUV | 0 | 0 | 0
150 | Storage | 163 | 10 |  | 360 | 8 | 8 | Unit Ventilator | 2880 | 3.3958 | 1
153 | Corridor | 0 | 0 |  |  | 0 | 0 | HUV | 0 | 0 | 0
165 | Gym Office | 152 | 10 |  | 130 | 2 | 2 | Unit Ventilator | 1040 | 8.7692 | 2
184 | Examination | 153 | 10 |  | 130 | 2 | 2 | Unit Ventilator | 1040 | 8.8269 | 2
200 | Classroom | 622 | 41 |  | 1350 | 30 | 30 | Unit Ventilator | 10800 | 3.4556 | 1
201 | Classroom | 530 | 35 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.7609 | 2
201A | Instructional Storage | 0 | 0 |  |  | 0 | 0 | HUV | 0 | 0 | 0
202 | Classroom | 519 | 34 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.6413 | 2
203 | Classroom | 434 | 28 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.7174 | 2
204 | Classroom | 550 | 36 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.9783 | 2
205 | Classroom | 436 | 29 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.7391 | 2
206 | Classroom | 500 | 33 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.4348 | 2
206A | Team Planning | 149 | 9 |  | 270 | 6 | 6 | Unit Ventilator | 2160 | 4.1389 | 2
207 | Classroom | 327 | 21 |  | 945 | 21 | 21 | Unit Ventilator | 7560 | 2.5952 | 1
208 | Corridor | 0 | 0 |  |  | 0 | 0 | HUV | 0 | 0 | 0
208 | Classroom | 509 | 33 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.5326 | 2
209 | Classroom | 552 | 36 |  | 625 | 14 | 14 | Unit Ventilator | 5000 | 6.624 | 2
210 | Classroom | 694 | 46 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 7.5435 | 2
211 | Classroom | 531 | 35 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.7717 | 2
212 | Classroom | 379 | 25 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.1196 | 2
213 | Classroom | 688 | 45 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 7.4783 | 2
214 | Classroom | 382 | 25 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.1522 | 2
214A | Instructional Storage | 0 | 0 |  |  | 0 | 0 | HUV | 0 | 0 | 0
215 | Classroom | 370 | 24 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.3036 | 1
216 | Classroom | 388 | 25 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 3.6149 | 1
217 | Classroom | 413 | 27 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.911 | 1
218 | Classroom | 328 | 21 |  | 625 | 14 | 14 | Unit Ventilator | 5000 | 3.936 | 1
218C | Classroom | 286 | 19 |  | 960 | 21 | 19 | Unit Ventilator | 7680 | 2.2344 | 1
219 | Classroom | 862 | 57 |  | 1800 | 40 | 40 | Unit Ventilator | 14400 | 3.5917 | 1
220 | Classroom | 980 | 65 |  | 1350 | 30 | 30 | Unit Ventilator | 10800 | 5.4444 | 2
221 | Classroom | 342 | 22 |  | 625 | 14 | 14 | Unit Ventilator | 5000 | 4.104 | 2
234 | Corridor | 0 | 0 |  |  | 0 | 0 | HUV | 0 | 0 | 0
244 | Counselor | 0 | 0 |  |  | 0 | 0 | HUV | 0 | 0 | 0
- | Nurse's Office | 279 | 18 |  | 150 | 3 | 3 | Unit Ventilator | 1200 | 13.95 | 3
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | James G. Blaine Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers Retest | 2nd Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Gym / Cafe. | 1104 | 73 |  | 3749 | 85 | 73 | Air Handling Unit | 29992 | 2.2086 | 1
- | Auditorium | 577 | 38 |  | 3161 | 71 | 38 | Air Handling Unit | 25288 | 1.369 | 1
100 | Classroom | 437 | 29 |  | 1415 | 32 | 29 | Unit Ventilator | 11320 | 2.3163 | 1
101 | Classroom | 684 | 45 |  | 1476 | 33 | 33 | Unit Ventilator | 11808 | 3.4756 | 1
102 | Classroom | 625 | 41 |  | 1460 | 33 | 33 | Unit Ventilator | 11680 | 3.2106 | 1
103 | Classroom | 461 | 30 |  | 1465 | 33 | 30 | Unit Ventilator | 11720 | 2.3601 | 1
104 | Classroom | 319 | 21 |  | 856 | 19 | 19 | Unit Ventilator | 6848 | 2.795 | 1
105 | Classroom | 306 | 20 |  | 655 | 14 | 14 | Unit Ventilator | 5240 | 3.5038 | 1
106 | Classroom | 452 | 30 |  | 921 | 20 | 20 | Unit Ventilator | 7368 | 3.6808 | 1
107 | Classroom | 274 | 18 |  | 970 | 22 | 18 | Unit Ventilator | 7760 | 2.1186 | 1
108 | Custodial | 251 | 16 |  | 835 | 18 | 16 | Unit Ventilator | 6680 | 2.2545 | 1
110 | Nurse |  | 0 | Yes | 452 | 10 | 10 | Unit Ventilator | 3616 | 0 | 0
200 | Classroom | 297 | 19 |  | 947 | 21 | 19 | Unit Ventilator | 7576 | 2.3522 | 1
201 | Classroom | 246 | 16 |  | 649 | 14 | 14 | Unit Ventilator | 5192 | 2.8428 | 1
202 | Classroom | 414 | 27 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 3.3173 | 1
203 | Classroom | 230 | 15 |  | 937 | 21 | 15 | Unit Ventilator | 7496 | 1.841 | 1
204 | Classroom | 359 | 23 |  | 958 | 21 | 21 | Unit Ventilator | 7664 | 2.8105 | 1
205 | Classroom | 286 | 19 |  | 937 | 21 | 19 | Unit Ventilator | 7496 | 2.2892 | 1
206 | Classroom | 447 | 29 |  | 952 | 21 | 21 | Unit Ventilator | 7616 | 3.5215 | 1
207 | Classroom | 291 | 19 |  | 956 | 21 | 19 | Unit Ventilator | 7648 | 2.2829 | 1
208 | Classroom | 314 | 20 |  | 968 | 22 | 20 | Unit Ventilator | 7744 | 2.4329 | 1
209 | Classroom | 349 | 23 |  | 975 | 22 | 22 | Unit Ventilator | 7800 | 2.6846 | 1
210 | Classroom | 236 | 15 |  | 931 | 21 | 15 | Unit Ventilator | 7448 | 1.9012 | 1
211 | Classroom | 287 | 19 |  | 982 | 22 | 19 | Unit Ventilator | 7856 | 2.192 | 1
212 | Classroom | 362 | 24 |  | 953 | 21 | 21 | Unit Ventilator | 7624 | 2.8489 | 1
213 | Classroom | 296 | 19 |  | 957 | 21 | 19 | Unit Ventilator | 7656 | 2.3197 | 1
214 | Classroom | 378 | 25 |  | 956 | 21 | 21 | Unit Ventilator | 7648 | 2.9655 | 1
215 | Classroom | 288 | 19 |  | 603 | 13 | 13 | Unit Ventilator | 4824 | 3.5821 | 1
216 | Classroom | 406 | 27 |  | 942 | 21 | 21 | Unit Ventilator | 7536 | 3.2325 | 1
217 | Classroom | 407 | 27 |  | 656 | 14 | 14 | Unit Ventilator | 5248 | 4.6532 | 2
300 | Classroom | 332 | 22 |  | 956 | 21 | 21 | Unit Ventilator | 7648 | 2.6046 | 1
301 | Classroom | 333 | 22 |  | 601 | 13 | 13 | Unit Ventilator | 4808 | 4.1556 | 2
302 | Classroom | 249 | 16 |  | 864 | 19 | 16 | Unit Ventilator | 6912 | 2.1615 | 1
303 | Classroom | 341 | 22 |  | 859 | 19 | 19 | Unit Ventilator | 6872 | 2.9773 | 1
304 | Classroom | 270 | 18 |  | 863 | 19 | 18 | Unit Ventilator | 6904 | 2.3465 | 1
305 | Classroom | 286 | 19 |  | 862 | 19 | 19 | Unit Ventilator | 6896 | 2.4884 | 1
306 | Classroom | 254 | 16 |  | 861 | 19 | 16 | Unit Ventilator | 6888 | 2.2125 | 1
307 | Classroom | 348 | 23 |  | 865 | 19 | 19 | Unit Ventilator | 6920 | 3.0173 | 1
308 | Classroom | 334 | 22 |  | 859 | 19 | 19 | Unit Ventilator | 6872 | 2.9162 | 1
309 | Classroom | 287 | 19 |  | 972 | 22 | 19 | Unit Ventilator | 7776 | 2.2145 | 1
310 | Classroom | 324 | 21 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 2.8521 | 1
311 | Classroom | 306 | 20 |  | 958 | 21 | 20 | Unit Ventilator | 7664 | 2.3956 | 1
312 | Classroom | 483 | 32 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 3.8132 | 1
313 | Classroom | 460 | 30 |  | 944 | 21 | 21 | Unit Ventilator | 7552 | 3.6547 | 1
314 | Classroom | 238 | 15 |  | 951 | 21 | 15 | Unit Ventilator | 7608 | 1.877 | 1
315 | Classroom | 359 | 23 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 4.0367 | 2
316 | Classroom | 315 | 21 |  | 952 | 21 | 21 | Unit Ventilator | 7616 | 2.4816 | 1
317 | Classroom | 288 | 19 |  | 651 | 14 | 14 | Unit Ventilator | 5208 | 3.318 | 1
- | Main Office |  | 0 | Yes | 1235 | 28 | 28 | Unit Ventilator | 9880 | 0 | 0
- | Principal |  | 0 | Yes | 361 | 8 | 8 | Unit Ventilator | 2888 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-20 | [7 empty] | 0 | 0 | 0
School: | Randolph Blankenburg Elementary-Middle School | House fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
K-1 | Classroom | 906 | 60 |  | 704 | 16 | 16 | House Fan | 5632 | 9.652 | 2
K-4 | Classroom | 828 | 55 |  | 704 | 16 | 16 | House Fan | 5632 | 8.821 | 2
B27 | Classroom | 517 | 34 |  | 1047 | 23 | 23 | House Fan | 8376 | 3.7034 | 1
10A | Vice Principal | 0 | 0 | Yes | 176 | 4 | 4 | N/A | 1408 | 0 | 0
29 | Classroom | 594 | 39 |  | 704 | 16 | 16 | House Fan | 5632 | 6.3281 | 2
30 | Classroom | 930 | 62 |  | 836 | 19 | 19 | House Fan | 6688 | 8.3433 | 2
101 | Classroom | 890 | 59 |  | 704 | 16 | 16 | House Fan | 5632 | 9.4815 | 2
102 | Classroom | 63 | 4 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0.67116 | 0
103 | Classroom | 954 | 63 |  | 704 | 16 | 16 | House Fan | 5632 | 10.1634 | 3
105 | Classroom | 907 | 60 |  | 704 | 16 | 16 | House Fan | 5632 | 9.6626 | 2
106 | Classroom | 988 | 65 |  | 704 | 16 | 16 | House Fan | 5632 | 10.5256 | 3
107 | Classroom | 959 | 63 |  | 704 | 16 | 16 | House Fan | 5632 | 10.2166 | 3
208 | Classroom | 620 | 41 |  | 704 | 16 | 16 | House Fan | 5632 | 6.6051 | 2
208A | Nurse's Office | 0 | 0 |  | 176 | 4 | 0 | N/A | 1408 | 0 | 0
209 | Classroom | 695 | 46 |  | 704 | 16 | 16 | House Fan | 5632 | 7.4041 | 2
210 | Classroom | 930 | 62 |  | 704 | 16 | 16 | House Fan | 5632 | 9.9077 | 2
211 | Classroom | 887 | 59 |  | 704 | 16 | 16 | House Fan | 5632 | 9.4496 | 2
212 | Classroom | 751 | 50 |  | 704 | 16 | 16 | House Fan | 5632 | 8.0007 | 2
213 | Classroom | 955 | 63 |  | 704 | 16 | 16 | House Fan | 5632 | 10.174 | 3
214 | Classroom | 950 | 63 |  | 704 | 16 | 16 | House Fan | 5632 | 10.1207 | 3
316 | Classroom | 0 | 0 | Yes | 880 | 20 | 20 | House Fan | 7040 | 0 | 0
317 | Classroom | 361 | 24 |  | 484 | 11 | 11 | House Fan | 3872 | 5.594 | 2
318 | Classroom | 588 | 39 |  | 704 | 16 | 16 | House Fan | 5632 | 6.2642 | 2
319 | Classroom | 341 | 22 |  | 704 | 16 | 16 | House Fan | 5632 | 3.6328 | 1
320 | Classroom | 483 | 32 |  | 704 | 16 | 16 | House Fan | 5632 | 5.1456 | 2
321 | Classroom | 743 | 49 |  | 704 | 16 | 16 | House Fan | 5632 | 7.9155 | 2
322 | Classroom | 877 | 58 |  | 704 | 16 | 16 | House Fan | 5632 | 9.343 | 2
323 | Classroom | 642 | 42 |  | 748 | 17 | 17 | House Fan | 5984 | 6.4372 | 2
324 | Classroom | 818 | 54 |  | 704 | 16 | 16 | House Fan | 5632 | 8.7145 | 2
325 | Classroom | 809 | 53 |  | 704 | 16 | 16 | House Fan | 5632 | 8.6186 | 2
326 | Classroom | 565 | 37 |  | 704 | 16 | 16 | House Fan | 5632 | 6.0192 | 2
327 | Classroom | 698 | 46 |  | 704 | 16 | 16 | House Fan | 5632 | 7.4361 | 2
328 | Classroom | 151 | 10 | Yes | 704 | 16 | 16 | House Fan | 5632 | 1.6087 | 1
329 | Classroom | 0 | 0 | Yes | 264 | 6 | 6 | House Fan | 2112 | 0 | 0
2121 | Storage | 0 | 0 | Yes | 399 | 9 | 9 | House Fan | 3192 | 0 | 0
- | Auditorium | 2451 | 163 |  | 3520 | 80 | 80 | House Fan | 28160 | 5.2223 | 2
- | Counselor Office | 0 | 0 | Yes | 220 | 5 | 5 | N/A | 1760 | 0 | 0
- | Gym | 0 | 0 | Yes | 3872 | 88 | 88 | N/A | 30976 | 0 | 0
- | Kitchen | 634 | 42 |  | 880 | 20 | 20 | House Fan | 7040 | 5.4034 | 2
- | Library | 865 | 57 |  | 1675 | 38 | 38 | House Fan | 13400 | 3.8731 | 1
- | Main Office | 0 | 0 | Yes | 308 | 7 | 7 | N/A | 2464 | 0 | 0
- | Principal Office | 0 | 0 | Yes | 160 | 3 | 3 | N/A | 1280 | 0 | 0
- | SEL Classroom | 970 | 64 |  | 704 | 16 | 16 | House Fan | 5632 | 10.3338 | 3
- | Staff Lounge | 0 | 0 | Yes | 399 | 9 | 9 | N/A | 3192 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-17 | [7 empty] | 0 | 0 | 0
School: | Bodine | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
401 | Classroom |  | 0 |  | 660 | 15 | 0 |  | 5280 | 0 | 0
402 | classroom |  | 0 |  | 616 | 14 | 0 |  | 4928 | 0 | 0
403 | Classroom |  | 0 |  | 598 | 13 | 0 |  | 4784 | 0 | 0
404 | Classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | 0 | 0
405 A | Dept Head |  | 0 |  | 98 | 2 | 0 |  | 784 | 0 | 0
405 B | Counselor |  | 0 |  | 133 | 3 | 0 |  | 1064 | 0 | 0
406 | Classroom |  | 0 |  | 672 | 15 | 0 |  | 5376 | 0 | 0
407 | Classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | 0 | 0
408 | Computer |  | 0 |  | 726 | 16 | 0 |  | 5808 | 0 | 0
409 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
301 | Classroom |  | 0 |  | 667 | 15 | 0 |  | 5336 | 0 | 0
302 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
303 | Classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | 0 | 0
304 | Classroom |  | 0 |  | 621 | 14 | 0 |  | 4968 | 0 | 0
305 | Faculty Area |  | 0 |  | 450 | 10 | 0 |  | 3600 | 0 | 0
306 | Classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | 0 | 0
307 | Classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | 0 | 0
308 | Classrrom |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
309 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
201 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
202 | Classroom |  | 0 |  | 660 | 15 | 0 |  | 5280 | 0 | 0
203 | Library |  | 0 |  | 1058 | 24 | 0 |  | 8464 | 0 | 0
203 | Library office |  | 0 |  | 140 | 3 | 0 |  | 1120 | 0 | 0
205 | Classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | 0 | 0
206 | Classroom |  | 0 |  | 621 | 14 | 0 |  | 4968 | 0 | 0
207 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
208 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
102 | Classroom |  | 0 |  | 880 | 20 | 0 |  | 7040 | 0 | 0
103 | Counselor |  | 0 |  | 110 | 2 | 0 |  | 880 | 0 | 0
104 | Teacher Lounge |  | 0 |  | 345 | 7 | 0 |  | 2760 | 0 | 0
105 A | Office |  | 0 |  | 63 | 1 | 0 |  | 504 | 0 | 0
105 B | Office |  | 0 |  | 108 | 2 | 0 |  | 864 | 0 | 0
105 C | Office |  | 0 |  | 81 | 1 | 0 |  | 648 | 0 | 0
108 | Room |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
109 | Room |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
2 | Art Room |  | 0 |  | 484 | 11 | 0 |  | 3872 | 0 | 0
- | Main Office |  | 0 |  | 322 | 7 | 0 |  | 2576 | 0 | 0
- | Principal Office |  | 0 |  | 96 | 2 | 0 |  | 768 | 0 | 0
- | Conferance Room |  | 0 |  | 220 | 5 | 0 |  | 1760 | 0 | 0
- | Gym / Lunchroom |  | 0 |  | 2760 | 62 | 0 |  | 22080 | 0 | 0
- | Kitchen |  | 0 |  | 648 | 14 | 0 |  | 5184 | 0 | 0
Sheet Last Modified: | 2021-04-28 | [7 empty] | 0 | 0 | 0
School: | Amedee F. Bregy Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Auditorium | 6957 | 463 |  | 4017 | 91 | 91 | House Fan | 32136 | 12.9892 | 3
- | Cafeteria | 934 | 62 |  | 1584 | 36 | 36 | House Fan | 12672 | 4.4223 | 2
- | Gym | 0 | 0 | Yes | 3872 | 88 | 88 | House Fan | 30976 | 0 | 0
- | Library | 991 | 66 |  | 1739 | 39 | 39 | House Fan | 13912 | 4.274 | 2
- | Basement Science Classroom | 557 | 37 |  | 1064 | 24 | 24 | House Fan | 8512 | 3.9262 | 1
- | Basement Storage | 143 | 9 |  | 396 | 9 | 9 | House Fan | 3168 | 2.7083 | 1
- | Basement Boy's Bathroom | 471 | 31 |  | 528 | 12 | 12 | House Fan | 4224 | 6.6903 | 2
- | Basement Girl's Bathroom | 434 | 28 |  | 528 | 12 | 12 | House Fan | 4224 | 6.1648 | 2
101 | Classroom | 271 | 18 |  | 660 | 15 | 15 | House Fan | 5280 | 3.0795 | 1
102 | Classroom | 312 | 20 |  | 660 | 15 | 15 | House Fan | 5280 | 3.5455 | 1
1K1 | Classroom | 823 | 54 |  | 660 | 15 | 15 | House Fan | 5280 | 9.3523 | 2
103 | Classroom | 51 | 3 |  | 650 | 14 | 3 | House Fan | 5200 | 0.58846 | 0
104 | Classroom | 564 | 37 |  | 650 | 14 | 14 | House Fan | 5200 | 6.5077 | 2
105 | Classroom | 255 | 17 |  | 616 | 14 | 14 | House Fan | 4928 | 3.1047 | 1
106 | Classroom | 723 | 48 |  | 616 | 14 | 14 | House Fan | 4928 | 8.8028 | 2
107 | Classroom | 664 | 44 |  | 616 | 14 | 14 | House Fan | 4928 | 8.0844 | 2
208 | Classroom | 866 | 57 |  | 660 | 15 | 15 | House Fan | 5280 | 9.8409 | 2
209 | Classroom | 751 | 50 |  | 660 | 15 | 15 | House Fan | 5280 | 8.5341 | 2
210 | Classroom | 128 | 8 | Yes | 652 | 14 | 14 | House Fan | 5216 | 1.4724 | 1
211 | Classroom | 663 | 44 |  | 616 | 14 | 14 | House Fan | 4928 | 8.0722 | 2
212 | Classroom | 669 | 44 |  | 660 | 15 | 15 | House Fan | 5280 | 7.6023 | 2
213 | Classroom | 694 | 46 |  | 660 | 15 | 15 | House Fan | 5280 | 7.8864 | 2
214 | Classroom | 629 | 41 |  | 660 | 15 | 15 | House Fan | 5280 | 7.1477 | 2
215 | Classroom | 279 | 18 |  | 660 | 15 | 15 | House Fan | 5280 | 3.1705 | 1
316 | Classroom | 404 | 26 |  | 660 | 15 | 15 | House Fan | 5280 | 4.5909 | 2
317 | Classroom | 0 | 0 | Yes | 656 | 14 | 14 | House Fan | 5248 | 0 | 0
318 | Classroom | 577 | 38 |  | 660 | 15 | 15 | House Fan | 5280 | 6.5568 | 2
319 | Classroom | 231 | 15 |  | 660 | 15 | 15 | House Fan | 5280 | 2.625 | 1
320 | Classroom | 726 | 48 |  | 704 | 16 | 16 | House Fan | 5632 | 7.7344 | 2
321 | Classroom | 298 | 19 |  | 704 | 16 | 16 | House Fan | 5632 | 3.1747 | 1
322 | Classroom | 511 | 34 |  | 704 | 16 | 16 | House Fan | 5632 | 5.4439 | 2
323 | Classroom | 702 | 46 |  | 660 | 15 | 15 | House Fan | 5280 | 7.9773 | 2
324 | Classroom | 375 | 25 |  | 660 | 15 | 15 | House Fan | 5280 | 4.2614 | 2
325 | Classroom | 623 | 41 |  | 616 | 14 | 14 | House Fan | 4928 | 7.5852 | 2
326 | Classroom | 557 | 37 |  | 654 | 14 | 14 | House Fan | 5232 | 6.3876 | 2
327 | Classroom | 525 | 35 |  | 654 | 14 | 14 | House Fan | 5232 | 6.0206 | 2
328 | Classroom | 664 | 44 |  | 660 | 15 | 15 | House Fan | 5280 | 7.5455 | 2
- | Principal Office |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | 0 | 0
- | Nurse Office |  | 0 | Yes | 220 | 5 | 5 | House Fan | 1760 | 0 | 0
Sheet Last Modified: | 2021-04-07 | [7 empty] | 0 | 0 | 0
School: | Bridesburg Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | Goldner Part 2 | [6 empty] | 0 | 0 | 0
| Devine Annex Retest | [7 empty] | 0 | 0 | 0
School: | Bridesburg Elementary School Annex | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Main Building | [8 empty] | 0 | 0 | 0
102 | Classroom | 422 | 28 |  | 846 | 19 | 19 | Unit Ventilator | 6768 | 3.7411 | 1
103 | Classroom | 377 | 25 |  | 686 | 15 | 15 | Unit Ventilator | 5488 | 4.1217 | 2
104 | Classroom | 476 | 31 |  | 993 | 22 | 22 | Unit Ventilator | 7944 | 3.5952 | 1
105 | Classroom | 300 | 20 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 3.3482 | 1
106 | Classroom | 536 | 35 |  | 972 | 22 | 22 | Unit Ventilator | 7776 | 4.1358 | 2
107 | Classroom | 334 | 22 |  | 737 | 16 | 16 | Unit Ventilator | 5896 | 3.3989 | 1
108 | Classroom | 322 | 21 |  | 1030 | 23 | 21 | Unit Ventilator | 8240 | 2.3447 | 1
109 | Classroom | 294 | 19 |  | 684 | 15 | 15 | Unit Ventilator | 5472 | 3.2237 | 1
110A | Counselor's Office | 198 | 13 |  | 130 | 2 | 2 | Unit Ventilator | 1040 | 11.4231 | 3
111 | Classroom | 372 | 24 |  | 253 | 5 | 5 | Unit Ventilator | 2024 | 11.0277 | 3
112 | Nurse's Office | 272 | 18 |  | 369 | 8 | 8 | Unit Ventilator | 2952 | 5.5285 | 2
112A | Classroom | 0 | 0 |  | 218 | 4 | 0 | Unit Ventilator | 1744 | 0 | 0
112B | Classroom | 0 | 0 |  | 218 | 4 | 0 | Unit Ventilator | 1744 | 0 | 0
113 | Classroom | 137 | 9 |  | 117 | 2 | 2 | Unit Ventilator | 936 | 8.7821 | 2
114 | Classroom | 327 | 21 |  | 930 | 21 | 21 | Unit Ventilator | 7440 | 2.6371 | 1
115 | Classroom | 281 | 18 |  | 659 | 14 | 14 | Unit Ventilator | 5272 | 3.198 | 1
116 | Library | 1510 | 100 |  | 1700 | 38 | 38 | Unit Ventilator | 13600 | 6.6618 | 2
200 | Classroom | 0 | 0 | Yes | 754 | 17 | 17 | Unit Ventilator | 6032 | 0 | 0
201 | Classroom | 136 | 9 |  | 609 | 13 | 9 | Unit Ventilator | 4872 | 1.6749 | 1
202 | Classroom | 312 | 20 |  | 539 | 12 | 12 | Unit Ventilator | 4312 | 4.3414 | 2
203 | Classroom | 377 | 25 |  | 714 | 16 | 16 | Unit Ventilator | 5712 | 3.9601 | 1
204 | Classroom | 152 | 10 |  | 695 | 15 | 10 | Unit Ventilator | 5560 | 1.6403 | 1
205 | Classroom | 1577 | 105 |  | 1129 | 25 | 25 | Unit Ventilator | 9032 | 10.4761 | 3
206 | Classroom | 157 | 10 |  | 715 | 16 | 10 | Unit Ventilator | 5720 | 1.6469 | 1
207 | Classroom | 247 | 16 |  | 725 | 16 | 16 | Unit Ventilator | 5800 | 2.5552 | 1
208 | Classroom | 351 | 23 |  | 650 | 14 | 14 | Unit Ventilator | 5200 | 4.05 | 2
209 | Classroom | 0 | 0 | Yes | 709 | 16 | 16 | Unit Ventilator | 5672 | 0 | 0
210 | Classroom | 147 | 9 |  | 759 | 17 | 9 | Unit Ventilator | 6072 | 1.4526 | 1
211 | Classroom | 147 | 9 |  | 735 | 16 | 9 | Unit Ventilator | 5880 | 1.5 | 1
212 | Classroom | 180 | 12 |  | 787 | 17 | 12 | Unit Ventilator | 6296 | 1.7154 | 1
213 | Classroom | 283 | 18 |  | 665 | 15 | 15 | Unit Ventilator | 5320 | 3.1917 | 1
214 | Classroom | 1248 | 83 |  | 845 | 19 | 19 | Unit Ventilator | 6760 | 11.0769 | 3
215 | Classroom | 457 | 30 |  | 677 | 15 | 15 | Unit Ventilator | 5416 | 5.0628 | 2
217 | Classroom | 282 | 18 |  | 735 | 16 | 16 | Unit Ventilator | 5880 | 2.8776 | 1
218 | Classroom | 292 | 19 |  | 601 | 13 | 13 | Unit Ventilator | 4808 | 3.6439 | 1
220 | Classroom | 287 | 19 |  | 706 | 16 | 16 | Unit Ventilator | 5648 | 3.0489 | 1
- | Hallway |  | 0 |  |  | 0 | 0 | HRU | 0 | 0 | 0
- | Hallway 2 |  | 0 |  |  | 0 | 0 | HRU | 0 | 0 | 0
- | Hallway Right |  | 0 |  |  | 0 | 0 | HRU | 0 | 0 | 0
- | Hallways 2 Center |  | 0 |  |  | 0 | 0 | HRU | 0 | 0 | 0
- | Gym | 0 | 0 |  | 3925 | 89 | 0 | N/A | 31400 | 0 | 0
- | Cafeteria | 0 | 0 |  | 3080 | 70 | 0 | N/A | 24640 | 0 | 0
- | Kitchen | 0 | 0 |  | 697 | 15 | 0 | N/A | 5576 | 0 | 0
- | Main Office | 1167 | 77 |  | 752 | 17 | 17 | HRU | 6016 | 11.639 | 3
Bridesburg Elementary School Annex | [8 empty] | 0 | 0 | 0
1 | Classroom |  | 0 | Yes | 710 | 16 | 16 | N/A | 5680 | 0 | 0
2 | Staff Lounge |  | 0 | Yes | 504 | 11 | 11 | N/A | 4032 | 0 | 0
3 | Classroom |  | 0 | Yes | 575 | 13 | 13 | N/A | 4600 | 0 | 0
4 | Vice Principal |  | 0 | Yes | 245 | 5 | 5 | N/A | 1960 | 0 | 0
5 | Classroom |  | 0 | Yes | 693 | 15 | 15 | N/A | 5544 | 0 | 0
6 | Classroom |  | 0 | Yes | 732 | 16 | 16 | N/A | 5856 | 0 | 0
7 | Classroom |  | 0 | Yes | 773 | 17 | 17 | N/A | 6184 | 0 | 0
8 | Classroom |  | 0 | Yes | 589 | 13 | 13 | N/A | 4712 | 0 | 0
9 | Classroom |  | 0 | Yes | 610 | 13 | 13 | N/A | 4880 | 0 | 0
10 | Classroom |  | 0 | Yes | 623 | 14 | 14 | N/A | 4984 | 0 | 0
11 | Classroom |  | 0 | Yes | 581 | 13 | 13 | N/A | 4648 | 0 | 0
12 | Classroom |  | 0 | Yes | 569 | 12 | 12 | N/A | 4552 | 0 | 0
13 | Classroom |  | 0 | Yes | 625 | 14 | 14 | N/A | 5000 | 0 | 0
14 | Classroom |  | 0 | Yes | 576 | 13 | 13 | N/A | 4608 | 0 | 0
15 | Classroom |  | 0 | Yes | 547 | 12 | 12 | N/A | 4376 | 0 | 0
- | Support Room |  | 0 | Yes | 140 | 3 | 3 | N/A | 1120 | 0 | 0
- | Speech Room |  | 0 | Yes | 152 | 3 | 3 | N/A | 1216 | 0 | 0
- | Nurse Office |  | 0 | Yes | 144 | 3 | 3 | N/A | 1152 | 0 | 0
- | Main Office |  | 0 | Yes | 334 | 7 | 7 | N/A | 2672 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Henry A. Brown Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Retest Report | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Admin | 418 | 27 |  | 1058 | 24 | 24 | FCU | 8464 | 2.9631 | 1
- | Cafeteria | 2904 | 193 |  | 1994 | 45 | 45 | AHU | 15952 | 10.9228 | 3
- | Gym | 1581 | 105 |  | 3360 | 76 | 76 | AHU | 26880 | 3.529 | 1
- | Library | 488 | 32 |  | 1486 | 33 | 32 | FCU | 11888 | 2.463 | 1
- | Nurses Room | 133 | 8 |  | 290 | 6 | 6 | FCU | 2320 | 3.4397 | 1
- | Outside Library | 366 | 24 |  | 900 | 20 | 20 | FCU | 7200 | 3.05 | 1
100 | Classroom | 328 | 21 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 3.4894 | 1
101 | Classroom | 395 | 26 |  | 730 | 16 | 16 | Unit Ventilator | 5840 | 4.0582 | 2
113 | Classroom | 296 | 19 |  | 745 | 16 | 16 | Unit Ventilator | 5960 | 2.9799 | 1
114 | Classroom | 309 | 20 |  | 700 | 15 | 15 | Unit Ventilator | 5600 | 3.3107 | 1
151 | Classroom | 779 | 51 |  | 784 | 17 | 17 | FCU | 6272 | 7.4522 | 2
153 | Classroom | 689 | 45 |  | 895 | 20 | 20 | FCU | 7160 | 5.7737 | 2
154 | Classroom | 590 | 39 |  | 780 | 17 | 17 | FCU | 6240 | 5.6731 | 2
156 | Classroom | 647 | 43 |  | 835 | 18 | 18 | FCU | 6680 | 5.8114 | 2
200 | Classroom | 608 | 40 |  | 905 | 20 | 20 | Unit Ventilator | 7240 | 5.0387 | 2
201 | Classroom | 633 | 42 |  | 900 | 20 | 20 | Unit Ventilator | 7200 | 5.275 | 2
202 | Classroom |  | 0 | Yes | 655 | 14 | 14 |  | 5240 | 0 | 0
206 | Classroom |  | 0 | Yes | 795 | 18 | 18 |  | 6360 | 0 | 0
209 | Classroom |  | 0 | Yes | 655 | 14 | 14 |  | 5240 | 0 | 0
211 | Classroom | 470 | 31 |  | 895 | 20 | 20 | Unit Ventilator | 7160 | 3.9385 | 1
212 | Classroom | 307 | 20 |  | 905 | 20 | 20 | Unit Ventilator | 7240 | 2.5442 | 1
213 | Classroom | 782 | 52 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 6.7029 | 2
214 | Classroom | 616 | 41 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 5.28 | 2
217 | Classroom | 250 | 16 |  | 665 | 15 | 15 | Unit Ventilator | 5320 | 2.8195 | 1
226 South | Classroom | 405 | 27 |  | 777 | 17 | 17 | Unit Ventilator | 6216 | 3.9093 | 1
226 West | Classroom | 458 | 30 |  | 777 | 17 | 17 | Unit Ventilator | 6216 | 4.4208 | 2
227 | Classroom | 487 | 32 |  | 740 | 16 | 16 | Unit Ventilator | 5920 | 4.9358 | 2
228 | Classroom | 685 | 45 |  | 775 | 17 | 17 | Unit Ventilator | 6200 | 6.629 | 2
229 | Computer Lab | 103 | 6 | Yes | 990 | 22 | 22 | FCU | 7920 | 0.7803 | 0
300 | Classroom | 582 | 38 |  | 905 | 20 | 20 | Unit Ventilator | 7240 | 4.8232 | 2
301 | Classroom | 535 | 35 |  | 890 | 20 | 20 | Unit Ventilator | 7120 | 4.5084 | 2
302 | Classroom | 151 | 10 |  | 695 | 15 | 10 | Unit Ventilator | 5560 | 1.6295 | 1
304 | Classroom | 445 | 29 |  | 825 | 18 | 18 | Unit Ventilator | 6600 | 4.0455 | 2
310 | Classroom | 657 | 43 |  | 715 | 16 | 16 | Unit Ventilator | 5720 | 6.8916 | 2
311 | Classroom | 241 | 16 |  | 935 | 21 | 16 | Unit Ventilator | 7480 | 1.9332 | 1
312 | Classroom | 426 | 28 |  | 935 | 21 | 21 | Unit Ventilator | 7480 | 3.4171 | 1
313 | Classroom | 327 | 21 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 2.6658 | 1
314 | Classroom | 512 | 34 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.1739 | 2
317 | Classroom | 165 | 11 |  | 660 | 15 | 11 | Unit Ventilator | 5280 | 1.875 | 1
318 | Classroom | 473 | 31 |  | 1090 | 24 | 24 | FCU | 8720 | 3.2546 | 1
319 | Classroom | 284 | 18 |  | 1125 | 25 | 18 | FCU | 9000 | 1.8933 | 1
322 South | Classroom | 174 | 11 |  | 745 | 16 | 11 | Unit Ventilator | 5960 | 1.7517 | 1
322 West | Classroom | 107 | 7 |  | 745 | 16 | 7 | Unit Ventilator | 5960 | 1.0772 | 1
323 | Classroom | 472 | 31 |  | 730 | 16 | 16 | Unit Ventilator | 5840 | 4.8493 | 2
324 | Classroom | 784 | 52 |  | 765 | 17 | 17 | Unit Ventilator | 6120 | 7.6863 | 2
325 West | Classroom | 533 | 35 |  | 890 | 20 | 20 | Unit Ventilator | 7120 | 4.4916 | 2
325 North | Classroom | 581 | 38 |  | 890 | 20 | 20 | Unit Ventilator | 7120 | 4.8961 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | Joseph H. Brown Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Emcor Mechanical Retest | Emcor Exhaust Report | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | GYM | 921 | 61 |  | 3510 | 79 | 61 | Unit Ventilator | 28080 | 1.9679 | 1
- | CAFE | 921 | 61 |  | 1440 | 32 | 32 | Unit Ventilator | 11520 | 4.7969 | 2
101 | classroom | 519 | 34 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 5.8358 | 2
102 | classroom | 562 | 37 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 6.3193 | 2
103 | classroom | 358 | 23 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 3.7658 | 1
104 | classroom | 932 | 62 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 8.2139 | 2
105 | classroom | 844 | 56 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 6.8804 | 2
106 | classroom | 786 | 52 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 6.4076 | 2
107 | classroom | 985 | 65 |  | 1104 | 25 | 25 | Unit Ventilator | 8832 | 6.6916 | 2
108 | classroom | 836 | 55 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 7.3678 | 2
109 | Counselor Office |  | 0 | Yes | 112 | 2 | 2 |  | 896 | 0 | 0
110 | Nurse Room |  | 0 |  | 224 | 5 | 0 | N/A | 1792 | 0 | 0
111 | Medical Waiting |  | 0 | Yes | 120 | 2 | 2 |  | 960 | 0 | 0
200 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
201 | classroom | 394 | 26 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.2826 | 2
202 | classroom | 0 | 0 | Yes | 667 | 15 | 15 | Unit Ventilator | 5336 | 0 | 0
203 | classroom | 417 | 27 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 4.6889 | 2
204 | classroom | 408 | 27 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.4348 | 2
205 | classroom | 550 | 36 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.9783 | 2
206 | classroom | 750 | 50 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 5.9211 | 2
206A | Room |  | 0 | Yes | 288 | 6 | 6 |  | 2304 | 0 | 0
207 | classroom | 484 | 32 |  | 506 | 11 | 11 | Unit Ventilator | 4048 | 7.1739 | 2
207A | Office |  | 0 | Yes | 168 | 3 | 3 |  | 1344 | 0 | 0
208 | classroom | 513 | 34 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.5761 | 2
209 | classroom | 723 | 48 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 7.6052 | 2
210 | classroom | 495 | 33 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 5.2069 | 2
211 | classroom | 376 | 25 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 4.2279 | 2
300 | classroom |  | 0 | Yes | 150 | 3 | 3 |  | 1200 | 0 | 0
301 | classroom | 605 | 40 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 6.8028 | 2
302 | classroom | 457 | 30 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.9674 | 2
303 | classroom | 389 | 25 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.2283 | 2
304 | classroom | 469 | 31 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 4.9334 | 2
305 | classroom | 0 | 0 | Yes | 713 | 16 | 16 | Unit Ventilator | 5704 | 0 | 0
306 | classroom | 0 | 0 | Yes | 874 | 19 | 19 | Unit Ventilator | 6992 | 0 | 0
307 | classroom | 419 | 27 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.5543 | 2
308 | classroom |  | 0 | Yes | 713 | 16 | 16 |  | 5704 | 0 | 0
Principal | Office |  | 0 | Yes | 160 | 3 | 3 |  | 1280 | 0 | 0
- | Main Office |  | 0 | Yes | 368 | 8 | 8 | N/A | 2944 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | William C Bryant Elementary School | House fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Gym | 1521 | 101 |  | 2765 | 62 | 62 | House Fan | 22120 | 4.1257 | 2
- | Shop Classroom | 795 | 53 |  | 740 | 16 | 16 | House Fan | 5920 | 8.0574 | 2
- | Art Room | 0 | 0 |  | 740 | 16 | 0 | House Fan | 5920 | 0 | 0
- | Cafeteria/Auditorium | 1853 | 123 |  | 2479 | 56 | 56 | AHU | 19832 | 5.6061 | 2
- | Principal's Office | 0 | 0 | Yes | 204 | 4 | 4 | House Fan | 1632 | 0 | 0
- | Office | 0 | 0 |  | 135 | 3 | 0 | House Fan | 1080 | 0 | 0
101 | Classroom | 1717 | 114 |  | 1013 | 23 | 23 | House Fan | 8104 | 12.7122 | 3
102 | Classroom | 888 | 59 |  | 696 | 15 | 15 | House Fan | 5568 | 9.569 | 2
103 | Classroom | 853 | 56 |  | 690 | 15 | 15 | House Fan | 5520 | 9.2717 | 2
104 | Classroom | 653 | 43 |  | 740 | 16 | 16 | House Fan | 5920 | 6.6182 | 2
105 | Classroom | 0 | 0 | Yes | 700 | 15 | 15 | House Fan | 5600 | 0 | 0
106 | Classroom | 0 | 0 | Yes | 740 | 16 | 16 | House Fan | 5920 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 718 | 16 | 16 | House Fan | 5744 | 0 | 0
108 | Classroom | 0 | 0 | Yes | 795 | 18 | 18 | House Fan | 6360 | 0 | 0
110 | Nurse Office | 0 | 0 | Yes | 219 | 4 | 4 | House Fan | 1752 | 0 | 0
111 | - |  | 0 |  | 731 | 16 | 0 | House Fan | 5848 | 0 | 0
112 | Main Office |  | 0 | Yes | 707 | 16 | 16 | House Fan | 5656 | 0 | 0
113 | Classroom | 0 | 0 | Yes | 674 | 15 | 15 | House Fan | 5392 | 0 | 0
114 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0
201 | Classroom | 1845 | 123 |  | 1013 | 23 | 23 | House Fan | 8104 | 13.6599 | 3
202 | Classroom | 843 | 56 |  | 686 | 15 | 15 | House Fan | 5488 | 9.2165 | 2
203 | Classroom | 108 | 7 | Yes | 690 | 15 | 15 | House Fan | 5520 | 1.1739 | 1
204 | Classroom | 893 | 59 |  | 740 | 16 | 16 | House Fan | 5920 | 9.0507 | 2
205 | Classroom | 0 | 0 | Yes | 700 | 15 | 15 | House Fan | 5600 | 0 | 0
206 | Classroom | 0 | 0 | Yes | 740 | 16 | 16 | House Fan | 5920 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 718 | 16 | 16 | House Fan | 5744 | 0 | 0
208 | Classroom | 0 | 0 | Yes | 795 | 18 | 18 | House Fan | 6360 | 0 | 0
209 | Classroom | 0 | 0 |  | 753 | 17 | 0 | House Fan | 6024 | 0 | 0
210 | Classroom | 0 | 0 | Yes | 715 | 16 | 16 | House Fan | 5720 | 0 | 0
211 | Classroom | 0 | 0 |  | 731 | 16 | 0 | House Fan | 5848 | 0 | 0
212 | Classroom | 0 | 0 | Yes | 707 | 16 | 16 | House Fan | 5656 | 0 | 0
213 | Classroom | 0 | 0 | Yes | 674 | 15 | 15 | House Fan | 5392 | 0 | 0
214 | Classroom | 0 | 0 |  | 713 | 16 | 0 | House Fan | 5704 | 0 | 0
- | IMC - Library | 0 | 0 |  | 2788 | 63 | 0 | Roof Top Unit | 22304 | 0 | 0
- | 2nd Flr Teacher's Lounge | 0 | 0 |  | 349 | 7 | 0 | House Fan | 2792 | 0 | 0
301 | Classroom | 387 | 25 |  | 1013 | 23 | 23 | House Fan | 8104 | 2.8653 | 1
302 | Classroom | 748 | 49 |  | 686 | 15 | 15 | House Fan | 5488 | 8.1778 | 2
303 | Classroom | 68 | 4 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0.73913 | 0
304 | Classroom | 156 | 10 | Yes | 740 | 16 | 16 | House Fan | 5920 | 1.5811 | 1
305 | Classroom | 0 | 0 | Yes | 700 | 15 | 15 | House Fan | 5600 | 0 | 0
306 | Classroom | 0 | 0 | Yes | 740 | 16 | 16 | House Fan | 5920 | 0 | 0
307 | Classroom | 0 | 0 |  | 718 | 16 | 0 | House Fan | 5744 | 0 | 0
308 | Classroom | 0 | 0 |  | 795 | 18 | 0 | House Fan | 6360 | 0 | 0
309 | Classroom | 0 | 0 |  | 753 | 17 | 0 | House Fan | 6024 | 0 | 0
310 | Classroom | 0 | 0 | Yes | 715 | 16 | 16 | House Fan | 5720 | 0 | 0
311 | Classroom | 0 | 0 | Yes | 731 | 16 | 16 | House Fan | 5848 | 0 | 0
312 | Classroom | 0 | 0 | Yes | 707 | 16 | 16 | House Fan | 5656 | 0 | 0
313 | Classroom | 0 | 0 | Yes | 674 | 15 | 15 | House Fan | 5392 | 0 | 0
314 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0
- | 3rd Flr Teacher's Lounge | 0 | 0 |  | 349 | 7 | 0 | House Fan | 2792 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-17 | [7 empty] | 0 | 0 | 0
School: | Building 21 (Kinsey) | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
600 | Classroom |  | 0 |  | 810 | 18 | 0 |  | 6480 | 0 | 0
2 | Classroom |  | 0 |  | 1104 | 25 | 0 |  | 8832 | 0 | 0
4 | Classroom |  | 0 |  | 884 | 20 | 0 |  | 7072 | 0 | 0
5 | Kitchen |  | 0 |  | 910 | 20 | 0 |  | 7280 | 0 | 0
112 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
112A | Nurse |  | 0 |  | 99 | 2 | 0 |  | 792 | 0 | 0
111 | Office |  | 0 |  | 319 | 7 | 0 |  | 2552 | 0 | 0
111A | Office |  | 0 |  | 140 | 3 | 0 |  | 1120 | 0 | 0
111B | Office |  | 0 |  | 168 | 3 | 0 |  | 1344 | 0 | 0
113 | Office |  | 0 |  | 475 | 10 | 0 |  | 3800 | 0 | 0
113A | Office |  | 0 |  | 81 | 1 | 0 |  | 648 | 0 | 0
113B | Office |  | 0 |  | 81 | 1 | 0 |  | 648 | 0 | 0
110 | Main Office |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
115 | Classroom |  | 0 |  | 140 | 3 | 0 |  | 1120 | 0 | 0
114 | Classroom |  | 0 |  | 81 | 1 | 0 |  | 648 | 0 | 0
109 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
108 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
107 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
106 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
105 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
104 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
103 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
102 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
101 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
116 | Aud |  | 0 |  | 5244 | 119 | 0 |  | 41952 | 0 | 0
201 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
202 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
203 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
204 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
205 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
206 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
207 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
208 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
210 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
211 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
212 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
213 | Nurse |  | 0 |  | 295 | 6 | 0 |  | 2360 | 0 | 0
214 | Office |  | 0 |  | 140 | 3 | 0 |  | 1120 | 0 | 0
209 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
215 | Office |  | 0 |  | 140 | 3 | 0 |  | 1120 | 0 | 0
301 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
302 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
303 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
304 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
305 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
306 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
307 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
308 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
309 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
310 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
311 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21 | [7 empty] | 0 | 0 | 0
School: | Camelot Academy @ Boone | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
300 | Office | 292 | 19 |  | 370 | 8 | 8 | Univent | 2960 | 5.9189 | 2
301 | Classroom | 335 | 22 |  | 803 | 18 | 18 | Univent | 6424 | 3.1289 | 1
302 | Classroom | 281 | 18 |  | 816 | 18 | 18 | Univent | 6528 | 2.5827 | 1
304 | Classroom | 292 | 19 |  | 1808 | 41 | 19 | Univent | 14464 | 1.2113 | 1
305 (309) | Classroom | 330 | 22 |  | 851 | 19 | 19 | Univent | 6808 | 2.9083 | 1
306 | Classroom | 364 | 24 |  | 966 | 21 | 21 | Univent | 7728 | 2.8261 | 1
307 | Classroom | 348 | 23 |  | 1647 | 37 | 23 | Univent | 13176 | 1.5847 | 1
308 | Office | 266 | 17 |  | 494 | 11 | 11 | Univent | 3952 | 4.0385 | 2
310 | Office | 135 | 9 |  | 399 | 9 | 9 | Univent | 3192 | 2.5376 | 1
312 | Classroom | 293 | 19 |  | 663 | 15 | 15 | Univent | 5304 | 3.3145 | 1
314 | Classroom | 218 | 14 |  | 458 | 10 | 10 | Univent | 3664 | 3.5699 | 1
316 | Classroom | 367 | 24 |  | 877 | 19 | 19 | Univent | 7016 | 3.1385 | 1
- | Principal Office | 424 | 28 |  | 312 | 7 | 7 | ERU | 2496 | 10.1923 | 3
200 | Classroom | 332 | 22 |  | 807 | 18 | 18 | Univent | 6456 | 3.0855 | 1
201 | Classroom | 305 | 20 |  | 593 | 13 | 13 | Univent | 4744 | 3.8575 | 1
202 | Classroom | 287 | 19 |  | 589 | 13 | 13 | Univent | 4712 | 3.6545 | 1
204 | Classroom | 300 | 20 |  | 1084 | 24 | 20 | Univent | 8672 | 2.0756 | 1
206 | Classroom | 434 | 28 |  | 962 | 21 | 21 | Univent | 7696 | 3.3836 | 1
207 | Classroom | 326 | 21 |  | 880 | 20 | 20 | Univent | 7040 | 2.7784 | 1
208 | Office | 239 | 15 |  | 494 | 11 | 11 | Univent | 3952 | 3.6285 | 1
209 | Classroom | 349 | 23 |  | 879 | 19 | 19 | Univent | 7032 | 2.9778 | 1
- | Academic Office | 308 | 20 |  | 311 | 7 | 7 | Univent | 2488 | 7.4277 | 2
- | Operations Office | 348 | 23 |  | 395 | 8 | 8 | ERU | 3160 | 6.6076 | 2
212 | Classroom | 380 | 25 |  | 567 | 12 | 12 | Univent | 4536 | 5.0265 | 2
214 | Classroom | 397 | 26 |  | 652 | 14 | 14 | Univent | 5216 | 4.5667 | 2
216 | Classroom | 408 | 27 |  | 651 | 14 | 14 | Univent | 5208 | 4.7005 | 2
104 | Conference Room | 424 | 28 |  | 497 | 11 | 11 | Univent | 3976 | 6.3984 | 2
- | Main Office | 372 | 24 |  | 1055 | 23 | 23 | Univent | 8440 | 2.6445 | 1
102 | Computer Lab | 304 | 20 | Yes | 1019 | 23 | 23 | Univent | 8152 | 2.2375 | 1
B5 | Classroom | 310 | 20 |  | 1248 | 28 | 20 | Univent | 9984 | 1.863 | 1
B6 | Cosmo Room 1 | 290 | 19 |  | 535 | 12 | 12 | Univent | 4280 | 4.0654 | 2
B7 | Hair Salon | 443 | 29 |  | 693 | 15 | 15 | Univent | 5544 | 4.7944 | 2
B8 | Barbershop | 275 | 18 |  | 539 | 12 | 12 | Univent | 4312 | 3.8265 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-14 | [7 empty] | 0 | 0 | 0
School: | Philadelphia High School for the Creative & Performing Arts | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
109 | Room | 714 | 47 |  | 1215.8 | 27 | 27 |  | 9726.4 | 4.4045 | 2
108 | Room | 0 | 0 |  | 872.49 | 19 | 0 |  | 6979.92 | 0 | 0
107 | Room | 468 | 31 |  | 1182.7 | 26 | 26 |  | 9461.6 | 2.9678 | 1
105 | Room | 0 | 0 |  | 1171.6 | 26 | 0 |  | 9372.8 | 0 | 0
110 | Office | 45 | 3 |  | 171.71 | 3 | 3 |  | 1373.68 | 1.9655 | 1
- | First Floor North Corridor | 290 | 19 |  | 3004.3 | 68 | 19 |  | 24034.4 | 0.72396 | 0
- | First Floor South Corridor | 118 | 7 |  | 1139.3 | 25 | 7 |  | 9114.4 | 0.77679 | 0
116 | Room | -100 | -6 |  | 216.61 | 4 | -6 |  | 1732.88 | -3.4624 | 0
106 | Editing Suite | 15 | 1 |  | 112.47 | 2 | 1 |  | 899.76 | 1.0003 | 1
106 | Room |  | 0 |  | 1119.1 | 25 | 0 |  | 8952.8 | 0 | 0
114 | Room | -61 | -4 |  | 845.65 | 19 | -4 |  | 6765.2 | -0.541 | 0
116 | Control Room | 219 | 14 |  | 327.76 | 7 | 7 |  | 2622.08 | 5.0113 | 2
- | Second Floor South Corridor Outside Stair 4 | 45 | 3 |  | 2223.7 | 50 | 3 |  | 17789.6 | 0.15177 | 0
- | Second Floor South Corridor | 0 | 0 |  | 1642.3 | 37 | 0 |  | 13138.4 | 0 | 0
- | Second Floor North Corridor | 301 | 20 |  | 1642.3 | 37 | 20 |  | 13138.4 | 1.3746 | 1
202 | Room | 78 | 5 |  | 275.81 | 6 | 5 |  | 2206.48 | 2.121 | 1
203 | Room | 142 | 9 |  | 1209.4 | 27 | 9 |  | 9675.2 | 0.8806 | 0
204 | Room | 616 | 41 |  | 1059.9 | 24 | 24 |  | 8479.2 | 4.3589 | 2
205 | Room | 607 | 40 |  | 874.01 | 19 | 19 |  | 6992.08 | 5.2088 | 2
206 | Room | 0 | 0 |  | 1206.6 | 27 | 0 |  | 9652.8 | 0 | 0
207 | Room | 613 | 40 |  | 891.99 | 20 | 20 |  | 7135.92 | 5.1542 | 2
208 | Room | 809 | 53 |  | 870.75 | 19 | 19 |  | 6966 | 6.9681 | 2
209 | Room | 584 | 38 |  | 871.76 | 19 | 19 |  | 6974.08 | 5.0243 | 2
210 | Room | 304 | 20 |  | 791.75 | 17 | 17 |  | 6334 | 2.8797 | 1
211 | Room | 420 | 28 |  | 1119.8 | 25 | 25 |  | 8958.4 | 2.813 | 1
213 | Room | -85 | -5 |  | 815.15 | 18 | -5 |  | 6521.2 | -0.78206 | 0
214 | Room | 567 | 37 |  | 1351.8 | 30 | 30 |  | 10814.4 | 3.1458 | 1
304 | Room | 15 | 1 |  | 1059.9 | 24 | 1 |  | 8479.2 | 0.10614 | 0
305 | Room | 70 | 4 |  | 192.7 | 4 | 4 |  | 1541.6 | 2.7244 | 1
306 | Room | 122 | 8 |  | 888.58 | 20 | 8 |  | 7108.64 | 1.0297 | 1
307 | Room | 0 | 0 |  | 251.97 | 5 | 0 |  | 2015.76 | 0 | 0
308 | Room | 533 | 35 |  | 1094.9 | 24 | 24 |  | 8759.2 | 3.651 | 1
310 | Room | 527 | 35 |  | 877.6 | 19 | 19 |  | 7020.8 | 4.5038 | 2
311 | Room | 824 | 54 |  | 1209 | 27 | 27 |  | 9672 | 5.1117 | 2
312 | Room | 101 | 6 |  | 892.16 | 20 | 6 |  | 7137.28 | 0.84906 | 0
313 | Room | -121 | -8 |  | 870.18 | 19 | -8 |  | 6961.44 | -1.0429 | 0
314 | Room | 342 | 22 |  | 771.96 | 17 | 17 |  | 6175.68 | 3.3227 | 1
315 | Room | -455 | -30 |  | 888.8 | 20 | -30 |  | 7110.4 | -3.8394 | 0
316 | Room | 1080 | 72 |  | 1532.3 | 34 | 34 |  | 12258.4 | 5.2862 | 2
317 | Room | 754 | 50 |  | 850.53 | 19 | 19 |  | 6804.24 | 6.6488 | 2
318 | Room | 849 | 56 |  | 1015 | 23 | 23 |  | 8120 | 6.2734 | 2
320 | Room | -20 | -1 |  | 94.85 | 2 | -1 |  | 758.8 | -1.5814 | 0
321 | Room | -15 | -1 |  | 77.87 | 1 | -1 |  | 622.96 | -1.4447 | 0
322 | Room | -17 | -1 |  | 58.45 | 1 | -1 |  | 467.6 | -2.1814 | 0
323 | Room | 35 | 2 |  | 1013.7 | 23 | 2 |  | 8109.6 | 0.25895 | 0
324 | Room | 30 | 2 |  | 257.05 | 5 | 2 |  | 2056.4 | 0.87532 | 0
326 | Room | -297 | -19 |  |  | 0 | -19 |  | 0 | 0 | 0
- | Third Floor North Corridor | 303 | 20 |  | 1655.3 | 37 | 20 |  | 13242.4 | 1.3729 | 1
- | Third Floor South Corridor | 0 | 0 |  | 1655.3 | 37 | 0 |  | 13242.4 | 0 | 0
400 | Room | 932 | 62 |  | 1893.6 | 43 | 43 |  | 15148.8 | 3.6914 | 1
401 | Room | 302 | 20 |  | 1794.2 | 40 | 20 |  | 14353.6 | 1.2624 | 1
402 | Room | 615 | 41 |  | 2176.1 | 49 | 41 |  | 17408.8 | 2.1196 | 1
403 | Room | -67 | -4 |  | 216.87 | 4 | -4 |  | 1734.96 | -2.3171 | 0
403 | Print Room | 130 | 8 |  | 275.87 | 6 | 6 |  | 2206.96 | 3.5343 | 1
403 | Room | 52 | 3 |  | 2280.1 | 51 | 3 |  | 18240.8 | 0.17105 | 0
404 | Room | 226 | 15 |  | 1882.5 | 42 | 15 |  | 15060 | 0.9004 | 0
405 | Room | 390 | 26 |  | 1656.39 | 37 | 26 |  | 13251.12 | 1.7659 | 1
405 | Prep Room | 45 | 3 |  |  | 0 | 0 |  | 0 | 0 | 0
406 | Room | 710 | 47 |  |  | 0 | 0 |  | 0 | 0 | 0
407 | Room | 113 | 7 |  |  | 0 | 0 |  | 0 | 0 | 0
408 | Room | 0 | 0 |  | 217.94 | 4 | 0 |  | 1743.52 | 0 | 0
- | 4th Floor Corridor South | 0 | 0 |  | 1677.4 | 38 | 0 |  | 13419.2 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Laura H. Carnell Elementary School | [7 empty] | 0 | 0 | 0
| Laura H. Carnell Little School House | House Fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | LSH Retest | [6 empty] | 0 | 0 | 0
| EMCOR | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Main Building | [8 empty] | 0 | 0 | 0
- | Basement Corridor | 0 | 0 |  | 450 | 10 | 0 | Unit Ventilator | 3600 | 0 | 0
- | Gym Office | 0 | 0 |  | 144 | 3 | 0 | N/A | 1152 | 0 | 0
B-3 | Art | 0 | 0 |  | 920 | 20 | 0 | House Fan | 7360 | 0 | 0
B-4 | Music | 0 | 0 |  | 660 | 15 | 0 | House Fan | 5280 | 0 | 0
B1 | Counselors | 0 | 0 |  | 630 | 14 | 0 | House Fan | 5040 | 0 | 0
B2 | Family Resource | 0 | 0 |  | 1023 | 23 | 0 | House Fan | 8184 | 0 | 0
B5 | Classroom | 519 | 34 |  | 800 | 18 | 18 | Unit Ventilator | 6400 | 4.8656 | 2
B6 | Classroom | 110 | 7 |  | 800 | 18 | 7 | Unit Ventilator | 6400 | 1.0312 | 1
B7 | Classroom | 421 | 28 |  | 800 | 18 | 18 | Unit Ventilator | 6400 | 3.9469 | 1
- | 1st flr Corridor |  | 0 |  | 828 | 18 | 0 | Unit Ventilator | 6624 | 0 | 0
- | Main Office | 0 | 0 |  | 483 | 10 | 0 | N/A | 3864 | 0 | 0
- | Principal's Office | 0 | 0 |  | 304 | 6 | 0 | N/A | 2432 | 0 | 0
- | 1st Flr Security | 0 | 0 |  | 81 | 1 | 0 | N/A | 648 | 0 | 0
- | 1st Flr Counselors | 0 | 0 |  | 126 | 2 | 0 | N/A | 1008 | 0 | 0
- | 1st Flr Office |  | 0 |  | 216 | 4 | 0 | N/A | 1728 | 0 | 0
101 | Classroom | 0 | 0 | Yes | 957 | 21 | 21 | House Fan | 7656 | 0 | 0
102 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan | 6960 | 0 | 0
103 | Classroom | 0 | 0 |  | 899 | 20 | 0 | House Fan | 7192 | 0 | 0
104 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | House Fan | 6960 | 0 | 0
105 | Classroom | 0 | 0 |  | 900 | 20 | 0 | House Fan | 7200 | 0 | 0
106 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan | 6960 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 | House Fan | 7200 | 0 | 0
108 | Classroom | 0 | 0 | Yes | 930 | 21 | 21 | House Fan | 7440 | 0 | 0
109 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 | House Fan | 7200 | 0 | 0
110 | Classroom | 0 | 0 |  | 960 | 21 | 0 | House Fan | 7680 | 0 | 0
111 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
112 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
113 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
- | 2nd flr Corridor |  | 0 |  | 828 | 18 | 0 | Unit Ventilator | 6624 | 0 | 0
- | 2nd Flr Nurse's | 0 | 0 |  | 216 | 4 | 0 | N/A | 1728 | 0 | 0
- | 2nd Flr. Office | 0 | 0 |  | 126 | 2 | 0 | N/A | 1008 | 0 | 0
- | Asst. Principal | 0 | 0 |  | 312 | 7 | 0 | N/A | 2496 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 928 | 21 | 21 | House Fan | 7424 | 0 | 0
202 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan | 6960 | 0 | 0
203 | Classroom | 0 | 0 |  | 899 | 20 | 0 | House Fan | 7192 | 0 | 0
206 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan | 6960 | 0 | 0
207 | Classroom | 0 | 0 |  | 900 | 20 | 0 | House Fan | 7200 | 0 | 0
208 | Classroom | 0 | 0 | Yes | 930 | 21 | 21 | House Fan | 7440 | 0 | 0
209 | Computer Lab | 0 | 0 |  | 900 | 20 | 0 | House Fan | 7200 | 0 | 0
210 | Computer Lab | 0 | 0 |  | 960 | 21 | 0 | House Fan | 7680 | 0 | 0
211 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
212 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
213 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
217 | Teachers Lounge | 0 | 0 |  | 552 | 12 | 0 | N/A | 4416 | 0 | 0
- | 3rd flr Corridor |  | 0 |  | 828 | 18 | 0 | Unit Ventilator | 6624 | 0 | 0
- | 3rd Flr. Office | 0 | 0 |  | 126 | 2 | 0 | N/A | 1008 | 0 | 0
300 East | Classroom | 0 | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0
300 West | Office | 0 | 0 |  | 99 | 2 | 0 | N/A | 792 | 0 | 0
301 | Classroom | 0 | 0 | Yes | 928 | 21 | 21 | House Fan | 7424 | 0 | 0
302 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | House Fan | 6960 | 0 | 0
303 | Classroom | 0 | 0 |  | 899 | 20 | 0 | House Fan | 7192 | 0 | 0
304 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | House Fan | 6960 | 0 | 0
305 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 | House Fan | 7200 | 0 | 0
306 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan | 6960 | 0 | 0
307 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 | House Fan | 7200 | 0 | 0
308 | Classroom | 0 | 0 | Yes | 930 | 21 | 21 | House Fan | 7440 | 0 | 0
309 | Classroom | 0 | 0 |  | 900 | 20 | 0 | House Fan | 7200 | 0 | 0
310 | Classroom | 0 | 0 |  | 960 | 21 | 0 | House Fan | 7680 | 0 | 0
312 | Classroom | 544 | 36 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 5.3125 | 2
313 | Classroom | 479 | 31 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 4.6777 | 2
314 | Classroom | 65 | 4 |  | 768 | 17 | 4 | Unit Ventilator | 6144 | 0.63477 | 0
317 | Speech | 0 | 0 |  | 117 | 2 | 0 | N/A | 936 | 0 | 0
- | Auditorium | 0 | 0 |  | 3456 | 78 | 0 | House Fan | 27648 | 0 | 0
- | Cafeteria | 0 | 0 |  | 986 | 22 | 0 | N/A | 7888 | 0 | 0
- | Dean's Office | 0 | 0 |  | 108 | 2 | 0 | N/A | 864 | 0 | 0
- | Gym | 0 | 0 |  | 3306 | 75 | 0 | N/A | 26448 | 0 | 0
- | IMC Classroom | 0 | 0 |  | 1363 | 30 | 0 | House Fan | 10904 | 0 | 0
- | IMC Office | 0 | 0 |  | 95 | 2 | 0 | House Fan | 760 | 0 | 0
Little School House | [8 empty] | 0 | 0 | 0
A-1 | Classroom | 293 | 19 |  | 1056 | 24 | 19 | AHU | 8448 | 2.081 | 1
A-3 | Classroom | 296 | 19 |  | 1056 | 24 | 19 | AHU | 8448 | 2.1023 | 1
A-2 | Classroom | 331 | 22 |  | 1056 | 24 | 22 | AHU | 8448 | 2.3509 | 1
A-4 | Classroom | 343 | 22 |  | 1056 | 24 | 22 | AHU | 8448 | 2.4361 | 1
A-5 | Classroom |  | 0 |  | 1056 | 24 | 0 | BCU | 8448 | 0 | 0
A-5 | Storage |  | 0 |  | 52 | 1 | 0 | BCU | 416 | 0 | 0
A-7 | Classroom |  | 0 |  | 1056 | 24 | 0 | BCU | 8448 | 0 | 0
A-6 | Classroom | 321 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.2798 | 1
A-8 | Classroom | 355 | 23 |  | 1056 | 24 | 23 | AHU | 8448 | 2.5213 | 1
A-9 | Classroom | 364 | 24 |  | 1056 | 24 | 24 | AHU | 8448 | 2.5852 | 1
A-11 | Classroom | 396 | 26 |  | 1056 | 24 | 24 | AHU | 8448 | 2.8125 | 1
A-10 | Classroom | 292 | 19 |  | 1056 | 24 | 19 | AHU | 8448 | 2.0739 | 1
A-12 | Classroom | 285 | 19 |  | 1056 | 24 | 19 | AHU | 8448 | 2.0241 | 1
- | Corridor | 0 | 0 |  | 1056 | 24 | 0 | AHU | 8448 | 0 | 0
- | Cafeteria | 2789 | 185 |  | 1850 | 42 | 42 | AHU | 14800 | 11.3068 | 3
- | BE Office | 76 | 5 |  | 88 | 2 | 2 | AHU | 704 | 6.4773 | 2
- | Main Office | 215 | 14 |  | 168 | 3 | 3 | AHU | 1344 | 9.5982 | 2
- | Vice Principal | 93 | 6 |  | 100 | 2 | 2 | AHU | 800 | 6.975 | 2
- | Counselor | 105 | 7 |  | 100 | 2 | 2 | AHU | 800 | 7.875 | 2
- | Comm Closet | 54 | 3 |  | 50 | 1 | 1 | AHU | 400 | 8.1 | 2
- | Storage | 73 | 4 |  | 250 | 5 | 4 | AHU | 2000 | 2.19 | 1
- | Lobby | 66 | 4 |  | 216 | 4 | 4 | AHU | 1728 | 2.2917 | 1
- | Store Room 1 Ceiling | 43 | 2 |  | 250 | 5 | 2 | BCU | 2000 | 1.29 | 1
- | Store Room 2 | 26 | 1 |  | 70 | 1 | 1 | BCU | 560 | 2.7857 | 1
- | Store Room 3 | 27 | 1 |  | 70 | 1 | 1 | BCU | 560 | 2.8929 | 1
- | Janitors Closet | 20 | 1 |  | 32 | 0 | 0 | BCU | 256 | 4.6875 | 2
- | Storage next to B.E. | 22 | 1 |  | 99 | 2 | 1 | BCU | 792 | 1.6667 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | George Washington Carver High School for Engineering and Science | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Retest | Devine 2nd Retest | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Carver Commons- in IMC Room 147 | 0 | 0 |  | 96 | 2 | 0 |  | 768 | 0 | 0
2 | Carver Commons- in IMC Room 147 | 0 | 0 |  | 147 | 3 | 0 |  | 1176 | 0 | 0
3 | Carver Commons- in IMC Room 147 | 0 | 0 |  | 143 | 3 | 0 |  | 1144 | 0 | 0
4 | Carver Commons- in IMC Room 147 | 0 | 0 |  | 99 | 2 | 0 |  | 792 | 0 | 0
104 | Room | 783 | 52 |  | 625 | 14 | 14 |  | 5000 | 9.396 | 2
107 | Room | 158 | 10 |  | 704 | 16 | 10 |  | 5632 | 1.6832 | 1
114 | Room | 0 | 0 |  | 840 | 19 | 0 |  | 6720 | 0 | 0
115 | Room | 305 | 20 |  | 840 | 19 | 19 |  | 6720 | 2.7232 | 1
123 | Room | 181 | 12 |  | 920 | 20 | 12 |  | 7360 | 1.4755 | 1
124 | Room | 85 | 5 |  | 480 | 10 | 5 |  | 3840 | 1.3281 | 1
125 | Room | 643 | 42 |  | 1753 | 39 | 39 |  | 14024 | 2.751 | 1
126 | Room | 399 | 26 |  | 750 | 17 | 17 |  | 6000 | 3.99 | 1
134 | Room | 221 | 14 |  | 566 | 12 | 12 |  | 4528 | 2.9284 | 1
135 | Room | 0 | 0 |  | 400 | 9 | 0 |  | 3200 | 0 | 0
136 | Room | 86 | 5 |  | 200 | 4 | 4 |  | 1600 | 3.225 | 1
137 | Womens Room | 0 | 0 |  | 280 | 6 | 0 |  | 2240 | 0 | 0
138 | Weight Room | 417 | 27 |  | 1500 | 34 | 27 |  | 12000 | 2.085 | 1
139 | PE Office | 0 | 0 |  | 176 | 4 | 0 |  | 1408 | 0 | 0
139 | Training Room | 0 | 0 |  | 139 | 3 | 0 |  | 1112 | 0 | 0
139A | Lavatory | 0 | 0 |  | 96 | 2 | 0 |  | 768 | 0 | 0
144 | Room | 235 | 15 |  | 1311 | 29 | 15 |  | 10488 | 1.3444 | 1
145 | Env. Science Lab | 373 | 24 |  | 2349 | 53 | 24 |  | 18792 | 1.1909 | 1
147 | IMC | 1282 | 85 |  | 4087 | 92 | 85 |  | 32696 | 2.3526 | 1
201 | Room | 0 | 0 |  | 1200 | 27 | 0 |  | 9600 | 0 | 0
202 | Room | 371 | 24 |  | 864 | 19 | 19 |  | 6912 | 3.2205 | 1
203 | Room | 294 | 19 |  | 864 | 19 | 19 |  | 6912 | 2.5521 | 1
209 | Room | 401 | 26 |  | 952 | 21 | 21 |  | 7616 | 3.1591 | 1
211 | Room | 367 | 24 |  | 960 | 21 | 21 |  | 7680 | 2.8672 | 1
212 | Room | 292 | 19 |  | 960 | 21 | 19 |  | 7680 | 2.2812 | 1
213 | Room | 295 | 19 |  | 960 | 21 | 19 |  | 7680 | 2.3047 | 1
214 | Room | 0 | 0 |  | 960 | 21 | 0 |  | 7680 | 0 | 0
217 | Room | 271 | 18 |  | 1250 | 28 | 18 |  | 10000 | 1.626 | 1
220 | Room | 0 | 0 |  | 1408 | 32 | 0 |  | 11264 | 0 | 0
221 | Room | 95 | 6 |  | 1680 | 38 | 6 |  | 13440 | 0.42411 | 0
222 | Room | 201 | 13 |  | 1200 | 27 | 13 |  | 9600 | 1.2563 | 1
224 | Room | 392 | 26 |  | 1680 | 38 | 26 |  | 13440 | 1.75 | 1
226 | Room | 309 | 20 |  | 1680 | 38 | 20 |  | 13440 | 1.3795 | 1
229 | Room | 0 | 0 |  | 1600 | 36 | 0 |  | 12800 | 0 | 0
230 | Room | 162 | 10 |  | 1680 | 38 | 10 |  | 13440 | 0.72321 | 0
301 | Room | 0 | 0 |  | 1157 | 26 | 0 |  | 9256 | 0 | 0
302 | Room | 834 | 55 |  | 864 | 19 | 19 |  | 6912 | 7.2396 | 2
303 | Room | 281 | 18 |  | 864 | 19 | 18 |  | 6912 | 2.4392 | 1
309 | Room | 462 | 30 |  | 864 | 19 | 19 |  | 6912 | 4.0104 | 2
311 | Room | 533 | 35 |  | 1041 | 23 | 23 |  | 8328 | 3.8401 | 1
312 | Room | 201 | 13 |  | 1118 | 25 | 13 |  | 8944 | 1.3484 | 1
313 | Room | 243 | 16 |  | 816 | 18 | 16 |  | 6528 | 2.2335 | 1
314 | Room | 389 | 25 |  | 816 | 18 | 18 |  | 6528 | 3.5754 | 1
317 | Room | 0 | 0 |  | 816 | 18 | 0 |  | 6528 | 0 | 0
318 | Room | 170 | 11 |  | 768 | 17 | 11 |  | 6144 | 1.6602 | 1
320 | Room | 142 | 9 |  | 1056 | 24 | 9 |  | 8448 | 1.0085 | 1
321 | Room | 487 | 32 |  | 1200 | 27 | 27 |  | 9600 | 3.0438 | 1
322 | Room | 460 | 30 |  | 1200 | 27 | 27 |  | 9600 | 2.875 | 1
324 | Room | 75 | 5 |  | 1200 | 27 | 5 |  | 9600 | 0.46875 | 0
327 | Room | 226 | 15 |  | 1519 | 34 | 15 |  | 12152 | 1.1159 | 1
329 | Room | 400 | 26 |  | 1440 | 32 | 26 |  | 11520 | 2.0833 | 1
- | Art Room | 756 | 50 |  | 2500 | 56 | 50 |  | 20000 | 2.268 | 1
- | Auditorium | 4245 | 283 |  | 5612 | 127 | 127 |  | 44896 | 5.6731 | 2
- | Cafeteria | 6739 | 449 |  | 3826 | 86 | 86 |  | 30608 | 13.2103 | 3
- | Dance Area | 104 | 6 |  | 1920 | 43 | 6 |  | 15360 | 0.40625 | 0
- | Dance Studio | 1644 | 109 |  | 336 | 7 | 7 |  | 2688 | 36.6964 | 4
- | Gymnasium | 13040 | 869 |  | 8949 | 203 | 203 |  | 71592 | 10.9286 | 3
- | Female Student Locker Room | 579 | 38 |  | 1200 | 27 | 27 |  | 9600 | 3.6187 | 1
- | Male Student Locker Room | 176 | 11 |  | 1200 | 27 | 11 |  | 9600 | 1.1 | 1
- | Female Staff Locker Room | 52 | 3 |  | 117 | 2 | 2 |  | 936 | 3.3333 | 1
- | Male Staff Locker Room | 446 | 29 |  | 112 | 2 | 2 |  | 896 | 29.8661 | 4
- | Male Staff Locker Room | 446 | 29 |  | 112 | 2 | 2 |  | 896 | 29.8661 | 4
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-06 | [7 empty] | 0 | 0 | 0
School: | Lewis C. Cassidy Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Boy's Gang Bathroom | 560 | 37 |  | 575 | 13 | 13 | House Fan | 4600 | 7.3043 | 2
- | Girl's Gang Bathroom | 326 | 21 |  | 396 | 9 | 9 | House Fan | 3168 | 6.1742 | 2
B | Teachers Lounge | 384 | 25 |  | 308 | 7 | 7 | House Fan | 2464 | 9.3506 | 2
B2 | Office | 0 | 0 | Yes | 748 | 17 | 17 |  | 5984 | 0 | 0
B3 | Classroom | 741 | 49 |  | 742 | 16 | 16 | House Fan | 5936 | 7.4899 | 2
B7 | Gym | 0 | 0 | Yes | 3872 | 88 | 88 | N/A | 30976 | 0 | 0
B8 | Classroom | 527 | 35 |  | 968 | 22 | 22 | House Fan | 7744 | 4.0832 | 2
101 | Classroom | 542 | 36 |  | 660 | 15 | 15 | House Fan | 5280 | 6.1591 | 2
102 | Classroom | 478 | 31 |  | 660 | 15 | 15 | House Fan | 5280 | 5.4318 | 2
103 | Classroom | 538 | 35 |  | 660 | 15 | 15 | House Fan | 5280 | 6.1136 | 2
104 | Classroom | 473 | 31 |  | 616 | 14 | 14 | House Fan | 4928 | 5.7589 | 2
105 | Office | 0 | 0 |  | 132 | 3 | 0 | N/A | 1056 | 0 | 0
106 | Classroom | 682 | 45 |  | 704 | 16 | 16 | House Fan | 5632 | 7.2656 | 2
107 | Classroom | 741 | 49 |  | 616 | 14 | 14 | House Fan | 4928 | 9.0219 | 2
108 | Classroom | 812 | 54 |  | 660 | 15 | 15 | House Fan | 5280 | 9.2273 | 2
109 | Classroom | 734 | 48 |  | 660 | 15 | 15 | House Fan | 5280 | 8.3409 | 2
201 | Nurses Office | 0 | 0 | Yes | 176 | 4 | 4 | N/A | 1408 | 0 | 0
202 | Classroom | 551 | 36 |  | 792 | 18 | 18 | House Fan | 6336 | 5.2178 | 2
203 | Classroom | 389 | 25 |  | 660 | 15 | 15 | House Fan | 5280 | 4.4205 | 2
204 | Classroom | 471 | 31 |  | 660 | 15 | 15 | House Fan | 5280 | 5.3523 | 2
205 | Teachers Lounge | 0 | 0 | Yes | 308 | 7 | 7 | N/A | 2464 | 0 | 0
206 | Asst Principal | 0 | 0 | Yes | 207 | 4 | 4 | N/A | 1656 | 0 | 0
207 | Classroom | 525 | 35 |  | 660 | 15 | 15 | House Fan | 5280 | 5.9659 | 2
208 | Small Classroom | 0 | 0 | Yes | 220 | 5 | 5 | House Fan | 1760 | 0 | 0
209 | Classroom | 675 | 45 |  | 660 | 15 | 15 | House Fan | 5280 | 7.6705 | 2
210 | Classroom | 551 | 36 |  | 616 | 14 | 14 | House Fan | 4928 | 6.7086 | 2
211 | Classroom | 565 | 37 |  | 660 | 15 | 15 | House Fan | 5280 | 6.4205 | 2
212 | Classroom | 611 | 40 |  | 660 | 15 | 15 | House Fan | 5280 | 6.9432 | 2
213 | Office | 0 | 0 | Yes | 264 | 6 | 6 | N/A | 2112 | 0 | 0
301 | Office | 0 | 0 | Yes | 264 | 6 | 6 | N/A | 2112 | 0 | 0
302 | Classroom | 562 | 37 |  | 704 | 16 | 16 | House Fan | 5632 | 5.9872 | 2
303 | Classroom | 430 | 28 |  | 704 | 16 | 16 | House Fan | 5632 | 4.581 | 2
304 | Classroom | 392 | 26 |  | 616 | 14 | 14 | House Fan | 4928 | 4.7727 | 2
305 | Classroom | 507 | 33 |  | 616 | 14 | 14 | House Fan | 4928 | 6.1729 | 2
306 | Classroom | 112 | 7 | Yes | 704 | 16 | 16 | House Fan | 5632 | 1.1932 | 1
307 | Classroom | 465 | 31 |  | 748 | 17 | 17 | House Fan | 5984 | 4.6624 | 2
308 | Classroom | 378 | 25 |  | 899 | 20 | 20 | House Fan | 7192 | 3.1535 | 1
309 | Classroom | 378 | 25 |  | 704 | 16 | 16 | House Fan | 5632 | 4.027 | 2
310 | Classroom | 154 | 10 |  | 660 | 15 | 10 | House Fan | 5280 | 1.75 | 1
311 | Classroom | 518 | 34 |  | 616 | 14 | 14 | House Fan | 4928 | 6.3068 | 2
312 | Classroom | 718 | 47 |  | 616 | 14 | 14 | House Fan | 4928 | 8.7419 | 2
313 | Classroom | 550 | 36 |  | 660 | 15 | 15 | House Fan | 5280 | 6.25 | 2
314 | Classroom | 561 | 37 |  | 660 | 15 | 15 | House Fan | 5280 | 6.375 | 2
315 | Storage | 0 | 0 |  | 264 | 6 | 0 | N/A | 2112 | 0 | 0
- | Attwood Lunch Rm | 940 | 62 |  | 836 | 19 | 19 | House Fan | 6688 | 8.433 | 2
- | Auditorium | 1895 | 126 |  | 3608 | 82 | 82 | House Fan | 28864 | 3.9392 | 1
- | Backstage Office | 0 | 0 |  | 132 | 3 | 0 | N/A | 1056 | 0 | 0
- | Lunch Room | 660 | 44 |  | 880 | 20 | 20 | House Fan | 7040 | 5.625 | 2
- | Library | 732 | 48 |  | 704 | 16 | 16 | House Fan | 5632 | 7.7983 | 2
- | Main Office | 0 | 0 | Yes | 308 | 7 | 7 | N/A | 2464 | 0 | 0
- | Principal's Office | 0 | 0 | Yes | 132 | 3 | 3 | N/A | 1056 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-19 | [7 empty] | 0 | 0 | 0
School: | Joseph W. Catharine Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | Main Building Part 2 | [6 empty] | 0 | 0 | 0
School: | Joseph W. Catharine Elementary School Annex | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Main Building | [8 empty] | 0 | 0 | 0
- | Lunch | 503 | 33 |  | 1247 | 28 | 28 | Unit Ventilator | 9976 | 3.0253 | 1
- | Gym | 976 | 65 |  | 4544 | 103 | 65 | Unit Ventilator | 36352 | 1.6109 | 1
102 | Classroom | 270 | 18 |  | 681 | 15 | 15 | Unit Ventilator | 5448 | 2.9736 | 1
103 | Classroom | 313 | 20 |  | 550 | 12 | 12 | Unit Ventilator | 4400 | 4.2682 | 2
104 | Classroom | 670 | 44 |  | 953 | 21 | 21 | Unit Ventilator | 7624 | 5.2728 | 2
105 | Classroom | 0 | 0 | Yes | 953 | 21 | 21 | Unit Ventilator | 7624 | 0 | 0
106 | Classroom | 0 | 0 | Yes | 842 | 19 | 19 | Unit Ventilator | 6736 | 0 | 0
107 | Classroom | 627 | 41 |  | 1062 | 24 | 24 | Unit Ventilator | 8496 | 4.428 | 2
108 | Classroom | 307 | 20 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.7542 | 1
- | Office | 212 | 14 |  | 367 | 8 | 8 | Unit Ventilator | 2936 | 4.3324 | 2
201 | Classroom | 407 | 27 |  | 676 | 15 | 15 | Unit Ventilator | 5408 | 4.5155 | 2
202 | Classroom | 331 | 22 |  | 683 | 15 | 15 | Unit Ventilator | 5464 | 3.6347 | 1
203 | Classroom | 306 | 20 |  | 673 | 15 | 15 | Unit Ventilator | 5384 | 3.4101 | 1
204 | Classroom | 144 | 9 | Yes | 708 | 16 | 16 | Unit Ventilator | 5664 | 1.5254 | 1
205 | Classroom | 300 | 20 |  | 678 | 15 | 15 | Unit Ventilator | 5424 | 3.3186 | 1
206 | Classroom | 0 | 0 | Yes | 855 | 19 | 19 | Unit Ventilator | 6840 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 504 | 11 | 11 | Unit Ventilator | 4032 | 0 | 0
208 | Classroom | 0 | 0 | Yes | 672 | 15 | 15 | Unit Ventilator | 5376 | 0 | 0
209 | Classroom | 0 | 0 | Yes | 709 | 16 | 16 | Unit Ventilator | 5672 | 0 | 0
210 | Classroom | 0 | 0 | Yes | 705 | 16 | 16 | Unit Ventilator | 5640 | 0 | 0
211 | Classroom | 0 | 0 | Yes | 673 | 15 | 15 | Unit Ventilator | 5384 | 0 | 0
301 | Classroom | 0 | 0 | Yes | 684 | 15 | 15 | Unit Ventilator | 5472 | 0 | 0
302 | Classroom | 0 | 0 | Yes | 684 | 15 | 15 | Unit Ventilator | 5472 | 0 | 0
303 | Classroom | 0 | 0 | Yes | 679 | 15 | 15 | Unit Ventilator | 5432 | 0 | 0
304 | Classroom | 173 | 11 | Yes | 708 | 16 | 16 | Unit Ventilator | 5664 | 1.8326 | 1
305 | Classroom | 209 | 13 | Yes | 698 | 15 | 15 | Unit Ventilator | 5584 | 2.2457 | 1
306 | Classroom | 0 | 0 | Yes | 872 | 19 | 19 | Unit Ventilator | 6976 | 0 | 0
307 | Classroom | 0 | 0 | Yes | 675 | 15 | 15 | Unit Ventilator | 5400 | 0 | 0
308 | Classroom | 198 | 13 | Yes | 674 | 15 | 15 | Unit Ventilator | 5392 | 2.2033 | 1
309 | Classroom | 284 | 18 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 3.0213 | 1
310 | Classroom | 297 | 19 |  | 707 | 16 | 16 | Unit Ventilator | 5656 | 3.1506 | 1
311 | Classroom | 0 | 0 | Yes | 674 | 15 | 15 | Unit Ventilator | 5392 | 0 | 0
- | Principal's office | 0 | 0 | Yes | 359 | 8 | 8 |  | 2872 | 0 | 0
- | Nurse office | 0 | 0 | Yes | 324 | 7 | 7 |  | 2592 | 0 | 0
- | Counselor Office | 0 | 0 | Yes | 109 | 2 | 2 |  | 872 | 0 | 0
Joseph W. Catherine Elementary School Annex | [8 empty] | 0 | 0 | 0
100 | Office |  | 0 | Yes | 273 | 6 | 6 | N/A | 2184 | 0 | 0
102 | K-1 Room |  | 0 | Yes | 680 | 15 | 15 | N/A | 5440 | 0 | 0
104 | K-2 Room |  | 0 | Yes | 714 | 16 | 16 | N/A | 5712 | 0 | 0
213 | K-3 |  | 0 | Yes | 1056 | 24 | 24 | N/A | 8448 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-28 | [7 empty] | 0 | 0 | 0
School: | Cayuga Elementary School (former St. Henry’s) | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Devine Brothers Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | classroom | 355 | 23 |  | 830 | 18 | 18 | Unit Ventilator | 6640 | 3.2078 | 1
102 | classroom | 375 | 25 |  | 740 | 16 | 16 | Unit Ventilator | 5920 | 3.8007 | 1
103 | classroom | 315 | 21 |  | 795 | 18 | 18 | Unit Ventilator | 6360 | 2.9717 | 1
104 | classroom | 280 | 18 |  | 796 | 18 | 18 | Unit Ventilator | 6368 | 2.6382 | 1
105 | Nurse's Office |  | 0 | Yes | 330 | 7 | 7 | N/A | 2640 | 0 | 0
106 | classroom | 275 | 18 |  | 403 | 9 | 9 | Unit Ventilator | 3224 | 5.1179 | 2
117 | classroom | 736 | 49 |  | 806 | 18 | 18 | Unit Ventilator | 6448 | 6.8486 | 2
118 | classroom | 625 | 41 |  | 688 | 15 | 15 | Unit Ventilator | 5504 | 6.8132 | 2
119 | classroom | 586 | 39 |  | 845 | 19 | 19 | Unit Ventilator | 6760 | 5.2012 | 2
120 | classroom | 335 | 22 |  | 670 | 15 | 15 | Unit Ventilator | 5360 | 3.75 | 1
201 | classroom | 325 | 21 |  | 830 | 18 | 18 | Unit Ventilator | 6640 | 2.9367 | 1
202 | classroom | 305 | 20 |  | 740 | 16 | 16 | Unit Ventilator | 5920 | 3.0912 | 1
203 | classroom | 380 | 25 |  | 795 | 18 | 18 | Unit Ventilator | 6360 | 3.5849 | 1
204 | classroom | 360 | 24 |  | 796 | 18 | 18 | Unit Ventilator | 6368 | 3.392 | 1
205 | classroom | 355 | 23 |  | 765 | 17 | 17 | Unit Ventilator | 6120 | 3.4804 | 1
206 | classroom | 310 | 20 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.9808 | 1
214 | classroom | 375 | 25 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 3.8633 | 1
215 | classroom | 365 | 24 |  | 693 | 15 | 15 | Unit Ventilator | 5544 | 3.9502 | 1
216 | classroom | 330 | 22 |  | 737 | 16 | 16 | Unit Ventilator | 5896 | 3.3582 | 1
217 | classroom | 1606 | 107 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 14.6533 | 3
301 | classroom | 345 | 23 |  | 830 | 18 | 18 | Unit Ventilator | 6640 | 3.1175 | 1
302 | classroom | 275 | 18 |  | 740 | 16 | 16 | Unit Ventilator | 5920 | 2.7872 | 1
303 | classroom | 380 | 25 |  | 795 | 18 | 18 | Unit Ventilator | 6360 | 3.5849 | 1
304 | classroom | 380 | 25 |  | 796 | 18 | 18 | Unit Ventilator | 6368 | 3.5804 | 1
305 | classroom | 553 | 36 |  | 765 | 17 | 17 | Unit Ventilator | 6120 | 5.4216 | 2
306 | classroom | 315 | 21 |  | 790 | 17 | 17 | Unit Ventilator | 6320 | 2.9905 | 1
- | Gym | 1213 | 80 |  | 2754 | 62 | 62 | AHU | 22032 | 3.3034 | 1
- | Basement Corridor | 90 | 6 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | Main Entrance Corridor | 46 | 3 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | 1st Floor Corridor | 31 | 2 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | Cafeteria | 936 | 62 |  | 3432 | 78 | 62 | AHU | 27456 | 2.0455 | 1
Sheet Last Modified: | 2091-04-29 | [7 empty] | 0 | 0 | 0
School: | Central High School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Ceramic | 253 | 16 |  | 723 | 16 | 16 |  | 5784 | 2.6245 | 1
2 | Kiln | 58 | 3 |  | 128 | 2 | 2 |  | 1024 | 3.3984 | 1
3 | Drafting Studio | 403 | 26 |  | 1366 | 31 | 26 |  | 10928 | 2.2127 | 1
4 | Fashion | 40 | 2 |  | 290 | 6 | 2 |  | 2320 | 1.0345 | 1
5 | Office | 64 | 4 |  | 349 | 7 | 4 |  | 2792 | 1.3754 | 1
6 | Photography | 32 | 2 |  | 171 | 3 | 2 |  | 1368 | 1.4035 | 1
7 | Computer Lab | 31 | 2 |  | 148 | 3 | 2 |  | 1184 | 1.5709 | 1
8 | Art Studio | 356 | 23 |  | 1452 | 33 | 23 |  | 11616 | 1.8388 | 1
9 | Printing Studio | 70 | 4 |  | 390 | 8 | 4 |  | 3120 | 1.3462 | 1
12 | Classroom | 333 | 22 |  | 840 | 19 | 19 |  | 6720 | 2.9732 | 1
13 | Classroom | 388 | 25 |  | 709 | 16 | 16 |  | 5672 | 4.1044 | 2
82 | Classroom | 301 | 20 |  | 1714 | 38 | 20 |  | 13712 | 1.3171 | 1
84 | Classroom | 300 | 20 |  | 1531 | 34 | 20 |  | 12248 | 1.4696 | 1
85 | Classroom | 300 | 20 |  | 1594 | 36 | 20 |  | 12752 | 1.4115 | 1
89 | Classroom | 389 | 25 |  | 1327 | 30 | 25 |  | 10616 | 2.1986 | 1
95 | Classroom | 604 | 40 |  | 1307 | 29 | 29 |  | 10456 | 3.466 | 1
97 | Classroom | 605 | 40 |  | 1216 | 27 | 27 |  | 9728 | 3.7315 | 1
98 | Classroom | 428 | 28 |  | 1374 | 31 | 28 |  | 10992 | 2.3362 | 1
99 | Classroom | 432 | 28 |  | 1258 | 28 | 28 |  | 10064 | 2.5755 | 1
101 | Classroom | 376 | 25 |  | 876 | 19 | 19 |  | 7008 | 3.2192 | 1
102 | Classroom | 370 | 24 |  | 852 | 19 | 19 |  | 6816 | 3.257 | 1
103 | Classroom | 387 | 25 |  | 876 | 19 | 19 |  | 7008 | 3.3134 | 1
104 | Classroom | 316 | 21 |  | 700 | 15 | 15 |  | 5600 | 3.3857 | 1
105 | Classroom | 305 | 20 |  | 675 | 15 | 15 |  | 5400 | 3.3889 | 1
106 | Classroom | 283 | 18 |  | 687 | 15 | 15 |  | 5496 | 3.0895 | 1
107 | Classroom | 288 | 19 |  | 706 | 16 | 16 |  | 5648 | 3.0595 | 1
108 | Classroom | 329 | 21 |  | 700 | 15 | 15 |  | 5600 | 3.525 | 1
109 | Classroom | 0 | 0 |  | 675 | 15 | 0 |  | 5400 | 0 | 0
110 | Office | 248 | 16 |  | 339 | 7 | 7 |  | 2712 | 5.4867 | 2
111 | Classroom | 0 | 0 |  | 654 | 14 | 0 |  | 5232 | 0 | 0
119 | Classroom | 0 | 0 |  | 470 | 10 | 0 |  | 3760 | 0 | 0
120 | Classroom | 332 | 22 |  | 857 | 19 | 19 |  | 6856 | 2.9055 | 1
121 | Classroom | 366 | 24 |  | 694 | 15 | 15 |  | 5552 | 3.9553 | 1
122 | Classroom | 346 | 23 |  | 724 | 16 | 16 |  | 5792 | 3.5843 | 1
123 | Classroom | 297 | 19 |  | 694 | 15 | 15 |  | 5552 | 3.2097 | 1
124 | Classroom | 280 | 18 |  | 680 | 15 | 15 |  | 5440 | 3.0882 | 1
125 | Classroom | 427 | 28 |  | 683 | 15 | 15 |  | 5464 | 4.6889 | 2
126 | Classroom | 415 | 27 |  | 720 | 16 | 16 |  | 5760 | 4.3229 | 2
127 | Classroom | 290 | 19 |  | 722 | 16 | 16 |  | 5776 | 3.0125 | 1
136 | Classroom | 281 | 18 |  | 297 | 6 | 6 |  | 2376 | 7.096 | 2
138 | Principal | 176 | 11 |  | 235 | 5 | 5 |  | 1880 | 5.617 | 2
141 | Classroom | 293 | 19 |  | 690 | 15 | 15 |  | 5520 | 3.1848 | 1
142 | Office | 377 | 25 |  | 982 | 22 | 22 |  | 7856 | 2.8793 | 1
143 | Classroom | 405 | 27 |  | 700 | 15 | 15 |  | 5600 | 4.3393 | 2
144 | Roster Office | 179 | 11 |  | 652 | 14 | 11 |  | 5216 | 2.059 | 1
201 | Classroom | 0 | 0 |  | 530 | 12 | 0 |  | 4240 | 0 | 0
202 | Classroom | 288 | 19 |  | 834 | 18 | 18 |  | 6672 | 2.5899 | 1
203 | Classroom | 293 | 19 |  | 681 | 15 | 15 |  | 5448 | 3.2269 | 1
204 | Classroom | 288 | 19 |  | 692 | 15 | 15 |  | 5536 | 3.1214 | 1
205 | Classroom | 283 | 18 |  | 676 | 15 | 15 |  | 5408 | 3.1398 | 1
206 | Classroom | 344 | 22 |  | 681 | 15 | 15 |  | 5448 | 3.7885 | 1
207 | Classroom | 344 | 22 |  | 705 | 16 | 16 |  | 5640 | 3.6596 | 1
208 | Classroom | 286 | 19 |  | 682 | 15 | 15 |  | 5456 | 3.1452 | 1
209 | Classroom | 306 | 20 |  | 694 | 15 | 15 |  | 5552 | 3.3069 | 1
210 | Office | 226 | 15 |  | 336 | 7 | 7 |  | 2688 | 5.0446 | 2
211 | Classroom | 0 | 0 |  | 650 | 14 | 0 |  | 5200 | 0 | 0
224 | Classroom | 646 | 43 |  | 831 | 18 | 18 |  | 6648 | 5.8303 | 2
225 | Classroom | 289 | 19 |  | 800 | 18 | 18 |  | 6400 | 2.7094 | 1
226 | Classroom | 286 | 19 |  | 700 | 15 | 15 |  | 5600 | 3.0643 | 1
227 | Classroom | 0 | 0 |  | 693 | 15 | 0 |  | 5544 | 0 | 0
229 | Classroom | 377 | 25 |  | 676 | 15 | 15 |  | 5408 | 4.1827 | 2
230 | Classroom | 358 | 23 |  | 680 | 15 | 15 |  | 5440 | 3.9485 | 1
231 | Classroom | 0 | 0 |  | 680 | 15 | 0 |  | 5440 | 0 | 0
232 | Classroom | 315 | 21 |  | 638 | 14 | 14 |  | 5104 | 3.703 | 1
233 | Classroom | 246 | 16 |  | 597 | 13 | 13 |  | 4776 | 3.0905 | 1
244 | Classroom | 357 | 23 |  | 840 | 19 | 19 |  | 6720 | 3.1875 | 1
245 | Classroom | 316 | 21 |  | 840 | 19 | 19 |  | 6720 | 2.8214 | 1
246 | Classroom | 315 | 21 |  | 683 | 15 | 15 |  | 5464 | 3.459 | 1
247 | Classroom | 368 | 24 |  | 686 | 15 | 15 |  | 5488 | 4.0233 | 2
248 | Classroom | 401 | 26 |  | 705 | 16 | 16 |  | 5640 | 4.266 | 2
249 | Classroom | 379 | 25 |  | 694 | 15 | 15 |  | 5552 | 4.0958 | 2
250 | Classroom | 314 | 20 |  | 687 | 15 | 15 |  | 5496 | 3.4279 | 1
251 | Classroom | 458 | 30 |  | 705 | 16 | 16 |  | 5640 | 4.8723 | 2
252 | Classroom | 364 | 24 |  | 670 | 15 | 15 |  | 5360 | 4.0746 | 2
253 | Classroom | 314 | 20 |  | 330 | 7 | 7 |  | 2640 | 7.1364 | 2
302 | classroom | 483 | 32 |  | 1260 | 28 | 28 |  | 10080 | 2.875 | 1
303 | Classroom | 331 | 22 |  | 1145 | 26 | 22 |  | 9160 | 2.1681 | 1
304 | Classroom | 291 | 19 |  | 670 | 15 | 15 |  | 5360 | 3.2575 | 1
305 | Theater | 250 | 16 |  | 480 | 10 | 10 |  | 3840 | 3.9062 | 1
306 | Classroom | 430 | 28 |  | 661 | 15 | 15 |  | 5288 | 4.879 | 2
307 | Classroom | 478 | 31 |  | 657 | 14 | 14 |  | 5256 | 5.4566 | 2
308 | Classroom | 209 | 13 |  | 624 | 14 | 13 |  | 4992 | 2.512 | 1
309 | Classroom | 200 | 13 |  | 700 | 15 | 13 |  | 5600 | 2.1429 | 1
311 | Computer Lab | 64 | 4 |  | 827 | 18 | 4 |  | 6616 | 0.58041 | 0
321C | Storage | 210 | 14 |  | 157 | 3 | 3 |  | 1256 | 10.0318 | 3
323 | Classroom | 256 | 17 |  | 1082 | 24 | 17 |  | 8656 | 1.7745 | 1
325 | Computer Lab | 314 | 20 |  | 654 | 14 | 14 |  | 5232 | 3.6009 | 1
326 | Classroom | 294 | 19 |  | 654 | 14 | 14 |  | 5232 | 3.3716 | 1
327 | Computer Lab | 356 | 23 |  | 654 | 14 | 14 |  | 5232 | 4.0826 | 2
328 | Music Room | 289 | 19 |  | 647 | 14 | 14 |  | 5176 | 3.3501 | 1
329 | Computer Lab | 205 | 13 |  | 296 | 6 | 6 |  | 2368 | 5.1943 | 2
402 | Classroom | 625 | 41 |  | 941 | 21 | 21 |  | 7528 | 4.9814 | 2
403 | Classroom | 391 | 26 |  | 779 | 17 | 17 |  | 6232 | 3.7644 | 1
406 | Classroom | 531 | 35 |  | 1102 | 25 | 25 |  | 8816 | 3.6139 | 1
407 | Classroom | 510 | 34 |  | 1102 | 25 | 25 |  | 8816 | 3.471 | 1
Gym | Gym |  | 0 | Yes | 16550 | 376 | 376 |  | 132400 | 0 | 0
- | Office Break Rm | 240 | 16 |  | 170 | 3 | 3 |  | 1360 | 10.5882 | 3
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-05-03 | [7 empty] | 0 | 0 | 0
School: | George W. Childs Elementary School @ Barratt | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Classroom |  | 0 | Yes | 1575 | 35 | 35 |  | 12600 | 0 | 0
2 | Classroom |  | 0 | Yes | 1075 | 24 | 24 |  | 8600 | 0 | 0
3 | Head Start Kitchen |  | 0 | Yes | 696 | 15 | 15 | House Fan | 5568 | 0 | 0
4 | - |  | 0 |  | 1224 | 27 | 0 | House Fan | 9792 | 0 | 0
5 | - |  | 0 | Yes | 1035 | 23 | 23 | House Fan | 8280 | 0 | 0
8 | Classroom |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | 0 | 0
100B | VP's Office |  | 0 |  | 143 | 3 | 0 | House Fan | 1144 | 0 | 0
100C | Conference Room |  | 0 |  | 221 | 5 | 0 | House Fan | 1768 | 0 | 0
102 | Classroom |  | 0 | Yes | 1012 | 23 | 23 | House Fan | 8096 | 0 | 0
103 | Classroom |  | 0 | Yes | 1012 | 23 | 23 | House Fan | 8096 | 0 | 0
105 | Classroom |  | 0 | Yes | 851 | 19 | 19 | House Fan | 6808 | 0 | 0
105a | - |  | 0 | Yes | 575 | 13 | 13 | House Fan | 4600 | 0 | 0
106 | Classroom |  | 0 | Yes | 800 | 18 | 18 | House Fan | 6400 | 0 | 0
107 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
109A | Counsleor |  | 0 |  | 240 | 5 | 0 | House Fan | 1920 | 0 | 0
109C | Dicipline Room |  | 0 |  | 240 | 5 | 0 |  | 1920 | 0 | 0
118 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
119 | Nurse |  | 0 | Yes | 420 | 9 | 9 | House Fan | 3360 | 0 | 0
121 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
201 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
203 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
205 | Classroom |  | 0 | Yes | 460 | 10 | 10 | House Fan | 3680 | 0 | 0
206 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
207 | Classroom |  | 0 | Yes | 504 | 11 | 11 | House Fan | 4032 | 0 | 0
208 | Classroom |  | 0 | Yes | 912 | 20 | 20 | House Fan | 7296 | 0 | 0
209 | Classroom |  | 0 | Yes | 828 | 18 | 18 | House Fan | 6624 | 0 | 0
210 | - |  | 0 | Yes | 912 | 20 | 20 | House Fan | 7296 | 0 | 0
212 | Classroom |  | 0 | Yes | 902 | 20 | 20 | House Fan | 7216 | 0 | 0
214 | Classroom |  | 0 | Yes | 966 | 21 | 21 | House Fan | 7728 | 0 | 0
215 | Classroom |  | 0 | Yes | 748 | 17 | 17 | House Fan | 5984 | 0 | 0
216 | Classroom |  | 0 | Yes | 1012 | 23 | 23 | House Fan | 8096 | 0 | 0
217 | - |  | 0 | Yes | 1450 | 32 | 32 | House Fan | 11600 | 0 | 0
219 | Classroom |  | 0 |  | 1450 | 32 | 0 | House Fan | 11600 | 0 | 0
220 | Classroom |  | 0 | Yes | 1058 | 24 | 24 | House Fan | 8464 | 0 | 0
222 | - |  | 0 | Yes | 1058 | 24 | 24 | House Fan | 8464 | 0 | 0
224 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
224B | - |  | 0 | Yes | 689 | 15 | 15 | House Fan | 5512 | 0 | 0
226 | Classroom |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | 0 | 0
2nd Floor | Special Needs Changing Room |  | 0 | Yes | 180 | 4 | 4 |  | 1440 | 0 | 0
301 | Classroom |  | 0 | Yes | 989 | 22 | 22 | House Fan | 7912 | 0 | 0
302 | Classroom |  | 0 | Yes | 989 | 22 | 22 | House Fan | 7912 | 0 | 0
304 | - |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | 0 | 0
305 | - |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
306 | - |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
307 | Classroom |  | 0 | Yes | 552 | 12 | 12 | House Fan | 4416 | 0 | 0
308 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
309 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
310 | Classroom |  | 0 | Yes | 805 | 18 | 18 | House Fan | 6440 | 0 | 0
311 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
313 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
314 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
315 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
316 | Teacher's Lounge |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
401 | - |  | 0 |  | 989 | 22 | 0 | House Fan | 7912 | 0 | 0
402 | - |  | 0 | Yes | 989 | 22 | 22 | House Fan | 7912 | 0 | 0
404 | Classroom |  | 0 | Yes | 989 | 22 | 22 | House Fan | 7912 | 0 | 0
405 | Classroom |  | 0 |  | 460 | 10 | 0 | House Fan | 3680 | 0 | 0
406 | - |  | 0 | Yes | 989 | 22 | 22 | House Fan | 7912 | 0 | 0
407 | - |  | 0 | Yes | 828 | 18 | 18 | House Fan | 6624 | 0 | 0
408 | Classroom |  | 0 | Yes | 989 | 22 | 22 | House Fan | 7912 | 0 | 0
409 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
411 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
412 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
| Auditorium |  | 0 |  | 4128 | 93 | 0 |  | 33024 | 0 | 0
- | Cafeteria |  | 0 | Yes | 5512 | 125 | 125 | House Fan | 44096 | 0 | 0
- | Special Needs Classroom |  | 0 | Yes | 345 | 7 | 7 | House Fan | 2760 | 0 | 0
- | IMC |  | 0 | Yes | 1725 | 39 | 39 | House Fan | 13800 | 0 | 0
- | Main Office |  | 0 | Yes | 726 | 16 | 16 | House Fan | 5808 | 0 | 0
- | Music Room |  | 0 |  | 726 | 16 | 0 | House Fan | 5808 | 0 | 0
- | Principal |  | 0 | Yes | 312 | 7 | 7 | House Fan | 2496 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Roberto Clemente Middle School and The LINC High School | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Part 2 | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 126 | 8 |  | 664 | 15 | 8 | 1 Univent & 1 AHU | 5312 | 1.4232 | 1
102 | Classroom | 54 | 3 |  | 664 | 15 | 3 | Univent | 5312 | 0.60994 | 0
103 | Classroom | 95 | 6 |  | 664 | 15 | 6 | 1 Univent & 1 AHU | 5312 | 1.073 | 1
104 | Classroom | 54 | 3 |  | 664 | 15 | 3 | Univent | 5312 | 0.60994 | 0
106 | Classroom | 24 | 1 |  | 312 | 7 | 1 |  | 2496 | 0.57692 | 0
107 | Classroom | 179 | 11 |  | 682 | 15 | 11 | 1 Unitvent & 2 AHU | 5456 | 1.9685 | 1
108 | Classroom | 108 | 7 |  | 682 | 15 | 7 | 1 Univent & 1 AHU | 5456 | 1.1877 | 1
109 | Classroom | 83 | 5 |  | 672 | 15 | 5 | 1 Univent & 1 AHU | 5376 | 0.92634 | 0
110 | Classroom | 54 | 3 |  | 530 | 12 | 3 | 1 Univent & 1 AHU | 4240 | 0.76415 | 0
111 | Classroom | 86 | 5 |  | 984 | 22 | 5 | 1 Univent & 1 AHU | 7872 | 0.65549 | 0
112 | Classroom | 113 | 7 |  | 984 | 22 | 7 | 1 Univent & 1 AHU | 7872 | 0.86128 | 0
113 | Classroom | 116 | 7 |  | 987 | 22 | 7 | 1 Univent & 1 AHU | 7896 | 0.88146 | 0
114 | Classroom | 87 | 5 |  | 987 | 22 | 5 | 1 Univent & 1 AHU | 7896 | 0.66109 | 0
115 | Classroom | 87 | 5 |  | 987 | 22 | 5 | 1 Univent & 1 AHU | 7896 | 0.66109 | 0
116 | Classroom | 82 | 5 |  | 987 | 22 | 5 | 1 Univent & 1 AHU | 7896 | 0.6231 | 0
121 | - | 24 | 1 |  | 264 | 6 | 1 |  | 2112 | 0.68182 | 0
125 | Classroom | 24 | 1 |  | 132 | 3 | 1 |  | 1056 | 1.3636 | 1
126 | Classroom | 24 | 1 |  | 132 | 3 | 1 |  | 1056 | 1.3636 | 1
128 | Classroom | 24 | 1 |  | 120 | 2 | 1 |  | 960 | 1.5 | 1
129 | Classroom | 24 | 1 |  | 120 | 2 | 1 |  | 960 | 1.5 | 1
131 | Classroom | 24 | 1 |  | 120 | 2 | 1 |  | 960 | 1.5 | 1
132 | Classroom | 24 | 1 |  | 120 | 2 | 1 |  | 960 | 1.5 | 1
144 | Classroom | 11 | 0 |  | 109 | 2 | 0 |  | 872 | 0.75688 | 0
145 | Classroom | 11 | 0 |  | 70 | 1 | 0 |  | 560 | 1.1786 | 1
146 | Classroom | 10 | 0 |  | 286 | 6 | 0 |  | 2288 | 0.26224 | 0
147 | Classroom | 10 | 0 |  | 160 | 3 | 0 |  | 1280 | 0.46875 | 0
148 | Classroom | 10 | 0 |  | 80 | 1 | 0 |  | 640 | 0.9375 | 0
149 | Classroom | 10 | 0 |  | 90 | 2 | 0 |  | 720 | 0.83333 | 0
150 | Classroom | 10 | 0 |  | 108 | 2 | 0 |  | 864 | 0.69444 | 0
151 | Classroom | 10 | 0 |  | 70 | 1 | 0 |  | 560 | 1.0714 | 1
152 | Classroom | 10 | 0 |  | 108 | 2 | 0 |  | 864 | 0.69444 | 0
153 | Classroom | 10 | 0 |  | 108 | 2 | 0 |  | 864 | 0.69444 | 0
201 | Classroom | 91 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 6528 | 0.8364 | 0
202 | Classroom | 63 | 4 |  | 816 | 18 | 4 | 1 Univent & 1 AHU | 6528 | 0.57904 | 0
203 | Classroom | 86 | 5 |  | 816 | 18 | 5 | 1 Univent & 1 AHU | 6528 | 0.79044 | 0
204 | Classroom | 48 | 3 |  | 816 | 18 | 3 | 1 Univent & 1 AHU | 6528 | 0.44118 | 0
205 | Classroom | 96 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 6528 | 0.88235 | 0
206 | Classroom | 198 | 13 |  | 816 | 18 | 13 | 1 Univent & 1 AHU | 6528 | 1.8199 | 1
207 | Classroom | 199 | 13 |  | 816 | 18 | 13 | 1 Univent & 1 AHU | 6528 | 1.829 | 1
208 | Classroom | 69 | 4 |  | 816 | 18 | 4 | 1 Univent & 1 AHU | 6528 | 0.63419 | 0
209 | Classroom | 186 | 12 |  | 816 | 18 | 12 | 1 Univent & 1 AHU | 6528 | 1.7096 | 1
210 | Classroom | 91 | 6 |  | 792 | 18 | 6 | 1 Univent & 1 AHU | 6336 | 0.86174 | 0
211 | Classroom | 191 | 12 |  | 675 | 15 | 12 | 1 Univent & 1 AHU | 5400 | 2.1222 | 1
212 | Classroom | 62 | 4 |  | 624 | 14 | 4 | 1 Univent & 1 AHU | 4992 | 0.74519 | 0
213 | Classroom | 150 | 10 |  | 675 | 15 | 10 | 1 Univent & 1 AHU | 5400 | 1.6667 | 1
214 | Classroom | 67 | 4 |  | 775 | 17 | 4 | 1 Univent & 1 AHU | 6200 | 0.64839 | 0
215 | Classroom | 90 | 6 |  | 675 | 15 | 6 | 1 Univent & 1 AHU | 5400 | 1 | 0
216 | Classroom | 44 | 2 |  | 689 | 15 | 2 | 1 Univent & 1 AHU | 5512 | 0.47896 | 0
217 | Classroom | 74 | 4 |  | 684 | 15 | 4 | 1 Univent & 1 AHU | 5472 | 0.8114 | 0
218 | Classroom | 64 | 4 |  | 684 | 15 | 4 | 1 Univent & 1 AHU | 5472 | 0.70175 | 0
219 | Classroom | 163 | 10 |  | 768 | 17 | 10 | 1 Univent & 1 AHU | 6144 | 1.5918 | 1
220 | Classroom | 42 | 2 |  | 768 | 17 | 2 | 1 Univent & 1 AHU | 6144 | 0.41016 | 0
221 | Classroom | 68 | 4 |  | 768 | 17 | 4 | 1 Univent & 1 AHU | 6144 | 0.66406 | 0
222 | Classroom | 37 | 2 |  | 768 | 17 | 2 | Univent | 6144 | 0.36133 | 0
223 | Classroom | 417 | 27 |  | 768 | 17 | 17 | 1 Univent & 1 AHU | 6144 | 4.0723 | 2
224 | Classroom | 69 | 4 |  | 768 | 17 | 4 | 1 Univent & 1 AHU | 6144 | 0.67383 | 0
225 | Classroom | 136 | 9 |  | 768 | 17 | 9 | 1 Univent & 1 AHU | 6144 | 1.3281 | 1
226 | Classroom | 63 | 4 |  | 816 | 18 | 4 | 1 Univent & 1 AHU | 6528 | 0.57904 | 0
227 | Classroom | 125 | 8 |  | 744 | 16 | 8 | 1 Univent & 1 AHU | 5952 | 1.2601 | 1
228 | Classroom | 58 | 3 |  | 744 | 16 | 3 | 1 Univent & 1 AHU | 5952 | 0.58468 | 0
301 | Classroom | 121 | 8 |  | 816 | 18 | 8 | 1 Univent & 1 AHU | 6528 | 1.1121 | 1
302 | Classroom | 98 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 6528 | 0.90074 | 0
303 | Classroom | 69 | 4 |  | 816 | 18 | 4 | Univent | 6528 | 0.63419 | 0
304 | Classroom | 97 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 6528 | 0.89154 | 0
305 | Classroom | 69 | 4 |  | 816 | 18 | 4 | Univent | 6528 | 0.63419 | 0
306 | Classroom | 132 | 8 |  | 816 | 18 | 8 | 1 Univent & 1 AHU | 6528 | 1.2132 | 1
307 | Classroom | 172 | 11 |  | 816 | 18 | 11 | 1 Univent & 1 AHU | 6528 | 1.5809 | 1
308 | Classroom | 95 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 6528 | 0.87316 | 0
309 | Classroom | 238 | 15 |  | 816 | 18 | 15 | 1 Univent & 1 AHU | 6528 | 2.1875 | 1
310 | Classroom | 210 | 14 |  | 792 | 18 | 14 | 1 Univent & 1 AHU | 6336 | 1.9886 | 1
311 | Classroom | 153 | 10 |  | 675 | 15 | 10 | 1 Univent & 1 AHU | 5400 | 1.7 | 1
312 | Classroom | 103 | 6 |  | 624 | 14 | 6 | 1 Univent & 1 AHU | 4992 | 1.238 | 1
313 | Classroom | 69 | 4 |  | 675 | 15 | 4 | Univent | 5400 | 0.76667 | 0
314 | Classroom | 100 | 6 |  | 775 | 17 | 6 | 1 Univent & 1 AHU | 6200 | 0.96774 | 0
315 | Classroom | 198 | 13 |  | 675 | 15 | 13 | 1 Univent & 1 AHU | 5400 | 2.2 | 1
316 | Classroom | 97 | 6 |  | 689 | 15 | 6 | 1 Univent & 1 AHU | 5512 | 1.0559 | 1
317 | Classroom | 106 | 7 |  | 684 | 15 | 7 | 1 Univent & 1 AHU | 5472 | 1.1623 | 1
318 | Classroom | 96 | 6 |  | 684 | 15 | 6 | 1 Univent & 1 AHU | 5472 | 1.0526 | 1
319 | Classroom | 139 | 9 |  | 757 | 17 | 9 | 1 Univent & 1 AHU | 6056 | 1.3771 | 1
320 | Classroom | 106 | 7 |  | 768 | 17 | 7 | 1 Univent & 1 AHU | 6144 | 1.0352 | 1
321 | Classroom | 101 | 6 |  | 768 | 17 | 6 | 1 Univent & 1 AHU | 6144 | 0.98633 | 0
322 | Classroom | 160 | 10 |  | 768 | 17 | 10 | 1 Univent & 1 AHU | 6144 | 1.5625 | 1
323 | Classroom | 104 | 6 |  | 768 | 17 | 6 | 1 Univent & 1 AHU | 6144 | 1.0156 | 1
324 | Classroom | 99 | 6 |  | 768 | 17 | 6 | 1 Univent & 1 AHU | 6144 | 0.9668 | 0
325 | Classroom | 180 | 12 |  | 768 | 17 | 12 | 1 Univent & 1 AHU | 6144 | 1.7578 | 1
326 | Classroom | 94 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 6528 | 0.86397 | 0
327 | Classroom | 120 | 8 |  | 744 | 16 | 8 | 1 Univent & 1 AHU | 5952 | 1.2097 | 1
328 | Classroom | 252 | 16 |  | 744 | 16 | 16 | 1 Univent & 1 AHU | 5952 | 2.5403 | 1
503 | Classroom | 180 | 12 |  | 714 | 16 | 12 | 1 Univent & 1 AHU | 5712 | 1.8908 | 1
504 | Classroom | 252 | 16 |  | 849 | 19 | 16 | AHU | 6792 | 2.2261 | 1
505 | Classroom | 149 | 9 |  | 1456 | 33 | 9 | 1 Univent & 1 AHU | 11648 | 0.76751 | 0
507 | Classroom | 217 | 14 |  | 1458 | 33 | 14 | 1 Univent & 1 AHU | 11664 | 1.1163 | 1
508 | Classroom | 149 | 9 |  | 765 | 17 | 9 | Univent | 6120 | 1.4608 | 1
509 | Classroom | 204 | 13 |  | 738 | 16 | 13 | 1 Univent & 1 AHU | 5904 | 2.0732 | 1
510 | Classroom | 205 | 13 |  | 848 | 19 | 13 | 1 Univent & 1 AHU | 6784 | 1.8131 | 1
511 | Classroom | 226 | 15 |  | 740 | 16 | 15 | 1 Univent & 1 AHU | 5920 | 2.2905 | 1
512 | Classroom | 196 | 13 |  | 833 | 18 | 13 | 1 Univent & 1 AHU | 6664 | 1.7647 | 1
- | Auditorium | 1643 | 109 |  | 8015 | 182 | 109 |  | 64120 | 1.5374 | 1
- | Basement / Cafe | 62 | 4 |  | 5900 | 134 | 4 |  | 47200 | 0.078814 | 0
- | cubicle-1 | 48 | 3 |  | 437 | 9 | 3 |  | 3496 | 0.8238 | 0
- | GYM | 2494 | 166 |  | 2633 | 59 | 59 |  | 21064 | 7.1041 | 2
- | library | 288 | 19 |  | 2675 | 60 | 19 |  | 21400 | 0.80748 | 0
- | mail room | 24 | 1 |  | 153 | 3 | 1 |  | 1224 | 1.1765 | 1
- | Link Main Office | 201 | 13 |  | 809 | 18 | 13 |  | 6472 | 1.8634 | 1
- | Clemente Main Office | 24 | 1 |  | 240 | 5 | 1 |  | 1920 | 0.75 | 0
Sheet Last Modified: | 2021-04-01 | [7 empty] | 0 | 0 | 0
School: | Cleveland | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
109 | - |  | 0 | Yes | 850 | 19 | 19 |  | 6800 | 0 | 0
110 | - |  | 0 | Yes | 840 | 19 | 19 |  | 6720 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-19 | [7 empty] | 0 | 0 | 0
School: | Benjamin B. Comegys Elementary School | House fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine | EMCOR | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
K-1 | Classroom | 418 | 27 |  | 2240 | 50 | 27 | Unit Ventilator | 17920 | 1.3996 | 1
K-2 | Classroom | 462 | 30 |  | 2240 | 50 | 30 | Unit Ventilator | 17920 | 1.5469 | 1
100 | Classroom | 366 | 24 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.1771 | 1
101 | Classroom | 369 | 24 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 3.3263 | 1
103 | Classroom | 273 | 18 |  | 864 | 19 | 18 | Unit Ventilator | 6912 | 2.3698 | 1
104 | Classroom | 0 | 0 | Yes | 576 | 13 | 13 | Unit Ventilator | 4608 | 0 | 0
105 | Classroom | 231 | 15 |  | 864 | 19 | 15 | Unit Ventilator | 6912 | 2.0052 | 1
106 | Classroom | 710 | 47 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 7.9241 | 2
200 | Classroom | 251 | 16 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 2.8013 | 1
201 | Classroom | 0 | 0 | Yes | 365 | 8 | 8 | Radiator | 2920 | 0 | 0
202 | Classroom | 371 | 24 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 4.1406 | 2
203 | Classroom | 1226 | 81 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 13.683 | 3
204 | Classroom | 426 | 28 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 4.7545 | 2
205 | Classroom | 366 | 24 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 4.0848 | 2
206 | Classroom | 320 | 21 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 3.5714 | 1
207 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | Unit Ventilator | 5824 | 0 | 0
208 | Classroom | 283 | 18 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 2.9155 | 1
209 | Classroom | 288 | 19 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 2.967 | 1
210 | Classroom | 303 | 20 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 3.1216 | 1
211 | Classroom | 272 | 18 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 2.8022 | 1
212 | Classroom | 135 | 9 |  | 728 | 16 | 9 | Unit Ventilator | 5824 | 1.3908 | 1
213 | Classroom | 913 | 60 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 9.4059 | 2
214 | Classroom | 446 | 29 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 4.5948 | 2
300 | Classroom | 226 | 15 |  | 728 | 16 | 15 | Unit Ventilator | 5824 | 2.3283 | 1
301 | Classroom | 254 | 16 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 2.6168 | 1
302 | Classroom | 322 | 21 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 3.3173 | 1
303 | Classroom | 213 | 14 |  | 728 | 16 | 14 | Unit Ventilator | 5824 | 2.1944 | 1
304 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | Unit Ventilator | 5824 | 0 | 0
305 | Classroom | 858 | 57 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 8.8393 | 2
306 | Classroom | 883 | 58 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 9.0968 | 2
307 | Classroom | 209 | 13 |  | 728 | 16 | 13 | Unit Ventilator | 5824 | 2.1532 | 1
- | Art Classroom | 385 | 25 |  | 616 | 14 | 14 | Unit Ventilator | 4928 | 4.6875 | 2
- | Main Office |  | 0 | Yes | 936 | 21 | 21 | Radiator | 7488 | 0 | 0
- | Principal Office |  | 0 | Yes | 360 | 8 | 8 | Radiator | 2880 | 0 | 0
- | Counselor Office |  | 0 | Yes | 391 | 8 | 8 | Radiator | 3128 | 0 | 0
- | Nurse Office |  | 0 | Yes | 280 | 6 | 6 | Radiator | 2240 | 0 | 0
- | Auditorium | 271 | 18 |  | 4320 | 98 | 18 | AHU | 34560 | 0.47049 | 0
- | Gym / Cafe | 477 | 31 |  | 3672 | 83 | 31 | AHU | 29376 | 0.97426 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Watson Comly Elementary School | House fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Emcor Fluidics | 2nd Retest | 3rd Retest | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
102 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
102A | Classroom |  | 0 |  | 155 | 3 | 0 | House Fan | 1240 | 0 | 0
103 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
103A | Classroom |  | 0 |  | 164 | 3 | 0 | House Fan | 1312 | 0 | 0
104 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
105 | Classroom | 555 | 37 |  | 910 | 20 | 20 | Unit Ventilator | 7280 | 4.5742 | 2
106 | Classroom | 581 | 38 |  | 910 | 20 | 20 | Unit Ventilator | 7280 | 4.7885 | 2
107 | Classroom | 609 | 40 |  | 910 | 20 | 20 | Unit Ventilator | 7280 | 5.0192 | 2
108 | Classroom |  | 0 | Yes | 910 | 20 | 20 | Unit Ventilator | 7280 | 0 | 0
110 (ESOL) | Classroom |  | 0 | Yes | 439 | 9 | 9 |  | 3512 | 0 | 0
201 | Classroom |  | 0 | Yes | 435 | 9 | 9 |  | 3480 | 0 | 0
201A | Classroom |  | 0 | Yes | 306 | 6 | 6 | House Fan | 2448 | 0 | 0
202 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
203 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
204 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
205 | Classroom |  | 0 | Yes | 690 | 15 | 15 | Unit Ventilator | 5520 | 0 | 0
206 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | 0 | 0
207 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | 0 | 0
208 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | 0 | 0
209 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | 0 | 0
210 | Classroom |  | 0 | Yes | 812 | 18 | 18 | Unit Ventilator | 6496 | 0 | 0
211 | Classroom | 147 | 9 |  | 812 | 18 | 9 | Unit Ventilator | 6496 | 1.3578 | 1
212 | Classroom | 199 | 13 | Yes | 812 | 18 | 18 | Unit Ventilator | 6496 | 1.8381 | 1
213 | Classroom | 197 | 13 |  | 812 | 18 | 13 | Unit Ventilator | 6496 | 1.8196 | 1
214 | Classroom | 156 | 10 | Yes | 812 | 18 | 18 | Unit Ventilator | 6496 | 1.4409 | 1
215 | Classroom | 510 | 34 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 4.7106 | 2
216 | Classroom | 385 | 25 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.556 | 1
Art | 1st Fl Art Room | 342 | 22 |  | 1672 | 38 | 22 | Unit Ventilator | 13376 | 1.5341 | 1
- | Art Teacher Office | 205 | 13 |  | 308 | 7 | 7 | MUA | 2464 | 4.9919 | 2
- | Special Needs Room | 335 | 22 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.0942 | 1
- | Music Room | 383 | 25 |  | 594 | 13 | 13 | Unit Ventilator | 4752 | 4.8359 | 2
- | Office - Main | 183 | 12 |  | 169 | 3 | 3 | Unit Ventilator | 1352 | 8.1213 | 2
- | Office-2 |  | 0 |  | 176 | 4 | 0 |  | 1408 | 0 | 0
- | 2nd Floor Counselors Office |  | 0 | Yes | 182 | 4 | 4 |  | 1456 | 0 | 0
- | Counslor waiting rm |  | 0 |  | 104 | 2 | 0 |  | 832 | 0 | 0
- | Conference room 1st floor |  | 0 |  | 338 | 7 | 0 |  | 2704 | 0 | 0
- | Amy's Room |  | 0 |  | 156 | 3 | 0 |  | 1248 | 0 | 0
- | Principals Office | 0 | 0 | Yes | 196 | 4 | 4 | N/A | 1568 | 0 | 0
- | Break Room | 0 | 0 |  | 390 | 8 | 0 | N/A | 3120 | 0 | 0
- | 2nd Floor Staff room |  | 0 |  | 170 | 3 | 0 |  | 1360 | 0 | 0
- | Nurse 1st Floor | 90 | 6 |  | 150 | 3 | 3 | MUA | 1200 | 4.5 | 2
- | Nurse Office | 125 | 8 |  | 344 | 7 | 7 | MUA | 2752 | 2.7253 | 1
- | Nurse waiting |  | 0 | Yes | 202 | 4 | 4 |  | 1616 | 0 | 0
- | Cafeteria |  | 0 | Yes | 3321 | 75 | 75 |  | 26568 | 0 | 0
- | Gym |  | 0 |  | 4838 | 109 | 0 |  | 38704 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-20 | [7 empty] | 0 | 0 | 0
School: | Russell Conwell Middle School / Conwell Annex | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Conwell Main Building | [8 empty] | 0 | 0 | 0
B1 | - |  | 0 |  | 1575 | 35 | 0 |  | 12600 | 0 | 0
B2 | - |  | 0 |  | 782 | 17 | 0 |  | 6256 | 0 | 0
Main Office | Office |  | 0 | Yes | 396 | 9 | 9 |  | 3168 | 0 | 0
Nurse | Office |  | 0 | Yes | 473 | 10 | 10 |  | 3784 | 0 | 0
102 | - |  | 0 |  | 575 | 13 | 0 |  | 4600 | 0 | 0
107 | - |  | 0 |  | 120 | 2 | 0 |  | 960 | 0 | 0
108 | - |  | 0 | Yes | 816 | 18 | 18 |  | 6528 | 0 | 0
109 | - |  | 0 | Yes | 850 | 19 | 19 |  | 6800 | 0 | 0
111 | - |  | 0 | Yes | 1200 | 27 | 27 |  | 9600 | 0 | 0
103/104/ IMC | - |  | 0 |  | 4300 | 97 | 0 |  | 34400 | 0 | 0
201 | - |  | 0 |  | 850 | 19 | 0 |  | 6800 | 0 | 0
202 | - |  | 0 |  | 840 | 19 | 0 |  | 6720 | 0 | 0
204 | - |  | 0 |  | 625 | 14 | 0 |  | 5000 | 0 | 0
205 | - |  | 0 |  | 550 | 12 | 0 |  | 4400 | 0 | 0
206 | - |  | 0 |  | 875 | 19 | 0 |  | 7000 | 0 | 0
207 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
208 | - |  | 0 |  | 805 | 18 | 0 |  | 6440 | 0 | 0
209 | - |  | 0 | Yes | 850 | 19 | 19 |  | 6800 | 0 | 0
301 | - |  | 0 | Yes | 720 | 16 | 16 |  | 5760 | 0 | 0
302 | - |  | 0 |  | 805 | 18 | 0 |  | 6440 | 0 | 0
303 | - |  | 0 |  | 550 | 12 | 0 |  | 4400 | 0 | 0
304 | - |  | 0 |  | 625 | 14 | 0 |  | 5000 | 0 | 0
305 | - |  | 0 |  | 506 | 11 | 0 |  | 4048 | 0 | 0
306 | - |  | 0 |  | 875 | 19 | 0 |  | 7000 | 0 | 0
307 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
308 | - |  | 0 |  | 805 | 18 | 0 |  | 6440 | 0 | 0
309 | - |  | 0 | Yes | 575 | 13 | 13 |  | 4600 | 0 | 0
Conwell Annex | [8 empty] | 0 | 0 | 0
1 | - |  | 0 |  | 1276 | 29 | 0 |  | 10208 | 0 | 0
9 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | 0 | 0
102 | - |  | 0 |  | 2318 | 52 | 0 |  | 18544 | 0 | 0
104 | - |  | 0 |  | 870 | 19 | 0 |  | 6960 | 0 | 0
203 | - |  | 0 |  | 4800 | 109 | 0 |  | 38400 | 0 | 0
200 | - |  | 0 |  | 512 | 11 | 0 |  | 4096 | 0 | 0
301 | - |  | 0 |  | 840 | 19 | 0 |  | 6720 | 0 | 0
305 | - |  | 0 |  | 630 | 14 | 0 |  | 5040 | 0 | 0
306 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Cook-Wissahickon Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Devine Retest | Capital | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Classroom | 310 | 20 |  | 695 | 15 | 15 | Unit Ventilator | 5560 | 3.3453 | 1
2 | Classroom | 280 | 18 |  | 950 | 21 | 18 | Unit Ventilator | 7600 | 2.2105 | 1
3 | Classroom | 443 | 29 |  | 513 | 11 | 11 | Unit Ventilator | 4104 | 6.4766 | 2
15 | - | 131 | 8 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
016A | - | 131 | 8 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
101 | Classroom | 341 | 22 |  | 717 | 16 | 16 | Unit Ventilator | 5736 | 3.5669 | 1
102 | Classroom | 694 | 46 |  | 700 | 15 | 15 | Unit Ventilator | 5600 | 7.4357 | 2
103 | Classroom | 0 | 0 |  | 1495 | 33 | 0 | Unit Ventilator | 11960 | 0 | 0
105 | Classroom | 337 | 22 |  | 1005 | 22 | 22 | Unit Ventilator | 8040 | 2.5149 | 1
106 | Classroom | 342 | 22 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.776 | 1
107 | Classroom | 327 | 21 |  | 630 | 14 | 14 | Unit Ventilator | 5040 | 3.8929 | 1
108 | Classroom | 352 | 23 |  | 441 | 10 | 10 | Unit Ventilator | 3528 | 5.9864 | 2
109 | Classroom | 585 | 39 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 5.1557 | 2
110 | Classroom | 280 | 18 |  | 674 | 15 | 15 | Unit Ventilator | 5392 | 3.1157 | 1
111 | Classroom | 285 | 19 |  | 386 | 8 | 8 | Unit Ventilator | 3088 | 5.5376 | 2
200 | Classroom | 366 | 24 |  | 636 | 14 | 14 | Unit Ventilator | 5088 | 4.316 | 2
200A | Classroom | 324 | 21 |  | 485 | 11 | 11 | Unit Ventilator | 3880 | 5.0103 | 2
201 | Classroom | 310 | 20 |  | 447 | 10 | 10 | Unit Ventilator | 3576 | 5.2013 | 2
202 | Classroom | 418 | 27 |  | 730 | 16 | 16 | Unit Ventilator | 5840 | 4.2945 | 2
203 | Classroom | 0 | 0 |  | 813 | 18 | 0 | Unit Ventilator | 6504 | 0 | 0
204 | Classroom | 326 | 21 |  | 867 | 19 | 19 | Unit Ventilator | 6936 | 2.8201 | 1
205 | Classroom | 401 | 26 |  | 716 | 16 | 16 | Unit Ventilator | 5728 | 4.2004 | 2
206 | Classroom | 0 | 0 |  | 810 | 18 | 0 | Unit Ventilator | 6480 | 0 | 0
207 | Classroom | 284 | 18 |  | 456 | 10 | 10 | Unit Ventilator | 3648 | 4.6711 | 2
208 | Classroom | 336 | 22 |  | 422 | 9 | 9 | Unit Ventilator | 3376 | 5.9716 | 2
209 | Classroom | 300 | 20 |  | 731 | 16 | 16 | Unit Ventilator | 5848 | 3.078 | 1
210 | Classroom | 315 | 21 |  | 731 | 16 | 16 | Unit Ventilator | 5848 | 3.2319 | 1
211 | Classroom | 0 | 0 |  | 872 | 19 | 0 | Unit Ventilator | 6976 | 0 | 0
212 | Classroom | 440 | 29 |  | 365 | 8 | 8 | Unit Ventilator | 2920 | 9.0411 | 2
213 | Room | 310 | 20 |  | 525 | 11 | 11 | Air Handling Unit | 4200 | 4.4286 | 2
- | Cafeteria | 2213 | 147 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Copy Room | 340 | 22 |  | 199 | 4 | 4 | Air Handling Unit | 1592 | 12.8141 | 3
- | Gymnasium | 1486 | 99 |  | 4325 | 98 | 98 | Air Handling Unit | 34600 | 2.5769 | 1
- | Library | 1180 | 78 |  | 2998 | 68 | 68 | Air Handling Unit | 23984 | 2.952 | 1
- | Main Office | 789 | 52 |  | 396 | 9 | 9 | Air Handling Unit | 3168 | 14.9432 | 3
- | Pricipal's office | 498 | 33 |  | 358 | 8 | 8 | Air Handling Unit | 2864 | 10.433 | 3
- | Speech Room | 330 | 22 |  | 358 | 8 | 8 | Air Handling Unit | 2864 | 6.9134 | 2
- | Prep and lounge |  | 0 |  | 602 | 13 | 0 |  | 4816 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | Jay Cooke Elementary School | House Fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100C | Classroom | 293 | 19 |  | 506 | 11 | 11 | House Fan | 4048 | 4.3429 | 2
101C | Classroom | 411 | 27 |  | 543 | 12 | 12 | House Fan | 4344 | 5.6768 | 2
102C | Classroom | 284 | 18 |  | 833 | 18 | 18 | House Fan | 6664 | 2.557 | 1
103 | Classroom | 531 | 35 |  | 1082 | 24 | 24 | House Fan | 8656 | 3.6807 | 1
104 | Classroom | 279 | 18 |  | 809 | 18 | 18 | House Fan | 6472 | 2.5865 | 1
105 | Classroom | 369 | 24 |  | 695 | 15 | 15 | House Fan | 5560 | 3.982 | 1
108 | Classroom | 328 | 21 |  | 858 | 19 | 19 | House Fan | 6864 | 2.8671 | 1
109 | Office | 313 | 20 |  | 548 | 12 | 12 | House Fan | 4384 | 4.2838 | 2
110 | Classroom | 422 | 28 |  | 665 | 15 | 15 | House Fan | 5320 | 4.7594 | 2
110A | Office | 335 | 22 |  | 333 | 7 | 7 | House Fan | 2664 | 7.545 | 2
201 | Classroom | 335 | 22 |  | 711 | 16 | 16 | House Fan | 5688 | 3.5338 | 1
202 | Classroom | 515 | 34 |  | 674 | 15 | 15 | House Fan | 5392 | 5.7307 | 2
202A | Classroom | 347 | 23 |  | 1015 | 23 | 23 | House Fan | 8120 | 2.564 | 1
203 | Classroom | 388 | 25 |  | 717 | 16 | 16 | House Fan | 5736 | 4.0586 | 2
205 | Office | 0 | 0 |  | 304 | 6 | 0 | House Fan(partial Duct) | 2432 | 0 | 0
206 | Office | 0 | 0 | Yes | 240 | 5 | 5 | House Fan(partial Duct) | 1920 | 0 | 0
207 | Classroom | 435 | 29 |  | 726 | 16 | 16 | House Fan | 5808 | 4.4938 | 2
207A | Classroom | 330 | 22 |  | 334 | 7 | 7 | House Fan | 2672 | 7.4102 | 2
208 | Classroom | 433 | 28 |  | 673 | 15 | 15 | House Fan | 5384 | 4.8254 | 2
208A | Storage | 279 | 18 |  | 720 | 16 | 16 |  | 5760 | 2.9062 | 1
209 | Classroom | 363 | 24 |  | 693 | 15 | 15 | House Fan | 5544 | 3.9286 | 1
210 | Classroom | 378 | 25 |  | 650 | 14 | 14 | House Fan | 5200 | 4.3615 | 2
211 | Classroom | 748 | 49 |  | 211 | 4 | 4 | House Fan | 1688 | 26.5877 | 4
212 | Classroom | 736 | 49 |  | 774 | 17 | 17 | House Fan | 6192 | 7.1318 | 2
213 | Classroom | 807 | 53 |  | 720 | 16 | 16 | House Fan | 5760 | 8.4062 | 2
214 | Classroom | 846 | 56 |  | 727 | 16 | 16 | House Fan | 5816 | 8.7276 | 2
215 | Classroom | 797 | 53 |  | 748 | 17 | 17 | House Fan | 5984 | 7.9913 | 2
216 | Classroom | 811 | 54 |  | 762 | 17 | 17 | House Fan | 6096 | 7.9823 | 2
217 | Classroom | 496 | 33 |  | 670 | 15 | 15 | House Fan | 5360 | 5.5522 | 2
301 | Classroom | 278 | 18 |  | 711 | 16 | 16 | House Fan | 5688 | 2.9325 | 1
302 | Classroom | 522 | 34 |  | 690 | 15 | 15 | House Fan | 5520 | 5.6739 | 2
302A | Classroom | 273 | 18 |  | 405 | 9 | 9 | House Fan | 3240 | 5.0556 | 2
303 | Classroom | 581 | 38 |  | 714 | 16 | 16 | House Fan | 5712 | 6.1029 | 2
303A | Classroom | 284 | 18 | Yes | 405 | 9 | 9 | House Fan | 3240 | 5.2593 | 2
303B | Classroom | 0 | 0 | Yes | 216 | 4 | 4 |  | 1728 | 0 | 0
304 | Classroom | 633 | 42 |  | 882 | 20 | 20 | House Fan | 7056 | 5.3827 | 2
305 | Classroom | 437 | 29 |  | 907 | 20 | 20 | House Fan | 7256 | 3.6136 | 1
306 | Classroom | 456 | 30 |  | 815 | 18 | 18 | House Fan | 6520 | 4.1963 | 2
307 | Classroom | 541 | 36 |  | 798 | 18 | 18 | House Fan | 6384 | 5.0846 | 2
308 | Classroom | 469 | 31 |  | 1031 | 23 | 23 | House Fan | 8248 | 3.4117 | 1
309 | Classroom | 456 | 30 |  | 896 | 20 | 20 | House Fan | 7168 | 3.817 | 1
310 | Classroom | 441 | 29 |  | 769 | 17 | 17 | House Fan | 6152 | 4.301 | 2
311 | Classroom | 617 | 41 |  | 985 | 22 | 22 | House Fan | 7880 | 4.698 | 2
312 | Classroom | 333 | 22 |  | 713 | 16 | 16 | House Fan | 5704 | 3.5028 | 1
312A | Classroom | 325 | 21 |  | 332 | 7 | 7 | House Fan | 2656 | 7.3419 | 2
313 | Classroom | 393 | 26 |  | 666 | 15 | 15 | House Fan | 5328 | 4.4257 | 2
313A | Classroom | 307 | 20 |  | 703 | 15 | 15 | House Fan | 5624 | 3.2752 | 1
314 | Classroom | 365 | 24 |  | 709 | 16 | 16 | House Fan | 5672 | 3.8611 | 1
315 | Classroom | 271 | 18 |  | 650 | 14 | 14 | House Fan | 5200 | 3.1269 | 1
316 | Classroom | 673 | 44 |  | 765 | 17 | 17 | House Fan | 6120 | 6.598 | 2
317 | Classroom | 278 | 18 |  | 729 | 16 | 16 | House Fan | 5832 | 2.8601 | 1
318 | Classroom | 744 | 49 |  | 730 | 16 | 16 | House Fan | 5840 | 7.6438 | 2
319 | Classroom | 656 | 43 |  | 719 | 16 | 16 | House Fan | 5752 | 6.8428 | 2
320 | Classroom | 764 | 50 |  | 700 | 15 | 15 | House Fan | 5600 | 8.1857 | 2
321 | Classroom | 480 | 32 |  | 787 | 17 | 17 | House Fan | 6296 | 4.5743 | 2
322 | Classroom | 353 | 23 |  | 653 | 14 | 14 | House Fan | 5224 | 4.0544 | 2
- | Asst. Principal Waiting Room | 125 | 8 |  | 118 | 2 | 2 | House Fan | 944 | 7.9449 | 2
- | Asst. Principal Office |  | 0 | Yes | 110 | 2 | 2 |  | 880 | 0 | 0
- | Auditorium | 3875 | 258 |  | 3793 | 86 | 86 | House Fan | 30344 | 7.6621 | 2
- | Boy's Cafeteria | 1403 | 93 |  | 2254 | 51 | 51 | House Fan | 18032 | 4.6684 | 2
- | Boy's Gym | 1455 | 97 |  | 2806 | 63 | 63 | House Fan | 22448 | 3.889 | 1
- | Counselor Waiting Room | 134 | 8 |  | 123 | 2 | 2 | House Fan | 984 | 8.1707 | 2
- | Counselor Office 1 | 0 | 0 | Yes | 92 | 2 | 2 | House Fan | 736 | 0 | 0
- | Counselor Office 2 | 0 | 0 |  | 101 | 2 | 0 | House Fan | 808 | 0 | 0
- | Counselor Office 3 | 0 | 0 |  | 156 | 3 | 0 |  | 1248 | 0 | 0
- | Girl's Cafeteria | 1178 | 78 |  | 1944 | 44 | 44 | House Fan | 15552 | 4.5448 | 2
- | Girl's Gym | 1461 | 97 |  | 2806 | 63 | 63 | House Fan | 22448 | 3.905 | 1
- | Kitchen | 321 | 21 |  | 409 | 9 | 9 | House Fan | 3272 | 5.8863 | 2
- | Library | 1042 | 69 |  | 2053 | 46 | 46 | House Fan | 16424 | 3.8066 | 1
- | Nurse Office | 53 | 3 | Yes | 186 | 4 | 4 | House Fan | 1488 | 2.1371 | 1
- | Principal Office | 141 | 9 |  | 336 | 7 | 7 | House Fan | 2688 | 3.1473 | 1
- | Weight Room | 842 | 56 |  | 1027 | 23 | 23 | House Fan | 8216 | 6.149 | 2
- | CASST Office | 0 | 0 | Yes | 264 | 6 | 6 |  | 2112 | 0 | 0
- | SPECM Speech Therapy Office | 0 | 0 |  | 112 | 2 | 0 |  | 896 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | William Cramp Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
102 | Office | 27 | 1 |  | 133 | 3 | 1 |  | 1064 | 1.5226 | 1
102A | Office | 20 | 1 |  | 133 | 3 | 1 |  | 1064 | 1.1278 | 1
103 | Small Classroom | 103 | 6 |  | 533 | 12 | 6 |  | 4264 | 1.4493 | 1
106 | Classroom | 387 | 25 |  | 1033 | 23 | 23 | Unit Ventilator | 8264 | 2.8098 | 1
107 | Counselor | 137 | 9 |  | 385 | 8 | 8 |  | 3080 | 2.6688 | 1
108 | Classroom | 148 | 9 | Yes | 1220 | 27 | 27 | Unit Ventilator | 9760 | 0.90984 | 0
109 | Classroom | 405 | 27 |  | 1120 | 25 | 25 | Unit Ventilator | 8960 | 2.7121 | 1
110 | Classroom | 277 | 18 |  | 1543 | 35 | 18 | Unit Ventilator | 12344 | 1.3464 | 1
111 | Classroom | 318 | 21 |  | 1228 | 27 | 21 | Unit Ventilator | 9824 | 1.9422 | 1
112 | Classroom | 498 | 33 |  | 1170 | 26 | 26 |  | 9360 | 3.1923 | 1
112E | Office | 29 | 1 |  | 200 | 4 | 1 |  | 1600 | 1.0875 | 1
113 | Classroom | 338 | 22 |  | 1311 | 29 | 22 | Unit Ventilator | 10488 | 1.9336 | 1
13A | Classroom | 307 | 20 |  | 1073 | 24 | 20 |  | 8584 | 2.1459 | 1
13B | Classroom | 500 | 33 |  | 1294 | 29 | 29 | Unit Ventilator | 10352 | 2.898 | 1
114 | Art | 385 | 25 |  | 876 | 19 | 19 | AHU | 7008 | 3.2962 | 1
115 | Classroom | 283 | 18 |  | 1559 | 35 | 18 |  | 12472 | 1.3614 | 1
119 | Office | 0 | 0 |  | 459 | 10 | 0 |  | 3672 | 0 | 0
200 | Classroom | 763 | 50 |  | 967 | 21 | 21 | Unit Ventilator | 7736 | 5.9178 | 2
201 | Classroom | 605 | 40 |  | 825 | 18 | 18 | Unit Ventilator | 6600 | 5.5 | 2
202 | Counselor | 26 | 1 |  | 151 | 3 | 1 |  | 1208 | 1.2914 | 1
203/212 | Speech | 27 | 1 |  | 151 | 3 | 1 |  | 1208 | 1.3411 | 1
204 | Classroom | 527 | 35 |  | 1050 | 23 | 23 | Unit Ventilator | 8400 | 3.7643 | 1
205 | Classroom | 128 | 8 |  | 902 | 20 | 8 | Unit Ventilator | 7216 | 1.0643 | 1
206 | Classroom | 437 | 29 |  | 1030 | 23 | 23 | Unit Ventilator | 8240 | 3.182 | 1
207 | Classroom | 440 | 29 |  | 971 | 22 | 22 | Unit Ventilator | 7768 | 3.3986 | 1
208 | Classroom | 544 | 36 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 4.2947 | 2
209 | Classroom | 438 | 29 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 3.6622 | 1
210 | Classroom | 462 | 30 |  | 967 | 21 | 21 | Unit Ventilator | 7736 | 3.5832 | 1
211 | Classroom | 118 | 7 |  | 976 | 22 | 7 | Unit Ventilator | 7808 | 0.90676 | 0
300 | Classroom | 782 | 52 |  | 866 | 19 | 19 | Unit Ventilator | 6928 | 6.7725 | 2
301 | Classroom | 675 | 45 |  | 982 | 22 | 22 | Unit Ventilator | 7856 | 5.1553 | 2
302 | Counselor | 42 | 2 |  | 151 | 3 | 2 |  | 1208 | 2.0861 | 1
303/312 | Office | 48 | 3 |  | 151 | 3 | 3 |  | 1208 | 2.3841 | 1
304 | Classroom | 133 | 8 |  | 1050 | 23 | 8 | Unit Ventilator | 8400 | 0.95 | 0
304 | Classroom | 330 | 22 |  | 1050 | 23 | 22 |  | 8400 | 2.3571 | 1
305 | Classroom | 393 | 26 |  | 968 | 22 | 22 | Unit Ventilator | 7744 | 3.0449 | 1
306 | Classroom | 122 | 8 |  | 855 | 19 | 8 | Unit Ventilator | 6840 | 1.0702 | 1
306 | Classroom | 501 | 33 |  | 855 | 19 | 19 |  | 6840 | 4.3947 | 2
307 | Classroom | 713 | 47 |  | 965 | 21 | 21 | Unit Ventilator | 7720 | 5.5415 | 2
308 | Classroom | 320 | 21 |  | 772 | 17 | 17 | Unit Ventilator | 6176 | 3.1088 | 1
309 | Classroom | 471 | 31 |  | 941 | 21 | 21 | Unit Ventilator | 7528 | 3.754 | 1
310 | Classroom | 327 | 21 |  | 972 | 22 | 21 | Unit Ventilator | 7776 | 2.5231 | 1
311 | Classroom | 421 | 28 |  | 896 | 20 | 20 | Unit Ventilator | 7168 | 3.524 | 1
313 | Classroom | 329 | 21 |  | 368 | 8 | 8 | Unit Ventilator | 2944 | 6.7052 | 2
- | Gym | 42 | 2 |  | 4800 | 109 | 2 | AHU | 38400 | 0.065625 | 0
- | LGI | 736 | 49 |  | 697 | 15 | 15 | AHU | 5576 | 7.9197 | 2
- | Admin Office | 827 | 55 |  | 251 | 5 | 5 | AHU | 2008 | 24.7112 | 4
- | Cafeteria | 630 | 42 |  | 7287 | 165 | 42 | AHU | 58296 | 0.64841 | 0
- | Computer Lab | 498 | 33 |  | 2840 | 64 | 33 | Unit Ventilator | 22720 | 1.3151 | 1
- | Computer Room | 1015 | 67 |  | 2437 | 55 | 55 | AHU | 19496 | 3.1237 | 1
- | Conference/Storage | 110 | 7 |  | 199 | 4 | 4 |  | 1592 | 4.1457 | 2
- | IMC Office | 40 | 2 |  | 141 | 3 | 2 |  | 1128 | 2.1277 | 1
- | IMC Library | 36 | 2 |  | 2456 | 55 | 2 |  | 19648 | 0.10993 | 0
- | Kitchen | 1510 | 100 |  | 972 | 22 | 22 |  | 7776 | 11.6512 | 3
- | Library North Classroom | 537 | 35 |  | 2635 | 59 | 35 | Unit Ventilator | 21080 | 1.5285 | 1
- | Library South Classroom | 443 | 29 |  | 362 | 8 | 8 | Unit Ventilator | 2896 | 9.1782 | 2
- | Mail Room | 47 | 3 |  | 133 | 3 | 3 |  | 1064 | 2.6504 | 1
- | Main Office | 113 | 7 |  | 571 | 12 | 7 |  | 4568 | 1.4842 | 1
- | Nurse Office | 109 | 7 |  | 374 | 8 | 7 |  | 2992 | 2.1858 | 1
- | Nurse Exam Room | 44 | 2 |  | 128 | 2 | 2 |  | 1024 | 2.5781 | 1
- | Principals Office | 60 | 4 |  | 258 | 5 | 4 |  | 2064 | 1.7442 | 1
- | Teachers Lounge | 354 | 23 |  | 775 | 17 | 17 |  | 6200 | 3.4258 | 1
- | Vice Principal's Office | 64 | 4 |  | 213 | 4 | 4 |  | 1704 | 2.2535 | 1
Sheet Last Modified: | 2021-04-05 | [7 empty] | 0 | 0 | 0
School: | Kenneth C. Crossan Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Kindergarten Classroom | 580 | 38 |  | 1088 | 24 | 24 | House Fan | 8704 | 3.9982 | 1
2 | Classroom | 555 | 37 |  | 900 | 20 | 20 | House Fan | 7200 | 4.625 | 2
3 | Classroom | 522 | 34 |  | 930 | 21 | 21 | House Fan | 7440 | 4.2097 | 2
4 | Classroom | 299 | 19 |  | 840 | 19 | 19 | House Fan | 6720 | 2.6696 | 1
5 | Kindergarten Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0
5 | Classroom | 505 | 33 |  | 600 | 13 | 13 | House Fan | 4800 | 6.3125 | 2
6 | Classroom | 820 | 54 |  | 805 | 18 | 18 | House Fan | 6440 | 7.6398 | 2
7 | Computer Classrm. | 437 | 29 |  | 900 | 20 | 20 | House Fan | 7200 | 3.6417 | 1
8 | Classroom | 580 | 38 |  | 1094 | 24 | 24 | House Fan | 8752 | 3.9762 | 1
9 | Classrom | 444 | 29 |  | 840 | 19 | 19 | House Fan | 6720 | 3.9643 | 1
9A | Teachers Rm. | 0 | 0 | Yes | 450 | 10 | 10 | N/A | 3600 | 0 | 0
10 | Classroom | 822 | 54 |  | 600 | 13 | 13 |  | 4800 | 10.275 | 3
11 | Classroom | 466 | 31 |  | 720 | 16 | 16 | House Fan | 5760 | 4.8542 | 2
12 | Classroom | 606 | 40 |  | 720 | 16 | 16 | House Fan | 5760 | 6.3125 | 2
13 | Classroom | 626 | 41 |  | 720 | 16 | 16 | House Fan | 5760 | 6.5208 | 2
- | Auditorium | 1107 | 73 |  | 2760 | 62 | 62 | House Fan | 22080 | 3.0082 | 1
- | Cafeteria/Gym | 0 | 0 |  | 2300 | 52 | 0 | N/A | 18400 | 0 | 0
- | Counselors Rm. | 0 | 0 | Yes | 450 | 10 | 10 | N/A | 3600 | 0 | 0
- | Grnd. Fl. Boys Bathrm. | 568 | 37 |  | 736 | 16 | 16 | House Fan | 5888 | 5.788 | 2
- | Grnd. Fl. Girls Bathrm. | 620 | 41 |  | 775 | 17 | 17 | House Fan | 6200 | 6 | 2
- | Ind. Arts Classroom | 0 | 0 |  | 600 | 13 | 0 | N/A | 4800 | 0 | 0
- | Library | 525 | 35 |  | 1152 | 26 | 26 | House Fan | 9216 | 3.418 | 1
- | Main Office | 0 | 0 | Yes | 460 | 10 | 10 | N/A | 3680 | 0 | 0
- | Nurse Office |  | 0 | Yes | 450 | 10 | 10 |  | 3600 | 0 | 0
- | Art Room |  | 0 | Yes | 600 | 13 | 13 |  | 4800 | 0 | 0
- | Principal's Ofice | 0 | 0 |  | 450 | 10 | 0 | N/A | 3600 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Anne Blakiston Day Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR / Chadwick | [7 empty] | 0 | 0 | 0
School: | Anne Blakiston Day Elementary School- Little School House | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Part 2 and Exhaust | Exhaust | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Anna Blakiston Day Elementary School- Main Building | [8 empty] | 0 | 0 | 0
101 | classroom | 186 | 12 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 1.5852 | 1
102 | classroom | 194 | 12 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 1.6534 | 1
103 | classroom | 45 | 3 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0.38352 | 0
104 | classroom | 75 | 5 | Yes | 1440 | 32 | 32 | Unit Ventilator | 11520 | 0.39062 | 0
105 | classroom | 126 | 8 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 1.0739 | 1
106 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0 | 0
107 | classroom | 210 | 14 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 1.7898 | 1
108 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0 | 0
109 | classroom |  | 0 | Yes | 880 | 20 | 20 |  | 7040 | 0 | 0
111 | Classroom |  | 0 | Yes | 880 | 20 | 20 |  | 7040 | 0 | 0
112 | Classroom |  | 0 | Yes | 260 | 5 | 5 |  | 2080 | 0 | 0
201 | classroom | 255 | 17 | Yes | 875 | 19 | 19 | Unit Ventilator | 7000 | 2.1857 | 1
202 | classroom | 257 | 17 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.1903 | 1
203 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0 | 0
204 | classroom | 365 | 24 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 3.1108 | 1
205 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0 | 0
206 | classroom | 84 | 5 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0.71591 | 0
207 | classroom | 0 | 0 | Yes | 575 | 13 | 13 | Unit Ventilator | 4600 | 0 | 0
208 | classroom | 47 | 3 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0.40057 | 0
209 | classroom | 235 | 15 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.0028 | 1
210 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0 | 0
211 | classroom | 244 | 16 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.0795 | 1
214 | Classroom |  | 0 | Yes | 228 | 5 | 5 |  | 1824 | 0 | 0
- | Auditorium | 0 | 0 |  | 3300 | 75 | 0 | AHU | 26400 | 0 | 0
- | GYM | 573 | 38 |  | 5000 | 113 | 38 | AHU | 40000 | 0.8595 | 0
- | Library | 0 | 0 |  | 2700 | 61 | 0 | RTU | 21600 | 0 | 0
Anna Blakiston Day Elementary School- Little School House | [8 empty] | 0 | 0 | 0
1 | classroom | 322 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.2869 | 1
2 | classroom | 274 | 18 |  | 1056 | 24 | 18 | AHU | 8448 | 1.946 | 1
3 | classroom | 322 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.2869 | 1
4 | classroom | 510 | 34 |  | 1056 | 24 | 24 | AHU | 8448 | 3.6222 | 1
5 | classroom | 302 | 20 |  | 1056 | 24 | 20 | AHU | 8448 | 2.1449 | 1
6 | classroom | 325 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.3082 | 1
7 | classroom | 302 | 20 |  | 1056 | 24 | 20 | AHU | 8448 | 2.1449 | 1
8 | classroom | 325 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.3082 | 1
9 | classroom | 302 | 20 |  | 1056 | 24 | 20 | AHU | 8448 | 2.1449 | 1
10 | classroom | 325 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.3082 | 1
11 | classroom | 302 | 20 |  | 1056 | 24 | 20 | AHU | 8448 | 2.1449 | 1
12 | classroom | 325 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.3082 | 1
- | Lunchroom | 1136 | 75 |  | 1750 | 39 | 39 | AHU | 14000 | 4.8686 | 2
- | Staff Bathroom Staff Toilet | 159 | 10 |  | 120 | 2 | 2 | N/A | 960 | 9.9375 | 2
- | Staff Bathroom Staff Toilet | 277 | 18 |  | 120 | 2 | 2 | N/A | 960 | 17.3125 | 3
- | Various Office | 392 | 26 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | Corridor | 224 | 14 |  |  | 0 | 0 | FCU | 0 | 0 | 0
- | Various Storage | 374 | 24 |  |  | 0 | 0 | AHU | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21 | [7 empty] | 0 | 0 | 0
School: | Julia deBurgos Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
108 | storage |  | 0 |  | 100 | 2 | 0 | AHU-1 | 800 | 0 | 0
111 | work rm |  | 0 |  | 100 | 2 | 0 | AHU-1 | 800 | 0 | 0
115 | office | 100 | 6 |  | 150 | 3 | 3 | AHU-1 | 1200 | 5 | 2
116 | classroom | 281 | 18 |  | 658 | 14 | 14 | Univent | 5264 | 3.2029 | 1
118 | classroom |  | 0 |  | 400 | 9 | 0 | AHU-1 | 3200 | 0 | 0
120 | classroom | 380 | 25 |  | 759 | 17 | 17 | Univent | 6072 | 3.7549 | 1
121 | classroom | 288 | 19 |  | 759 | 17 | 17 | Univent | 6072 | 2.8458 | 1
123 | classroom | 486 | 32 |  | 759 | 17 | 17 | Univent | 6072 | 4.8024 | 2
125 | classroom | 307 | 20 |  | 759 | 17 | 17 | Univent | 6072 | 3.0336 | 1
129 | classroom | 335 | 22 |  | 640 | 14 | 14 | Univent | 5120 | 3.9258 | 1
130 | classroom | 295 | 19 |  | 672 | 15 | 15 | Univent | 5376 | 3.2924 | 1
132 | classroom | 470 | 31 |  | 704 | 16 | 16 | Univent | 5632 | 5.0071 | 2
133 | classroom | 345 | 23 |  | 880 | 20 | 20 | Univent | 7040 | 2.9403 | 1
134 | classroom | 301 | 20 |  | 667 | 15 | 15 | AHU-5 | 5336 | 3.3846 | 1
135 | classroom | 552 | 36 |  | 750 | 17 | 17 | Univent | 6000 | 5.52 | 2
136 | classroom | 291 | 19 |  | 750 | 17 | 17 | Univent | 6000 | 2.91 | 1
138 | classroom | 734 | 48 |  | 748 | 17 | 17 | AHU-5 | 5984 | 7.3596 | 2
139 | classroom | 0 | 0 | Yes | 704 | 16 | 16 | AHU-5 | 5632 | 0 | 0
139B | PRACTICE RM | 0 | 0 |  | 100 | 2 | 0 | AHU-5 | 800 | 0 | 0
139C | PRACTICE RM | 0 | 0 |  | 100 | 2 | 0 | AHU-5 | 800 | 0 | 0
148 | office | 244 | 16 |  | 350 | 7 | 7 | AHU-5 | 2800 | 5.2286 | 2
148A | office | 130 | 8 |  | 100 | 2 | 2 | AHU-5 | 800 | 9.75 | 2
148B | office | 54 | 3 |  | 110 | 2 | 2 | AHU-5 | 880 | 3.6818 | 1
148C | office | 37 | 2 |  | 100 | 2 | 2 | AHU-5 | 800 | 2.775 | 1
148D | office | 51 | 3 |  | 100 | 2 | 2 | AHU-5 | 800 | 3.825 | 1
148E | office | 67 | 4 |  | 100 | 2 | 2 | AHU-5 | 800 | 5.025 | 2
148F | office | 89 | 5 |  | 100 | 2 | 2 | AHU-5 | 800 | 6.675 | 2
148G | office | 44 | 2 |  | 100 | 2 | 2 | AHU-5 | 800 | 3.3 | 1
148H | office | 26 | 1 |  | 100 | 2 | 1 | AHU-5 | 800 | 1.95 | 1
148I | office | 64 | 4 |  | 100 | 2 | 2 | AHU-5 | 800 | 4.8 | 2
148L | office | 126 | 8 |  | 242 | 5 | 5 | AHU-5 | 1936 | 3.905 | 1
149 | office | 59 | 3 |  | 100 | 2 | 2 | AHU-5 | 800 | 4.425 | 2
- | Nurse Office |  | 0 | Yes | 180 | 4 | 4 | AHU-5 | 1440 | 0 | 0
151 | WAITING RM | 22 | 1 | Yes | 180 | 4 | 4 | AHU-5 | 1440 | 0.91667 | 0
151A | OFFICE | 0 | 0 |  | 110 | 2 | 0 | AHU-5 | 880 | 0 | 0
151B | OFFICE | 17 | 1 |  | 150 | 3 | 1 | AHU-5 | 1200 | 0.85 | 0
151C | OFFICE | 17 | 1 |  | 80 | 1 | 1 | AHU-5 | 640 | 1.5938 | 1
151E | OFFICE | 0 | 0 |  | 100 | 2 | 0 | AHU-5 | 800 | 0 | 0
152f | office | 39 | 2 |  | 99 | 2 | 2 | AHU-5 | 792 | 2.9545 | 1
152g | office | 47 | 3 |  | 99 | 2 | 2 | AHU-5 | 792 | 3.5606 | 1
152h | office | 0 | 0 |  | 208 | 4 | 0 | AHU-5 | 1664 | 0 | 0
152j | office | 178 | 11 |  | 288 | 6 | 6 | AHU-5 | 2304 | 4.6354 | 2
152k | office | 160 | 10 |  | 368 | 8 | 8 | AHU-5 | 2944 | 3.2609 | 1
202 | classroom | 608 | 40 |  | 759 | 17 | 17 | Univent | 6072 | 6.0079 | 2
203 | classroom | 481 | 32 |  | 759 | 17 | 17 | Univent | 6072 | 4.753 | 2
207 | classroom | 310 | 20 |  | 1081 | 24 | 20 | Univent | 8648 | 2.1508 | 1
208 | classroom | 331 | 22 |  | 621 | 14 | 14 | Univent | 4968 | 3.9976 | 1
211 | classroom | 300 | 20 |  | 759 | 17 | 17 | Univent | 6072 | 2.9644 | 1
212 | classroom | 405 | 27 |  | 759 | 17 | 17 | Univent | 6072 | 4.002 | 2
213 | classroom | 345 | 23 |  | 759 | 17 | 17 | Univent | 6072 | 3.4091 | 1
215 | office | 385 | 25 |  | 675 | 15 | 15 | AHU-1 | 5400 | 4.2778 | 2
218 | classroom | 720 | 48 |  | 759 | 17 | 17 | Univent | 6072 | 7.1146 | 2
220 | classroom | 360 | 24 |  | 759 | 17 | 17 | Univent | 6072 | 3.5573 | 1
221 | classroom | 310 | 20 |  | 759 | 17 | 17 | Univent | 6072 | 3.0632 | 1
225 | classroom | 413 | 27 |  | 759 | 17 | 17 | Univent | 6072 | 4.081 | 2
226 | classroom | 328 | 21 |  | 759 | 17 | 17 | Univent | 6072 | 3.2411 | 1
228 | classroom | 345 | 23 |  | 759 | 17 | 17 | Univent | 6072 | 3.4091 | 1
229 | classroom | 300 | 20 |  | 759 | 17 | 17 | Univent | 6072 | 2.9644 | 1
230 | classroom | 345 | 23 |  | 1196 | 27 | 23 | Univent | 9568 | 2.1635 | 1
236 | classroom | 83 | 5 |  | 494 | 11 | 5 | AHU-5 | 3952 | 1.2601 | 1
236A | STORAGE | 150 | 10 |  | 171 | 3 | 3 | AHU-5 | 1368 | 6.5789 | 2
236B | OFFICE | 0 | 0 |  | 171 | 3 | 0 | AHU-5 | 1368 | 0 | 0
237B | STORAGE | 37 | 2 |  | 165 | 3 | 2 | AHU-5 | 1320 | 1.6818 | 1
237C | OFFICE | 63 | 4 |  | 165 | 3 | 3 | AHU-5 | 1320 | 2.8636 | 1
238 | classroom | 442 | 29 |  | 759 | 17 | 17 | Univent | 6072 | 4.3676 | 2
239 | classroom | 284 | 18 |  | 759 | 17 | 17 | Univent | 6072 | 2.8063 | 1
302 | classroom | 430 | 28 |  | 1081 | 24 | 24 | Univent | 8648 | 2.9833 | 1
306 | classroom | 289 | 19 |  | 526 | 11 | 11 | Univent | 4208 | 4.1207 | 2
307 | classroom | 299 | 19 |  | 621 | 14 | 14 | Univent | 4968 | 3.6111 | 1
308 | classroom | 285 | 19 |  | 504 | 11 | 11 | Univent | 4032 | 4.2411 | 2
310 | classroom | 320 | 21 |  | 759 | 17 | 17 | Univent | 6072 | 3.1621 | 1
311 | classroom | 365 | 24 |  | 759 | 17 | 17 | Univent | 6072 | 3.6067 | 1
312 | classroom | 325 | 21 |  | 759 | 17 | 17 | Univent | 6072 | 3.2115 | 1
313 | office | 453 | 30 |  | 675 | 15 | 15 | AHU-1 | 5400 | 5.0333 | 2
316 | classroom | 345 | 23 |  | 759 | 17 | 17 | Univent | 6072 | 3.4091 | 1
317 | classroom | 380 | 25 |  | 759 | 17 | 17 | Univent | 6072 | 3.7549 | 1
319 | classroom | 307 | 20 |  | 989 | 22 | 20 | Unit Ventilator | 7912 | 2.3281 | 1
319A | storage | 233 | 15 |  | 367 | 8 | 8 | Unit Ventilator | 2936 | 4.7616 | 2
323 | classroom | 336 | 22 |  | 759 | 17 | 17 | Univent | 6072 | 3.3202 | 1
324 | classroom | 384 | 25 |  | 759 | 17 | 17 | Univent | 6072 | 3.7945 | 1
326 | classroom | 423 | 28 |  | 759 | 17 | 17 | Univent | 6072 | 4.1798 | 2
327 | classroom | 453 | 30 |  | 759 | 17 | 17 | Univent | 6072 | 4.4763 | 2
328 | classroom | 425 | 28 |  | 759 | 17 | 17 | Univent | 6072 | 4.1996 | 2
335 | STUDIO | 389 | 25 |  | 798 | 18 | 18 | AHU-8 | 6384 | 3.656 | 1
336 | classroom | 366 | 24 |  | 759 | 17 | 17 | Univent | 6072 | 3.6166 | 1
337 | classroom | 375 | 25 |  | 759 | 17 | 17 | Univent | 6072 | 3.7055 | 1
- | BOYS LOCKER ROOM | 80 | 5 |  | 143 | 3 | 3 | AHU-5 | 1144 | 4.1958 | 2
- | FRONT IMC LIBRARY | 118 | 7 |  | 171 | 3 | 3 | AHU-5 | 1368 | 5.1754 | 2
- | GIRLS LOCKER ROOM | 84 | 5 |  | 143 | 3 | 3 | AHU-5 | 1144 | 4.4056 | 2
- | GYM OFFICE | 41 | 2 |  | 225 | 5 | 2 | AHU-5 | 1800 | 1.3667 | 1
- | LIBRARY | 892 | 59 |  | 3276 | 74 | 59 | AHU-8 | 26208 | 2.0421 | 1
- | Mail Room | 159 | 10 |  | 200 | 4 | 4 | AHU-5 | 1600 | 5.9625 | 2
- | Main Office | 618 | 41 |  | 924 | 21 | 21 | AHU-5 | 7392 | 5.0162 | 2
- | Principal Office | 208 | 13 |  | 324 | 7 | 7 | AHU-5 | 2592 | 4.8148 | 2
- | Staff Locker Room |  | 0 |  | 70 | 1 | 0 | AHU-1 | 560 | 0 | 0
- | Storage Office | 38 | 2 |  | 100 | 2 | 2 | AHU-5 | 800 | 2.85 | 1
- | Cafeteria | 4650 | 310 |  | 6020 | 136 | 136 | AHU-2 | 48160 | 5.7932 | 2
- | Gym | 3322 | 221 |  | 5904 | 134 | 134 | ahu-6 | 47232 | 4.22 | 2
- | Auditorium | 3405 | 227 |  | 2983 | 67 | 67 | AHU-7 | 23864 | 8.561 | 2
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | Stephen Decatur Elementary School | [7 empty] | 0 | 0 | 0
| Stephen Decatur Elementary School Annex | [7 empty] | 0 | 0 | 0
| Stephen Decatur Elementary School White Building | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | Devine Brothers | Devine Retest | Emcor Retest 2-15 |  |  |  |  | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Decatur Main Building | [8 empty] | 0 | 0 | 0
K-1 | classroom | 283 | 18 |  | 1450 | 32 | 18 | Unit Ventilator | 11600 | 1.4638 | 1
K-2 | classroom | 375 | 25 |  | 1450 | 32 | 25 | Unit Ventilator | 11600 | 1.9397 | 1
100 | classroom | 329 | 21 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 2.7508 | 1
101 | classroom | 271 | 18 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 2.5248 | 1
102 | classroom | 228 | 15 |  | 897 | 20 | 15 | Unit Ventilator | 7176 | 1.9064 | 1
103 | classroom | 253 | 16 |  | 805 | 18 | 16 | Unit Ventilator | 6440 | 2.3571 | 1
104 | classroom | 240 | 16 |  | 897 | 20 | 16 | Unit Ventilator | 7176 | 2.0067 | 1
105 | classroom | 321 | 21 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 2.9907 | 1
106 | Nurse's Office |  | 0 | Yes | 357 | 8 | 8 | N/A | 2856 | 0 | 0
107 | classroom | 326 | 21 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 3.0373 | 1
108 | classroom | 322 | 21 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 2.6923 | 1
109 | classroom | 326 | 21 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 2.8731 | 1
110 | classroom | 301 | 20 |  | 702 | 15 | 15 | Unit Ventilator | 5616 | 3.2158 | 1
200 | Classroom | 352 | 23 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 3.2795 | 1
201 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | 0 | 0
202 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | 0 | 0
203 | Classroom | 234 | 15 |  | 854 | 19 | 15 | Unit Ventilator | 6832 | 2.055 | 1
204 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | 0 | 0
205 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | 0 | 0
206 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | 0 | 0
208 | Classroom | 301 | 20 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 2.8043 | 1
210 | Classroom | 242 | 16 |  | 805 | 18 | 16 | Unit Ventilator | 6440 | 2.2547 | 1
212 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | 0 | 0
214 | Classroom | 247 | 16 |  | 391 | 8 | 8 | Unit Ventilator | 3128 | 4.7379 | 2
216/218 | Classroom | 599 | 39 |  | 1702 | 38 | 38 | Unit Ventilator | 13616 | 2.6395 | 1
217 | Classroom | 283 | 18 |  | 1352 | 30 | 18 | Unit Ventilator | 10816 | 1.5699 | 1
219 | Classroom | 274 | 18 |  | 798 | 18 | 18 | Unit Ventilator | 6384 | 2.5752 | 1
220 | Classroom | 184 | 12 | Yes | 865 | 19 | 19 | Unit Ventilator | 6920 | 1.5954 | 1
300 | Classroom |  | 0 | Yes | 910 | 20 | 20 |  | 7280 | 0 | 0
301 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0
302 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0
303 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0
304 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0
305 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0
306 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0
308 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0
310 | Classroom |  | 0 | Yes | 910 | 20 | 20 |  | 7280 | 0 | 0
312 | Classroom | 277 | 18 |  | 391 | 8 | 8 | Unit Ventilator | 3128 | 5.3133 | 2
314 | Classroom | 241 | 16 |  | 397 | 9 | 9 | Unit Ventilator | 3176 | 4.5529 | 2
316 | Classroom | 238 | 15 |  | 851 | 19 | 15 | Unit Ventilator | 6808 | 2.0975 | 1
317 | Classroom |  | 0 | Yes | 910 | 20 | 20 |  | 7280 | 0 | 0
318 | Classroom |  | 0 | Yes | 850 | 19 | 19 |  | 6800 | 0 | 0
319 | Classroom |  | 0 | Yes | 910 | 20 | 20 |  | 7280 | 0 | 0
320 | Classroom |  | 0 | Yes | 910 | 20 | 20 |  | 7280 | 0 | 0
- | AP | N/A | 0 |  | 126 | 2 | 0 | N/A | 1008 | #VALUE! | #VALUE!
- | Auditorium | 675 | 45 |  | 2800 | 63 | 45 | AHU | 22400 | 1.808 | 1
- | Basement | 0 | 0 |  | 456 | 10 | 0 | N/A | 3648 | 0 | 0
B-1 | - |  | 0 | Yes | 731 | 16 | 16 | Unit Ventilator | 5848 | 0 | 0
B-2 | Counselors | 356 | 23 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 3.0514 | 1
- | Dean | N/A | 0 |  | 126 | 2 | 0 | N/A | 1008 | #VALUE! | #VALUE!
- | ESOL | 275 | 18 |  | 750 | 17 | 17 | Unit Ventilator | 6000 | 2.75 | 1
- | GYM | 1543 | 102 |  | 4108 | 93 | 93 | AHU | 32864 | 2.8171 | 1
- | IMC | 301 | 20 |  | 1404 | 31 | 20 | RTU | 11232 | 1.6079 | 1
- | Main Office | 360 | 24 |  | 999 | 22 | 22 | Unit Ventilator | 7992 | 2.7027 | 1
- | Cafeteria | 0 | 0 | Yes | 6161 | 140 | 140 | Unit Ventilator | 49288 | 0 | 0
Decatur Annex | [8 empty] | 0 | 0 | 0
A-1 | classroom | 335 | 22 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 2.8714 | 1
A-2 | classroom | 294 | 19 |  | 899 | 20 | 19 | Unit Ventilator | 7192 | 2.4527 | 1
A-3 | classroom | 329 | 21 |  | 874 | 19 | 19 | Unit Ventilator | 6992 | 2.8232 | 1
A-4 | classroom | 285 | 19 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 2.5088 | 1
A-5 | classroom | 326 | 21 |  | 861 | 19 | 19 | Unit Ventilator | 6888 | 2.8397 | 1
A-6 | classroom | 322 | 21 |  | 789 | 17 | 17 | Unit Ventilator | 6312 | 3.0608 | 1
A-7 | classroom | 317 | 21 |  | 899 | 20 | 20 | Unit Ventilator | 7192 | 2.6446 | 1
A-8 | classroom | 332 | 22 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.9928 | 1
A-9 | classroom | 288 | 19 |  | 879 | 19 | 19 | Unit Ventilator | 7032 | 2.4573 | 1
A-10 | classroom | 281 | 18 |  | 888 | 20 | 18 | Unit Ventilator | 7104 | 2.3733 | 1
Decatur White Building | [8 empty] | 0 | 0 | 0
1 | classroom | 315 | 21 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 2.7 | 1
2 | classroom | 241 | 16 |  | 888 | 20 | 16 | Unit Ventilator | 7104 | 2.0355 | 1
3 | classroom | 340 | 22 |  | 878 | 19 | 19 | Unit Ventilator | 7024 | 2.9043 | 1
4 | classroom | 284 | 18 |  | 845 | 19 | 18 | Unit Ventilator | 6760 | 2.5207 | 1
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | William Dick Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | Exhaust Report | Retest Report | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 355 | 23 |  | 963 | 21 | 21 | Unit Ventilator | 7704 | 2.7648 | 1
102 | Classroom | 319 | 21 |  | 963 | 21 | 21 | Unit Ventilator | 7704 | 2.4844 | 1
103 | Nurses Office |  | 0 | Yes | 825 | 18 | 18 |  | 6600 | 0 | 0
104 | Classroom | 481 | 32 |  | 1036 | 23 | 23 | Unit Ventilator | 8288 | 3.4821 | 1
105 | Office | 0 | 0 | Yes | 4046 | 91 | 91 | Unit Ventilator | 32368 | 0 | 0
105-A | Principal's Office |  | 0 | Yes | 280 | 6 | 6 |  | 2240 | 0 | 0
106 | Small room |  | 0 | Yes | 303 | 6 | 6 |  | 2424 | 0 | 0
107 | Classroom | 328 | 21 |  | 1050 | 23 | 21 | Unit Ventilator | 8400 | 2.3429 | 1
108 | Classroom | 167 | 11 |  | 1055 | 23 | 11 | Unit Ventilator | 8440 | 1.1872 | 1
109 | Classroom | 237 | 15 | Yes | 1048 | 23 | 23 | Unit Ventilator | 8384 | 1.6961 | 1
111 | Classroom | 176 | 11 | Yes | 1272 | 28 | 28 | Unit Ventilator | 10176 | 1.0377 | 1
112 | Classroom | 345 | 23 |  | 1275 | 28 | 23 | Unit Ventilator | 10200 | 2.0294 | 1
200 | Room |  | 0 | Yes | 133 | 3 | 3 |  | 1064 | 0 | 0
201 | Classroom | 356 | 23 |  | 747 | 16 | 16 | Unit Ventilator | 5976 | 3.5743 | 1
202 | Classroom | 286 | 19 |  | 1051 | 23 | 19 | Unit Ventilator | 8408 | 2.0409 | 1
203 | Classroom | 158 | 10 | Yes | 1052 | 23 | 23 | Unit Ventilator | 8416 | 1.1264 | 1
204 | Classroom | 142 | 9 | Yes | 1035 | 23 | 23 | Unit Ventilator | 8280 | 1.029 | 1
205 | Classroom | 191 | 12 | Yes | 1057 | 24 | 24 | Unit Ventilator | 8456 | 1.3553 | 1
207 | Classroom | 199 | 13 | Yes | 1009 | 22 | 22 | Unit Ventilator | 8072 | 1.4792 | 1
208 | Classroom | 207 | 13 | Yes | 1049 | 23 | 23 | Unit Ventilator | 8392 | 1.48 | 1
209 | Classroom | 317 | 21 |  | 1055 | 23 | 21 | Unit Ventilator | 8440 | 2.2536 | 1
211 | Classroom | 286 | 19 |  | 1049 | 23 | 19 | Unit Ventilator | 8392 | 2.0448 | 1
212 | Classroom | 344 | 22 |  | 1048 | 23 | 22 | Unit Ventilator | 8384 | 2.4618 | 1
213 | Classroom | 235 | 15 | Yes | 1049 | 23 | 23 | Unit Ventilator | 8392 | 1.6802 | 1
214 | Classroom | 119 | 7 | Yes | 1029 | 23 | 23 | Unit Ventilator | 8232 | 0.86735 | 0
300 | Counselor's Office |  | 0 | Yes | 164 | 3 | 3 |  | 1312 | 0 | 0
301 | Classroom | 136 | 9 | Yes | 741 | 16 | 16 | Unit Ventilator | 5928 | 1.3765 | 1
302 | Classroom | 398 | 26 |  | 1053 | 23 | 23 | Unit Ventilator | 8424 | 2.8348 | 1
303 | Library | 241 | 16 | Yes | 1032 | 23 | 23 | Unit Ventilator | 8256 | 1.7515 | 1
304 | Classroom | 169 | 11 | Yes | 1049 | 23 | 23 | Unit Ventilator | 8392 | 1.2083 | 1
305 | Classroom | 330 | 22 |  | 1213 | 27 | 22 | Unit Ventilator | 9704 | 2.0404 | 1
307 | Classroom | 101 | 6 | Yes | 1057 | 24 | 24 | Unit Ventilator | 8456 | 0.71665 | 0
308 | Classroom | 133 | 8 | Yes | 1028 | 23 | 23 | Unit Ventilator | 8224 | 0.97033 | 0
309 | Classroom | 369 | 24 |  | 1048 | 23 | 23 | Unit Ventilator | 8384 | 2.6407 | 1
311 | Classroom | 406 | 27 |  | 1050 | 23 | 23 | Unit Ventilator | 8400 | 2.9 | 1
312 | Classroom | 281 | 18 |  | 1046 | 23 | 18 | Unit Ventilator | 8368 | 2.0148 | 1
313 | Classroom | 53 | 3 | Yes | 1046 | 23 | 23 | Unit Ventilator | 8368 | 0.38002 | 0
314 | Classroom | 0 | 0 | Yes | 1047 | 23 | 23 | Unit Ventilator | 8376 | 0 | 0
- | Gymnasium | 248 | 16 |  | 739 | 16 | 16 | Unit Ventilator | 5912 | 2.5169 | 1
- | Auditorium |  | 0 |  | 4436 | 100 | 0 | AHU | 35488 | 0 | 0
- | Building Engineer's Office |  | 0 | Yes | 482 | 10 | 10 |  | 3856 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-03 | [7 empty] | 0 | 0 | 0
School: | Hamilton Disston Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Mechanical Rm. |  | 0 |  | 570 | 12 | 0 | House Fan | 4560 | 0 | 0
B1 | Cafeteria | 1021 | 68 |  | 1680 | 38 | 38 | House Fan | 13440 | 4.558 | 2
B2 | Food Service | 1059 | 70 |  | 816 | 18 | 18 | House Fan | 6528 | 9.7335 | 2
B3 | Gym | 0 | 0 | Yes | 3840 | 87 | 87 | House Fan | 30720 | 0 | 0
- | Gym Office | 0 | 0 |  | 288 | 6 | 0 | House Fan | 2304 | 0 | 0
B4 | Classroom | 0 | 0 | Yes | 1008 | 22 | 22 | House Fan | 8064 | 0 | 0
B5 | Classroom | 1005 | 67 |  | 864 | 19 | 19 | House Fan | 6912 | 8.724 | 2
B6 | Classroom | 768 | 51 |  | 984 | 22 | 22 | House Fan | 7872 | 5.8537 | 2
017B | Basement Girls Bathroom | 464 | 30 |  | 504 | 11 | 11 | House Fan | 4032 | 6.9048 | 2
011B | Basement Boys Bathroom | 271 | 18 |  | 528 | 12 | 12 | House Fan | 4224 | 3.8494 | 1
101 | Classroom | 545 | 36 |  | 816 | 18 | 18 | House Fan | 6528 | 5.0092 | 2
102 | Classroom | 764 | 50 |  | 720 | 16 | 16 | House Fan | 5760 | 7.9583 | 2
103 | Classroom | 821 | 54 |  | 864 | 19 | 19 | House Fan | 6912 | 7.1267 | 2
104 | Classroom | 593 | 39 |  | 766 | 17 | 17 | House Fan | 6128 | 5.8061 | 2
104A | Office | 0 | 0 | Yes | 168 | 3 | 3 | House Fan | 1344 | 0 | 0
- | Auditorium | 3956 | 263 |  | 2784 | 63 | 63 | House Fan | 22272 | 10.6573 | 3
105 | Classroom | 635 | 42 |  | 766 | 17 | 17 | House Fan | 6128 | 6.2174 | 2
106 | Classroom | 403 | 26 |  | 864 | 19 | 19 | House Fan | 6912 | 3.4983 | 1
107 | Classroom | 574 | 38 |  | 720 | 16 | 16 | House Fan | 5760 | 5.9792 | 2
108 | Classroom | 593 | 39 |  | 816 | 18 | 18 | House Fan | 6528 | 5.4504 | 2
- | Nurses Office | 0 | 0 | Yes | 200 | 4 | 4 | House Fan | 1600 | 0 | 0
201 | Classroom | 447 | 29 |  | 816 | 18 | 18 | House Fan | 6528 | 4.1085 | 2
202 | Classroom | 668 | 44 |  | 720 | 16 | 16 | House Fan | 5760 | 6.9583 | 2
203 | Classroom | 601 | 40 |  | 864 | 19 | 19 | House Fan | 6912 | 5.217 | 2
203A | Climate Office | 0 | 0 | Yes | 280 | 6 | 6 | House Fan | 2240 | 0 | 0
204 | Classroom | 548 | 36 |  | 816 | 18 | 18 | House Fan | 6528 | 5.0368 | 2
204A | AP Office | 0 | 0 |  | 180 | 4 | 0 | House Fan | 1440 | 0 | 0
205 | Classroom | 301 | 20 |  | 816 | 18 | 18 | House Fan | 6528 | 2.7665 | 1
- | Counselor's Office | 0 | 0 | Yes | 260 | 5 | 5 | House Fan | 2080 | 0 | 0
206 | Classroom | 570 | 38 |  | 864 | 19 | 19 | House Fan | 6912 | 4.9479 | 2
207 | Classroom | 421 | 28 |  | 720 | 16 | 16 | House Fan | 5760 | 4.3854 | 2
208 | Classroom | 281 | 18 |  | 816 | 18 | 18 | House Fan | 6528 | 2.5827 | 1
- | Helping Hands Office | 0 | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | 0 | 0
301A | Office | 0 | 0 |  | 280 | 6 | 0 | House Fan | 2240 | 0 | 0
301 | Classroom | 365 | 24 |  | 816 | 18 | 18 | House Fan | 6528 | 3.3548 | 1
302 | Classroom | 563 | 37 |  | 720 | 16 | 16 | House Fan | 5760 | 5.8646 | 2
303 | Classroom | 442 | 29 |  | 864 | 19 | 19 | House Fan | 6912 | 3.8368 | 1
304 | Classroom | 657 | 43 |  | 816 | 18 | 18 | House Fan | 6528 | 6.0386 | 2
305 | Classroom | 53 | 3 | Yes | 870 | 19 | 19 | House Fan | 6960 | 0.4569 | 0
306 | Classroom | 186 | 12 |  | 864 | 19 | 12 | House Fan | 6912 | 1.6146 | 1
307 | Classroom | 56 | 3 | Yes | 957 | 21 | 21 | House Fan | 7656 | 0.43887 | 0
308 | Classroom | 489 | 32 |  | 864 | 19 | 19 | House Fan | 6912 | 4.2448 | 2
309 | Classroom | 127 | 8 | Yes | 900 | 20 | 20 | House Fan | 7200 | 1.0583 | 1
310 | Classroom | 96 | 6 | Yes | 816 | 18 | 18 | House Fan | 6528 | 0.88235 | 0
311 | Classroom | 611 | 40 |  | 864 | 19 | 19 | House Fan | 6912 | 5.3038 | 2
312 | Classroom | 424 | 28 |  | 720 | 16 | 16 | House Fan | 5760 | 4.4167 | 2
313 | Classroom | 411 | 27 |  | 816 | 18 | 18 | House Fan | 6528 | 3.7776 | 1
313A | Office | 0 | 0 |  | 816 | 18 | 0 | House Fan | 6528 | 0 | 0
- | Library | 747 | 49 |  | 2156 | 49 | 49 | RTU-1 | 17248 | 2.5986 | 1
- | Office | 155 | 10 |  | 312 | 7 | 7 | RTU-1 | 2496 | 3.726 | 1
- | Office | 55 | 3 |  | 312 | 7 | 3 | RTU-1 | 2496 | 1.3221 | 1
- | Main Office | 0 | 0 | Yes | 308 | 7 | 7 | RTU-2 | 2464 | 0 | 0
- | Principal Office | 0 | 0 |  | 160 | 3 | 0 | RTU-2 | 1280 | 0 | 0
- | Faculty Lounge | 0 | 0 |  | 312 | 7 | 0 | RTU-2 | 2496 | 0 | 0
- | Modular Classroom | 0 | 0 |  | 720 | 16 | 0 | AHU | 5760 | 0 | 0
Sheet Last Modified: | 2021-04-19 | [7 empty] | 0 | 0 | 0
School: | Murrell Dobbins Vocational High School | [7 empty] | 0 | 0 | 0
Vendor: | Capital | Devine Brothers | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
016 B-5 | Classroom | 1130 | 75 |  | 2511 | 57 | 57 |  | 20088 | 3.3751 | 1
016 B-6 | Classroom | 536 | 35 |  | 2511 | 57 | 35 |  | 20088 | 1.601 | 1
016 B-7 | Classroom | 718 | 47 |  | 2424 | 55 | 47 |  | 19392 | 2.2215 | 1
016 B-8 | Classroom | 494 | 32 |  | 2543 | 57 | 32 |  | 20344 | 1.4569 | 1
120 | Classroom | 249 | 16 |  | 597 | 13 | 13 |  | 4776 | 3.1281 | 1
122-A | Classroom | 325 | 21 |  | 1226 | 27 | 21 |  | 9808 | 1.9882 | 1
122-B | Classroom | 391 | 26 |  | 1226 | 27 | 26 |  | 9808 | 2.3919 | 1
123-A | Classroom | 287 | 19 |  | 1445 | 32 | 19 |  | 11560 | 1.4896 | 1
123-B | Classroom | 0 | 0 |  | 1445 | 32 | 0 |  | 11560 | 0 | 0
123C | Classroom | 0 | 0 |  | 136 | 3 | 0 |  | 1088 | 0 | 0
123J | Classroom | 428 | 28 |  | 322 | 7 | 7 |  | 2576 | 9.9689 | 2
130 | Classroom | 284 | 18 |  | 1017 | 23 | 18 |  | 8136 | 2.0944 | 1
131-A | Classroom | 0 | 0 |  | 2226 | 50 | 0 |  | 17808 | 0 | 0
131-B | Classroom | 458 | 30 |  | 2226 | 50 | 30 |  | 17808 | 1.5431 | 1
131-C | Classroom | 0 | 0 |  | 2226 | 50 | 0 |  | 17808 | 0 | 0
131-D | Classroom | 232 | 15 |  | 2226 | 50 | 15 |  | 17808 | 0.78167 | 0
134 | Classroom | 0 | 0 |  | 596 | 13 | 0 |  | 4768 | 0 | 0
201 | Library/IMC | 397 | 26 |  | 3115 | 70 | 26 |  | 24920 | 0.95586 | 0
220-A | Classroom | 760 | 50 |  | 435 | 9 | 9 |  | 3480 | 13.1034 | 3
220-B | Classroom | 452 | 30 |  | 210 | 4 | 4 |  | 1680 | 16.1429 | 3
220-C | Classroom | 398 | 26 |  | 210 | 4 | 4 |  | 1680 | 14.2143 | 3
220-D | Classroom | 411 | 27 |  | 308 | 7 | 7 |  | 2464 | 10.0081 | 3
222 | Classroom | 299 | 19 |  | 1228 | 27 | 19 |  | 9824 | 1.8261 | 1
223 | Classroom | 393 | 26 |  | 720 | 16 | 16 |  | 5760 | 4.0938 | 2
225 | Classroom | 394 | 26 |  | 735 | 16 | 16 |  | 5880 | 4.0204 | 2
227-A | Classroom | 505 | 33 |  | 871 | 19 | 19 |  | 6968 | 4.3485 | 2
227-B | Classroom | 335 | 22 |  | 871 | 19 | 19 |  | 6968 | 2.8846 | 1
231-A | Classroom | 0 | 0 |  | 1125 | 25 | 0 |  | 9000 | 0 | 0
231-B | Classroom | 141 | 9 |  | 1125 | 25 | 9 |  | 9000 | 0.94 | 0
233-A | Classroom | 371 | 24 |  | 2122 | 48 | 24 |  | 16976 | 1.3113 | 1
233-B | Classroom | 347 | 23 |  | 2122 | 48 | 23 |  | 16976 | 1.2264 | 1
233-C | Classroom | 319 | 21 |  | 2122 | 48 | 21 |  | 16976 | 1.1275 | 1
234 | Classroom | 0 | 0 |  | 771 | 17 | 0 |  | 6168 | 0 | 0
236 | Classroom | 381 | 25 |  | 1030 | 23 | 23 |  | 8240 | 2.7743 | 1
236,234,233, | Classrooms | 6741 | 449 |  | 792 | 18 | 18 |  | 6336 | 63.8352 | 5
232, & 231 | [8 empty] | 0 | 0 | 0
- | 2nd E/Center Corr | 375 | 25 |  | 2310 | 52 | 25 |  | 18480 | 1.2175 | 1
- | 2nd East Corr | 312 | 20 |  | 2310 | 52 | 20 |  | 18480 | 1.013 | 1
- | 2nd W/Center Corr | 292 | 19 |  | 2310 | 52 | 19 |  | 18480 | 0.94805 | 0
- | 2nd West Corr | 0 | 0 |  | 2310 | 52 | 0 |  | 18480 | 0 | 0
300 | Classroom | 451 | 30 |  | 975 | 22 | 22 |  | 7800 | 3.4692 | 1
305,330,331, | Classrooms | 7434 | 495 |  | 792 | 18 | 18 |  | 6336 | 70.3977 | 5
332, & 332A | [8 empty] | 0 | 0 | 0
315-A | Classroom | 300 | 20 |  | 1008 | 22 | 20 |  | 8064 | 2.2321 | 1
315-B | Classroom | 390 | 26 |  | 1008 | 22 | 22 |  | 8064 | 2.9018 | 1
317 | Classroom | 346 | 23 |  | 832 | 18 | 18 |  | 6656 | 3.119 | 1
321,323,322, | Classrooms | 5053 | 336 |  | 792 | 18 | 18 |  | 6336 | 47.8504 | 4
322A, &322B | [8 empty] | 0 | 0 | 0
322-A | Classroom | 0 | 0 |  | 3737 | 84 | 0 |  | 29896 | 0 | 0
322-B | Classroom | 171 | 11 |  | 3737 | 84 | 11 |  | 29896 | 0.34319 | 0
322-C | Classroom | 0 | 0 |  | 3737 | 84 | 0 |  | 29896 | 0 | 0
322-D | Classroom | 680 | 45 |  | 3737 | 84 | 45 |  | 29896 | 1.3647 | 1
322-E | Classroom | 756 | 50 |  | 3737 | 84 | 50 |  | 29896 | 1.5173 | 1
322B | Classroom | 89 | 5 |  | 187 | 4 | 4 |  | 1496 | 3.5695 | 1
323-A | Classroom | 682 | 45 |  | 1035 | 23 | 23 |  | 8280 | 4.942 | 2
331-A | Classroom | 538 | 35 |  | 1852 | 42 | 35 |  | 14816 | 2.1787 | 1
331-B | Classroom | 221 | 14 |  | 1852 | 42 | 14 |  | 14816 | 0.89498 | 0
332-A | Classroom | 352 | 23 |  | 963 | 21 | 21 |  | 7704 | 2.7414 | 1
332-B | Classroom | 371 | 24 |  | 963 | 21 | 21 |  | 7704 | 2.8894 | 1
333-A | Classroom | 478 | 31 |  | 1862 | 42 | 31 |  | 14896 | 1.9253 | 1
333-B | Classroom | 0 | 0 |  | 1862 | 42 | 0 |  | 14896 | 0 | 0
333-C | Classroom | 543 | 36 |  | 1862 | 42 | 36 |  | 14896 | 2.1872 | 1
335 | Classroom | 393 | 26 |  | 250 | 5 | 5 |  | 2000 | 11.79 | 3
- | 3rd E/Center Corr | 296 | 19 |  | 2310 | 52 | 19 |  | 18480 | 0.96104 | 0
- | 3rd East Corr | 310 | 20 |  | 2310 | 52 | 20 |  | 18480 | 1.0065 | 1
- | 3rd W/Center Corr | 437 | 29 |  | 2310 | 52 | 29 |  | 18480 | 1.4188 | 1
- | 3rd West Corr | 0 | 0 |  | 2310 | 52 | 0 |  | 18480 | 0 | 0
400-A | Classroom | 356 | 23 |  | 2045 | 46 | 23 |  | 16360 | 1.3056 | 1
400-B | Classroom | 333 | 22 |  | 2045 | 46 | 22 |  | 16360 | 1.2213 | 1
400, 402, 403, & 403A | Classroom | 21 | 1 |  | 2310 | 52 | 1 |  | 18480 | 0.068182 | 0
401-A | Classroom | 0 | 0 |  | 1080 | 24 | 0 |  | 8640 | 0 | 0
401-B | Classroom | 168 | 11 |  | 1080 | 24 | 11 |  | 8640 | 1.1667 | 1
401A | Storage | 264 | 17 |  | 222 | 5 | 5 |  | 1776 | 8.9189 | 2
402-A | Classroom | 0 | 0 |  | 951 | 21 | 0 |  | 7608 | 0 | 0
402-B | Classroom | 194 | 12 |  | 951 | 21 | 12 |  | 7608 | 1.53 | 1
403-A | Classroom | 257 | 17 |  | 2279 | 51 | 17 |  | 18232 | 0.84577 | 0
403-B | Classroom | 81 | 5 |  | 2279 | 51 | 5 |  | 18232 | 0.26656 | 0
403-C | Classroom | 190 | 12 |  | 2279 | 51 | 12 |  | 18232 | 0.62527 | 0
403-D | Classroom | 226 | 15 |  | 2279 | 51 | 15 |  | 18232 | 0.74375 | 0
410-A | Classroom | 273 | 18 |  | 1058 | 24 | 18 |  | 8464 | 1.9353 | 1
410-B | Classroom | 273 | 18 |  | 1058 | 24 | 18 |  | 8464 | 1.9353 | 1
411-A | Classroom | 0 | 0 |  | 1067 | 24 | 0 |  | 8536 | 0 | 0
411-B | Classroom | 0 | 0 |  | 1067 | 24 | 0 |  | 8536 | 0 | 0
412 | Classroom | 422 | 28 |  | 1066 | 24 | 24 |  | 8528 | 2.969 | 1
413 | Classroom | 0 | 0 |  | 952 | 21 | 0 |  | 7616 | 0 | 0
414 | Classroom | 364 | 24 |  | 921 | 20 | 20 |  | 7368 | 2.9642 | 1
420-A | Classroom | 766 | 51 |  | 745 | 16 | 16 |  | 5960 | 7.7114 | 2
420-B | Classroom | 326 | 21 |  | 745 | 16 | 16 |  | 5960 | 3.2819 | 1
422-A | Classroom | 514 | 34 |  | 2438 | 55 | 34 |  | 19504 | 1.5812 | 1
422-B | Classroom | 417 | 27 |  | 2438 | 55 | 27 |  | 19504 | 1.2828 | 1
422-C | Classroom | 407 | 27 |  | 2438 | 55 | 27 |  | 19504 | 1.2521 | 1
423 & 420 | Classrooms | 0 | 0 |  | 576 | 13 | 0 |  | 4608 | 0 | 0
423-A | Classroom | 0 | 0 |  | 1372 | 31 | 0 |  | 10976 | 0 | 0
423-B | Classroom | 0 | 0 |  | 1372 | 31 | 0 |  | 10976 | 0 | 0
430-A | Classroom | 300 | 20 |  | 1431 | 32 | 20 |  | 11448 | 1.5723 | 1
430-B | Classroom | 319 | 21 |  | 1431 | 32 | 21 |  | 11448 | 1.6719 | 1
430,431, & 432 | Classrooms | 8038 | 535 |  | 792 | 18 | 18 |  | 6336 | 76.1174 | 5
431-A | Classroom | 673 | 44 |  | 2491 | 56 | 44 |  | 19928 | 2.0263 | 1
431-B | Classroom | 221 | 14 |  | 2491 | 56 | 14 |  | 19928 | 0.6654 | 0
431-C | Classroom | 533 | 35 |  | 2491 | 56 | 35 |  | 19928 | 1.6048 | 1
431-D | Classroom | 347 | 23 |  | 2491 | 56 | 23 |  | 19928 | 1.0448 | 1
431-E | Classroom | 325 | 21 |  | 2491 | 56 | 21 |  | 19928 | 0.97852 | 0
- | 4th E/Center Corr | 0 | 0 |  | 2310 | 52 | 0 |  | 18480 | 0 | 0
- | 4th East Corr | 0 | 0 |  | 2310 | 52 | 0 |  | 18480 | 0 | 0
- | 4th W/ Center Corr | 199 | 13 |  | 2310 | 52 | 13 |  | 18480 | 0.6461 | 0
- | 4th West Corr | 267 | 17 |  | 2310 | 52 | 17 |  | 18480 | 0.86688 | 0
500 | Classroom | 299 | 19 |  | 1160 | 26 | 19 |  | 9280 | 1.9332 | 1
500-A | Classroom | 301 | 20 |  | 270 | 6 | 6 |  | 2160 | 8.3611 | 2
501 | Classroom | 388 | 25 |  | 956 | 21 | 21 |  | 7648 | 3.0439 | 1
502-A | Classroom | 206 | 13 |  | 956 | 21 | 13 |  | 7648 | 1.6161 | 1
502-B | Classroom | 258 | 17 |  | 956 | 21 | 17 |  | 7648 | 2.0241 | 1
503-A | Classroom | 208 | 13 |  | 956 | 21 | 13 |  | 7648 | 1.6318 | 1
503-B | Classroom | 144 | 9 |  | 956 | 21 | 9 |  | 7648 | 1.1297 | 1
504-A | Classroom | 224 | 14 |  | 957 | 21 | 14 |  | 7656 | 1.7555 | 1
504-B | Classroom | 108 | 7 |  | 957 | 21 | 7 |  | 7656 | 0.84639 | 0
505 | Classroom | 0 | 0 |  | 863 | 19 | 0 |  | 6904 | 0 | 0
506-A | Classroom | 0 | 0 |  | 833 | 18 | 0 |  | 6664 | 0 | 0
506-B | Classroom | 280 | 18 |  | 833 | 18 | 18 |  | 6664 | 2.521 | 1
507-A | Classroom | 221 | 14 |  | 1032 | 23 | 14 |  | 8256 | 1.6061 | 1
507-B | Classroom | 467 | 31 |  | 1032 | 23 | 23 |  | 8256 | 3.3939 | 1
510-A | Classroom | 313 | 20 |  | 1085 | 24 | 20 |  | 8680 | 2.1636 | 1
510-B | Classroom | 323 | 21 |  | 1085 | 24 | 21 |  | 8680 | 2.2327 | 1
511 | Classroom | 293 | 19 |  | 954 | 21 | 19 |  | 7632 | 2.3035 | 1
512 | Classroom | 344 | 22 |  | 712 | 16 | 16 |  | 5696 | 3.6236 | 1
513 | Classroom | 294 | 19 |  | 712 | 16 | 16 |  | 5696 | 3.0969 | 1
514 | Classroom | 311 | 20 |  | 665 | 15 | 15 |  | 5320 | 3.5075 | 1
515 | Classroom | 358 | 23 |  | 818 | 18 | 18 |  | 6544 | 3.2824 | 1
516 | Classroom | 394 | 26 |  | 819 | 18 | 18 |  | 6552 | 3.6081 | 1
520-B | Classroom | 0 | 0 |  | 221 | 5 | 0 |  | 1768 | 0 | 0
522 | Classroom | 0 | 0 |  | 316 | 7 | 0 |  | 2528 | 0 | 0
523 | Classroom | 0 | 0 |  | 795 | 18 | 0 |  | 6360 | 0 | 0
524 | Classroom | 0 | 0 |  | 800 | 18 | 0 |  | 6400 | 0 | 0
525 | Classroom | 378 | 25 |  | 851 | 19 | 19 |  | 6808 | 3.3314 | 1
526-A | Classroom | 57 | 3 |  | 961 | 21 | 3 |  | 7688 | 0.44485 | 0
526-B | Classroom | 377 | 25 |  | 961 | 21 | 21 |  | 7688 | 2.9422 | 1
530 | Classroom | 293 | 19 |  | 821 | 18 | 18 |  | 6568 | 2.6766 | 1
531-A | Classroom | 576 | 38 |  | 724 | 16 | 16 |  | 5792 | 5.9669 | 2
531-B | Classroom | 81 | 5 |  | 724 | 16 | 5 |  | 5792 | 0.83909 | 0
532 | Classroom | 292 | 19 |  | 879 | 19 | 19 |  | 7032 | 2.4915 | 1
533-A | Classroom | 225 | 15 |  | 800 | 18 | 15 |  | 6400 | 2.1094 | 1
533-B | Classroom | 0 | 0 |  | 800 | 18 | 0 |  | 6400 | 0 | 0
534-A | Classroom | 438 | 29 |  | 1036 | 23 | 23 |  | 8288 | 3.1708 | 1
534-B | Classroom | 0 | 0 |  | 1036 | 23 | 0 |  | 8288 | 0 | 0
535 | Classroom | 0 | 0 |  | 1006 | 22 | 0 |  | 8048 | 0 | 0
- | 5th E.Cent Corr | 201 | 13 |  | 2310 | 52 | 13 |  | 18480 | 0.6526 | 0
- | 5th East Corr. | 0 | 0 |  | 2310 | 52 | 0 |  | 18480 | 0 | 0
- | 5th W.Cent Corr | 276 | 18 |  | 2310 | 52 | 18 |  | 18480 | 0.8961 | 0
601-A | Classroom | 138 | 9 |  | 1553 | 35 | 9 |  | 12424 | 0.66645 | 0
601-B | Classroom | 0 | 0 |  | 1553 | 35 | 0 |  | 12424 | 0 | 0
601-C | Classroom | 0 | 0 |  | 1553 | 35 | 0 |  | 12424 | 0 | 0
603-A | Classroom | 0 | 0 |  | 962 | 21 | 0 |  | 7696 | 0 | 0
603-B | Classroom | 229 | 15 |  | 962 | 21 | 15 |  | 7696 | 1.7853 | 1
604 | Classroom | 0 | 0 |  | 400 | 9 | 0 |  | 3200 | 0 | 0
610 | Classroom | 331 | 22 |  | 738 | 16 | 16 |  | 5904 | 3.3638 | 1
611 | Classroom | 460 | 30 |  | 712 | 16 | 16 |  | 5696 | 4.8455 | 2
612 | Classroom | 298 | 19 |  | 704 | 16 | 16 |  | 5632 | 3.1747 | 1
613 | Classroom | 257 | 17 |  | 711 | 16 | 16 |  | 5688 | 2.711 | 1
614 | Classroom | 270 | 18 |  | 800 | 18 | 18 |  | 6400 | 2.5312 | 1
615 | Classroom | 382 | 25 |  | 814 | 18 | 18 |  | 6512 | 3.5197 | 1
622-A | Classroom | 0 | 0 |  | 801 | 18 | 0 |  | 6408 | 0 | 0
622-B | Classroom | 242 | 16 |  | 801 | 18 | 16 |  | 6408 | 2.2659 | 1
623 | Classroom | 682 | 45 |  | 679 | 15 | 15 |  | 5432 | 7.5331 | 2
624 | Classroom | 267 | 17 |  | 820 | 18 | 17 |  | 6560 | 2.4421 | 1
625 | Classroom | 174 | 11 |  | 680 | 15 | 11 |  | 5440 | 1.9191 | 1
627 | Classroom | 815 | 54 |  | 794 | 18 | 18 |  | 6352 | 7.6984 | 2
- | 6th Center Corr. | 0 | 0 |  | 792 | 18 | 0 |  | 6336 | 0 | 0
- | 6th East Corr. | 466 | 31 |  | 792 | 18 | 18 |  | 6336 | 4.4129 | 2
- | Admin | 4788 | 319 |  | 786 | 17 | 17 |  | 6288 | 45.687 | 4
- | Auditorium | 0 | 0 | Yes | 10676 | 242 | 242 |  | 85408 | 0 | 0
- | Boy's Gym | 0 | 0 |  | 5940 | 135 | 0 |  | 47520 | 0 | 0
- | Girl's Gym | 0 | 0 |  | 5696 | 129 | 0 |  | 45568 | 0 | 0
- | Lunch Rm | 0 | 0 |  | 4563 | 103 | 0 |  | 36504 | 0 | 0
- | Lunch Rm | 0 | 0 |  | 4563 | 103 | 0 |  | 36504 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | James Dobson Middle School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | 0 | 0
101 | Classroom |  | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | 0 | 0
103 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
104 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
106 | Office |  | 0 | Yes | 638 | 14 | 14 | House Fan | 5104 | 0 | 0
107 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
108 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
109 | Classroom |  | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | 0 | 0
201 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
202 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
203 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
204 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
205 | Office |  | 0 | Yes | 342 | 7 | 7 | House Fan | 2736 | 0 | 0
206 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
207 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
208 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
209 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
210 | Office |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
303/304 | Classroom |  | 0 | Yes | 1320 | 30 | 30 | House Fan | 10560 | 0 | 0
306/307 | Classroom |  | 0 | Yes | 1320 | 30 | 30 | House Fan | 10560 | 0 | 0
308 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
309 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
313 | Classroom |  | 0 | Yes | 858 | 19 | 19 | House Fan | 6864 | 0 | 0
- | Councelors office |  | 0 | Yes | 243 | 5 | 5 |  | 1944 | 0 | 0
- | Main Office |  | 0 | Yes | 510 | 11 | 11 | House Fan | 4080 | 0 | 0
- | Principals office |  | 0 | Yes | 236 | 5 | 5 | House Fan | 1888 | 0 | 0
- | Gym |  | 0 | Yes | 3080 | 70 | 70 |  | 24640 | 0 | 0
- | Cafeteria large |  | 0 |  | 944 | 21 | 0 |  | 7552 | 0 | 0
- | Auditorium |  | 0 |  | 3124 | 71 | 0 |  | 24992 | 0 | 0
- | Library |  | 0 | Yes | 1320 | 30 | 30 |  | 10560 | 0 | 0
- | Nurses office |  | 0 | Yes | 264 | 6 | 6 |  | 2112 | 0 | 0
| Cafeteria small |  | 0 |  | 919 | 20 |  |  | 7352 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21 | [7 empty] | 0 | 0 | 0
School: | Tanner Duckrey Elementary School | [7 empty] | 0 | 0 | 0
| Exhaust Report | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B19 | Art Room | 358 | 23 |  | 1032 | 23 | 23 | AHU | 8256 | 2.6017 | 1
B21 | Classroom | 0 | 0 | Yes | 1029 | 23 | 23 | Unit Ventilator | 8232 | 0 | 0
111 | Classroom | 718 | 47 |  | 1115 | 25 | 25 | Unit Ventilator | 8920 | 4.8296 | 2
114 | Classroom | 284 | 18 |  | 941 | 21 | 18 | Unit Ventilator | 7528 | 2.2635 | 1
117 | Classroom | 608 | 40 |  | 940 | 21 | 21 | Unit Ventilator | 7520 | 4.8511 | 2
118 | Classroom | 271 | 18 |  | 691 | 15 | 15 | Unit Ventilator | 5528 | 2.9414 | 1
119 | - | 276 | 18 | Yes | 1237 | 28 | 28 | Unit Ventilator | 9896 | 1.6734 | 1
120 | Classroom | 638 | 42 |  | 1024 | 23 | 23 | Unit Ventilator | 8192 | 4.6729 | 2
121A | Classroom | 367 | 24 |  | 715 | 16 | 16 | Unit Ventilator | 5720 | 3.8497 | 1
121B | Classroom | 315 | 21 |  | 795 | 18 | 18 | Unit Ventilator | 6360 | 2.9717 | 1
122 | Classroom | 413 | 27 |  | 1027 | 23 | 23 | Unit Ventilator | 8216 | 3.0161 | 1
124 | Classroom | 686 | 45 |  | 921 | 20 | 20 | Unit Ventilator | 7368 | 5.5863 | 2
126 | Classroom | 310 | 20 |  | 927 | 21 | 20 | Unit Ventilator | 7416 | 2.5081 | 1
128 | Classroom | 409 | 27 |  | 1012 | 23 | 23 | Unit Ventilator | 8096 | 3.0311 | 1
130 | Classroom | 429 | 28 |  | 1101 | 25 | 25 | Unit Ventilator | 8808 | 2.9223 | 1
200 | - | 639 | 42 |  | 1036 | 23 | 23 | Unit Ventilator | 8288 | 4.626 | 2
201 | - | 803 | 53 |  | 1050 | 23 | 23 | Unit Ventilator | 8400 | 5.7357 | 2
204 | - | 564 | 37 |  | 952 | 21 | 21 | Unit Ventilator | 7616 | 4.4433 | 2
207 | - | 0 | 0 | Yes | 951 | 21 | 21 | Unit Ventilator | 7608 | 0 | 0
208 | - | 786 | 52 |  | 917 | 20 | 20 | Unit Ventilator | 7336 | 6.4286 | 2
209 | - | 648 | 43 |  | 951 | 21 | 21 | Unit Ventilator | 7608 | 5.1104 | 2
210 | - | 638 | 42 |  | 953 | 21 | 21 | Unit Ventilator | 7624 | 5.021 | 2
211 | - | 617 | 41 |  | 919 | 20 | 20 | Unit Ventilator | 7352 | 5.0354 | 2
212 | - |  | 0 | Yes | 1023 | 23 | 23 |  | 8184 | 0 | 0
213 | - | 830 | 55 |  | 1088 | 24 | 24 | Unit Ventilator | 8704 | 5.7215 | 2
214 | - | 819 | 54 |  | 1037 | 23 | 23 | Unit Ventilator | 8296 | 5.9233 | 2
215 | - | 475 | 31 |  | 1035 | 23 | 23 | Unit Ventilator | 8280 | 3.442 | 1
216 | - | 838 | 55 |  | 1039 | 23 | 23 | Unit Ventilator | 8312 | 6.0491 | 2
216A | - | 384 | 25 |  | 926 | 21 | 21 | Unit Ventilator | 7408 | 3.1102 | 1
217 | - | 546 | 36 |  | 922 | 20 | 20 | Unit Ventilator | 7376 | 4.4414 | 2
218 | - | 307 | 20 |  | 922 | 20 | 20 | Unit Ventilator | 7376 | 2.4973 | 1
219 | - | 348 | 23 |  | 925 | 21 | 21 | Unit Ventilator | 7400 | 2.8216 | 1
220 | - | 459 | 30 |  | 411 | 9 | 9 | Unit Ventilator | 3288 | 8.3759 | 2
220A | - | 290 | 19 |  | 330 | 7 | 7 | Unit Ventilator | 2640 | 6.5909 | 2
221 | - | 556 | 37 |  | 873 | 19 | 19 | Unit Ventilator | 6984 | 4.7766 | 2
221A | - | 432 | 28 |  | 194 | 4 | 4 | Unit Ventilator | 1552 | 16.701 | 3
222 | - | 334 | 22 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 2.8629 | 1
223 | - | 538 | 35 |  | 872 | 19 | 19 | Unit Ventilator | 6976 | 4.6273 | 2
- | Auditorium/Cafe | 264 | 17 | Yes | 5376 | 122 | 122 | AHU | 43008 | 0.3683 | 0
- | Faculty Lounge | 1156 | 77 |  | 513 | 11 | 11 | Unit Ventilator | 4104 | 16.9006 | 3
- | Kitchen | 203 | 13 |  | 2070 | 47 | 13 | AHU | 16560 | 0.73551 | 0
- | Library | 336 | 22 |  | 1914 | 43 | 22 | AHU | 15312 | 1.3166 | 1
- | Main Office | 1063 | 70 |  | 903 | 20 | 20 | Unit Ventilator | 7224 | 8.8289 | 2
- | Nurse | 334 | 22 |  | 387 | 8 | 8 | Unit Ventilator | 3096 | 6.4729 | 2
- | Science Room | 1464 | 97 |  | 799 | 18 | 18 | Unit Ventilator | 6392 | 13.7422 | 3
- | Gym | 215 | 14 |  | 4808 | 109 | 14 | AHU | 38464 | 0.33538 | 0
Sheet Last Modified: | 2021-04-06 | [7 empty] | 0 | 0 | 0
School: | Paul L. Dunbar High School | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
102 | Clasroom | 0 | 0 | Yes | 730 | 16 | 16 | House Fan | 5840 | 0 | 0
103 | office | 0 | 0 | Yes | 682 | 15 | 15 | House Fan | 5456 | 0 | 0
103 | bathroom | 0 | 0 |  | 49 | 1 | 0 | House Fan | 392 | 0 | 0
104 | Lunchroom | 0 | 0 | Yes | 1413 | 32 | 32 | House Fan | 11304 | 0 | 0
105 | Classroom | 0 | 0 | Yes | 730 | 16 | 16 | House Fan | 5840 | 0 | 0
105 | Bathroom | 0 | 0 |  | 54 | 1 | 0 | House Fan | 432 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 914 | 20 | 20 | House Fan | 7312 | 0 | 0
107 | Bathroom | 0 | 0 |  | 41 | 0 | 0 | House Fan | 328 | 0 | 0
108 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | House Fan | 5456 | 0 | 0
108 | Bathroom | 0 | 0 |  | 45 | 1 | 0 | House Fan | 360 | 0 | 0
109 | Climate rm | 0 | 0 | Yes | 251 | 5 | 5 | House Fan | 2008 | 0 | 0
109 | Bathroom | 0 | 0 |  | 58 | 1 | 0 | House Fan | 464 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | House Fan | 5456 | 0 | 0
202 | Classroom | 0 | 0 | Yes | 698 | 15 | 15 | House Fan | 5584 | 0 | 0
203 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | House Fan | 5456 | 0 | 0
204 | Classroom | 0 | 0 | Yes | 666 | 15 | 15 | House Fan | 5328 | 0 | 0
205 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | House Fan | 5456 | 0 | 0
206 | Classroom | 0 | 0 | Yes | 716 | 16 | 16 | House Fan | 5728 | 0 | 0
207 | Art room | 0 | 0 | Yes | 838 | 19 | 19 | House Fan | 6704 | 0 | 0
208 | Classroom | 0 | 0 | Yes | 679 | 15 | 15 | House Fan | 5432 | 0 | 0
209 | scc room | 0 | 0 | Yes | 457 | 10 | 10 | House Fan | 3656 | 0 | 0
300 | computer lab | 0 | 0 | Yes | 688 | 15 | 15 | House Fan | 5504 | 0 | 0
301 | Classroom | 0 | 0 | Yes | 688 | 15 | 15 | House Fan | 5504 | 0 | 0
302 | Classroom | 0 | 0 | Yes | 704 | 15 | 15 | House Fan | 5632 | 0 | 0
303 | Classroom | 0 | 0 | Yes | 670 | 15 | 15 | House Fan | 5360 | 0 | 0
304 | Classroom | 0 | 0 | Yes | 643 | 14 | 14 | House Fan | 5144 | 0 | 0
305 | Classroom | 0 | 0 | Yes | 691 | 15 | 15 | House Fan | 5528 | 0 | 0
306 | Classroom | 0 | 0 | Yes | 725 | 16 | 16 | House Fan | 5800 | 0 | 0
307 | Classroom | 0 | 0 | Yes | 966 | 21 | 21 | House Fan | 7728 | 0 | 0
308 |  | 0 |  |  | 688 |  | 0 | House Fan | 5504 | 0 | 0
309 |  | 0 |  |  | 360 |  | 0 | House Fan | 2880 | 0 | 0
310 |  | 0 |  |  | 172 |  | 0 | House Fan | 1376 | 0 | 0
- | Auditorium | 0 | 0 |  | 3202 | 72 | 0 | House Fan | 25616 | 0 | 0
- | Boys bathroom near rm 307 | 0 | 0 |  | 297 | 6 | 0 | N/A | 2376 | 0 | 0
- | Boys bathroom near Nurse's Office | 0 | 0 |  | 144 | 3 | 0 | N/A | 1152 | 0 | 0
- | Basement Boys Bathroom | 0 | 0 |  | 599 | 13 | 0 | N/A | 4792 | 0 | 0
- | Basement Boys Bathroom | 0 | 0 |  | 317 | 7 | 0 | N/A | 2536 | 0 | 0
- | Girls bathroom near rm 301 | 0 | 0 |  | 415 | 9 | 0 | N/A | 3320 | 0 | 0
- | Basement Girls Bathroom | 0 | 0 |  | 387 | 8 | 0 | N/A | 3096 | 0 | 0
- | Girls bathroom near rm 201 | 0 | 0 |  | 441 | 10 | 0 | N/A | 3528 | 0 | 0
- | Gym | 0 | 0 |  | 2723 | 61 | 0 | House Fan | 21784 | 0 | 0
- | IMC | 0 | 0 | Yes | 1168 | 26 | 26 | House Fan | 9344 | 0 | 0
- | Main Office | 0 | 0 | Yes | 360 | 8 | 8 | House Fan | 2880 | 0 | 0
- | Nurse Office | 0 | 0 | Yes | 175 | 3 | 3 | House Fan | 1400 | 0 | 0
- | Principal Office | 0 | 0 | Yes | 231 | 5 | 5 | House Fan | 1848 | 0 | 0
- | Asst Principal Office |  | 0 | Yes | 879 | 19 | 19 | House Fan | 7032 | 0 | 0
- | Counselor Office |  | 0 | Yes | 458 | 10 | 10 | House Fan | 3664 | 0 | 0
- | Teachers Lounge | 0 | 0 |  | 605 | 13 | 0 | House Fan | 4840 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-20 | [7 empty] | 0 | 0 | 0
School: | Thomas Edison High School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Retest | [6 empty] | 0 | 0 | 0
| Devine 2nd Retest | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Office | 85 | 5 |  | 568 | 12 | 5 | AHU | 4544 | 1.1224 | 1
102 | Nurse | 212 | 14 |  | 498 | 11 | 11 | AHU | 3984 | 3.1928 | 1
103A | Mail room | 261 | 17 |  | 414 | 9 | 9 | AHU | 3312 | 4.7283 | 2
104 | Office | 66 | 4 |  | 140 | 3 | 3 | AHU | 1120 | 3.5357 | 1
105 | Office | 171 | 11 |  | 284 | 6 | 6 | AHU | 2272 | 4.5158 | 2
105C | Conference | 79 | 5 |  | 242 | 5 | 5 | AHU | 1936 | 2.4483 | 1
106 | Office | 94 | 6 |  | 119 | 2 | 2 | AHU | 952 | 5.9244 | 2
107 | Office | 68 | 4 |  | 112 | 2 | 2 | AHU | 896 | 4.5536 | 2
108 | Office | 61 | 4 |  | 86 | 1 | 1 | AHU | 688 | 5.3198 | 2
109 | Office | 56 | 3 |  | 74 | 1 | 1 | AHU | 592 | 5.6757 | 2
110 | Office | 71 | 4 |  | 86 | 1 | 1 | AHU | 688 | 6.1919 | 2
111 | Office | 68 | 4 |  | 86 | 1 | 1 | AHU | 688 | 5.9302 | 2
112 | Office | 80 | 5 |  | 86 | 1 | 1 | AHU | 688 | 6.9767 | 2
113 | Office | 63 | 4 |  | 86 | 1 | 1 | AHU | 688 | 5.4942 | 2
114 | Office | 115 | 7 |  | 86 | 1 | 1 | AHU | 688 | 10.0291 | 3
115 | Office | 124 | 8 |  | 86 | 1 | 1 | AHU | 688 | 10.814 | 3
116 | Office | 160 | 10 |  | 242 | 5 | 5 | AHU | 1936 | 4.9587 | 2
117 | Office | 92 | 6 |  | 20 | 0 | 0 | AHU | 160 | 34.5 | 4
118 | Office | 55 | 3 |  | 83 | 1 | 1 | AHU | 664 | 4.9699 | 2
120 | Office | 70 | 4 |  | 90 | 2 | 2 | AHU | 720 | 5.8333 | 2
121 | Office | 56 | 3 |  | 90 | 2 | 2 | AHU | 720 | 4.6667 | 2
122 | Office | 69 | 4 |  | 90 | 2 | 2 | AHU | 720 | 5.75 | 2
123 | Office | 59 | 3 |  | 90 | 2 | 2 | AHU | 720 | 4.9167 | 2
124 | Office | 57 | 3 |  | 90 | 2 | 2 | AHU | 720 | 4.75 | 2
125 | Office | 68 | 4 |  | 90 | 2 | 2 | AHU | 720 | 5.6667 | 2
127B | Office | 136 | 9 |  | 174 | 3 | 3 | AHU | 1392 | 5.8621 | 2
128 | Conference | 658 | 43 |  | 676 | 15 | 15 | AHU | 5408 | 7.3003 | 2
129 | Office | 150 | 10 |  | 281 | 6 | 6 | AHU | 2248 | 4.0036 | 2
130 | Office | 262 | 17 |  | 345 | 7 | 7 | AHU | 2760 | 5.6957 | 2
131 | Break Room | 84 | 5 |  | 131 | 2 | 2 | AHU | 1048 | 4.8092 | 2
132 | Classroom | 292 | 19 |  | 713 | 16 | 16 | AHU | 5704 | 3.0715 | 1
133 | Classroom | 273 | 18 |  | 566 | 12 | 12 | AHU | 4528 | 3.6175 | 1
134 | Classroom | 575 | 38 |  | 2286 | 51 | 38 | AHU | 18288 | 1.8865 | 1
135 | Classroom | 460 | 30 |  | 1604 | 36 | 30 | AHU | 12832 | 2.1509 | 1
135A | Kitchen | 61 | 4 |  | 37 | 0 | 0 | AHU | 296 | 12.3649 | 3
135B | Office | 78 | 5 |  | 137 | 3 | 3 | AHU | 1096 | 4.2701 | 2
136 | Classroom | 310 | 20 |  | 1144 | 26 | 20 | AHU | 9152 | 2.0323 | 1
136B | Classroom | 483 | 32 |  | 1142 | 25 | 25 | AHU | 9136 | 3.1721 | 1
137 | Classroom | 297 | 19 |  | 2086 | 47 | 19 | AHU | 16688 | 1.0678 | 1
137A | Office | 77 | 5 |  | 228 | 5 | 5 | AHU | 1824 | 2.5329 | 1
138 | Womens Locker Room | 1166 | 77 |  | 4342 | 98 | 77 | AHU | 34736 | 2.014 | 1
138A | Office | 50 | 3 |  | 78 | 1 | 1 | AHU | 624 | 4.8077 | 2
138B | Office | 124 | 8 |  | 314 | 7 | 7 | AHU | 2512 | 2.9618 | 1
139 | Mens Locker Room | 1278 | 85 |  | 3031 | 68 | 68 | AHU | 24248 | 3.1623 | 1
139A | Office | 122 | 8 |  | 77 | 1 | 1 | AHU | 616 | 11.8831 | 3
139B | Storage | 66 | 4 |  | 178 | 4 | 4 | AHU | 1424 | 2.7809 | 1
141 | Physical Fitness | 603 | 40 |  | 1325 | 30 | 30 | AHU | 10600 | 3.4132 | 1
144A | Bathroom | 52 | 3 |  | 333 | 7 | 3 | AHU | 2664 | 1.1712 | 1
144B | Bathroom | 36 | 2 |  | 211 | 4 | 2 | AHU | 1688 | 1.2796 | 1
145 | Plumbing Shop | 6184 | 412 |  | 1635 | 37 | 37 | AHU | 13080 | 28.367 | 4
145 | Classroom | 358 | 23 |  | 2286 | 51 | 23 | AHU | 18288 | 1.1745 | 1
145B | Classroom | 161 | 10 |  | 498 | 11 | 10 | AHU | 3984 | 2.4247 | 1
146 | Office | 297 | 19 |  | 1280 | 29 | 19 | AHU | 10240 | 1.7402 | 1
146 | Office | 332 | 22 |  | 276 | 6 | 6 | AHU | 2208 | 9.0217 | 2
147 | Storage | 87 | 5 |  | 476 | 10 | 5 | AHU | 3808 | 1.3708 | 1
147 | Classroom | 553 | 36 |  | 1497 | 34 | 34 | AHU | 11976 | 2.7705 | 1
148 | Classroom |  | 0 | Yes | 3146 | 71 | 71 |  | 25168 | 0 | 0
149 | Camera Room | 88 | 5 |  | 208 | 4 | 4 | AHU | 1664 | 3.1731 | 1
150 | Classroom | 375 | 25 |  | 814 | 18 | 18 | AHU | 6512 | 3.4552 | 1
150A | Office | 0 | 0 |  | 165 | 3 | 0 | AHU | 1320 | 0 | 0
150B | Studio | 114 | 7 |  | 1182 | 26 | 7 | AHU | 9456 | 0.72335 | 0
151A | Classroom | 534 | 35 |  | 1233 | 28 | 28 | AHU | 9864 | 3.2482 | 1
151B | Classroom | 912 | 60 |  | 1441 | 32 | 32 | AHU | 11528 | 4.7467 | 2
152 | Classroom | 655 | 43 |  | 794 | 18 | 18 | AHU | 6352 | 6.187 | 2
152A | Classroom | 994 | 66 |  | 244 | 5 | 5 | AHU | 1952 | 30.5533 | 4
152B | Classroom | 901 | 60 |  | 1073 | 24 | 24 | AHU | 8584 | 6.2978 | 2
153A | Classroom | 321 | 21 |  | 533 | 12 | 12 | AHU | 4264 | 4.5169 | 2
153B | Classroom | 302 | 20 |  | 107 | 2 | 2 | AHU | 856 | 21.1682 | 3
154A | Office | 278 | 18 |  | 175 | 3 | 3 | AHU | 1400 | 11.9143 | 3
154E | Classroom | 0 | 0 |  | 516 | 11 | 0 | AHU | 4128 | 0 | 0
154H | Classroom | 304 | 20 |  | 407 | 9 | 9 | AHU | 3256 | 5.602 | 2
154D 154A | Theory | 240 | 16 |  | 514 | 11 | 11 | AHU | 4112 | 3.5019 | 1
156 | Classroom | 293 | 19 |  | 514 | 11 | 11 | AHU | 4112 | 4.2753 | 2
157 | Classroom | 961 | 64 |  | 1255 | 28 | 28 | AHU | 10040 | 5.743 | 2
158 | Classroom | 592 | 39 |  | 1234 | 28 | 28 | AHU | 9872 | 3.5981 | 1
160 | Classroom | 727 | 48 |  | 1267 | 28 | 28 | AHU | 10136 | 4.3035 | 2
160A | Office | 78 | 5 |  | 119 | 2 | 2 | AHU | 952 | 4.916 | 2
161 | Classroom | 551 | 36 |  | 1440 | 32 | 32 | AHU | 11520 | 2.8698 | 1
161A | Office | 88 | 5 |  | 120 | 2 | 2 | AHU | 960 | 5.5 | 2
161H | Classroom | 52 | 3 |  | 36 | 0 | 0 | AHU | 288 | 10.8333 | 3
161I | Practice room | 9 | 0 |  | 36 | 0 | 0 | AHU | 288 | 1.875 | 1
161J | Classroom | 73 | 4 |  | 90 | 2 | 2 | AHU | 720 | 6.0833 | 2
164 | Classroom | 1398 | 93 |  | 825 | 18 | 18 | AHU | 6600 | 12.7091 | 3
164B | Classroom | 402 | 26 |  | 159 | 3 | 3 | AHU | 1272 | 18.9623 | 3
171 | Classroom | 0 | 0 |  | 1392 | 31 | 0 | AHU | 11136 | 0 | 0
201 | Classroom | 333 | 22 |  | 679 | 15 | 15 | AHU | 5432 | 3.6782 | 1
202 | Classroom | 334 | 22 |  | 677 | 15 | 15 | AHU | 5416 | 3.7001 | 1
203 | Classroom | 325 | 21 |  | 680 | 15 | 15 | AHU | 5440 | 3.5846 | 1
204 | Classroom | 436 | 29 |  | 770 | 17 | 17 | AHU | 6160 | 4.2468 | 2
205 | Classroom | 601 | 40 |  | 1444 | 32 | 32 | AHU | 11552 | 3.1215 | 1
205B | Storage | 153 | 10 |  | 375 | 8 | 8 | AHU | 3000 | 3.06 | 1
207 | Classroom | 845 | 56 |  | 2973 | 67 | 56 | AHU | 23784 | 2.1317 | 1
209 | Classroom | 472 | 31 |  | 1646 | 37 | 31 | AHU | 13168 | 2.1507 | 1
209B | Storage | 112 | 7 |  | 279 | 6 | 6 | AHU | 2232 | 3.0108 | 1
210 | Classroom | 466 | 31 |  | 1552 | 35 | 31 | AHU | 12416 | 2.2519 | 1
210B | Storage | 190 | 12 |  | 331 | 7 | 7 | AHU | 2648 | 4.3051 | 2
212 | Office | 134 | 8 |  | 174 | 3 | 3 | AHU | 1392 | 5.7759 | 2
213A | Classroom | 384 | 25 |  | 721 | 16 | 16 | AHU | 5768 | 3.9945 | 1
213B | Classroom | 312 | 20 |  | 872 | 19 | 19 | AHU | 6976 | 2.6835 | 1
214 | Classroom | 282 | 18 |  | 703 | 15 | 15 | AHU | 5624 | 3.0085 | 1
215 | Classroom | 286 | 19 |  | 828 | 18 | 18 | AHU | 6624 | 2.5906 | 1
216 | Office | 164 | 10 |  | 397 | 9 | 9 | AHU | 3176 | 3.0982 | 1
217 | Classroom | 356 | 23 |  | 601 | 13 | 13 | AHU | 4808 | 4.4426 | 2
218 | Classroom | 352 | 23 |  | 639 | 14 | 14 | AHU | 5112 | 4.1315 | 2
219 | Office | 129 | 8 |  | 265 | 6 | 6 | AHU | 2120 | 3.6509 | 1
220 | Classroom | 444 | 29 |  | 715 | 16 | 16 | AHU | 5720 | 4.6573 | 2
220 | Classroom | 456 | 30 |  | 715 | 16 | 16 | AHU | 5720 | 4.7832 | 2
221 | Classroom | 321 | 21 |  | 720 | 16 | 16 | AHU | 5760 | 3.3438 | 1
222 | Classroom | 328 | 21 |  | 680 | 15 | 15 | AHU | 5440 | 3.6176 | 1
223 | Classroom | 299 | 19 |  | 781 | 17 | 17 | AHU | 6248 | 2.8713 | 1
224 | Classroom | 292 | 19 |  | 790 | 17 | 17 | AHU | 6320 | 2.7722 | 1
225 | Classroom | 284 | 18 |  | 749 | 17 | 17 | AHU | 5992 | 2.8438 | 1
226 | Classroom | 293 | 19 |  | 721 | 16 | 16 | AHU | 5768 | 3.0479 | 1
229 | Library | 1039 | 69 |  | 6194 | 140 | 69 | AHU | 49552 | 1.2581 | 1
229A | Office | 79 | 5 |  | 117 | 2 | 2 | AHU | 936 | 5.0641 | 2
229B | Office | 148 | 9 |  | 229 | 5 | 5 | AHU | 1832 | 4.8472 | 2
229C | Computer Lab | 100 | 6 |  | 270 | 6 | 6 | AHU | 2160 | 2.7778 | 1
230 | Office | 79 | 5 |  | 218 | 4 | 4 | AHU | 1744 | 2.7179 | 1
231 | Classroom | 308 | 20 |  | 613 | 13 | 13 | AHU | 4904 | 3.7684 | 1
232 | Office | 144 | 9 |  | 931 | 21 | 9 | AHU | 7448 | 1.16 | 1
233 | Classroom | 325 | 21 |  | 613 | 13 | 13 | AHU | 4904 | 3.9763 | 1
234 | Classroom | 334 | 22 |  | 700 | 15 | 15 | AHU | 5600 | 3.5786 | 1
235 | Classroom | 457 | 30 |  | 592 | 13 | 13 | AHU | 4736 | 5.7897 | 2
236 | Classroom | 431 | 28 |  | 720 | 16 | 16 | AHU | 5760 | 4.4896 | 2
237 | Classroom | 220 | 14 |  | 931 | 21 | 14 | AHU | 7448 | 1.7723 | 1
238 | Classroom | 112 | 7 |  | 606 | 13 | 7 | AHU | 4848 | 1.3861 | 1
239 | Classroom | 494 | 32 |  | 627 | 14 | 14 | AHU | 5016 | 5.9091 | 2
240 | Classroom | 957 | 63 |  | 1407 | 31 | 31 | AHU | 11256 | 5.1013 | 2
241 | Classroom | 318 | 21 |  | 714 | 16 | 16 | AHU | 5712 | 3.3403 | 1
241A | Classroom | 156 | 10 |  | 700 | 15 | 10 | AHU | 5600 | 1.6714 | 1
242 | Classroom | 1072 | 71 |  | 1512 | 34 | 34 | AHU | 12096 | 5.3175 | 2
243 | Classroom | 605 | 40 |  | 2253 | 51 | 40 | AHU | 18024 | 2.014 | 1
245 | Classroom | 403 | 26 |  | 1908 | 43 | 26 | AHU | 15264 | 1.5841 | 1
245A | Office | 107 | 7 |  | 258 | 5 | 5 | AHU | 2064 | 3.1105 | 1
246 | Classroom | 380 | 25 |  | 2009 | 45 | 25 | AHU | 16072 | 1.4186 | 1
246B | Classroom | 308 | 20 |  | 510 | 11 | 11 | AHU | 4080 | 4.5294 | 2
247 | Classroom | 676 | 45 |  | 1992 | 45 | 45 | AHU | 15936 | 2.5452 | 1
247A | Classroom | 383 | 25 |  | 495 | 11 | 11 | AHU | 3960 | 5.803 | 2
249 | Classroom | 307 | 20 |  | 888 | 20 | 20 | AHU | 7104 | 2.5929 | 1
250 | Classroom | 121 | 8 |  | 142 | 3 | 3 | AHU | 1136 | 6.3908 | 2
251 | Classroom | 223 | 14 |  | 504 | 11 | 11 | AHU | 4032 | 3.3185 | 1
253 | Classroom | 0 | 0 |  | 939 | 21 | 0 | AHU | 7512 | 0 | 0
301 | Science Lab | 428 | 28 |  | 940 | 21 | 21 | AHU | 7520 | 3.4149 | 1
302 | science prep | 0 | 0 |  | 197 | 4 | 0 | AHU | 1576 | 0 | 0
304 | Classroom | 448 | 29 |  | 1086 | 24 | 24 | AHU | 8688 | 3.0939 | 1
305 | Classroom | 428 | 28 |  | 469 | 10 | 10 | AHU | 3752 | 6.8443 | 2
307 | Lab | 150 | 10 |  | 370 | 8 | 8 | AHU | 2960 | 3.0405 | 1
307B | Office | 205 | 13 |  | 161 | 3 | 3 | AHU | 1288 | 9.5497 | 2
307C | Office | 152 | 10 |  | 92 | 2 | 2 | AHU | 736 | 12.3913 | 3
308 | Science Lab | 360 | 24 |  | 1015 | 23 | 23 | AHU | 8120 | 2.6601 | 1
309 | Science Prep | 316 | 21 |  | 260 | 5 | 5 | AHU | 2080 | 9.1154 | 2
310 | Classroom | 331 | 22 |  | 990 | 22 | 22 | AHU | 7920 | 2.5076 | 1
311 | Classroom | 417 | 27 |  | 997 | 22 | 22 | AHU | 7976 | 3.1369 | 1
313 | Classroom | 389 | 25 |  | 716 | 16 | 16 | AHU | 5728 | 4.0747 | 2
314 | Classroom | 296 | 19 |  | 793 | 18 | 18 | AHU | 6344 | 2.7995 | 1
315 | Classroom | 410 | 27 |  | 804 | 18 | 18 | AHU | 6432 | 3.8246 | 1
316 | Classroom | 326 | 21 |  | 750 | 17 | 17 | AHU | 6000 | 3.26 | 1
317A | Office | 58 | 3 |  | 213 | 4 | 3 | AHU | 1704 | 2.0423 | 1
317B | Office | 42 | 2 |  | 220 | 5 | 2 | AHU | 1760 | 1.4318 | 1
318 | Classroom | 378 | 25 |  | 678 | 15 | 15 | AHU | 5424 | 4.1814 | 2
319 | Classroom | 329 | 21 |  | 678 | 15 | 15 | AHU | 5424 | 3.6394 | 1
320 | Classroom | 325 | 21 |  | 678 | 15 | 15 | AHU | 5424 | 3.5951 | 1
321 | Classroom | 367 | 24 |  | 678 | 15 | 15 | AHU | 5424 | 4.0597 | 2
322 | Faculty Lounge | 34 | 2 |  | 196 | 4 | 2 | AHU | 1568 | 1.301 | 1
324 | Classroom | 282 | 18 |  | 611 | 13 | 13 | AHU | 4888 | 3.4615 | 1
325 | Classroom | 326 | 21 |  | 703 | 15 | 15 | AHU | 5624 | 3.478 | 1
326 | Classroom | 280 | 18 |  | 681 | 15 | 15 | AHU | 5448 | 3.0837 | 1
327 | Classroom | 310 | 20 |  | 702 | 15 | 15 | AHU | 5616 | 3.312 | 1
328 | Office | 135 | 9 |  | 334 | 7 | 7 | AHU | 2672 | 3.0314 | 1
328A and B | Office | 229 | 15 |  | 391 | 8 | 8 | AHU | 3128 | 4.3926 | 2
329 | Classroom | 310 | 20 |  | 573 | 13 | 13 | AHU | 4584 | 4.0576 | 2
330 | Classroom | 330 | 22 |  | 573 | 13 | 13 | AHU | 4584 | 4.3194 | 2
331 | Classroom | 425 | 28 |  | 708 | 16 | 16 | AHU | 5664 | 4.5021 | 2
333 | Classroom | 304 | 20 |  | 697 | 15 | 15 | AHU | 5576 | 3.2712 | 1
334 | Classroom | 296 | 19 |  | 631 | 14 | 14 | AHU | 5048 | 3.5182 | 1
335 | Classroom | 280 | 18 |  | 614 | 13 | 13 | AHU | 4912 | 3.4202 | 1
336 | Classroom | 282 | 18 |  | 632 | 14 | 14 | AHU | 5056 | 3.3465 | 1
338 | Classroom | 283 | 18 |  | 678 | 15 | 15 | AHU | 5424 | 3.1305 | 1
339 | Office | 47 | 3 |  | 322 | 7 | 3 | AHU | 2576 | 1.0947 | 1
340 | Classroom | 281 | 18 |  | 931 | 21 | 18 | AHU | 7448 | 2.2637 | 1
341A | Classroom | 300 | 20 |  | 834 | 18 | 18 | AHU | 6672 | 2.6978 | 1
341B | Classroom | 122 | 8 |  | 262 | 5 | 5 | AHU | 2096 | 3.4924 | 1
342 | Classroom | 332 | 22 |  | 587 | 13 | 13 | AHU | 4696 | 4.2419 | 2
344 | Classroom | 311 | 20 |  | 820 | 18 | 18 | AHU | 6560 | 2.8445 | 1
345 | Classroom | 290 | 19 |  | 1154 | 26 | 19 | AHU | 9232 | 1.8847 | 1
- | Main office Rear reception desk | 79 | 5 |  | 429 | 9 | 5 | AHU | 3432 | 1.3811 | 1
- | Main office | 221 | 14 |  | 1109 | 25 | 14 | AHU | 8872 | 1.4946 | 1
- | Student Store | 236 | 15 |  | 339 | 7 | 7 | AHU | 2712 | 5.2212 | 2
- | Teaching Kitchen | 2167 | 144 |  | 2843 | 64 | 64 | AHU | 22744 | 5.7167 | 2
- | Cafeteria | 0 | 0 |  | 8970 | 203 | 0 | AHU | 71760 | 0 | 0
- | Teaching Kitchen | 2480 | 165 |  | 1316 | 29 | 29 | AHU | 10528 | 14.1337 | 3
- | Kitchen | 1030 | 68 |  | 1361 | 30 | 30 | AHU | 10888 | 5.676 | 2
- | Kitchen Hood | 3846 | 256 |  | N/A | 0 | 0 | AHU | #VALUE! | #VALUE! | #VALUE!
- | Auditorium | 6454 | 430 |  | 5600 | 127 | 127 | AHU | 44800 | 8.6438 | 2
- | 1st Floor NE | 176 | 11 |  | 20126 | 457 | 11 | AHU | 161008 | 0.065587 | 0
- | Heavy Equipment | 2723 | 181 |  | 3189 | 72 | 72 | AHU | 25512 | 6.404 | 2
- | Autobody | 4337 | 289 |  | 444 | 10 | 10 | AHU | 3552 | 73.2601 | 5
- | Welding | 1296 | 86 |  | 520 | 11 | 11 | AHU | 4160 | 18.6923 | 3
- | Sheet Metal | 3436 | 229 |  | 514 | 11 | 11 | AHU | 4112 | 50.1362 | 5
- | Warehouse Classroom | 8094 | 539 |  | 533 | 12 | 12 | AHU | 4264 | 113.8931 | 5
- | Gym | 7088 | 472 |  | 15450 | 351 | 351 | AHU | 123600 | 3.4408 | 1
- | Factory Lab | 3833 | 255 |  | 417 | 9 | 9 | AHU | 3336 | 68.9388 | 5
- | 1st Floor | 210 | 14 |  | 2760 | 62 | 14 | AHU | 22080 | 0.57065 | 0
- | Vending Machine Repair | 317 | 21 |  | 3167 | 71 | 21 | AHU | 25336 | 0.75071 | 0
- | Boiler Room | 3303 | 220 |  | 4914 | 111 | 111 | AHU | 39312 | 5.0412 | 2
- | Maint. Break room | 153 | 10 |  | 461 | 10 | 10 | AHU | 3688 | 2.4892 | 1
- | Eng. Office | 128 | 8 |  | 187 | 4 | 4 | AHU | 1496 | 5.1337 | 2
- | Weight Room | 990 | 66 |  | 939 | 21 | 21 | AHU | 7512 | 7.9073 | 2
- | Offices | 3928 | 261 |  | 90 | 2 | 2 | AHU | 720 | 327.3333 | 6
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21 | [7 empty] | 0 | 0 | 0
School: | Franklin S. Edmonds Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B1 | Classroom | 0 | 0 | Yes | 400 | 9 | 9 | Unit Ventilator | 3200 | 0 | 0
B2 | Kitchen | 75 | 5 |  | 572 | 13 | 5 | Unit Ventilator | 4576 | 0.98339 | 0
B3 | Kitchen | 165 | 11 |  | 480 | 10 | 10 | Unit Ventilator | 3840 | 2.5781 | 1
H2 | Office |  | 0 | Yes | 178 | 4 | 4 |  | 1424 | 0 | 0
101 | Classroom | 165 | 11 | Yes | 1128 | 25 | 25 | Unit Ventilator | 9024 | 1.0971 | 1
102 | Classroom | 441 | 29 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.1321 | 1
103 | Classroom | 397 | 26 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.4462 | 1
104 | Classroom | 455 | 30 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.2315 | 1
105 | Classroom | 412 | 27 |  | 1128 | 25 | 25 | Unit Ventilator | 9024 | 2.7394 | 1
106 | Classroom | 460 | 30 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.267 | 1
107 | Classroom | 256 | 17 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 2.6667 | 1
108 | Classroom | 567 | 37 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 4.027 | 2
109 | Classroom | 527 | 35 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.7429 | 1
110 | Classroom | 431 | 28 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.0611 | 1
111 | Classroom | 634 | 42 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 4.7173 | 2
112A | Office |  | 0 | Yes | 364 | 8 | 8 | Not supplied | 2912 | 0 | 0
112B | Office |  | 0 | Yes | 210 | 4 | 4 |  | 1680 | 0 | 0
113 | Classroom | 662 | 44 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 4.9256 | 2
114 | Office |  | 0 | Yes | 364 | 8 | 8 | Unit Ventilator | 2912 | 0 | 0
115 | Classroom | 551 | 36 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 4.0997 | 2
115A | Office |  | 0 | Yes | 252 | 5 | 5 |  | 2016 | 0 | 0
116 | Classroom | 169 | 11 | Yes | 736 | 16 | 16 | Unit Ventilator | 5888 | 1.7221 | 1
117 | Classroom | 299 | 19 |  | 912 | 20 | 19 | Unit Ventilator | 7296 | 2.4589 | 1
118 | Classroom | 281 | 18 |  | 912 | 20 | 18 | Unit Ventilator | 7296 | 2.3109 | 1
118A | Office |  | 0 |  | 175 | 3 | 0 |  | 1400 | 0 | 0
119 | Classroom | 282 | 18 |  | 912 | 20 | 18 | Unit Ventilator | 7296 | 2.3191 | 1
120 | Classroom | 0 | 0 | Yes | 912 | 20 | 20 | Unit Ventilator | 7296 | 0 | 0
121 | Classroom | 0 | 0 | Yes | 912 | 20 | 20 | Unit Ventilator | 7296 | 0 | 0
122 | Classroom | 340 | 22 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 2.7961 | 1
201 | Classroom | 503 | 33 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.5724 | 1
202 | Classroom | 418 | 27 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.9688 | 1
203 | Classroom | 415 | 27 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.9474 | 1
204 | Classroom | 395 | 26 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.8054 | 1
205 | Classroom | 491 | 32 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.4872 | 1
206 | Classroom | 414 | 27 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.9403 | 1
207 | Classroom | 485 | 32 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.4446 | 1
208 | Classroom | 348 | 23 |  | 1056 | 24 | 23 | Unit Ventilator | 8448 | 2.4716 | 1
209 | Classroom | 431 | 28 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.0611 | 1
210 | Classroom | 304 | 20 |  | 1056 | 24 | 20 | Unit Ventilator | 8448 | 2.1591 | 1
211 | Classroom | 322 | 21 |  | 1056 | 24 | 21 | Unit Ventilator | 8448 | 2.2869 | 1
212 | Classroom | 31 | 2 | Yes | 1056 | 24 | 24 | Unit Ventilator | 8448 | 0.22017 | 0
213 | Classroom | 186 | 12 |  | 1008 | 22 | 12 | Unit Ventilator | 8064 | 1.3839 | 1
215 | Classroom | 509 | 33 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 3.7872 | 1
216 | Library | 969 | 64 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 7.2098 | 2
217 | Classroom | 503 | 33 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 3.7426 | 1
217-A | VP office |  | 0 | Yes | 252 | 5 | 5 | Convector | 2016 | 0 | 0
218 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0
219 | Classroom | 44 | 2 |  | 1008 | 22 | 2 | Unit Ventilator | 8064 | 0.32738 | 0
- | Auditorium | 1860 | 124 |  | 1849 | 42 | 42 | AHU | 14792 | 7.5446 | 2
- | Gym | 1195 | 79 |  | 2795 | 63 | 63 | AHU | 22360 | 3.2066 | 1
- | Lunch | 0 | 0 |  | 780 | 17 | 0 | Unit Ventilator | 6240 | 0 | 0
- | Cafeteria | 411 | 27 | Yes | 1560 | 35 | 35 | Unit Ventilator | 12480 | 1.976 | 1
- | Kitchen | 0 | 0 | Yes | 400 | 9 | 9 | Unit Ventilator | 3200 | 0 | 0
| Women Helper |  | 0 | Yes | 262 | 5 | 5 |  | 2096 | 0 | 0
- | Nurse | 0 | 0 | Yes | 280 | 6 | 6 | N/A | 2240 | 0 | 0
- | Prin. Office | 0 | 0 | Yes | 322 | 7 | 7 | Convector | 2576 | 0 | 0
- | Main Office | 0 | 0 | Yes | 650 | 14 | 14 | Convector | 5200 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | Lewis Elkin Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Part 1 | Devine Part 2 | Devine Part 3 | [5 empty] | 0 | 0 | 0
School: | Elkin Little School House | [7 empty] | 0 | 0 | 0
Vendor: | Devine | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Main Building | [8 empty] | 0 | 0 | 0
101 | Classroom | 391 | 26 |  | 420 | 9 | 9 | Unit Ventilator | 3360 | 6.9821 | 2
102 | Classroom | 0 | 0 | Yes | 1136 | 25 | 25 | Unit Ventilator | 9088 | 0 | 0
103 | Classroom | 299 | 19 | Yes | 1303 | 29 | 29 | Unit Ventilator | 10424 | 1.721 | 1
104 | Classroom | 293 | 19 |  | 1201 | 27 | 19 | Unit Ventilator | 9608 | 1.8297 | 1
105 | Classroom | 301 | 20 | Yes | 1269 | 28 | 28 | Unit Ventilator | 10152 | 1.779 | 1
106 | Classroom | 300 | 20 |  | 418 | 9 | 9 | Unit Ventilator | 3344 | 5.3828 | 2
107 | Classroom | 411 | 27 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 3.4365 | 1
108 | Classroom | 386 | 25 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 3.2274 | 1
109 | Classroom | 389 | 25 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 3.2525 | 1
110 | Classroom | 376 | 25 |  | 821 | 18 | 18 | Unit Ventilator | 6568 | 3.4348 | 1
111 | Classroom | 313 | 20 |  | 938 | 21 | 20 | Unit Ventilator | 7504 | 2.5027 | 1
112 | Classroom | 363 | 24 |  | 898 | 20 | 20 | Unit Ventilator | 7184 | 3.0317 | 1
113 | Classroom | 318 | 21 |  | 898 | 20 | 20 | Unit Ventilator | 7184 | 2.6559 | 1
114 | Classroom | 349 | 23 |  | 898 | 20 | 20 | Unit Ventilator | 7184 | 2.9148 | 1
115 | Classroom | 345 | 23 |  | 1024 | 23 | 23 | Unit Ventilator | 8192 | 2.5269 | 1
116 | Lounge | 133 | 8 |  | 309 | 7 | 7 | Unit Ventilator | 2472 | 3.2282 | 1
117 | Classroom | 129 | 8 |  | 215 | 4 | 4 | Unit Ventilator | 1720 | 4.5 | 2
117 | Office | 96 | 6 |  | 317 | 7 | 6 | Unit Ventilator | 2536 | 2.2713 | 1
117A | Classroom Vestibule | 171 | 11 |  | 102 | 2 | 2 | Unit Ventilator | 816 | 12.5735 | 3
118 | Office | 109 | 7 |  | 122 | 2 | 2 | Unit Ventilator | 976 | 6.7008 | 2
119 | Office | 105 | 7 |  | 117 | 2 | 2 | Unit Ventilator | 936 | 6.7308 | 2
120 | Security Office | 214 | 14 |  | 259 | 5 | 5 | Unit Ventilator | 2072 | 6.1969 | 2
121 | Office |  | 0 | Yes | 400 | 9 | 9 |  | 3200 | 0 | 0
201 | Classroom | 496 | 33 |  | 772 | 17 | 17 | Unit Ventilator | 6176 | 4.8187 | 2
202 | Classroom | 325 | 21 |  | 933 | 21 | 21 | Unit Ventilator | 7464 | 2.6125 | 1
203 | Classroom | 385 | 25 |  | 838 | 19 | 19 | Unit Ventilator | 6704 | 3.4457 | 1
204 | Classroom | 360 | 24 |  | 756 | 17 | 17 | Unit Ventilator | 6048 | 3.5714 | 1
204A | Office | 178 | 11 |  | 201 | 4 | 4 | Unit Ventilator | 1608 | 6.6418 | 2
205 | Classroom | 334 | 22 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 3.0736 | 1
206 | Classroom | 402 | 26 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 3.6994 | 1
207 | Classroom | 357 | 23 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 3.2853 | 1
207A | Office | 74 | 4 |  | 201 | 4 | 4 | Unit Ventilator | 1608 | 2.7612 | 1
208 | Classroom | 388 | 25 |  | 762 | 17 | 17 | Unit Ventilator | 6096 | 3.8189 | 1
209 | Classroom | 365 | 24 |  | 811 | 18 | 18 | Unit Ventilator | 6488 | 3.3755 | 1
210 | Classroom | 285 | 19 |  | 814 | 18 | 18 | Unit Ventilator | 6512 | 2.6259 | 1
211 | Classroom | 430 | 28 |  | 746 | 16 | 16 | Unit Ventilator | 5968 | 4.3231 | 2
211A | Office | 161 | 10 |  | 201 | 4 | 4 | Unit Ventilator | 1608 | 6.0075 | 2
212 | Classroom | 312 | 20 |  | 810 | 18 | 18 | Unit Ventilator | 6480 | 2.8889 | 1
213 | Classroom | 358 | 23 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 3.2945 | 1
214 | Classroom | 376 | 25 |  | 786 | 17 | 17 | Unit Ventilator | 6288 | 3.5878 | 1
215 | Classroom | 0 | 0 | Yes | 863 | 19 | 19 | Unit Ventilator | 6904 | 0 | 0
215A | Classroom | 131 | 8 |  | 201 | 4 | 4 | Unit Ventilator | 1608 | 4.8881 | 2
216 | Classroom | 395 | 26 |  | 855 | 19 | 19 | Unit Ventilator | 6840 | 3.4649 | 1
217 | Classroom | 493 | 32 |  | 1259 | 28 | 28 | Unit Ventilator | 10072 | 2.9369 | 1
218 | Classroom | 437 | 29 |  | 788 | 17 | 17 | Unit Ventilator | 6304 | 4.1593 | 2
219 | Classroom | 76 | 5 |  | 117 | 2 | 2 | Unit Ventilator | 936 | 4.8718 | 2
220 | Library | 1770 | 118 |  | 2982 | 67 | 67 | Unit Ventilator | 23856 | 4.4517 | 2
220A | Office | 214 | 14 |  | 373 | 8 | 8 | Unit Ventilator | 2984 | 4.3029 | 2
220B | Office | 0 | 0 |  | 421 | 9 | 0 | N/A | 3368 | 0 | 0
220C | Office | 0 | 0 |  | 398 | 9 | 0 | N/A | 3184 | 0 | 0
221 | Room | 0 | 0 |  | 141 | 3 | 0 | Unit Ventilator | 1128 | 0 | 0
B01 | Classroom | 360 | 24 |  | 1859 | 42 | 24 | Unit Ventilator | 14872 | 1.4524 | 1
B02 | Classroom | 364 | 24 |  | 928 | 21 | 21 | Unit Ventilator | 7424 | 2.9418 | 1
B03 | Classroom | 183 | 12 |  | 525 | 11 | 11 | Unit Ventilator | 4200 | 2.6143 | 1
B04 | Classroom | 300 | 20 |  | 613 | 13 | 13 | Unit Ventilator | 4904 | 3.6705 | 1
- | Assistant Principal's Office | 40 | 2 |  | 98 | 2 | 2 | Unit Ventilator | 784 | 3.0612 | 1
- | Auditorium | 0 | 0 |  | 7138 | 162 | 0 | Unit Ventilator | 57104 | 0 | 0
- | Main Office Conference Room | 0 | 0 |  | 181 | 4 | 0 | Unit Ventilator | 1448 | 0 | 0
- | Copy room | 34 | 2 |  | 179 | 4 | 2 | Unit Ventilator | 1432 | 1.4246 | 1
- | Parent Resources Office | 0 | 0 |  | 84 | 1 | 0 | Unit Ventilator | 672 | 0 | 0
- | Education Office | 57 | 3 |  | 207 | 4 | 3 | Unit Ventilator | 1656 | 2.0652 | 1
- | Gymnasium | 3457 | 230 |  | 4778 | 108 | 108 | Unit Ventilator | 38224 | 5.4264 | 2
- | Ms. Potts' Office | 46 | 3 |  | 133 | 3 | 3 | Unit Ventilator | 1064 | 2.594 | 1
- | Health Office/Nurses Area/Nurse's Suite | 480 | 32 |  | 637 | 14 | 14 | Unit Ventilator | 5096 | 5.6515 | 2
- | Cafeteria/Lunchroom | 1731 | 115 |  | 2558 | 58 | 58 | Unit Ventilator | 20464 | 5.0753 | 2
- | Principal's Office | 34 | 2 |  | 167 | 3 | 2 | Unit Ventilator | 1336 | 1.5269 | 1
- | Main Office | 235 | 15 | Yes | 674 | 15 | 15 | Unit Ventilator | 5392 | 2.615 | 1
- | Teacher's Lounge | 0 | 0 |  | 623 | 14 | 0 | Unit Ventilator | 4984 | 0 | 0
- | Library (Wall mount unit, south area) | 33 | 2 |  | 2775 | 63 | 2 | Unit Ventilator | 22200 | 0.089189 | 0
LSH Building | [8 empty] | 0 | 0 | 0
1 | Classroom | 829 | 55 |  | 1018 | 23 | 23 | AHU | 8144 | 6.1076 | 2
2 | Classroom | 619 | 41 |  | 1018 | 23 | 23 | AHU | 8144 | 4.5604 | 2
3 | Classroom | 651 | 43 |  | 1018 | 23 | 23 | AHU | 8144 | 4.7962 | 2
4 | Classroom | 486 | 32 |  | 1018 | 23 | 23 | AHU | 8144 | 3.5806 | 1
5 | Classroom | 410 | 27 |  | 1018 | 23 | 23 | AHU | 8144 | 3.0206 | 1
6 | Classroom | 586 | 39 |  | 1018 | 23 | 23 | AHU | 8144 | 4.3173 | 2
7 | Classroom | 379 | 25 |  | 1018 | 23 | 23 | AHU | 8144 | 2.7922 | 1
8 | Classroom | 519 | 34 |  | 1018 | 23 | 23 | AHU | 8144 | 3.8237 | 1
- | Main Office | 0 | 0 |  | 295 | 6 | 0 | AHU | 2360 | 0 | 0
- | Multi Purpose Room | 1105 | 73 |  | 1995 | 45 | 45 | AHU | 15960 | 4.1541 | 2
- | Teacher's Lounge | 0 | 0 |  | 220 | 5 | 0 | AHU | 1760 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-12 | [7 empty] | 0 | 0 | 0
School: | Ellwood Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | Exhaust | Retest | [5 empty] | 0 | 0 | 0
| Devine 2nd Retest | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | 100 | 13 | 0 | Yes | 1465 | 33 | 33 | Unit Ventilator | 11720 | 0.066553 | 0
100 A | Counselor Office |  | 0 | Yes | 297 | 6 | 6 |  | 2376 | 0 | 0
100 B-C | Nurse |  | 0 | Yes | 342 | 7 | 7 |  | 2736 | 0 | 0
100 E | Main Office |  | 0 | Yes | 416 | 9 | 9 |  | 3328 | 0 | 0
102 | 102 | 414 | 27 |  | 574 | 13 | 13 | Unit Ventilator | 4592 | 5.4094 | 2
102 C | Principal |  | 0 | Yes | 400 | 9 | 9 |  | 3200 | 0 | 0
103 | 103 | 328 | 21 |  | 582 | 13 | 13 | Unit Ventilator | 4656 | 4.2268 | 2
104 | 104 | 392 | 26 |  | 701 | 15 | 15 | Unit Ventilator | 5608 | 4.194 | 2
105 | 105 | 457 | 30 |  | 1158 | 26 | 26 | Unit Ventilator | 9264 | 2.9598 | 1
107 | 107 | 420 | 28 |  | 905 | 20 | 20 | Unit Ventilator | 7240 | 3.4807 | 1
108 | 108 | 443 | 29 |  | 906 | 20 | 20 | Unit Ventilator | 7248 | 3.6672 | 1
109 | 109 | 468 | 31 |  | 904 | 20 | 20 | Unit Ventilator | 7232 | 3.8827 | 1
110 | 110 | 372 | 24 |  | 916 | 20 | 20 | Unit Ventilator | 7328 | 3.0459 | 1
111 | 111 | 260 | 17 |  | 448 | 10 | 10 | Unit Ventilator | 3584 | 4.3527 | 2
201 | 201 | 520 | 34 |  | 940 | 21 | 21 | Unit Ventilator | 7520 | 4.1489 | 2
202 | 202 | 195 | 13 |  | 912 | 20 | 13 | Unit Ventilator | 7296 | 1.6036 | 1
203 | 203 | 640 | 42 |  | 903 | 20 | 20 | Unit Ventilator | 7224 | 5.3156 | 2
204 | 204 | 430 | 28 |  | 914 | 20 | 20 | Unit Ventilator | 7312 | 3.5284 | 1
206 | 206 | 409 | 27 |  | 860 | 19 | 19 | Unit Ventilator | 6880 | 3.5669 | 1
207 | 207 | 423 | 28 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 3.4786 | 1
208 | 208 | 417 | 27 |  | 904 | 20 | 20 | Unit Ventilator | 7232 | 3.4596 | 1
210 | 210 | 154 | 10 |  | 903 | 20 | 10 | Unit Ventilator | 7224 | 1.2791 | 1
211 | 211 | 511 | 34 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 4.2023 | 2
212 | 212 | 534 | 35 |  | 975 | 22 | 22 | Unit Ventilator | 7800 | 4.1077 | 2
- | Auditorium | 0 | 0 |  | 2900 | 65 | 0 | AHU | 23200 | 0 | 0
- | Gym | 2115 | 141 |  | 3922 | 89 | 89 | AHU | 31376 | 4.0445 | 2
- | Library | 0 | 0 | Yes | 2809 | 63 | 63 | AHU | 22472 | 0 | 0
- | Floor 1 East Corridor | 0 | 0 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
- | Floor 1 East Corridor | 0 | 0 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
Sheet Last Modified: | 2021-03-17 | [7 empty] | 0 | 0 | 0
School: | Philadelphia Military Academy At Elverson | [7 empty] | 0 | 0 | 0
Vendor: | Meehan | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
103 | Conference room | 788 | 52 |  | 690 | 15 | 15 |  | 5520 | 8.5652 | 2
104 | IMC | 973 | 64 |  | 690 | 15 | 15 |  | 5520 | 10.5761 | 3
105 | Conference room | 354 | 23 |  | 690 | 15 | 15 |  | 5520 | 3.8478 | 1
106 | Weight room | 871 | 58 |  | 943 | 21 | 21 |  | 7544 | 6.9274 | 2
107 | Classroom | 1423 | 94 |  | 690 | 15 | 15 |  | 5520 | 15.4674 | 3
108 | Classroom | 787 | 52 |  | 690 | 15 | 15 |  | 5520 | 8.5543 | 2
111 | Classroom | 625 | 41 |  | 736 | 16 | 16 |  | 5888 | 6.3689 | 2
112 | Classroom | 112 | 7 |  | 736 | 16 | 7 |  | 5888 | 1.1413 | 1
113 | Classroom | 728 | 48 |  | 736 | 16 | 16 |  | 5888 | 7.4185 | 2
114 | Classroom | 525 | 35 |  | 1180 | 26 | 26 |  | 9440 | 3.3369 | 1
201 | Classroom | 1325 | 88 |  | 690 | 15 | 15 |  | 5520 | 14.4022 | 3
202 | Classroom | 180 | 12 |  | 690 | 15 | 12 |  | 5520 | 1.9565 | 1
203 | Classroom | 428 | 28 |  | 690 | 15 | 15 |  | 5520 | 4.6522 | 2
204 | Classroom | 487 | 32 |  | 690 | 15 | 15 |  | 5520 | 5.2935 | 2
205 | Classroom | 73 | 4 |  | 805 | 18 | 4 |  | 6440 | 0.68012 | 0
206 | Classroom | 796 | 53 |  | 943 | 21 | 21 |  | 7544 | 6.3309 | 2
207 | Classroom | 63 | 4 |  | 690 | 15 | 4 |  | 5520 | 0.68478 | 0
208 | Classroom | 445 | 29 |  | 690 | 15 | 15 |  | 5520 | 4.837 | 2
211 | Classroom | 0 | 0 |  | 736 | 16 | 0 |  | 5888 | 0 | 0
212 | Classroom | 0 | 0 |  | 736 | 16 | 0 |  | 5888 | 0 | 0
213 | Classroom | 670 | 44 |  | 736 | 16 | 16 |  | 5888 | 6.8274 | 2
214 | Classroom | 0 | 0 |  | 736 | 16 | 0 |  | 5888 | 0 | 0
215 | Classroom | 745 | 49 |  | 736 | 16 | 16 |  | 5888 | 7.5917 | 2
301 | Classroom | 142 | 9 |  | 690 | 15 | 9 |  | 5520 | 1.5435 | 1
302 | Classroom | 447 | 29 |  | 690 | 15 | 15 |  | 5520 | 4.8587 | 2
303 | Classroom | 117 | 7 |  | 690 | 15 | 7 |  | 5520 | 1.2717 | 1
304 | Classroom | 147 | 9 |  | 690 | 15 | 9 |  | 5520 | 1.5978 | 1
305 | Classroom | 120 | 8 |  | 805 | 18 | 8 |  | 6440 | 1.118 | 1
306 | Classroom | 796 | 53 |  | 1048 | 23 | 23 |  | 8384 | 5.6966 | 2
307 | Classroom | 370 | 24 |  | 690 | 15 | 15 |  | 5520 | 4.0217 | 2
308 | Classroom | 477 | 31 |  | 690 | 15 | 15 |  | 5520 | 5.1848 | 2
309 | Classroom | 115 | 7 |  | 690 | 15 | 7 |  | 5520 | 1.25 | 1
311 | Classroom | 572 | 38 |  | 736 | 16 | 16 |  | 5888 | 5.8288 | 2
312 | Classroom | 0 | 0 |  | 736 | 16 | 0 |  | 5888 | 0 | 0
313 | Classroom | 697 | 46 |  | 736 | 16 | 16 |  | 5888 | 7.1026 | 2
314 | Classroom | 0 | 0 |  | 736 | 16 | 0 |  | 5888 | 0 | 0
315 | Classroom | 0 | 0 |  | 736 | 16 | 0 |  | 5888 | 0 | 0
- | Cafeteria / Kitchen | 970 | 64 |  | 2595 | 58 | 58 |  | 20760 | 2.8035 | 1
- | Hallway | 462 | 30 |  | 1400 | 31 | 30 |  | 11200 | 2.475 | 1
- | Hallway | 0 | 0 |  | 1400 | 31 | 0 |  | 11200 | 0 | 0
- | Hallway | 432 | 28 |  | 1400 | 31 | 28 |  | 11200 | 2.3143 | 1
- | main office | 1050 | 70 |  | 744 | 16 | 16 |  | 5952 | 10.5847 | 3
- | Office / storage | 735 | 49 |  | 720 | 16 | 16 |  | 5760 | 7.6562 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21 | [7 empty] | 0 | 0 | 0
School: | Eleanor Emlen Elementary School | House fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Part 2 | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B001 | Classroom | 736 | 49 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 7.5 | 2
B002 | Classroom | 0 | 0 | Yes | 1848 | 42 | 42 | Unit Ventilator | 14784 | 0 | 0
B003 | Classroom | 994 | 66 |  | 1032 | 23 | 23 | Unit Ventilator | 8256 | 7.2238 | 2
B004A | Classroom | 701 | 46 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 6.8457 | 2
B004B | Classroom | 360 | 24 |  | 816 | 18 | 18 | Unit Ventilator | 6528 | 3.3088 | 1
B005 | Classroom | 419 | 27 |  | 546 | 12 | 12 | Unit Ventilator | 4368 | 5.7555 | 2
101 | Classroom | 857 | 57 |  | 768 | 17 | 17 | House Fan | 6144 | 8.3691 | 2
102 | Classroom | 267 | 17 |  | 690 | 15 | 15 | House Fan | 5520 | 2.9022 | 1
103 | Classroom | 517 | 34 |  | 690 | 15 | 15 | House Fan | 5520 | 5.6196 | 2
104 | Office | 193 | 12 |  | 88 | 2 | 2 | House Fan | 704 | 16.4489 | 3
104D | Waiting Room | 255 | 17 |  | 90 | 2 | 2 | House Fan | 720 | 21.25 | 3
104D | Office | 199 | 13 |  | 396 | 9 | 9 | House Fan | 3168 | 3.7689 | 1
104D | Storage | 136 | 9 |  | 207 | 4 | 4 | House Fan | 1656 | 4.9275 | 2
104D | Nurse | 173 | 11 |  | 144 | 3 | 3 | House Fan | 1152 | 9.0104 | 2
105 | Waiting Room | 174 | 11 |  | 248 | 5 | 5 | House Fan | 1984 | 5.2621 | 2
105A | Office | 93 | 6 |  | 182 | 4 | 4 | House Fan | 1456 | 3.8324 | 1
105B | Office | 85 | 5 |  | 126 | 2 | 2 | House Fan | 1008 | 5.0595 | 2
105C | Office | 103 | 6 |  | 126 | 2 | 2 | House Fan | 1008 | 6.131 | 2
106 | Classroom | 378 | 25 |  | 690 | 15 | 15 | House Fan | 5520 | 4.1087 | 2
107 | Classroom | 289 | 19 |  | 792 | 18 | 18 | House Fan | 6336 | 2.7367 | 1
108 | Classroom | 643 | 42 |  | 690 | 15 | 15 | House Fan | 5520 | 6.9891 | 2
109 | Classroom | 782 | 52 |  | 1050 | 23 | 23 | House Fan | 8400 | 5.5857 | 2
110 | Classroom | 485 | 32 |  | 621 | 14 | 14 | House Fan | 4968 | 5.8575 | 2
200 | Classroom | 0 | 0 | Yes | 528 | 12 | 12 | House Fan | 4224 | 0 | 0
201 | Classroom | 531 | 35 |  | 800 | 18 | 18 | House Fan | 6400 | 4.9781 | 2
202 | Classroom | 312 | 20 |  | 690 | 15 | 15 | House Fan | 5520 | 3.3913 | 1
203 | Classroom | 273 | 18 |  | 690 | 15 | 15 | House Fan | 5520 | 2.9674 | 1
204 | Classroom | 97 | 6 | Yes | 690 | 15 | 15 | House Fan | 5520 | 1.0543 | 1
205 | Classroom | 443 | 29 |  | 690 | 15 | 15 | House Fan | 5520 | 4.8152 | 2
206 | Classroom | 267 | 17 |  | 900 | 20 | 17 | House Fan | 7200 | 2.225 | 1
207 | Classroom | 372 | 24 |  | 690 | 15 | 15 | House Fan | 5520 | 4.0435 | 2
208 | Classroom | 437 | 29 |  | 805 | 18 | 18 | House Fan | 6440 | 4.0714 | 2
209 | Classroom | 504 | 33 |  | 690 | 15 | 15 | House Fan | 5520 | 5.4783 | 2
210 | Classroom | 361 | 24 |  | 690 | 15 | 15 | House Fan | 5520 | 3.9239 | 1
211 | Classroom | 416 | 27 |  | 690 | 15 | 15 | House Fan | 5520 | 4.5217 | 2
213 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
214 | Classroom | 0 | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
215 | Classroom | 0 | 0 | Yes | 744 | 16 | 16 | House Fan | 5952 | 0 | 0
216 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
217 | Classroom | 0 | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
218 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
301 | Classroom |  | 0 | Yes | 1190 | 27 |  |  | 9520 | 0 | 0
302 | Classroom | 695 | 46 |  | 660 | 15 | 15 | House Fan | 5280 | 7.8977 | 2
303 | Classroom | 99 | 6 | Yes | 660 | 15 | 15 | House Fan | 5280 | 1.125 | 1
304 | Classroom | 719 | 47 |  | 660 | 15 | 15 | House Fan | 5280 | 8.1705 | 2
305 | Classroom | 427 | 28 |  | 616 | 14 | 14 | House Fan | 4928 | 5.1989 | 2
306 | Classroom | 259 | 17 |  | 638 | 14 | 14 | House Fan | 5104 | 3.0447 | 1
307 | Classroom | 336 | 22 |  | 690 | 15 | 15 | House Fan | 5520 | 3.6522 | 1
308 | Classroom | 372 | 24 |  | 660 | 15 | 15 | House Fan | 5280 | 4.2273 | 2
308A | Classroom |  | 0 | Yes | 220 | 5 |  |  | 1760 | 0 | 0
309 | Classroom | 105 | 7 | Yes | 690 | 15 | 15 | House Fan | 5520 | 1.1413 | 1
310 | Classroom | 346 | 23 |  | 540 | 12 | 12 | House Fan | 4320 | 4.8056 | 2
311 | Classroom | 178 | 11 |  | 690 | 15 | 11 | House Fan | 5520 | 1.9348 | 1
Portable Building | Cafeteria 1 |  | 0 |  | 1840 | 41 |  |  | 14720 | 0 | 0
Portable Building | Cafeteria 2 |  | 0 |  | 989 | 22 |  |  | 7912 | 0 | 0
- | Auditorium | 0 | 0 | Yes | 5336 | 121 | 121 | House Fan | 42688 | 0 | 0
- | Basement Office/Classroom | 617 | 41 |  | 1088 | 24 | 24 | House Fan | 8704 | 4.2532 | 2
- | Gym | 3331 | 222 |  | 5005 | 113 | 113 | AHU | 40040 | 4.9915 | 2
- | Prinicipal Office |  | 0 |  | 108 | 2 | 0 |  | 864 | 0 | 0
- | Main Office |  | 0 |  | 234 | 5 | 0 |  | 1872 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | Louis H. Farrell Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | Retest | [6 empty] | 0 | 0 | 0
| Devine 2nd Retest | Devine 3rd Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
A-2 | LS | 269 | 17 |  | 891 | 20 | 17 | Unit Ventilator | 7128 | 2.2643 | 1
A-3 | LS | 319 | 21 |  | 891 | 20 | 20 | Unit Ventilator | 7128 | 2.6852 | 1
A-4 | LS | 259 | 17 |  | 540 | 12 | 12 | Unit Ventilator | 4320 | 3.5972 | 1
A-6 | LS | 274 | 18 |  | 891 | 20 | 18 | Unit Ventilator | 7128 | 2.3064 | 1
A-10 | A-10 | 290 | 19 |  | 1130 | 25 | 19 | RTU | 9040 | 1.9248 | 1
A-11 | A-11 | 276 | 18 |  | 800 | 18 | 18 | RTU | 6400 | 2.5875 | 1
A-12 | A-12 | 296 | 19 |  | 800 | 18 | 18 | RTU | 6400 | 2.775 | 1
A-13 | A-13 | 306 | 20 |  | 800 | 18 | 18 | RTU | 6400 | 2.8687 | 1
A-14 | A-14 | 293 | 19 |  | 800 | 18 | 18 | RTU | 6400 | 2.7469 | 1
A-15 | A-15 | 331 | 22 |  | 800 | 18 | 18 | RTU | 6400 | 3.1031 | 1
A-16 | A-16 | 303 | 20 |  | 800 | 18 | 18 | RTU | 6400 | 2.8406 | 1
A-21 | A-21 | 314 | 20 |  | 800 | 18 | 18 | RTU | 6400 | 2.9438 | 1
A-22 | A-22 | 285 | 19 |  | 800 | 18 | 18 | RTU | 6400 | 2.6719 | 1
A-23 | A-23 | 293 | 19 |  | 800 | 18 | 18 | RTU | 6400 | 2.7469 | 1
A-24 | A-24 | 293 | 19 |  | 800 | 18 | 18 | RTU | 6400 | 2.7469 | 1
A-25 | A-25 | 333 | 22 |  | 800 | 18 | 18 | RTU | 6400 | 3.1219 | 1
A-26 | A-26 | 316 | 21 |  | 800 | 18 | 18 | RTU | 6400 | 2.9625 | 1
100 | LS | 328 | 21 |  | 1813 | 41 | 21 | Unit Ventilator | 14504 | 1.3569 | 1
101 | LS | 326 | 21 |  | 1813 | 41 | 21 | Unit Ventilator | 14504 | 1.3486 | 1
103 | LS | 406 | 27 |  | 925 | 21 | 21 | Unit Ventilator | 7400 | 3.2919 | 1
105 | AS | 318 | 21 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 3.5491 | 1
108 |  |  |  | Yes | 350 |  |  | N/A | 2800 | 0 | 0
111 | AS | 241 | 16 |  | 950 | 21 | 16 | Unit Ventilator | 7600 | 1.9026 | 1
112 | ? | 282 | 18 |  | 950 | 21 | 18 | Unit Ventilator | 7600 | 2.2263 | 1
113 | ? | 222 | 14 |  | 950 | 21 | 14 | Unit Ventilator | 7600 | 1.7526 | 1
200 | LIT/SS | 318 | 21 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 2.5105 | 1
201 | M/SC | 278 | 18 |  | 950 | 21 | 18 | Unit Ventilator | 7600 | 2.1947 | 1
202 | LS | 297 | 19 |  | 950 | 21 | 19 | Unit Ventilator | 7600 | 2.3447 | 1
203 | RELA/LS/EL PI | 297 | 19 |  | 950 | 21 | 19 | Unit Ventilator | 7600 | 2.3447 | 1
204 | Classroom |  | 0 | Yes | 288 | 6 | 6 | Unit Ventilator | 2304 | 0 | 0
205 | M/SC/SS | 345 | 23 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 2.7237 | 1
206 | RELA | 327 | 21 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 2.5816 | 1
207 | ESOL | 372 | 24 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 2.9368 | 1
208 | MATH | 308 | 20 |  | 950 | 21 | 20 | Unit Ventilator | 7600 | 2.4316 | 1
209 | M/SC/SS | 294 | 19 |  | 950 | 21 | 19 | Unit Ventilator | 7600 | 2.3211 | 1
209A |  |  |  | Yes | 310 |  |  | N/A | 2480 | 0 | 0
210 | RELA/SS | 203 | 13 |  | 950 | 21 | 13 | Unit Ventilator | 7600 | 1.6026 | 1
211 | MATH/SC | 245 | 16 |  | 950 | 21 | 16 | Unit Ventilator | 7600 | 1.9342 | 1
212 | RELA | 293 | 19 |  | 950 | 21 | 19 | Unit Ventilator | 7600 | 2.3132 | 1
213 | SC/SS | 283 | 18 |  | 950 | 21 | 18 | Unit Ventilator | 7600 | 2.2342 | 1
300 | RELA / SS | 265 | 17 |  | 950 | 21 | 17 | Unit Ventilator | 7600 | 2.0921 | 1
301 | CSC | 277 | 18 |  | 950 | 21 | 18 | Unit Ventilator | 7600 | 2.1868 | 1
302 | MATH | 254 | 16 |  | 950 | 21 | 16 | Unit Ventilator | 7600 | 2.0053 | 1
303 | SC/SS | 224 | 14 |  | 950 | 21 | 14 | Unit Ventilator | 7600 | 1.7684 | 1
304 | Room |  | 0 | Yes | 192 | 4 | 4 |  | 1536 | 0 | 0
305 | SC/MATH | 287 | 19 |  | 950 | 21 | 19 | Unit Ventilator | 7600 | 2.2658 | 1
306 | MATH | 300 | 20 |  | 950 | 21 | 20 | Unit Ventilator | 7600 | 2.3684 | 1
307 | SS/RELA | 226 | 15 |  | 950 | 21 | 15 | Unit Ventilator | 7600 | 1.7842 | 1
308 | RELA/EL B | 277 | 18 |  | 950 | 21 | 18 | Unit Ventilator | 7600 | 2.1868 | 1
309 | SC/SS | 277 | 18 |  | 1175 | 26 | 18 | Unit Ventilator | 9400 | 1.7681 | 1
310 | MATH | 346 | 23 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 2.7316 | 1
311 | RELA EL PI | 232 | 15 |  | 950 | 21 | 15 | Unit Ventilator | 7600 | 1.8316 | 1
312 | SS/RELA ALG | 203 | 13 |  | 950 | 21 | 13 | Unit Ventilator | 7600 | 1.6026 | 1
313 | SC/MATH | 223 | 14 |  | 950 | 21 | 14 | Unit Ventilator | 7600 | 1.7605 | 1
- | Lunchroom | 815 | 54 |  | 2604 | 59 | 54 | Unit Ventilator | 20832 | 2.3474 | 1
Gymnasium | Gymnasium |  | 0 | Yes | 3940 | 89 | 89 |  | 31520 | 0 | 0
Gymnasium | Office |  | 0 | Yes | 247 | 5 | 5 |  | 1976 | 0 | 0
- | Auditorium | 72 | 4 |  | 3808 | 86 | 4 | Unit Ventilator | 30464 | 0.14181 | 0
- | Main Office |  | 0 | Yes | 279 | 6 | 6 | N/A | 2232 | 0 | 0
- | Principal Office |  | 0 |  | 288 | 6 | 0 | N/A | 2304 | 0 | 0
Vice Principal | Office |  | 0 | Yes | 96 | 2 | 2 |  | 768 | 0 | 0
- | Counselor Office |  | 0 | Yes | 288 | 6 | 6 | N/A | 2304 | 0 | 0
Building Engineer | Office |  | 0 | Yes | 275 | 6 | 6 |  | 2200 | 0 | 0
- | IMC |  | 0 | Yes | 1485 | 33 | 33 | N/A | 11880 | 0 | 0
- | Nurse |  | 0 | Yes | 234 | 5 | 5 | N/A | 1872 | 0 | 0
Sheet Last Modified: | 2021-03-23 | [7 empty] | 0 | 0 | 0
School: | D. Newlin Fell Elementary-Middle School | House fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
2 | Music Room | 519 | 34 |  | 418 | 9 | 9 | House Fan | 3344 | 9.3122 | 2
100 | Classroom | 677 | 45 |  | 704 | 16 | 16 | House Fan | 5632 | 7.2124 | 2
101 | Classroom | 791 | 52 |  | 308 | 7 | 7 | House Fan | 2464 | 19.2614 | 3
102 | Classroom | 653 | 43 |  | 704 | 16 | 16 | House Fan | 5632 | 6.9567 | 2
103 | Classroom | 588 | 39 |  | 660 | 15 | 15 | House Fan | 5280 | 6.6818 | 2
104 | Classroom | 604 | 40 |  | 660 | 15 | 15 | House Fan | 5280 | 6.8636 | 2
105 | Classroom | 960 | 64 |  | 660 | 15 | 15 | House Fan | 5280 | 10.9091 | 3
106 | Classroom | 560 | 37 |  | 660 | 15 | 15 | House Fan | 5280 | 6.3636 | 2
107 | Classroom | 760 | 50 |  | 682 | 15 | 15 | House Fan | 5456 | 8.3578 | 2
108 | Classroom | 550 | 36 |  | 638 | 14 | 14 | House Fan | 5104 | 6.4655 | 2
109 | Classroom | 491 | 32 |  | 687 | 15 | 15 | House Fan | 5496 | 5.3603 | 2
200 | Classroom | 362 | 24 |  | 682 | 15 | 15 | House Fan | 5456 | 3.9809 | 1
201 | Classroom | 750 | 50 |  | 638 | 14 | 14 | House Fan | 5104 | 8.8166 | 2
202 | Classroom | 840 | 56 |  | 682 | 15 | 15 | House Fan | 5456 | 9.2375 | 2
203 | Classroom | 411 | 27 |  | 660 | 15 | 15 | House Fan | 5280 | 4.6705 | 2
204 | Classroom | 952 | 63 |  | 660 | 15 | 15 | House Fan | 5280 | 10.8182 | 3
205 | Library | 670 | 44 |  | 638 | 14 | 14 | House Fan | 5104 | 7.8762 | 2
206 | Library | 668 | 44 |  | 638 | 14 | 14 | House Fan | 5104 | 7.8527 | 2
207 | Classroom | 512 | 34 |  | 682 | 15 | 15 | House Fan | 5456 | 5.6305 | 2
208 | Classroom | 765 | 51 |  | 638 | 14 | 14 | House Fan | 5104 | 8.9929 | 2
209 | Classroom | 478 | 31 |  | 682 | 15 | 15 | House Fan | 5456 | 5.2566 | 2
300 | Classroom | 500 | 33 |  | 704 | 16 | 16 | House Fan | 5632 | 5.3267 | 2
301 | Classroom | 406 | 27 |  | 638 | 14 | 14 | House Fan | 5104 | 4.7727 | 2
302 | Classroom | 110 | 7 |  | 682 | 15 | 7 | House Fan | 5456 | 1.2097 | 1
303 | Classroom | 426 | 28 |  | 660 | 15 | 15 | House Fan | 5280 | 4.8409 | 2
304 | Classroom | 630 | 42 |  | 660 | 15 | 15 | House Fan | 5280 | 7.1591 | 2
305 | Classroom | 888 | 59 |  | 660 | 15 | 15 | House Fan | 5280 | 10.0909 | 3
306 | Classroom | 791 | 52 |  | 660 | 15 | 15 | House Fan | 5280 | 8.9886 | 2
307 | Classroom | 407 | 27 |  | 682 | 15 | 15 | House Fan | 5456 | 4.4758 | 2
308 | Classroom | 641 | 42 |  | 638 | 14 | 14 | House Fan | 5104 | 7.5353 | 2
309 | Classroom | 645 | 43 |  | 704 | 16 | 16 | House Fan | 5632 | 6.8714 | 2
309A | Classroom |  | 0 | Yes | 275 | 6 | 6 | N/A | 2200 | 0 | 0
310 | Classroom | 310 | 20 |  | 275 | 6 | 6 | House Fan | 2200 | 8.4545 | 2
- | Auditrium | 3031 | 202 |  | 3055 | 69 | 69 | House Fan | 24440 | 7.4411 | 2
- | Boys Bathroom | 300 | 20 |  | 114 | 2 | 2 | N/A | 912 | 19.7368 | 3
- | Cafeteria | 375 | 25 |  | 990 | 22 | 22 | House Fan | 7920 | 2.8409 | 1
- | Girls Bathroom | 421 | 28 |  | 96 | 2 | 2 | N/A | 768 | 32.8906 | 4
- | Gym | 0 | 0 | Yes | 3219 | 73 | 73 | N/A | 25752 | 0 | 0
- | Main Office | 0 | 0 | Yes | 330 | 7 | 7 | House Fan | 2640 | 0 | 0
- | Principal Office |  | 0 | Yes | 288 | 6 | 6 | N/A | 2304 | 0 | 0
- | Nurse Office | 0 | 0 | Yes | 220 | 5 | 5 | House Fan | 1760 | 0 | 0
- | PTA Room | 900 | 60 |  | 1540 | 35 | 35 | House Fan | 12320 | 4.3831 | 2
- | Speech Room | 438 | 29 |  | 506 | 11 | 11 | House Fan | 4048 | 6.4921 | 2
- | Teachers Lounge | 0 | 0 |  | 330 | 7 | 0 | House Fan | 2640 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | Samuel Fels High School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
A100 | Classroom | 69 | 4 |  | 290 | 6 | 4 |  | 2320 | 1.7845 | 1
A103 | Classroom | 125 | 8 |  | 870 | 19 | 8 |  | 6960 | 1.0776 | 1
A105 | Classroom | 148 | 9 |  | 870 | 19 | 9 |  | 6960 | 1.2759 | 1
A106 | Classroom | 147 | 9 |  | 870 | 19 | 9 |  | 6960 | 1.2672 | 1
A107 | Classroom | 135 | 9 |  | 870 | 19 | 9 |  | 6960 | 1.1638 | 1
A108 | Classroom | 39 | 2 |  | 870 | 19 | 2 |  | 6960 | 0.33621 | 0
A109 | Classroom | 162 | 10 |  | 870 | 19 | 10 |  | 6960 | 1.3966 | 1
A110 | Classroom | 162 | 10 |  | 870 | 19 | 10 |  | 6960 | 1.3966 | 1
A111 | Classroom | 167 | 11 |  | 870 | 19 | 11 |  | 6960 | 1.4397 | 1
A113 | Classroom | 161 | 10 |  | 870 | 19 | 10 |  | 6960 | 1.3879 | 1
A114 | Classroom | 0 | 0 |  | 930 | 21 | 0 |  | 7440 | 0 | 0
A120 | Office | 125 | 8 |  | 144 | 3 | 3 |  | 1152 | 6.5104 | 2
A123 | Classroom | 298 | 19 |  | 900 | 20 | 19 |  | 7200 | 2.4833 | 1
A124 | Classroom | 345 | 23 |  | 900 | 20 | 20 |  | 7200 | 2.875 | 1
A125 | Classroom | 376 | 25 |  | 900 | 20 | 20 |  | 7200 | 3.1333 | 1
A126 | Classroom | 266 | 17 |  | 900 | 20 | 17 |  | 7200 | 2.2167 | 1
A130 | Classroom | 697 | 46 |  | 900 | 20 | 20 |  | 7200 | 5.8083 | 2
A131 | Classroom | 155 | 10 |  | 900 | 20 | 10 |  | 7200 | 1.2917 | 1
A132 | Classroom | 291 | 19 |  | 960 | 21 | 19 |  | 7680 | 2.2734 | 1
A135 | Classroom | 645 | 43 |  | 960 | 21 | 21 |  | 7680 | 5.0391 | 2
A136 | Classroom | 162 | 10 |  | 960 | 21 | 10 |  | 7680 | 1.2656 | 1
A137 | Classroom | 229 | 15 |  | 1320 | 30 | 15 |  | 10560 | 1.3011 | 1
A138 | Classroom | 963 | 64 |  | 1376 | 31 | 31 |  | 11008 | 5.2489 | 2
A139 | Classroom | 161 | 10 |  | 1376 | 31 | 10 |  | 11008 | 0.87754 | 0
A140 | Classroom | 1027 | 68 |  | 1376 | 31 | 31 |  | 11008 | 5.5977 | 2
A142 | Classroom | 1338 | 89 |  | 1271 | 28 | 28 |  | 10168 | 7.8954 | 2
A143 | Classroom | 964 | 64 |  | 1505 | 34 | 34 |  | 12040 | 4.804 | 2
A144 | Classroom | 937 | 62 |  | 1394 | 31 | 31 |  | 11152 | 5.0412 | 2
A148 | Hallway | 193 | 12 |  |  | 0 | 0 |  | 0 | 0 | 0
A150 | Hallway | 255 | 17 |  |  | 0 | 0 |  | 0 | 0 | 0
A152 | Hallway | 180 | 12 |  |  | 0 | 0 |  | 0 | 0 | 0
A200 | Classroom | 451 | 30 |  | 290 | 6 | 6 |  | 2320 | 11.6638 | 3
A203 | Classroom | 252 | 16 |  | 870 | 19 | 16 |  | 6960 | 2.1724 | 1
A205 | Classroom | 332 | 22 |  | 870 | 19 | 19 |  | 6960 | 2.8621 | 1
A206 | Classroom | 911 | 60 |  | 870 | 19 | 19 |  | 6960 | 7.8534 | 2
A207 | Classroom | 536 | 35 |  | 870 | 19 | 19 |  | 6960 | 4.6207 | 2
A208 | Classroom | 1475 | 98 |  | 870 | 19 | 19 |  | 6960 | 12.7155 | 3
A209 | Classroom | 620 | 41 |  | 870 | 19 | 19 |  | 6960 | 5.3448 | 2
A210 | Classroom | 1060 | 70 |  | 870 | 19 | 19 |  | 6960 | 9.1379 | 2
A211 | Classroom | 1246 | 83 |  | 870 | 19 | 19 |  | 6960 | 10.7414 | 3
A212 | Classroom | 1262 | 84 |  | 1271 | 28 | 28 |  | 10168 | 7.4469 | 2
A213 | Classroom | 879 | 58 |  | 961 | 21 | 21 |  | 7688 | 6.86 | 2
A214 | Classroom | 667 | 44 |  | 961 | 21 | 21 |  | 7688 | 5.2055 | 2
A220 | Office | 7 | 0 |  | 144 | 3 | 0 |  | 1152 | 0.36458 | 0
A223 | Classroom | 486 | 32 |  | 1860 | 42 | 32 |  | 14880 | 1.9597 | 1
A225 | Classroom | 90 | 6 |  | 160 | 3 | 3 |  | 1280 | 4.2188 | 2
A226 | Classroom | 323 | 21 |  | 900 | 20 | 20 |  | 7200 | 2.6917 | 1
A227 | Classroom | 830 | 55 |  | 960 | 21 | 21 |  | 7680 | 6.4844 | 2
A231 | Classroom | 260 | 17 |  | 1320 | 30 | 17 |  | 10560 | 1.4773 | 1
A236 | Classroom | 8 | 0 |  | 120 | 2 | 0 |  | 960 | 0.5 | 0
A237 | Classroom | 9 | 0 |  | 104 | 2 | 0 |  | 832 | 0.64904 | 0
A238 | Classroom | 207 | 13 |  | 1680 | 38 | 13 |  | 13440 | 0.92411 | 0
A239 | Classroom | 1272 | 84 |  | 1376 | 31 | 31 |  | 11008 | 6.9331 | 2
A240 | Classroom | 249 | 16 |  | 224 | 5 | 5 |  | 1792 | 8.3371 | 2
A241 | Classroom | 1797 | 119 |  | 1364 | 31 | 31 |  | 10912 | 9.8809 | 2
A242 | Classroom | 1960 | 130 |  | 1320 | 30 | 30 |  | 10560 | 11.1364 | 3
A243 | Classroom | 960 | 64 |  | 1320 | 30 | 30 |  | 10560 | 5.4545 | 2
A244 | Classroom | 1222 | 81 |  | 1505 | 34 | 34 |  | 12040 | 6.0897 | 2
A245 | Classroom | 695 | 46 |  | 1394 | 31 | 31 |  | 11152 | 3.7392 | 1
A248 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
A250 | Hallway | 297 | 19 |  |  | 0 | 0 |  | 0 | 0 | 0
A252 | Hallway | 566 | 37 |  |  | 0 | 0 |  | 0 | 0 | 0
A255 | Classroom | 0 | 0 |  | 120 | 2 | 0 |  | 960 | 0 | 0
B100 | Classroom | 0 | 0 |  | 930 | 21 | 0 |  | 7440 | 0 | 0
B102 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0
B103 | Classroom | 0 | 0 |  | 1023 | 23 | 0 |  | 8184 | 0 | 0
B105 | Classroom | 0 | 0 |  | 1311 | 29 | 0 |  | 10488 | 0 | 0
B106 | Classroom | 0 | 0 |  | 280 | 6 | 0 |  | 2240 | 0 | 0
B107 | Classroom | 0 | 0 |  | 1265 | 28 | 0 |  | 10120 | 0 | 0
B108 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0
B109 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0
B117 | Classroom | 0 | 0 |  | 576 | 13 | 0 |  | 4608 | 0 | 0
B118 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0
B120 | Classroom | 0 | 0 |  | 208 | 4 | 0 |  | 1664 | 0 | 0
B123 | Classroom | 0 | 0 |  | 990 | 22 | 0 |  | 7920 | 0 | 0
B124 | Classroom | 0 | 0 |  | 990 | 22 | 0 |  | 7920 | 0 | 0
B125 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
B126 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
B127 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
B128 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
B200 | Classroom | 0 | 0 |  | 930 | 21 | 0 |  | 7440 | 0 | 0
B201 | Classroom | 0 | 0 |  | 1316 | 29 | 0 |  | 10528 | 0 | 0
B201B | Classroom | 0 | 0 |  | 224 | 5 | 0 |  | 1792 | 0 | 0
B202 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0
B203 | Classroom | 0 | 0 |  | 1023 | 23 | 0 |  | 8184 | 0 | 0
B204 | Classroom | 0 | 0 |  | 1311 | 29 | 0 |  | 10488 | 0 | 0
B205 | Classroom | 0 | 0 |  | 1265 | 28 | 0 |  | 10120 | 0 | 0
B208 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0
B209 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0
B210 | Classroom | 0 | 0 |  | 144 | 3 | 0 |  | 1152 | 0 | 0
B218 | Classroom | 0 | 0 |  | 990 | 22 | 0 |  | 7920 | 0 | 0
B219 | Classroom | 0 | 0 |  | 990 | 22 | 0 |  | 7920 | 0 | 0
B222 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
B223 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
B224 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
B225 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
C101 | Front of house | 160 | 10 |  | 384 | 8 | 8 |  | 3072 | 3.125 | 1
C103 | Auditorium | 12689 | 845 |  | 9310 | 211 | 211 |  | 74480 | 10.2221 | 3
C105 | Stage | 770 | 51 |  | 3400 | 77 | 51 |  | 27200 | 1.6985 | 1
C106 | Classroom | 0 | 0 |  | 1302 | 29 | 0 |  | 10416 | 0 | 0
C107 | Backstage | 59 | 3 |  | 870 | 19 | 3 |  | 6960 | 0.50862 | 0
C108 | Classroom | 39 | 2 |  | 870 | 19 | 2 |  | 6960 | 0.33621 | 0
C109 | Classroom | 77 | 5 |  | 870 | 19 | 5 |  | 6960 | 0.66379 | 0
C110 | Classroom | 89 | 5 |  | 870 | 19 | 5 |  | 6960 | 0.76724 | 0
C111 | Classroom | 576 | 38 |  | 870 | 19 | 19 |  | 6960 | 4.9655 | 2
C112 | Classroom | 112 | 7 |  | 870 | 19 | 7 |  | 6960 | 0.96552 | 0
C113 | Classroom | 1414 | 94 |  | 2016 | 45 | 45 |  | 16128 | 5.2604 | 2
C114 | Classroom | 20 | 1 |  | 870 | 19 | 1 |  | 6960 | 0.17241 | 0
C115 | Classroom | 18 | 1 |  | 840 | 19 | 1 |  | 6720 | 0.16071 | 0
C116 | Classroom | 20 | 1 |  | 840 | 19 | 1 |  | 6720 | 0.17857 | 0
C117 | Classroom | 18 | 1 |  | 840 | 19 | 1 |  | 6720 | 0.16071 | 0
C118 | Classroom | 210 | 14 |  | 840 | 19 | 14 |  | 6720 | 1.875 | 1
C119 | Classroom | 168 | 11 |  | 840 | 19 | 11 |  | 6720 | 1.5 | 1
C121 | Classroom | 0 | 0 |  | 840 | 19 | 0 |  | 6720 | 0 | 0
D104 | Locker room | 4 | 0 |  | 1680 | 38 | 0 |  | 13440 | 0.017857 | 0
D105 | Locker room | 5 | 0 |  | 1680 | 38 | 0 |  | 13440 | 0.022321 | 0
D106 | Office | 25 | 1 |  | 120 | 2 | 1 |  | 960 | 1.5625 | 1
D109 | Locker room | 12 | 0 |  | 522 | 11 | 0 |  | 4176 | 0.17241 | 0
D111 | Locker room | 8 | 0 |  | 522 | 11 | 0 |  | 4176 | 0.11494 | 0
D112 | Office | 22 | 1 |  | 240 | 5 | 1 |  | 1920 | 0.6875 | 0
D113 | Office | 26 | 1 |  | 240 | 5 | 1 |  | 1920 | 0.8125 | 0
D114 | Locker room | 39 | 2 |  | 720 | 16 | 2 |  | 5760 | 0.40625 | 0
D115 | Office | 0 | 0 |  | 260 | 5 | 0 |  | 2080 | 0 | 0
D116 | Weight room | 181 | 12 |  | 1392 | 31 | 12 |  | 11136 | 0.97522 | 0
D119 | Classroom | 91 | 6 |  | 1240 | 28 | 6 |  | 9920 | 0.5504 | 0
D126 | Vestibule | 42 | 2 |  |  | 0 | 0 |  | 0 | 0 | 0
D128 | Hallway | 249 | 16 |  |  | 0 | 0 |  | 0 | 0 | 0
E100A | Library | 274 | 18 |  | 9200 | 209 | 18 |  | 73600 | 0.22337 | 0
E100B | Office | 28 | 1 |  | 225 | 5 | 1 |  | 1800 | 0.93333 | 0
E101 | Classroom | 17 | 1 |  | 992 | 22 | 1 |  | 7936 | 0.12853 | 0
E102 | Office | 12 | 0 |  | 225 | 5 | 0 |  | 1800 | 0.4 | 0
E103 | Office | 14 | 0 |  | 225 | 5 | 0 |  | 1800 | 0.46667 | 0
E104 | Office | 0 | 0 |  | 150 | 3 | 0 |  | 1200 | 0 | 0
E105A | Storage | 6 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
E105B | Storage | 8 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
E107 | Office | 52 | 3 |  | 286 | 6 | 3 |  | 2288 | 1.3636 | 1
E111 | Office | 0 | 0 |  | 368 | 8 | 0 |  | 2944 | 0 | 0
E112 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
E113 | Office | 0 | 0 |  | 132 | 3 | 0 |  | 1056 | 0 | 0
E114 | Office | 0 | 0 |  | 84 | 1 | 0 |  | 672 | 0 | 0
E115 | Office | 0 | 0 |  | 180 | 4 | 0 |  | 1440 | 0 | 0
E116 | Office | 0 | 0 |  | 72 | 1 | 0 |  | 576 | 0 | 0
E117 | Office | 0 | 0 |  | 120 | 2 | 0 |  | 960 | 0 | 0
E118 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
E119 | Office | 0 | 0 |  | 400 | 9 | 0 |  | 3200 | 0 | 0
E120 | Office | 0 | 0 |  | 180 | 4 | 0 |  | 1440 | 0 | 0
E121 | Office | 0 | 0 |  | 180 | 4 | 0 |  | 1440 | 0 | 0
E123 | Office | 0 | 0 |  | 220 | 5 | 0 |  | 1760 | 0 | 0
E124 | Office | 0 | 0 |  | 220 | 5 | 0 |  | 1760 | 0 | 0
E125 | Office | 0 | 0 |  | 150 | 3 | 0 |  | 1200 | 0 | 0
E126 | Office | 0 | 0 |  | 216 | 4 | 0 |  | 1728 | 0 | 0
E127 | Office | 0 | 0 |  | 90 | 2 | 0 |  | 720 | 0 | 0
E128 | Office | 0 | 0 |  | 150 | 3 | 0 |  | 1200 | 0 | 0
E129 | Office | 0 | 0 |  | 216 | 4 | 0 |  | 1728 | 0 | 0
E130 | Office | 0 | 0 |  | 285 | 6 | 0 |  | 2280 | 0 | 0
E131 | Office | 0 | 0 |  | 195 | 4 | 0 |  | 1560 | 0 | 0
E132 | Office | 0 | 0 |  | 195 | 4 | 0 |  | 1560 | 0 | 0
E133 | Office | 0 | 0 |  | 315 | 7 | 0 |  | 2520 | 0 | 0
E134 | Office | 0 | 0 |  | 315 | 7 | 0 |  | 2520 | 0 | 0
E137 | Office | 0 | 0 |  | 420 | 9 | 0 |  | 3360 | 0 | 0
E139 | Office | 0 | 0 |  | 264 | 6 | 0 |  | 2112 | 0 | 0
E144 | Server room | 0 | 0 |  | 368 | 8 | 0 |  | 2944 | 0 | 0
E146 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
E147 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
E148 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
E149 | Vestibule | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
E150 | Vestibule | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
E151 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
E152 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
E157 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
E201 | Office | 0 | 0 |  | 126 | 2 | 0 |  | 1008 | 0 | 0
E202 | Office | 0 | 0 |  | 126 | 2 | 0 |  | 1008 | 0 | 0
E203B | Office | 0 | 0 |  | 266 | 6 | 0 |  | 2128 | 0 | 0
E204 | Office | 0 | 0 |  | 126 | 2 | 0 |  | 1008 | 0 | 0
E205 | Office | 0 | 0 |  | 126 | 2 | 0 |  | 1008 | 0 | 0
E209 | Office | 0 | 0 |  | 1040 | 23 | 0 |  | 8320 | 0 | 0
E210 | Hallway | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
F100 | Cafeteria | 8136 | 542 |  | 8448 | 192 | 192 |  | 67584 | 7.223 | 2
F101 | Kitchen | 1521 | 101 |  | 1636 | 37 | 37 |  | 13088 | 6.9728 | 2
F104 | Kitchen | 81 | 5 |  | 230 | 5 | 5 |  | 1840 | 2.6413 | 1
F106 | Kitchen | 99 | 6 |  | 306 | 6 | 6 |  | 2448 | 2.4265 | 1
F107 | Kitchen | 0 | 0 |  | 401 | 9 | 0 |  | 3208 | 0 | 0
F108 | Kitchen | 199 | 13 |  | 836 | 19 | 13 |  | 6688 | 1.7853 | 1
F109 | Maintenance | 59 | 3 |  | 686 | 15 | 3 |  | 5488 | 0.64504 | 0
F110 | Maintenance | 40 | 2 |  | 256 | 5 | 2 |  | 2048 | 1.1719 | 1
F111 | Maintenance | 69 | 4 |  | 162 | 3 | 3 |  | 1296 | 3.1944 | 1
F112 | Maintenance | 89 | 5 |  | 340 | 7 | 5 |  | 2720 | 1.9632 | 1
F116 | Kitchen | 0 | 0 |  | 1636 | 37 | 0 |  | 13088 | 0 | 0
F119 | Engineer's office | 135 | 9 |  | 176 | 4 | 4 |  | 1408 | 5.7528 | 2
F120 | Hallway | 149 | 9 |  |  | 0 | 0 |  | 0 | 0 | 0
F121 | Hallway | 1306 | 87 |  |  | 0 | 0 |  | 0 | 0 | 0
- | Gym | 2098 | 139 |  | 13184 | 299 | 139 |  | 105472 | 1.1935 | 1
- | Office | 0 | 0 |  | 120 | 2 | 0 |  | 960 | 0 | 0
- | Storage | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
- | Pool | 5277 | 351 |  | 6426 | 146 | 146 |  | 51408 | 6.159 | 2
- | Principal Office | 0 | 0 |  | 288 | 6 | 0 |  | 2304 | 0 | 0
- | Stage | 3751 | 250 |  | 3400 | 77 | 77 |  | 27200 | 8.2743 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-06 | [7 empty] | 0 | 0 | 0
School: | Feltonville Arts & Sciences Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
104 | Classroom | 256 | 17 |  | 775 | 17 | 17 |  | 6200 | 2.4774 | 1
105 | Classroom | 614 | 40 |  | 810 | 18 | 18 |  | 6480 | 5.6852 | 2
106 | Classroom | 599 | 39 |  | 802 | 18 | 18 |  | 6416 | 5.6016 | 2
107 | Classroom | 428 | 28 |  | 804 | 18 | 18 |  | 6432 | 3.9925 | 1
108 | Classroom | 352 | 23 |  | 802 | 18 | 18 |  | 6416 | 3.2918 | 1
109 | Classroom | 699 | 46 |  | 791 | 17 | 17 |  | 6328 | 6.6277 | 2
110 | Classroom | 311 | 20 |  | 838 | 19 | 19 |  | 6704 | 2.7834 | 1
111 | Classroom | 232 | 15 |  | 953 | 21 | 15 |  | 7624 | 1.8258 | 1
112 | Classroom | 311 | 20 |  | 633 | 14 | 14 |  | 5064 | 3.6848 | 1
205 | Classroom | 455 | 30 |  | 774 | 17 | 17 |  | 6192 | 4.4089 | 2
206 | Classroom | 398 | 26 |  | 759 | 17 | 17 |  | 6072 | 3.9328 | 1
207 | Classroom | 352 | 23 |  | 749 | 17 | 17 |  | 5992 | 3.5247 | 1
208 | Classroom | 313 | 20 |  | 812 | 18 | 18 |  | 6496 | 2.891 | 1
210 | Classroom | 0 | 0 | Yes | 808 | 18 | 18 |  | 6464 | 0 | 0
211 | Classroom | 650 | 43 |  | 765 | 17 | 17 |  | 6120 | 6.3725 | 2
212 | Classroom | 283 | 18 |  | 802 | 18 | 18 |  | 6416 | 2.6465 | 1
214 | Classroom | 605 | 40 |  | 632 | 14 | 14 |  | 5056 | 7.1796 | 2
301 | Classroom | 288 | 19 |  | 776 | 17 | 17 |  | 6208 | 2.7835 | 1
302 | Classroom | 297 | 19 |  | 760 | 17 | 17 |  | 6080 | 2.9309 | 1
303 | Classroom | 305 | 20 |  | 817 | 18 | 18 |  | 6536 | 2.7999 | 1
304 | Classroom | 700 | 46 |  | 811 | 18 | 18 |  | 6488 | 6.4735 | 2
305 | Classroom | 357 | 23 |  | 808 | 18 | 18 |  | 6464 | 3.3137 | 1
306 | Classroom | 490 | 32 |  | 783 | 17 | 17 |  | 6264 | 4.6935 | 2
307 | Classroom | 309 | 20 |  | 803 | 18 | 18 |  | 6424 | 2.8861 | 1
308 | Classroom | 211 | 14 | Yes | 809 | 18 | 18 |  | 6472 | 1.9561 | 1
309 | Classroom | 1419 | 94 |  | 2223 | 50 | 50 |  | 17784 | 4.7874 | 2
- | Basement | 4061 | 270 |  | 4615 | 104 | 104 |  | 36920 | 6.5997 | 2
- | Cafeteria, Kitchen, Faculty Room | 761 | 50 |  | 5110 | 116 | 50 |  | 40880 | 1.1169 | 1
- | Classroom above 214 | 403 | 26 |  | 631 | 14 | 14 |  | 5048 | 4.79 | 2
- | Classroom Art Lab Computer Lab | 315 | 21 | Yes | 1017 | 23 | 23 |  | 8136 | 2.323 | 1
- | Classroom Science Lab 1 | 345 | 23 |  | 993 | 22 | 22 |  | 7944 | 2.6057 | 1
- | Classroom Science Lab 2 3rd Floor | 344 | 22 |  | 989 | 22 | 22 |  | 7912 | 2.6087 | 1
- | Classroom Science Lab 2 Right | 455 | 30 |  | 989 | 22 | 22 |  | 7912 | 3.4505 | 1
- | Classroom Science Lab STEM Lab Left | 740 | 49 |  | 1631 | 37 | 37 |  | 13048 | 3.4028 | 1
- | Dean's Office 1st Floor | 31 | 2 | Yes | 170 | 3 | 3 |  | 1360 | 1.3676 | 1
- | Dean's Office 2nd Floor | 18 | 1 | Yes | 170 | 3 | 3 |  | 1360 | 0.79412 | 0
- | Dean's Office 3rd Floor | 38 | 2 | Yes | 168 | 3 | 3 |  | 1344 | 1.6964 | 1
- | Drama Room | 747 | 49 |  | 3095 | 70 | 49 |  | 24760 | 1.8102 | 1
- | First Floor | 5315 | 354 |  | 6974 | 158 | 158 |  | 55792 | 5.7159 | 2
- | First Floor Multi-Purpose Room | 572 | 38 |  | 3095 | 70 | 38 |  | 24760 | 1.3861 | 1
- | Gym | 1186 | 79 |  | 5237 | 119 | 79 |  | 41896 | 1.6985 | 1
- | Health Room | 0 | 0 | Yes | 594 | 13 | 13 |  | 4752 | 0 | 0
- | Second Floor | 1094 | 72 |  | 4743 | 107 | 72 |  | 37944 | 1.7299 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Feltonville Intermediate Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | Exhaust Report | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | - |  | 0 | Yes | 462 | 10 | 10 |  | 3696 | 0 | 0
101 | - |  | 0 |  | 948 | 21 | 0 |  | 7584 | 0 | 0
101A | - |  | 0 |  | 127 | 2 | 0 |  | 1016 | 0 | 0
102 | - |  | 0 | Yes | 243 | 5 | 5 |  | 1944 | 0 | 0
103 | - |  | 0 |  | 101 | 2 | 0 |  | 808 | 0 | 0
103A | - |  | 0 |  | 125 | 2 | 0 |  | 1000 | 0 | 0
104 | - |  | 0 | Yes | 967 | 21 | 21 |  | 7736 | 0 | 0
106 | - |  | 0 | Yes | 1120 | 25 | 25 |  | 8960 | 0 | 0
107 | - |  | 0 |  | 213 | 4 | 0 |  | 1704 | 0 | 0
108 | Room |  | 0 | Yes | 1436 | 32 | 32 |  | 11488 | 0 | 0
109 | Room | 0 | 0 | Yes | 893 | 20 | 20 |  | 7144 | 0 | 0
110 | Room | 647 | 43 |  | 1479 | 33 | 33 |  | 11832 | 3.2809 | 1
112 | Room |  | 0 | Yes | 1415 | 32 | 32 |  | 11320 | 0 | 0
112A | - |  | 0 |  | 129 | 2 | 0 |  | 1032 | 0 | 0
113 | Room |  | 0 |  | 1200 | 27 | 0 |  | 9600 | 0 | 0
114 | - |  | 0 | Yes | 976 | 22 | 22 |  | 7808 | 0 | 0
116 | - |  | 0 |  | 1064 | 24 | 0 |  | 8512 | 0 | 0
118 | Gym Office | 0 | 0 |  | 1027 | 23 | 0 |  | 8216 | 0 | 0
153A | Small Office Inside M/O |  | 0 |  | 108 | 2 | 0 |  | 864 | 0 | 0
156B | Counselor #2 |  | 0 |  | 182 | 4 | 0 |  | 1456 | 0 | 0
157 | - |  | 0 |  | 108 | 2 | 0 |  | 864 | 0 | 0
200 | - |  | 0 |  | 478 | 10 | 0 |  | 3824 | 0 | 0
201 | - |  | 0 | Yes | 1071 | 24 | 24 |  | 8568 | 0 | 0
202 | - |  | 0 |  | 578 | 13 | 0 |  | 4624 | 0 | 0
202A | - |  | 0 |  | 179 | 4 | 0 |  | 1432 | 0 | 0
203 | - |  | 0 | Yes | 677 | 15 | 15 |  | 5416 | 0 | 0
203A | - |  | 0 |  | 436 | 9 | 0 |  | 3488 | 0 | 0
204 | - |  | 0 | Yes | 574 | 13 | 13 |  | 4592 | 0 | 0
205 | - |  | 0 |  | 829 | 18 | 0 |  | 6632 | 0 | 0
206 | - |  | 0 | Yes | 629 | 14 | 14 |  | 5032 | 0 | 0
206A | - |  | 0 |  | 220 | 5 | 0 |  | 1760 | 0 | 0
207 | - |  | 0 | Yes | 818 | 18 | 18 |  | 6544 | 0 | 0
207A | - |  | 0 |  | 126 | 2 | 0 |  | 1008 | 0 | 0
208 | - |  | 0 | Yes | 752 | 17 | 17 |  | 6016 | 0 | 0
208A | - |  | 0 |  | 113 | 2 | 0 |  | 904 | 0 | 0
209 | - |  | 0 | Yes | 788 | 17 | 17 |  | 6304 | 0 | 0
210 | - | 225 | 15 | Yes | 740 | 16 | 16 |  | 5920 | 2.2804 | 1
300 | - |  | 0 | Yes | 858 | 19 | 19 |  | 6864 | 0 | 0
301 | - |  | 0 | Yes | 491 | 11 | 11 |  | 3928 | 0 | 0
302 | - |  | 0 | Yes | 765 | 17 | 17 |  | 6120 | 0 | 0
303 | - |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
304 | - |  | 0 |  | 505 | 11 | 0 |  | 4040 | 0 | 0
305 | - |  | 0 | Yes | 626 | 14 | 14 |  | 5008 | 0 | 0
306 | - |  | 0 | Yes | 769 | 17 | 17 |  | 6152 | 0 | 0
307 | - |  | 0 | Yes | 1108 | 25 | 25 |  | 8864 | 0 | 0
307A | - |  | 0 |  | 73 | 1 | 0 |  | 584 | 0 | 0
307B | - |  | 0 |  | 127 | 2 | 0 |  | 1016 | 0 | 0
309 | - |  | 0 |  | 488 | 11 | 0 |  | 3904 | 0 | 0
309A | - |  | 0 |  | 135 | 3 | 0 |  | 1080 | 0 | 0
311 | - |  | 0 | Yes | 842 | 19 | 19 |  | 6736 | 0 | 0
313 | - |  | 0 | Yes | 662 | 15 | 15 |  | 5296 | 0 | 0
315 | - |  | 0 | Yes | 735 | 16 | 16 |  | 5880 | 0 | 0
- | Bradham Office |  | 0 |  | 141 | 3 | 0 |  | 1128 | 0 | 0
- | Cafeteria (2nd Floor) |  | 0 |  | 5423 | 123 | 0 |  | 43384 | 0 | 0
- | Confrence Room |  | 0 |  | 216 | 4 | 0 |  | 1728 | 0 | 0
- | Counselor |  | 0 |  | 132 | 3 | 0 |  | 1056 | 0 | 0
- | Custodial Staff Room |  | 0 |  | 118 | 2 | 0 |  | 944 | 0 | 0
- | Food Service Locker Room |  | 0 |  | 83 | 1 | 0 |  | 664 | 0 | 0
- | Food Service Manager's Office |  | 0 |  | 56 | 1 | 0 |  | 448 | 0 | 0
- | Gymnasium |  | 0 |  | 4006 | 91 | 0 |  | 32048 | 0 | 0
- | Kitchen |  | 0 |  | 954 | 21 | 0 |  | 7632 | 0 | 0
- | Main Office |  | 0 |  | 505 | 11 | 0 |  | 4040 | 0 | 0
- | MPR / Auditorium |  | 0 | Yes | 2669 | 60 | 60 |  | 21352 | 0 | 0
- | Nurse |  | 0 |  | 191 | 4 | 0 |  | 1528 | 0 | 0
- | Nurse Waiting Area |  | 0 |  | 159 | 3 | 0 |  | 1272 | 0 | 0
- | Principal's Office |  | 0 |  | 351 | 7 | 0 |  | 2808 | 0 | 0
- | Psychologist's Office |  | 0 |  | 66 | 1 | 0 |  | 528 | 0 | 0
- | Storage |  | 0 |  | 107 | 2 | 0 |  | 856 | 0 | 0
- | Storage Room #2 |  | 0 |  | 99 | 2 | 0 |  | 792 | 0 | 0
- | Supply Closet |  | 0 |  | 126 | 2 | 0 |  | 1008 | 0 | 0
- | Teacher's Lounge |  | 0 |  | 226 | 5 | 0 |  | 1808 | 0 | 0
- | 1st Floor Lunchroom | 0 | 0 |  | 2677 | 60 | 0 |  | 21416 | 0 | 0
- | Closet | 34 | 2 |  | 40 | 0 | 0 |  | 320 | 6.375 | 2
- | 3rd Floor Lunchroom |  | 0 |  | 4452 | 101 | 0 |  | 35616 | 0 | 0
- | Cafeteria Manager's Office | 75 | 5 |  | 55 | 1 | 1 |  | 440 | 10.2273 | 3
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-02-23 | [7 empty] | 0 | 0 | 0
School: | Feltonville Headstart | House Fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | N/A | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-24 | [7 empty] | 0 | 0 | 0
School: | Thomas Finletter Academics Plus Elementary School | House fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine |  | Devine Brothers Retest | [5 empty] | 0 | 0 | 0
School: | Finletter LSH | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Finletter Main Building | [8 empty] | 0 | 0 | 0
101 | Classroom | 535 | 35 |  | 1056 | 24 | 24 | House Fan | 8448 | 3.7997 | 1
102 | Classroom | 458 | 30 |  | 1056 | 24 | 24 | House Fan | 8448 | 3.2528 | 1
103 | Classroom | 621 | 41 |  | 1056 | 24 | 24 | House Fan | 8448 | 4.4105 | 2
104 | Classroom | 595 | 39 |  | 870 | 19 | 19 | House Fan | 6960 | 5.1293 | 2
105 | Classroom | 554 | 36 |  | 870 | 19 | 19 | House Fan | 6960 | 4.7759 | 2
106 | Classroom | 1227 | 81 |  | 870 | 19 | 19 | House Fan | 6960 | 10.5776 | 3
107 | Classroom | 980 | 65 |  | 870 | 19 | 19 | House Fan | 6960 | 8.4483 | 2
108 | Classroom | 817 | 54 |  | 899 | 20 | 20 | House Fan | 7192 | 6.8159 | 2
109 | Classroom | 876 | 58 |  | 899 | 20 | 20 | House Fan | 7192 | 7.3081 | 2
110 | Classroom | 535 | 35 |  | 928 | 21 | 21 | House Fan | 7424 | 4.3238 | 2
201 | Classroom | 477 | 31 |  | 1056 | 24 | 24 | House Fan | 8448 | 3.3878 | 1
202 | Classroom | 334 | 22 |  | 1056 | 24 | 22 | House Fan | 8448 | 2.3722 | 1
203 | Classroom | 411 | 27 |  | 1056 | 24 | 24 | House Fan | 8448 | 2.919 | 1
204 | Classroom | 916 | 61 |  | 870 | 19 | 19 | House Fan | 6960 | 7.8966 | 2
205 | Classroom | 1018 | 67 |  | 870 | 19 | 19 | House Fan | 6960 | 8.7759 | 2
206 | Classroom | 1222 | 81 |  | 870 | 19 | 19 | House Fan | 6960 | 10.5345 | 3
207 | Classroom | 1203 | 80 |  | 870 | 19 | 19 | House Fan | 6960 | 10.3707 | 3
208 | Classroom | 450 | 30 |  | 899 | 20 | 20 | House Fan | 7192 | 3.7542 | 1
209 | Classroom | 363 | 24 |  | 899 | 20 | 20 | House Fan | 7192 | 3.0284 | 1
210 | Classroom | 434 | 28 |  | 928 | 21 | 21 | House Fan | 7424 | 3.5075 | 1
211 | Classroom | 0 | 0 |  | 195 | 4 | 0 | N/A | 1560 | 0 | 0
212 | Classroom | 0 | 0 |  | 384 | 8 | 0 | N/A | 3072 | 0 | 0
301 | Classroom | 278 | 18 |  | 1056 | 24 | 18 | House Fan | 8448 | 1.9744 | 1
302 | Classroom | 458 | 30 |  | 1056 | 24 | 24 | House Fan | 8448 | 3.2528 | 1
303 | Classroom | 125 | 8 |  | 1056 | 24 | 8 | House Fan | 8448 | 0.88778 | 0
304 | Classroom | 288 | 19 |  | 870 | 19 | 19 | House Fan | 6960 | 2.4828 | 1
305 | Classroom | 645 | 43 |  | 870 | 19 | 19 | House Fan | 6960 | 5.5603 | 2
306 | Classroom | 289 | 19 |  | 870 | 19 | 19 | House Fan | 6960 | 2.4914 | 1
307 | Classroom | 654 | 43 |  | 870 | 19 | 19 | House Fan | 6960 | 5.6379 | 2
308 | Classroom | 345 | 23 |  | 899 | 20 | 20 | House Fan | 7192 | 2.8782 | 1
309 | Classroom | 319 | 21 |  | 899 | 20 | 20 | House Fan | 7192 | 2.6613 | 1
310 | Classroom | 675 | 45 |  | 928 | 21 | 21 | House Fan | 7424 | 5.4553 | 2
311 | Classroom | 705 | 47 |  | 667 | 15 | 15 | House Fan | 5336 | 7.9273 | 2
312 | Classroom | 0 | 0 |  | 275 | 6 | 0 | N/A | 2200 | 0 | 0
402 | Health | 335 | 22 |  | 588 | 13 | 13 | House Fan | 4704 | 4.273 | 2
403 | Music Room | 491 | 32 |  | 990 | 22 | 22 | House Fan | 7920 | 3.7197 | 1
- | Annex Classroom | 65 | 4 |  | 960 | 21 | 4 | House Fan | 7680 | 0.50781 | 0
- | Art | 882 | 58 |  | 1421 | 32 | 32 | House Fan | 11368 | 4.6552 | 2
- | Auditorium | 3675 | 245 |  | 3431 | 77 | 77 | House Fan | 27448 | 8.0334 | 2
- | Health Classroom | 0 | 0 |  | 250 | 5 | 0 | House Fan | 2000 | 0 | 0
- | Gym/Cafe |  | 0 | Yes | 3432 | 78 | 78 |  | 27456 | 0 | 0
- | Main office | 0 | 0 | Yes | 322 | 7 | 7 | N/A | 2576 | 0 | 0
Finletter LSH | [8 empty] | 0 | 0 | 0
105 | Womens Staff Bathroom |  | 0 |  | 96 | 2 | 0 | AHU | 768 | 0 | 0
105 | Mens Staff Bathroom |  | 0 |  | 77 | 1 | 0 | AHU | 616 | 0 | 0
106 | Custodial | 57 | 3 |  | 36 | 0 | 0 | AHU | 288 | 11.875 | 3
111 | Lobby |  | 0 |  | 187 | 4 | 0 | AHU | 1496 | 0 | 0
112 | Office | 118 | 7 |  | 110 | 2 | 2 | AHU | 880 | 8.0455 | 2
113 | Office | 118 | 7 |  | 110 | 2 | 2 | AHU | 880 | 8.0455 | 2
114 | General Storage | 216 | 14 |  | 54 | 1 | 1 | AHU | 432 | 30 | 4
115 | Multipurpose Room | 2476 | 165 |  | 2166 | 49 | 49 | AHU | 17328 | 8.5734 | 2
116 | Corridor #2 |  | 0 |  | 120 | 2 | 0 | AHU | 960 | 0 | 0
123 | Custodial Storage | 76 | 5 |  | 54 | 1 | 1 | AHU | 432 | 10.5556 | 3
125 | Academic Storage | 66 | 4 |  | 18 | 0 | 0 | AHU | 144 | 27.5 | 4
A | Classroom | 341 | 22 |  | 986 | 22 | 22 | AHU | 7888 | 2.5938 | 1
B | Classroom | 332 | 22 |  | 986 | 22 | 22 | AHU | 7888 | 2.5254 | 1
C | Classroom | 341 | 22 |  | 986 | 22 | 22 | AHU | 7888 | 2.5938 | 1
D | Classroom | 332 | 22 |  | 986 | 22 | 22 | AHU | 7888 | 2.5254 | 1
E | Classroom | 327 | 21 |  | 986 | 22 | 21 | AHU | 7888 | 2.4873 | 1
F | Classroom | 327 | 21 |  | 986 | 22 | 21 | AHU | 7888 | 2.4873 | 1
G | Classroom | 327 | 21 |  | 986 | 22 | 21 | AHU | 7888 | 2.4873 | 1
H | Classroom | 327 | 21 |  | 986 | 22 | 21 | AHU | 7888 | 2.4873 | 1
I | Classroom | 293 | 19 |  | 986 | 22 | 19 | AHU | 7888 | 2.2287 | 1
J | Classroom | 359 | 23 |  | 986 | 22 | 22 | AHU | 7888 | 2.7307 | 1
K | Classroom | 293 | 19 |  | 986 | 22 | 19 | AHU | 7888 | 2.2287 | 1
L | Classroom | 359 | 23 |  | 986 | 22 | 22 | AHU | 7888 | 2.7307 | 1
- | Custodial Office |  | 0 | Yes |  | 0 | 0 | AHU | 0 | 0 | 0
- | Teachers Lounge |  | 0 | No | 288 | 6 | 0 | AHU | 2304 | 0 | 0
Sheet Last Modified: | 2021-03-22 | [7 empty] | 0 | 0 | 0
School: | Fitler Academic Plus Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Meehan | Devine Retest | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
105 | Classroom | 707 | 47 |  | 1024 | 23 | 23 | House Fan | 8192 | 5.1782 | 2
106 | Classroom | 796 | 53 |  | 720 | 16 | 16 | House Fan | 5760 | 8.2917 | 2
107 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
201 | Classroom | 834 | 55 |  | 1024 | 23 | 23 | House Fan | 8192 | 6.1084 | 2
202 | Classroom | 879 | 58 |  | 1024 | 23 | 23 | House Fan | 8192 | 6.438 | 2
203 | Classroom | 510 | 34 |  | 1024 | 23 | 23 | House Fan | 8192 | 3.7354 | 1
204 | Classroom | 951 | 63 |  | 1024 | 23 | 23 | House Fan | 8192 | 6.9653 | 2
205 | Classroom | 716 | 47 |  | 1024 | 23 | 23 | House Fan | 8192 | 5.2441 | 2
206 | Classroom | 668 | 44 |  | 720 | 16 | 16 | House Fan | 5760 | 6.9583 | 2
207 | Classroom | 78 | 5 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0.8125 | 0
301 | Classroom | 860 | 57 |  | 720 | 16 | 16 | House Fan | 5760 | 8.9583 | 2
302 | Classroom | 550 | 36 |  | 1024 | 23 | 23 | House Fan | 8192 | 4.0283 | 2
303 | Classroom | 538 | 35 |  | 1024 | 23 | 23 | House Fan | 8192 | 3.9404 | 1
304 | Classroom | 957 | 63 |  | 1024 | 23 | 23 | House Fan | 8192 | 7.0093 | 2
305 | Classroom | 746 | 49 |  | 1024 | 23 | 23 | House Fan | 8192 | 5.4639 | 2
306 | Classroom | 637 | 42 |  | 720 | 16 | 16 | House Fan | 5760 | 6.6354 | 2
307 | Classroom | 364 | 24 | Yes | 720 | 16 | 16 | House Fan | 5760 | 3.7917 | 1
- | Combo room | 883 | 58 |  | 1024 | 23 | 23 | House Fan | 8192 | 6.4673 | 2
- | Gym | 1325 | 88 |  | 1344 | 30 | 30 | House Fan | 10752 | 7.394 | 2
- | Library | 1641 | 109 |  | 2400 | 54 | 54 | House Fan | 19200 | 5.1281 | 2
- | Main office | 850 | 56 |  | 1156 | 26 | 26 | House Fan | 9248 | 5.5147 | 2
- | Restroom | 781 | 52 |  | 660 | 15 | 15 | House Fan | 5280 | 8.875 | 2
- | Counselors Office | 1062 | 70 |  | 175 | 3 | 3 | ERU | 1400 | 45.5143 | 4
- | Cafeteria | 0 | 0 |  | 1944 | 44 | 0 | NA | 15552 | 0 | 0
- | Nurses Office |  | 0 | Yes | 75 | 1 | 1 |  | 600 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-12 | [7 empty] | 0 | 0 | 0
School: | Aloysius L. Fitzpatrick Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Part 2 | Part 3 | [5 empty] | 0 | 0 | 0
School: | Aloysius L. Fitzpatrick Elementary School Annex | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Part 2 | Part 3 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Main Building | [8 empty] | 0 | 0 | 0
B-10 | Classroom | 313 | 20 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 3.3345 | 1
100 | Classroom | 298 | 19 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.3864 | 1
101 | Classroom | 281 | 18 |  | 744 | 16 | 16 | Unit Ventilator | 5952 | 2.8327 | 1
102 | Classroom | 315 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.8125 | 1
103 | Classroom | 289 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.5804 | 1
104 | Classroom | 337 | 22 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 3.1398 | 1
105 | Classroom | 306 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7321 | 1
106 | Classroom | 293 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6161 | 1
107 | Classroom | 287 | 19 |  | 576 | 13 | 13 | Unit Ventilator | 4608 | 3.737 | 1
108 | Classroom | 409 | 27 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.7047 | 1
109 | Classroom | 26 | 1 | Yes | 600 | 13 | 13 | Unit Ventilator | 4800 | 0.325 | 0
110 | Classroom | 340 | 22 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.0357 | 1
112 | Classroom | 341 | 22 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.0888 | 1
200 | Classroom | 319 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.8482 | 1
201 | Classroom | 275 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4554 | 1
202 | Classroom | 300 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6786 | 1
203 | Classroom | 309 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7589 | 1
204 | Classroom | 290 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.5893 | 1
205 | Classroom | 314 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.8036 | 1
206 | Library | 656 | 43 |  | 1680 | 38 | 38 | Unit Ventilator | 13440 | 2.9286 | 1
207 | Classroom | 326 | 21 |  | 425 | 9 | 9 | Unit Ventilator | 3400 | 5.7529 | 2
210 | Classroom | 293 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6161 | 1
212 | Classroom | 334 | 22 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9821 | 1
214 | Classroom | 304 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7143 | 1
216 | Classroom | 325 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9018 | 1
218 | Classroom | 307 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7411 | 1
300 | Classroom | 289 | 19 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.5087 | 1
301 | Classroom | 305 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7232 | 1
302 | Classroom | 281 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.5089 | 1
303 | Classroom | 299 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6696 | 1
304 | Classroom | 329 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9375 | 1
305 | Classroom | 294 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.625 | 1
306 | Classroom | 607 | 40 |  | 1704 | 38 | 38 | Unit Ventilator | 13632 | 2.6717 | 1
307 | Classroom | 340 | 22 |  | 425 | 9 | 9 | Unit Ventilator | 3400 | 6 | 2
310 | Classroom | 299 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6696 | 1
312 | Classroom | 326 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9107 | 1
314 | Classroom | 304 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7143 | 1
316 | Classroom | 329 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9375 | 1
318 | Classroom | 337 | 22 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.0089 | 1
- | Auditorium | 92 | 6 |  | 1825 | 41 | 6 | AHU | 14600 | 0.37808 | 0
B-1 | Classroom | 466 | 31 |  | 966 | 21 | 21 | Unit Ventilator | 7728 | 3.618 | 1
B-2 | Classroom | 287 | 19 |  | 966 | 21 | 19 | Unit Ventilator | 7728 | 2.2283 | 1
B-4 | Classroom | 236 | 15 |  | 704 | 16 | 15 | Unit Ventilator | 5632 | 2.5142 | 1
B-8 | Classroom | 269 | 17 |  | 792 | 18 | 17 | Unit Ventilator | 6336 | 2.5473 | 1
- | Cafeteria | 72 | 4 |  | 2835 | 64 | 4 | Unit Ventilator | 22680 | 0.19048 | 0
- | Gymnasium | 72 | 4 | Yes | 3922 | 89 | 89 | AHU | 31376 | 0.13768 | 0
- | Main Office | 284 | 18 |  | 1000 | 22 | 18 | Unit Ventilator | 8000 | 2.13 | 1
- | Music | 29 | 1 |  | 768 | 17 | 1 | Unit Ventilator | 6144 | 0.2832 | 0
Annex Building | [8 empty] | 0 | 0 | 0
9 | Classroom | 165 | 11 | Yes | 1040 | 23 | 23 | Unit Ventilator | 8320 | 1.1899 | 1
10 | Classroom | 310 | 20 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.691 | 1
11 | Classroom | 311 | 20 |  | 962 | 21 | 20 | Unit Ventilator | 7696 | 2.4246 | 1
12 | Classroom | 291 | 19 |  | 1040 | 23 | 19 | Unit Ventilator | 8320 | 2.0986 | 1
Sheet Last Modified: | 2021-04-14 | [7 empty] | 0 | 0 | 0
School: | Edwin Forrest Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
School: | Edwin Forrest Elementary School- Little School House | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Brothers Part 2 | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Edwin Forrest Elementary School Main Building | [8 empty] | 0 | 0 | 0
- | Auditorium | 955 | 63 |  | 3552 | 80 | 63 | Unit Ventilator | 28416 | 2.0165 | 1
- | PreK | 281 | 18 |  | 1084 | 24 | 18 | Unit Ventilator | 8672 | 1.9442 | 1
101 | admin |  | 0 | Yes | 920 | 20 | 20 | House Fan | 7360 | 0 | 0
102 | 2nd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
103 | admin |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
104 | Specialist K-6 |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
105 | 2nd grade |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
106 | 2nd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
107 | 4th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
108 | 2nd |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
109 | 2nd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
- | Main Office |  | 0 | Yes | 336 | 7 | 7 | House Fan | 2688 | 0 | 0
110 | 2nd |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
- | Principal Office |  | 0 | Yes | 210 | 4 | 4 | House Fan | 1680 | 0 | 0
- | Nurses Office |  | 0 | Yes | 264 | 6 | 6 | House Fan | 2112 | 0 | 0
201 | 4th |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
202 | 4th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
203 | 4th |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
204 | 4th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
205 | 3rd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
206 | 3rd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
207 | 3rd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
208 | 3rd |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
209 | 3rd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
210 | 3rd |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
211 | small group instruction |  | 0 | Yes | 192 | 4 | 4 | House Fan | 1536 | 0 | 0
212 | counselor office |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | 0 | 0
- | Teachers Lounge |  | 0 | Yes | 253 | 5 | 5 | House Fan | 2024 | 0 | 0
301 | 6th |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
302 | 6th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
303 | 6th |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
304 | 5th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
305 | 5th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
306 | 6th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
307 | 6th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
308 | 5th |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
309 | 5th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
310 | 5th |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
311 | 3rd fl computer room |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
312 | Small group instruction |  | 0 | Yes | 192 | 4 | 4 | House Fan | 1536 | 0 | 0
314 |  |  |  | Yes | 180 |  |  | House Fan | 1440 | 0 | 0
- | Speech Room |  | 0 | Yes | 180 | 4 | 4 | House Fan | 1440 | 0 | 0
b1 | music room |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
b2a | Small group instruction |  | 0 | Yes | 352 | 8 | 8 | House Fan | 2816 | 0 | 0
b2 | Small group instruction |  | 0 | Yes | 352 | 8 | 8 | House Fan | 2816 | 0 | 0
b3 | Small group instruction |  | 0 | Yes | 506 | 11 | 11 | House Fan | 4048 | 0 | 0
B4 | Computer Lab |  | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | 0 | 0
- | Gym/caf |  | 0 | Yes | 3432 | 78 | 78 | N/A | 27456 | 0 | 0
- | Kitchen |  | 0 | Yes | 609 | 13 | 13 | House Fan | 4872 | 0 | 0
- | 2nd Flr Counselor Office |  | 0 | Yes | 195 | 4 | 4 | House Fan | 1560 | 0 | 0
- | 3rd Flr Counselor Office |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | 0 | 0
Edwin Forrest Elementary School- Little School House | [8 empty] | 0 | 0 | 0
P1 | - | 348 | 23 |  | 986 | 22 | 22 | Unit Ventilator | 7888 | 2.6471 | 1
P2 | - | 303 | 20 |  | 986 | 22 | 20 | Unit Ventilator | 7888 | 2.3048 | 1
P3 | - | 362 | 24 |  | 986 | 22 | 22 | Unit Ventilator | 7888 | 2.7535 | 1
P4 | - | 327 | 21 |  | 986 | 22 | 21 | Unit Ventilator | 7888 | 2.4873 | 1
P5 | - | 304 | 20 |  | 986 | 22 | 20 | Unit Ventilator | 7888 | 2.3124 | 1
P6 | - | 390 | 26 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.6022 | 1
P7 | - | 308 | 20 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 2.8448 | 1
P8 | - | 308 | 20 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 2.8448 | 1
P9 | - | 382 | 25 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.5283 | 1
P10 | - | 312 | 20 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 2.8818 | 1
P11 | - | 311 | 20 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 2.8725 | 1
P12 | - | 316 | 21 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 2.9187 | 1
P13 | - | 327 | 21 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.0203 | 1
- | Administration and Corridors | 727 | 48 |  | 576 | 13 | 13 | AHU | 4608 | 9.4661 | 2
- | Cafeteria | 78 | 5 | Yes | 2014 | 45 | 45 | AHU | 16112 | 0.29047 | 0
- | Faculty Break Room | 312 | 20 |  | 210 | 4 | 4 | Unit Ventilator | 1680 | 11.1429 | 3
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-08 | [7 empty] | 0 | 0 | 0
School: | Fox Chase Elementary School | [7 empty] | 0 | 0 | 0
| Fox Chase Farm | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Fox Chase Main Building | [8 empty] | 0 | 0 | 0
101 | Classroom | 338 | 22 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.0179 | 1
102 | Classroom | 316 | 21 |  | 1104 | 25 | 21 | Unit Ventilator | 8832 | 2.1467 | 1
103 | Classroom | 291 | 19 |  | 989 | 22 | 19 | Unit Ventilator | 7912 | 2.2068 | 1
104 | Classroom | 302 | 20 |  | 960 | 21 | 20 | Unit Ventilator | 7680 | 2.3594 | 1
105 | Classroom | 312 | 20 |  | 984 | 22 | 20 | Unit Ventilator | 7872 | 2.378 | 1
105A | Office | 0 | 0 | Yes | 216 | 4 | 4 | Unit Ventilator | 1728 | 0 | 0
107 | Examing Room |  | 0 | Yes | 234 | 5 | 5 | N/A | 1872 | 0 | 0
107A | Office | 0 | 0 | Yes | 225 | 5 | 5 | N/A | 1800 | 0 | 0
108 | Classroom |  | 0 | Yes | 216 | 4 | 4 |  | 1728 | 0 | 0
109 | Classroom | 315 | 21 |  | 1035 | 23 | 21 | Unit Ventilator | 8280 | 2.2826 | 1
110 | Classroom | 300 | 20 |  | 1032 | 23 | 20 | Unit Ventilator | 8256 | 2.1802 | 1
111 | Classroom | 155 | 10 | Yes | 1012 | 23 | 23 | Unit Ventilator | 8096 | 1.1487 | 1
112 | Classroom | 161 | 10 | Yes | 1081 | 24 | 24 | Unit Ventilator | 8648 | 1.117 | 1
201 | Classroom | 341 | 22 |  | 943 | 21 | 21 | Unit Ventilator | 7544 | 2.7121 | 1
202 | Classroom | 382 | 25 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 3.194 | 1
203 | Classroom | 382 | 25 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 3.194 | 1
204 | Classroom | 237 | 15 |  | 462 | 10 | 10 | Unit Ventilator | 3696 | 3.8474 | 1
205 | Classroom | 192 | 12 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | 1.5385 | 1
206 | Classroom | 391 | 26 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 3.2155 | 1
207 | Classroom | 0 | 0 | Yes | 943 | 21 | 21 | Unit Ventilator | 7544 | 0 | 0
208 | Classroom | 71 | 4 | Yes | 960 | 21 | 21 | Unit Ventilator | 7680 | 0.55469 | 0
3340 | Ag Room |  | 0 | Yes | 1283 | 29 | 29 | Unit Ventilator | 10264 | 0 | 0
- | 1st Floor Teacher's Lounge | 0 | 0 |  | 336 | 7 | 0 | N/A | 2688 | 0 | 0
A-1 | Classroom | 281 | 18 |  | 836 | 19 | 18 | Unit Ventilator | 6688 | 2.5209 | 1
A-2 | Classroom | 283 | 18 |  | 836 | 19 | 18 | Unit Ventilator | 6688 | 2.5389 | 1
A-3 | Classroom | 319 | 21 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.8618 | 1
A-4 | Classroom | 252 | 16 |  | 836 | 19 | 16 | Unit Ventilator | 6688 | 2.2608 | 1
A-5 | Classroom | 241 | 16 |  | 836 | 19 | 16 | Unit Ventilator | 6688 | 2.1621 | 1
A-6 | Classroom | 295 | 19 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.6465 | 1
C-1 | Classroom |  | 0 | Yes | 1560 | 35 | 35 | N/A | 12480 | 0 | 0
C-4 | Classroom |  | 0 | Yes | 380 | 8 | 8 | N/A | 3040 | 0 | 0
- | Annex | 0 | 0 |  | 1283 | 29 | 0 | Unit Ventilator | 10264 | 0 | 0
- | Auditorium | 0 | 0 |  | 4420 | 100 | 0 | AHU | 35360 | 0 | 0
Instrument Room | Stage Area |  | 0 | Yes | 228 | 5 | 5 |  | 1824 | 0 | 0
- | Cafeteria | 704 | 46 |  | 2340 | 53 | 46 | Unit Ventilator | 18720 | 2.2564 | 1
- | Counselor | 0 | 0 |  | 230 | 5 | 0 | N/A | 1840 | 0 | 0
- | Dental Office | 0 | 0 | Yes | 208 | 4 | 4 | N/A | 1664 | 0 | 0
- | Examining Room | 0 | 0 |  | 234 | 5 | 0 | N/A | 1872 | 0 | 0
- | Gym | 0 | 0 |  | 5429 | 123 | 0 | AHU | 43432 | 0 | 0
- | Kitchen Storage | 296 | 19 |  | 260 | 5 | 5 | Unit Ventilator | 2080 | 8.5385 | 2
- | Main Office | 0 | 0 | Yes | 226 | 5 | 5 | N/A | 1808 | 0 | 0
- | Music Room | 581 | 38 |  | 1400 | 31 | 31 | Unit Ventilator | 11200 | 3.1125 | 1
- | Nurse | 0 | 0 | Yes | 234 | 5 | 5 | N/A | 1872 | 0 | 0
- | Principal | 0 | 0 | Yes | 234 | 5 | 5 | N/A | 1872 | 0 | 0
Fox Chase Farm | [8 empty] | 0 | 0 | 0
- | Data Closet | 14 | 0 |  | 30 | 0 | 0 | AC | 240 | 3.5 | 1
- | Kitchen | 190 | 12 |  | 156 | 3 | 3 | AC | 1248 | 9.1346 | 2
- | Men's Bathroom | 56 | 3 |  | 225 | 5 | 3 | AC | 1800 | 1.8667 | 1
- | Teaching Area Classroom | 658 | 43 |  | 1692 | 38 | 38 | AC | 13536 | 2.9167 | 1
- | Women's Bathroom | 55 | 3 |  | 225 | 5 | 3 | AC | 1800 | 1.8333 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Anne Frank Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Retest | [6 empty] | 0 | 0 | 0
School: | Anne Frank Elementary School- Little School House | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Frank Main Building | [8 empty] | 0 | 0 | 0
100 | Classroom | 283 | 18 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.4566 | 1
101 | Classroom | 284 | 18 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.4653 | 1
102 | Classroom | 236 | 15 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.0486 | 1
103 | Classroom | 260 | 17 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.2569 | 1
104 | Classroom | 56 | 3 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0.48611 | 0
106 | Classroom | 0 | 0 |  | 240 | 5 | 0 | Unit Ventilator | 1920 | 0 | 0
108 | Classroom | 191 | 12 | Yes | 456 | 10 | 10 | Unit Ventilator | 3648 | 3.1414 | 1
109 | Classroom | 0 | 0 | Yes | 456 | 10 | 10 | Unit Ventilator | 3648 | 0 | 0
110 | Classroom | 305 | 20 | Yes | 1032 | 23 | 23 | Unit Ventilator | 8256 | 2.2166 | 1
125 | Classroom | 348 | 23 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 3.8839 | 1
- | Admin Office | 0 | 0 |  | 135 | 3 | 0 | Unit Ventilator | 1080 | 0 | 0
200 | Classroom | 283 | 18 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.4566 | 1
201 | Library | 60 | 4 | Yes | 875 | 19 | 19 | Unit Ventilator | 7000 | 0.51429 | 0
202 | Classroom | 293 | 19 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.5434 | 1
203 | Classroom | 304 | 20 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.6389 | 1
204 | Classroom | 322 | 21 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.7951 | 1
205 | Classroom | 215 | 14 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.8663 | 1
206 | Classroom | 205 | 13 |  | 240 | 5 | 5 | Unit Ventilator | 1920 | 6.4062 | 2
207 | Classroom | 257 | 17 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.2309 | 1
208 | Classroom | 299 | 19 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.5955 | 1
209 | Classroom | 203 | 13 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.7622 | 1
210 | Classroom | 225 | 15 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.9531 | 1
211 | Classroom | 333 | 22 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.8906 | 1
212 | Classroom | 153 | 10 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.3281 | 1
213 | Classroom | 226 | 15 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.9618 | 1
214 | Classroom |  | 0 | Yes | 864 | 19 | 19 |  | 6912 | 0 | 0
215 | Classroom | 284 | 18 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.4653 | 1
- | Library | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0
300 | Classroom | 241 | 16 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.092 | 1
301 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0
302 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0
303 | Classroom | 185 | 12 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.6059 | 1
304 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0
305 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0
306 | Classroom | 0 | 0 | Yes | 240 | 5 | 5 | Unit Ventilator | 1920 | 0 | 0
307 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0
308 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0
309 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0
310 | Classroom | 127 | 8 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.1024 | 1
311 | Classroom | 42 | 2 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0.36458 | 0
312 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0
313 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0
315 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0
| Auditorium | 0 | 0 |  | 3180 | 72 | 0 |  | 25440 | 0 | 0
| Cafeteria | 0 | 0 | Yes | 2720 | 61 | 61 |  | 21760 | 0 | 0
| Gymnasium | 0 | 0 | Yes | 3657 | 83 | 83 |  | 29256 | 0 | 0
| Gymnasium Office |  | 0 |  | 165 | 3 | 0 |  | 1320 | 0 | 0
- | Counselor Office | 0 | 0 | Yes | 132 | 3 | 3 | NA | 1056 | 0 | 0
- | Main Office | 60 | 4 | Yes | 951 | 21 | 21 | Unit Ventilator | 7608 | 0.47319 | 0
- | Nurses Office | 0 | 0 | Yes | 304 | 6 | 6 | NA | 2432 | 0 | 0
- | Principals Office | 0 | 0 | Yes | 210 | 4 | 4 | NA | 1680 | 0 | 0
- | Vice Principals Office | 0 | 0 | Yes | 72 | 1 | 1 | NA | 576 | 0 | 0
Frank LSH | [8 empty] | 0 | 0 | 0
1 | Classroom | 931 | 62 |  | 928 | 21 | 21 | BCU | 7424 | 7.5242 | 2
2 | Classroom | 595 | 39 |  | 928 | 21 | 21 | BCU | 7424 | 4.8087 | 2
3 | Classroom | 945 | 63 |  | 928 | 21 | 21 | BCU | 7424 | 7.6374 | 2
4 | Classroom | 610 | 40 |  | 928 | 21 | 21 | BCU | 7424 | 4.93 | 2
5 | Classroom | 322 | 21 |  | 928 | 21 | 21 | BCU | 7424 | 2.6024 | 1
6 | Classroom | 307 | 20 | Yes | 928 | 21 | 21 | BCU | 7424 | 2.4811 | 1
7 | Classroom | 310 | 20 | Yes | 928 | 21 | 21 | BCU | 7424 | 2.5054 | 1
8 | Classroom | 305 | 20 | Yes | 928 | 21 | 21 | BCU | 7424 | 2.465 | 1
9 | Classroom | 370 | 24 |  | 928 | 21 | 21 | BCU | 7424 | 2.9903 | 1
10 | Classroom | 329 | 21 |  | 928 | 21 | 21 | BCU | 7424 | 2.6589 | 1
11 | Classroom | 396 | 26 |  | 928 | 21 | 21 | BCU | 7424 | 3.2004 | 1
12 | Classroom | 319 | 21 |  | 928 | 21 | 21 | BCU | 7424 | 2.5781 | 1
- | Bathrooms, Corridor and Main Entrance | 284 | 18 |  | 225 | 5 | 5 | FCU | 1800 | 9.4667 | 2
- | Corner Facilities/Guidance Office | 0 | 0 |  | 196 | 4 | 0 | FCU | 1568 | 0 | 0
- | Counselor Office | 0 | 0 | Yes | 100 | 2 | 2 | FCU | 800 | 0 | 0
- | Janitor Close and Storage Rooms | 262 | 17 |  | 24 | 0 | 0 | FCU | 192 | 81.875 | 5
- | Main Office | 587 | 39 |  | 315 | 7 | 7 | FCU | 2520 | 13.9762 | 3
- | Cafeteria | 922 | 61 |  | 1696 | 38 | 38 | BCU | 13568 | 4.0772 | 2
- | Art Teacher Office | 102 | 6 |  | 100 | 2 | 2 | BCU | 800 | 7.65 | 2
- | ESL Teacher Office | 110 | 7 |  | 100 | 2 | 2 | BCU | 800 | 8.25 | 2
- | ESL Room | 241 | 16 |  | 80 | 1 | 1 | BCU | 640 | 22.5938 | 3
Frank Annex | [8 empty] | 0 | 0 | 0
7 | Classroom | 36 | 2 | Yes | 1080 | 24 | 24 | Unit Ventilator | 8640 | 0.25 | 0
8 | Classroom | 235 | 15 | Yes | 1080 | 24 | 24 | Unit Ventilator | 8640 | 1.6319 | 1
- | gang girlsnboys |  | 0 |  | 480 | 10 | 0 | N/A | 3840 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-17 | [7 empty] | 0 | 0 | 0
School: | Frankford High School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
9 | Classroom | 122 | 8 |  | 1836 | 41 | 8 | Unit Ventilator | 14688 | 0.49837 | 0
11 | Classroom | 0 | 0 |  | 2011 | 45 | 0 | Unit Ventilator | 16088 | 0 | 0
12 | Classroom | 0 | 0 |  | 2011 | 45 | 0 | Unit Ventilator | 16088 | 0 | 0
14 | Classroom | 167 | 11 |  | 812 | 18 | 11 | Unit Ventilator | 6496 | 1.5425 | 1
15-14 | Classroom | 0 | 0 |  | N/A | 0 | 0 | Unit Ventilator | #VALUE! | #VALUE! | #VALUE!
15A | Classroom | 107 | 7 |  | 812 | 18 | 7 | Unit Ventilator | 6496 | 0.9883 | 0
16 | Classroom | 0 | 0 |  | 476 | 10 | 0 | Unit Ventilator | 3808 | 0 | 0
17 | Classroom | 0 | 0 |  | 952 | 21 | 0 | Unit Ventilator | 7616 | 0 | 0
18 | Classroom | 76 | 5 |  | 884 | 20 | 5 | Unit Ventilator | 7072 | 0.6448 | 0
19 | Classroom | 55 | 3 |  | 576 | 13 | 3 | Unit Ventilator | 4608 | 0.71615 | 0
20 | Classroom | 0 | 0 |  | 1023 | 23 | 0 | Unit Ventilator | 8184 | 0 | 0
124 | Classroom | 210 | 14 |  | 1702 | 38 | 14 | Unit Ventilator | 13616 | 0.92538 | 0
222 | Classroom | 80 | 5 |  | 889 | 20 | 5 | Unit Ventilator | 7112 | 0.67492 | 0
223 | Classroom | 163 | 10 |  | 991 | 22 | 10 | Unit Ventilator | 7928 | 1.2336 | 1
224 | Classroom | 80 | 5 |  | 991 | 22 | 5 | Unit Ventilator | 7928 | 0.60545 | 0
225 | Classroom | 50 | 3 |  | 1005 | 22 | 3 | Unit Ventilator | 8040 | 0.37313 | 0
226 | Classroom | 149 | 9 |  | 991 | 22 | 9 | Unit Ventilator | 7928 | 1.1276 | 1
227 | Classroom | 128 | 8 |  | 864 | 19 | 8 | Unit Ventilator | 6912 | 1.1111 | 1
228 | Classroom | 255 | 17 |  | 899 | 20 | 17 | Unit Ventilator | 7192 | 2.1274 | 1
229 | Classroom | 0 | 0 |  | 462 | 10 | 0 | Unit Ventilator | 3696 | 0 | 0
230 | Classroom | 181 | 12 |  | 1001 | 22 | 12 | Unit Ventilator | 8008 | 1.3561 | 1
231A | Classroom | 286 | 19 |  | 986 | 22 | 19 | Unit Ventilator | 7888 | 2.1755 | 1
232A | Classroom | 80 | 5 |  | 1048 | 23 | 5 | Unit Ventilator | 8384 | 0.57252 | 0
233 | Classroom | 40 | 2 |  | 1120 | 25 | 2 | Unit Ventilator | 8960 | 0.26786 | 0
326 | Classroom | 91 | 6 |  | 775 | 17 | 6 | Unit Ventilator | 6200 | 0.88065 | 0
327 | Classroom | 48 | 3 |  | 775 | 17 | 3 | Unit Ventilator | 6200 | 0.46452 | 0
330-331 | Classroom | 166 | 11 |  | 969 | 22 | 11 | Unit Ventilator | 7752 | 1.2848 | 1
332 | Classroom | 84 | 5 |  | 1505 | 34 | 5 | Unit Ventilator | 12040 | 0.4186 | 0
333 | Classroom | 0 | 0 |  | 1505 | 34 | 0 | Unit Ventilator | 12040 | 0 | 0
335 | Classroom | 0 | 0 |  | 1120 | 25 | 0 | Unit Ventilator | 8960 | 0 | 0
- | IMC | 264 | 17 |  | 5398 | 122 | 17 | Unit Ventilator | 43184 | 0.3668 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21 | [7 empty] | 0 | 0 | 0
School: | Benjamin Franklin Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Devine 2nd Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Basement Boy's Restroom | 0 | 0 |  | 234 | 5 | 0 | AHU | 1872 | 0 | 0
- | Basement Girl's Restroom | 0 | 0 |  | 234 | 5 | 0 | AHU | 1872 | 0 | 0
- | 1st Floor Boy's Restroom | 27 | 1 |  | 234 | 5 | 1 | AHU | 1872 | 0.86538 | 0
- | 1st Floor Girl's Restroom | 40 | 2 |  | 234 | 5 | 2 | AHU | 1872 | 1.2821 | 1
- | 2nd Floor Girl's Restroom | 28 | 1 |  | 234 | 5 | 1 | AHU | 1872 | 0.89744 | 0
- | 2nd Floor Boy's Restroom | 40 | 2 |  | 234 | 5 | 2 | AHU | 1872 | 1.2821 | 1
1 | Classroom |  | 0 | Yes | 304 | 6 | 6 | Unit Ventilator | 2432 | 0 | 0
1B | Classroom |  | 0 | Yes | 667 | 15 |  |  | 5336 | 0 | 0
6 | Classroom | 350 | 23 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.3654 | 1
7 | Cafeteria | 1972 | 131 |  | 2800 | 63 | 63 | AHU | 22400 | 5.2821 | 2
8 | Classroom | 299 | 19 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.875 | 1
- | Kitchen | 1585 | 105 |  | 1023 | 23 | 23 | AHU | 8184 | 11.6202 | 3
- | Kitchen Office | 225 | 15 |  | 80 | 1 | 1 | AHU | 640 | 21.0938 | 3
101 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
102 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
103 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
104 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | 0 | 0
105 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | 0 | 0
106 | Classroom |  | 0 | Yes | 650 | 14 | 14 |  | 5200 | 0 | 0
107 | Classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0
110 | Classroom | 352 | 23 |  | 780 | 17 | 17 | House Fan | 6240 | 3.3846 | 1
111 | Classroom | 321 | 21 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.0865 | 1
112 | Classroom | 300 | 20 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.8846 | 1
113 | Classroom | 312 | 20 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3 | 1
114 | Classroom | 410 | 27 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.9423 | 1
115 | Classroom | 346 | 23 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.3269 | 1
116 | Asst Principals Office | 352 | 23 |  | 207 | 4 | 4 | Unit Ventilator | 1656 | 12.7536 | 3
117 | Classroom | 332 | 22 |  | 609 | 13 | 13 | Unit Ventilator | 4872 | 4.0887 | 2
201 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
202 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
203 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
204 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | 0 | 0
205 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | 0 | 0
206 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | 0 | 0
207 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | 0 | 0
208 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
209 | Library | 568 | 37 | Yes | 1600 | 36 | 36 | Unit Ventilator | 12800 | 2.6625 | 1
210 | Trs Lounge | 330 | 22 |  | 380 | 8 | 8 | Unit Ventilator | 3040 | 6.5132 | 2
212 | TECH LAB | 487 | 32 |  | 1600 | 36 | 32 | Unit Ventilator | 12800 | 2.2828 | 1
214 | Classroom | 305 | 20 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.9327 | 1
215 | Classroom | 325 | 21 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.125 | 1
216 | Classroom | 325 | 21 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.125 | 1
217 | Classroom | 287 | 19 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.7596 | 1
218 | Classroom | 323 | 21 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.1058 | 1
219 | Classroom | 291 | 19 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.7981 | 1
220 | Counselor's Office | 287 | 19 |  | 207 | 4 | 4 | Unit Ventilator | 1656 | 10.3986 | 3
221 | Classroom | 314 | 20 |  | 605 | 13 | 13 | Unit Ventilator | 4840 | 3.8926 | 1
- | Faculty Lounge | 0 | 0 |  | 160 | 3 | 0 | Unit Ventilator | 1280 | 0 | 0
- | Nurses Office |  | 0 | Yes | 132 | 3 | 3 |  | 1056 | 0 | 0
- | Psychology Office | 33 | 2 |  | 90 | 2 | 2 | Unit Ventilator | 720 | 2.75 | 1
- | Main Office |  | 0 | Yes | 220 | 5 | 5 |  | 1760 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-19 | [7 empty] | 0 | 0 | 0
School: | Benjamin Franklin High School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Weight room | 63 | 4 |  | 713 | 16 | 4 | HV+ AHU | 5704 | 0.66269 | 0
2 | Weight room | 0 | 0 |  | 775 | 17 | 0 | HV | 6200 | 0 | 0
3 | Weight room | 0 | 0 |  | 1632 | 37 | 0 | HV | 13056 | 0 | 0
4 | Welding | 9254 | 616 |  | 2176 | 49 | 49 | MUA | 17408 | 31.8957 | 4
4A | Classroom | 280 | 18 |  | 640 | 14 | 14 | AC | 5120 | 3.2812 | 1
6 | Classroom | 0 | 0 | Yes | 2655 | 60 | 60 | AHU | 21240 | 0 | 0
7 | Classroom | 0 | 0 |  | 216 | 4 | 0 | AHU | 1728 | 0 | 0
8 | Classroom | 0 | 0 |  | 588 | 13 | 0 | AHU | 4704 | 0 | 0
9 | Classroom | 0 | 0 |  | 621 | 14 | 0 | AHU | 4968 | 0 | 0
10 | Machine Shop | 810 | 54 |  | 2961 | 67 | 54 | HV | 23688 | 2.0517 | 1
11 | Classroom | 176 | 11 |  | 1740 | 39 | 11 | AC | 13920 | 0.75862 | 0
12 | Classroom | 842 | 56 |  | 1581 | 35 | 35 | HV | 12648 | 3.9943 | 1
13 | Classroom | 175 | 11 |  | 1239 | 28 | 11 | AC | 9912 | 1.0593 | 1
13A | Classroom | 93 | 6 |  | 552 | 12 | 6 | AC | 4416 | 1.2636 | 1
14 | Classroom | 136 | 9 |  | 756 | 17 | 9 | AC | 6048 | 1.3492 | 1
15 | Classroom | 155 | 10 |  | 912 | 20 | 10 | AC | 7296 | 1.2747 | 1
15A | Practice Room | 77 | 5 |  | 77 | 1 | 1 | HV | 616 | 7.5 | 2
15B | Practice Room | 188 | 12 |  | 77 | 1 | 1 | HV | 616 | 18.3117 | 3
15C | Practice Room | 143 | 9 |  | 77 | 1 | 1 | HV | 616 | 13.9286 | 3
15D | Music Office | 142 | 9 |  | 180 | 4 | 4 | HV | 1440 | 5.9167 | 2
16 | Lecture Hall | 2049 | 136 |  | 2068 | 47 | 47 | HV | 16544 | 7.4311 | 2
17 | Lecture Hall | 387 | 25 |  | 2280 | 51 | 25 | HV | 18240 | 1.273 | 1
18 | Classroom | 803 | 53 |  | 1080 | 24 | 24 | AC | 8640 | 5.5764 | 2
19 | Classroom | 781 | 52 |  | 1344 | 30 | 30 | AC | 10752 | 4.3583 | 2
20 | Classroom | 635 | 42 |  | 828 | 18 | 18 | AC | 6624 | 5.7518 | 2
100 | Classroom | 280 | 18 |  | 775 | 17 | 17 | UV | 6200 | 2.7097 | 1
102 | Classroom | 382 | 25 |  | 961 | 21 | 21 | UV | 7688 | 2.9813 | 1
110 | Room | 0 | 0 |  | 195 | 4 | 0 | FC | 1560 | 0 | 0
111A | Room | 0 | 0 |  | 104 | 2 | 0 | FC | 832 | 0 | 0
113 | Room | 0 | 0 |  | 315 | 7 | 0 | FC | 2520 | 0 | 0
115 | Room | 0 | 0 |  | 352 | 8 | 0 | FC | 2816 | 0 | 0
116 | Room | 0 | 0 |  | 196 | 4 | 0 | FC | 1568 | 0 | 0
150 | Kitchen | 0 | 0 |  | 1955 | 44 | 0 | RTU | 15640 | 0 | 0
152 | Cafeteria | 0 | 0 |  | 3363 | 76 | 0 | RTU | 26904 | 0 | 0
200 | Living Room | 140 | 9 |  | 819 | 18 | 9 | UV | 6552 | 1.2821 | 1
201 | Classroom | 217 | 14 |  | 792 | 18 | 14 | UV | 6336 | 2.0549 | 1
202 | Office-A | 201 | 13 |  | 600 | 13 | 13 | UV | 4800 | 2.5125 | 1
202 | Office-B | 171 | 11 |  | 396 | 9 | 9 | UV | 3168 | 3.2386 | 1
204 | Principal Office | 41 | 2 |  | 180 | 4 | 2 | OAS-1A & OAS-1B | 1440 | 1.7083 | 1
206 | Co-Principal | 40 | 2 |  | 120 | 2 | 2 | OAS-1A & OAS-1B | 960 | 2.5 | 1
207 | Classroom | 257 | 17 |  | 792 | 18 | 17 | UV | 6336 | 2.4337 | 1
209 | Storage | 189 | 12 |  | 165 | 3 | 3 | UV | 1320 | 8.5909 | 2
209B | Office | 287 | 19 |  | 180 | 4 | 4 | UV | 1440 | 11.9583 | 3
211 | Classroom | 358 | 23 |  | 713 | 16 | 16 | UV | 5704 | 3.7658 | 1
212 | Work Room | 49 | 3 |  | 297 | 6 | 3 | OAS-1A & OAS-1B | 2376 | 1.2374 | 1
214 | Office | 57 | 3 |  | 121 | 2 | 2 | OAS-1A & OAS-1B | 968 | 3.5331 | 1
215 | Classroom | 295 | 19 |  | 806 | 18 | 18 | UV | 6448 | 2.745 | 1
216 | Conference | 44 | 2 |  | 72 | 1 | 1 | OAS-1A & OAS-1B | 576 | 4.5833 | 2
217 | Learning Lounge | 263 | 17 |  | 572 | 13 | 13 | UV | 4576 | 3.4484 | 1
218 | College Office | 50 | 3 |  | 132 | 3 | 3 | OAS-1A & OAS-1B | 1056 | 2.8409 | 1
220 | College | 49 | 3 |  | 120 | 2 | 2 | OAS-1A & OAS-1B | 960 | 3.0625 | 1
222 | Health Suite | 45 | 3 |  | 256 | 5 | 3 | OAS-1A & OAS-1B | 2048 | 1.3184 | 1
222A | Nurse Office | 50 | 3 |  | 108 | 2 | 2 | OAS-1A & OAS-1B | 864 | 3.4722 | 1
222B | Exam | 48 | 3 |  | 99 | 2 | 2 | OAS-1A & OAS-1B | 792 | 3.6364 | 1
223A | Dining | 856 | 57 |  | 1760 | 40 | 40 | UV | 14080 | 3.6477 | 1
229 | Classroom |  | 0 | Yes | 589 | 13 | 13 |  | 4712 | 0 | 0
231 | Office | 150 | 10 |  | 210 | 4 | 4 | UV | 1680 | 5.3571 | 2
232 | Health Suite | 221 | 14 |  | 464 | 10 | 10 | OAS-1A & OAS-1B | 3712 | 3.5722 | 1
232B | Storage | 0 | 0 |  | 45 | 1 | 0 | OAS-1A & OAS-1B | 360 | 0 | 0
232C | Nurse Health | 0 | 0 |  | 99 | 2 | 0 | AC | 792 | 0 | 0
232D | Nurse Health | 0 | 0 |  | 106 | 2 | 0 | AC | 848 | 0 | 0
238 | Conference | 119 | 7 |  | 228 | 5 | 5 | OAS-1A & OAS-1B | 1824 | 3.9145 | 1
240 | Office | 131 | 8 |  | 143 | 3 | 3 | OAS-1A & OAS-1B | 1144 | 6.8706 | 2
242 | Storage | 146 | 9 |  | 71 | 1 | 1 | OAS-1A & OAS-1B | 568 | 15.4225 | 3
244 | Office | 124 | 8 |  | 143 | 3 | 3 | OAS-1A & OAS-1B | 1144 | 6.5035 | 2
246 | Open Work Area | 119 | 7 |  | 252 | 5 | 5 | OAS-1A & OAS-1B | 2016 | 3.5417 | 1
248 | Office | 135 | 9 |  | 143 | 3 | 3 | OAS-1A & OAS-1B | 1144 | 7.0804 | 2
250 | Main Office | 408 | 27 |  | 675 | 15 | 15 | UV | 5400 | 4.5333 | 2
300 | Collaboration | 25 | 1 |  | 264 | 6 | 1 | OAS-1A & OAS-1B | 2112 | 0.71023 | 0
301 | Classroom | 192 | 12 |  | 792 | 18 | 12 | UV | 6336 | 1.8182 | 1
302 | Classroom | 233 | 15 |  | 900 | 20 | 15 | UV | 7200 | 1.9417 | 1
304 | Classroom | 255 | 17 |  | 851 | 19 | 17 | UV | 6808 | 2.2474 | 1
306 | Classroom | 218 | 14 |  | 897 | 20 | 14 | UV | 7176 | 1.8227 | 1
308 | Classroom | 206 | 13 |  | 759 | 17 | 13 | UV | 6072 | 2.0356 | 1
309 | Classroom | 308 | 20 |  | 736 | 16 | 16 | UV | 5888 | 3.1386 | 1
311 | Classroom | 301 | 20 |  | 576 | 13 | 13 | UV | 4608 | 3.9193 | 1
315 | Classroom | 138 | 9 |  | 759 | 17 | 9 | UV | 6072 | 1.3636 | 1
316 | Classroom | 482 | 32 |  | 759 | 17 | 17 | UV | 6072 | 4.7628 | 2
317 | Classroom | 182 | 12 | Yes | 1173 | 26 | 26 | UV | 9384 | 1.1637 | 1
318 | Classroom | 146 | 9 | Yes | 713 | 16 | 16 | UV | 5704 | 1.5358 | 1
319 | Classroom | 209 | 13 |  | 736 | 16 | 13 | UV | 5888 | 2.1298 | 1
320 | Classroom | 165 | 11 |  | 736 | 16 | 11 | UV | 5888 | 1.6814 | 1
321A | Office | 96 | 6 |  | 154 | 3 | 3 | UV | 1232 | 4.6753 | 2
321B | Storage | 289 | 19 |  | 154 | 3 | 3 | UV | 1232 | 14.0747 | 3
322 | Classroom | 154 | 10 | Yes | 736 | 16 | 16 | UV | 5888 | 1.5693 | 1
324 | Classroom | 0 | 0 |  | 558 | 12 | 0 | UV | 4464 | 0 | 0
326 | Classroom | 225 | 15 |  | 900 | 20 | 15 | UV | 7200 | 1.875 | 1
327 | Office | 236 | 15 |  | 240 | 5 | 5 | UV | 1920 | 7.375 | 2
328 | LSS Community Rm | 43 | 2 |  | 288 | 6 | 2 | OAS-1A & OAS-1B | 2304 | 1.1198 | 1
329 | Classroom | 224 | 14 |  | 936 | 21 | 14 | UV | 7488 | 1.7949 | 1
400 | Collaboration | 0 | 0 |  | 264 | 6 | 0 | OAS-1A & OAS-1B | 2112 | 0 | 0
401 | Classroom | 0 | 0 |  | 759 | 17 | 0 | UV | 6072 | 0 | 0
402 | Classroom | 264 | 17 |  | 1311 | 29 | 17 | UV | 10488 | 1.5103 | 1
404 | Classroom | 250 | 16 |  | 345 | 7 | 7 | UV | 2760 | 5.4348 | 2
406 | Classroom | 330 | 22 |  | 1311 | 29 | 22 | UV | 10488 | 1.8879 | 1
407 | Classroom | 258 | 17 |  | 736 | 16 | 16 | UV | 5888 | 2.6291 | 1
409 | Classroom | 97 | 6 |  | 736 | 16 | 6 | UV | 5888 | 0.98845 | 0
411 | Classroom | 648 | 43 |  | 552 | 12 | 12 | UV | 4416 | 8.8043 | 2
415 | Classroom | 178 | 11 |  | 759 | 17 | 11 | UV | 6072 | 1.7589 | 1
416 | Classroom | 155 | 10 |  | 851 | 19 | 10 | UV | 6808 | 1.366 | 1
417 | Classroom | 3 | 0 |  | 713 | 16 | 0 | UV | 5704 | 0.031557 | 0
418 | Classroom | 182 | 12 |  | 851 | 19 | 12 | UV | 6808 | 1.604 | 1
419 | Classroom | 219 | 14 |  | 736 | 16 | 14 | UV | 5888 | 2.2317 | 1
420 | Classroom | 162 | 10 |  | 828 | 18 | 10 | UV | 6624 | 1.4674 | 1
421 | Office | 86 | 5 |  | 529 | 12 | 5 | UV | 4232 | 1.2193 | 1
422 | Classroom | 132 | 8 |  | 828 | 18 | 8 | UV | 6624 | 1.1957 | 1
424 | Office | 158 | 10 |  | 99 | 2 | 2 | UV | 792 | 11.9697 | 3
426 | Classroom | 73 | 4 |  | 900 | 20 | 4 | UV | 7200 | 0.60833 | 0
427 | Classroom | 339 | 22 |  | 1200 | 27 | 22 | UV | 9600 | 2.1187 | 1
428 | Collaboration | 62 | 4 |  | 444 | 10 | 4 | OAS-1A & OAS-1B | 3552 | 1.0473 | 1
500 | Collaboration | 22 | 1 |  | 322 | 7 | 1 | OAS-1A & OAS-1B | 2576 | 0.51242 | 0
501 | Classroom | 201 | 13 |  | 825 | 18 | 13 | UV | 6600 | 1.8273 | 1
502 | Classroom | 681 | 45 |  | 1380 | 31 | 31 | UV | 11040 | 3.7011 | 1
504 | Storage | 216 | 14 |  | 352 | 8 | 8 | UV | 2816 | 4.6023 | 2
506 | Classroom | 477 | 31 |  | 1357 | 30 | 30 | UV | 10856 | 2.6363 | 1
507 | Classroom | 155 | 10 |  | 851 | 19 | 10 | UV | 6808 | 1.366 | 1
509 | Classroom | 194 | 12 |  | 805 | 18 | 12 | UV | 6440 | 1.8075 | 1
515 | Classroom | 269 | 17 |  | 920 | 20 | 17 | UV | 7360 | 2.1929 | 1
516 | Classroom | 162 | 10 |  | 1012 | 23 | 10 | UV | 8096 | 1.2006 | 1
517 | Classroom | 647 | 43 |  | 943 | 21 | 21 | UV | 7544 | 5.1458 | 2
518 | Classroom | 73 | 4 |  | 851 | 19 | 4 | UV | 6808 | 0.64336 | 0
519 | Classroom | 201 | 13 |  | 693 | 15 | 13 | UV | 5544 | 2.1753 | 1
520 | Classroom | 515 | 34 |  | 858 | 19 | 19 | UV | 6864 | 4.5017 | 2
522A | Office | 21 | 1 |  | 100 | 2 | 1 | OAS-1A & OAS-1B | 800 | 1.575 | 1
523 | Classroom | 950 | 63 |  | 1344 | 30 | 30 | UV | 10752 | 5.3013 | 2
524 | Staff Lounge | 527 | 35 |  | 375 | 8 | 8 | UV | 3000 | 10.54 | 3
526 | Classroom | 1235 | 82 |  | 1175 | 26 | 26 | UV | 9400 | 7.883 | 2
601 | Classroom | 231 | 15 |  | 936 | 21 | 15 | UV | 7488 | 1.851 | 1
602 | Classroom | 325 | 21 |  | 920 | 20 | 20 | UV | 7360 | 2.6495 | 1
603 | Production Studio | 25 | 1 |  | 160 | 3 | 1 | OAS-1A & OAS-1B | 1280 | 1.1719 | 1
603A | Control Rm | 25 | 1 |  | 96 | 2 | 1 | OAS-1A & OAS-1B | 768 | 1.9531 | 1
604 | Classroom | 568 | 37 |  | 460 | 10 | 10 | UV | 3680 | 9.2609 | 2
605 | Classroom | 609 | 40 |  | 1152 | 26 | 26 | UV | 9216 | 3.9648 | 1
606 | Classroom | 140 | 9 |  | 621 | 14 | 9 | UV | 4968 | 1.6908 | 1
609 | Classroom | 614 | 40 |  | 900 | 20 | 20 | UV | 7200 | 5.1167 | 2
611 | Classroom | 256 | 17 |  | 900 | 20 | 17 | UV | 7200 | 2.1333 | 1
612 | Classroom | 208 | 13 |  | 714 | 16 | 13 | UV | 5712 | 2.1849 | 1
613 | Classroom | 564 | 37 |  | 792 | 18 | 18 | UV | 6336 | 5.3409 | 2
614 | Classroom | 290 | 19 |  | 756 | 17 | 17 | UV | 6048 | 2.877 | 1
615 | Storage | 261 | 17 |  | 336 | 7 | 7 | UV | 2688 | 5.8259 | 2
616 | Classroom | 265 | 17 |  | 900 | 20 | 17 | UV | 7200 | 2.2083 | 1
617 | Office | 92 | 6 |  | 300 | 6 | 6 | UV | 2400 | 2.3 | 1
620 | Classroom | 750 | 50 |  | 900 | 20 | 20 | UV | 7200 | 6.25 | 2
620 | Classroom | 567 | 37 |  | 2304 | 52 | 37 | UV | 18432 | 1.8457 | 1
- | Auditorium | 1102 | 73 |  | 8648 | 196 | 73 | AHU | 69184 | 0.95571 | 0
- | Faculty/Office | 0 | 0 |  | 330 | 7 | 0 | AC | 2640 | 0 | 0
- | Practice Room 1 | 0 | 0 |  | 77 | 1 | 0 | HV | 616 | 0 | 0
- | Practice Room 2 | 0 | 0 |  | 77 | 1 | 0 | HV | 616 | 0 | 0
- | Practice Room 3 | 0 | 0 |  | 77 | 1 | 0 | HV | 616 | 0 | 0
- | Kitchen Office | 15 | 1 |  | 99 | 2 | 1 | RTU | 792 | 1.1364 | 1
- | Weight Room | 163 | 10 |  | 1632 | 37 | 10 | AHU | 13056 | 0.74908 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | Franklin Learning Center | [7 empty] | 0 | 0 | 0
Vendor: | Devine | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 318 | 21 |  | 840 | 19 | 19 |  | 6720 | 2.8393 | 1
101/102 | Classroom | 144 | 9 |  | 1426 | 32 | 9 |  | 11408 | 0.75736 | 0
103 / 104 | Conference | 811 | 54 |  | 1612 | 36 | 36 |  | 12896 | 3.7733 | 1
105 | Classroom | 186 | 12 |  | 690 | 15 | 12 |  | 5520 | 2.0217 | 1
108 | ESOL |  | 0 |  | 242 | 5 | 0 |  | 1936 | 0 | 0
111 | Classroom | 44 | 2 |  | 221 | 5 | 2 |  | 1768 | 1.4932 | 1
120 | Classroom | 528 | 35 |  | 625 | 14 | 14 |  | 5000 | 6.336 | 2
121 | Classroom | 486 | 32 |  | 806 | 18 | 18 |  | 6448 | 4.5223 | 2
122 | Classroom | 640 | 42 |  | 744 | 16 | 16 |  | 5952 | 6.4516 | 2
123 | Classroom | 705 | 47 |  | 660 | 15 | 15 |  | 5280 | 8.0114 | 2
124 | Classroom | 504 | 33 |  | 266 | 6 | 6 |  | 2128 | 14.2105 | 3
125 | Classroom | 615 | 41 |  | 575 | 13 | 13 |  | 4600 | 8.0217 | 2
126 | Classroom | 615 | 41 |  | 275 | 6 | 6 |  | 2200 | 16.7727 | 3
129 | Classroom | 238 | 15 |  | 675 | 15 | 15 |  | 5400 | 2.6444 | 1
132 | Classroom | 264 | 17 |  | 414 | 9 | 9 |  | 3312 | 4.7826 | 2
132a | Classroom | 391 | 26 |  | 690 | 15 | 15 |  | 5520 | 4.25 | 2
133 | Classroom | 730 | 48 |  | 759 | 17 | 17 |  | 6072 | 7.2134 | 2
200 | Classroom | 447 | 29 |  | 950 | 21 | 21 |  | 7600 | 3.5289 | 1
201 | Classroom | 372 | 24 |  | 713 | 16 | 16 |  | 5704 | 3.913 | 1
202 | Classroom | 349 | 23 |  | 690 | 15 | 15 |  | 5520 | 3.7935 | 1
203 / 204 | Classroom | 655 | 43 |  | 1426 | 32 | 32 |  | 11408 | 3.445 | 1
205 | Classroom | 294 | 19 |  | 713 | 16 | 16 |  | 5704 | 3.0926 | 1
206 | Classroom | 0 | 0 |  | 198 | 4 | 0 |  | 1584 | 0 | 0
207 | Classroom | 37 | 2 |  | 925 | 21 | 2 |  | 7400 | 0.3 | 0
208 | Classroom | 314 | 20 |  | 782 | 17 | 17 |  | 6256 | 3.0115 | 1
209 | Classroom | 638 | 42 |  | 875 | 19 | 19 |  | 7000 | 5.4686 | 2
210 | Classroom | 661 | 44 |  | 782 | 17 | 17 |  | 6256 | 6.3395 | 2
212 | Classroom | 621 | 41 |  | 851 | 19 | 19 |  | 6808 | 5.473 | 2
213 | Classroom | 0 | 0 |  | 165 | 3 | 0 |  | 1320 | 0 | 0
214 | Classroom | 580 | 38 |  | 625 | 14 | 14 |  | 5000 | 6.96 | 2
215 | Classroom | 446 | 29 |  | 720 | 16 | 16 |  | 5760 | 4.6458 | 2
216 | Classroom | 486 | 32 |  | 960 | 21 | 21 |  | 7680 | 3.7969 | 1
217 | Classroom | 410 | 27 |  | 960 | 21 | 21 |  | 7680 | 3.2031 | 1
218 | Classroom | 377 | 25 |  | 600 | 13 | 13 |  | 4800 | 4.7125 | 2
220 | Classroom | 174 | 11 |  | 980 | 22 | 11 |  | 7840 | 1.3316 | 1
221 | IMC/ Library | 433 | 28 |  | 1536 | 34 | 28 |  | 12288 | 2.1143 | 1
221 | Office | 210 | 14 |  | 154 | 3 | 3 |  | 1232 | 10.2273 | 3
300 | Classroom | 88 | 5 |  | 900 | 20 | 5 |  | 7200 | 0.73333 | 0
301 | Classroom | 215 | 14 |  | 506 | 11 | 11 |  | 4048 | 3.1868 | 1
302 | Classroom | 403 | 26 |  | 975 | 22 | 22 |  | 7800 | 3.1 | 1
303 | Classroom | 368 | 24 |  | 936 | 21 | 21 |  | 7488 | 2.9487 | 1
304 | Classroom | 287 | 19 |  | 575 | 13 | 13 |  | 4600 | 3.7435 | 1
305 | Classroom | 392 | 26 |  | 713 | 16 | 16 |  | 5704 | 4.1234 | 2
306 | Classroom | 168 | 11 |  | 297 | 6 | 6 |  | 2376 | 4.2424 | 2
307 | Classroom | 729 | 48 |  | 700 | 15 | 15 |  | 5600 | 7.8107 | 2
309 | Classroom | 443 | 29 |  | 480 | 10 | 10 |  | 3840 | 6.9219 | 2
310 | Medical Classroom | 1312 | 87 |  | 1403 | 31 | 31 |  | 11224 | 7.0135 | 2
310 | Doctor's Office | 3 | 0 |  | 77 | 1 | 0 |  | 616 | 0.29221 | 0
310 | Bathroom | 12 | 0 |  | 120 | 2 | 0 |  | 960 | 0.75 | 0
310 | Storage | 11 | 0 |  | 140 | 3 | 0 |  | 1120 | 0.58929 | 0
312 | Classroom | 538 | 35 |  | 575 | 13 | 13 |  | 4600 | 7.0174 | 2
312 | Councelor | 0 | 0 |  | 950 | 21 | 0 |  | 7600 | 0 | 0
315 | Classroom | 255 | 17 |  | 675 | 15 | 15 |  | 5400 | 2.8333 | 1
316 | Classroom | 353 | 23 |  | 644 | 14 | 14 |  | 5152 | 4.111 | 2
317 | Classroom | 465 | 31 |  | 950 | 21 | 21 |  | 7600 | 3.6711 | 1
318 | Classroom | 465 | 31 |  | 897 | 20 | 20 |  | 7176 | 3.888 | 1
318 | Prep Room / Chemistry |  | 0 |  | 156 | 3 | 0 |  | 1248 | 0 | 0
318 | Secure Closet |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
319 | Classroom | 263 | 17 |  | 575 | 13 | 13 |  | 4600 | 3.4304 | 1
321 | Classroom | 506 | 33 |  | 588 | 13 | 13 |  | 4704 | 6.4541 | 2
322 | Computer | 0 | 0 |  | 299 | 6 | 0 |  | 2392 | 0 | 0
323 | Classroom | 374 | 24 |  | 598 | 13 | 13 |  | 4784 | 4.6906 | 2
324 | Classroom | 104 | 6 |  | 552 | 12 | 6 |  | 4416 | 1.413 | 1
325 | Classroom | 118 | 7 |  | 594 | 13 | 7 |  | 4752 | 1.4899 | 1
- | Cafeteria | 1320 | 88 |  | 2808 | 63 | 63 |  | 22464 | 3.5256 | 1
- | Gym |  | 0 |  | 3649 | 82 | 0 |  | 29192 | 0 | 0
- | Office | 58 | 3 |  | 230 | 5 | 3 |  | 1840 | 1.8913 | 1
- | Office | 223 | 14 |  | 567 | 12 | 12 |  | 4536 | 2.9497 | 1
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Horace H. Furness High School | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Classroom |  | 0 |  | 1224 | 27 | 0 |  | 9792 | 0 | 0
3 | Classroom |  | 0 |  | 672 | 15 | 0 |  | 5376 | 0 | 0
4 | Classroom |  | 0 |  | 840 | 19 | 0 |  | 6720 | 0 | 0
5 | Classroom |  | 0 |  | 840 | 19 | 0 |  | 6720 | 0 | 0
101 | Classroom | 306 | 20 |  | 667 | 15 | 15 |  | 5336 | 3.4408 | 1
102 | Classroom |  | 0 |  | 768 | 17 | 0 |  | 6144 | 0 | 0
103 | classroom | 297 | 19 |  | 667 | 15 | 15 |  | 5336 | 3.3396 | 1
104 | Classroom |  | 0 |  | 896 | 20 | 0 |  | 7168 | 0 | 0
105 | classroom |  | 0 |  | 667 | 15 | 0 |  | 5336 | 0 | 0
106 | classroom | 326 | 21 |  | 667 | 15 | 15 |  | 5336 | 3.6657 | 1
107 | Library | 1463 | 97 |  | 2448 | 55 | 55 |  | 19584 | 4.4822 | 2
112 | Classroom |  | 0 |  | 448 | 10 | 0 |  | 3584 | 0 | 0
201 | classroom | 272 | 18 |  | 735 | 16 | 16 |  | 5880 | 2.7755 | 1
201A | Room |  | 0 |  | 448 | 10 | 0 |  | 3584 | 0 | 0
202 | Classroom |  | 0 |  | 1536 | 34 | 0 |  | 12288 | 0 | 0
203 | classroom | 540 | 36 |  | 874 | 19 | 19 |  | 6992 | 4.6339 | 2
204 | classroom | 443 | 29 |  | 814 | 18 | 18 |  | 6512 | 4.0817 | 2
205 | classroom | 392 | 26 |  | 667 | 15 | 15 |  | 5336 | 4.4078 | 2
206 | classroom |  | 0 |  | 667 | 15 | 0 |  | 5336 | 0 | 0
207 | classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | 0 | 0
208 | classroom | 328 | 21 |  | 660 | 15 | 15 |  | 5280 | 3.7273 | 1
209 | classroom |  | 0 |  | 725 | 16 | 0 |  | 5800 | 0 | 0
210 | classroom |  | 0 |  | 696 | 15 | 0 |  | 5568 | 0 | 0
211 | classroom | 319 | 21 |  | 696 | 15 | 15 |  | 5568 | 3.4375 | 1
212 | classroom | 359 | 23 |  | 696 | 15 | 15 |  | 5568 | 3.8685 | 1
213 | classroom | 316 | 21 |  | 696 | 15 | 15 |  | 5568 | 3.4052 | 1
214 | classroom |  | 0 |  | 696 | 15 | 0 |  | 5568 | 0 | 0
215 | Classroom |  | 0 |  | 576 | 13 | 0 |  | 4608 | 0 | 0
218 | classroom | 367 | 24 |  | 720 | 16 | 16 |  | 5760 | 3.8229 | 1
219A | classroom |  | 0 |  | 783 | 17 | 0 |  | 6264 | 0 | 0
219B | classroom | 275 | 18 |  | 1100 | 25 | 18 |  | 8800 | 1.875 | 1
220 | classroom | 292 | 19 |  | 690 | 15 | 15 |  | 5520 | 3.1739 | 1
221 | classroom | 490 | 32 |  | 770 | 17 | 17 |  | 6160 | 4.7727 | 2
221A | classroom | 380 | 25 |  | 770 | 17 | 17 |  | 6160 | 3.7013 | 1
222 | classroom |  | 0 |  | 161 | 3 | 0 |  | 1288 | 0 | 0
222A | Room |  | 0 |  | 560 | 12 | 0 |  | 4480 | 0 | 0
301A | classroom 301 | 360 | 24 |  | 690 | 15 | 15 |  | 5520 | 3.913 | 1
301B | classroom 301 | 345 | 23 |  | 672 | 15 | 15 |  | 5376 | 3.8504 | 1
302A | classroom 302 | 272 | 18 |  | 1056 | 24 | 18 |  | 8448 | 1.9318 | 1
302B | classroom 302 | 356 | 23 |  | 624 | 14 | 14 |  | 4992 | 4.2788 | 2
303 | classroom | 438 | 29 |  | 770 | 17 | 17 |  | 6160 | 4.2662 | 2
304 | classroom |  | 0 |  | 690 | 15 | 0 |  | 5520 | 0 | 0
305 | classroom |  | 0 |  | 672 | 15 | 0 |  | 5376 | 0 | 0
306 | classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | 0 | 0
307 | classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | 0 | 0
308 | classroom | 246 | 16 |  | 720 | 16 | 16 |  | 5760 | 2.5625 | 1
309 | classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | 0 | 0
310A | classroom |  | 0 |  | 1008 | 22 | 0 |  | 8064 | 0 | 0
310b | classroom |  | 0 |  | 1344 | 30 | 0 |  | 10752 | 0 | 0
311A | classroom | 201 | 13 |  | 1008 | 22 | 13 |  | 8064 | 1.4955 | 1
311B | classroom |  | 0 |  | 1148 | 26 | 0 |  | 9184 | 0 | 0
312A | classroom |  | 0 |  | 960 | 21 | 0 |  | 7680 | 0 | 0
312B | classroom |  | 0 |  | 400 | 9 | 0 |  | 3200 | 0 | 0
313A | classroom | 175 | 11 |  | 1008 | 22 | 11 |  | 8064 | 1.3021 | 1
313B | classroom |  | 0 |  | 480 | 10 | 0 |  | 3840 | 0 | 0
314 | Classroom |  | 0 |  | 448 | 10 | 0 |  | 3584 | 0 | 0
315 | Classroom |  | 0 |  | 392 | 8 | 0 |  | 3136 | 0 | 0
316 | classroom | 73 | 4 |  | 696 | 15 | 4 |  | 5568 | 0.78664 | 0
317A | classroom |  | 0 |  | 1137 | 25 | 0 |  | 9096 | 0 | 0
317B | classroom | 117 | 7 |  | 1008 | 22 | 7 |  | 8064 | 0.87054 | 0
318A | classroom |  | 0 |  | 1152 | 26 | 0 |  | 9216 | 0 | 0
318B | classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | 0 | 0
319A | classroom | 392 | 26 |  | 1056 | 24 | 24 |  | 8448 | 2.7841 | 1
319B | classroom | 215 | 14 |  | 320 | 7 | 7 |  | 2560 | 5.0391 | 2
320A | classroom |  | 0 |  | 920 | 20 | 0 |  | 7360 | 0 | 0
320B | classroom |  | 0 |  | 1056 | 24 | 0 |  | 8448 | 0 | 0
321A | classroom |  | 0 |  | 1056 | 24 | 0 |  | 8448 | 0 | 0
321B | classroom | 302 | 20 |  | 1056 | 24 | 20 |  | 8448 | 2.1449 | 1
- | Cafeteria | 153 | 10 |  | 3665 | 83 | 10 |  | 29320 | 0.3131 | 0
Main Office | Office |  | 0 |  | 1248 | 28 | 0 |  | 9984 | 0 | 0
Assistant Principal | Office |  | 0 |  | 360 | 8 | 0 |  | 2880 | 0 | 0
Burke | Office |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
SSO | Office |  | 0 |  | 240 | 5 | 0 |  | 1920 | 0 | 0
Nurse | Suite |  | 0 |  | 960 | 21 | 0 |  | 7680 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Girard Academic Music Program (GAMP) High School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | CAFE | 9130 | 608 |  | 977 | 22 | 22 |  | 7816 | 70.087 | 5
- | GYM |  | 0 |  | 6667 | 151 | 0 |  | 53336 | 0 | 0
- | GYM OFFICE |  | 0 |  | 99 | 2 | 0 |  | 792 | 0 | 0
- | LOWER HALF OF AUDITORIUM | 13845 | 923 |  | 6498 | 147 | 147 |  | 51984 | 15.9799 | 3
- | UPPER HALF OF AUDITORIUM | 14721 | 981 |  | 3247 | 73 | 73 |  | 25976 | 34.0029 | 4
Principal | Office | 0 | 0 | Yes | 363 | 8 | 8 |  | 2904 | 0 | 0
Assistant Principal | Office | 0 | 0 |  | 169 | 3 | 0 |  | 1352 | 0 | 0
Main Office | Office | 0 | 0 | Yes | 266 | 6 | 6 |  | 2128 | 0 | 0
Counselor 1 | Office | 0 | 0 | Yes | 134 | 3 | 3 |  | 1072 | 0 | 0
Counselor 2 | Office | 0 | 0 | Yes | 246 | 5 | 5 |  | 1968 | 0 | 0
Nurse | Office | 0 | 0 | Yes | 88 | 2 | 2 |  | 704 | 0 | 0
Lunch Room | Lunch Room | 0 | 0 |  | 2580 | 58 | 0 |  | 20640 | 0 | 0
Orchestra Room | Orchestra Room | 0 | 0 | Yes | 1082 | 24 | 24 |  | 8656 | 0 | 0
Orchestra Room | Office |  | 0 |  | 330 | 7 |  |  | 2640 | 0 | 0
Band Room | Band Room | 0 | 0 | Yes | 1221 | 27 | 27 |  | 9768 | 0 | 0
102 | Classroom | 0 | 0 | Yes | 685 | 15 | 15 |  | 5480 | 0 | 0
103 | Classroom | 0 | 0 | Yes | 722 | 16 | 16 |  | 5776 | 0 | 0
104/105 | Classroom | 0 | 0 | Yes | 1063 | 24 | 24 |  | 8504 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 735 | 16 | 16 |  | 5880 | 0 | 0
108 | Classroom | 0 | 0 | Yes | 695 | 15 | 15 |  | 5560 | 0 | 0
109 | Classroom | 0 | 0 | Yes | 685 | 15 | 15 |  | 5480 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 679 | 15 | 15 |  | 5432 | 0 | 0
202 | Classroom | 0 | 0 | Yes | 679 | 15 | 15 |  | 5432 | 0 | 0
203 | Classroom | 0 | 0 | Yes | 715 | 16 | 16 |  | 5720 | 0 | 0
204 | Classroom | 0 | 0 | Yes | 683 | 15 | 15 |  | 5464 | 0 | 0
205 | Classroom | 0 | 0 | Yes | 680 | 15 | 15 |  | 5440 | 0 | 0
206 | Classroom | 0 | 0 | Yes | 711 | 16 | 16 |  | 5688 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 734 | 16 | 16 |  | 5872 | 0 | 0
208 | Classroom | 0 | 0 | Yes | 634 | 14 | 14 |  | 5072 | 0 | 0
209 | Classroom | 0 | 0 | Yes | 686 | 15 | 15 |  | 5488 | 0 | 0
211 | Classroom | 0 | 0 |  | 394 | 8 | 0 |  | 3152 | 0 | 0
301 | Classroom | 0 | 0 | Yes | 689 | 15 | 15 |  | 5512 | 0 | 0
302 | Classroom | 0 | 0 | Yes | 645 | 14 | 14 |  | 5160 | 0 | 0
303 | Classroom | 0 | 0 | Yes | 669 | 15 | 15 |  | 5352 | 0 | 0
304 | Classroom | 0 | 0 | Yes | 725 | 16 | 16 |  | 5800 | 0 | 0
305 | Classroom | 0 | 0 | Yes | 729 | 16 | 16 |  | 5832 | 0 | 0
306 | Classroom | 0 | 0 | Yes | 950 | 21 | 21 |  | 7600 | 0 | 0
307A | Classroom | 0 | 0 | Yes | 292 | 6 | 6 |  | 2336 | 0 | 0
308 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0
309 | Classroom | 0 | 0 | Yes | 687 | 15 | 15 |  | 5496 | 0 | 0
311 | Classroom | 0 | 0 | Yes | 348 | 7 | 7 |  | 2784 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-12 | [7 empty] | 0 | 0 | 0
School: | Edward Gideon Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Emcor Retest | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 309 | 20 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 2.8436 | 1
102 | Classroom | 380 | 25 |  | 745 | 16 | 16 | Unit Ventilator | 5960 | 3.8255 | 1
Hallway @ 102 | Hallway | 0 | 0 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
- | Girls Bathroom next to Room 102 |  | 0 |  | 262 | 5 | 0 | N/A | 2096 | 0 | 0
- | Boys Bathroom next to Room 102 |  | 0 |  | 294 | 6 | 0 | N/A | 2352 | 0 | 0
103 | Classroom | 247 | 16 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
103 A | - |  | 0 |  | 207 | 4 | 0 | Unit Ventilator | 1656 | 0 | 0
103 B | - |  | 0 |  | 175 | 3 | 0 | Unit Ventilator | 1400 | 0 | 0
104 | Classroom | 226 | 15 |  | 450 | 10 | 10 | Unit Ventilator | 3600 | 3.7667 | 1
104 A | - |  | 0 |  | 97 | 2 | 0 | Unit Ventilator | 776 | 0 | 0
104 B | - |  | 0 |  | 151 | 3 | 0 | Unit Ventilator | 1208 | 0 | 0
104 C | - |  | 0 |  | 134 | 3 | 0 | Unit Ventilator | 1072 | 0 | 0
104 | Counselor |  | 0 |  | 451 | 10 | 0 | Unit Ventilator | 3608 | 0 | 0
105 | Classroom | 323 | 21 |  | 872 | 19 | 19 | Unit Ventilator | 6976 | 2.7781 | 1
Hallway @ 105 | Hallway | 325 | 21 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
106A | Main Office |  | 0 | Yes | 394 | 8 | 8 | Unit Ventilator | 3152 | 0 | 0
106E | Principal Office |  | 0 | Yes | 166 | 3 | 3 | Unit Ventilator | 1328 | 0 | 0
109 | Classroom | 351 | 23 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 3.0682 | 1
110 | Classroom | 374 | 24 |  | 811 | 18 | 18 | Unit Ventilator | 6488 | 3.4587 | 1
111 | Classroom | 253 | 16 |  | 866 | 19 | 16 | Unit Ventilator | 6928 | 2.1911 | 1
113 A | School police |  | 0 |  | 317 | 7 | 0 | Unit Ventilator | 2536 | 0 | 0
113 b | inner office |  | 0 |  | 153 | 3 | 0 | Unit Ventilator | 1224 | 0 | 0
113 c | inner office |  | 0 | Yes | 164 | 3 | 3 | Unit Ventilator | 1312 | 0 | 0
201 | Classroom | 154 | 10 |  | 1019 | 23 | 10 | Unit Ventilator | 8152 | 1.1335 | 1
Hallway @ 201 | Hallway | 225 | 15 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
202 | Classroom | 537 | 35 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 4.3588 | 2
203 | Classroom | 0 | 0 | Yes | 938 | 21 | 21 | Unit Ventilator | 7504 | 0 | 0
204 | Classroom | 319 | 21 |  | 788 | 17 | 17 | Unit Ventilator | 6304 | 3.0362 | 1
205 | Classroom | 296 | 19 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 2.7007 | 1
206 | Classroom | 310 | 20 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 2.8285 | 1
Hallway @ 206 | Hallway | 0 | 0 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
207 | Classroom | 350 | 23 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 3.1934 | 1
- | Boys Bathroom outside Room 207 |  | 0 |  | 164 | 3 | 0 | N/A | 1312 | 0 | 0
208 | Classroom | 328 | 21 |  | 825 | 18 | 18 | Unit Ventilator | 6600 | 2.9818 | 1
- | Female Staff Bathroom outside Room 208 |  | 0 |  | 61 | 1 | 0 | N/A | 488 | 0 | 0
- | Girls Bathroom outside Room 208 |  | 0 |  | 127 | 2 | 0 | N/A | 1016 | 0 | 0
209 | Classroom | 310 | 20 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 2.8285 | 1
210 | Classroom | 253 | 16 |  | 811 | 18 | 16 | Unit Ventilator | 6488 | 2.3397 | 1
211 | Classroom | 262 | 17 |  | 829 | 18 | 17 | Unit Ventilator | 6632 | 2.3703 | 1
212 | Classroom | 365 | 24 |  | 825 | 18 | 18 | Unit Ventilator | 6600 | 3.3182 | 1
Hallway @ 212 | Hallway | 215 | 14 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
213 | Classroom | 357 | 23 |  | 426 | 9 | 9 | Unit Ventilator | 3408 | 6.2852 | 2
301 | Classroom | 189 | 12 | Yes | 829 | 18 | 18 | Unit Ventilator | 6632 | 1.7099 | 1
302 | Classroom | 298 | 19 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 2.719 | 1
302 A | Bathroom |  | 0 |  | 232 | 5 | 0 | N/A | 1856 | 0 | 0
302 B | Bathroom |  | 0 |  | 147 | 3 | 0 | N/A | 1176 | 0 | 0
303 | Classroom | 0 | 0 | Yes | 894 | 20 | 20 | Unit Ventilator | 7152 | 0 | 0
304 | Classroom | 316 | 21 |  | 788 | 17 | 17 | Unit Ventilator | 6304 | 3.0076 | 1
305 | Classroom | 422 | 28 |  | 820 | 18 | 18 | Unit Ventilator | 6560 | 3.8598 | 1
306 | Classroom | 288 | 19 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 2.6277 | 1
Hallway @ 306 | Hallway | 0 | 0 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
307 | Classroom | 351 | 23 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 3.2026 | 1
308 | Classroom | 476 | 31 |  | 826 | 18 | 18 | Unit Ventilator | 6608 | 4.322 | 2
Hallway @ 308 | Hallway | 250 | 16 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
309 | Classroom | 349 | 23 |  | 826 | 18 | 18 | Unit Ventilator | 6608 | 3.1689 | 1
310 | Classroom | 321 | 21 |  | 811 | 18 | 18 | Unit Ventilator | 6488 | 2.9686 | 1
311 | Classroom | 331 | 22 |  | 829 | 18 | 18 | Unit Ventilator | 6632 | 2.9946 | 1
312 | Classroom | 367 | 24 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 3.3485 | 1
Hallway @ 312 | Hallway | 215 | 14 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
- | Auditorium | 630 | 42 |  |  | 0 | 0 | AHU | 0 | 0 | 0
GYM | GYM | 572 | 38 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
Hallway @ Elevator | Hallway | 0 | 0 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
Hallway @ Stair D | Hallway | 231 | 15 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
- | Nurse | 0 | 0 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
- | Teachers Lounge | 0 | 0 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
- | Auditorium |  | 0 |  | 2998 | 68 | 0 | AHU | 23984 | 0 | 0
- | Auditorium Rear classroom |  | 0 |  | 251 | 5 | 0 | AHU | 2008 | 0 | 0
- | Boys bathroom outside main offce |  | 0 |  | 303 | 6 | 0 | N/A | 2424 | 0 | 0
- | 3rd floor Boys bathroom |  | 0 |  | 220 | 4 | 0 | N/A | 1760 | 0 | 0
- | Building Engineer Office |  | 0 |  | 99 | 2 | 0 | N/A | 792 | 0 | 0
- | 3rd floor Girls bathroom |  | 0 |  | 192 | 4 | 0 | N/A | 1536 | 0 | 0
- | Girls bathroom outside main offce |  | 0 |  | 300 | 6 | 0 | N/A | 2400 | 0 | 0
- | 3rd floor Gym Teacher office |  | 0 |  | 284 | 6 | 0 | N/A | 2272 | 0 | 0
- | 3rd floor Gym/Lunchroom |  | 0 |  | 3603 | 81 | 0 | Unit Ventilator | 28824 | 0 | 0
- | Kitchen |  | 0 |  | 509 | 11 | 0 | N/A | 4072 | 0 | 0
- | Parent & teacher conf rm |  | 0 |  | 123 | 2 | 0 | Unit Ventilator | 984 | 0 | 0
- | Principal Conf rm |  | 0 |  | 159 | 3 | 0 | Unit Ventilator | 1272 | 0 | 0
- | Teacher Lounge |  | 0 |  | 436 | 9 | 0 | Unit Ventilator | 3488 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Stephen Girard Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Meehan | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | 100 | 51 | 3 | Yes | 672 | 15 | 15 | Unit Ventilator | 5376 | 0.5692 | 0
101 | 101 | 114 | 7 | Yes | 1200 | 27 | 27 | Unit Ventilator | 9600 | 0.7125 | 0
103 | 103 | 27 | 1 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0.24107 | 0
105 | 105 | 62 | 4 |  | 840 | 19 | 4 | Unit Ventilator | 6720 | 0.55357 | 0
118 | Speech Classroom |  | 0 | Yes | 275 | 6 | 6 | N/A | 2200 | 0 | 0
200 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
201 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
202 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
203 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
204 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
205 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
206 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
207 | Classroom |  | 0 | Yes | 375 | 8 | 8 | Unit Ventilator | 3000 | 0 | 0
208 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
209 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
210 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
216 | Classroom |  | 0 |  | 200 | 4 | 0 |  | 1600 | 0 | 0
300 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
301 | Classroom |  | 0 |  | 840 | 19 | 0 | Unit Ventilator | 6720 | 0 | 0
302 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
303 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
304 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
305 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
306 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
307 / 309 | Classroom |  | 0 | Yes | 1375 | 31 | 31 | Unit Ventilator | 11000 | 0 | 0
308 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
308A | Classroom |  | 0 |  | 364 | 8 | 0 |  | 2912 | 0 | 0
310 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
- | Auditorium | 11536 | 769 |  | 2600 | 59 | 59 | AHU | 20800 | 33.2769 | 4
- | Gymnasium | 1656 | 110 |  | 3550 | 80 | 80 | AHU | 28400 | 3.4986 | 1
- | IMC | 227 | 15 |  | 1846 | 41 | 15 | Unit Ventilator | 14768 | 0.92226 | 0
- | Nurse |  | 0 | Yes | 170 | 3 | 3 | N/A | 1360 | 0 | 0
- | Principal Office |  | 0 | Yes | 294 | 6 | 6 |  | 2352 | 0 | 0
- | Main Office |  | 0 | Yes | 396 | 9 | 9 | Unit Ventilator | 3168 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | Philadelphia High School for Girls | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B-12 | Showers | 2144 | 142 |  | 2163 | 49 | 49 | AHU | 17304 | 7.4341 | 2
B-13 | Visitors' Lockers | 0 | 0 |  | 256 | 5 | 0 | Unit Ventilator | 2048 | 0 | 0
B-14 | Home Lockers | 0 | 0 |  | 316 | 7 | 0 | Unit Ventilator | 2528 | 0 | 0
B-16 | Girls' Locker Room | 1254 | 83 |  | 4702 | 106 | 83 | Unit Ventilator | 37616 | 2.0002 | 1
G-1 | Classroom | 292 | 19 |  | 1032 | 23 | 19 | Unit Ventilator | 8256 | 2.1221 | 1
G-3 | Classroom | 459 | 30 |  | 1216 | 27 | 27 | Unit Ventilator | 9728 | 2.831 | 1
G-6 | - | 0 | 0 |  | 734 | 16 | 0 | Unit Ventilator | 5872 | 0 | 0
G-8 | Dance | 277 | 18 |  | 1275 | 28 | 18 | Unit Ventilator | 10200 | 1.6294 | 1
G-10 | Classroom | 281 | 18 |  | 741 | 16 | 16 | Unit Ventilator | 5928 | 2.8441 | 1
G-11 | Classroom | 274 | 18 |  | 745 | 16 | 16 | Unit Ventilator | 5960 | 2.7584 | 1
G-12 | Classroom | 222 | 14 |  | 714 | 16 | 14 | Unit Ventilator | 5712 | 2.3319 | 1
G-17 | Classroom | 93 | 6 |  | 748 | 17 | 6 | Unit Ventilator | 5984 | 0.93249 | 0
G-19 | Classroom | 277 | 18 |  | 718 | 16 | 16 | Unit Ventilator | 5744 | 2.8935 | 1
1 | Fitness Room | 227 | 15 |  | 1169 | 26 | 15 | Unit Ventilator | 9352 | 1.4564 | 1
2 | Fitness Room | 506 | 33 |  | 2048 | 46 | 33 | Unit Ventilator | 16384 | 1.853 | 1
100 | Classroom | 306 | 20 |  | 756 | 17 | 17 | Unit Ventilator | 6048 | 3.0357 | 1
101 | Classroom | 275 | 18 |  | 756 | 17 | 17 | Unit Ventilator | 6048 | 2.7282 | 1
102 | Archives | 145 | 9 |  | 689 | 15 | 9 | Unit Ventilator | 5512 | 1.5784 | 1
104 | Classroom | 221 | 14 |  | 756 | 17 | 14 | Unit Ventilator | 6048 | 2.1925 | 1
105 | Instruments | 612 | 40 |  | 2376 | 54 | 40 | Unit Ventilator | 19008 | 1.9318 | 1
106 | Roster Office | 208 | 13 |  | 778 | 17 | 13 | Unit Ventilator | 6224 | 2.0051 | 1
107 | Office | 290 | 19 |  | 799 | 18 | 18 | Unit Ventilator | 6392 | 2.7222 | 1
108 | Office | 0 | 0 |  | 769 | 17 | 0 | Unit Ventilator | 6152 | 0 | 0
109 | Office | 291 | 19 |  | 790 | 17 | 17 | Unit Ventilator | 6320 | 2.7627 | 1
110 | Office | 203 | 13 |  | 768 | 17 | 13 | Unit Ventilator | 6144 | 1.9824 | 1
111 | Poetry | 188 | 12 |  | 1182 | 26 | 12 | Unit Ventilator | 9456 | 1.1929 | 1
111-A | Health Office | 0 | 0 |  | 462 | 10 | 0 | Unit Ventilator | 3696 | 0 | 0
112 | Classroom | 0 | 0 |  | 767 | 17 | 0 | Unit Ventilator | 6136 | 0 | 0
113 | Classroom | 0 | 0 |  | 1655 | 37 | 0 | Unit Ventilator | 13240 | 0 | 0
114 | Classroom | 0 | 0 |  | 769 | 17 | 0 | Unit Ventilator | 6152 | 0 | 0
115 | Classroom | 0 | 0 |  | 1749 | 39 | 0 | Unit Ventilator | 13992 | 0 | 0
116 | Classroom | 0 | 0 |  | 749 | 17 | 0 | Unit Ventilator | 5992 | 0 | 0
118 | Classroom | 0 | 0 |  | 752 | 17 | 0 | Unit Ventilator | 6016 | 0 | 0
200 | Classroom | 0 | 0 |  | 775 | 17 | 0 | Unit Ventilator | 6200 | 0 | 0
201 | Classroom | 221 | 14 |  | 763 | 17 | 14 | Unit Ventilator | 6104 | 2.1723 | 1
202 | Classroom | 213 | 14 |  | 771 | 17 | 14 | Unit Ventilator | 6168 | 2.072 | 1
204 | Classroom | 0 | 0 |  | 771 | 17 | 0 | Unit Ventilator | 6168 | 0 | 0
205 | Music Office | 472 | 31 |  | 2334 | 53 | 31 | Unit Ventilator | 18672 | 1.5167 | 1
206 | Classroom | 0 | 0 |  | 780 | 17 | 0 | Unit Ventilator | 6240 | 0 | 0
207 | Classroom | 289 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8223 | 1
208 | Classroom | 213 | 14 |  | 776 | 17 | 14 | Unit Ventilator | 6208 | 2.0586 | 1
209 | Classroom | 251 | 16 |  | 786 | 17 | 16 | Unit Ventilator | 6288 | 2.395 | 1
210 | Classroom | 255 | 17 |  | 781 | 17 | 17 | Unit Ventilator | 6248 | 2.4488 | 1
211 | Classroom | 268 | 17 |  | 744 | 16 | 16 | Unit Ventilator | 5952 | 2.7016 | 1
212 | Classroom | 388 | 25 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.7308 | 1
214 | Classroom | 251 | 16 |  | 776 | 17 | 16 | Unit Ventilator | 6208 | 2.4259 | 1
215 | Classroom | 402 | 26 |  | 781 | 17 | 17 | Unit Ventilator | 6248 | 3.8604 | 1
216 | Classroom | 244 | 16 |  | 772 | 17 | 16 | Unit Ventilator | 6176 | 2.3705 | 1
217 | Classroom | 178 | 11 |  | 787 | 17 | 11 | Unit Ventilator | 6296 | 1.6963 | 1
218 | Classroom | 0 | 0 |  | 789 | 17 | 0 | Unit Ventilator | 6312 | 0 | 0
219 | Classroom | 54 | 3 |  | 783 | 17 | 3 | Unit Ventilator | 6264 | 0.51724 | 0
221 | Classroom | 290 | 19 |  | 841 | 19 | 19 | Unit Ventilator | 6728 | 2.5862 | 1
223 | Classroom | 0 | 0 |  | 891 | 20 | 0 | Unit Ventilator | 7128 | 0 | 0
300 | Classroom | 270 | 18 |  | 786 | 17 | 17 | Unit Ventilator | 6288 | 2.5763 | 1
302 | Classroom | 416 | 27 |  | 996 | 22 | 22 | Unit Ventilator | 7968 | 3.1325 | 1
303 | Classroom | 555 | 37 |  | 1052 | 23 | 23 | Unit Ventilator | 8416 | 3.9567 | 1
304 | Classroom | 525 | 35 |  | 1007 | 22 | 22 | Unit Ventilator | 8056 | 3.9101 | 1
305 | Classroom | 279 | 18 |  | 791 | 17 | 17 | Unit Ventilator | 6328 | 2.6454 | 1
306 | Classroom | 378 | 25 |  | 1034 | 23 | 23 | Unit Ventilator | 8272 | 2.7418 | 1
307 | Classroom | 0 | 0 |  | 781 | 17 | 0 | Unit Ventilator | 6248 | 0 | 0
308 | Classroom | 158 | 10 |  | 1048 | 23 | 10 | Unit Ventilator | 8384 | 1.1307 | 1
309 | Classroom | 188 | 12 |  | 787 | 17 | 12 | Unit Ventilator | 6296 | 1.7916 | 1
310 | Classroom | 403 | 26 |  | 1115 | 25 | 25 | Unit Ventilator | 8920 | 2.7108 | 1
311 | Classroom | 186 | 12 |  | 792 | 18 | 12 | Unit Ventilator | 6336 | 1.7614 | 1
312 | Classroom | 240 | 16 |  | 1015 | 23 | 16 | Unit Ventilator | 8120 | 1.7734 | 1
313 | Classroom | 202 | 13 |  | 779 | 17 | 13 | Unit Ventilator | 6232 | 1.9448 | 1
314 | Classroom | 329 | 21 |  | 1008 | 22 | 21 | Unit Ventilator | 8064 | 2.4479 | 1
315 | Classroom | 289 | 19 |  | 790 | 17 | 17 | Unit Ventilator | 6320 | 2.7437 | 1
316 | Classroom | 326 | 21 |  | 788 | 17 | 17 | Unit Ventilator | 6304 | 3.1028 | 1
317 | Classroom | 169 | 11 |  | 780 | 17 | 11 | Unit Ventilator | 6240 | 1.625 | 1
319 | Classroom | 351 | 23 |  | 706 | 16 | 16 | Unit Ventilator | 5648 | 3.7288 | 1
321 | Classroom | 293 | 19 |  | 716 | 16 | 16 | Unit Ventilator | 5728 | 3.0691 | 1
- | Auditorium | 946 | 63 |  | 10546 | 239 | 63 | AHU | 84368 | 0.67277 | 0
- | Gymnasium | 287 | 19 |  | 10449 | 237 | 19 | AHU | 83592 | 0.206 | 0
- | Main Cafeteria | 2523 | 168 |  | 12220 | 277 | 168 | Unit Ventilator | 97760 | 1.5485 | 1
- | Faculty Cafeteria | 549 | 36 |  | 1172 | 26 | 26 | Unit Ventilator | 9376 | 3.5132 | 1
- | Main Office | 192 | 12 |  | 1054 | 23 | 12 | Unit Ventilator | 8432 | 1.3662 | 1
- | Library | 538 | 35 |  | 5853 | 133 | 35 | Unit Ventilator | 46824 | 0.68939 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Samuel Gompers Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Capital | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Kindergarten | 334 | 22 |  | 2002 | 45 | 22 | Unit Ventilator | 16016 | 1.2512 | 1
102 | Classroom | 429 | 28 |  | 1106 | 25 | 25 | Unit Ventilator | 8848 | 2.9091 | 1
104 | Classroom | 450 | 30 |  | 1099 | 24 | 24 | Unit Ventilator | 8792 | 3.071 | 1
105 | Classroom | 444 | 29 |  | 1094 | 24 | 24 | Unit Ventilator | 8752 | 3.0439 | 1
106 | Classroom | 436 | 29 |  | 1095 | 24 | 24 | Unit Ventilator | 8760 | 2.9863 | 1
107 | Classroom | 432 | 28 |  | 1102 | 25 | 25 | Unit Ventilator | 8816 | 2.9401 | 1
B-107 | Library | 492 | 32 |  | 1241 | 28 | 28 | Unit Ventilator | 9928 | 2.9734 | 1
B-107A | Workroom | 28 | 1 |  | 204 | 4 | 1 | Unit Ventilator | 1632 | 1.0294 | 1
A-108 | Teacher Room | 138 | 9 |  | 387 | 8 | 8 | Unit Ventilator | 3096 | 2.6744 | 1
A-112 | Infirmary | 21 | 1 |  | 198 | 4 | 1 | Unit Ventilator | 1584 | 0.79545 | 0
A-113 | Waiting | 80 | 5 |  | 155 | 3 | 3 | FCU | 1240 | 3.871 | 1
A-114 | Nurse’s Office | 339 | 22 |  | 186 | 4 | 4 | FCU | 1488 | 13.6694 | 3
A-121 | Examination | 226 | 15 |  | 310 | 7 | 7 | FCU | 2480 | 5.4677 | 2
A-122 | Office | 22 | 1 |  | 133 | 3 | 1 | Unit Ventilator | 1064 | 1.2406 | 1
A-124 | Counselor Office | 34 | 2 |  | 178 | 4 | 2 | Unit Ventilator | 1424 | 1.4326 | 1
A-131 | General Office | 51 | 3 |  | 488 | 11 | 3 | Unit Ventilator | 3904 | 0.78381 | 0
A-133 | Principal Office | 32 | 2 |  | 232 | 5 | 2 | Unit Ventilator | 1856 | 1.0345 | 1
A-137 | Conference | 96 | 6 |  | 333 | 7 | 6 | Unit Ventilator | 2664 | 2.1622 | 1
A-150 | Office | 117 | 7 |  | 324 | 7 | 7 | FCU | 2592 | 2.7083 | 1
A-153 | Office | 122 | 8 |  | 322 | 7 | 7 | FCU | 2576 | 2.8416 | 1
201 | Classroom | 429 | 28 |  | 1083 | 24 | 24 | Unit Ventilator | 8664 | 2.9709 | 1
202 | Classroom | 431 | 28 |  | 1074 | 24 | 24 | Unit Ventilator | 8592 | 3.0098 | 1
203 | Classroom | 432 | 28 |  | 1075 | 24 | 24 | Unit Ventilator | 8600 | 3.014 | 1
204 | Classroom | 265 | 17 |  | 544 | 12 | 12 | Unit Ventilator | 4352 | 3.6535 | 1
205 | Classroom | 418 | 27 |  | 1109 | 25 | 25 | Unit Ventilator | 8872 | 2.8269 | 1
A-205 | Teachers Room | 156 | 10 |  | 353 | 8 | 8 | Unit Ventilator | 2824 | 3.3144 | 1
206 | Classroom | 433 | 28 |  | 1110 | 25 | 25 | Unit Ventilator | 8880 | 2.9257 | 1
207 | Classroom | 435 | 29 |  | 1112 | 25 | 25 | Unit Ventilator | 8896 | 2.9339 | 1
208 | Classroom | 438 | 29 |  | 1095 | 24 | 24 | Unit Ventilator | 8760 | 3 | 1
A-208 | After School Programs | 65 | 4 |  | 441 | 10 | 4 | Unit Ventilator | 3528 | 1.1054 | 1
B-209 | Classroom | 262 | 17 |  | 537 | 12 | 12 | Unit Ventilator | 4296 | 3.6592 | 1
B-210 | Classroom | 437 | 29 |  | 1093 | 24 | 24 | Unit Ventilator | 8744 | 2.9986 | 1
B-211 | Classroom | 435 | 29 |  | 1095 | 24 | 24 | Unit Ventilator | 8760 | 2.9795 | 1
212 | Classroom | 419 | 27 |  | 1084 | 24 | 24 | Unit Ventilator | 8672 | 2.899 | 1
213 | Classroom | 454 | 30 |  | 1087 | 24 | 24 | Unit Ventilator | 8696 | 3.1325 | 1
A-217 | Cafeteria | 466 | 31 |  | 1943 | 44 | 31 | AHU | 15544 | 1.7988 | 1
A-218 | Gymnasium | 1290 | 86 |  | 3950 | 89 | 86 | AHU | 31600 | 2.4494 | 1
Portable | R1 |  | 0 | Yes | 843 | 19 | 19 |  | 6744 | 0 | 0
Portable | R2 |  | 0 | Yes | 842 | 19 | 19 |  | 6736 | 0 | 0
Portable | R3 |  | 0 | Yes | 852 | 19 | 19 |  | 6816 | 0 | 0
Portable | R4 |  | 0 | Yes | 1033 | 23 | 23 |  | 8264 | 0 | 0
Portable | R5 |  | 0 | Yes | 1022 | 23 | 23 |  | 8176 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-22 | [7 empty] | 0 | 0 | 0
School: | Joseph Greenberg Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Borthers | Devine Brothers Retest | [6 empty] | 0 | 0 | 0
|  | Devine Brothers 2nd Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 325 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9438 | 1
101 | Classroom | 335 | 22 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.0344 | 1
102 | Classroom | 380 | 25 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.442 | 1
103 | Classroom | 288 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6087 | 1
104 | Classroom | 284 | 18 |  | 384 | 8 | 8 | Unit Ventilator | 3072 | 5.5469 | 2
105 | Nurse | 300 | 20 |  | 432 | 9 | 9 | Unit Ventilator | 3456 | 5.2083 | 2
106 | Classroom | 530 | 35 |  | 1012 | 23 | 23 | Unit Ventilator | 8096 | 3.9279 | 1
107 | Classroom | 671 | 44 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 5.8247 | 2
107A | Meeting room |  | 0 | Yes | 432 | 9 | 9 | Unit Ventilator | 3456 | 0 | 0
108 | Classroom | 441 | 29 |  | 1012 | 23 | 23 | Unit Ventilator | 8096 | 3.2683 | 1
109 | Classroom | 298 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6993 | 1
111 | Classroom | 291 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6359 | 1
200 | Classroom | 308 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.7899 | 1
201 | Classroom | 281 | 18 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.5453 | 1
202 | Classroom | 295 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6721 | 1
203 | Classroom | 351 | 23 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.1793 | 1
204 | Classroom | 317 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.8714 | 1
205 | Classroom | 326 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9529 | 1
207 | Classroom | 320 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.8986 | 1
209 | Classroom | 345 | 23 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.125 | 1
210 | Classroom | 316 | 21 |  | 384 | 8 | 8 | Unit Ventilator | 3072 | 6.1719 | 2
211 | Classroom | 281 | 18 |  | 368 | 8 | 8 | Unit Ventilator | 2944 | 5.7269 | 2
211a | Classroom | 375 | 25 |  | 621 | 14 | 14 | Unit Ventilator | 4968 | 4.529 | 2
211b | Classroom | 307 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.7808 | 1
212 | Classroom | 351 | 23 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.1793 | 1
213 | Classroom | 344 | 22 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.1159 | 1
214 | Classroom | 345 | 23 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.125 | 1
215 | Classroom | 375 | 25 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.3967 | 1
216 | Classroom | 312 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.8261 | 1
217 | Classroom | 326 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9529 | 1
300 | Classroom | 325 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9438 | 1
301 | Classroom | 291 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6359 | 1
302 | Classroom | 285 | 19 |  | 552 | 12 | 12 | Unit Ventilator | 4416 | 3.8723 | 1
303 | Classroom | 330 | 22 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9891 | 1
304 | Classroom | 325 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9438 | 1
305 | Classroom | 321 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9076 | 1
306 | Classroom | 289 | 19 |  | 384 | 8 | 8 | Unit Ventilator | 3072 | 5.6445 | 2
307 | Classroom | 345 | 23 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.125 | 1
309 | Classroom | 350 | 23 |  | 1242 | 28 | 23 | Unit Ventilator | 9936 | 2.1135 | 1
313 | Classroom | 302 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.7355 | 1
314 | Classroom | 289 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6178 | 1
315 | Classroom | 321 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9076 | 1
316 | Classroom | 311 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.817 | 1
317 | Classroom | 331 | 22 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9982 | 1
318 | Classroom | 314 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.8442 | 1
319 | Classroom | 311 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.817 | 1
321 | Classroom | 288 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6087 | 1
400 | Classroom | 375 | 25 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.2552 | 1
401 | IMC Classroom | 310 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.808 | 1
- | Auditorium | 12200 | 813 |  | 3213 | 73 | 73 | AHU | 25704 | 28.4781 | 4
- | Cafeteria | 7911 | 527 |  | 5250 | 119 | 119 | AHU | 42000 | 11.3014 | 3
- | Gym | 8800 | 586 |  | 3978 | 90 | 90 | AHU | 31824 | 16.5913 | 3
- | IMC Classroom | 220 | 14 |  | 828 | 18 | 14 | Unit Ventilator | 6624 | 1.9928 | 1
- | Teacher Lounge | 448 | 29 |  | 168 | 3 | 3 | Unit Ventilator | 1344 | 20 | 3
- | Main Office | 280 | 18 |  | 1134 | 25 | 18 | Unit Ventilator | 9072 | 1.8519 | 1
- | Dean's office |  | 0 | Yes | 135 | 3 | 3 | Unit Ventilator | 1080 | 0 | 0
- | Assistant principal office |  | 0 | Yes | 135 | 3 | 3 | Unit Ventilator | 1080 | 0 | 0
- | Principal's Office |  | 0 | Yes | 432 | 9 | 9 | Unit Ventilator | 3456 | 0 | 0
- | Kitchen |  | 0 | Yes | 864 | 19 | 19 | N/A | 6912 | 0 | 0
- | BE office | 275 | 18 |  | 441 | 10 | 10 | N/A | 3528 | 4.6769 | 2
- | Custodial office | 95 | 6 |  | 195 | 4 | 4 | N/A | 1560 | 3.6538 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | Albert M. Greenfield Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Meehan | Devine | Capital Part I | [5 empty] | 0 | 0 | 0
Vendor: | Capital Part II | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B06 | Music rm. | 329 | 21 |  | 416 | 9 | 9 | AHU | 3328 | 5.9315 | 2
B17 | Storage | 229 | 15 |  | 320 | 7 | 7 | N/A | 2560 | 5.3672 | 2
B36 | Music main | 452 | 30 |  | 962 | 21 | 21 | AHU | 7696 | 3.5239 | 1
B37 | Music Office | 151 | 10 |  | 168 | 3 | 3 | AHU | 1344 | 6.7411 | 2
B38 | Practice rm | 44 | 2 |  | 64 | 1 | 1 | AHU | 512 | 5.1562 | 2
B40 | Music Ensamble | 163 | 10 |  | 312 | 7 | 7 | AHU | 2496 | 3.9183 | 1
101 | Reception | 121 | 8 |  | 360 | 8 | 8 | AHU | 2880 | 2.5208 | 1
102 |  | 0 |  | Yes | 120 |  |  | N/A | 960 | 0 | 0
103 | Offices | 0 | 0 | Yes | 120 | 2 | 2 | AHU | 960 | 0 | 0
104 | Offices | 0 | 0 | Yes | 120 | 2 | 2 | AHU | 960 | 0 | 0
105 | Sensory Room | 46 | 3 |  | 120 | 2 | 2 | AHU | 960 | 2.875 | 1
106 | Office | 76 | 5 |  | 231 | 5 | 5 | AHU | 1848 | 2.4675 | 1
107 | Nurse Reception | 0 | 0 | Yes | 81 | 1 | 1 | AHU | 648 | 0 | 0
107A | Nurse Office | 48 | 3 | Yes | 189 | 4 | 4 | AHU | 1512 | 1.9048 | 1
107B | Offices | 0 | 0 | Yes | 99 | 2 | 2 | AHU | 792 | 0 | 0
107C | Storage | 0 | 0 |  | 110 | 2 | 0 | N/A | 880 | 0 | 0
108 | Conference | 65 | 4 |  | 238 | 5 | 4 | AHU | 1904 | 2.0483 | 1
109 | Admin | 0 | 0 | Yes | 130 | 2 | 2 | AHU | 1040 | 0 | 0
110 | Classroom | 340 | 22 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 2.7244 | 1
111 | Classroom | 491 | 32 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 3.9343 | 1
112 | Classroom | 366 | 24 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 2.9327 | 1
113A | Classroom | 1038 | 69 |  | 676 | 15 | 15 | Unit Ventilator | 5408 | 11.5163 | 3
126 | Lobby | 55 | 3 |  | 676 | 15 | 3 | Unit Ventilator | 5408 | 0.61021 | 0
128 | Corridor | 60 | 4 |  | 456 | 10 | 4 | Unit Ventilator | 3648 | 0.98684 | 0
129 | Principal Office | 94 | 6 |  | 220 | 5 | 5 | Unit Ventilator | 1760 | 3.2045 | 1
201 | Classroom | 150 | 10 |  | 260 | 5 | 5 | Unit Ventilator | 2080 | 4.3269 | 2
202 | Classroom | 390 | 26 |  | 884 | 20 | 20 | Unit Ventilator | 7072 | 3.3088 | 1
203 | Classroom | 302 | 20 |  | 884 | 20 | 20 | Unit Ventilator | 7072 | 2.5622 | 1
204 | Classroom | 493 | 32 |  | 725 | 16 | 16 | Unit Ventilator | 5800 | 5.1 | 2
205 | Classroom | 475 | 31 |  | 850 | 19 | 19 | Unit Ventilator | 6800 | 4.1912 | 2
206 | Classroom | 488 | 32 |  | 918 | 20 | 20 | Unit Ventilator | 7344 | 3.9869 | 1
207 | Classroom | 570 | 38 |  | 990 | 22 | 22 | Unit Ventilator | 7920 | 4.3182 | 2
208 | Classroom | 407 | 27 |  | 362 | 8 | 8 | Unit Ventilator | 2896 | 8.4323 | 2
208A | Classroom | 74 | 4 |  | 195 | 4 | 4 | Unit Ventilator | 1560 | 2.8462 | 1
209 | Classroom | 461 | 30 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 5.1451 | 2
210 | Classroom | 357 | 23 |  | 957 | 21 | 21 | Unit Ventilator | 7656 | 2.7978 | 1
211 | Classroom | 545 | 36 |  | 990 | 22 | 22 | Unit Ventilator | 7920 | 4.1288 | 2
212 | Classroom | 416 | 27 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.8424 | 1
213 | Classroom | 444 | 29 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 3.6039 | 1
214 | Classroom | 430 | 28 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.7326 | 1
215 | Classroom | 429 | 28 |  | 952 | 21 | 21 | Unit Ventilator | 7616 | 3.3797 | 1
216 | Classroom | 180 | 12 |  | 325 | 7 | 7 | Unit Ventilator | 2600 | 4.1538 | 2
217 | Classroom | 206 | 13 |  | 420 | 9 | 9 | Unit Ventilator | 3360 | 3.6786 | 1
218 | Classroom | 0 | 0 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
225 | Library | 1255 | 83 |  | 3628 | 82 | 82 | Unit Ventilator | 29024 | 2.5944 | 1
301 | Classroom | 570 | 38 |  | 957 | 21 | 21 | Unit Ventilator | 7656 | 4.4671 | 2
302 | Classroom | 289 | 19 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.5087 | 1
303 | Classroom | 328 | 21 |  | 957 | 21 | 21 | Unit Ventilator | 7656 | 2.5705 | 1
304 | Classroom | 501 | 33 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 4.9834 | 2
305 | Classroom | 336 | 22 |  | 1020 | 23 | 22 | Unit Ventilator | 8160 | 2.4706 | 1
306 | Classroom | 545 | 36 |  | 1020 | 23 | 23 | Unit Ventilator | 8160 | 4.0074 | 2
307 | Classroom | 374 | 24 |  | 506 | 11 | 11 | Unit Ventilator | 4048 | 5.5435 | 2
308 | Classroom | 418 | 27 |  | 460 | 10 | 10 | Unit Ventilator | 3680 | 6.8152 | 2
309 | Classroom | 550 | 36 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 4.4643 | 2
310 | Classroom | 441 | 29 |  | 1020 | 23 | 23 | Unit Ventilator | 8160 | 3.2426 | 1
311 | Classroom | 439 | 29 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 3.5633 | 1
312 | Classroom | 401 | 26 |  | 696 | 15 | 15 | Unit Ventilator | 5568 | 4.3211 | 2
313 | Classroom | 530 | 35 |  | 957 | 21 | 21 | Unit Ventilator | 7656 | 4.1536 | 2
314 | Classroom | 325 | 21 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 2.8409 | 1
315 | Classroom | 568 | 37 |  | 1650 | 37 | 37 | Unit Ventilator | 13200 | 2.5818 | 1
316 | Classroom | 318 | 21 |  | 1650 | 37 | 21 | Unit Ventilator | 13200 | 1.4455 | 1
317 | Classroom | 300 | 20 |  | 1664 | 37 | 20 | Unit Ventilator | 13312 | 1.3522 | 1
318 | Classroom | 62 | 4 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
- | B.E. Office | 139 | 9 |  | 88 | 2 | 2 | AHU | 704 | 11.8466 | 3
- | GYM | 1357 | 90 |  | 6110 | 138 | 90 | AHU | 48880 | 1.6657 | 1
- | Stage/Auditorium/Cafeteria | 0 | 0 |  | 4588 | 104 | 0 | AHU | 36704 | 0 | 0
- | Kitchen | 47 | 3 |  | 403 | 9 | 3 | AHU | 3224 | 0.87469 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-07 | [7 empty] | 0 | 0 | 0
School: | Horatio Hackett Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Part 2 | Part 3 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
104 | Library | 501 | 33 | Yes | 1920 | 43 | 43 | Unit Ventilator | 15360 | 1.957 | 1
106 | Gym Mechanical | 497 | 33 |  | 624 | 14 | 14 | AHU | 4992 | 5.9736 | 2
107 | Gym Mechanical | 959 | 63 |  | 1400 | 31 | 31 | AHU | 11200 | 5.1375 | 2
108 | Lounge | 299 | 19 |  | 560 | 12 | 12 | Unit Ventilator | 4480 | 4.0045 | 2
109 | Classroom | 394 | 26 |  | 1136 | 25 | 25 | Unit Ventilator | 9088 | 2.6012 | 1
110 | Classroom | 323 | 21 |  | 1024 | 23 | 21 | Unit Ventilator | 8192 | 2.3657 | 1
111 | Classroom | 284 | 18 |  | 776 | 17 | 17 | Unit Ventilator | 6208 | 2.7448 | 1
112 | Classroom | 280 | 18 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 2.9167 | 1
201 | Classroom | 279 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4911 | 1
202 | Classroom | 658 | 43 |  | 784 | 17 | 17 | Unit Ventilator | 6272 | 6.2946 | 2
203 | Classroom | 335 | 22 |  | 784 | 17 | 17 | Unit Ventilator | 6272 | 3.2047 | 1
204 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0
205 | Classroom | 475 | 31 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 4.2411 | 2
205A | Sm office / Speech Room | 223 | 14 |  | 304 | 6 | 6 | Unit Ventilator | 2432 | 5.5016 | 2
206 | Classroom | 0 | 0 | Yes | 696 | 15 | 15 | Unit Ventilator | 5568 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 488 | 11 | 11 | Unit Ventilator | 3904 | 0 | 0
207A | Small Office | 120 | 8 |  | 248 | 5 | 5 | Unit Ventilator | 1984 | 3.629 | 1
208 | Classroom | 278 | 18 |  | 784 | 17 | 17 | Unit Ventilator | 6272 | 2.6594 | 1
209 | Classroom | 362 | 24 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 4.0402 | 2
210 | Classroom | 0 | 0 | Yes | 784 | 17 | 17 | Unit Ventilator | 6272 | 0 | 0
211 | Classroom | 334 | 22 |  | 784 | 17 | 17 | Unit Ventilator | 6272 | 3.1952 | 1
212 | Classroom | 355 | 23 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.1696 | 1
212A | Office/Councelors |  | 0 |  | 336 | 7 | 0 | N/A | 2688 | 0 | 0
214 | Classroom | 455 | 30 |  | 864 | 19 | 19 | AHU | 6912 | 3.9497 | 1
215 | Classroom | 405 | 27 |  | 920 | 20 | 20 | AHU | 7360 | 3.3016 | 1
216 | Classroom | 505 | 33 |  | 832 | 18 | 18 | AHU | 6656 | 4.5523 | 2
217 | Classroom | 390 | 26 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.8086 | 1
218 | Classroom | 311 | 20 | Yes | 976 | 22 | 22 | AHU | 7808 | 2.3899 | 1
219 | Classroom | 405 | 27 |  | 880 | 20 | 20 | AHU | 7040 | 3.4517 | 1
219c | Classroom | 123 | 8 |  | 288 | 6 | 6 | Unit Ventilator | 2304 | 3.2031 | 1
305 | Classroom | 400 | 26 |  | 1000 | 22 | 22 | Unit Ventilator | 8000 | 3 | 1
306 | Classroom | 0 | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | 0 | 0
307 | Classroom | 315 | 21 |  | 824 | 18 | 18 | Unit Ventilator | 6592 | 2.8671 | 1
308 | Classroom | 329 | 21 |  | 824 | 18 | 18 | Unit Ventilator | 6592 | 2.9945 | 1
308D | Councelors | 38 | 2 | Yes | 384 | 8 | 8 | Unit Ventilator | 3072 | 0.74219 | 0
309 | Classroom | 395 | 26 |  | 944 | 21 | 21 | Unit Ventilator | 7552 | 3.1382 | 1
- | Caf/Auditorium | 1435 | 95 |  | 6914 | 157 | 95 | AHU | 55312 | 1.5566 | 1
- | GYM | 964 | 64 |  | 4770 | 108 | 64 | AHU | 38160 | 1.5157 | 1
- | Kitchen | 413 | 27 |  | 954 | 21 | 21 | AHU | 7632 | 3.2469 | 1
- | Main Office | 304 | 20 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.7404 | 1
- | Nurses Office | 50 | 3 | Yes | 564 | 12 | 12 | Unit Ventilator | 4512 | 0.66489 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-08 | [7 empty] | 0 | 0 | 0
School: | Andrew Hamilton Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Capital | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
104 | Classroom | 398 | 26 |  | 598 | 13 | 13 | Unit Ventilator | 4784 | 4.9916 | 2
106 | Classroom | 407 | 27 |  | 755 | 17 | 17 | Unit Ventilator | 6040 | 4.043 | 2
107 | Classroom | 376 | 25 |  | 599 | 13 | 13 | Unit Ventilator | 4792 | 4.7078 | 2
111 | Cafeteria | 1724 | 114 |  | 2444 | 55 | 55 | AHU | 19552 | 5.2905 | 2
112 | Auditorium | 813 | 54 |  | 3875 | 88 | 54 | AHU | 31000 | 1.5735 | 1
119 | Music | 391 | 26 |  | 827 | 18 | 18 | AHU | 6616 | 3.5459 | 1
121 | Gym | 1663 | 110 |  | 4628 | 105 | 105 | AHU | 37024 | 2.695 | 1
127 | Classroom | 595 | 39 |  | 1186 | 26 | 26 | Unit Ventilator | 9488 | 3.7626 | 1
128 | Classroom | 628 | 41 |  | 1370 | 31 | 31 | Unit Ventilator | 10960 | 3.438 | 1
129 | Classroom | 565 | 37 |  | 1112 | 25 | 25 | Unit Ventilator | 8896 | 3.8107 | 1
130 | Classroom | 608 | 40 |  | 1378 | 31 | 31 | Unit Ventilator | 11024 | 3.3091 | 1
131 | Classroom | 575 | 38 |  | 1169 | 26 | 26 | Unit Ventilator | 9352 | 3.6891 | 1
200 | Classroom | 415 | 27 |  | 763 | 17 | 17 | Unit Ventilator | 6104 | 4.0793 | 2
201 | Classroom | 527 | 35 |  | 776 | 17 | 17 | Unit Ventilator | 6208 | 5.0934 | 2
202 | Teachers Lounge | 300 | 20 |  | 469 | 10 | 10 | Unit Ventilator | 3752 | 4.7974 | 2
205 | Team Planning | 353 | 23 |  | 431 | 9 | 9 | Unit Ventilator | 3448 | 6.1427 | 2
206 | Classroom | 454 | 30 |  | 595 | 13 | 13 | Unit Ventilator | 4760 | 5.7227 | 2
207 | Classroom | 454 | 30 |  | 847 | 19 | 19 | Unit Ventilator | 6776 | 4.0201 | 2
209 | General Office | 750 | 50 |  | 866 | 19 | 19 | Unit Ventilator | 6928 | 6.4954 | 2
223 | Classroom | 432 | 28 |  | 847 | 19 | 19 | Unit Ventilator | 6776 | 3.8253 | 1
224 | Classroom | 426 | 28 |  | 837 | 19 | 19 | Unit Ventilator | 6696 | 3.8172 | 1
225 | Classroom | 394 | 26 |  | 837 | 19 | 19 | Unit Ventilator | 6696 | 3.5305 | 1
226 | Classroom | 393 | 26 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.5089 | 1
227 | Classroom | 395 | 26 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 3.5607 | 1
228 | Classroom | 477 | 31 |  | 847 | 19 | 19 | Unit Ventilator | 6776 | 4.2237 | 2
300 | Classroom | 400 | 26 |  | 793 | 18 | 18 | Unit Ventilator | 6344 | 3.7831 | 1
301 | Classroom | 421 | 28 |  | 791 | 17 | 17 | Unit Ventilator | 6328 | 3.9918 | 1
302 | Classroom | 393 | 26 |  | 786 | 17 | 17 | Unit Ventilator | 6288 | 3.75 | 1
303 | Classroom | 365 | 24 |  | 640 | 14 | 14 | Unit Ventilator | 5120 | 4.2773 | 2
306 | Classroom | 413 | 27 |  | 793 | 18 | 18 | Unit Ventilator | 6344 | 3.9061 | 1
307 | Classroom | 464 | 30 |  | 793 | 18 | 18 | Unit Ventilator | 6344 | 4.3884 | 2
309 | Classroom | 306 | 20 |  | 597 | 13 | 13 | Unit Ventilator | 4776 | 3.8442 | 1
310 | Classroom | 0 | 0 | Yes | 708 | 16 | 16 |  | 5664 | 0 | 0
311J | Janitors | 173 | 11 |  | 59 | 1 | 1 | Unit Ventilator | 472 | 21.9915 | 3
314 | Office | 551 | 36 |  | 214 | 4 | 4 | Unit Ventilator | 1712 | 19.3107 | 3
315 | Office | 724 | 48 |  | 214 | 4 | 4 | Unit Ventilator | 1712 | 25.3738 | 4
318 | Classroom | 382 | 25 |  | 911 | 20 | 20 | Unit Ventilator | 7288 | 3.1449 | 1
319 | Classroom | 0 | 0 | Yes | 616 | 14 | 14 | Unit Ventilator | 4928 | 0 | 0
320 | Team Planning | 0 | 0 | Yes | 235 | 5 | 5 | Unit Ventilator | 1880 | 0 | 0
321 | Team Planning | 300 | 20 |  | 243 | 5 | 5 | Unit Ventilator | 1944 | 9.2593 | 2
322 | Classroom | 450 | 30 |  | 820 | 18 | 18 | Unit Ventilator | 6560 | 4.1159 | 2
323 | Classroom | 0 | 0 | Yes | 620 | 14 | 14 | Unit Ventilator | 4960 | 0 | 0
327 | Office | 432 | 28 |  | 201 | 4 | 4 | Unit Ventilator | 1608 | 16.1194 | 3
328 | Office | 735 | 49 |  | 233 | 5 | 5 | Unit Ventilator | 1864 | 23.6588 | 3
331 | Classroom | 0 | 0 | Yes | 667 | 15 | 15 | Unit Ventilator | 5336 | 0 | 0
332 | Classroom | 339 | 22 |  | 625 | 14 | 14 | Unit Ventilator | 5000 | 4.068 | 2
333 | Classroom | 423 | 28 |  | 894 | 20 | 20 | Unit Ventilator | 7152 | 3.5487 | 1
334 | Classroom | 393 | 26 |  | 800 | 18 | 18 | Unit Ventilator | 6400 | 3.6844 | 1
335 | Classroom | 838 | 55 |  | 1684 | 38 | 38 | Unit Ventilator | 13472 | 3.7322 | 1
336 | Classroom | 375 | 25 |  | 908 | 20 | 20 | Unit Ventilator | 7264 | 3.0975 | 1
337 | Classroom | 0 | 0 | Yes | 932 | 21 | 21 | Unit Ventilator | 7456 | 0 | 0
- | Library | 2442 | 162 |  | 3672 | 83 | 83 | Unit Ventilator | 29376 | 4.9877 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21 | [7 empty] | 0 | 0 | 0
School: | John Hancock Demonstrative Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 127 | 8 |  | 528 | 12 | 8 | Unit Ventilator | 4224 | 1.804 | 1
102 | Classroom | 416 | 27 |  | 750 | 17 | 17 | Unit Ventilator | 6000 | 4.16 | 2
103 | Classroom | 123 | 8 |  | 567 | 12 | 8 | Unit Ventilator | 4536 | 1.627 | 1
104 | Classroom | 283 | 18 |  | 483 | 10 | 10 | Unit Ventilator | 3864 | 4.3944 | 2
105 | Classroom | 0 | 0 | Yes | 567 | 12 | 12 | Unit Ventilator | 4536 | 0 | 0
106 | Classroom | 171 | 11 |  | 756 | 17 | 11 | Unit Ventilator | 6048 | 1.6964 | 1
107 | Classroom | 237 | 15 |  | 806 | 18 | 15 | Unit Ventilator | 6448 | 2.2053 | 1
108 | Classroom | 0 | 0 | Yes | 648 | 14 | 14 | Unit Ventilator | 5184 | 0 | 0
109 | Classroom | 173 | 11 |  | 638 | 14 | 11 | Unit Ventilator | 5104 | 2.0337 | 1
110 | Classroom | 233 | 15 |  | 812 | 18 | 15 | Unit Ventilator | 6496 | 2.1521 | 1
111 | Classroom | 168 | 11 |  | 588 | 13 | 11 | Unit Ventilator | 4704 | 2.1429 | 1
200 | Classroom | 323 | 21 | Yes | 510 | 11 | 11 | Unit Ventilator | 4080 | 4.75 | 2
200A | Office |  | 0 | Yes |  | 0 | 0 |  | 0 | 0 | 0
202 | Classroom | 432 | 28 |  | 1271 | 28 | 28 | Unit Ventilator | 10168 | 2.5492 | 1
203 | Classroom | 299 | 19 |  | 588 | 13 | 13 | Unit Ventilator | 4704 | 3.8138 | 1
204 | Classroom | 324 | 21 |  | 575 | 13 | 13 | Unit Ventilator | 4600 | 4.2261 | 2
205 | Classroom | 255 | 17 |  | 616 | 14 | 14 | Unit Ventilator | 4928 | 3.1047 | 1
206 | Classroom | 324 | 21 |  | 1116 | 25 | 21 | Unit Ventilator | 8928 | 2.1774 | 1
207 | Classroom | 310 | 20 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.691 | 1
208 | Classroom | 308 | 20 |  | 837 | 19 | 19 | Unit Ventilator | 6696 | 2.7599 | 1
209 | Classroom | 312 | 20 |  | 868 | 19 | 19 | Unit Ventilator | 6944 | 2.6959 | 1
210 | Classroom | 303 | 20 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 3.1216 | 1
211 | Classroom | 298 | 19 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 2.9642 | 1
212 | Classroom |  | 0 | Yes | 744 | 16 | 16 | Unit Ventilator | 5952 | 0 | 0
213 | Classroom | 174 | 11 | Yes | 806 | 18 | 18 | Unit Ventilator | 6448 | 1.6191 | 1
214 | Computer Lab | 312 | 20 |  | 462 | 10 | 10 | Unit Ventilator | 3696 | 5.0649 | 2
215 | Classroom | 0 | 0 | Yes | 364 | 8 | 8 | Unit Ventilator | 2912 | 0 | 0
216 | Classroom | 0 | 0 |  | 364 | 8 | 0 | Unit Ventilator | 2912 | 0 | 0
217 | Classroom | 334 | 22 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 2.8629 | 1
219 | Classroom | 294 | 19 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.7841 | 1
218 | Nurse Office |  | 0 | Yes | 252 | 5 | 5 |  | 2016 | 0 | 0
220 | Office | 0 | 0 | Yes | 126 | 2 | 2 | Unit Ventilator | 1008 | 0 | 0
B213 | Classroom |  | 0 | Yes | 363 | 8 | 8 |  | 2904 | 0 | 0
B3 | Faculty Lounge | 184 | 12 | Yes | 540 | 12 | 12 | Unit Ventilator | 4320 | 2.5556 | 1
B13 | Classroom |  | 0 | Yes |  | 0 | 0 |  | 0 | 0 | 0
HS215 | Classroom |  | 0 | Yes | 608 | 13 | 13 |  | 4864 | 0 | 0
HS216 | Classroom |  | 0 | Yes | 608 | 13 | 13 |  | 4864 | 0 | 0
- | Classroom Behind kitchen | 37 | 2 |  | 224 | 5 | 2 | Unit Ventilator | 1792 | 1.2388 | 1
- | Gym Office | 0 | 0 | Yes | 100 | 2 | 2 | Unit Ventilator | 800 | 0 | 0
- | Gym |  | 0 |  | 288 | 6 | 0 | AHU | 2304 | 0 | 0
- | Cafeteria | 0 | 0 |  | 4600 | 104 | 0 | AHU | 36800 | 0 | 0
- | Kitchen | 0 | 0 | Yes | 448 | 10 | 10 | Unit Ventilator | 3584 | 0 | 0
- | Main Lobby | 0 | 0 |  | 720 | 16 | 0 | Unit Ventilator | 5760 | 0 | 0
- | Main Office | 201 | 13 |  | 340 | 7 | 7 | Unit Ventilator | 2720 | 4.4338 | 2
- | Main Office Side Office | 0 | 0 |  | 104 | 2 | 0 | Unit Ventilator | 832 | 0 | 0
- | Principals Office | 196 | 13 |  | 238 | 5 | 5 | Unit Ventilator | 1904 | 6.1765 | 2
Assistant Principal | Office |  | 0 | Yes |  | 0 | 0 |  | 0 | 0 | 0
Dean | Office |  | 0 | Yes |  | 0 | 0 |  | 0 | 0 | 0
- | Library | 692 | 46 |  | 1520 | 34 | 34 | Unit Ventilator | 12160 | 3.4145 | 1
- | Office Across from 210 | 0 | 0 |  | 120 | 2 | 0 | N/A | 960 | 0 | 0
- | Office across from gym | 0 | 0 |  | 204 | 4 | 0 | Unit Ventilator | 1632 | 0 | 0
- | Office across from Room 107 | 76 | 5 |  | 140 | 3 | 3 | Unit Ventilator | 1120 | 4.0714 | 2
- | Office across from room 110 | 115 | 7 |  | 140 | 3 | 3 | Unit Ventilator | 1120 | 6.1607 | 2
- | Office Next to gym | 0 | 0 |  | 80 | 1 | 0 | Unit Ventilator | 640 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-05-03 | [7 empty] | 0 | 0 | 0
School: | Warren G. Harding Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | - |  | 0 |  | 288 | 6 | 0 |  | 2304 | 0 | 0
101a | - |  | 0 |  | 288 | 6 | 0 |  | 2304 | 0 | 0
102 | - |  | 0 | Yes | 1128 | 25 | 25 |  | 9024 | 0 | 0
102a | - |  | 0 |  | 100 | 2 | 0 |  | 800 | 0 | 0
103 | - |  | 0 |  | 720 | 16 | 0 |  | 5760 | 0 | 0
104 | - |  | 0 | Yes | 888 | 20 | 20 |  | 7104 | 0 | 0
104a | - |  | 0 |  | 110 | 2 | 0 |  | 880 | 0 | 0
105 | - |  | 0 |  | 648 | 14 | 0 |  | 5184 | 0 | 0
105b | - |  | 0 |  | 770 | 17 | 0 |  | 6160 | 0 | 0
106c | - |  | 0 |  | 248 | 5 | 0 |  | 1984 | 0 | 0
107 | - |  | 0 |  | 936 | 21 | 0 |  | 7488 | 0 | 0
107a | - |  | 0 |  | 248 | 5 | 0 |  | 1984 | 0 | 0
107b | - |  | 0 |  | 50 | 1 | 0 |  | 400 | 0 | 0
107c | - |  | 0 |  | 25 | 0 | 0 |  | 200 | 0 | 0
108 | - |  | 0 | Yes | 886 | 20 | 20 |  | 7088 | 0 | 0
108a | - |  | 0 |  | 130 | 2 | 0 |  | 1040 | 0 | 0
108b | - |  | 0 |  | 25 | 0 | 0 |  | 200 | 0 | 0
108c | - |  | 0 |  | 50 | 1 | 0 |  | 400 | 0 | 0
109 | - |  | 0 |  | 576 | 13 | 0 |  | 4608 | 0 | 0
109a | - |  | 0 |  | 135 | 3 | 0 |  | 1080 | 0 | 0
110 | - |  | 0 |  | 912 | 20 | 0 |  | 7296 | 0 | 0
110a | - |  | 0 |  | 40 | 0 | 0 |  | 320 | 0 | 0
111 | - |  | 0 |  | 624 | 14 | 0 |  | 4992 | 0 | 0
112 | - |  | 0 |  | 576 | 13 | 0 |  | 4608 | 0 | 0
112a | - |  | 0 |  | 308 | 7 | 0 |  | 2464 | 0 | 0
113 | - |  | 0 |  | 360 | 8 | 0 |  | 2880 | 0 | 0
113a | - |  | 0 |  | 242 | 5 | 0 |  | 1936 | 0 | 0
113b | - |  | 0 |  | 352 | 8 | 0 |  | 2816 | 0 | 0
114 | - |  | 0 | Yes | 204 | 4 | 4 |  | 1632 | 0 | 0
116 | - |  | 0 |  | 2120 | 48 | 0 |  | 16960 | 0 | 0
116a | - |  | 0 |  | 416 | 9 | 0 |  | 3328 | 0 | 0
117 | - |  | 0 |  | 2700 | 61 | 0 |  | 21600 | 0 | 0
201 | - |  | 0 | Yes | 360 | 8 | 8 |  | 2880 | 0 | 0
201a | - |  | 0 |  | 432 | 9 | 0 |  | 3456 | 0 | 0
202 | - |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | 0 | 0
203 | - |  | 0 |  | 288 | 6 | 0 |  | 2304 | 0 | 0
203B | - |  | 0 | Yes | 200 | 4 | 4 |  | 1600 | 0 | 0
204 | - |  | 0 | Yes | 720 | 16 | 16 |  | 5760 | 0 | 0
205 | - |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | 0 | 0
206 | - |  | 0 |  | 319 | 7 | 0 |  | 2552 | 0 | 0
206a | - |  | 0 |  | 224 | 5 | 0 |  | 1792 | 0 | 0
206b | - |  | 0 |  | 112 | 2 | 0 |  | 896 | 0 | 0
208 | - |  | 0 | Yes | 792 | 18 | 18 |  | 6336 | 0 | 0
209 | IMC |  | 0 | Yes | 2160 | 49 | 49 |  | 17280 | 0 | 0
211 | - |  | 0 |  | 936 | 21 | 0 |  | 7488 | 0 | 0
212 | - |  | 0 |  | 888 | 20 | 0 |  | 7104 | 0 | 0
213 | - |  | 0 |  | 336 | 7 | 0 |  | 2688 | 0 | 0
214 | - |  | 0 |  | 696 | 15 | 0 |  | 5568 | 0 | 0
215 | - |  | 0 | Yes | 648 | 14 | 14 |  | 5184 | 0 | 0
216 | - |  | 0 |  | 744 | 16 | 0 |  | 5952 | 0 | 0
217 | - |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
218 | - |  | 0 |  | 792 | 18 | 0 |  | 6336 | 0 | 0
219 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | 0 | 0
220 | - |  | 0 |  | 744 | 16 | 0 |  | 5952 | 0 | 0
221 | - |  | 0 |  | 744 | 16 | 0 |  | 5952 | 0 | 0
222 | - |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | 0 | 0
223 | - |  | 0 | Yes | 816 | 18 | 18 |  | 6528 | 0 | 0
224 | - |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | 0 | 0
225 | - |  | 0 |  | 144 | 3 | 0 |  | 1152 | 0 | 0
301 | - |  | 0 |  | 648 | 14 | 0 |  | 5184 | 0 | 0
302 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | 0 | 0
303 | - |  | 0 | Yes | 390 | 8 | 8 |  | 3120 | 0 | 0
304 | - |  | 0 |  | 720 | 16 | 0 |  | 5760 | 0 | 0
305 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | 0 | 0
306 | - |  | 0 |  | 966 | 21 | 0 |  | 7728 | 0 | 0
307a | - |  | 0 |  | 360 | 8 | 0 |  | 2880 | 0 | 0
307b | - |  | 0 |  | 600 | 13 | 0 |  | 4800 | 0 | 0
308a | - |  | 0 |  | 480 | 10 | 0 |  | 3840 | 0 | 0
308b | - |  | 0 |  | 336 | 7 | 0 |  | 2688 | 0 | 0
309 | - |  | 0 |  | 816 | 18 | 0 |  | 6528 | 0 | 0
310 | - |  | 0 |  | 1056 | 24 | 0 |  | 8448 | 0 | 0
311 | - |  | 0 |  | 960 | 21 | 0 |  | 7680 | 0 | 0
311a | - |  | 0 |  | 143 | 3 | 0 |  | 1144 | 0 | 0
312 | - |  | 0 | Yes | 936 | 21 | 21 |  | 7488 | 0 | 0
313 | - |  | 0 |  | 984 | 22 | 0 |  | 7872 | 0 | 0
314 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | 0 | 0
315 | - |  | 0 |  | 360 | 8 | 0 |  | 2880 | 0 | 0
316 | - |  | 0 |  | 720 | 16 | 0 |  | 5760 | 0 | 0
317 | - |  | 0 | Yes | 720 | 16 | 16 |  | 5760 | 0 | 0
318 | - |  | 0 |  | 744 | 16 | 0 |  | 5952 | 0 | 0
320 | - |  | 0 |  | 816 | 18 | 0 |  | 6528 | 0 | 0
321 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | 0 | 0
322 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | 0 | 0
323 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | 0 | 0
324 | - |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | 0 | 0
325 | - |  | 0 |  | 816 | 18 | 0 |  | 6528 | 0 | 0
326 | - |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
- | Main Office |  | 0 | Yes | 468 | 10 | 10 |  | 3744 | 0 | 0
- | Nurse Office |  | 0 | Yes | 144 | 3 | 3 |  | 1152 | 0 | 0
- | Auditorium |  | 0 |  | 1944 | 44 | 0 |  | 15552 | 0 | 0
- | Girls Lunchroom |  | 0 |  | 2173 | 49 | 0 |  | 17384 | 0 | 0
- | Girls Gym |  | 0 |  | 1419 | 32 | 0 |  | 11352 | 0 | 0
- | Boy's Lunchroom |  | 0 |  | 2173 | 49 | 0 |  | 17384 | 0 | 0
- | Boy's Gym |  | 0 |  | 1419 | 32 | 0 |  | 11352 | 0 | 0
Sheet Last Modified: | 2021-04-21 | [7 empty] | 0 | 0 | 0
School: | Avery D. Harrington Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | Devine Retest | [6 empty] | 0 | 0 | 0
| EMCOR Retest | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B1 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | House Fan | 6440 | 0 | 0
B2 | Classroom | 0 | 0 | Yes | 594 | 13 | 13 | House Fan | 4752 | 0 | 0
B3 | Classroom | 530 | 35 |  | 1122 | 25 | 25 | Unit Ventilator | 8976 | 3.5428 | 1
B4 | B4 | 295 | 19 |  | 1064 | 24 | 19 | Unit Ventilator | 8512 | 2.0794 | 1
B5 | Classroom | 299 | 19 |  | 910 | 20 | 19 | Unit Ventilator | 7280 | 2.4643 | 1
B6 | - | 363 | 24 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.3528 | 1
B8 | Classroom | 0 | 0 | Yes | 651 | 14 | 0 | House Fan | 5208 | 0 | 0
B9 | - |  | 0 | Yes | 600 | 13 | 13 |  | 4800 | 0 | 0
10A | Classroom |  | 0 | Yes | 253 | 5 |  |  | 2024 | 0 | 0
101 | Classroom | 0 | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | 0 | 0
102 | Teachers Lounge |  | 0 |  | 216 | 4 | 0 | House Fan | 1728 | 0 | 0
103 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
104 | Classroom |  | 0 | Yes | 840 | 19 | 19 | House Fan | 6720 | 0 | 0
106 | Classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 725 | 16 | 16 | House Fan | 5800 | 0 | 0
108 | Classroom | 0 | 0 | Yes | 750 | 17 | 17 | House Fan | 6000 | 0 | 0
109 | Classroom | 651 | 43 |  | 1120 | 25 | 25 | Unit Ventilator | 8960 | 4.3594 | 2
109A | Classroom |  | 0 | Yes | 168 | 3 |  |  | 1344 | 0 | 0
109B | Classroom |  | 0 | Yes | 170 | 3 |  |  | 1360 | 0 | 0
201 | Classroom |  | 0 | Yes | 775 | 17 | 17 | House Fan | 6200 | 0 | 0
202 | Classroom |  | 0 | Yes | 750 | 17 | 17 | House Fan | 6000 | 0 | 0
203 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | 0 | 0
203a | Asst Princ Office |  | 0 | Yes | 403 | 9 | 9 | House Fan | 3224 | 0 | 0
204 | Classroom |  | 0 | Yes | 900 | 20 | 20 | House Fan | 7200 | 0 | 0
205 | Classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan | 6912 | 0 | 0
206 | Classroom |  | 0 | Yes | 840 | 19 | 19 | House Fan | 6720 | 0 | 0
207 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
208 | Classroom |  | 0 | Yes | 696 | 15 | 15 | House Fan | 5568 | 0 | 0
301 | Classroom |  | 0 | Yes | 900 | 20 | 20 | House Fan | 7200 | 0 | 0
302 | Classroom |  | 0 | Yes | 780 | 17 | 17 | House Fan | 6240 | 0 | 0
303 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | 0 | 0
303a | Counselor Office |  | 0 | Yes | 403 | 9 | 9 | House Fan | 3224 | 0 | 0
304 | Classroom |  | 0 | Yes | 930 | 21 | 21 | House Fan | 7440 | 0 | 0
305 | Classroom |  | 0 | Yes | 810 | 18 | 18 | House Fan | 6480 | 0 | 0
306 | Classroom |  | 0 | Yes | 870 | 19 | 19 | House Fan | 6960 | 0 | 0
307 | Classroom |  | 0 | Yes | 725 | 16 | 16 | House Fan | 5800 | 0 | 0
308 | Classroom |  | 0 | Yes | 754 | 17 | 17 | House Fan | 6032 | 0 | 0
- | Library | 1190 | 79 |  | 3822 | 86 | 79 | Unit Ventilator | 30576 | 2.3352 | 1
- | Auditorium | 130 | 8 |  | 90 | 2 | 2 | AHU | 720 | 10.8333 | 3
- | Gym |  | 0 |  | 2760 | 62 | 0 |  | 22080 | 0 | 0
- | Gym / Storeroom | 0 | 0 |  | 513 | 11 | 0 | AHU | 4104 | 0 | 0
| Kitchen |  | 0 | Yes | 120 | 2 |  |  | 960 | 0 | 0
- | Nurse Office |  | 0 | Yes | 190 | 4 | 4 | House Fan | 1520 | 0 | 0
- | Main Office |  | 0 | Yes | 420 | 9 | 9 | House Fan | 3360 | 0 | 0
- | Principal Office |  | 0 | Yes | 377 | 8 | 8 | House Fan | 3016 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-06 | [7 empty] | 0 | 0 | 0
School: | John F. Hartranft Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 560 | 37 |  | 1519 | 34 | 34 | Unit Ventilator | 12152 | 2.765 | 1
100A | Office | 0 | 0 |  | 108 | 2 | 0 | AHU | 864 | 0 | 0
100C | Office |  | 0 | Yes | 144 | 3 | 3 |  | 1152 | 0 | 0
100E | Office | 0 | 0 |  | 304 | 6 | 0 | AHU | 2432 | 0 | 0
100G | Office |  | 0 | Yes | 304 | 6 | 6 | AHU | 2432 | 0 | 0
100J | Office | 0 | 0 | Yes | 77 | 1 | 1 | AHU | 616 | 0 | 0
101 | Classroom | 310 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7679 | 1
102 | Classroom | 309 | 20 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 1.78 | 1
103 | Classroom | 344 | 22 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 1.9816 | 1
104 | Classroom | 440 | 29 |  | 1178 | 26 | 26 | Unit Ventilator | 9424 | 2.8014 | 1
105 | Classroom | 348 | 23 |  | 1178 | 26 | 23 | Unit Ventilator | 9424 | 2.2156 | 1
106 | Classroom | 258 | 17 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 1.4862 | 1
107 | Classroom | 488 | 32 |  | 1302 | 29 | 29 | Unit Ventilator | 10416 | 2.8111 | 1
108 | Classroom | 346 | 23 |  | 1178 | 26 | 23 | Unit Ventilator | 9424 | 2.2029 | 1
109 | Classroom | 226 | 15 | Yes | 1178 | 26 | 26 | Unit Ventilator | 9424 | 1.4389 | 1
110 | Classroom | 277 | 18 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 1.5956 | 1
111 | Classroom | 519 | 34 |  | 966 | 21 | 21 | Unit Ventilator | 7728 | 4.0295 | 2
112 | Classroom | 500 | 33 |  | 1302 | 29 | 29 | Unit Ventilator | 10416 | 2.8802 | 1
113 | Classroom | 485 | 32 |  | 874 | 19 | 19 | Unit Ventilator | 6992 | 4.1619 | 2
114 | Classroom | 407 | 27 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 3.2132 | 1
115 | Classroom | 316 | 21 | Yes | 1305 | 29 | 29 | Unit Ventilator | 10440 | 1.8161 | 1
116 | Classroom | 261 | 17 | Yes | 1305 | 29 | 29 | Unit Ventilator | 10440 | 1.5 | 1
117 | Classroom | 313 | 20 | Yes | 1305 | 29 | 29 | Unit Ventilator | 10440 | 1.7989 | 1
118 | Classroom | 473 | 31 |  | 1305 | 29 | 29 | Unit Ventilator | 10440 | 2.7184 | 1
118A | Classroom | 12 | 0 | Yes | 680 | 15 | 15 | AHU | 5440 | 0.13235 | 0
121 | Classroom | 55 | 3 | Yes | 792 | 18 | 18 | AHU | 6336 | 0.52083 | 0
121 | Backroom | 59 | 3 |  | 310 | 7 | 3 | AHU | 2480 | 1.4274 | 1
200 | Classroom | 368 | 24 | Yes | 1462 | 33 | 33 | Unit Ventilator | 11696 | 1.8878 | 1
201 | Classroom | 647 | 43 |  | 1178 | 26 | 26 | Unit Ventilator | 9424 | 4.1193 | 2
202 | Classroom | 454 | 30 |  | 1302 | 29 | 29 | Unit Ventilator | 10416 | 2.6152 | 1
203 | Classroom | 355 | 23 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 2.0449 | 1
204 | Classroom | 258 | 17 | Yes | 1178 | 26 | 26 | Unit Ventilator | 9424 | 1.6426 | 1
205 | Classroom | 491 | 32 |  | 1178 | 26 | 26 | Unit Ventilator | 9424 | 3.1261 | 1
206 | Classroom | 282 | 18 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 1.6244 | 1
207 | Classroom | 225 | 15 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 1.2961 | 1
208 | Classroom | 247 | 16 | Yes | 1179 | 26 | 26 | Unit Ventilator | 9432 | 1.5712 | 1
209 | Classroom | 274 | 18 | Yes | 1179 | 26 | 26 | Unit Ventilator | 9432 | 1.743 | 1
210 | Classroom | 485 | 32 |  | 1302 | 29 | 29 | Unit Ventilator | 10416 | 2.7938 | 1
211 | Classroom | 519 | 34 |  | 1302 | 29 | 29 | Unit Ventilator | 10416 | 2.9896 | 1
212 | Classroom | 309 | 20 | Yes | 1178 | 26 | 26 | Unit Ventilator | 9424 | 1.9673 | 1
214 | Classroom | 325 | 21 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 3.117 | 1
- | Cafeteria | 2300 | 153 |  | 1593 | 36 | 36 | AHU | 12744 | 10.8286 | 3
- | Cafeteria Entrance Hallway | 0 | 0 |  | 730 | 16 | 0 | AHU | 5840 | 0 | 0
- | Conference/Office | 0 | 0 |  | 304 | 6 | 0 | AHU | 2432 | 0 | 0
- | Engineer Office | 0 | 0 |  | 112 | 2 | 0 | AHU | 896 | 0 | 0
- | Engineer Breakroom | 0 | 0 |  | 99 | 2 | 0 | AHU | 792 | 0 | 0
- | Gym | 3499 | 233 |  | 6160 | 140 | 140 | AHU | 49280 | 4.2601 | 2
- | Kitchen | 0 | 0 |  | 864 | 19 | 0 | AHU | 6912 | 0 | 0
- | Main Office | 0 | 0 | Yes | 1056 | 24 | 24 | AHU | 8448 | 0 | 0
- | Nurse Office | 0 | 0 | Yes | 425 | 9 | 9 | AHU | 3400 | 0 | 0
- | Principal Office | 0 | 0 | Yes | 228 | 5 | 5 | AHU | 1824 | 0 | 0
- | Rear Entrance Hallway | 0 | 0 |  | 736 | 16 | 0 | AHU | 5888 | 0 | 0
- | Teacher Office | 0 | 0 |  | 77 | 1 | 0 | AHU | 616 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Haverford Child Development Center | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Brothers Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
2 | Classroom | 291 | 19 | Yes | 1058 | 24 | 24 | RTU | 8464 | 2.0629 | 1
3 | Classroom | 323 | 21 | Yes | 1058 | 24 | 24 | RTU | 8464 | 2.2897 | 1
4 | Classroom | 277 | 18 | Yes | 1058 | 24 | 24 | RTU | 8464 | 1.9636 | 1
5 | Classroom | 374 | 24 |  | 1058 | 24 | 24 | RTU | 8464 | 2.6512 | 1
5A | Office | 15 | 1 |  | 170 | 3 | 1 | RTU | 1360 | 0.66176 | 0
6 | Conference | 418 | 27 |  | 621 | 14 | 14 | RTU | 4968 | 5.0483 | 2
7 | Conference | 415 | 27 |  | 621 | 14 | 14 | RTU | 4968 | 5.0121 | 2
8 | Classroom | 287 | 19 |  | 560 | 12 | 12 | RTU | 4480 | 3.8438 | 1
8A | Office | 336 | 22 |  | 210 | 4 | 4 | RTU | 1680 | 12 | 3
9 | Classroom | 723 | 48 |  | 962 | 21 | 21 | RTU | 7696 | 5.6367 | 2
10A | Lounge | 34 | 2 |  | 216 | 4 | 2 | RTU | 1728 | 1.1806 | 1
10B | Book Storage | 11 | 0 |  | 288 | 6 | 0 | RTU | 2304 | 0.28646 | 0
- | Gym | 1065 | 71 |  | 2204 | 50 | 50 | RTU | 17632 | 3.6241 | 1
- | Lobby | 18 | 1 |  | 608 | 13 | 1 | RTU | 4864 | 0.22204 | 0
- | Storage | 89 | 5 |  | 572 | 13 | 5 | RTU | 4576 | 1.167 | 1
- | BE Office | 18 | 1 |  | 128 | 2 | 1 | RTU | 1024 | 1.0547 | 1
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-05 | [7 empty] | 0 | 0 | 0
School: | Charles W. Henry Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Devine Part 2 | Devine Part 3 | Devine Part 4 |  |  |  |  | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 0 | 0 | Yes | 650 | 14 | 14 | Unit Ventilator | 5200 | 0 | 0
102 | Classroom | 443 | 29 |  | 837 | 19 | 19 | Unit Ventilator | 6696 | 3.9695 | 1
103 | Classroom | 371 | 24 |  | 817 | 18 | 18 | Unit Ventilator | 6536 | 3.4058 | 1
104 | Classroom | 374 | 24 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 3.4291 | 1
104A | Office | 0 | 0 | Yes | 57 | 1 | 1 |  | 456 | 0 | 0
105 | Classroom | 397 | 26 |  | 951 | 21 | 21 | Unit Ventilator | 7608 | 3.1309 | 1
106 | Classroom | 308 | 20 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 2.8344 | 1
108 | Classroom | 481 | 32 |  | 650 | 14 | 14 | Unit Ventilator | 5200 | 5.55 | 2
109 | Classroom | 763 | 50 |  | 712 | 16 | 16 | Unit Ventilator | 5696 | 8.0372 | 2
110 | Classroom | 756 | 50 |  | 650 | 14 | 14 | Unit Ventilator | 5200 | 8.7231 | 2
110A | Office | 0 | 0 | Yes | 98 | 2 | 2 |  | 784 | 0 | 0
114 | Classroom | 773 | 51 |  | 749 | 17 | 17 |  | 5992 | 7.7403 | 2
201 | Classroom | 289 | 19 |  | 775 | 17 | 17 | Unit Ventilator | 6200 | 2.7968 | 1
202 | Classroom | 314 | 20 |  | 765 | 17 | 17 | Unit Ventilator | 6120 | 3.0784 | 1
203 | Classroom | 282 | 18 |  | 781 | 17 | 17 | Unit Ventilator | 6248 | 2.7081 | 1
203A | Office | 0 | 0 | Yes | 115 | 2 | 2 |  | 920 | 0 | 0
204 | Classroom | 262 | 17 | Yes | 847 | 19 | 19 | Unit Ventilator | 6776 | 2.32 | 1
206 | Classroom | 285 | 19 |  | 546 | 12 | 12 | Unit Ventilator | 4368 | 3.9148 | 1
207 | Classroom | 273 | 18 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 2.5123 | 1
208 | Classroom | 265 | 17 |  | 787 | 17 | 17 | Unit Ventilator | 6296 | 2.5254 | 1
208A | Office | 0 | 0 | Yes | 170 | 3 | 3 |  | 1360 | 0 | 0
209 | Classroom | 0 | 0 | Yes | 800 | 18 | 18 | Unit Ventilator | 6400 | 0 | 0
210 | Classroom | 398 | 26 |  | 946 | 21 | 21 | Unit Ventilator | 7568 | 3.1554 | 1
214 | Classroom | 282 | 18 | Yes | 1736 | 39 | 39 | Unit Ventilator | 13888 | 1.2183 | 1
215 | Classroom | 387 | 25 |  | 1128 | 25 | 25 | Unit Ventilator | 9024 | 2.5731 | 1
216 | Classroom | 284 | 18 |  | 546 | 12 | 12 | Unit Ventilator | 4368 | 3.9011 | 1
217 | Classroom | 393 | 26 |  | 544 | 12 | 12 | Unit Ventilator | 4352 | 5.4182 | 2
218 | Classroom | 307 | 20 | Yes | 1023 | 23 | 23 | Unit Ventilator | 8184 | 2.2507 | 1
- | Art Classroom | 249 | 16 |  | 778 | 17 | 16 | Unit Ventilator | 6224 | 2.4004 | 1
- | Auditorium | 1908 | 127 |  | 2417 | 54 | 54 | Unit Ventilator | 19336 | 5.9206 | 2
- | Cafe | 0 | 0 | Yes | 2104 | 47 | 47 | Unit Ventilator | 16832 | 0 | 0
- | Gym | 1076 | 71 | Yes | 3199 | 72 | 72 | Unit Ventilator | 25592 | 2.5227 | 1
- | Janitor Office | 0 | 0 |  |  | 0 | 0 | N/A | 0 | 0 | 0
- | Music Classroom | 292 | 19 |  | 833 | 18 | 18 | Unit Ventilator | 6664 | 2.6291 | 1
- | Sensory Classroom | 0 | 0 | Yes | 377 | 8 | 8 | Unit Ventilator | 3016 | 0 | 0
- | Counselor's Office | 0 | 0 |  | 299 | 6 | 0 |  | 2392 | 0 | 0
- | Nurse's Office | 0 | 0 | Yes | 263 | 5 | 5 |  | 2104 | 0 | 0
- | Medical Waiting Room | 0 | 0 | Yes | 177 | 4 | 4 |  | 1416 | 0 | 0
- | Principal's Office | 0 | 0 | Yes | 307 | 6 | 6 |  | 2456 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-16 | [7 empty] | 0 | 0 | 0
School: | Edward Heston Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Brothers 2nd Retest | [6 empty] | 0 | 0 | 0
| Devine Brothers 3rd Retest | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 148 | 9 |  | 440 | 10 | 9 | AHU | 3520 | 2.5227 | 1
102 | Office | 44 | 2 |  | 180 | 4 | 2 | AHU | 1440 | 1.8333 | 1
103 | Classroom | 70 | 4 |  | 308 | 7 | 4 | AHU | 2464 | 1.7045 | 1
103B | Office | 53 | 3 |  | 418 | 9 | 3 | AHU | 3344 | 0.95096 | 0
104 | Vestible | 25 | 1 |  | 220 | 5 | 1 | Unit Ventilator | 1760 | 0.85227 | 0
104A | Office | 36 | 2 |  | 102 | 2 | 2 | AHU | 816 | 2.6471 | 1
104B | Security Office | 56 | 3 |  | 123 | 2 | 2 | AHU | 984 | 3.4146 | 1
104C | Office | 27 | 1 |  | 99 | 2 | 1 | AHU | 792 | 2.0455 | 1
106 | Classroom | 328 | 21 | Yes | 1540 | 35 | 35 | Unit Ventilator | 12320 | 1.5974 | 1
107 | Classroom | 35 | 2 | Yes | 440 | 10 | 10 | AHU | 3520 | 0.59659 | 0
107A | Office | 74 | 4 |  | 840 | 19 | 4 | AHU | 6720 | 0.66071 | 0
107B | Storage | 17 | 1 |  | 196 | 4 | 1 | AHU | 1568 | 0.65051 | 0
108 | Classroom | 296 | 19 | Yes | 1540 | 35 | 35 | Unit Ventilator | 12320 | 1.4416 | 1
109 | Classroom | 275 | 18 |  | 440 | 10 | 10 | AHU | 3520 | 4.6875 | 2
110 | Classroom | 322 | 21 | Yes | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.2869 | 1
112 | Classroom | 312 | 20 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.799 | 1
114 | Classroom | 276 | 18 |  | 1012 | 23 | 18 | Unit Ventilator | 8096 | 2.0455 | 1
116 | Classroom | 279 | 18 | Yes | 968 | 22 | 22 | Unit Ventilator | 7744 | 2.1617 | 1
127 | Kitchen | 169 | 11 |  | 972 | 22 | 11 | AHU | 7776 | 1.304 | 1
200 | Classroom | 296 | 19 |  | 264 | 6 | 6 | Unit Ventilator | 2112 | 8.4091 | 2
202 | Classroom | 276 | 18 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 2.9403 | 1
204 | Classroom | 316 | 21 |  | 396 | 9 | 9 | Unit Ventilator | 3168 | 5.9848 | 2
206 | Classroom | 317 | 21 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 3.3771 | 1
208 | Classroom | 281 | 18 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 2.8175 | 1
210 | Classroom | 318 | 21 |  | 528 | 12 | 12 | Unit Ventilator | 4224 | 4.517 | 2
212 | Classroom | 329 | 21 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 3.2988 | 1
214 | Classroom | 318 | 21 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 3.1885 | 1
216 | Classroom | 270 | 18 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 2.7072 | 1
218 | Classroom | 291 | 19 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 2.9178 | 1
220 | Classroom | 424 | 28 |  | 748 | 17 | 17 | AHU | 5984 | 4.2513 | 2
222 | Classroom | 289 | 19 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 2.8977 | 1
224 | Classroom | 284 | 18 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.6894 | 1
228 | Room | 55 | 3 | Yes | 264 | 6 | 6 | Unit Ventilator | 2112 | 1.5625 | 1
232 | Classroom | 285 | 19 |  | 264 | 6 | 6 | Unit Ventilator | 2112 | 8.0966 | 2
300 | Lounge | 347 | 23 |  | 264 | 6 | 6 | Unit Ventilator | 2112 | 9.858 | 2
301 | Classroom | 175 | 11 | Yes | 1568 | 35 | 35 | AHU | 12544 | 0.83705 | 0
302 | Classroom | 291 | 19 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 3.1001 | 1
304 | Classroom | 284 | 18 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 2.8476 | 1
306 | Classroom | 327 | 21 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 3.2787 | 1
308 | Classroom | 321 | 21 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 3.4197 | 1
310 | Room | 0 | 0 | Yes | 748 | 17 | 17 | Unit Ventilator | 5984 | 0 | 0
312 | Classroom | 289 | 19 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 2.8977 | 1
314 | Room | 53 | 3 | Yes | 792 | 18 | 18 | Unit Ventilator | 6336 | 0.50189 | 0
316 | Classroom | 290 | 19 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.7462 | 1
318 | Room | 0 | 0 | Yes | 748 | 17 | 17 | Unit Ventilator | 5984 | 0 | 0
320 | Classroom | 303 | 20 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 3.0381 | 1
322 | Room | 249 | 16 |  | 748 | 17 | 16 | Unit Ventilator | 5984 | 2.4967 | 1
324 | Classroom | 302 | 20 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 3.0281 | 1
328 | Classroom | 298 | 19 |  | 264 | 6 | 6 | Unit Ventilator | 2112 | 8.4659 | 2
- | Copy Room | 38 | 2 |  | 44 | 1 | 1 | Unit Ventilator | 352 | 6.4773 | 2
- | Main office | 78 | 5 | Yes | 484 | 11 | 11 | Unit Ventilator | 3872 | 1.2087 | 1
- | Nurse | 30 | 2 |  | 176 | 4 | 2 | Unit Ventilator | 1408 | 1.2784 | 1
- | Nurse Examination | 76 | 5 |  | 88 | 2 | 2 | Unit Ventilator | 704 | 6.4773 | 2
- | Principal | 43 | 2 |  | 176 | 4 | 2 | Unit Ventilator | 1408 | 1.8324 | 1
- | Cafeteria/Aud | 4461 | 297 |  | 4268 | 97 | 97 | AHU | 34144 | 7.8392 | 2
- | Gym | 2645 | 176 |  | 4620 | 105 | 105 | AHU | 36960 | 4.2938 | 2
- | IMC | 1002 | 66 |  | 2948 | 67 | 66 | AHU | 23584 | 2.5492 | 1
- | IMC/Classrooms | 58 | 3 |  | 176 | 4 | 3 | AHU | 1408 | 2.4716 | 1
- | Teachers Lounge | 52 | 3 | Yes | 296 | 6 | 6 | AHU | 2368 | 1.3176 | 1
- | Dean's Office | 31 | 2 |  | 117 | 2 | 2 | AHU | 936 | 1.9872 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Hill-Freedman World Academy at Leeds Campus | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Room |  | 0 |  | 775 | 17 | 0 |  | 6200 | 0 | 0
2 | Room |  | 0 |  | 1008 | 22 | 0 |  | 8064 | 0 | 0
3 | Room | 0 | 0 |  | 832 | 18 | 0 |  | 6656 | 0 | 0
4 | Room |  | 0 |  | 784 | 17 | 0 |  | 6272 | 0 | 0
5 | Office |  | 0 |  | 240 | 5 | 0 |  | 1920 | 0 | 0
5 | Room |  | 0 |  | 1300 | 29 | 0 |  | 10400 | 0 | 0
6 | Office |  | 0 |  | 64 | 1 | 0 |  | 512 | 0 | 0
6 | Room | 0 | 0 |  | 300 | 6 | 0 |  | 2400 | 0 | 0
7 | Room | 0 | 0 |  | 672 | 15 | 0 |  | 5376 | 0 | 0
8 | Room |  | 0 |  | 500 | 11 | 0 |  | 4000 | 0 | 0
9 | Room |  | 0 |  | 1300 | 29 | 0 |  | 10400 | 0 | 0
10 | Room |  | 0 |  | 840 | 19 | 0 |  | 6720 | 0 | 0
119 | Classroom |  | 0 | Yes | 504 | 11 | 11 |  | 4032 | 0 | 0
121 | Classroom |  | 0 | Yes | 525 | 11 | 11 |  | 4200 | 0 | 0
124 | Classroom |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | 0 | 0
131 | Classroom |  | 0 | Yes | 735 | 16 | 16 |  | 5880 | 0 | 0
134 | Classroom |  | 0 | Yes | 1224 | 27 | 27 |  | 9792 | 0 | 0
- | Auditorium |  | 0 |  | 8760 | 199 | 0 |  | 70080 | 0 | 0
Main Office | Office |  | 0 |  | 588 | 13 | 0 |  | 4704 | 0 | 0
Principal | Office |  | 0 |  | 154 | 3 | 0 |  | 1232 | 0 | 0
Nurse | Office Suite |  | 0 | Yes | 892 | 20 | 20 |  | 7136 | 0 | 0
- | Boys Gym | 1074 | 71 |  | 5760 | 130 | 71 |  | 46080 | 1.3984 | 1
- | Boys Locker Room |  | 0 |  | 3420 | 77 | 0 |  | 27360 | 0 | 0
- | Cafeteria |  | 0 |  | 11360 | 258 | 0 |  | 90880 | 0 | 0
- | Conference Room |  | 0 |  | 390 | 8 | 0 |  | 3120 | 0 | 0
- | Girls Gym |  | 0 |  | 5760 | 130 | 0 |  | 46080 | 0 | 0
- | Girls Locker Room |  | 0 |  | 3420 | 77 | 0 |  | 27360 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-28 | [7 empty] | 0 | 0 | 0
School: | Thomas Holme Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Part 2 | Part 3 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Classroom | 619 | 41 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 4.6941 | 2
2 | Classroom | 524 | 34 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 3.9737 | 1
3 | Classroom | 285 | 19 |  | 920 | 20 | 19 | Unit Ventilator | 7360 | 2.3234 | 1
4 | Classroom | 576 | 38 |  | 1058 | 24 | 24 | Unit Ventilator | 8464 | 4.0832 | 2
5 | Classroom | 550 | 36 |  | 1058 | 24 | 24 | Unit Ventilator | 8464 | 3.8989 | 1
61 | Classroom | 214 | 14 | Yes | 1040 | 23 | 23 | Unit Ventilator | 8320 | 1.5433 | 1
62 | Truancy Court | 207 | 13 | Yes | 520 | 11 | 11 | Unit Ventilator | 4160 | 2.9856 | 1
63 | Classroom | 312 | 20 | Yes | 1040 | 23 | 23 | Unit Ventilator | 8320 | 2.25 | 1
64 | Classroom | 527 | 35 |  | 1040 | 23 | 23 | Unit Ventilator | 8320 | 3.8005 | 1
65 | Classroom | 300 | 20 | Yes | 1040 | 23 | 23 | Unit Ventilator | 8320 | 2.1635 | 1
66 | Classroom | 423 | 28 |  | 1040 | 23 | 23 | Unit Ventilator | 8320 | 3.0505 | 1
101 | Classroom | 679 | 45 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.5353 | 2
102 | Classroom | 626 | 41 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.1033 | 2
103 | Classroom | 500 | 33 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.0761 | 2
104 | Classroom | 615 | 41 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.0136 | 2
105 | Classroom | 628 | 41 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.1196 | 2
106 | Classroom | 697 | 46 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 7.5761 | 2
107 | Classroom | 321 | 21 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 2.5078 | 1
108 | Classroom |  | 0 | Yes | 108 | 2 | 2 |  | 864 | 0 | 0
109 | Classroom | 503 | 33 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.1005 | 2
110 | Classroom | 483 | 32 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 3.9375 | 1
111 | Classroom | 553 | 36 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.5082 | 2
112 | Classroom | 568 | 37 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.6304 | 2
113 | Classroom | 622 | 41 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.0707 | 2
201 | Classroom | 649 | 43 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.2908 | 2
202 | Classroom | 320 | 21 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 2.6087 | 1
203 | Classroom | 261 | 17 |  | 920 | 20 | 17 | Unit Ventilator | 7360 | 2.1277 | 1
204 | Classroom | 469 | 31 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 3.8234 | 1
205 | Classroom | 658 | 43 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.3641 | 2
206 | Classroom | 624 | 41 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.087 | 2
207 | Classroom | 607 | 40 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.9484 | 2
208 | Classroom | 626 | 41 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.1033 | 2
209 | Classroom | 764 | 50 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 6.2283 | 2
210 | Classroom | 589 | 39 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.8016 | 2
211 | Classroom | 279 | 18 |  | 920 | 20 | 18 | Unit Ventilator | 7360 | 2.2745 | 1
212 | Classroom | 597 | 39 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.8668 | 2
213 | Classroom | 664 | 44 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.413 | 2
214 | Classroom | 681 | 45 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.5516 | 2
215 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | 0 | 0
216 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | 0 | 0
- | Auditorium | 0 | 0 |  | 2880 | 65 | 0 | AHU | 23040 | 0 | 0
- | Cafeteria | 127 | 8 |  | 2250 | 51 | 8 | Unit Ventilator | 18000 | 0.42333 | 0
- | Kitchen |  | 0 | Yes | 475 | 10 | 10 |  | 3800 | 0 | 0
- | Main Office |  | 0 | Yes | 231 | 5 | 5 | Purifier | 1848 | 0 | 0
- | Principal Office |  | 0 | Yes | 150 | 3 | 3 |  | 1200 | 0 | 0
- | Vice Principal Office |  | 0 | Yes | 84 | 1 | 1 |  | 672 | 0 | 0
- | Nurse Office |  | 0 | Yes | 204 | 4 | 4 |  | 1632 | 0 | 0
- | Counselor Office |  | 0 | Yes | 135 | 3 | 3 |  | 1080 | 0 | 0
- | Admin Office |  | 0 | Yes | 156 | 3 | 3 |  | 1248 | 0 | 0
- | Dean Office |  | 0 | Yes | 140 | 3 | 3 |  | 1120 | 0 | 0
- | School Police Office |  | 0 | Yes | 99 | 2 | 2 |  | 792 | 0 | 0
- | Gym | 189 | 12 | Yes | 3950 | 89 | 89 | Unit Ventilator | 31600 | 0.35886 | 0
- | Music | 0 | 0 |  | 2340 | 53 | 0 | AHU | 18720 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Francis Hopkinson Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Main Building Retest | [6 empty] | 0 | 0 | 0
School: | Francis Hopkinson Elementary School- Little School House | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Main Building | [8 empty] | 0 | 0 | 0
101 | Classrooms | 1030 | 68 |  | 687 | 15 | 15 | House Fan | 5496 | 11.2445 | 3
102 | Classrooms | 873 | 58 |  | 627 | 14 | 14 | House Fan | 5016 | 10.4426 | 3
103 | Classrooms | 276 | 18 |  | 696 | 15 | 15 | House Fan | 5568 | 2.9741 | 1
104 | Classrooms | 1044 | 69 |  | 643 | 14 | 14 | House Fan | 5144 | 12.1773 | 3
105 | Classrooms | 562 | 37 |  | 638 | 14 | 14 | House Fan | 5104 | 6.6066 | 2
106 | Classroom | 953 | 63 |  | 648 | 14 | 14 | House Fan | 5184 | 11.0301 | 3
107 | Classroom | 1035 | 69 |  | 638 | 14 | 14 | House Fan | 5104 | 12.1669 | 3
108 | Classrooms | 432 | 28 |  | 675 | 15 | 15 | House Fan | 5400 | 4.8 | 2
109 | Classrooms | 635 | 42 |  | 631 | 14 | 14 | House Fan | 5048 | 7.5475 | 2
110 | Classroom | 322 | 21 |  | 695 | 15 | 15 | House Fan | 5560 | 3.4748 | 1
201 | Classrooms | 707 | 47 |  | 696 | 15 | 15 | House Fan | 5568 | 7.6185 | 2
202 | Classroom | 767 | 51 |  | 656 | 14 | 14 | House Fan | 5248 | 8.7691 | 2
203 | Classrooms | 734 | 48 |  | 693 | 15 | 15 | House Fan | 5544 | 7.9437 | 2
204 | Classrooms | 787 | 52 |  | 647 | 14 | 14 | House Fan | 5176 | 9.1229 | 2
205 | Classroom | 737 | 49 |  | 674 | 15 | 15 | House Fan | 5392 | 8.201 | 2
206 | Classroom | 792 | 52 |  | 657 | 14 | 14 | House Fan | 5256 | 9.0411 | 2
207 | Classrooms | 618 | 41 |  | 679 | 15 | 15 | House Fan | 5432 | 6.8262 | 2
208 | Classroom | 702 | 46 |  | 686 | 15 | 15 | House Fan | 5488 | 7.6749 | 2
209 | Classroom | 892 | 59 |  | 667 | 15 | 15 | House Fan | 5336 | 10.03 | 3
210 | Classroom | 386 | 25 |  | 687 | 15 | 15 | House Fan | 5496 | 4.214 | 2
300 | Office |  | 0 | Yes | 275 | 6 | 6 | House Fan | 2200 | 0 | 0
301 | Classrooms | 425 | 28 |  | 677 | 15 | 15 | House Fan | 5416 | 4.7083 | 2
302 | Classroom | 0 | 0 | Yes | 668 | 15 | 15 | House Fan | 5344 | 0 | 0
303 | Classrooms | 263 | 17 |  | 694 | 15 | 15 | House Fan | 5552 | 2.8422 | 1
304 | Classrooms | 612 | 40 |  | 614 | 13 | 13 | House Fan | 4912 | 7.4756 | 2
305 | Classroom | 437 | 29 |  | 672 | 15 | 15 | House Fan | 5376 | 4.8772 | 2
306 | Classroom | 497 | 33 |  | 696 | 15 | 15 | House Fan | 5568 | 5.3556 | 2
307 | Classrooms | 1017 | 67 |  | 661 | 15 | 15 | House Fan | 5288 | 11.5393 | 3
308 | Classroom | 604 | 40 |  | 664 | 15 | 15 | House Fan | 5312 | 6.8223 | 2
309 | Classroom | 702 | 46 |  | 673 | 15 | 15 | House Fan | 5384 | 7.8232 | 2
310 | Classroom | 321 | 21 |  | 668 | 15 | 15 | House Fan | 5344 | 3.604 | 1
311 | Classrooms | 393 | 26 |  | 638 | 14 | 14 | House Fan | 5104 | 4.6199 | 2
- | Auditorium | 1307 | 87 |  | 3184 | 72 | 72 | House Fan | 25472 | 3.0787 | 1
- | B Art Room | 242 | 16 |  | 570 | 12 | 12 | House Fan | 4560 | 3.1842 | 1
- | B Café / Gym | 0 | 0 | Yes | 3572 | 81 | 81 | N/A | 28576 | 0 | 0
- | B ESOL Room | 269 | 17 |  | 683 | 15 | 15 | House Fan | 5464 | 2.9539 | 1
- | B Music Room | 603 | 40 |  | 688 | 15 | 15 | House Fan | 5504 | 6.5734 | 2
- | B Science Room | 864 | 57 |  | 704 | 16 | 16 | House Fan | 5632 | 9.2045 | 2
- | Main Office |  | 0 | Yes | 345 | 7 | 7 |  | 2760 | 0 | 0
- | Vice Principal's Office |  | 0 | Yes | 126 | 2 | 2 |  | 1008 | 0 | 0
- | Nurse Office |  | 0 | Yes | 275 | 6 | 6 |  | 2200 | 0 | 0
P1 | Classroom | 198 | 13 | Yes | 1184 | 26 | 26 | Unit Ventilator | 9472 | 1.2542 | 1
P2 | Classroom | 348 | 23 |  | 747 | 16 | 16 | Unit Ventilator | 5976 | 3.494 | 1
Hopkinson LSH | [8 empty] | 0 | 0 | 0
1 | Room | 308 | 20 |  | 877 | 19 | 19 | AHU | 7016 | 2.634 | 1
2 | Room | 323 | 21 |  | 900 | 20 | 20 | AHU | 7200 | 2.6917 | 1
3 | Room | 318 | 21 |  | 885 | 20 | 20 | AHU | 7080 | 2.6949 | 1
4 | Room | 349 | 23 |  | 908 | 20 | 20 | AHU | 7264 | 2.8827 | 1
5 | Room | 308 | 20 |  | 863 | 19 | 19 | AHU | 6904 | 2.6767 | 1
6 | Room | 256 | 17 | Yes | 876 | 19 | 19 | AHU | 7008 | 2.1918 | 1
- | Corridor and Bathrooms | 46 | 3 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | Multi-Purpose Room | 626 | 41 |  | 2003 | 45 | 41 | AHU | 16024 | 2.344 | 1
- | Office Area | 204 | 13 |  | 352 | 8 | 8 | AHU | 2816 | 4.3466 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-01 | [7 empty] | 0 | 0 | 0
School: | Henry H. Houston Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom |  | 0 | Yes | 784 | 17 | 17 | House Fan | 6272 | 0 | 0
102 | Classroom |  | 0 | Yes | 651 | 14 | 14 | House Fan | 5208 | 0 | 0
103 | Classroom |  | 0 | Yes | 664 | 15 | 15 | House Fan | 5312 | 0 | 0
103A | Classroom |  | 0 |  | 157 | 3 | 0 | House Fan | 1256 | 0 | 0
104 | Classroom |  | 0 | Yes | 675 | 15 | 15 | House Fan | 5400 | 0 | 0
105 | Office/Principal |  | 0 |  | 354 | 8 | 0 | House Fan | 2832 | 0 | 0
106 | Classroom |  | 0 | Yes | 651 | 14 | 14 | House Fan | 5208 | 0 | 0
107 | Classroom |  | 0 | Yes | 459 | 10 | 10 | House Fan | 3672 | 0 | 0
108 | Classroom |  | 0 | Yes | 681 | 15 | 15 | House Fan | 5448 | 0 | 0
109 | Classroom |  | 0 | Yes | 950 | 21 | 21 | House Fan | 7600 | 0 | 0
111 | Classroom | 276 | 18 |  | 375 | 8 | 8 | House Fan and Univent | 3000 | 5.52 | 2
112 | Classroom | 350 | 23 |  | 312 | 7 | 7 | House Fan and Univent | 2496 | 8.4135 | 2
201 | Classroom |  | 0 |  | 561 | 12 | 0 | House Fan | 4488 | 0 | 0
202 | Classroom |  | 0 |  | 701 | 15 | 0 | House Fan | 5608 | 0 | 0
203 | Classroom |  | 0 |  | 207 | 4 | 0 | House Fan | 1656 | 0 | 0
204 | Classroom |  | 0 |  | 710 | 16 | 0 | House Fan | 5680 | 0 | 0
205 | Classroom |  | 0 |  | 653 | 14 | 0 | House Fan | 5224 | 0 | 0
206 | Classroom |  | 0 |  | 660 | 15 | 0 | House Fan | 5280 | 0 | 0
207 | Classroom |  | 0 |  | 769 | 17 | 0 | House Fan | 6152 | 0 | 0
208 | Classroom |  | 0 |  | 750 | 17 | 0 | House Fan | 6000 | 0 | 0
209 | Classroom |  | 0 |  | 693 | 15 | 0 | House Fan | 5544 | 0 | 0
210 | Classroom |  | 0 |  | 437 | 9 | 0 | N/A | 3496 | 0 | 0
211 | Classroom | 329 | 21 |  | 795 | 18 | 18 | Unit Ventilator | 6360 | 3.1038 | 1
212 | Classroom | 309 | 20 |  | 396 | 9 | 9 | Unit Ventilator | 3168 | 5.8523 | 2
213 | Classroom | 274 | 18 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
301 | Classroom |  | 0 |  | 667 | 15 | 0 | House Fan | 5336 | 0 | 0
302 | Classroom |  | 0 | Yes | 661 | 15 | 15 | House Fan | 5288 | 0 | 0
303 | Classroom |  | 0 |  | 664 | 15 | 0 | House Fan | 5312 | 0 | 0
304 | Classroom |  | 0 |  | 729 | 16 | 0 | House Fan | 5832 | 0 | 0
305 | Classroom |  | 0 |  | 674 | 15 | 0 | House Fan | 5392 | 0 | 0
306 | Classroom |  | 0 |  | 670 | 15 | 0 | House Fan | 5360 | 0 | 0
307 | Classroom |  | 0 |  | 758 | 17 | 0 | House Fan | 6064 | 0 | 0
308 | Classroom |  | 0 |  | 716 | 16 | 0 | House Fan | 5728 | 0 | 0
309 | Classroom |  | 0 |  | 613 | 13 | 0 | House Fan | 4904 | 0 | 0
309A | Small Office |  | 0 |  | 201 | 4 | 0 | House Fan | 1608 | 0 | 0
- | Kitchen | 0 | 0 |  | 638 | 14 | 0 | N/A | 5104 | 0 | 0
- | Auditorium | 1853 | 123 |  | 1500 | 34 | 34 | AHU 1 and 2 | 12000 | 9.265 | 2
- | Library | 0 | 0 |  | 1404 | 31 | 0 | RTU | 11232 | 0 | 0
- | Gym |  | 0 | Yes | 2232 | 50 | 50 | N/A | 17856 | 0 | 0
- | Old Art Room |  | 0 |  | 631 | 14 | 0 | N/A | 5048 | 0 | 0
- | Cafeteria | 0 | 0 |  | 4500 | 102 | 0 | Nesbitt Unit Ventilator | 36000 | 0 | 0
- | Old School Store A | 230 | 15 |  | 863 | 19 | 15 | Nesbitt Unit Ventilator | 6904 | 1.9988 | 1
- | Old School Store B | 345 | 23 |  | 311 | 7 | 7 | Nesbitt Unit Ventilator | 2488 | 8.3199 | 2
- | New School Store | 347 | 23 |  | 291 | 6 | 6 | Nesbitt Unit Ventilator | 2328 | 8.9433 | 2
- | Medical Suite Large |  | 0 |  | 242 | 5 |  |  | 1936 | 0 | 0
- | Medical Suite Small |  | 0 |  | 126 | 2 |  |  | 1008 | 0 | 0
- | Medical Suite Medium |  | 0 |  | 238 | 5 | 0 | House Fan | 1904 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21 | [7 empty] | 0 | 0 | 0
School: | Julia Ward Howe Academics Plus Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B-1 | Art | 751 | 50 |  | 754 | 17 | 17 | House Fan | 6032 | 7.4702 | 2
1 | Classroom | 1269 | 84 |  | 690 | 15 | 15 | House Fan | 5520 | 13.7935 | 3
2 | Classroom | 1240 | 82 |  | 690 | 15 | 15 | House Fan | 5520 | 13.4783 | 3
3 | Classroom | 344 | 22 |  | 690 | 15 | 15 | House Fan | 5520 | 3.7391 | 1
4 | Classroom | 455 | 30 |  | 690 | 15 | 15 | House Fan | 5520 | 4.9457 | 2
5 | Classroom | 1500 | 100 |  | 196 | 4 | 4 | House Fan | 1568 | 57.398 | 5
6 | Classroom | 479 | 31 |  | 713 | 16 | 16 | House Fan | 5704 | 5.0386 | 2
7 | Classroom | 1470 | 98 |  | 690 | 15 | 15 | House Fan | 5520 | 15.9783 | 3
8 | Classroom | 1454 | 96 |  | 690 | 15 | 15 | House Fan | 5520 | 15.8043 | 3
9 | Classroom | 564 | 37 |  | 720 | 16 | 16 | House Fan | 5760 | 5.875 | 2
10 | Classroom | 1739 | 115 |  | 690 | 15 | 15 | House Fan | 5520 | 18.9022 | 3
11 | Classroom | 628 | 41 |  | 690 | 15 | 15 | House Fan | 5520 | 6.8261 | 2
12 | Classroom | 829 | 55 |  | 720 | 16 | 16 | House Fan | 5760 | 8.6354 | 2
13 | Library | 0 | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0
14 | Classroom | 1302 | 86 |  | 690 | 15 | 15 | House Fan | 5520 | 14.1522 | 3
15 | Classroom | 1044 | 69 |  | 690 | 15 | 15 | House Fan | 5520 | 11.3478 | 3
16 | Computer Lab | 0 | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
17 | Classroom | 548 | 36 |  | 690 | 15 | 15 | House Fan | 5520 | 5.9565 | 2
18 | Classroom | 824 | 54 |  | 690 | 15 | 15 | House Fan | 5520 | 8.9565 | 2
19 | Classroom | 869 | 57 |  | 690 | 15 | 15 | House Fan | 5520 | 9.4457 | 2
20 | Classroom | 0 | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
21 | Classroom | 149 | 9 | Yes | 690 | 15 | 15 | House Fan | 5520 | 1.6196 | 1
22 | Classroom | 898 | 59 |  | 690 | 15 | 15 | House Fan | 5520 | 9.7609 | 2
23 | Classroom | 210 | 14 |  | 690 | 15 | 14 | House Fan | 5520 | 2.2826 | 1
23A | - |  | 0 | Yes | 91 | 2 | 2 | House Fan | 728 | 0 | 0
24 | Classroom | 0 | 0 |  | 350 | 7 | 0 | House Fan | 2800 | 0 | 0
- | Cafeteria | 0 | 0 | Yes | 1566 | 35 | 35 | House Fan | 12528 | 0 | 0
- | Gym |  | 0 | Yes | 1060 | 24 | 24 | House Fan | 8480 | 0 | 0
- | Jugg Room |  | 0 |  | 195 | 4 | 0 | House Fan | 1560 | 0 | 0
- | Main Office |  | 0 |  | 238 | 5 | 0 | House Fan | 1904 | 0 | 0
- | Principals Office |  | 0 | Yes | 180 | 4 | 4 | House Fan | 1440 | 0 | 0
- | Counselors Office |  | 0 |  | 162 | 3 | 0 | House Fan | 1296 | 0 | 0
- | Psychologists Office |  | 0 | Yes | 99 | 2 | 2 | House Fan | 792 | 0 | 0
- | Lounge |  | 0 |  | 266 | 6 | 0 | House Fan | 2128 | 0 | 0
- | Security |  | 0 | Yes | 91 | 2 | 2 | House Fan | 728 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-06 | [7 empty] | 0 | 0 | 0
School: | New William H. Hunter Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Retest | [6 empty] | 0 | 0 | 0
| Devine 2nd Retest | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Office | 40 | 2 |  | 149 | 3 | 2 | AHU-3 | 1192 | 2.0134 | 1
2 | Office | 33 | 2 |  | 143 | 3 | 2 | AHU-3 | 1144 | 1.7308 | 1
3 | Office | 24 | 1 |  | 72 | 1 | 1 | AHU-3 | 576 | 2.5 | 1
4 | Office | 48 | 3 |  | 92 | 2 | 2 | AHU-3 | 736 | 3.913 | 1
101A | Classroom | 363 | 24 |  | 695 | 15 | 15 | AHU-1 | 5560 | 3.9173 | 1
101B | Classroom | 378 | 25 |  | 695 | 15 | 15 | AHU-1 + UV | 5560 | 4.0791 | 2
101C | Classroom | 358 | 23 |  | 650 | 14 | 14 | AHU-1 | 5200 | 4.1308 | 2
101D | Classroom | 551 | 36 |  | 650 | 14 | 14 | AHU-1 + UV | 5200 | 6.3577 | 2
101E | Classroom | 351 | 23 |  | 610 | 13 | 13 | AHU-1 | 4880 | 4.3156 | 2
101F | Classroom | 393 | 26 |  | 650 | 14 | 14 | AHU-1 + UV | 5200 | 4.5346 | 2
102 | Classroom | 375 | 25 |  | 410 | 9 | 9 | AHU-1 and UV | 3280 | 6.8598 | 2
107 | Main Office Entry | 103 | 6 |  | 350 | 7 | 6 | AHU-3 | 2800 | 2.2071 | 1
107 | Main Office | 195 | 13 | Yes | 1125 | 25 | 25 | AHU-3 | 9000 | 1.3 | 1
108 | Classroom | 666 | 44 |  | 715 | 16 | 16 | AHU-5 + UV | 5720 | 6.986 | 2
109 | Classroom | 497 | 33 |  | 695 | 15 | 15 | AHU-5 + UV | 5560 | 5.3633 | 2
110 | Classroom | 477 | 31 |  | 695 | 15 | 15 | AHU-5 + UV | 5560 | 5.1475 | 2
111 | Classroom | 632 | 42 |  | 695 | 15 | 15 | AHU-5 + UV | 5560 | 6.8201 | 2
112 | Classroom | 496 | 33 |  | 695 | 15 | 15 | AHU-5 + UV | 5560 | 5.3525 | 2
113 | Music Room | 456 | 30 |  | 1430 | 32 | 30 | AHU-7 | 11440 | 2.3916 | 1
113 | Practice Rm 1 | 23 | 1 |  | 72 | 1 | 1 | AHU-7 | 576 | 2.3958 | 1
113 | Practice Rm 2 | 27 | 1 |  | 78 | 1 | 1 | AHU-7 | 624 | 2.5962 | 1
201 | IMC | 1373 | 91 |  | 2995 | 68 | 68 | AHU-10 + UV | 23960 | 3.4382 | 1
202 | Classroom | 467 | 31 |  | 1125 | 25 | 25 | Unit Ventilator and AHU | 9000 | 3.1133 | 1
202 | Media | 0 | 0 | Yes | 385 | 8 | 8 | Unit Ventilator and AHU | 3080 | 0 | 0
BAS 205 | IMC - Reading Small Classroom | 303 | 20 |  | 102 | 2 | 2 | Tightened damper Actuator to the shaft | 816 | 22.2794 | 3
BAS 206 | IMC - Reading Small Classroom | 317 | 21 |  | 859 | 19 | 19 | Tightened damper Actuator to the shaft | 6872 | 2.7678 | 1
206 | Classroom | 464 | 30 |  | 842 | 19 | 19 | AHU-1 + UV | 6736 | 4.133 | 2
207 | Classroom | 610 | 40 |  | 1325 | 30 | 30 | Unit Ventilator and AHU | 10600 | 3.4528 | 1
208 | Classroom | 318 | 21 | Yes | 1395 | 31 | 31 | Unit Ventilator and AHU | 11160 | 1.7097 | 1
208 | Computer Lab | 81 | 5 |  | 1210 | 27 | 5 |  | 9680 | 0.50207 | 0
209 | Classroom | 293 | 19 |  | 750 | 17 | 17 | AHU-1 + UV | 6000 | 2.93 | 1
210 | Classroom | 526 | 35 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 5.2321 | 2
211 | Classroom | 551 | 36 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 5.4808 | 2
212 | Classroom | 426 | 28 |  | 753 | 17 | 17 | Unit Ventilator and AHU | 6024 | 4.243 | 2
213 | Classroom | 497 | 33 |  | 753 | 17 | 17 | Unit Ventilator and AHU | 6024 | 4.9502 | 2
214 | Classroom | 478 | 31 |  | 724 | 16 | 16 | Unit Ventilator and AHU | 5792 | 4.9517 | 2
215 | Art Room | 367 | 24 | Yes | 1324 | 30 | 30 | AHU-12 | 10592 | 2.0789 | 1
304 | Classroom | 367 | 24 |  | 725 | 16 | 16 | Unit Ventilator and AHU | 5800 | 3.7966 | 1
305 | Classroom | 431 | 28 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 4.2871 | 2
306 | Classroom | 395 | 26 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 3.929 | 1
307 | Classroom | 315 | 21 |  | 753 | 17 | 17 | Unit Ventilator and AHU | 6024 | 3.1375 | 1
308 | Classroom | 350 | 23 |  | 753 | 17 | 17 | Unit Ventilator and AHU | 6024 | 3.4861 | 1
309 | Classroom | 340 | 22 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 3.382 | 1
310 | Classroom | 361 | 24 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 3.5908 | 1
311 | Classroom | 317 | 21 |  | 753 | 17 | 17 | Unit Ventilator and AHU | 6024 | 3.1574 | 1
312 | Classroom | 427 | 28 |  | 753 | 17 | 17 | Unit Ventilator and AHU | 6024 | 4.253 | 2
313 | Classroom | 387 | 25 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 3.8495 | 1
314 | Classroom | 411 | 27 |  | 715 | 16 | 16 | Unit Ventilator and AHU | 5720 | 4.3112 | 2
315 | Classroom | 363 | 24 |  | 810 | 18 | 18 | Unit Ventilator and AHU | 6480 | 3.3611 | 1
- | Auditorium | 2966 | 197 |  | 2910 | 66 | 66 | AHU-6 | 23280 | 7.6443 | 2
- | Cafeteria | 2006 | 133 |  | 3590 | 81 | 81 | AHU | 28720 | 4.1908 | 2
- | Kitchen | 35 | 2 | Yes | 1116 | 25 | 25 | AHU-3 | 8928 | 0.23522 | 0
- | Nurses Office | 98 | 6 |  | 105 | 2 | 2 | FC 5-1 | 840 | 7 | 2
- | Nurse Exam Room | 110 | 7 |  | 94 | 2 | 2 | FC 5-1 | 752 | 8.7766 | 2
- | Nurses Waiting Room | 108 | 7 |  | 130 | 2 | 2 | FC 5-1 | 1040 | 6.2308 | 2
- | Principal Office | 74 | 4 | Yes | 322 | 7 | 7 | AHU-3 | 2576 | 1.7236 | 1
- | Conference Room | 147 | 9 |  | 429 | 9 | 9 | AHU-3 | 3432 | 2.5699 | 1
- | Gym | 1430 | 95 |  | 4969 | 112 | 95 | AHU-8 + AHU-9 | 39752 | 2.1584 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-13 | [7 empty] | 0 | 0 | 0
School: | Andrew Jackson Elementary School | House fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B1 | Music Room | 324 | 21 |  | 1036 | 23 | 21 | AHU | 8288 | 2.3456 | 1
101 | Classroom | 536 | 35 |  | 1190 | 27 | 27 | AHU | 9520 | 3.3782 | 1
102 | Classroom | 436 | 29 |  | 638 | 14 | 14 | AHU | 5104 | 5.1254 | 2
103 | Classroom | 567 | 37 |  | 805 | 18 | 18 | AHU | 6440 | 5.2826 | 2
104 | Classroom | 363 | 24 |  | 840 | 19 | 19 | AHU | 6720 | 3.2411 | 1
105 | Classroom | 398 | 26 |  | 828 | 18 | 18 | AHU | 6624 | 3.6051 | 1
106 | Classroom | 740 | 49 |  | 748 | 17 | 17 | AHU | 5984 | 7.4198 | 2
107 | Classroom | 567 | 37 |  | 736 | 16 | 16 | AHU | 5888 | 5.7779 | 2
107B | - |  | 0 | Yes | 132 | 3 | 3 | N/A | 1056 | 0 | 0
107C | - |  | 0 | Yes | 220 | 5 | 5 | N/A | 1760 | 0 | 0
108 | Classroom | 396 | 26 |  | 841 | 19 | 19 | AHU | 6728 | 3.5315 | 1
109 | Classroom | 669 | 44 |  | 1218 | 27 | 27 | AHU | 9744 | 4.1195 | 2
110 | Classroom | 482 | 32 |  | 848 | 19 | 19 | AHU | 6784 | 4.263 | 2
201 | Classroom | 581 | 38 |  | 1225 | 27 | 27 | AHU | 9800 | 3.5571 | 1
202 | Classroom | 346 | 23 |  | 726 | 16 | 16 | AHU | 5808 | 3.5744 | 1
203 | Classroom | 384 | 25 |  | 864 | 19 | 19 | AHU | 6912 | 3.3333 | 1
204 | Classroom | 453 | 30 |  | 850 | 19 | 19 | AHU | 6800 | 3.9971 | 1
204A | Office | 0 | 0 | Yes | 468 | 10 | 10 |  | 3744 | 0 | 0
205 | Classroom | 304 | 20 |  | 840 | 19 | 19 | AHU | 6720 | 2.7143 | 1
206 | Classroom | 531 | 35 |  | 864 | 19 | 19 | AHU | 6912 | 4.6094 | 2
207 | Classroom | 614 | 40 |  | 805 | 18 | 18 | AHU | 6440 | 5.7205 | 2
208 | Classroom | 367 | 24 |  | 850 | 19 | 19 | AHU | 6800 | 3.2382 | 1
209/210 | Classroom | 1387 | 92 |  | 1680 | 38 | 38 | AHU | 13440 | 6.192 | 2
211 | Classroom | 490 | 32 |  | 840 | 19 | 19 | AHU | 6720 | 4.375 | 2
301 | Classroom | 530 | 35 |  | 980 | 22 | 22 | AHU | 7840 | 4.0561 | 2
302 | Classroom | 303 | 20 |  | 816 | 18 | 18 | AHU | 6528 | 2.7849 | 1
303 | Classroom | 88 | 5 | Yes | 828 | 18 | 18 |  | 6624 | 0.7971 | 0
304 | Classroom | 427 | 28 |  | 805 | 18 | 18 | AHU | 6440 | 3.9783 | 1
304A | Office | 0 | 0 | Yes | 442 | 10 | 10 |  | 3536 | 0 | 0
305 | Classroom | 619 | 41 |  | 840 | 19 | 19 | AHU | 6720 | 5.5268 | 2
306 | Classroom | 528 | 35 |  | 840 | 19 | 19 | AHU | 6720 | 4.7143 | 2
307 | Classroom | 375 | 25 |  | 782 | 17 | 17 | AHU | 6256 | 3.5965 | 1
308 | Classroom | 417 | 27 |  | 816 | 18 | 18 | AHU | 6528 | 3.8327 | 1
- | Gym/Cafeteria | 2408 | 160 |  | 3005 | 68 | 68 | AHU | 24040 | 6.01 | 2
- | Library | 740 | 49 |  | 2320 | 52 | 49 | AHU | 18560 | 2.3922 | 1
- | I.M.C. Office | 160 | 10 |  | 400 | 9 | 9 | AHU | 3200 | 3 | 1
- | Main Office | 0 | 0 | Yes | 484 | 11 | 11 |  | 3872 | 0 | 0
- | Princpal's Office |  | 0 | Yes | 308 | 7 | 7 | N/A | 2464 | 0 | 0
- | Nurse's Office |  | 0 | Yes | 264 | 6 | 6 | N/A | 2112 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | James Martin- Alternative Middle Years (Middle School) | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 0 | 0 | Yes | 696 | 15 | 15 |  | 5568 | 0 | 0
106 | Classroom | 280 | 18 |  | 720 | 16 | 16 |  | 5760 | 2.9167 | 1
107 | Classroom | 313 | 20 |  | 720 | 16 | 16 |  | 5760 | 3.2604 | 1
108 | Classroom | 0 | 0 | Yes | 696 | 15 | 15 |  | 5568 | 0 | 0
109 | Classroom | 0 | 0 | Yes | 672 | 15 | 15 |  | 5376 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 |  | 5760 | 0 | 0
202 | Classroom | 0 | 0 | Yes | 750 | 17 | 17 |  | 6000 | 0 | 0
203 | Classroom | 306 | 20 |  | 750 | 17 | 17 |  | 6000 | 3.06 | 1
204 | Lounge | 371 | 24 |  | 480 | 10 | 10 |  | 3840 | 5.7969 | 2
205 | Classroom | 345 | 23 |  | 912 | 20 | 20 |  | 7296 | 2.8372 | 1
206 | School Store | 291 | 19 |  | 384 | 8 | 8 |  | 3072 | 5.6836 | 2
207 | Classroom | 309 | 20 |  | 750 | 17 | 17 |  | 6000 | 3.09 | 1
208 | Classroom | 331 | 22 |  | 720 | 16 | 16 |  | 5760 | 3.4479 | 1
209 | Classroom | 303 | 20 |  | 667 | 15 | 15 |  | 5336 | 3.407 | 1
210 | Classroom | 292 | 19 |  | 667 | 15 | 15 |  | 5336 | 3.2834 | 1
211 | Classroom | 0 | 0 | Yes | 672 | 15 | 15 |  | 5376 | 0 | 0
214 | Security Office | 0 | 0 | Yes | 256 | 5 | 5 |  | 2048 | 0 | 0
301 | Classroom | 0 | 0 | Yes | 696 | 15 | 15 |  | 5568 | 0 | 0
302 | Classroom | 0 | 0 | Yes | 696 | 15 | 15 |  | 5568 | 0 | 0
303 | Classroom | 301 | 20 |  | 720 | 16 | 16 |  | 5760 | 3.1354 | 1
304 | Classroom | 275 | 18 |  | 720 | 16 | 16 |  | 5760 | 2.8646 | 1
305 | Classroom | 297 | 19 |  | 696 | 15 | 15 |  | 5568 | 3.2004 | 1
306 | Classroom | 284 | 18 |  | 720 | 16 | 16 |  | 5760 | 2.9583 | 1
307 | Classroom | 297 | 19 |  | 768 | 17 | 17 |  | 6144 | 2.9004 | 1
308 | Classroom | 317 | 21 |  | 696 | 15 | 15 |  | 5568 | 3.4159 | 1
309 | Classroom | 272 | 18 |  | 696 | 15 | 15 |  | 5568 | 2.931 | 1
310 | Classroom | 293 | 19 |  | 720 | 16 | 16 |  | 5760 | 3.0521 | 1
311 | Art Room | 0 | 0 | Yes | 928 | 21 | 21 |  | 7424 | 0 | 0
314 | Office | 0 | 0 | Yes | 256 | 5 | 5 |  | 2048 | 0 | 0
- | Boys Cafeteria | 0 | 0 | Yes | 851 | 19 | 19 |  | 6808 | 0 | 0
- | Counselors Office | 0 | 0 | Yes | 160 | 3 | 3 |  | 1280 | 0 | 0
- | Girls Cafeteria | 0 | 0 | Yes | 1728 | 39 | 39 |  | 13824 | 0 | 0
- | Gym | 0 | 0 |  | 1760 | 40 | 0 |  | 14080 | 0 | 0
- | IMC-A | 270 | 18 |  | 720 | 16 | 16 |  | 5760 | 2.8125 | 1
- | IMC-B | 292 | 19 |  | 720 | 16 | 16 |  | 5760 | 3.0417 | 1
- | IMC-C | 283 | 18 |  | 720 | 16 | 16 |  | 5760 | 2.9479 | 1
- | Main Office | 0 | 0 | Yes | 360 | 8 | 8 |  | 2880 | 0 | 0
- | Nurses Office | 0 | 0 | Yes | 256 | 5 | 5 |  | 2048 | 0 | 0
- | Teachers Lounge | 0 | 0 |  | 480 | 10 | 0 |  | 3840 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | Abraham S. Jenks Elementary School | House fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
14 | Classroom | 422 | 28 |  | 638 | 14 | 14 | House Fan | 5104 | 4.9608 | 2
15 | Cafeteria | 221 | 14 |  | 638 | 14 | 14 | House Fan | 5104 | 2.598 | 1
101 | Classroom | 459 | 30 |  | 660 | 15 | 15 | House Fan | 5280 | 5.2159 | 2
102 | Classroom | 1235 | 82 |  | 660 | 15 | 15 | House Fan | 5280 | 14.0341 | 3
103 | Classroom | 1253 | 83 |  | 660 | 15 | 15 | House Fan | 5280 | 14.2386 | 3
104 | Classroom | 919 | 61 |  | 660 | 15 | 15 | House Fan | 5280 | 10.4432 | 3
105 | Classroom | 632 | 42 |  | 660 | 15 | 15 | House Fan | 5280 | 7.1818 | 2
106 | Classroom | 748 | 49 |  | 660 | 15 | 15 | House Fan | 5280 | 8.5 | 2
201 | Classroom | 1277 | 85 |  | 690 | 15 | 15 | House Fan | 5520 | 13.8804 | 3
202 | Classroom | 522 | 34 |  | 690 | 15 | 15 | House Fan | 5520 | 5.6739 | 2
203 | Classroom | 1094 | 72 |  | 690 | 15 | 15 | House Fan | 5520 | 11.8913 | 3
204 | Classroom | 803 | 53 |  | 690 | 15 | 15 | House Fan | 5520 | 8.7283 | 2
205 | Classroom | 749 | 49 |  | 690 | 15 | 15 | House Fan | 5520 | 8.1413 | 2
206 | Classroom | 1198 | 79 |  | 690 | 15 | 15 | House Fan | 5520 | 13.0217 | 3
207 | Classroom | 1279 | 85 |  | 744 | 16 | 16 | House Fan | 5952 | 12.8931 | 3
- | Principals Office |  | 0 | Yes | 165 | 3 | 3 |  | 1320 | 0 | 0
- | Main Office |  | 0 | Yes | 195 | 4 | 4 |  | 1560 | 0 | 0
- | Teacher Lounge |  | 0 |  | 165 | 3 | 0 |  | 1320 | 0 | 0
- | Nurses Office |  | 0 | Yes | 190 | 4 | 4 |  | 1520 | 0 | 0
- | Library | 176 | 11 |  | 638 | 14 | 11 | House Fan | 5104 | 2.069 | 1
- | Auditorium | 217 | 14 |  | 1540 | 35 | 14 | UV | 12320 | 1.0568 | 1
- | Cafeteria | 362 | 24 |  | 638 | 14 | 14 | House Fan | 5104 | 4.2555 | 2
- | North Trailer Classroom | 227 | 15 |  | N/A | 0 | 0 | N/A used for storage | #VALUE! | #VALUE! | #VALUE!
- | South Trailer Classroom | 261 | 17 |  | 638 | 14 | 14 | AHU | 5104 | 3.0682 | 1
- | Gym |  | 0 | Yes | 1700 | 38 | 38 | N/A | 13600 | 0 | 0
Sheet Last Modified: | 2021-04-28 | [7 empty] | 0 | 0 | 0
School: | John S. Jenks Elementary-Middle School | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
322 | Classroom |  | 0 | Yes | 658 | 14 | 14 | House Fan | 5264 | 0 | 0
321 | Classroom |  | 0 | Yes | 692 | 15 | 15 | House Fan | 5536 | 0 | 0
320 | Classroom |  | 0 | Yes | 685 | 15 | 15 | House Fan | 5480 | 0 | 0
319B | - |  | 0 | Yes | 658 | 14 | 14 | House Fan | 5264 | 0 | 0
319A | - |  | 0 | Yes | 305 | 6 | 6 | House Fan | 2440 | 0 | 0
318 | Classroom |  | 0 | Yes | 654 | 14 | 14 | House Fan | 5232 | 0 | 0
317 | Classroom |  | 0 | Yes | 674 | 15 | 15 | House Fan | 5392 | 0 | 0
316 | Classroom |  | 0 | Yes | 693 | 15 | 15 | House Fan | 5544 | 0 | 0
315 | Classroom |  | 0 | Yes | 654 | 14 | 14 | House Fan | 5232 | 0 | 0
214 | Classroom |  | 0 | Yes | 671 | 15 | 15 | House Fan | 5368 | 0 | 0
213 | Classroom |  | 0 | Yes | 689 | 15 | 15 | House Fan | 5512 | 0 | 0
212 | Classroom |  | 0 | Yes | 683 | 15 | 15 | House Fan | 5464 | 0 | 0
211 | Classroom |  | 0 | Yes | 673 | 15 | 15 | House Fan | 5384 | 0 | 0
210 | Classroom |  | 0 | Yes | 671 | 15 | 15 | House Fan | 5368 | 0 | 0
209 | Classroom |  | 0 | Yes | 680 | 15 | 15 | House Fan | 5440 | 0 | 0
208 | Classroom |  | 0 | Yes | 695 | 15 | 15 | House Fan | 5560 | 0 | 0
207 | Classroom |  | 0 | Yes | 636 | 14 | 14 | House Fan | 5088 | 0 | 0
110 | - |  | 0 | Yes | 336 | 7 | 7 | House Fan | 2688 | 0 | 0
109 | - |  | 0 | Yes | 156 | 3 | 3 | house Fan | 1248 | 0 | 0
106 | IMC |  | 0 | Yes | 671 | 15 | 15 | House Fan | 5368 | 0 | 0
105 | Classroom |  | 0 | Yes | 640 | 14 | 14 | House Fan | 5120 | 0 | 0
104 | Classroom |  | 0 | Yes | 627 | 14 | 14 | House Fan | 5016 | 0 | 0
103 | Classroom |  | 0 | Yes | 666 | 15 | 15 | House Fan | 5328 | 0 | 0
102 | Classroom |  | 0 | Yes | 668 | 15 | 15 | House Fan | 5344 | 0 | 0
101 | Classroom |  | 0 | Yes | 602 | 13 | 13 | House Fan | 4816 | 0 | 0
100 | Classroom |  | 0 | Yes | 1053 | 23 | 23 | House Fan | 8424 | 0 | 0
- | Kindergarten Classroom |  | 0 | Yes | 1512 | 34 | 34 | House Fan | 12096 | 0 | 0
- | Gym |  | 0 | Yes | 4500 | 102 | 102 |  | 36000 | 0 | 0
- | Main Office |  | 0 | Yes | 385 | 8 | 8 |  | 3080 | 0 | 0
- | Principal Office |  | 0 | Yes | 112 | 2 | 2 |  | 896 | 0 | 0
- | Library |  | 0 | Yes | 616 | 13 | 13 |  | 4928 | 0 | 0
- | Teachers Lounge |  | 0 | Yes | 402 | 9 | 9 |  | 3216 | 0 | 0
- | Spo |  | 0 | Yes | 180 | 4 | 4 |  | 1440 | 0 | 0
- | Counselor Office |  | 0 | Yes | 165 | 3 | 3 |  | 1320 | 0 | 0
- | Nurse Office |  | 0 | Yes | 263 | 5 | 5 |  | 2104 | 0 | 0
- | Speech Room |  | 0 | Yes | 103 | 2 | 2 |  | 824 | 0 | 0
- | Auditorium |  | 0 |  | 3463 | 78 | 0 |  | 27704 | 0 | 0
- | Copy Room |  | 0 |  | 166 | 3 | 0 |  | 1328 | 0 | 0
- | Art Room |  | 0 | Yes | 1085 | 24 | 24 |  | 8680 | 0 | 0
- | Lego Room |  | 0 | Yes | 165 | 3 | 3 |  | 1320 | 0 | 0
- | Kitchen |  | 0 | Yes | 578 | 13 | 13 |  | 4624 | 0 | 0
- | Gym Office |  | 0 |  | 588 | 13 | 0 |  | 4704 | 0 | 0
- | Home & school |  | 0 |  | 364 | 8 | 0 |  | 2912 | 0 | 0
- | Boys Room |  | 0 |  | 144 | 3 | 0 |  | 1152 | 0 | 0
- | Girls Room |  | 0 |  | 144 | 3 | 0 |  | 1152 | 0 | 0
- | Boys room by gym |  | 0 |  | 614 | 13 | 0 |  | 4912 | 0 | 0
- | Girls room by gym |  | 0 |  | 614 | 13 | 0 |  | 4912 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-06 | [7 empty] | 0 | 0 | 0
School: | Juniata Park Academy Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Classroom | 1020 | 68 |  | 1100 | 25 | 25 | RTU/UV | 8800 | 6.9545 | 2
2 | Classroom | 897 | 59 |  | 1108 | 25 | 25 | RTU/UV | 8864 | 6.0718 | 2
3 | Classroom | 1328 | 88 |  | 1108 | 25 | 25 | RTU/UV | 8864 | 8.9892 | 2
4 | Classroom | 1321 | 88 |  | 1093 | 24 | 24 | RTU/UV | 8744 | 9.0645 | 2
5 | Classroom | 975 | 65 |  | 1123 | 25 | 25 | RTU/UV | 8984 | 6.5116 | 2
6 | Classroom | 874 | 58 |  | 1125 | 25 | 25 | RTU/UV | 9000 | 5.8267 | 2
100 | Classroom | 750 | 50 |  | 660 | 15 | 15 | RTU/UV | 5280 | 8.5227 | 2
101 | Classroom | 969 | 64 |  | 660 | 15 | 15 | RTU/UV | 5280 | 11.0114 | 3
102 | Classroom | 836 | 55 |  | 952 | 21 | 21 | RTU/UV | 7616 | 6.5861 | 2
103 | Classroom | 1212 | 80 |  | 792 | 18 | 18 | RTU/UV | 6336 | 11.4773 | 3
104 | Classroom | 1119 | 74 |  | 792 | 18 | 18 | RTU/UV | 6336 | 10.5966 | 3
105 | Classroom | 2327 | 155 |  | 794 | 18 | 18 | RTU/UV | 6352 | 21.9805 | 3
106 | Classroom | 1053 | 70 |  | 794 | 18 | 18 | RTU/UV | 6352 | 9.9465 | 2
107 | Classroom | 789 | 52 |  | 794 | 18 | 18 | RTU/UV | 6352 | 7.4528 | 2
108 | Classroom | 952 | 63 |  | 794 | 18 | 18 | RTU/UV | 6352 | 8.9924 | 2
109 | Classroom | 910 | 60 |  | 794 | 18 | 18 | RTU/UV | 6352 | 8.5957 | 2
110 | Classroom | 817 | 54 |  | 794 | 18 | 18 | RTU/UV | 6352 | 7.7173 | 2
111 | Classroom | 1240 | 82 |  | 794 | 18 | 18 | RTU/UV | 6352 | 11.7128 | 3
112 | Classroom | 1129 | 75 |  | 794 | 18 | 18 | RTU/UV | 6352 | 10.6644 | 3
113 | Classroom | 967 | 64 |  | 794 | 18 | 18 | RTU/UV | 6352 | 9.1341 | 2
114 | Classroom | 906 | 60 |  | 794 | 18 | 18 | RTU/UV | 6352 | 8.5579 | 2
115 | Classroom | 1064 | 70 |  | 792 | 18 | 18 | RTU/UV | 6336 | 10.0758 | 3
117 | Girls' Toilet Room | 115 | 7 |  | 140 | 3 | 3 | RTU/UV | 1120 | 6.1607 | 2
116 | Classroom | 853 | 56 |  | 792 | 18 | 18 | RTU/UV | 6336 | 8.0777 | 2
117 | Classroom | 636 | 42 |  | 672 | 15 | 15 | RTU/UV | 5376 | 7.0982 | 2
120 | Boys' Toilet Room | 120 | 8 |  | 200 | 4 | 4 | RTU/UV | 1600 | 4.5 | 2
200 | Classroom | 661 | 44 |  | 609 | 13 | 13 | RTU/UV | 4872 | 8.1404 | 2
201 | Classroom | 638 | 42 |  | 772 | 17 | 17 | RTU/UV | 6176 | 6.1982 | 2
202 | Classroom | 449 | 29 |  | 721 | 16 | 16 | RTU/UV | 5768 | 4.6706 | 2
203 | Classroom | 691 | 46 |  | 673 | 15 | 15 | RTU/UV | 5384 | 7.7006 | 2
204 | Classroom | 534 | 35 |  | 794 | 18 | 18 | RTU/UV | 6352 | 5.0441 | 2
205 | Classroom | 627 | 41 |  | 794 | 18 | 18 | RTU/UV | 6352 | 5.9225 | 2
205 | Girls' Toilet Room | 22 | 1 |  | 182 | 4 | 1 | RTU/UV | 1456 | 0.90659 | 0
206 | Classroom | 530 | 35 |  | 794 | 18 | 18 | RTU/UV | 6352 | 5.0063 | 2
207 | Classroom | 539 | 35 |  | 794 | 18 | 18 | RTU/UV | 6352 | 5.0913 | 2
208 | Classroom | 665 | 44 |  | 794 | 18 | 18 | RTU/UV | 6352 | 6.2815 | 2
208 | Boys' Toilet Room | 24 | 1 |  | 195 | 4 | 1 | RTU/UV | 1560 | 0.92308 | 0
209 | Classroom | 509 | 33 |  | 794 | 18 | 18 | RTU/UV | 6352 | 4.8079 | 2
210 | Classroom | 310 | 20 |  | 794 | 18 | 18 | RTU/UV | 6352 | 2.9282 | 1
211 | Classroom | 418 | 27 |  | 794 | 18 | 18 | RTU/UV | 6352 | 3.9484 | 1
212 | Classroom | 487 | 32 |  | 794 | 18 | 18 | RTU/UV | 6352 | 4.6001 | 2
213 | Classroom | 539 | 35 |  | 794 | 18 | 18 | RTU/UV | 6352 | 5.0913 | 2
215 | Classroom | 538 | 35 |  | 794 | 18 | 18 | RTU/UV | 6352 | 5.0819 | 2
217 | Classroom | 683 | 45 |  | 793 | 18 | 18 | RTU/UV | 6344 | 6.4596 | 2
229 | Girls' Toilet Room | 330 | 22 |  | 195 | 4 | 4 | RTU/UV | 1560 | 12.6923 | 3
235 | Boys' Toilet Room | 140 | 9 |  | 200 | 4 | 4 | RTU/UV | 1600 | 5.25 | 2
- | Main Office | 740 | 49 |  | 500 | 11 | 11 | RTU/UV | 4000 | 11.1 | 3
- | Confrence Room | 475 | 31 |  | 203 | 4 | 4 | RTU/UV | 1624 | 17.5493 | 3
- | Main Office 4 | 255 | 17 |  | 153 | 3 | 3 | RTU/UV | 1224 | 12.5 | 3
- | Main Office 3 | 255 | 17 |  | 120 | 2 | 2 | RTU/UV | 960 | 15.9375 | 3
- | Main Office 2 | 260 | 17 |  | 120 | 2 | 2 | RTU/UV | 960 | 16.25 | 3
- | Main Office 1 | 310 | 20 |  | 162 | 3 | 3 | RTU/UV | 1296 | 14.3519 | 3
- | Main Office Work Room | 245 | 16 |  | 165 | 3 | 3 | RTU/UV | 1320 | 11.1364 | 3
- | Principals Office | 365 | 24 |  | 201 | 4 | 4 | RTU/UV | 1608 | 13.6194 | 3
- | Principal Bathroom | 52 | 3 |  | 77 | 1 | 1 | RTU/UV | 616 | 5.0649 | 2
- | IMC Workroom | 79 | 5 |  | 347 | 7 | 5 | RTU/UV | 2776 | 1.7075 | 1
- | IMC Conference Rm | 128 | 8 |  | 360 | 8 | 8 | RTU/UV | 2880 | 2.6667 | 1
- | IMC Reference | 62 | 4 |  | 260 | 5 | 4 | RTU/UV | 2080 | 1.7885 | 1
- | IMC Main Area North | 320 | 21 |  | 1432 | 32 | 21 | RTU/UV | 11456 | 1.676 | 1
- | IMC Main Area South | 217 | 14 |  | 1432 | 32 | 14 | RTU/UV | 11456 | 1.1365 | 1
- | Library | 710 | 47 |  | 2864 | 65 | 47 | RTU/UV | 22912 | 1.8593 | 1
- | Art Room | 701 | 46 |  | 1202 | 27 | 27 | RTU/UV | 9616 | 4.374 | 2
- | Music Classroom | 738 | 49 |  | 1248 | 28 | 28 | RTU/UV | 9984 | 4.4351 | 2
- | Cafeteria | 9535 | 635 |  | 4250 | 96 | 96 | RTU/UV | 34000 | 16.8265 | 3
- | Food Service | 135 | 9 | Yes | 1600 | 36 | 36 | RTU/UV | 12800 | 0.63281 | 0
- | Computer Lab | 1062 | 70 |  | 1000 | 22 | 22 | RTU/UV | 8000 | 7.965 | 2
- | Science Lab | 1041 | 69 |  | 1436 | 32 | 32 | RTU/UV | 11488 | 5.437 | 2
- | Tech Ed | 1222 | 81 |  | 1415 | 32 | 32 | RTU/UV | 11320 | 6.477 | 2
- | Health Suite | 575 | 38 |  | 250 | 5 | 5 | RTU/UV | 2000 | 17.25 | 3
- | Conference Rm | 37 | 2 |  | 99 | 2 | 2 | RTU/UV | 792 | 2.803 | 1
- | Corridor | 405 | 27 |  |  | 0 | 0 | RTU/UV | 0 | 0 | 0
- | Lounge | 220 | 14 |  | 418 | 9 | 9 | RTU/UV | 3344 | 3.9474 | 1
- | Refrence Rm | 165 | 11 |  | 120 | 2 | 2 | RTU/UV | 960 | 10.3125 | 3
- | Boys' Toilet Room | 327 | 21 |  | 200 | 4 | 4 | RTU/UV | 1600 | 12.2625 | 3
- | Girls' Toilet Room | 227 | 15 |  | 140 | 3 | 3 | RTU/UV | 1120 | 12.1607 | 3
- | Storage | 190 | 12 |  | 156 | 3 | 3 | RTU/UV | 1248 | 9.1346 | 2
- | Trash Rm | 160 | 10 |  | 213 | 4 | 4 | RTU/UV | 1704 | 5.6338 | 2
- | Work Room | 160 | 10 |  | 152 | 3 | 3 | RTU/UV | 1216 | 7.8947 | 2
- | Workshop | 210 | 14 |  | 153 | 3 | 3 | RTU/UV | 1224 | 10.2941 | 3
- | Bldg Engineer | 160 | 10 |  | 150 | 3 | 3 | RTU/UV | 1200 | 8 | 2
- | Gym |  | 0 |  | 6809 | 154 | 0 | AHU | 54472 | 0 | 0
Sheet Last Modified: | 2021-04-13 | [7 empty] | 0 | 0 | 0
School: | General Philip Kearny Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Exhaust Report | Retest | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Classroom | 0 | 0 |  | 780 | 17 | 0 | UV | 6240 | 0 | 0
2 | classroom | 900 | 60 |  | 780 | 17 | 17 | UV | 6240 | 8.6538 | 2
3 | classroom | 1129 | 75 |  | 780 | 17 | 17 | UV | 6240 | 10.8558 | 3
4 | classroom | 1177 | 78 |  | 780 | 17 | 17 | UV | 6240 | 11.3173 | 3
100 | classroom | 1118 | 74 |  | 750 | 17 | 17 | House Fan | 6000 | 11.18 | 3
101 | classroom | 1353 | 90 |  | 700 | 15 | 15 | House Fan | 5600 | 14.4964 | 3
103 | classroom | 1342 | 89 |  | 945 | 21 | 21 | House Fan | 7560 | 10.6508 | 3
105 | classroom | 1642 | 109 |  | 696 | 15 | 15 | House Fan | 5568 | 17.694 | 3
107 | classroom | 314 | 20 |  | 744 | 16 | 16 | House Fan | 5952 | 3.1653 | 1
200 | classroom | 1129 | 75 |  | 696 | 15 | 15 | House Fan | 5568 | 12.1659 | 3
201 | classroom | 1048 | 69 |  | 696 | 15 | 15 | House Fan | 5568 | 11.2931 | 3
202 | classroom | 1034 | 68 |  | 783 | 17 | 17 | House Fan | 6264 | 9.9042 | 2
203 | classroom | 1345 | 89 |  | 810 | 18 | 18 | House Fan | 6480 | 12.4537 | 3
204 | classroom | 1224 | 81 |  | 324 | 7 | 7 | House Fan | 2592 | 28.3333 | 4
207 | classroom | 1653 | 110 |  | 768 | 17 | 17 | House Fan | 6144 | 16.1426 | 3
300 | classroom | 1129 | 75 |  | 672 | 15 | 15 | House Fan | 5376 | 12.6004 | 3
301 | classroom | 990 | 66 |  | 725 | 16 | 16 | House Fan | 5800 | 10.2414 | 3
302 | classroom | 623 | 41 |  | 783 | 17 | 17 | House Fan | 6264 | 5.9674 | 2
303 | classroom | 986 | 65 |  | 810 | 18 | 18 | House Fan | 6480 | 9.1296 | 2
305 | classroom | 1268 | 84 |  | 720 | 16 | 16 | House Fan | 5760 | 13.2083 | 3
306 | classroom | 1338 | 89 |  | 414 | 9 | 9 | House Fan | 3312 | 24.2391 | 4
307 | classroom | 1067 | 71 |  | 768 | 17 | 17 | House Fan | 6144 | 10.4199 | 3
308 | classroom | 931 | 62 |  | 675 | 15 | 15 | House Fan | 5400 | 10.3444 | 3
309 | classroom | 1059 | 70 |  | 675 | 15 | 15 | House Fan | 5400 | 11.7667 | 3
310 | classroom | 1114 | 74 |  | 675 | 15 | 15 | House Fan | 5400 | 12.3778 | 3
311 | classroom | 1191 | 79 |  | 675 | 15 | 15 | House Fan | 5400 | 13.2333 | 3
312 | classroom | 924 | 61 |  | 414 | 9 | 9 | House Fan | 3312 | 16.7391 | 3
312 | classroom | 1529 | 101 |  | 414 | 9 | 9 | House Fan | 3312 | 27.6993 | 4
315 | classroom | 1386 | 92 |  | 702 | 15 | 15 | House Fan | 5616 | 14.8077 | 3
- | Gym | 9069 | 604 |  | 6100 | 138 | 138 | RTU | 48800 | 11.1504 | 3
- | Main office |  | 0 | Yes | 340 | 7 | 7 | House Fan | 2720 | 0 | 0
- | Principal office |  | 0 | Yes | 320 | 7 | 7 | House Fan | 2560 | 0 | 0
| Cafeteria |  | 0 | Yes | 3240 | 73 | 73 |  | 25920 | 0 | 0
- | Auditorium |  | 0 |  | 3240 | 73 | 0 | House Fan | 25920 | 0 | 0
- | Faculty |  | 0 |  | 336 | 7 | 0 |  | 2688 | 0 | 0
- | Kitchen |  | 0 |  | 700 | 15 | 0 | House Fan | 5600 | 0 | 0
- | Nurse |  | 0 | Yes | 171 | 3 | 3 | House Fan | 1368 | 0 | 0
- | Lunchroom |  | 0 | Yes | 3078 | 69 | 69 | House Fan | 24624 | 0 | 0
Sheet Last Modified: | 2021-04-22 | [7 empty] | 0 | 0 | 0
School: | William D. Kelley Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Part 2 | [6 empty] | 0 | 0 | 0
| Devine Part 3 | Devine Part 4 | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 315 | 21 |  | 1053 | 23 | 21 | UV | 8424 | 2.2436 | 1
102 | Classroom | 322 | 21 |  | 880 | 20 | 20 | UV | 7040 | 2.7443 | 1
103 | Classroom | 319 | 21 |  | 735 | 16 | 16 | UV | 5880 | 3.2551 | 1
104 | Classroom | 318 | 21 |  | 805 | 18 | 18 | UV | 6440 | 2.9627 | 1
104B | Classroom | 301 | 20 |  | 870 | 19 | 19 | UV | 6960 | 2.5948 | 1
105 | Classroom | 357 | 23 |  | 735 | 16 | 16 | UV | 5880 | 3.6429 | 1
106 | Classroom | 395 | 26 |  | 735 | 16 | 16 | UV | 5880 | 4.0306 | 2
108 | Classroom | 376 | 25 |  | 735 | 16 | 16 | UV | 5880 | 3.8367 | 1
109 | Classroom | 302 | 20 |  | 735 | 16 | 16 | UV | 5880 | 3.0816 | 1
110 | Classroom | 321 | 21 |  | 442 | 10 | 10 | UV | 3536 | 5.4468 | 2
111 | Classroom | 339 | 22 |  | 735 | 16 | 16 | UV | 5880 | 3.4592 | 1
200 | Classroom | 357 | 23 |  | 700 | 15 | 15 | UV | 5600 | 3.825 | 1
201 | Classroom | 302 | 20 |  | 720 | 16 | 16 | UV | 5760 | 3.1458 | 1
202 | Classroom | 330 | 22 |  | 770 | 17 | 17 | UV | 6160 | 3.2143 | 1
203 | Classroom | 314 | 20 |  | 735 | 16 | 16 | UV | 5880 | 3.2041 | 1
204 | Classroom | 355 | 23 |  | 735 | 16 | 16 | UV | 5880 | 3.6224 | 1
205 | Classroom | 344 | 22 |  | 735 | 16 | 16 | UV | 5880 | 3.5102 | 1
206 | Classroom | 284 | 18 |  | 406 | 9 | 9 | UV | 3248 | 5.2463 | 2
207 | Classroom | 332 | 22 |  | 735 | 16 | 16 | UV | 5880 | 3.3878 | 1
208 | IMC | 302 | 20 |  | 1540 | 35 | 20 | UV | 12320 | 1.4708 | 1
209 | Classroom | 341 | 22 |  | 770 | 17 | 17 | UV | 6160 | 3.3214 | 1
210 | IMC | 323 | 21 |  | 1540 | 35 | 21 | UV | 12320 | 1.5731 | 1
211 | Classroom | 307 | 20 |  | 735 | 16 | 16 | UV | 5880 | 3.1327 | 1
212 | Classroom | 305 | 20 |  | 510 | 11 | 11 | UV | 4080 | 4.4853 | 2
214 | Classroom | 339 | 22 |  | 735 | 16 | 16 | UV | 5880 | 3.4592 | 1
216 | Classroom | 330 | 22 |  | 735 | 16 | 16 | UV | 5880 | 3.3673 | 1
218 | Classroom | 180 | 12 |  | 143 | 3 | 3 | UV | 1144 | 9.4406 | 2
300 | Classroom | 311 | 20 |  | 700 | 15 | 15 | UV | 5600 | 3.3321 | 1
301 | Classroom | 320 | 21 |  | 720 | 16 | 16 | UV | 5760 | 3.3333 | 1
302 | Classroom | 416 | 27 |  | 770 | 17 | 17 | UV | 6160 | 4.0519 | 2
303 | Classroom | 380 | 25 |  | 735 | 16 | 16 | UV | 5880 | 3.8776 | 1
304 | Classroom | 305 | 20 |  | 735 | 16 | 16 | UV | 5880 | 3.1122 | 1
306 | Classroom | 281 | 18 |  | 406 | 9 | 9 | UV | 3248 | 5.1909 | 2
307 | Classroom | 292 | 19 |  | 735 | 16 | 16 | UV | 5880 | 2.9796 | 1
308 | Classroom | 385 | 25 |  | 735 | 16 | 16 | UV | 5880 | 3.9286 | 1
309 | Classroom | 318 | 21 |  | 735 | 16 | 16 | UV | 5880 | 3.2449 | 1
310 | Classroom | 163 | 10 | Yes | 735 | 16 | 16 | UV | 5880 | 1.6633 | 1
311 | Classroom | 334 | 22 |  | 735 | 16 | 16 | UV | 5880 | 3.4082 | 1
312 | Classroom | 275 | 18 |  | 510 | 11 | 11 | UV | 4080 | 4.0441 | 2
314 | Classroom | 325 | 21 |  | 735 | 16 | 16 | UV | 5880 | 3.3163 | 1
316 | Classroom | 302 | 20 |  | 735 | 16 | 16 | UV | 5880 | 3.0816 | 1
318 | Classroom | 181 | 12 |  | 143 | 3 | 3 | UV | 1144 | 9.493 | 2
- | Auditorium | 1841 | 122 |  | 4278 | 97 | 97 | AHU | 34224 | 3.2276 | 1
- | Gymnasium | 899 | 59 |  | 3588 | 81 | 59 | AHU | 28704 | 1.8792 | 1
- | Library | 625 | 41 |  | 1540 | 35 | 35 | UV | 12320 | 3.0438 | 1
- | Main Office | 101 | 6 | Yes | 483 | 10 | 10 | AHU | 3864 | 1.5683 | 1
- | Nurse Office | 84 | 5 | Yes | 368 | 8 | 8 |  | 2944 | 1.712 | 1
- | Admin Asst. Office | 38 | 2 |  | 99 | 2 | 2 |  | 792 | 2.8788 | 1
- | Principal's Office | 41 | 2 |  | 315 | 7 | 2 |  | 2520 | 0.97619 | 0
- | Conference/Office | 90 | 6 |  | 384 | 8 | 6 |  | 3072 | 1.7578 | 1
- | Counselor's Office | 0 | 0 |  | 442 | 10 | 0 |  | 3536 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | John B. Kelly Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Capital | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Retest | 2nd Retest | [5 empty] | 0 | 0 | 0
| Devine 3rd Retest | Devine 4th Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Teachers Dining | 340 | 22 |  | 868 | 19 | 19 | UV | 6944 | 2.9378 | 1
102 | Classroom | 497 | 33 |  | 850 | 19 | 19 | UV | 6800 | 4.3853 | 2
102A | Classroom | 155 | 10 |  | 550 | 12 | 10 | UV | 4400 | 2.1136 | 1
103 | Classroom | 673 | 44 |  | 850 | 19 | 19 | UV | 6800 | 5.9382 | 2
103A | Classroom | 216 | 14 |  | 550 | 12 | 12 | UV | 4400 | 2.9455 | 1
104 | Classroom | 607 | 40 |  | 850 | 19 | 19 | UV | 6800 | 5.3559 | 2
105 | Classroom | 592 | 39 |  | 850 | 19 | 19 | UV | 6800 | 5.2235 | 2
106 | Classroom | 576 | 38 |  | 850 | 19 | 19 | UV | 6800 | 5.0824 | 2
107 | Classroom | 572 | 38 |  | 850 | 19 | 19 | UV | 6800 | 5.0471 | 2
108 | Classroom | 576 | 38 |  | 850 | 19 | 19 | UV | 6800 | 5.0824 | 2
109 | Classroom | 539 | 35 |  | 850 | 19 | 19 | UV | 6800 | 4.7559 | 2
110 | Classroom | 434 | 28 |  | 850 | 19 | 19 | UV | 6800 | 3.8294 | 1
111 | Classroom | 336 | 22 |  | 850 | 19 | 19 | UV | 6800 | 2.9647 | 1
112 | Classroom | 627 | 41 |  | 850 | 19 | 19 | UV | 6800 | 5.5324 | 2
113 | Classroom | 320 | 21 |  | 850 | 19 | 19 | UV | 6800 | 2.8235 | 1
114 | Classroom | 534 | 35 |  | 850 | 19 | 19 | UV | 6800 | 4.7118 | 2
160 | Classroom | 305 | 20 |  | 942 | 21 | 20 | UV | 7536 | 2.4283 | 1
160 | Main Office | 182 | 12 |  | 232 | 5 | 5 | UV | 1856 | 5.8836 | 2
201 | Classroom | 370 | 24 |  | 850 | 19 | 19 | UV | 6800 | 3.2647 | 1
202 | Classroom | 494 | 32 |  | 850 | 19 | 19 | UV | 6800 | 4.3588 | 2
202A | Office | 33 | 2 |  | 140 | 3 | 2 | UV | 1120 | 1.7679 | 1
203 | Classroom | 744 | 49 |  | 1088 | 24 | 24 | UV | 8704 | 5.1287 | 2
204 | Classroom | 609 | 40 |  | 850 | 19 | 19 | UV | 6800 | 5.3735 | 2
204A | Classroom | 282 | 18 |  | 550 | 12 | 12 | UV | 4400 | 3.8455 | 1
205 | Classroom | 327 | 21 |  | 850 | 19 | 19 | UV | 6800 | 2.8853 | 1
205A | Classroom | 293 | 19 |  | 550 | 12 | 12 | UV | 4400 | 3.9955 | 1
206 | Classroom | 284 | 18 |  | 1088 | 24 | 18 | UV | 8704 | 1.9577 | 1
207 | Classroom | 468 | 31 |  | 850 | 19 | 19 | UV | 6800 | 4.1294 | 2
208 | Classroom | 586 | 39 |  | 850 | 19 | 19 | UV | 6800 | 5.1706 | 2
209 | Classroom | 381 | 25 |  | 850 | 19 | 19 | UV | 6800 | 3.3618 | 1
210 | Classroom | 341 | 22 |  | 1088 | 24 | 22 | UV | 8704 | 2.3506 | 1
210A | Office | 188 | 12 |  | 136 | 3 | 3 | UV | 1088 | 10.3676 | 3
211 | Classroom | 530 | 35 |  | 850 | 19 | 19 | UV | 6800 | 4.6765 | 2
212 | Classroom | 729 | 48 |  | 850 | 19 | 19 | UV | 6800 | 6.4324 | 2
212A | Classroom | 289 | 19 |  | 550 | 12 | 12 | UV | 4400 | 3.9409 | 1
213 | Classroom | 661 | 44 |  | 850 | 19 | 19 | UV | 6800 | 5.8324 | 2
213A | Classroom | 233 | 15 |  | 550 | 12 | 12 | UV | 4400 | 3.1773 | 1
214 | Classroom | 588 | 39 |  | 1088 | 24 | 24 | UV | 8704 | 4.0533 | 2
215 | Classroom | 341 | 22 |  | 676 | 15 | 15 | UV | 5408 | 3.7833 | 1
216 | Classroom | 425 | 28 |  | 850 | 19 | 19 | UV | 6800 | 3.75 | 1
217 East | Classroom | 294 | 19 |  | 1006 | 22 | 19 | UV | 8048 | 2.1918 | 1
217 North | Classroom | 227 | 15 |  | 1093 | 24 | 15 | UV | 8744 | 1.5576 | 1
217 South Center | Classroom | 382 | 25 |  | 1069 | 24 | 24 | UV | 8552 | 2.6801 | 1
217 West Center | Classroom | 285 | 19 |  | 1093 | 24 | 19 | UV | 8744 | 1.9556 | 1
- | Admin/Asst. Office | 66 | 4 |  | 179 | 4 | 4 | UV | 1432 | 2.7654 | 1
- | Administration Offices | 1305 | 87 |  | 535 | 12 | 12 | UV | 4280 | 18.2944 | 3
ART | Art Classroom | 731 | 48 |  | 1350 | 30 | 30 | UV | 10800 | 4.0611 | 2
ART -A | Art Classroom | 401 | 26 |  |  | 0 | 0 | UV | 0 | 0 | 0
ART -B | Art Classroom | 557 | 37 |  |  | 0 | 0 | UV | 0 | 0 | 0
ART -C | Art Classroom | 111 | 7 |  |  | 0 | 0 | UV | 0 | 0 | 0
ART -D | Art Classroom | 318 | 21 |  |  | 0 | 0 | UV | 0 | 0 | 0
- | Auditorium | 1721 | 114 |  | 6080 | 138 | 114 | UV | 48640 | 2.1229 | 1
- | 1st Flr A-Wing Left Boys Bathroom | 53 | 3 |  | 88 | 2 | 2 | AHU | 704 | 4.517 | 2
- | 2nd Flr A-Wing Left Boys Bathroom | 101 | 6 |  | 96 | 2 | 2 | AHU | 768 | 7.8906 | 2
- | 2nd Flr A-Wing Right Boys Bathroom | 43 | 2 |  | 103 | 2 | 2 | AHU | 824 | 3.1311 | 1
- | Conference Room | 139 | 9 |  | 211 | 4 | 4 | AHU | 1688 | 4.9408 | 2
- | Copy/Storage Room | 110 | 7 |  | 165 | 3 | 3 | AHU | 1320 | 5 | 2
- | Corridor | 41 | 2 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | Counselor Office | 58 | 3 |  | 123 | 2 | 2 | AHU | 984 | 3.5366 | 1
- | Dressing - A Backstage | 307 | 20 |  | 232 | 5 | 5 | UV | 1856 | 9.9246 | 2
- | Dressing - B Backstage | 461 | 30 |  | 196 | 4 | 4 | UV | 1568 | 17.6403 | 3
- | Dressing - C Backstage | 493 | 32 |  | 190 | 4 | 4 | UV | 1520 | 19.4605 | 3
- | Dressing - D Backstage | 275 | 18 |  | 199 | 4 | 4 | UV | 1592 | 10.3643 | 3
- | 1st Flr A-Wing Left Girls Bathroom | 41 | 2 |  | 109 | 2 | 2 | AHU | 872 | 2.8211 | 1
- | 2nd Flr A-Wing Left Girls Bathroom | 78 | 5 |  | 106 | 2 | 2 | AHU | 848 | 5.5189 | 2
- | 2nd Flr A-Wing Right Girls Bathroom | 54 | 3 |  | 103 | 2 | 2 | AHU | 824 | 3.932 | 1
- | IMC | 0 | 0 |  | 8471 | 192 | 0 | AHU | 67768 | 0 | 0
- | IMC North Side | 947 | 63 |  | 480 | 10 | 10 | AHU | 3840 | 14.7969 | 3
- | IMC South Side | 822 | 54 |  | 480 | 10 | 10 | AHU | 3840 | 12.8438 | 3
- | IMC Entry from Office | 0 | 0 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | IMC Entry to Hall | 0 | 0 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | IMC-1 Office | 80 | 5 |  | 293 | 6 | 5 | AHU | 2344 | 2.0478 | 1
- | IMC-2 Storage | 151 | 10 |  | 330 | 7 | 7 | AHU | 2640 | 3.4318 | 1
- | IMC-4 Storage | 175 | 11 |  | 372 | 8 | 8 | AHU | 2976 | 3.5282 | 1
- | IMC-5 Data/Storage | 68 | 4 |  | 277 | 6 | 4 | AHU | 2216 | 1.8412 | 1
- | Cafeteria | 0 | 0 |  | 1195 | 27 | 0 | AHU | 9560 | 0 | 0
- | Cafeteria | 1928 | 128 |  | 4807 | 109 | 109 | AHU | 38456 | 3.0081 | 1
- | Gym | 2934 | 195 |  | 387 | 8 | 8 | AHU | 3096 | 56.8605 | 5
- | Music Classroom A | 326 | 21 |  |  | 0 | 0 | UV | 0 | 0 | 0
- | Music Classroom B | 555 | 37 |  |  | 0 | 0 | UV | 0 | 0 | 0
- | Music Classroom C | 152 | 10 |  |  | 0 | 0 | UV | 0 | 0 | 0
- | Music Classroom D | 106 | 7 |  |  | 0 | 0 | UV | 0 | 0 | 0
- | Main Music Classroom | 463 | 30 |  | 380 | 8 | 8 | UV | 3040 | 9.1382 | 2
- | Music Office | 136 | 9 |  | 355 | 8 | 8 | AHU | 2840 | 2.8732 | 1
- | Nurse Exam Room | 0 | 0 |  | 209 | 4 | 0 | AHU | 1672 | 0 | 0
- | Nurse Exam Room | 43 | 2 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | Nurses Office | 0 | 0 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | Nurses Rest | 68 | 4 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | Nurses Suite | 411 | 27 |  |  | 0 | 0 | UV | 0 | 0 | 0
- | Aud & Dental | 31 | 2 |  | 270 | 6 | 2 | AHU | 2160 | 0.86111 | 0
- | Principals Office | 98 | 6 |  | 270 | 6 | 6 | AHU | 2160 | 2.7222 | 1
- | Speech/Com | 388 | 25 |  | 736 | 16 | 16 | UV | 5888 | 3.9538 | 1
- | Server Room | 55 | 3 |  | 121 | 2 | 2 | Split System | 968 | 3.4091 | 1
- | Storage | 247 | 16 |  | 809 | 18 | 16 | AHU | 6472 | 2.2899 | 1
- | Office / Waiting Room | 277 | 18 |  |  | 0 | 0 | AHU | 0 | 0 | 0
K - 1 | Kindergarten | 452 | 30 |  | 1488 | 33 | 30 | UV | 11904 | 2.2782 | 1
K - 2 | Kindergarten | 490 | 32 |  | 1488 | 33 | 32 | UV | 11904 | 2.4698 | 1
K - 3 | Kindergarten | 498 | 33 |  | 1488 | 33 | 33 | UV | 11904 | 2.5101 | 1
K - 4 | Kindergarten | 635 | 42 |  | 1488 | 33 | 33 | UV | 11904 | 3.2006 | 1
K - 5 | Kindergarten | 280 | 18 |  | 1488 | 33 | 18 | UV | 11904 | 1.4113 | 1
K - 6 | Kindergarten | 300 | 20 |  | 1488 | 33 | 20 | UV | 11904 | 1.5121 | 1
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Kenderton Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Part 2 | Part 3 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 229 | 15 |  | 1012 | 23 | 15 | UV | 8096 | 1.6971 | 1
101 | Classroom | 451 | 30 |  | 1680 | 38 | 30 | UV | 13440 | 2.0134 | 1
102 | Classroom | 458 | 30 |  | 1652 | 37 | 30 | UV | 13216 | 2.0793 | 1
103 | Classroom | 331 | 22 | Yes | 1344 | 30 | 30 | UV | 10752 | 1.8471 | 1
104 | Nurse |  | 0 | Yes | 275 | 6 | 6 |  | 2200 | 0 | 0
200A | Classroom | 198 | 13 |  | 442 | 10 | 10 | UV | 3536 | 3.3597 | 1
200 | Classroom | 0 | 0 |  | 891 | 20 | 0 | UV | 7128 | 0 | 0
201 | Classroom | 278 | 18 | Yes | 891 | 20 | 20 | UV | 7128 | 2.3401 | 1
202 | Classroom | 331 | 22 |  | 918 | 20 | 20 | UV | 7344 | 2.7042 | 1
203 | Classroom | 297 | 19 |  | 980 | 22 | 19 | UV | 7840 | 2.273 | 1
204 | Classroom | 302 | 20 |  | 918 | 20 | 20 | UV | 7344 | 2.4673 | 1
205 | Classroom | 198 | 13 |  | 918 | 20 | 13 | UV | 7344 | 1.6176 | 1
206 | Classroom | 273 | 18 |  | 616 | 14 | 14 | UV | 4928 | 3.3239 | 1
207 | Classroom | 273 | 18 |  | 918 | 20 | 18 | UV | 7344 | 2.2304 | 1
208 | Classroom | 191 | 12 | Yes | 120 | 2 | 2 | UV | 960 | 11.9375 | 3
209 | Classroom | 283 | 18 |  | 918 | 20 | 18 | UV | 7344 | 2.3121 | 1
211 | Classroom | 276 | 18 |  | 286 | 6 | 6 | UV | 2288 | 7.2378 | 2
213 | Classroom | 271 | 18 |  | 918 | 20 | 18 | UV | 7344 | 2.2141 | 1
300 | Classroom | 278 | 18 | Yes | 918 | 20 | 20 | UV | 7344 | 2.2712 | 1
301 | Classroom | 271 | 18 |  | 918 | 20 | 18 | UV | 7344 | 2.2141 | 1
302 | Classroom | 272 | 18 | Yes | 918 | 20 | 20 | UV | 7344 | 2.2222 | 1
303 | Classroom | 296 | 19 |  | 980 | 22 | 19 | UV | 7840 | 2.2653 | 1
304 | Classroom | 276 | 18 |  | 864 | 19 | 18 | UV | 6912 | 2.3958 | 1
306 | Classroom | 316 | 21 |  | 918 | 20 | 20 | UV | 7344 | 2.5817 | 1
307 | Classroom | 281 | 18 | Yes | 924 | 21 | 21 | UV | 7392 | 2.2808 | 1
308 | Classroom | 0 | 0 | Yes | 924 | 21 | 21 | UV | 7392 | 0 | 0
309 | Classroom | 0 | 0 |  | 980 | 22 | 0 | UV | 7840 | 0 | 0
310 | Classroom | 0 | 0 | Yes | 616 | 14 | 14 | UV | 4928 | 0 | 0
311 | Classroom | 0 | 0 | Yes | 918 | 20 | 20 | UV | 7344 | 0 | 0
312 | Computer Room |  | 0 | Yes | 860 | 19 | 19 |  | 6880 | 0 | 0
313 | Classroom | 0 | 0 | Yes | 918 | 20 | 20 | UV | 7344 | 0 | 0
314 | Classroom | 0 | 0 |  | 280 | 6 | 0 | UV | 2240 | 0 | 0
315 | Classroom | 0 | 0 | Yes | 918 | 20 | 20 | UV | 7344 | 0 | 0
316 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | UV | 6720 | 0 | 0
319 | Classroom | 0 | 0 |  | 918 | 20 | 0 | UV | 7344 | 0 | 0
400 | Classroom | 286 | 19 |  | 2660 | 60 | 19 | UV | 21280 | 0.80639 | 0
401 | Classroom | 279 | 18 |  | 918 | 20 | 18 | UV | 7344 | 2.2794 | 1
402 | Classroom | 313 | 20 |  | 918 | 20 | 20 | UV | 7344 | 2.5572 | 1
403 | Classroom | 340 | 22 |  | 918 | 20 | 20 | UV | 7344 | 2.7778 | 1
404 | Classroom | 0 | 0 |  | 868 | 19 | 0 | UV | 6944 | 0 | 0
406 | Classroom | 291 | 19 |  | 918 | 20 | 19 | UV | 7344 | 2.3775 | 1
407 | Classroom | 0 | 0 | Yes | 924 | 21 | 21 | UV | 7392 | 0 | 0
408 | Classroom | 0 | 0 | Yes | 918 | 20 | 20 | UV | 7344 | 0 | 0
409 | Classroom | 0 | 0 | Yes | 980 | 22 | 22 | UV | 7840 | 0 | 0
410 | Classroom | 335 | 22 | Yes | 644 | 14 | 14 | UV | 5152 | 3.9014 | 1
411 | Classroom | 0 | 0 |  | 918 | 20 | 0 | UV | 7344 | 0 | 0
412 | Classroom | 276 | 18 |  | 308 | 7 | 7 | UV | 2464 | 6.7208 | 2
413 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | UV | 6720 | 0 | 0
414 | Classroom | 0 | 0 | Yes | 270 | 6 | 6 | UV | 2160 | 0 | 0
415 | Classroom | 0 | 0 |  | 918 | 20 | 0 | UV | 7344 | 0 | 0
- | Parent Resource | 0 | 0 |  | 2 | 0 | 0 | UV | 16 | 0 | 0
- | Main Office | 42 | 2 |  | 406 | 9 | 2 | UV | 3248 | 0.77586 | 0
- | Principal's Office |  | 0 |  | 320 | 7 | 0 |  | 2560 | 0 | 0
- | Asist Prince | 172 | 11 |  | 11 | 0 | 0 | UV | 88 | 117.2727 | 5
Sheet Last Modified: | 2021-04-19 | [7 empty] | 0 | 0 | 0
School: | Kensington High School | House fan Abated | [6 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | - |  | 0 |  | 675 | 15 | 0 |  | 5400 | 0 | 0
2 | - |  | 0 |  | 1014 | 23 | 0 |  | 8112 | 0 | 0
3 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
4 | - |  | 0 |  | 364 | 8 | 0 |  | 2912 | 0 | 0
5 | - |  | 0 |  | 850 | 19 | 0 |  | 6800 | 0 | 0
100 | Main Office |  | 0 |  | 1014 | 23 | 0 |  | 8112 | 0 | 0
102 | - |  | 0 | Yes | 800 | 18 | 18 |  | 6400 | 0 | 0
103 | IMC |  | 0 |  | 1690 | 38 | 0 |  | 13520 | 0 | 0
104 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
105 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
107 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
108 | - |  | 0 |  | 962 | 21 | 0 |  | 7696 | 0 | 0
109 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
111 | - |  | 0 |  | 910 | 20 | 0 |  | 7280 | 0 | 0
114 | - |  | 0 | Yes | 728 | 16 | 16 |  | 5824 | 0 | 0
115 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
116 | - |  | 0 |  | 702 | 15 | 0 |  | 5616 | 0 | 0
117 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
118 | - |  | 0 | Yes | 728 | 16 | 16 |  | 5824 | 0 | 0
120 | - |  | 0 |  | 845 | 19 | 0 |  | 6760 | 0 | 0
125 | - |  | 0 |  | 1020 | 23 | 0 |  | 8160 | 0 | 0
200 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
201 | - |  | 0 |  | 962 | 21 | 0 |  | 7696 | 0 | 0
202 | - |  | 0 |  | 910 | 20 | 0 |  | 7280 | 0 | 0
203 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
204 | - |  | 0 |  | 702 | 15 | 0 |  | 5616 | 0 | 0
205 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
207 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
208 | - |  | 0 |  | 884 | 20 | 0 |  | 7072 | 0 | 0
209 | - |  | 0 |  | 546 | 12 | 0 |  | 4368 | 0 | 0
210 | - |  | 0 |  | 546 | 12 | 0 |  | 4368 | 0 | 0
211 | - |  | 0 |  | 884 | 20 | 0 |  | 7072 | 0 | 0
214 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
215 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
217 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
218 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
221 | - |  | 0 |  | 1037 | 23 | 0 |  | 8296 | 0 | 0
300 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
301 | - |  | 0 |  | 910 | 20 | 0 |  | 7280 | 0 | 0
302 | - |  | 0 |  | 910 | 20 | 0 |  | 7280 | 0 | 0
303 | - |  | 0 |  | 702 | 15 | 0 |  | 5616 | 0 | 0
304 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
305 | - |  | 0 |  | 702 | 15 | 0 |  | 5616 | 0 | 0
307 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
308 | - |  | 0 |  | 910 | 20 | 0 |  | 7280 | 0 | 0
309 | - |  | 0 |  | 546 | 12 | 0 |  | 4368 | 0 | 0
310 | - |  | 0 |  | 546 | 12 | 0 |  | 4368 | 0 | 0
311 | - |  | 0 |  | 884 | 20 | 0 |  | 7072 | 0 | 0
314 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
315 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
316 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
317 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
318 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
322 | Gym |  | 0 |  | 6360 | 144 | 0 |  | 50880 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-22 | [7 empty] | 0 | 0 | 0
School: | Kensington Creative and Performing Arts (CAPA) High School | [7 empty] | 0 | 0 | 0
Vendor: | Meehan | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Auditorium |  | 0 |  | 5100 | 115 | 0 |  | 40800 | 0 | 0
- | Gymnasium |  | 0 |  | 8400 | 190 | 0 |  | 67200 | 0 | 0
101b | - |  | 0 |  | 450 | 10 | 0 |  | 3600 | 0 | 0
101 | - |  | 0 |  | 400 | 9 | 0 |  | 3200 | 0 | 0
103 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | 0 | 0
106 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | 0 | 0
118 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
119 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
121 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
122 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
123 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
131 | - |  | 0 |  | 1150 | 26 | 0 |  | 9200 | 0 | 0
134 | - |  | 0 | Yes | 700 | 15 | 15 |  | 5600 | 0 | 0
135 | - |  | 0 |  | 750 | 17 | 0 |  | 6000 | 0 | 0
201 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | 0 | 0
209 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
210 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
212 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
213 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
214 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
216 | - |  | 0 | Yes | 1400 | 31 | 31 |  | 11200 | 0 | 0
217 | - |  | 0 |  | 1400 | 31 | 0 |  | 11200 | 0 | 0
218 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | 0 | 0
220 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | 0 | 0
221 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | 0 | 0
224 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
225 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
- | Cafe |  | 0 |  | 2400 | 54 | 0 |  | 19200 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Kensington Health Sciences Academy High School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Room | 247 | 16 |  | 857 | 19 | 16 |  | 6856 | 2.1616 | 1
102 | Room | 338 | 22 |  | 792 | 18 | 18 |  | 6336 | 3.2008 | 1
103 | Room | 206 | 13 |  | 854 | 19 | 13 |  | 6832 | 1.8091 | 1
104 | Room | 248 | 16 |  | 834 | 18 | 16 |  | 6672 | 2.2302 | 1
105 | Room | 212 | 14 |  | 854 | 19 | 14 |  | 6832 | 1.8618 | 1
106 | Room | 548 | 36 |  | 834 | 18 | 18 |  | 6672 | 4.9281 | 2
107 & 107A | Room | 613 | 40 |  | 783 | 17 | 17 |  | 6264 | 5.8716 | 2
110 | Room | 184 | 12 |  | 793 | 18 | 12 |  | 6344 | 1.7402 | 1
114 | Nurse |  | 0 |  | 114 | 2 | 0 |  | 912 | 0 | 0
115 | Room | 191 | 12 |  | 337 | 7 | 7 |  | 2696 | 4.2507 | 2
116 | Room | 171 | 11 |  | 848 | 19 | 11 |  | 6784 | 1.5124 | 1
201 | Room | 506 | 33 |  | 919 | 20 | 20 |  | 7352 | 4.1295 | 2
203 | Room | 0 | 0 |  | 795 | 18 | 0 |  | 6360 | 0 | 0
208 | 2nd Floor Bed and Dental Area | 1803 | 120 |  | 943 | 21 | 21 |  | 7544 | 14.3399 | 3
211 | Room | 273 | 18 |  | 860 | 19 | 18 |  | 6880 | 2.3808 | 1
212 | Room | 77 | 5 |  | 456 | 10 | 5 |  | 3648 | 1.2664 | 1
213 | Room | 250 | 16 |  | 681 | 15 | 15 |  | 5448 | 2.7533 | 1
214 | Dental Classroom | 171 | 11 |  | 794 | 18 | 11 |  | 6352 | 1.6152 | 1
215 | Room | 204 | 13 |  | 689 | 15 | 13 |  | 5512 | 2.2206 | 1
216 | Room | 191 | 12 |  | 756 | 17 | 12 |  | 6048 | 1.8948 | 1
217 | Room | 222 | 14 |  | 681 | 15 | 14 |  | 5448 | 2.4449 | 1
218 | Room | 276 | 18 |  | 599 | 13 | 13 |  | 4792 | 3.4558 | 1
- | Cafeteria | 586 | 39 |  | 1697 | 38 | 38 |  | 13576 | 2.5899 | 1
Sheet Last Modified: | 2021-03-30 | [7 empty] | 0 | 0 | 0
School: | Francis Scott Key Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | [8 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Gym |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
102 | Classroom |  | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0
103 | Classroom |  | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0
104 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
105 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
106 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
107 | Classroom |  | 0 |  | 437 | 9 | 0 | House Fan | 3496 | 0 | 0
108 | Classroom |  | 0 |  | 667 | 15 | 0 | House Fan | 5336 | 0 | 0
109 | Classroom |  | 0 |  | 667 | 15 | 0 | House Fan | 5336 | 0 | 0
110 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
111 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
212 | Classroom |  | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0
213 | Classroom |  | 0 | Yes | 837 | 19 | 19 | House Fan | 6696 | 0 | 0
215 | IMC |  | 0 | Yes | 1536 | 34 | 34 | House Fan | 12288 | 0 | 0
216 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
217 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
218 | Classroom |  | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0
219 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
220 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
221 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
222 | Computer Lab |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0
323 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan | 5704 | 0 | 0
324 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan | 5704 | 0 | 0
325 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan | 5704 | 0 | 0
326 | Classroom |  | 0 |  | 736 | 16 | 0 | House Fan | 5888 | 0 | 0
327 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan | 5704 | 0 | 0
328 | Classroom |  | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
329 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
330 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
331 | Classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0
332 | Classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0
333 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
- | Boy's Gang Bathrrom |  | 0 |  | 620 | 14 | 0 | N/A | 4960 | 0 | 0
- | Caferteria |  | 0 | Yes | 2240 | 50 | 50 | House Fan | 17920 | 0 | 0
- | Counselor's Office |  | 0 |  | 180 | 4 | 0 | House Fan | 1440 | 0 | 0
- | Girls Gang Bathrrom |  | 0 |  | 620 | 14 | 0 | N/A | 4960 | 0 | 0
- | Main Office |  | 0 | Yes | 361 | 8 | 8 | House Fan | 2888 | 0 | 0
- | Nurse |  | 0 | Yes | 391 | 8 | 8 | House Fan | 3128 | 0 | 0
- | Principle's Office |  | 0 |  | 276 | 6 | 0 | House Fan | 2208 | 0 | 0
- | Teachers' Lounge |  | 0 |  | 391 | 8 | 0 | House Fan | 3128 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-24 | [7 empty] | 0 | 0 | 0
School: | Eliza B. Kirkbride Elementary-Middle | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | - |  | 0 | Yes | 805 | 18 | 18 | House Fan | 6440 | 0 | 0
102 | - |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
103 | - |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
104 | - |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
106 | - |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
107 | - |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
108 | - |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
109 | - |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
110 | - |  | 0 | Yes | 841 | 19 | 19 | House Fan | 6728 | 0 | 0
201 | - |  | 0 | Yes | 814 | 18 | 18 | House Fan | 6512 | 0 | 0
202 | - |  | 0 |  | 660 | 15 | 0 | House Fan | 5280 | 0 | 0
203 | - |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
204 | - |  | 0 |  | 660 | 15 | 0 | House Fan | 5280 | 0 | 0
205 | - |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
208 | - |  | 0 | Yes | 638 | 14 | 14 | House Fan | 5104 | 0 | 0
209 | - |  | 0 |  | 638 | 14 | 0 | House Fan | 5104 | 0 | 0
210 | - |  | 0 | Yes | 841 | 19 | 19 | House Fan | 6728 | 0 | 0
211 | - |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
212 | - |  | 0 |  | 638 | 14 | 0 | House Fan | 5104 | 0 | 0
301 | - |  | 0 |  | 851 | 19 | 0 | House Fan | 6808 | 0 | 0
302 | - |  | 0 |  | 660 | 15 | 0 | House Fan | 5280 | 0 | 0
303 | - |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | 0 | 0
304 | - |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
305/306 | - |  | 0 |  | 1357 | 30 | 0 | House Fan | 10856 | 0 | 0
307 | - |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
308 | - |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
309 | - |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
310 | - |  | 0 |  | 841 | 19 | 0 | House Fan | 6728 | 0 | 0
311 | - |  | 0 |  | 660 | 15 | 0 | House Fan | 5280 | 0 | 0
312 | - |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
- | Art |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
- | Counselor Suite |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
- | Gym |  | 0 | Yes | 3680 | 83 | 83 | House Fan | 29440 | 0 | 0
- | Library |  | 0 | Yes | 1380 | 31 | 31 | House Fan | 11040 | 0 | 0
- | Lunchroom1 |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
- | Lunchroom2 |  | 0 | Yes | 1100 | 25 | 25 | House Fan | 8800 | 0 | 0
- | Main Office |  | 0 | Yes | 322 | 7 | 7 | House Fan | 2576 | 0 | 0
- | Nurse Office |  | 0 | Yes | 96 | 2 | 2 | House Fan | 768 | 0 | 0
- | Principal Office |  | 0 | Yes | 240 | 5 | 5 | House Fan | 1920 | 0 | 0
- | Teacher Lounge/BE office |  | 0 | Yes | 960 | 21 | 21 | House Fan | 7680 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-20 | [7 empty] | #VALUE! | #VALUE! | #VALUE!
School: | John Hancock Demonstration Middle School @ General J Harry LaBrum Campus | [7 empty] | 0 | 0 | 0
| LaBrum Building | LaBrum Retest | [6 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | #VALUE! | #VALUE! | #VALUE!
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
102 | Classroom | 391 | 26 |  | 875 | 19 | 19 | UV | 7000 | 3.3514 | 1
102A | Classroom | 230 | 15 |  | 578 | 13 | 13 | UV | 4624 | 2.9844 | 1
103 | Classroom | 0 | 0 | Yes | 910 | 20 | 20 | UV | 7280 | 0 | 0
104 | Classroom | 622 | 41 |  | 612 | 13 | 13 | UV | 4896 | 7.6225 | 2
105 | Classroom | 150 | 10 | Yes | 1152 | 26 | 26 | UV | 9216 | 0.97656 | 0
106 | Classroom | 320 | 21 |  | 342 | 7 | 7 | UV | 2736 | 7.0175 | 2
107 | Classroom | 221 | 14 | Yes | 1044 | 23 | 23 | UV | 8352 | 1.5876 | 1
201 | Classroom | 362 | 24 |  | 864 | 19 | 19 | UV | 6912 | 3.1424 | 1
202 | Classroom | 267 | 17 |  | 782 | 17 | 17 | UV | 6256 | 2.5607 | 1
203 | Classroom | 245 | 16 | Yes | 884 | 20 | 20 | UV | 7072 | 2.0786 | 1
204 | Classroom | 240 | 16 | Yes | 1116 | 25 | 25 | UV | 8928 | 1.6129 | 1
205 | Classroom | 311 | 20 |  | 900 | 20 | 20 | UV | 7200 | 2.5917 | 1
206 | Classroom | 583 | 38 |  | 858 | 19 | 19 | UV | 6864 | 5.0962 | 2
207 | Classroom | 340 | 22 |  | 840 | 19 | 19 | UV | 6720 | 3.0357 | 1
208 | Classroom | 462 | 30 |  | 816 | 18 | 18 | UV | 6528 | 4.2463 | 2
209 | Classroom | 410 | 27 |  | 720 | 16 | 16 | UV | 5760 | 4.2708 | 2
210 | Classroom | 327 | 21 |  | 888 | 20 | 20 | UV | 7104 | 2.7618 | 1
212 | Classroom | 390 | 26 |  | 875 | 19 | 19 | UV | 7000 | 3.3429 | 1
213 | Classroom | 336 | 22 |  | 864 | 19 | 19 | UV | 6912 | 2.9167 | 1
214 | Classroom | 366 | 24 |  | 828 | 18 | 18 | UV | 6624 | 3.3152 | 1
- | Admin | 0 | 0 | Yes | 286 | 6 | 6 | UV | 2288 | 0 | 0
- | Cafeteria | 450 | 30 |  | 2765 | 62 | 30 | UV | 22120 | 1.2206 | 1
- | Gym | 0 | 0 |  | 5248 | 119 | 0 |  | 41984 | 0 | 0
- | Library | 538 | 35 |  | 2016 | 45 | 35 | UV | 16128 | 2.0015 | 1
- | Nurse's Room | 0 | 0 | Yes | 550 | 12 | 12 | UV | 4400 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | Robert E. Lamberton Elementary School | [7 empty] | 0 | 0 | 0
School: | Robert E. Lamberton Elementary- Little School House | [7 empty] | 0 | 0 | 0
School: | Robert E. Lamberton Elementary- Little School House- Part 2 | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Main Building | [8 empty] | 0 | 0 | 0
1A | Music Room | 261 | 17 |  | 506 | 11 | 11 | UV | 4048 | 3.8686 | 1
1B | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | UV | 5760 | 0 | 0
2A | Classroom | 264 | 17 |  | 504 | 11 | 11 | UV | 4032 | 3.9286 | 1
4 | Classroom | 159 | 10 | Yes | 2024 | 46 | 46 | UV | 16192 | 0.58918 | 0
5A | Classroom | 0 | 0 | Yes | 600 | 13 | 13 | UV | 4800 | 0 | 0
6 | Classroom | 0 | 0 | Yes | 625 | 14 | 14 | UV | 5000 | 0 | 0
7 | Classroom |  | 0 | Yes | 1206 | 27 | 27 | UV | 9648 | 0 | 0
101 | Classroom | 457 | 30 |  | 506 | 11 | 11 | UV | 4048 | 6.7737 | 2
102 | Classroom | 348 | 23 |  | 1012 | 23 | 23 | UV | 8096 | 2.5791 | 1
103 | Classroom | 466 | 31 |  | 989 | 22 | 22 | UV | 7912 | 3.5339 | 1
104 | Classroom | 335 | 22 | Yes | 1012 | 23 | 23 | UV | 8096 | 2.4827 | 1
105 | Classroom | 277 | 18 | Yes | 989 | 22 | 22 | UV | 7912 | 2.1006 | 1
106 | Classroom | 198 | 13 | Yes | 1012 | 23 | 23 | UV | 8096 | 1.4674 | 1
107 | Classroom | 406 | 27 |  | 1012 | 23 | 23 | UV | 8096 | 3.0089 | 1
108 | Classroom | 271 | 18 |  | 667 | 15 | 15 | UV | 5336 | 3.0472 | 1
109 | Classroom | 351 | 23 |  | 1012 | 23 | 23 | UV | 8096 | 2.6013 | 1
110 | Classroom | 420 | 28 |  | 989 | 22 | 22 | UV | 7912 | 3.185 | 1
111 | Classroom | 338 | 22 |  | 989 | 22 | 22 | UV | 7912 | 2.5632 | 1
112 | Classroom | 0 | 0 | Yes | 989 | 22 | 22 | UV | 7912 | 0 | 0
113 | Classroom | 280 | 18 |  | 575 | 13 | 13 | UV | 4600 | 3.6522 | 1
114 | Classroom | 271 | 18 | Yes | 874 | 19 | 19 | UV | 6992 | 2.3255 | 1
115 | Classroom | 278 | 18 | Yes | 874 | 19 | 19 | UV | 6992 | 2.3856 | 1
116 | Classroom | 387 | 25 |  | 874 | 19 | 19 | UV | 6992 | 3.3209 | 1
117 | Classroom | 176 | 11 | Yes | 874 | 19 | 19 | UV | 6992 | 1.5103 | 1
118 | Classroom | 243 | 16 | Yes | 1012 | 23 | 23 | UV | 8096 | 1.8009 | 1
119 | Assitant Principal |  | 0 | Yes | 361 | 8 | 8 |  | 2888 | 0 | 0
120A | Tescher's Lounge |  | 0 | Yes | 377 | 8 | 8 |  | 3016 | 0 | 0
120 | Nurse |  | 0 |  | 501 | 11 | 0 |  | 4008 | 0 | 0
121 | Special Education |  | 0 | Yes | 531 | 12 | 12 |  | 4248 | 0 | 0
201 | Classroom | 320 | 21 | Yes | 989 | 22 | 22 | UV | 7912 | 2.4267 | 1
202 | Classroom | 0 | 0 | Yes | 667 | 15 | 15 | UV | 5336 | 0 | 0
203 | Classroom | 418 | 27 |  | 989 | 22 | 22 | UV | 7912 | 3.1699 | 1
204 | Classroom | 511 | 34 |  | 1012 | 23 | 23 | UV | 8096 | 3.7871 | 1
205 | Classroom | 560 | 37 |  | 1012 | 23 | 23 | UV | 8096 | 4.1502 | 2
206 | Classroom | 770 | 51 |  | 1012 | 23 | 23 | UV | 8096 | 5.7065 | 2
207 | Classroom | 0 | 0 | Yes | 1012 | 23 | 23 | UV | 8096 | 0 | 0
208 | Classroom | 246 | 16 | Yes | 989 | 22 | 22 | UV | 7912 | 1.8655 | 1
209 | Classroom | 446 | 29 |  | 1012 | 23 | 23 | UV | 8096 | 3.3053 | 1
210A | Classroom | 233 | 15 |  | 504 | 11 | 11 | UV | 4032 | 3.4673 | 1
210B | Classroom | 0 | 0 | Yes | 504 | 11 | 11 | UV | 4032 | 0 | 0
215 | Classroom | 0 | 0 | Yes | 874 | 19 | 19 | UV | 6992 | 0 | 0
216 | Classroom | 0 | 0 | Yes | 874 | 19 | 19 | UV | 6992 | 0 | 0
217 | Classroom | 220 | 14 | Yes | 874 | 19 | 19 | UV | 6992 | 1.8879 | 1
218 | Classroom | 359 | 23 |  | 874 | 19 | 19 | UV | 6992 | 3.0807 | 1
220 | Classroom | 232 | 15 | Yes | 1012 | 23 | 23 | UV | 8096 | 1.7194 | 1
221 | Classroom | 441 | 29 |  | 1058 | 24 | 24 | UV | 8464 | 3.1262 | 1
- | Principal |  | 0 | Yes | 387 | 8 | 8 |  | 3096 | 0 | 0
- | Main Office |  | 0 | Yes | 784 | 17 | 17 |  | 6272 | 0 | 0
- | Auditorium | 4864 | 324 |  | 5832 | 132 | 132 | AHU | 46656 | 6.2551 | 2
Lamberton LSH | [8 empty] | 0 | 0 | 0
15 | Classroom | 313 | 20 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.5296 | 1
16 | Classroom | 299 | 19 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.4165 | 1
17 | Classroom | 317 | 21 |  | 928 | 21 | 21 | AHU | 7424 | 2.562 | 1
18 | Classroom | 329 | 21 |  | 928 | 21 | 21 | AHU | 7424 | 2.6589 | 1
19 | Classroom | 291 | 19 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.3518 | 1
20 | Classroom | 295 | 19 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.3842 | 1
21 | Classroom | 316 | 21 |  | 928 | 21 | 21 | AHU | 7424 | 2.5539 | 1
22 | Classroom | 324 | 21 |  | 928 | 21 | 21 | AHU | 7424 | 2.6185 | 1
23 | Classroom | 314 | 20 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.5377 | 1
24 | Classroom | 327 | 21 |  | 928 | 21 | 21 | AHU | 7424 | 2.6428 | 1
25 | Classroom | 287 | 19 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.3195 | 1
26 | Classroom | 303 | 20 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.4488 | 1
- | Main Office | 4 | 0 | Yes | 300 | 6 | 6 | AHU | 2400 | 0.1 | 0
- | Multi Purpose | 1539 | 102 |  | 1749 | 39 | 39 | AHU | 13992 | 6.5995 | 2
- | Janitor | 0 | 0 |  | 80 | 1 | 0 | AHU | 640 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-16 | [7 empty] | 0 | 0 | 0
School: | Lankenau Environmental Science High School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
201 | Classroom | 407 | 27 |  | 585 | 13 | 13 |  | 4680 | 5.2179 | 2
205 | Classroom | 242 | 16 |  | 534 | 12 | 12 |  | 4272 | 3.3989 | 1
206 | Classroom | 183 | 12 |  | 529 | 12 | 12 |  | 4232 | 2.5945 | 1
207 | Classroom | 182 | 12 |  | 529 | 12 | 12 |  | 4232 | 2.5803 | 1
208 | Classroom | 178 | 11 |  | 522 | 11 | 11 |  | 4176 | 2.5575 | 1
210 | Classroom | 117 | 7 |  | 493 | 11 | 7 |  | 3944 | 1.7799 | 1
211 | Classroom | 120 | 8 |  | 475 | 10 | 8 |  | 3800 | 1.8947 | 1
212 | Classroom | 63 | 4 |  | 507 | 11 | 4 |  | 4056 | 0.93195 | 0
213 | Classroom | 63 | 4 |  | 531 | 12 | 4 |  | 4248 | 0.88983 | 0
214 | Classroom | 67 | 4 |  | 603 | 13 | 4 |  | 4824 | 0.83333 | 0
302 | Classroom | 84 | 5 |  | 586 | 13 | 5 |  | 4688 | 1.0751 | 1
303 | Classroom | 87 | 5 |  | 589 | 13 | 5 |  | 4712 | 1.1078 | 1
304 | Classroom | 85 | 5 |  | 573 | 13 | 5 |  | 4584 | 1.1126 | 1
305 | Classroom | 73 | 4 |  | 613 | 13 | 4 |  | 4904 | 0.89315 | 0
307 | Classroom | 517 | 34 |  | 1146 | 26 | 26 |  | 9168 | 3.3835 | 1
308 | 308 | 412 | 27 |  | 879 | 19 | 19 |  | 7032 | 3.5154 | 1
308B | 308B | 38 | 2 |  | 350 | 7 | 2 |  | 2800 | 0.81429 | 0
309 | Classroom | 611 | 40 |  | 1120 | 25 | 25 |  | 8960 | 4.0915 | 2
- | Auditorium storage 1 | 23 | 1 |  | 67 | 1 | 1 |  | 536 | 2.5746 | 1
- | Auditorium storage 2 | 22 | 1 |  | 109 | 2 | 1 |  | 872 | 1.5138 | 1
- | Botany / Storage area | 198 | 13 |  | 3264 | 74 | 13 |  | 26112 | 0.45496 | 0
- | Cafeteria | 706 | 47 |  | 1326 | 30 | 30 |  | 10608 | 3.9932 | 1
- | Cafeteria 2 (Small) | 158 | 10 |  | 518 | 11 | 10 |  | 4144 | 2.2876 | 1
- | Cafeteria 3 (Main) | 662 | 44 |  | 1536 | 34 | 34 |  | 12288 | 3.2324 | 1
- | Conference Room | 55 | 3 |  | 254 | 5 | 3 |  | 2032 | 1.624 | 1
- | Counselors Office | 241 | 16 |  | 700 | 15 | 15 |  | 5600 | 2.5821 | 1
- | Dean's Office | 54 | 3 |  | 280 | 6 | 3 |  | 2240 | 1.4464 | 1
- | Gym | 606 | 40 |  | 2089 | 47 | 40 |  | 16712 | 2.1757 | 1
- | Lounge | 141 | 9 |  | 409 | 9 | 9 |  | 3272 | 2.5856 | 1
- | Main Office | 166 | 11 |  | 605 | 13 | 11 |  | 4840 | 2.0579 | 1
- | Music Assembly | 1020 | 68 |  | 2424 | 55 | 55 |  | 19392 | 3.1559 | 1
- | Nurse's Office | 44 | 2 |  | 247 | 5 | 2 |  | 1976 | 1.336 | 1
- | Principal's office | 109 | 7 |  | 280 | 6 | 6 |  | 2240 | 2.9196 | 1
- | Science Storage | 60 | 4 |  | 355 | 8 | 4 |  | 2840 | 1.2676 | 1
202 | - |  | 0 |  | 585 | 13 | 13 |  | 4680 | 0 | 0
203 | - |  | 0 |  | 527 | 11 | 11 |  | 4216 | 0 | 0
204 | - |  | 0 |  | 535 | 12 | 13 |  | 4280 | 0 | 0
209 | - |  | 0 |  | 535 | 12 | 13 |  | 4280 | 0 | 0
- | Roster Chair |  | 0 |  | 156 | 3 | 3 |  | 1248 | 0 | 0
306 | - |  | 0 |  | 900 | 20 | 20 |  | 7200 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | Henry W. Lawton Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 956 | 63 |  | 990 | 22 | 22 | UV | 7920 | 7.2424 | 2
102 | Classroom | 407 | 27 |  | 990 | 22 | 22 | UV | 7920 | 3.0833 | 1
103 | Classroom | 547 | 36 |  | 730 | 16 | 16 | UV | 5840 | 5.6199 | 2
104 | Classroom | 327 | 21 |  | 796 | 18 | 18 | UV | 6368 | 3.081 | 1
105 | Classroom | 464 | 30 |  | 730 | 16 | 16 | UV | 5840 | 4.7671 | 2
106 | Classroom | 432 | 28 |  | 796 | 18 | 18 | UV | 6368 | 4.0704 | 2
107 | Classroom | 376 | 25 |  | 730 | 16 | 16 | UV | 5840 | 3.863 | 1
108 | Classroom | 641 | 42 |  | 676 | 15 | 15 | UV | 5408 | 7.1117 | 2
109 | Classroom | 519 | 34 |  | 730 | 16 | 16 | UV | 5840 | 5.3322 | 2
110 | Classroom | 699 | 46 |  | 676 | 15 | 15 | UV | 5408 | 7.7552 | 2
111 | Classroom | 685 | 45 |  | 720 | 16 | 16 | UV | 5760 | 7.1354 | 2
112 | Classroom | 929 | 61 |  | 930 | 21 | 21 | UV | 7440 | 7.4919 | 2
113 | Classroom | 742 | 49 |  | 720 | 16 | 16 | UV | 5760 | 7.7292 | 2
114 | Classroom | 705 | 47 |  | 930 | 21 | 21 | UV | 7440 | 5.6855 | 2
115 | Classroom | 712 | 47 |  | 720 | 16 | 16 | UV | 5760 | 7.4167 | 2
117 | Classroom | 671 | 44 |  | 720 | 16 | 16 | UV | 5760 | 6.9896 | 2
119 | Classroom | 713 | 47 |  | 720 | 16 | 16 | UV | 5760 | 7.4271 | 2
121 | Classroom | 571 | 38 |  | 720 | 16 | 16 | UV | 5760 | 5.9479 | 2
123 | Classroom | 400 | 26 |  | 720 | 16 | 16 | UV | 5760 | 4.1667 | 2
201 | Classroom | 411 | 27 |  | 816 | 18 | 18 | UV | 6528 | 3.7776 | 1
202 | Classroom | 658 | 43 |  | 816 | 18 | 18 | UV | 6528 | 6.0478 | 2
203 | Classroom | 455 | 30 |  | 816 | 18 | 18 | UV | 6528 | 4.182 | 2
204 | Classroom | 790 | 52 |  | 816 | 18 | 18 | UV | 6528 | 7.261 | 2
205 | Classroom | 802 | 53 |  | 816 | 18 | 18 | UV | 6528 | 7.3713 | 2
206 | Classroom | 611 | 40 |  | 816 | 18 | 18 | UV | 6528 | 5.6158 | 2
207 | Classroom | 814 | 54 |  | 720 | 16 | 16 | UV | 5760 | 8.4792 | 2
208 | Classroom | 320 | 21 |  | 816 | 18 | 18 | UV | 6528 | 2.9412 | 1
209 | Classroom | 653 | 43 |  | 720 | 16 | 16 | UV | 5760 | 6.8021 | 2
211 | Classroom | 707 | 47 |  | 720 | 16 | 16 | UV | 5760 | 7.3646 | 2
213 | Classroom | 649 | 43 |  | 720 | 16 | 16 | UV | 5760 | 6.7604 | 2
214 | Classroom | 289 | 19 |  | 540 | 12 | 12 | UV | 4320 | 4.0139 | 2
215 | Classroom | 730 | 48 |  | 720 | 16 | 16 | UV | 5760 | 7.6042 | 2
216 | Classroom | 332 | 22 |  | 768 | 17 | 17 | UV | 6144 | 3.2422 | 1
217 | Classroom | 364 | 24 |  | 720 | 16 | 16 | UV | 5760 | 3.7917 | 1
218 | Classroom | 716 | 47 |  | 676 | 15 | 15 | UV | 5408 | 7.9438 | 2
219 | Classroom | 672 | 44 |  | 720 | 16 | 16 | UV | 5760 | 7 | 2
220 | Classroom | 639 | 42 |  | 676 | 15 | 15 | UV | 5408 | 7.0895 | 2
222 | Classroom | 683 | 45 |  | 540 | 12 | 12 | UV | 4320 | 9.4861 | 2
224 | Classroom | 633 | 42 |  | 720 | 16 | 16 | UV | 5760 | 6.5938 | 2
226 | Classroom | 1102 | 73 |  | 540 | 12 | 12 | UV | 4320 | 15.3056 | 3
- | Art (Large) | 477 | 31 |  | 1258 | 28 | 28 | UV | 10064 | 2.8438 | 1
- | Cafeteria | 632 | 42 |  | 2310 | 52 | 42 | AHU | 18480 | 2.0519 | 1
- | Computer | 886 | 59 |  | 1440 | 32 | 32 | UV | 11520 | 4.6146 | 2
- | IMC | 426 | 28 |  | 2620 | 59 | 28 | UV | 20960 | 1.2195 | 1
- | Main Office | 232 | 15 |  | 275 | 6 | 6 | UV | 2200 | 6.3273 | 2
- | Nurse's Office | 283 | 18 |  | 363 | 8 | 8 | UV | 2904 | 5.8471 | 2
- | Science (Large) | 375 | 25 |  | 1088 | 24 | 24 | UV | 8704 | 2.585 | 1
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | Henry C. Lea Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Chadwick | Devine Part 2 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
L1 | Classroom | 166 | 11 |  | 696 | 15 | 11 | UV | 5568 | 1.7888 | 1
L3 | Classroom | 0 | 0 |  | 624 | 14 | 0 | UV | 4992 | 0 | 0
L4 | Classroom | 191 | 12 |  | 696 | 15 | 12 | UV | 5568 | 2.0582 | 1
L5 | Classroom | 208 | 13 |  | 864 | 19 | 13 | UV | 6912 | 1.8056 | 1
L7 | Classroom | 247 | 16 |  | 768 | 17 | 16 | UV | 6144 | 2.4121 | 1
B2 | Classroom |  | 0 | Yes | 1457 | 33 | 33 |  | 11656 | 0 | 0
101 | Classroom | 312 | 20 |  | 1225 | 27 | 20 | UV | 9800 | 1.9102 | 1
102 | Classroom | 319 | 21 |  | 1295 | 29 | 21 | UV | 10360 | 1.8475 | 1
103 | Classroom | 284 | 18 |  | 810 | 18 | 18 | AHU | 6480 | 2.6296 | 1
105 | Classroom | 287 | 19 |  | 840 | 19 | 19 | AHU | 6720 | 2.5625 | 1
106 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
107 | Classroom | 289 | 19 |  | 840 | 19 | 19 | AHU | 6720 | 2.5804 | 1
108 | Classroom | 301 | 20 |  | 840 | 19 | 19 | AHU | 6720 | 2.6875 | 1
109 | Classroom | 295 | 19 |  | 840 | 19 | 19 | AHU | 6720 | 2.6339 | 1
110 | Classroom | 298 | 19 |  | 840 | 19 | 19 | AHU | 6720 | 2.6607 | 1
111 | Classroom | 289 | 19 |  | 840 | 19 | 19 | AHU | 6720 | 2.5804 | 1
125 | Counselor's Office |  | 0 | Yes | 126 | 2 | 2 |  | 1008 | 0 | 0
127 | Classroom |  | 0 | Yes | 126 | 2 | 2 |  | 1008 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 1015 | 23 | 23 | UV | 8120 | 0 | 0
202 | Classroom | 0 | 0 | Yes | 980 | 22 | 22 | UV | 7840 | 0 | 0
203 | Classroom |  | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
204 | Classroom |  | 0 | Yes | 840 | 19 | 19 |  | 6720 | 0 | 0
204a | Classroom | 0 | 0 | Yes | 252 | 5 | 5 | AHU | 2016 | 0 | 0
205 | Classroom | 0 | 0 | Yes | 810 | 18 | 18 | AHU | 6480 | 0 | 0
206 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | AHU | 6960 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
208 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
209 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
210 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
211 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
212 | Classroom | 0 | 0 | Yes | 212 | 4 | 4 | AHU | 1696 | 0 | 0
301/302 | Library | 380 | 25 | Yes | 5400 | 122 | 122 | UV | 43200 | 0.52778 | 0
303 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
304 | Classroom | 0 | 0 | Yes | 690 | 15 | 15 | AHU | 5520 | 0 | 0
304A | Room |  | 0 | Yes | 266 | 6 | 6 |  | 2128 | 0 | 0
306 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
307 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
308 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
309 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
310 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
311 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
312 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0
313 | Classroom | 0 | 0 |  | 840 | 19 | 0 | AHU | 6720 | 0 | 0
- | Auditorium | 0 | 0 |  | 2296 | 52 | 0 | AHU | 18368 | 0 | 0
- | Side Cafeteria | 490 | 32 | Yes | 1800 | 40 | 40 | AHU | 14400 | 2.0417 | 1
- | Front Cafeteria | 352 | 23 | Yes | 1560 | 35 | 35 | AHU | 12480 | 1.6923 | 1
- | Computer Lab | 276 | 18 |  | 1456 | 33 | 18 | AHU | 11648 | 1.4217 | 1
- | Corridor | 156 | 10 |  | 650 | 14 | 10 | UV | 5200 | 1.8 | 1
- | Gym | 0 | 0 | Yes | 3950 | 89 | 89 | AHU | 31600 | 0 | 0
- | Main Office | 212 | 14 |  | 460 | 10 | 10 | AHU | 3680 | 3.4565 | 1
- | Nurse's Bathroom | 0 | 0 |  | 28 | 0 | 0 | AHU | 224 | 0 | 0
- | Nurse's Office |  | 0 | Yes | 168 | 3 | 3 | AHU | 1344 | 0 | 0
- | Nurse's Exam Room |  | 0 |  | 88 | 2 | 0 | AHU | 704 | 0 | 0
- | Office Bathroom | 0 | 0 |  | 25 | 0 | 0 | AHU | 200 | 0 | 0
- | Principal's Office | 0 | 0 | Yes | 160 | 3 | 3 | UV | 1280 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-22 | [7 empty] | 0 | 0 | 0
School: | Amy Northwest @ Levering Middle School | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom |  | 0 |  | 750 | 17 | 0 |  | 6000 | 0 | 0
103 | Classroom |  | 0 | Yes | 725 | 16 | 16 |  | 5800 | 0 | 0
106 | Nurse Office |  | 0 | Yes | 668 | 15 | 15 |  | 5344 | 0 | 0
107 | Classroom |  | 0 |  | 666 | 15 | 0 |  | 5328 | 0 | 0
109 | IMC |  | 0 | Yes | 1457 | 33 | 33 |  | 11656 | 0 | 0
203 | Classroom |  | 0 | Yes | 675 | 15 | 15 |  | 5400 | 0 | 0
204 | Classroom |  | 0 | Yes | 683 | 15 | 15 |  | 5464 | 0 | 0
205 | Classroom |  | 0 | Yes | 663 | 15 | 15 |  | 5304 | 0 | 0
206 | Classroom |  | 0 |  | 691 | 15 | 0 |  | 5528 | 0 | 0
207 | Classroom |  | 0 |  | 672 | 15 | 0 |  | 5376 | 0 | 0
209 | Classroom |  | 0 | Yes | 685 | 15 | 15 |  | 5480 | 0 | 0
210 | Classroom |  | 0 |  | 677 | 15 | 0 |  | 5416 | 0 | 0
303/304 | Classroom |  | 0 | Yes | 1253 | 28 | 28 |  | 10024 | 0 | 0
305 | Classroom |  | 0 | Yes | 675 | 15 | 15 |  | 5400 | 0 | 0
306 | Classroom |  | 0 | Yes | 692 | 15 | 15 |  | 5536 | 0 | 0
307 | Classroom |  | 0 | Yes | 670 | 15 | 15 |  | 5360 | 0 | 0
310 | Classroom |  | 0 |  | 1065 | 24 | 0 |  | 8520 | 0 | 0
Annex 1 | Classroom |  | 0 | Yes | 733 | 16 | 16 |  | 5864 | 0 | 0
Annex 2 | Classroom |  | 0 | Yes | 709 | 16 | 16 |  | 5672 | 0 | 0
Annex 3 | Classroom |  | 0 |  | 730 | 16 | 0 |  | 5840 | 0 | 0
Annex 4 | Classroom |  | 0 | Yes | 707 | 16 | 16 |  | 5656 | 0 | 0
Annex 5 | Classroom |  | 0 | Yes | 723 | 16 | 16 |  | 5784 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-01 | [7 empty] | 0 | 0 | 0
School: | Abraham Lincoln High School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | EMCOR Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
2 | Room 2 Office | 93 | 6 |  | 576 | 13 | 6 | AHU #7 | 4608 | 1.2109 | 1
3 | Room 3 Storage | 99 | 6 |  | 576 | 13 | 6 | AHU #8 | 4608 | 1.2891 | 1
4 | Room 4 Electrical | 103 | 6 |  | 576 | 13 | 6 | AHU #9 | 4608 | 1.3411 | 1
5 | Room 5 Kitchen | 461 | 30 |  | 576 | 13 | 13 | AHU #10 | 4608 | 6.0026 | 2
6 | Child Care | 1116 | 74 |  | 576 | 13 | 13 | AHU #11 | 4608 | 14.5312 | 3
8 | Child Care | 2029 | 135 |  | 1665 | 37 | 37 | AHU #12 | 13320 | 9.1396 | 2
100 | Classroom | 760 | 50 |  | 363 | 8 | 8 | UV1+UV2+AHU-2 | 2904 | 15.7025 | 3
100A | Classroom | 615 | 41 |  |  | 0 | 0 | UV+AHU-2 | 0 | 0 | 0
101 | Classroom | 1715 | 114 |  | 1247 | 28 | 28 | UV1+UV2+AHU-2 | 9976 | 10.3148 | 3
102 | Classroom | 1244 | 82 |  | 130 | 2 | 2 | UV+AHU-2 | 1040 | 71.7692 | 5
102A | Office | 25 | 1 |  | 140 | 3 | 1 | AHU-2 | 1120 | 1.3393 | 1
102B | Office | 35 | 2 |  | 107 | 2 | 2 | AHU-2 | 856 | 2.4533 | 1
103 | Classroom | 1636 | 109 |  | 1410 | 32 | 32 | UV1+UV2+AHU-2 | 11280 | 8.7021 | 2
104 | Classroom | 1067 | 71 |  | 806 | 18 | 18 | UV1+UV2+AHU-2 | 6448 | 9.9287 | 2
105 | Classroom | 1322 | 88 |  | 1140 | 25 | 25 | UV1+UV2+AHU-2 | 9120 | 8.6974 | 2
106 | Classroom | 1182 | 78 |  | 957 | 21 | 21 | UV1+UV2+AHU-2 | 7656 | 9.2633 | 2
107 | Classroom | 1894 | 126 |  | 1426 | 32 | 32 | UV1+UV2+AHU-2 | 11408 | 9.9614 | 2
107A | Storage Room | 300 | 20 |  |  | 0 | 0 | AHU-1 | 0 | 0 | 0
108 | Classroom | 1212 | 80 |  | 899 | 20 | 20 | UV1+UV2+AHU-2 | 7192 | 10.1112 | 3
109 | 109 OFFICE | 144 | 9 |  | 99 | 2 | 2 | AHU-2 / FC | 792 | 10.9091 | 3
110 | Classroom | 1159 | 77 |  | 868 | 19 | 19 | UV1+UV2+AHU-1 | 6944 | 10.0144 | 3
111 | Classroom | 1827 | 121 |  | 1426 | 32 | 32 | UV1+UV2+AHU-1 | 11408 | 9.609 | 2
112 | Classroom | 990 | 66 |  | 868 | 19 | 19 | UV1+UV2+AHU-1 | 6944 | 8.5541 | 2
114 | Classroom | 1114 | 74 |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 6696 | 9.9821 | 2
116 | Classroom | 663 | 44 |  | 896 | 20 | 20 | UV1+UV2+AHU-1 | 7168 | 5.5497 | 2
118 | Classroom | 932 | 62 |  | 1748 | 39 | 39 | UV1+UV2+AHU-1 | 13984 | 3.9989 | 1
120 | Classroom | 1141 | 76 |  | 864 | 19 | 19 | UV1+UV2+AHU-1 | 6912 | 9.9045 | 2
121 | Classroom | 1025 | 68 |  | 945 | 21 | 21 | UV1+UV2+AHU-1 | 7560 | 8.1349 | 2
122 | Classroom | 941 | 62 |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 6696 | 8.4319 | 2
123 | Classroom | 1848 | 123 |  | 2208 | 50 | 50 | UV1+UV2+UV1+UV2+AHU-1 | 17664 | 6.2772 | 2
124 | Classroom | 865 | 57 |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 6696 | 7.7509 | 2
125 | Classroom | 984 | 65 |  | 888 | 20 | 20 | UV1+UV2+AHU-1 | 7104 | 8.3108 | 2
126 | Classroom | 843 | 56 |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 6696 | 7.5538 | 2
128 | Classroom | 598 | 39 |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 6696 | 5.3584 | 2
129 | Classroom | 740 | 49 |  | 890 | 20 | 20 | UV1+UV2+AHU-1 | 7120 | 6.236 | 2
130 | Security | 0 | 0 |  | 108 | 2 | 0 | AHU-4 | 864 | 0 | 0
131 | Police | 0 | 0 |  | 180 | 4 | 0 | AHU-4 | 1440 | 0 | 0
132 | Classroom | 728 | 48 |  |  | 0 | 0 | UV1+UV2+UV3+UV4 | 0 | 0 | 0
133a | book room | 0 | 0 |  |  | 0 | 0 | AHU-4 | 0 | 0 | 0
135 | Classroom | 0 | 0 |  | 840 | 19 | 0 | UV1+UV2 | 6720 | 0 | 0
136 | office | 0 | 0 |  | 140 | 3 | 0 | AHU-4 | 1120 | 0 | 0
136a | storage | 0 | 0 |  |  | 0 | 0 | AHU-4 | 0 | 0 | 0
137 | storage | 0 | 0 |  |  | 0 | 0 | AHU-4 | 0 | 0 | 0
137a | storage | 0 | 0 |  |  | 0 | 0 | AHU-4 | 0 | 0 | 0
139 | office | 0 | 0 |  | 74.75 | 1 | 0 | AHU-4 | 598 | 0 | 0
140 | Main Office and waiting | 0 | 0 |  | 338 | 7 | 0 | AHU-4 | 2704 | 0 | 0
141 | Office | 0 | 0 |  |  | 0 | 0 | AHU-4 | 0 | 0 | 0
142 | Office | 0 | 0 |  |  | 0 | 0 | AHU-4 | 0 | 0 | 0
143 | Office | 0 | 0 |  | 99 | 2 | 0 | AHU-4 | 792 | 0 | 0
144 | Office | 0 | 0 |  | 105 | 2 | 0 | AHU-4 | 840 | 0 | 0
145 | Office | 0 | 0 |  | 110 | 2 | 0 | AHU-4 | 880 | 0 | 0
146 | Work Room | 0 | 0 |  | 636 | 14 | 0 | AHU-4 | 5088 | 0 | 0
147 | Conference | 0 | 0 |  | 192 | 4 | 0 | AHU-4 | 1536 | 0 | 0
147A | records | 0 | 0 |  | 300 | 6 | 0 | AHU-4 | 2400 | 0 | 0
149 | Health Suite | 0 | 0 |  | 495 | 11 | 0 | AHU-4 | 3960 | 0 | 0
149a | Exam | 0 | 0 |  | 188 | 4 | 0 | AHU-4 | 1504 | 0 | 0
149b | Exam | 0 | 0 |  | 197 | 4 | 0 | AHU-4 | 1576 | 0 | 0
149c | Office | 0 | 0 |  | 197 | 4 | 0 | AHU-4 | 1576 | 0 | 0
149D | Office | 0 | 0 |  | 109 | 2 | 0 | AHU-4 | 872 | 0 | 0
149E | Meditation | 0 | 0 |  | 209 | 4 | 0 | AHU-4 | 1672 | 0 | 0
150 | office | 0 | 0 |  | 117 | 2 | 0 | AHU-4 | 936 | 0 | 0
151 | copy center | 0 | 0 |  | 418 | 9 | 0 | AHU-4 | 3344 | 0 | 0
154 | office | 0 | 0 |  | 117 | 2 | 0 | AHU-4 | 936 | 0 | 0
155 | office | 0 | 0 |  | 121 | 2 | 0 | AHU-4 | 968 | 0 | 0
156 | work room | 0 | 0 |  | 875 | 19 | 0 | AHU-4 | 7000 | 0 | 0
157 | Records | 0 | 0 |  | 96 | 2 | 0 | AHU-4 | 768 | 0 | 0
158 | Roster Room | 0 | 0 |  | 143 | 3 | 0 | AHU-4 | 1144 | 0 | 0
159 | Office | 0 | 0 |  | 96 | 2 | 0 | AHU-4 | 768 | 0 | 0
160 | Classroom | 1346 | 89 |  | 1428 | 32 | 32 | UV1+UV2+AHU-3 | 11424 | 7.0693 | 2
160's | Men's Staff Restroom | 740 | 49 |  |  | 0 | 0 | AHU-3 | 0 | 0 | 0
160's | Women's Staff Restroom | 685 | 45 |  |  | 0 | 0 | AHU-3 | 0 | 0 | 0
160A | Science Prep | 423 | 28 |  | 891 | 20 | 20 | AHU-3 | 7128 | 3.5606 | 1
161 | Classroom | 829 | 55 |  | 891 | 20 | 20 | UV1+UV2+AHU-3 | 7128 | 6.9781 | 2
162 | Classroom | 1327 | 88 |  | 688 | 15 | 15 | UV1+UV2+AHU-3 | 5504 | 14.4658 | 3
163 | Classroom | 895 | 59 |  | 868 | 19 | 19 | UV1+UV2+AHU-3 | 6944 | 7.7333 | 2
164 | Classroom | 1334 | 88 |  | 1419 | 32 | 32 | UV1+UV2+AHU-3 | 11352 | 7.0507 | 2
164a | Science Prep | 44 | 2 |  |  | 0 | 0 | AHU-3 | 0 | 0 | 0
165 | Classroom | 942 | 62 |  | 868 | 19 | 19 | UV1+UV2+AHU-3 | 6944 | 8.1394 | 2
166 | Classroom | 1071 | 71 |  | 1155 | 26 | 26 | UV1+UV2+AHU-3 | 9240 | 6.9545 | 2
167 | Classroom | 458 | 30 |  | 918 | 20 | 20 | UV1+UV2+AHU-3 | 7344 | 3.7418 | 1
168 | Classroom | 1150 | 76 |  | 868 | 19 | 19 | UV1+UV2+AHU-3 | 6944 | 9.9366 | 2
169 | Classroom | 684 | 45 |  | 952 | 21 | 21 | UV1+UV2+AHU-3 | 7616 | 5.3887 | 2
170 | Classroom | 787 | 52 |  | 891 | 20 | 20 | UV+UV+AHU-3 | 7128 | 6.6246 | 2
171 | Classroom | 1006 | 67 |  | 918 | 20 | 20 | UV1+UV2+AHU-3 | 7344 | 8.219 | 2
172 | Classroom | 994 | 66 |  | 891 | 20 | 20 | UV1+UV2+AHU-3 | 7128 | 8.367 | 2
173 | Classroom | 565 | 37 |  | 891 | 20 | 20 | AHU-3 | 7128 | 4.7559 | 2
174 | Classroom | 736 | 49 |  | 896 | 20 | 20 | UV1+UV2+AHU-3 | 7168 | 6.1607 | 2
175 | Classroom | 1415 | 94 |  | 891 | 20 | 20 | UV1+UV2+AHU-3 | 7128 | 11.9108 | 3
176 | Classroom | 903 | 60 |  | 800 | 18 | 18 | UV1+UV2+AHU-3 | 6400 | 8.4656 | 2
177 | Classroom | 867 | 57 |  | 918 | 20 | 20 | UV1+UV2+AHU-3 | 7344 | 7.0833 | 2
190 | Music Classroom | 1656 | 110 |  | 1395 | 31 | 31 | AHU-8 | 11160 | 8.9032 | 2
190 | Office | 82 | 5 |  | 225 | 5 | 5 | AHU-8 | 1800 | 2.7333 | 1
190 | Storage | 52 | 3 |  | 1716 | 39 | 3 | AHU-8 | 13728 | 0.22727 | 0
190A | Classroom | 315 | 21 |  | 90 | 2 | 2 | AHU-8 | 720 | 26.25 | 4
190D | Classroom | 166 | 11 |  | 623 | 14 | 11 | AHU-8 | 4984 | 1.9984 | 1
190E | Classroom | 191 | 12 |  | 336 | 7 | 7 | AHU-8 | 2688 | 4.2634 | 2
191 | Music Classroom | 1393 | 92 |  | 2100 | 47 | 47 | AHU-8 | 16800 | 4.975 | 2
191A | Classroom | 68 | 4 |  | 56 | 1 | 1 | AHU-8 | 448 | 9.1071 | 2
191B | Classroom | 72 | 4 |  | 90 | 2 | 2 | AHU-8 | 720 | 6 | 2
191C | Classroom | 83 | 5 |  | 90 | 2 | 2 | AHU-8 | 720 | 6.9167 | 2
192 | Classroom | 998 | 66 |  | 1189 | 27 | 27 | AHU-8 | 9512 | 6.2952 | 2
200 | Classroom | 1117 | 74 |  | 1240 | 28 | 28 | UV1+UV2+AHU-2 | 9920 | 6.756 | 2
201 | Classroom | 1325 | 88 |  | 1485 | 33 | 33 | UV1+UV2+AHU-2 | 11880 | 6.6919 | 2
201A | Science Prep | 255 | 17 |  | 1486 | 33 | 17 | AHU-2 | 11888 | 1.287 | 1
202 | Classroom | 1325 | 88 |  | 2270 | 51 | 51 | UV1+UV2+UV3+AHU-2 | 18160 | 4.3778 | 2
202A | Office | 44 | 2 |  | 99 | 2 | 2 | AHU-2 | 792 | 3.3333 | 1
203 | Classroom | 1339 | 89 |  | 1575 | 35 | 35 | UV1+UV2+AHU-2 | 12600 | 6.3762 | 2
204 | Classroom | 403 | 26 |  | 806 | 18 | 18 | UV1+UV2+AHU-2 | 6448 | 3.75 | 1
205 | Classroom | 652 | 43 |  | 1395 | 31 | 31 | UV1+UV2+AHU-2 | 11160 | 3.5054 | 1
206 | Office Suite toilet |  | 0 |  | 1254 | 28 | 0 | AHU-2 | 10032 | 0 | 0
207 | Classroom | 1006 | 67 |  | 891 | 20 | 20 | UV1+UV2+AHU-2 | 7128 | 8.468 | 2
208 | Classroom | 759 | 50 |  | 1152 | 26 | 26 | UV1+UV2+AHU-2 | 9216 | 4.9414 | 2
209 | Classroom | 419 | 27 |  | 864 | 19 | 19 | UV1+UV2+AHU-2 | 6912 | 3.6372 | 1
210 | Classroom | 614 | 40 |  | 837 | 19 | 19 | UV1+UV2+AHU-2 | 6696 | 5.5018 | 2
211 | Classroom | 994 | 66 |  | 390 | 8 | 8 | UV1+UV2+AHU-1 | 3120 | 19.1154 | 3
212 | Classroom | 615 | 41 |  | 858 | 19 | 19 | UV1+UV2+AHU-2 | 6864 | 5.3759 | 2
213 | Classroom | 995 | 66 |  | 891 | 20 | 20 | UV1+UV2+AHU-1 | 7128 | 8.3754 | 2
214 | Classroom | 625 | 41 |  | 924 | 21 | 21 | UV1+UV2+AHU-1 | 7392 | 5.0731 | 2
216 | Classroom | 564 | 37 |  | 918 | 20 | 20 | UV1+UV2+AHU-1 | 7344 | 4.6078 | 2
218 | Classroom | 729 | 48 |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 6696 | 6.5323 | 2
220 | Classroom | 1242 | 82 |  | 1395 | 31 | 31 | UV1+UV2+AHU-1 | 11160 | 6.6774 | 2
221 | Classroom | 653 | 43 |  | 924 | 21 | 21 | UV1+UV2+AHU-1 | 7392 | 5.3003 | 2
222 | Classroom | 909 | 60 |  | 891 | 20 | 20 | UV1+UV2+AHU-1 | 7128 | 7.6515 | 2
223 | Classroom | 848 | 56 |  | 864 | 19 | 19 | UV1+UV2+AHU-1 | 6912 | 7.3611 | 2
224 | Classroom | 2035 | 135 |  | 1972 | 44 | 44 | UV1+UV2+UV3+UV4+AHU-1 | 15776 | 7.7396 | 2
224A | Office | 96 | 6 |  | 121 | 2 | 2 | AHU-1 | 968 | 5.9504 | 2
225 | Classroom | 639 | 42 |  | 918 | 20 | 20 | UV1+UV2+AHU-1 | 7344 | 5.2206 | 2
226 | Classroom | 1282 | 85 |  | 1870 | 42 | 42 | UV1+UV2+UV3+UV4+AHU-1 | 14960 | 5.1417 | 2
226A | Office | 41 | 2 |  | 123 | 2 | 2 | AHU-1 | 984 | 2.5 | 1
227 | Classroom | 825 | 55 |  | 891 | 20 | 20 | UV1+UV2+AHU-1 | 7128 | 6.9444 | 2
228 | Classroom | 551 | 36 |  | 924 | 21 | 21 | UV1+UV2+AHU-1 | 7392 | 4.4724 | 2
229 | Classroom | 800 | 53 |  | 878 | 19 | 19 | UV1+UV2+AHU-1 | 7024 | 6.8337 | 2
- | 2nd floor Corridor | 1498 | 99 |  |  | 0 | 0 | AHU-1 | 0 | 0 | 0
- | Gym | 40145 | 2676 |  | 18327 | 416 | 416 | AHU-9+AHU-10 | 146616 | 16.4286 | 3
- | 2nd Floor B Corridor | 543 | 36 |  |  | 0 | 0 | AHU-2 | 0 | 0 | 0
- | 2nd Floor Staff toilet |  | 0 |  |  | 0 | 0 | AHU-2 | 0 | 0 | 0
- | Auditorium | 16961 | 1130 |  | 6745 | 153 | 153 | AHU-6 | 53960 | 18.8595 | 3
- | Small Gym | 0 | 0 |  | 6438 | 146 | 0 | AHU-11 | 51504 | 0 | 0
- | Weight Room | 0 | 0 |  | 2450 | 55 | 0 | AHU-12 | 19600 | 0 | 0
- | Counselor Center | 0 | 0 |  |  | 0 | 0 | AHU-4 | 0 | 0 | 0
- | Child Care- Hallway | 240 | 16 |  |  | 0 | 0 | AHU #13 | 0 | 0 | 0
- | Child Care- Kitchen | 47 | 3 |  | 330 | 7 | 3 | AHU-7 | 2640 | 1.0682 | 1
- | Child Care- Lending Library | 96 | 6 | Yes | 1184 | 26 | 26 | AHU-7 | 9472 | 0.60811 | 0
- | Library/IMC | 1522 | 101 |  | 8640 | 196 | 101 | AHU #14 | 69120 | 1.3212 | 1
- | Child Care Office | 9 | 0 |  | 99 | 2 | 0 | AHU-7 | 792 | 0.68182 | 0
- | Admin 140's Area Corridor | 0 | 0 |  | 375 | 8 | 0 | AHU-4 | 3000 | 0 | 0
- | Gym Office |  | 0 |  | 343 | 7 | 0 |  | 2744 | 0 | 0
- | Gym office 2 |  | 0 |  | 280 | 6 | 0 |  | 2240 | 0 | 0
- | Gym office 3 |  | 0 |  | 260 | 5 | 0 |  | 2080 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-12 | [7 empty] | 0 | 0 | 0
School: | Lingelbach Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Part 2 | Part 3 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 227 | 15 |  | 968 | 22 | 15 | UV | 7744 | 1.7588 | 1
102 | Classroom | 477 | 31 |  | 968 | 22 | 22 | UV | 7744 | 3.6958 | 1
103 | Classroom | 219 | 14 |  | 889 | 20 | 14 | UV | 7112 | 1.8476 | 1
104 | Classroom | 0 | 0 |  | 963 | 21 | 0 | UV | 7704 | 0 | 0
105 | Classroom | 268 | 17 |  | 941 | 21 | 17 | UV | 7528 | 2.136 | 1
106 | Classroom | 293 | 19 |  | 971 | 22 | 19 | UV | 7768 | 2.2631 | 1
200 | Classroom | 444 | 29 |  | 1394 | 31 | 29 | UV | 11152 | 2.3888 | 1
200A | Classroom | 675 | 45 |  | 1235 | 28 | 28 | UV | 9880 | 4.0992 | 2
201 | Classroom | 514 | 34 |  | 969 | 22 | 22 | UV | 7752 | 3.9783 | 1
202 | Classroom | 280 | 18 |  | 969 | 22 | 18 | UV | 7752 | 2.1672 | 1
203 | Classroom | 278 | 18 |  | 971 | 22 | 18 | UV | 7768 | 2.1473 | 1
204 | Classroom | 290 | 19 |  | 971 | 22 | 19 | UV | 7768 | 2.24 | 1
205 | Classroom | 336 | 22 |  | 955 | 21 | 21 | UV | 7640 | 2.6387 | 1
206 | Classroom | 278 | 18 |  | 969 | 22 | 18 | UV | 7752 | 2.1517 | 1
301 | Classroom | 285 | 19 |  | 940 | 21 | 19 | UV | 7520 | 2.2739 | 1
302 | Classroom | 795 | 53 |  | 937 | 21 | 21 | UV | 7496 | 6.3634 | 2
303 | Classroom | 837 | 55 |  | 933 | 21 | 21 | UV | 7464 | 6.7283 | 2
303A | Classroom | 357 | 23 |  | 463 | 10 | 10 | UV | 3704 | 5.7829 | 2
304 | Classroom | 406 | 27 |  | 464 | 10 | 10 | UV | 3712 | 6.5625 | 2
305 | Classroom | 395 | 26 |  | 967 | 21 | 21 | UV | 7736 | 3.0636 | 1
306 | Classroom | 906 | 60 |  | 944 | 21 | 21 | UV | 7552 | 7.1981 | 2
- | Main Office |  | 0 | Yes | 332 | 7 | 7 |  | 2656 | 0 | 0
- | Principals Office |  | 0 | Yes | 262 | 5 | 5 |  | 2096 | 0 | 0
- | Nurses Office |  | 0 | Yes | 269 | 6 | 6 |  | 2152 | 0 | 0
- | Auditorium | 841 | 56 |  | 2847 | 64 | 56 | AHU | 22776 | 2.2155 | 1
- | Gym/Cafeteria | 1451 | 96 |  | 2340 | 53 | 53 | AHU | 18720 | 4.6506 | 2
- | North Stairwell | 0 | 0 |  | 168 | 3 | 0 | UV | 1344 | 0 | 0
- | South Stairwell | 0 | 0 |  | 168 | 3 | 0 | UV | 1344 | 0 | 0
- | Library | 855 | 57 |  | 2312 | 52 | 52 | UV | 18496 | 2.7736 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-05 | [7 empty] | 0 | 0 | 0
School: | Alain Locke Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Brothers Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Auditorium | 2700 | 180 |  | 3658 | 83 | 83 | AHU | 29264 | 5.5358 | 2
- | Gym/Cafeteria | 2014 | 134 |  | 4464 | 101 | 101 | AHU | 35712 | 3.3837 | 1
- | Library | 585 | 39 |  | 1352 | 30 | 30 | UV | 10816 | 3.2452 | 1
- | Main Office | 425 | 28 |  | 1213 | 27 | 27 | UV | 9704 | 2.6278 | 1
- | Principals Office | 0 | 0 | Yes | 384 | 8 | 8 | UV | 3072 | 0 | 0
100 | Classroom | 421 | 28 |  | 840 | 19 | 19 | UV | 6720 | 3.7589 | 1
101 | Classroom | 454 | 30 |  | 840 | 19 | 19 | UV | 6720 | 4.0536 | 2
102 | Classroom | 425 | 28 |  | 864 | 19 | 19 | UV | 6912 | 3.6892 | 1
103 | Classroom | 318 | 21 |  | 432 | 9 | 9 | UV | 3456 | 5.5208 | 2
104 | Classroom | 405 | 27 |  | 744 | 16 | 16 | UV | 5952 | 4.0827 | 2
105 | Classroom | 453 | 30 |  | 840 | 19 | 19 | UV | 6720 | 4.0446 | 2
107 | Classroom | 435 | 29 |  | 1064 | 24 | 24 | UV | 8512 | 3.0663 | 1
108A | Office A Library |  | 0 | Yes | 156 | 3 | 3 |  | 1248 | 0 | 0
108B | Office B Library |  | 0 | Yes | 156 | 3 | 3 |  | 1248 | 0 | 0
109 | Classroom | 428 | 28 |  | 864 | 19 | 19 | UV | 6912 | 3.7153 | 1
111 | Classroom | 394 | 26 |  | 840 | 19 | 19 | UV | 6720 | 3.5179 | 1
112 | Classroom | 330 | 22 |  | 840 | 19 | 19 | UV | 6720 | 2.9464 | 1
113 | Classroom | 416 | 27 |  | 980 | 22 | 22 | UV | 7840 | 3.1837 | 1
115 | Classroom | 393 | 26 |  | 1248 | 28 | 26 | UV | 9984 | 2.3618 | 1
116A | Counselor Office |  | 0 | Yes | 132 | 3 | 3 |  | 1056 | 0 | 0
116B | COVID Quarantine |  | 0 | Yes | 132 | 3 | 3 |  | 1056 | 0 | 0
117 | Classroom | 321 | 21 |  | 1440 | 32 | 21 | UV | 11520 | 1.6719 | 1
200 | Classroom | 592 | 39 |  | 875 | 19 | 19 | UV | 7000 | 5.0743 | 2
201 | Classroom | 340 | 22 |  | 864 | 19 | 19 | UV | 6912 | 2.9514 | 1
202 | Classroom | 341 | 22 |  | 875 | 19 | 19 | UV | 7000 | 2.9229 | 1
203 | Classroom | 485 | 32 |  | 864 | 19 | 19 | UV | 6912 | 4.2101 | 2
204 | Classroom | 279 | 18 |  | 875 | 19 | 18 | UV | 7000 | 2.3914 | 1
205 | Classroom | 295 | 19 |  | 864 | 19 | 19 | UV | 6912 | 2.5608 | 1
207A | Classroom | 0 | 0 | Yes | 168 | 3 | 3 | UV | 1344 | 0 | 0
207B | Classroom | 300 | 20 |  | 336 | 7 | 7 | UV | 2688 | 6.6964 | 2
208 | Classroom | 349 | 23 |  | 1225 | 27 | 23 | UV | 9800 | 2.1367 | 1
209 | Classroom | 348 | 23 |  | 864 | 19 | 19 | UV | 6912 | 3.0208 | 1
210 | Classroom | 295 | 19 |  | 480 | 10 | 10 | UV | 3840 | 4.6094 | 2
211 | Classroom | 360 | 24 |  | 864 | 19 | 19 | UV | 6912 | 3.125 | 1
212 | Classroom | 332 | 22 |  | 840 | 19 | 19 | UV | 6720 | 2.9643 | 1
213 | Classroom | 297 | 19 |  | 875 | 19 | 19 | UV | 7000 | 2.5457 | 1
300 | Classroom | 419 | 27 |  | 840 | 19 | 19 | UV | 6720 | 3.7411 | 1
301 | Classroom | 416 | 27 |  | 840 | 19 | 19 | UV | 6720 | 3.7143 | 1
302 | Classroom | 375 | 25 |  | 840 | 19 | 19 | UV | 6720 | 3.3482 | 1
303 | Classroom | 395 | 26 |  | 840 | 19 | 19 | UV | 6720 | 3.5268 | 1
304 | Classroom | 398 | 26 |  | 840 | 19 | 19 | UV | 6720 | 3.5536 | 1
305 | Classroom | 411 | 27 |  | 840 | 19 | 19 | UV | 6720 | 3.6696 | 1
307A | Office | 205 | 13 |  | 336 | 7 | 7 | UV | 2688 | 4.5759 | 2
307B | Office | 0 | 0 | Yes | 168 | 3 | 3 | UV | 1344 | 0 | 0
308 | Classroom | 383 | 25 |  | 864 | 19 | 19 | UV | 6912 | 3.3247 | 1
309 | Classroom | 365 | 24 |  | 840 | 19 | 19 | UV | 6720 | 3.2589 | 1
310 | Classroom | 325 | 21 |  | 875 | 19 | 19 | UV | 7000 | 2.7857 | 1
311 | Classroom | 309 | 20 |  | 840 | 19 | 19 | UV | 6720 | 2.7589 | 1
312 | Classroom | 419 | 27 |  | 840 | 19 | 19 | UV | 6720 | 3.7411 | 1
313 | Classroom | 346 | 23 |  | 840 | 19 | 19 | UV | 6720 | 3.0893 | 1
- | Nurses office |  | 0 | Yes | 352 | 8 | 8 | UV | 2816 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-08 | [7 empty] | 0 | 0 | 0
School: | William Loesche Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Brothers Retest | [6 empty] | 0 | 0 | 0
| Devine Brothers 2nd Retest | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 286 | 19 |  | 840 | 19 | 19 | UV | 6720 | 2.5536 | 1
101 | Classroom | 282 | 18 |  | 840 | 19 | 18 | UV | 6720 | 2.5179 | 1
102 | Classroom | 82 | 5 | Yes | 784 | 17 | 17 | UV | 6272 | 0.78444 | 0
103 | Classroom | 288 | 19 |  | 840 | 19 | 19 | UV | 6720 | 2.5714 | 1
104 | Classroom | 0 | 0 |  | 840 | 19 | 0 | UV | 6720 | 0 | 0
105 | Classroom | 300 | 20 |  | 840 | 19 | 19 | UV | 6720 | 2.6786 | 1
107 | Classroom | 288 | 19 |  | 840 | 19 | 19 | UV | 6720 | 2.5714 | 1
108 | Classroom | 213 | 14 | Yes | 1122 | 25 | 25 | UV | 8976 | 1.4238 | 1
109 | Classroom | 185 | 12 |  | 840 | 19 | 12 | UV | 6720 | 1.6518 | 1
110 | Classroom | 156 | 10 | Yes | 840 | 19 | 19 | UV | 6720 | 1.3929 | 1
111 | Classroom | 190 | 12 | Yes | 882 | 20 | 20 | UV | 7056 | 1.6156 | 1
112 | Classroom | 285 | 19 |  | 729 | 16 | 16 | UV | 5832 | 2.9321 | 1
200 | Classroom | 258 | 17 |  | 840 | 19 | 17 | UV | 6720 | 2.3036 | 1
201 | Classroom | 292 | 19 |  | 840 | 19 | 19 | UV | 6720 | 2.6071 | 1
202 | Classroom | 283 | 18 |  | 840 | 19 | 18 | UV | 6720 | 2.5268 | 1
203 | Classroom | 158 | 10 | Yes | 840 | 19 | 19 | UV | 6720 | 1.4107 | 1
204 | Classroom | 262 | 17 |  | 840 | 19 | 17 | UV | 6720 | 2.3393 | 1
205 | Classroom | 205 | 13 | Yes | 840 | 19 | 19 | UV | 6720 | 1.8304 | 1
206 | Classroom | 153 | 10 |  | 476 | 10 | 10 | UV | 3808 | 2.4107 | 1
207 | Classroom | 297 | 19 |  | 840 | 19 | 19 | UV | 6720 | 2.6518 | 1
208 | Classroom | 210 | 14 |  | 840 | 19 | 14 | UV | 6720 | 1.875 | 1
208A | Classroom | 150 | 10 |  | 252 | 5 | 5 | UV | 2016 | 4.4643 | 2
209 | Classroom | 184 | 12 | Yes | 840 | 19 | 19 | UV | 6720 | 1.6429 | 1
210 | Classroom | 193 | 12 |  | 780 | 17 | 12 | UV | 6240 | 1.8558 | 1
211 | Classroom | 142 | 9 | Yes | 783 | 17 | 17 | UV | 6264 | 1.3602 | 1
212 | Classroom | 267 | 17 |  | 840 | 19 | 17 | UV | 6720 | 2.3839 | 1
214 | Classroom | 280 | 18 |  | 1212 | 27 | 18 | UV | 9696 | 1.7327 | 1
215 | Classroom | 268 | 17 |  | 1232 | 28 | 17 | UV | 9856 | 1.6315 | 1
216 | Classroom | 415 | 27 |  | 756 | 17 | 17 | UV | 6048 | 4.1171 | 2
217 | Classroom | 276 | 18 |  | 841 | 19 | 18 | UV | 6728 | 2.4614 | 1
218 | Classroom | 144 | 9 | Yes | 840 | 19 | 19 | UV | 6720 | 1.2857 | 1
219 | Classroom | 106 | 7 | Yes | 840 | 19 | 19 | UV | 6720 | 0.94643 | 0
220 | Classroom | 246 | 16 |  | 870 | 19 | 16 | UV | 6960 | 2.1207 | 1
221 | Classroom | 140 | 9 |  | 870 | 19 | 9 | UV | 6960 | 1.2069 | 1
222 | Classroom | 106 | 7 |  | 840 | 19 | 7 | UV | 6720 | 0.94643 | 0
223 | Classroom | 175 | 11 |  | 840 | 19 | 11 | UV | 6720 | 1.5625 | 1
224 | Classroom | 94 | 6 |  | 840 | 19 | 6 | UV | 6720 | 0.83929 | 0
A-1 | Classroom | 242 | 16 |  | 884 | 20 | 16 | UV | 7072 | 2.0532 | 1
A-2 | Classroom | 254 | 16 |  | 884 | 20 | 16 | UV | 7072 | 2.155 | 1
A-3 | Classroom | 298 | 19 |  | 884 | 20 | 19 | UV | 7072 | 2.5283 | 1
A-4 | Classroom | 281 | 18 |  | 884 | 20 | 18 | UV | 7072 | 2.384 | 1
- | A-wing Mech. Rm | 0 | 0 |  | 358 | 8 | 0 | UV | 2864 | 0 | 0
- | Auditorium | 0 | 0 |  | 3600 | 81 | 0 | AHU | 28800 | 0 | 0
B-1 | Classroom | 314 | 20 |  | 806 | 18 | 18 | UV | 6448 | 2.9218 | 1
B-2 | Classroom | 311 | 20 |  | 806 | 18 | 18 | UV | 6448 | 2.8939 | 1
B-3 | Classroom | 300 | 20 |  | 806 | 18 | 18 | UV | 6448 | 2.7916 | 1
B-4 | Classroom | 313 | 20 |  | 806 | 18 | 18 | UV | 6448 | 2.9125 | 1
B-5 | Classroom | 287 | 19 |  | 806 | 18 | 18 | UV | 6448 | 2.6706 | 1
B-6 | Classroom | 297 | 19 |  | 905 | 20 | 19 | UV | 7240 | 2.4613 | 1
B-7 | Classroom | 285 | 19 |  | 905 | 20 | 19 | UV | 7240 | 2.3619 | 1
B-8 | Classroom | 304 | 20 |  | 905 | 20 | 20 | UV | 7240 | 2.5193 | 1
B-9 | Classroom | 282 | 18 |  | 905 | 20 | 18 | UV | 7240 | 2.337 | 1
- | Backstage | 0 | 0 |  | 180 | 4 | 0 | UV | 1440 | 0 | 0
- | Backstage Dressing Rm. | 172 | 11 |  | 252 | 5 | 5 | UV | 2016 | 5.119 | 2
- | Cafeteria | 0 | 0 | Yes | 5540 | 125 | 125 | AHU | 44320 | 0 | 0
- | GYM | 0 | 0 |  | 4496 | 102 | 0 | AHU | 35968 | 0 | 0
- | Library | 0 | 0 |  | 1131 | 25 | 0 | UV | 9048 | 0 | 0
- | Main Office | 292 | 19 |  | 992 | 22 | 19 | UV | 7936 | 2.2077 | 1
- | Nurse's Office | 94 | 6 |  | 706 | 16 | 6 | UV | 5648 | 0.99858 | 0
- | Principal's Office | 148 | 9 |  | 308 | 7 | 7 | UV | 2464 | 3.6039 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-24 | [7 empty] | 0 | 0 | 0
School: | James Logan Elementary-Middle School | House Fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B-1 | Classroom | 1228 | 81 |  | 889 | 20 | 20 | House Fan | 7112 | 10.36 | 3
B-2 | Classroom | 975 | 65 |  | 737 | 16 | 16 | House Fan | 5896 | 9.922 | 2
B-3 | Classroom | 1131 | 75 |  | 1017 | 23 | 23 | House Fan | 8136 | 8.3407 | 2
101 | Classroom | 539 | 35 |  | 729 | 16 | 16 | House Fan | 5832 | 5.5453 | 2
102 | Classroom | 578 | 38 |  | 732 | 16 | 16 | House Fan | 5856 | 5.9221 | 2
103 | Classroom | 593 | 39 |  | 724 | 16 | 16 | House Fan | 5792 | 6.143 | 2
104 | Classroom | 674 | 44 |  | 676 | 15 | 15 | House Fan | 5408 | 7.4778 | 2
104A | Office | 0 | 0 |  | 177 | 4 | 0 | House Fan | 1416 | 0 | 0
105 | Teacher's Lounge | 617 | 41 |  | 650 | 14 | 14 | House Fan | 5200 | 7.1192 | 2
106 | Classroom | 621 | 41 |  | 726 | 16 | 16 | House Fan | 5808 | 6.4153 | 2
107 | Classroom | 376 | 25 |  | 722 | 16 | 16 | House Fan | 5776 | 3.9058 | 1
108 | Classroom | 849 | 56 |  | 717 | 16 | 16 | House Fan | 5736 | 8.8808 | 2
201 | IMC | 509 | 33 |  | 639 | 14 | 14 | House Fan | 5112 | 5.9742 | 2
202 | IMC | 632 | 42 |  | 639 | 14 | 14 | House Fan | 5112 | 7.4178 | 2
203 | Classroom | 551 | 36 |  | 720 | 16 | 16 | House Fan | 5760 | 5.7396 | 2
204 | Office Storage | 0 | 0 |  | 201 | 4 | 0 | House Fan | 1608 | 0 | 0
205 | Classroom | 519 | 34 |  | 718 | 16 | 16 | House Fan | 5744 | 5.4213 | 2
205A | Office | 0 | 0 |  | 164 | 3 | 0 | House Fan | 1312 | 0 | 0
206 | Classroom | 715 | 47 |  | 735 | 16 | 16 | House Fan | 5880 | 7.2959 | 2
206A | Counselor | 0 | 0 |  | 231 | 5 | 0 | House Fan | 1848 | 0 | 0
207 | Classroom | 394 | 26 |  | 723 | 16 | 16 | House Fan | 5784 | 4.0871 | 2
208 | Classroom | 423 | 28 |  | 724 | 16 | 16 | House Fan | 5792 | 4.3819 | 2
209 | Classroom | 575 | 38 |  | 725 | 16 | 16 | House Fan | 5800 | 5.9483 | 2
209A | Classroom | 0 | 0 |  | 260 | 5 | 0 | House Fan | 2080 | 0 | 0
301 | Classroom | 522 | 34 |  | 679 | 15 | 15 | House Fan | 5432 | 5.7658 | 2
302 | Classroom | 549 | 36 |  | 679 | 15 | 15 | House Fan | 5432 | 6.0641 | 2
303 | Classroom | 458 | 30 |  | 724 | 16 | 16 | House Fan | 5792 | 4.7445 | 2
304 | Classroom | 481 | 32 |  | 714 | 16 | 16 | House Fan | 5712 | 5.0525 | 2
305 | Classroom | 347 | 23 |  | 890 | 20 | 20 | House Fan | 7120 | 2.9242 | 1
306 | Classroom | 381 | 25 |  | 750 | 17 | 17 | House Fan | 6000 | 3.81 | 1
307 | Classroom | 312 | 20 |  | 992 | 22 | 20 | House Fan | 7936 | 2.3589 | 1
308 | Classroom | 466 | 31 |  | 751 | 17 | 17 | House Fan | 6008 | 4.6538 | 2
309 | Classroom | 508 | 33 |  | 992 | 22 | 22 | House Fan | 7936 | 3.8407 | 1
310 | Classroom | 477 | 31 |  | 720 | 16 | 16 | House Fan | 5760 | 4.9688 | 2
311 | Classroom | 409 | 27 |  | 703 | 15 | 15 | House Fan | 5624 | 4.3634 | 2
312 | Classroom | 491 | 32 |  | 730 | 16 | 16 | House Fan | 5840 | 5.0445 | 2
313 | Classroom | 570 | 38 |  | 721 | 16 | 16 | House Fan | 5768 | 5.9293 | 2
- | Auditorium | 2427 | 161 |  | 3685 | 83 | 83 | House Fan | 29480 | 4.9396 | 2
- | Boys' Bathroom | 125 | 8 |  | 561 | 12 | 8 | N/A | 4488 | 1.6711 | 1
- | Girls' Bathroom | 73 | 4 |  | 547 | 12 | 4 | N/A | 4376 | 1.0009 | 1
- | Cafeteria | 1258 | 83 |  | 1726 | 39 | 39 | House Fan | 13808 | 5.4664 | 2
- | Speech Classroom | 0 | 0 | Yes | 192 | 4 | 4 | House Fan | 1536 | 0 | 0
- | Gym | 0 | 0 | Yes | 3970 | 90 | 90 | N/A | 31760 | 0 | 0
- | Nurse's Office | 0 | 0 | Yes | 220 | 5 | 5 | House Fan | 1760 | 0 | 0
- | IMC Office | 0 | 0 |  | 158 | 3 | 0 | House Fan | 1264 | 0 | 0
- | Main Office | 0 | 0 | Yes | 333 | 7 | 7 | House Fan | 2664 | 0 | 0
- | Principal's Office | 0 | 0 | Yes | 342 | 7 | 7 | House Fan | 2736 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-26 | [7 empty] | 0 | 0 | 0
School: | W.C. Longstreth Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100D | Faculty Dining | 96 | 6 |  | 625 | 14 | 6 | AHU-6 | 5000 | 1.152 | 1
102 | Main Office | 110 | 7 |  | 646 | 14 | 7 | AHU-6 | 5168 | 1.2771 | 1
102C | Principal Office | 77 | 5 |  | 225 | 5 | 5 | AHU-6 | 1800 | 2.5667 | 1
102D | Comference Room | 72 | 4 |  | 198 | 4 | 4 | AHU-6 | 1584 | 2.7273 | 1
103 | Classroom | 141 | 9 |  | 704 | 16 | 9 | AHU-1 | 5632 | 1.5021 | 1
105 | Classroom | 206 | 13 |  | 609 | 13 | 13 | AHU-1 | 4872 | 2.5369 | 1
106 | Art Room | 610 | 40 |  | 1333 | 30 | 30 | AHU-2 | 10664 | 3.4321 | 1
107 | Classroom | 468 | 31 |  | 1320 | 30 | 30 | AHU-1 | 10560 | 2.6591 | 1
109 | Classroom | 469 | 31 |  | 1276 | 29 | 29 | AHU-1 | 10208 | 2.7567 | 1
110 | Nurses Suite | 45 | 3 |  | 180 | 4 | 3 | AHU-6 | 1440 | 1.875 | 1
110C | Nurses Office | 102 | 6 |  | 132 | 3 | 3 | AHU-6 | 1056 | 5.7955 | 2
110D | Audio Rm | 101 | 6 |  | 132 | 3 | 3 | AHU-6 | 1056 | 5.7386 | 2
110E | Audio Rm | 78 | 5 |  | 48 | 1 | 1 | AHU-6 | 384 | 12.1875 | 3
111 | Classroom | 487 | 32 |  | 1232 | 28 | 28 | AHU-1 | 9856 | 2.9647 | 1
112A | Building Engineers Office | 90 | 6 |  | 88 | 2 | 2 | AHU-6 | 704 | 7.6705 | 2
113 | Classroom | 361 | 24 |  | 1364 | 31 | 24 | AHU-1 | 10912 | 1.985 | 1
200 | Library | 715 | 47 |  | 2859 | 64 | 47 | AHU-5 | 22872 | 1.8757 | 1
200A | Computer Lab | 119 | 7 |  | 704 | 16 | 7 | AHU-5 | 5632 | 1.2678 | 1
200B | Consortium | 67 | 4 |  | 552 | 12 | 4 | AHU-5 | 4416 | 0.91033 | 0
201 | Classroom | 403 | 26 |  | 818 | 18 | 18 | AHU-1 | 6544 | 3.695 | 1
202 | Classroom | 360 | 24 |  | 510 | 11 | 11 | AHU-2 | 4080 | 5.2941 | 2
203 | Classroom | 321 | 21 |  | 544 | 12 | 12 | AHU-1 | 4352 | 4.4256 | 2
204 | Classroom | 206 | 13 | Yes | 510 | 11 | 11 | AHU-2 | 4080 | 3.0294 | 1
205 | Classroom | 273 | 18 |  | 544 | 12 | 12 | AHU-1 | 4352 | 3.7638 | 1
206 | Classroom | 364 | 24 |  | 510 | 11 | 11 | AHU-2 | 4080 | 5.3529 | 2
207 | Classroom | 419 | 27 |  | 544 | 12 | 12 | AHU-1 | 4352 | 5.7767 | 2
208 | Classroom | 309 | 20 |  | 510 | 11 | 11 | AHU-2 | 4080 | 4.5441 | 2
209 | Classroom | 417 | 27 |  | 544 | 12 | 12 | AHU-1 | 4352 | 5.7491 | 2
210 | Classroom | 276 | 18 |  | 510 | 11 | 11 | AHU-2 | 4080 | 4.0588 | 2
211 | Classroom | 88 | 5 |  | 576 | 13 | 5 | AHU-1 | 4608 | 1.1458 | 1
212 | Classroom | 304 | 20 |  | 765 | 17 | 17 | AHU-2 | 6120 | 2.9804 | 1
213 | Classroom | 303 | 20 |  | 810 | 18 | 18 | AHU-1 | 6480 | 2.8056 | 1
214 | Classroom - WEIGHT ROOM | 669 | 44 |  | 1204 | 27 | 27 | AHU-2 | 9632 | 4.1674 | 2
215 | Classroom | 141 | 9 |  | 285 | 6 | 6 | AHU-1 | 2280 | 3.7105 | 1
219 | Classroom | 175 | 11 |  | 220 | 5 | 5 | AHU-1 | 1760 | 5.9659 | 2
220 | Classroom | 61 | 4 |  | 612 | 13 | 4 | AHU-2 | 4896 | 0.74755 | 0
301 | Classroom | 311 | 20 |  | 595 | 13 | 13 | AHU-1 | 4760 | 3.9202 | 1
303 | Classroom | 323 | 21 |  | 561 | 12 | 12 | AHU-1 | 4488 | 4.3182 | 2
304 | Classroom | 220 | 14 |  | 570 | 12 | 12 | AHU-2 | 4560 | 2.8947 | 1
305 | Classroom | 316 | 21 |  | 577 | 13 | 13 | AHU-1 | 4616 | 4.1075 | 2
306 | Classroom | 462 | 30 |  | 510 | 11 | 11 | AHU-2 | 4080 | 6.7941 | 2
307 | Classroom | 331 | 22 |  | 577 | 13 | 13 | AHU-1 | 4616 | 4.3024 | 2
308 | Classroom | 327 | 21 |  | 510 | 11 | 11 | AHU-2 | 4080 | 4.8088 | 2
309 | Classroom | 356 | 23 |  | 594 | 13 | 13 | AHU-1 | 4752 | 4.4949 | 2
310 | Classroom | 320 | 21 |  | 527 | 11 | 11 | AHU-2 | 4216 | 4.5541 | 2
311 | Classroom | 340 | 22 |  | 576 | 13 | 13 | AHU-1 | 4608 | 4.4271 | 2
312 | Classroom | 332 | 22 |  | 544 | 12 | 12 | AHU-2 | 4352 | 4.5772 | 2
313 | Classroom | 422 | 28 |  | 840 | 19 | 19 | AHU-1 | 6720 | 3.7679 | 1
314 | Classroom | 577 | 38 |  | 1290 | 29 | 29 | AHU-2 | 10320 | 3.3547 | 1
315 | Classroom | 145 | 9 |  | 280 | 6 | 6 | AHU-1 | 2240 | 3.8839 | 1
319 | Classroom | 129 | 8 |  | 220 | 5 | 5 | AHU-1 | 1760 | 4.3977 | 2
320 | Classroom | 171 | 11 |  | 210 | 4 | 4 | AHU-2 | 1680 | 6.1071 | 2
- | Auditorium | 1337 | 89 |  | 3540 | 80 | 80 | AHU-3 | 28320 | 2.8326 | 1
- | Cafeteria | 2211 | 147 |  | 3658 | 83 | 83 | AHU-4 | 29264 | 4.5332 | 2
- | Diagnostic Center | 213 | 14 |  | 306 | 6 | 6 | AHU-6 | 2448 | 5.2206 | 2
- | Main Office Admin | 82 | 5 |  | 110 | 2 | 2 | AHU-6 | 880 | 5.5909 | 2
- | Main Storage Room | 27 | 1 |  | 192 | 4 | 1 | AHU-6 | 1536 | 1.0547 | 1
- | Nurses Suite Laundry | 115 | 7 |  | 372 | 8 | 7 | AHU-6 | 2976 | 2.3185 | 1
- | Gym | 0 | 0 |  | 4720 | 107 | 0 | AHU 1 and 2 | 37760 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-26 | [7 empty] | 0 | 0 | 0
School: | James R. Lowell Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B010A | Boys Bathroom | 725 | 48 |  | 667 | 15 | 15 | N/A | 5336 | 8.1522 | 2
B10 | Music | 0 | 0 |  | 925 | 21 | 0 | N/A | 7400 | 0 | 0
B11 | Classroom | 346 | 23 |  | 695 | 15 | 15 | House Fan | 5560 | 3.7338 | 1
B12 | Girls Bathroom | 305 | 20 |  | 695 | 15 | 15 | House Fan | 5560 | 3.2914 | 1
B8 | Classroom | 175 | 11 |  | 576 | 13 | 11 | House Fan | 4608 | 2.2786 | 1
B9 | Classroom | 388 | 25 |  | 667 | 15 | 15 | House Fan | 5336 | 4.3628 | 2
100 | Classroom | 0 | 0 |  | 240 | 5 | 0 | House Fan | 1920 | 0 | 0
101 | Classroom | 285 | 19 |  | 566 | 12 | 12 | House Fan | 4528 | 3.7765 | 1
102 | Classroom | 327 | 21 |  | 559 | 12 | 12 | House Fan | 4472 | 4.3873 | 2
103 | Classroom | 325 | 21 |  | 100 | 2 | 2 | House Fan | 800 | 24.375 | 4
104 | Classroom | 102 | 6 |  | 640 | 14 | 6 | House Fan | 5120 | 1.1953 | 1
105 | Classroom | 593 | 39 |  | 654 | 14 | 14 | House Fan | 5232 | 6.8005 | 2
106 | Classroom | 399 | 26 |  | 566 | 12 | 12 | House Fan | 4528 | 5.2871 | 2
107 | Classroom | 0 | 0 |  | 667 | 15 | 0 | House Fan | 5336 | 0 | 0
108 | Classroom | 154 | 10 |  | 650 | 14 | 10 | House Fan | 5200 | 1.7769 | 1
109 | Classroom | 304 | 20 |  | 602 | 13 | 13 | House Fan | 4816 | 3.7874 | 1
110 | Classroom | 0 | 0 |  | 207 | 4 | 0 | House Fan | 1656 | 0 | 0
111 | Counselor |  | 0 |  | 154 | 3 | 0 |  | 1232 | 0 | 0
200 | Classroom | 0 | 0 |  | 240 | 5 | 0 | House Fan | 1920 | 0 | 0
201 | Classroom | 300 | 20 |  | 654 | 14 | 14 | House Fan | 5232 | 3.4404 | 1
202 | Computer Room |  | 0 |  | 810 | 18 | 0 |  | 6480 | 0 | 0
203 | Classroom | 647 | 43 |  | 654 | 14 | 14 | House Fan | 5232 | 7.4197 | 2
204 | Classroom | 457 | 30 |  | 650 | 14 | 14 | House Fan | 5200 | 5.2731 | 2
205 | Classroom | 531 | 35 |  | 650 | 14 | 14 | House Fan | 5200 | 6.1269 | 2
206 | Classroom | 247 | 16 |  | 695 | 15 | 15 | House Fan | 5560 | 2.6655 | 1
207 | Classroom | 102 | 6 |  | 694 | 15 | 6 | House Fan | 5552 | 1.1023 | 1
207 | Faculty Room | 0 | 0 |  | 207 | 4 | 0 | N/A | 1656 | 0 | 0
208 | Classroom | 200 | 13 |  | 695 | 15 | 13 | House Fan | 5560 | 2.1583 | 1
209 | Classroom | 139 | 9 |  | 650 | 14 | 9 | House Fan | 5200 | 1.6038 | 1
210 | Classroom | 275 | 18 |  | 560 | 12 | 12 | House Fan | 4480 | 3.683 | 1
211 | Classroom | 0 | 0 |  | 420 | 9 | 0 | House Fan | 3360 | 0 | 0
300 | Classroom | 0 | 0 |  | 240 | 5 | 0 | House Fan | 1920 | 0 | 0
301A | Classroom | 132 | 8 |  | 566 | 12 | 8 | House Fan | 4528 | 1.7491 | 1
301B | Classroom | 139 | 9 |  | 300 | 6 | 6 | House Fan | 2400 | 3.475 | 1
302 | Classroom | 145 | 9 |  | 240 | 5 | 5 | House Fan | 1920 | 4.5312 | 2
303 | Classroom | 318 | 21 |  | 666 | 15 | 15 | House Fan | 5328 | 3.5811 | 1
304 | Classroom | 387 | 25 |  | 610 | 13 | 13 | House Fan | 4880 | 4.7582 | 2
305 | Classroom | 432 | 28 |  | 620 | 14 | 14 | House Fan | 4960 | 5.2258 | 2
306 | Classroom | 249 | 16 |  | 650 | 14 | 14 | House Fan | 5200 | 2.8731 | 1
307 | Classroom | 325 | 21 |  | 650 | 14 | 14 | House Fan | 5200 | 3.75 | 1
308 | Classroom | 322 | 21 |  | 650 | 14 | 14 | House Fan | 5200 | 3.7154 | 1
309 | Classroom | 262 | 17 |  | 654 | 14 | 14 | House Fan | 5232 | 3.0046 | 1
310 | Classroom | 203 | 13 |  | 636 | 14 | 13 | House Fan | 5088 | 2.3939 | 1
311 | Classroom | 0 | 0 |  | 221 | 5 | 0 | House Fan | 1768 | 0 | 0
312 | Classroom | 0 | 0 |  | 273 | 6 | 0 | House Fan | 2184 | 0 | 0
- | Library | 213 | 14 |  | 1040 | 23 | 14 | AHU | 8320 | 1.5361 | 1
- | Entrance Lobby | 290 | 19 |  | 325 | 7 | 7 | N/A | 2600 | 6.6923 | 2
- | Gym | 0 | 0 |  | 4368 | 99 | 0 | AHU | 34944 | 0 | 0
- | Music Rm | 127 | 8 |  | 286 | 6 | 6 | Unit Ventilator | 2288 | 3.3304 | 1
S-11 | Classroom | 419 | 27 |  | 810 | 18 | 18 | Unit Ventilator | 6480 | 3.8796 | 1
S-12 | Classroom | 906 | 60 |  | 692 | 15 | 15 | Unit Ventilator | 5536 | 9.8194 | 2
S-13 | Classroom | 635 | 42 |  | 692 | 15 | 15 | Unit Ventilator | 5536 | 6.8822 | 2
S-14 | Classroom | 715 | 47 |  | 695 | 15 | 15 | Unit Ventilator | 5560 | 7.7158 | 2
S-15 | Classroom | 411 | 27 |  | 692 | 15 | 15 | Unit Ventilator | 5536 | 4.4545 | 2
S-16 | Classroom | 502 | 33 |  | 692 | 15 | 15 | Unit Ventilator | 5536 | 5.4408 | 2
S-17 | Classroom | 371 | 24 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.3605 | 1
S-18 | Classroom | 482 | 32 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 4.3659 | 2
S-19 | Classroom | 742 | 49 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 6.721 | 2
S-21 | Classroom | 429 | 28 |  | 640 | 14 | 14 | Unit Ventilator | 5120 | 5.0273 | 2
S-22 | Classroom | 663 | 44 |  | 640 | 14 | 14 | Unit Ventilator | 5120 | 7.7695 | 2
S-23 | Classroom | 480 | 32 |  | 654 | 14 | 14 | Unit Ventilator | 5232 | 5.5046 | 2
S-24 | Classroom | 333 | 22 |  | 636 | 14 | 14 | Unit Ventilator | 5088 | 3.9269 | 1
S-25 | Classroom | 844 | 56 |  | 636 | 14 | 14 | Unit Ventilator | 5088 | 9.9528 | 2
S-26 | Classroom | 490 | 32 |  | 654 | 14 | 14 | Unit Ventilator | 5232 | 5.6193 | 2
S-27 | Storage | 393 | 26 |  | 610 | 13 | 13 | Unit Ventilator | 4880 | 4.832 | 2
S-27 | Classroom | 266 | 17 |  | 610 | 13 | 13 | Unit Ventilator | 4880 | 3.2705 | 1
S-28 | Classroom | 450 | 30 |  | 610 | 13 | 13 | Unit Ventilator | 4880 | 5.5328 | 2
S-29 | Classroom | 260 | 17 |  | 610 | 13 | 13 | Unit Ventilator | 4880 | 3.1967 | 1
S-30 | Teacher's Lounge | 378 | 25 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 3.3042 | 1
S-31 | Office | 508 | 33 |  | 140 | 3 | 3 | Unit Ventilator | 1120 | 27.2143 | 4
- | Main Office |  | 0 |  | 338 | 7 | 0 |  | 2704 | 0 | 0
- | Principals Office |  | 0 |  | 364 | 8 | 0 |  | 2912 | 0 | 0
- | Nurses Office |  | 0 |  | 240 | 5 | 0 |  | 1920 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | James R. Ludlow Elementary-Middle School | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
3 | Art |  | 0 |  | 667 | 15 | 0 | House Fan | 5336 | 0 | 0
100B | Home and School |  | 0 |  | 121 | 2 | 0 | House Fan | 968 | 0 | 0
100C | Counselor |  | 0 |  | 195 | 4 | 0 | House Fan | 1560 | 0 | 0
101 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
102 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
103 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | 0 | 0
104 | Classroom |  | 0 | Yes | 638 | 14 | 14 | House Fan | 5104 | 0 | 0
105 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
106 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
107 | Classroom |  | 0 |  | 920 | 20 | 0 | House Fan | 7360 | 0 | 0
108 | Classroom |  | 0 | Yes | 638 | 14 | 14 | House Fan | 5104 | 0 | 0
109 | Classroom |  | 0 | Yes | 841 | 19 | 19 | House Fan | 6728 | 0 | 0
110 | Counselor |  | 0 |  | 128 | 2 | 0 | House Fan | 1024 | 0 | 0
200 | Classroom |  | 0 | Yes | 552 | 12 | 12 | House Fan | 4416 | 0 | 0
201 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
202 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
203 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
204 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
207 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
208 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
209 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
211 | Classroom |  | 0 | Yes | 841 | 19 | 19 | House Fan | 6728 | 0 | 0
300 | Ladies lounge |  | 0 |  | 276 | 6 | 0 | House Fan | 2208 | 0 | 0
300A | Ladies lounge |  | 0 |  | 276 | 6 | 0 | House Fan | 2208 | 0 | 0
301 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
302 | Classroom |  | 0 | Yes | 782 | 17 | 17 | House Fan | 6256 | 0 | 0
303 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | 0 | 0
304 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
305 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
306 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
307 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
308 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
309 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
310 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
311 | Classroom |  | 0 | Yes | 406 | 9 | 9 | House Fan | 3248 | 0 | 0
- | Library |  | 0 | Yes | 1298 | 29 | 29 | House Fan | 10384 | 0 | 0
- | Gym |  | 0 | Yes | 5208 | 118 | 118 |  | 41664 | 0 | 0
- | Kitchen |  | 0 | Yes | 1288 | 29 | 29 | House Fan | 10304 | 0 | 0
- | Lunchroom/Cafetorium |  | 0 |  | 3157 | 71 | 0 | House Fan | 25256 | 0 | 0
- | Main office |  | 0 | Yes | 322 | 7 | 7 | House Fan | 2576 | 0 | 0
- | Nurses Office |  | 0 | Yes | 128 | 2 | 2 | House Fan | 1024 | 0 | 0
- | Principals office |  | 0 | Yes | 165 | 3 | 3 | House Fan | 1320 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-08 | [7 empty] | 0 | 0 | 0
School: | John Marshall Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
102 | Classroom | 723 | 48 |  | 832 | 18 | 18 | House Fan | 6656 | 6.5174 | 2
103 | Classroom | 653 | 43 |  | 449 | 10 | 10 | House Fan | 3592 | 10.9076 | 3
104 | Classroom | 684 | 45 |  | 781 | 17 | 17 | House Fan | 6248 | 6.5685 | 2
105 | Classroom | 717 | 47 |  | 738 | 16 | 16 | House Fan | 5904 | 7.2866 | 2
106 | Classroom | 624 | 41 |  | 893 | 20 | 20 | House Fan | 7144 | 5.2408 | 2
107 | Classroom | 575 | 38 |  | 623 | 14 | 14 | House Fan | 4984 | 6.9222 | 2
200 | Classroom | 640 | 42 |  | 790 | 17 | 17 | House Fan | 6320 | 6.0759 | 2
201 | Classroom | 692 | 46 |  | 803 | 18 | 18 | House Fan | 6424 | 6.4633 | 2
202 | Classroom | 691 | 46 |  | 746 | 16 | 16 | House Fan | 5968 | 6.9471 | 2
203 | Classroom | 556 | 37 |  | 770 | 17 | 17 | House Fan | 6160 | 5.4156 | 2
204 | Classroom | 678 | 45 |  | 715 | 16 | 16 | House Fan | 5720 | 7.1119 | 2
205 | Classroom | 765 | 51 |  | 225 | 5 | 5 | House Fan | 1800 | 25.5 | 4
206 | Classroom | 535 | 35 |  | 548 | 12 | 12 | House Fan | 4384 | 7.3221 | 2
300 | Classroom | 596 | 39 |  | 766 | 17 | 17 | House Fan | 6128 | 5.8355 | 2
300A | Classroom |  | 0 | Yes | 510 | 11 | 11 | Wndow Fan | 4080 | 0 | 0
301 | Classroom | 531 | 35 |  | 884 | 20 | 20 | House Fan | 7072 | 4.5051 | 2
302 | Classroom | 683 | 45 |  | 766 | 17 | 17 | House Fan | 6128 | 6.6873 | 2
303 | Classroom | 785 | 52 |  | 748 | 17 | 17 | House Fan | 5984 | 7.871 | 2
304 | Classroom | 793 | 52 |  | 779 | 17 | 17 | House Fan | 6232 | 7.6348 | 2
305 | Classroom | 668 | 44 |  | 757 | 17 | 17 | House Fan | 6056 | 6.6182 | 2
306 | Classroom | 609 | 40 |  | 876 | 19 | 19 | House Fan | 7008 | 5.214 | 2
- | 1st Fl. Corridor | 1954 | 130 |  | 352 | 8 | 8 | N/A | 2816 | 41.6335 | 4
- | Grnd. Fl. Boys Bathrm. | 402 | 26 |  | 234 | 5 | 5 | N/A | 1872 | 12.8846 | 3
- | Grnd. Fl. Girls Bathrm. | 333 | 22 |  | 156 | 3 | 3 | N/A | 1248 | 16.0096 | 3
- | Main Office | 343 | 22 |  | 298 | 6 | 6 | House Fan | 2384 | 8.6326 | 2
- | Nurse / office | 340 | 22 |  | 420 | 9 | 9 | House Fan | 3360 | 6.0714 | 2
- | Cafeteria |  | 0 | Yes | 3129 | 71 | 71 | Wndow Fan | 25032 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-24 | [7 empty] | 0 | 0 | 0
School: | Thurgood Marshall Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 99 | 6 | Yes | 875 | 19 | 19 |  | 7000 | 0.84857 | 0
101 | Classroom | 112 | 7 | Yes | 875 | 19 | 19 |  | 7000 | 0.96 | 0
102 | Classroom | 53 | 3 | Yes | 875 | 19 | 19 |  | 7000 | 0.45429 | 0
103 | Classroom | 60 | 4 | Yes | 875 | 19 | 19 |  | 7000 | 0.51429 | 0
104 | Classroom | 310 | 20 |  | 589 | 13 | 13 |  | 4712 | 3.9474 | 1
105 | Classroom | 143 | 9 | Yes | 624 | 14 | 14 |  | 4992 | 1.7188 | 1
106 | Office | 154 | 10 |  | 143 | 3 | 3 |  | 1144 | 8.0769 | 2
106A | Office | 0 | 0 |  | 99 | 2 | 0 |  | 792 | 0 | 0
106B | Office | 0 | 0 |  | 99 | 2 | 0 |  | 792 | 0 | 0
106C | Office | 168 | 11 |  | 99 | 2 | 2 |  | 792 | 12.7273 | 3
106D | Office | 180 | 12 |  | 126 | 2 | 2 |  | 1008 | 10.7143 | 3
106E | Office | 165 | 11 |  | 130 | 2 | 2 |  | 1040 | 9.5192 | 2
106G | Office | 191 | 12 |  | 130 | 2 | 2 |  | 1040 | 11.0192 | 3
106H | Hallway | 0 | 0 |  | 528 | 12 | 0 |  | 4224 | 0 | 0
106 RR | Office | 513 | 34 |  | 52.5 | 1 | 1 |  | 420 | 73.2857 | 5
107 | Classroom | 82 | 5 |  | 720 | 16 | 5 |  | 5760 | 0.85417 | 0
107-2 | Classroom | 0 | 0 |  | 215 | 4 | 0 |  | 1720 | 0 | 0
107A | Classroom | 89 | 5 |  | 816 | 18 | 5 |  | 6528 | 0.81801 | 0
108 | Classroom | 38 | 2 |  | 506 | 11 | 2 |  | 4048 | 0.56324 | 0
108A | Classroom | 37 | 2 |  | 128 | 2 | 2 |  | 1024 | 2.168 | 1
109 | Classroom | 71 | 4 |  | 1196 | 27 | 4 |  | 9568 | 0.44523 | 0
110 | Classroom | 382 | 25 |  | 682 | 15 | 15 |  | 5456 | 4.2009 | 2
111 | Classroom | 216 | 14 | Yes | 630 | 14 | 14 |  | 5040 | 2.5714 | 1
113A | Principals Office | 18 | 1 |  | 340 | 7 | 1 |  | 2720 | 0.39706 | 0
113D | Admin Office | 33 | 2 |  | 99 | 2 | 2 |  | 792 | 2.5 | 1
113E | Admin Office | 24 | 1 |  | 99 | 2 | 1 |  | 792 | 1.8182 | 1
113F | Admin Office | 25 | 1 |  | 99 | 2 | 1 |  | 792 | 1.8939 | 1
113G | Admin Office | 20 | 1 |  | 99 | 2 | 1 |  | 792 | 1.5152 | 1
115 | Classroom | 142 | 9 |  | 782 | 17 | 9 |  | 6256 | 1.3619 | 1
200 | Classroom | 88 | 5 |  | 875 | 19 | 5 |  | 7000 | 0.75429 | 0
201 | Classroom | 157 | 10 | Yes | 875 | 19 | 19 |  | 7000 | 1.3457 | 1
202 | Classroom | 75 | 5 | Yes | 875 | 19 | 19 |  | 7000 | 0.64286 | 0
203 | Classroom | 73 | 4 | Yes | 875 | 19 | 19 |  | 7000 | 0.62571 | 0
204 | Classroom | 90 | 6 | Yes | 993 | 22 | 22 |  | 7944 | 0.67976 | 0
205 | Classroom | 53 | 3 |  | 327.75 | 7 | 3 |  | 2622 | 1.2128 | 1
206A | Classroom | 42 | 2 |  | 154 | 3 | 2 |  | 1232 | 2.0455 | 1
206B | Classroom | 31 | 2 |  | 270 | 6 | 2 |  | 2160 | 0.86111 | 0
206C | Classroom | 49 | 3 |  | 127 | 2 | 2 |  | 1016 | 2.8937 | 1
207 | Library | 519 | 34 |  | 2108 | 47 | 34 |  | 16864 | 1.8465 | 1
208 | Computer Lab | 73 | 4 | Yes | 1024 | 23 | 23 |  | 8192 | 0.53467 | 0
209 | Music Room | 0 | 0 |  | 1171 | 26 | 0 |  | 9368 | 0 | 0
215 | Faculty Lounge | 279 | 18 |  | 400 | 9 | 9 |  | 3200 | 5.2313 | 2
300 | Classroom | 140 | 9 | Yes | 875 | 19 | 19 |  | 7000 | 1.2 | 1
301 | Classroom | 125 | 8 | Yes | 875 | 19 | 19 |  | 7000 | 1.0714 | 1
302 | Classroom | 200 | 13 | Yes | 875 | 19 | 19 |  | 7000 | 1.7143 | 1
303 | Classroom | 37 | 2 |  | 875 | 19 | 2 |  | 7000 | 0.31714 | 0
304 | Classroom | 86 | 5 | Yes | 960 | 21 | 21 |  | 7680 | 0.67188 | 0
305 | Classroom | 111 | 7 |  | 782 | 17 | 7 |  | 6256 | 1.0646 | 1
306 | Classroom | 200 | 13 |  | 782 | 17 | 13 |  | 6256 | 1.9182 | 1
307 | Classroom | 132 | 8 |  | 782 | 17 | 8 |  | 6256 | 1.266 | 1
308 | Classroom | 33 | 2 |  | 782 | 17 | 2 |  | 6256 | 0.3165 | 0
310 | Classroom | 65 | 4 |  | 782 | 17 | 4 |  | 6256 | 0.6234 | 0
311 | Classroom | 632 | 42 |  | 782 | 17 | 17 |  | 6256 | 6.0614 | 2
312 | Classroom | 99 | 6 |  | 782 | 17 | 6 |  | 6256 | 0.94949 | 0
313 | Classroom | 76 | 5 |  | 782 | 17 | 5 |  | 6256 | 0.7289 | 0
314 | Classroom | 87 | 5 |  | 782 | 17 | 5 |  | 6256 | 0.8344 | 0
315 | Classroom | 112 | 7 |  | 782 | 17 | 7 |  | 6256 | 1.0742 | 1
404 | Classroom | 90 | 6 |  | 1156 | 26 | 6 |  | 9248 | 0.58391 | 0
405 | Classroom | 129 | 8 |  | 782 | 17 | 8 |  | 6256 | 1.2372 | 1
405A | Office | 0 | 0 |  | 112 | 2 | 0 |  | 896 | 0 | 0
406 | Classroom | 93 | 6 |  | 782 | 17 | 6 |  | 6256 | 0.89194 | 0
407 | Classroom | 147 | 9 |  | 782 | 17 | 9 |  | 6256 | 1.4098 | 1
408 | Classroom | 40 | 2 |  | 782 | 17 | 2 |  | 6256 | 0.38363 | 0
409A | Office | 23 | 1 |  | 140 | 3 | 1 |  | 1120 | 1.2321 | 1
410 | Classroom | 0 | 0 |  | 782 | 17 | 0 |  | 6256 | 0 | 0
411 | Classroom | 86 | 5 |  | 782 | 17 | 5 |  | 6256 | 0.82481 | 0
412 | Classroom | 94 | 6 |  | 782 | 17 | 6 |  | 6256 | 0.90153 | 0
413 | Classroom | 76 | 5 |  | 782 | 17 | 5 |  | 6256 | 0.7289 | 0
414 | Classroom | 84 | 5 |  | 782 | 17 | 5 |  | 6256 | 0.80563 | 0
415 | Classroom | 100 | 6 |  | 782 | 17 | 6 |  | 6256 | 0.95908 | 0
- | Auditorium | 369 | 24 |  | 2162 | 49 | 24 |  | 17296 | 1.2801 | 1
- | Stage | 0 | 0 |  | 630 | 14 | 0 |  | 5040 | 0 | 0
- | Building Engineer Office | 0 | 0 |  | 120 | 2 | 0 |  | 960 | 0 | 0
- | Cafeteria | 3225 | 215 |  | 4400 | 100 | 100 |  | 35200 | 5.4972 | 2
- | East Kitchen | 0 | 0 |  | 360 | 8 | 0 |  | 2880 | 0 | 0
- | West Kitchen | 0 | 0 |  | 1040 | 23 | 0 |  | 8320 | 0 | 0
- | Kitchen Office | 75 | 5 |  | 120 | 2 | 2 |  | 960 | 4.6875 | 2
- | Gym | 4507 | 300 |  | 5005 | 113 | 113 |  | 40040 | 6.7537 | 2
- | Nurses Office | 154 | 10 |  | 143 | 3 | 3 |  | 1144 | 8.0769 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-19 | [7 empty] | 0 | 0 | 0
School: | Jules E. Mastbaum High School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
SDP Building Name | Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | #VALUE! | #VALUE! | #VALUE!
Old Building | 101 | Classroom | 0 | 0 |  | 959 | 21 | 0 | 0 | 0 | 0
Old Building | 102 | Classroom | 0 | 0 |  | 967 | 21 | 0 | 0 | 0 | 0
Old Building | 103 | Classroom | 304 | 20 |  | 1130 | 25 | 20 | 0 | 0 | 0
Old Building | 104 | Classroom | 455 | 30 |  | 801 | 18 | 18 | 0 | 0 | 0
Old Building | 105 | Carpentry Shop |  | 0 | Yes | 2502 | 56 | 56 | #VALUE! | #VALUE! | #VALUE!
Old Building | 201 | Classroom | 0 | 0 |  | 585 | 13 | 0 | 0 | 0 | 0
Old Building | 202 | Classroom | 237 | 15 |  | 190 | 4 | 4 | 0 | 0 | 0
Old Building | 206 | Classroom | 569 | 37 |  | 1045 | 23 | 23 | 0 | 0 | 0
Old Building | 207 | Classroom | 0 | 0 |  | 906 | 20 | 0 | 0 | 0 | 0
Old Building | 209 | Classroom | 738 | 49 |  | 603 | 13 | 13 | 0 | 0 | 0
Old Building | 301 | Classroom | 680 | 45 |  | 583 | 13 | 13 | 0 | 0 | 0
Old Building | 302 | Classroom | 271 | 18 |  | 915 | 20 | 18 | 0 | 0 | 0
Old Building | 304 | Classroom | 256 | 17 |  | 943 | 21 | 17 | 0 | 0 | 0
Old Building | 306 | Classroom | 1285 | 85 |  | 1099 | 24 | 24 | 0 | 0 | 0
Old Building | 308 | Classroom | 292 | 19 |  | 971 | 22 | 19 | 0 | 0 | 0
Old Building | 310A | Classroom | 279 | 18 |  | 1015 | 23 | 18 | 0 | 0 | 0
Old Building | 311 | Classroom | 0 | 0 |  | 940 | 21 | 0 | 0 | 0 | 0
Old Building | 313 | Classroom | 572 | 38 |  | 939 | 21 | 21 | 0 | 0 | 0
Old Building | 315 | Classroom | 404 | 26 |  | 611 | 13 | 13 | 0 | 0 | 0
Old Building | 401 | Classroom | 194 | 12 |  | 562 | 12 | 12 | 0 | 0 | 0
Old Building | 402 | Classroom | 588 | 39 |  | 924 | 20 | 20 | 0 | 0 | 0
Old Building | 404 | Classroom | 337 | 22 |  | 936 | 21 | 21 | 0 | 0 | 0
Old Building | 406 | Classroom | 590 | 39 |  | 658 | 14 | 14 | 0 | 0 | 0
Old Building | 407 | Classroom | 0 | 0 |  | 750 | 17 | 0 | 0 | 0 | 0
Old Building | 408 | Classroom | 0 | 0 |  | 677 | 15 | 0 | 0 | 0 | 0
Old Building | 409 | Classroom | 0 | 0 |  | 659 | 14 | 0 | 0 | 0 | 0
Old Building | 410 | Classroom | 737 | 49 |  | 539 | 12 | 12 | 0 | 0 | 0
Old Building | 412 | Classroom | 956 | 63 |  | 935 | 21 | 21 | 0 | 0 | 0
Old Building | 413 | Classroom | 349 | 23 |  | 460 | 10 | 10 | 0 | 0 | 0
Old Building | 414 | Classroom | 446 | 29 |  | 462 | 10 | 10 | 0 | 0 | 0
Old Building | 415 | Classroom | 600 | 40 |  | 601 | 13 | 13 | 0 | 0 | 0
Old Building | 501 | Classroom | 0 | 0 |  | 583 | 13 | 0 | 0 | 0 | 0
Old Building | 505 | Classroom | 1040 | 69 |  | 701 | 15 | 15 | 0 | 0 | 0
Old Building | 506 | Classroom | 0 | 0 |  | 110 | 2 | 0 | 0 | 0 | 0
Old Building | 510 | Classroom | 595 | 39 |  | 652 | 14 | 14 | 0 | 0 | 0
Old Building | 511 | Classroom |  | 0 | Yes | 917 | 20 |  | #VALUE! | #VALUE! | #VALUE!
Old Building | 512 | Classroom | 0 | 0 |  | 734 | 16 | 0 | 0 | 0 | 0
Old Building | 513 | Classroom | 708 | 47 |  | 745 | 16 | 16 | 0 | 0 | 0
Old Building | 601 | Classroom | 352 | 23 |  | 562 | 12 | 12 | 0 | 0 | 0
Old Building | 602 | Classroom | 838 | 55 |  | 935 | 21 | 21 | 0 | 0 | 0
Old Building | 603 | Classroom | 1066 | 71 |  | 929 | 21 | 21 | 0 | 0 | 0
Old Building | 604 | Classroom | 604 | 40 |  | 884 | 20 | 20 | 0 | 0 | 0
Old Building | 605 | Classroom | 555 | 37 |  | 964 | 21 | 21 | 0 | 0 | 0
Old Building | 607 | Classroom | 733 | 48 |  | 930 | 21 | 21 | 0 | 0 | 0
Old Building | 609 | Classroom | 350 | 23 |  | 498 | 11 | 11 | 0 | 0 | 0
Old Building | 610 | Classroom | 1042 | 69 |  | 939 | 21 | 21 | 0 | 0 | 0
Old Building | 611 | Classroom | 944 | 62 |  | 943 | 21 | 21 | 0 | 0 | 0
Old Building | 612 | Classroom | 357 | 23 |  | 598 | 13 | 13 | 0 | 0 | 0
Old Building | 613 | Classroom | 312 | 20 |  | 696 | 15 | 15 | 0 | 0 | 0
Old Building | 614 | Classroom | 0 | 0 |  | 823 | 18 | 0 | 0 | 0 | 0
Old Building | 615 | Classroom | 411 | 27 |  | 1008 | 22 | 22 | 0 | 0 | 0
Old Building | 616 | Classroom | 1153 | 76 |  | 901 | 20 | 20 | 0 | 0 | 0
Old Building | 617 | Classroom | 0 | 0 |  | 899 | 20 | 0 | 0 | 0 | 0
Old Building | B1 A | Wood Shop | 475 | 31 |  | 2780 | 63 | 31 | 0 | 0 | 0
Old Building | B2 A | Classroom | 499 | 33 |  | 967 | 21 | 21 | 0 | 0 | 0
Old Building | - | Auditorium | 1222 | 81 |  | 4005 | 91 | 81 | 0 | 0 | 0
Old Building | - | 3rd Flr. Gym | 2212 | 147 |  | 3295 | 74 | 74 | 0 | 0 | 0
Old Building | - | 3rd Flr.Gym Locker Room | 3013 | 200 |  | 1903 | 43 | 43 | 0 | 0 | 0
Old Building | - | Stage | 532 | 35 |  | 993 | 22 | 22 | 0 | 0 | 0
Old Building | - | 1st Floor N Corridor | 301 | 20 |  | 160 | 3 | 3 | 0 | 0 | 0
Old Building | - | 1st Floor E Corridor | 536 | 35 |  | 160 | 3 | 3 | 0 | 0 | 0
Old Building | - | 1st Floor S Corridor | 427 | 28 |  | 2120 | 48 | 28 | 0 | 0 | 0
Old Building | - | 1st Floor W Corridor | 382 | 25 |  | 160 | 3 | 3 | 0 | 0 | 0
Old Building | - | 2nd Floor S Corridor | 438 | 29 |  | 2120 | 48 | 29 | 0 | 0 | 0
Old Building | - | 2nd Floor W Corridor | 465 | 31 |  | 160 | 3 | 3 | 0 | 0 | 0
Old Building | - | 2nd Floor N Corridor | 711 | 47 |  | 2120 | 48 | 47 | 0 | 0 | 0
Old Building | - | 2nd Floor E Corridor | 720 | 48 |  | 160 | 3 | 3 | 0 | 0 | 0
Old Building | - | 3rd Floor E Corridor | 504 | 33 |  |  | 0 | 0 | 0 | 0 | 0
Old Building | - | 3rd Floor N Corridor | 619 | 41 |  | 2120 | 48 | 41 | 0 | 0 | 0
Old Building | - | 3rd Floor W Corridor | 761 | 50 |  |  | 0 | 0 | 0 | 0 | 0
Old Building | - | 3rd Floor S Corridor | 569 | 37 |  | 2120 | 48 | 37 | 0 | 0 | 0
Old Building | - | 4th Floor N Corridor | 502 | 33 |  | 2120 | 48 | 33 | 0 | 0 | 0
Old Building | - | 4th Floor E Corridor | 633 | 42 |  |  | 0 | 0 | 0 | 0 | 0
Old Building | - | 4th Floor S Corridor | 0 | 0 |  | 2120 | 48 | 0 | 0 | 0 | 0
Old Building | - | 4th Floor W Corridor | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
Old Building | - | 5th Floor N Corridor | 593 | 39 |  | 2120 | 48 | 39 | 0 | 0 | 0
Old Building | - | 5th Floor Library | 1677 | 111 |  | 2115 | 48 | 48 | 0 | 0 | 0
Old Building | - | 6th Floor S Corridor | 683 | 45 |  | 2120 | 48 | 45 | 0 | 0 | 0
Old Building | - | 6th Floor W Corridor | 918 | 61 |  |  | 0 | 0 | 0 | 0 | 0
Old Building | - | 6th Floor N Corridor | 530 | 35 |  | 2120 | 48 | 35 | 0 | 0 | 0
Old Building | - | 6th Floor E Corridor | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
Old Building | - | Café | 1559 | 103 |  | 734 | 16 | 16 | 0 | 0 | 0
New Building | 120 | Auto Shop | 1016 | 67 |  | 2981 | 67 | 67 | 0 | 0 | 0
New Building | 124 | Auto Shop | 8220 | 548 |  | 4344 | 98 | 98 | 0 | 0 | 0
New Building | 220-221 | Electrical Shop | 0 | 0 |  | 1973 | 44 | 0 | 0 | 0 | 0
New Building | 224-223 | Shop | 2067 | 137 |  | 1150 | 26 | 26 | 0 | 0 | 0
New Building | 225-226 | Shop | 2858 | 190 |  | 3743 | 85 | 85 | 0 | 0 | 0
New Building | 324-323 | 324-323 | 877 | 58 |  | 2781 | 63 | 58 | 0 | 0 | 0
New Building | 326-325 | 326-325 | 1135 | 75 |  | 2395 | 54 | 54 | 0 | 0 | 0
New Building | 420 | 420 | 0 | 0 |  | 1250 | 28 | 0 | 0 | 0 | 0
New Building | 421 | 421 | 0 | 0 |  | 1873 | 42 | 0 | 0 | 0 | 0
New Building | 423 | 423 | 487 | 32 |  | 1693 | 38 | 32 | 0 | 0 | 0
New Building | 426 | 426 Plumbing Shop | 1678 | 111 |  | 1265 | 28 | 28 | 0 | 0 | 0
New Building | 427-426 | 427-426 | 0 | 0 |  | 1583 | 35 | 0 | 0 | 0 | 0
New Building | - | Gym | 958 | 63 |  | 7556 | 171 | 63 | 0 | 0 | 0
New Building | - | Gym Locker Rm. | 0 | 0 |  | 5738 | 130 | 0 | 0 | 0 | 0
New Building | 321 | Nursing | 614 | 40 |  | 1898 | 43 | 40 | 0 | 0 | 0
New Building | - | Weld Shop | 2329 | 155 |  | 625 | 14 | 14 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-07 | [7 empty] | 0 | 0 | 0
School: | Julia R. Masterman Laboratory and Demonstration High School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
8 | Music Room |  | 0 |  | 630 | 14 | 0 |  | 5040 | 0 | 0
9 | Classroom | 0 | 0 |  | 874 | 19 | 0 |  | 6992 | 0 | 0
11 | Classroom | 0 | 0 |  | 825 | 18 | 0 | AHU Inoperable | 6600 | 0 | 0
11A | Classroom | 0 | 0 |  | 368 | 8 | 0 | AHU Inoperable | 2944 | 0 | 0
12 | Classroom | 0 | 0 |  | 832 | 18 | 0 | AHU Inoperable | 6656 | 0 | 0
14 | Art Room |  | 0 |  | 1023 | 23 | 0 | AHU Inoperable | 8184 | 0 | 0
15 | Classroom | 0 | 0 |  | 1148 | 26 | 0 |  | 9184 | 0 | 0
101 | Classroom | 0 | 0 | Yes | 704 | 16 | 16 | AHU Inoperable | 5632 | 0 | 0
102 | Music Room | 0 | 0 |  | 836 | 19 | 0 | AHU Inoperable | 6688 | 0 | 0
103 | Classroom | 0 | 0 |  | 638 | 14 | 0 | AHU Inoperable | 5104 | 0 | 0
104 | Classroom | 0 | 0 |  | 660 | 15 | 0 | AHU Inoperable | 5280 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 704 | 16 | 16 | AHU Inoperable | 5632 | 0 | 0
202 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0
203 | Classroom | 0 | 0 | Yes | 644 | 14 | 14 | AHU Inoperable | 5152 | 0 | 0
204 | Library | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0
205 | Fitness Storage | 0 | 0 | Yes | 690 | 15 | 15 | AHU Inoperable | 5520 | 0 | 0
206 | Fitness Storage | 0 | 0 |  | 704 | 16 | 0 | AHU Inoperable | 5632 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 660 | 15 | 15 | AHU Inoperable | 5280 | 0 | 0
208 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0
209 | Classroom | 0 | 0 |  | 187 | 4 | 0 | AHU Inoperable | 1496 | 0 | 0
210 | Classroom | 0 | 0 |  | 187 | 4 | 0 | AHU Inoperable | 1496 | 0 | 0
211 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | AHU Inoperable | 5456 | 0 | 0
212 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0
213 | Classroom | 0 | 0 |  | 374 | 8 | 0 | AHU Inoperable | 2992 | 0 | 0
214 | Classroom | 0 | 0 |  | 374 | 8 | 0 | AHU Inoperable | 2992 | 0 | 0
218 | Main Office |  | 0 | Yes | 210 | 4 | 4 | AHU Inoperable | 1680 | 0 | 0
301 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 |  | 5456 | 0 | 0
302 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0
303 | Classroom | 0 | 0 |  | 660 | 15 | 0 | AHU Inoperable | 5280 | 0 | 0
304 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0
305 | Classroom | 0 | 0 | Yes | 638 | 14 | 14 | AHU Inoperable | 5104 | 0 | 0
306 | Classroom | 0 | 0 |  | 144 | 3 | 0 | AHU Inoperable | 1152 | 0 | 0
307 | Classroom |  | 0 |  | 726 | 16 | 0 | AHU Inoperable | 5808 | 0 | 0
307A | Office |  | 0 |  | 264 | 6 | 0 |  | 2112 | 0 | 0
308 | Classroom | 0 | 0 |  | 1210 | 27 | 0 |  | 9680 | 0 | 0
309 | Office | 0 | 0 |  | 300 | 6 | 0 | AHU Inoperable | 2400 | 0 | 0
310 | Classroom | 0 | 0 |  | 96 | 2 | 0 | AHU Inoperable | 768 | 0 | 0
311 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0
312 | Classroom | 0 | 0 |  | 1078 | 24 | 0 | AHU Inoperable | 8624 | 0 | 0
313 | Room |  | 0 |  | 374 | 8 | 0 | AHU Inoperable | 2992 | 0 | 0
402 | Classroom | 0 | 0 |  | 880 | 20 | 0 |  | 7040 | 0 | 0
404 | Classroom | 0 | 0 |  | 704 | 16 | 0 | AHU Inoperable | 5632 | 0 | 0
406 | Classroom | 0 | 0 |  | 504 | 11 | 0 | AHU Inoperable | 4032 | 0 | 0
408 | Classroom | 0 | 0 |  | 672 | 15 | 0 | AHU Inoperable | 5376 | 0 | 0
410 | Classroom | 0 | 0 |  | 1008 | 22 | 0 | AHU Inoperable | 8064 | 0 | 0
412 | Office | 0 | 0 |  | 205 | 4 | 0 | AHU Inoperable | 1640 | 0 | 0
502 | Classroom | 0 | 0 |  | 880 | 20 | 0 | AHU Inoperable | 7040 | 0 | 0
506 | Classroom | 0 | 0 |  | 690 | 15 | 0 | AHU Inoperable | 5520 | 0 | 0
- | Game Room |  | 0 |  | 790 | 17 | 0 | AHU Inoperable | 6320 | 0 | 0
- | Auditorium | 0 | 0 |  | 5850 | 132 | 0 |  | 46800 | 0 | 0
- | Cafeteria | 0 | 0 |  | 3600 | 81 | 0 | AHU Inoperable | 28800 | 0 | 0
- | Counselor's Office |  | 0 |  | 110 | 2 | 0 | AHU Inoperable | 880 | 0 | 0
- | Counselor's Office |  | 0 |  | 110 | 2 | 0 |  | 880 | 0 | 0
- | Faculty Cafeteria | 0 | 0 |  | 726 | 16 | 0 |  | 5808 | 0 | 0
- | Gym | 0 | 0 | Yes | 6208 | 141 | 141 | AHU Inoperable | 49664 | 0 | 0
- | Boy's Locker Room |  | 0 |  | 580 | 13 | 0 |  | 4640 | 0 | 0
- | Girl's Locker Room |  | 0 |  | 209 | 4 | 0 |  | 1672 | 0 | 0
- | Health room |  | 0 |  | 100 | 2 | 0 |  | 800 | 0 | 0
- | Kitchen | 0 | 0 |  | 828 | 18 | 0 | AHU Inoperable | 6624 | 0 | 0
- | LIbrary Room |  | 0 |  | 620 | 14 | 0 |  | 4960 | 0 | 0
- | Library Office |  | 0 |  | 231 | 5 | 0 |  | 1848 | 0 | 0
- | Library A |  | 0 |  | 506 | 11 | 0 |  | 4048 | 0 | 0
- | Library B |  | 0 |  | 651 | 14 | 0 |  | 5208 | 0 | 0
- | Library C |  | 0 |  | 230 | 5 | 0 |  | 1840 | 0 | 0
- | Nurse Office | 0 | 0 | Yes | 170 | 3 | 3 | AHU Inoperable | 1360 | 0 | 0
| Nurse Examining |  | 0 | Yes | 100 | 2 | 2 |  | 800 | 0 | 0
| Nurse Roster Room |  | 0 | Yes | 288 | 6 | 6 |  | 2304 | 0 | 0
- | Robotics | 0 | 0 |  | 420 | 9 | 0 | AHU Inoperable | 3360 | 0 | 0
- | Science Office |  | 0 |  | 187 | 4 | 0 |  | 1496 | 0 | 0
- | Principal 's Office |  | 0 |  | 210 | 4 | 0 |  | 1680 | 0 | 0
- | Assant Principal's Office |  | 0 |  | 140 | 3 | 0 |  | 1120 | 0 | 0
- | Operations Office |  | 0 |  | 56 | 1 | 0 |  | 448 | 0 | 0
- | Office Waiting Area |  | 0 |  | 275 | 6 | 0 |  | 2200 | 0 | 0
- | Roster Office |  | 0 |  | 136 | 3 | 0 |  | 1088 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Mayfair Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Part 2 | Devine Part 3 | [5 empty] | 0 | 0 | 0
Vendor: | Capital | Capital Update | Capital Part 2 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 207 | 13 |  | 696 | 15 | 13 | Unit Ventilator | 5568 | 2.2306 | 1
101 | Classroom | 201 | 13 |  | 696 | 15 | 13 | Unit Ventilator | 5568 | 2.1659 | 1
102 | Classroom | 197 | 13 |  | 598 | 13 | 13 | Unit Ventilator | 4784 | 2.4707 | 1
103 | Classroom | 189 | 12 |  | 720 | 16 | 12 | Unit Ventilator | 5760 | 1.9688 | 1
104 | Classroom | 355 | 23 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.8587 | 1
105 | Classroom | 231 | 15 |  | 624 | 14 | 14 | Unit Ventilator | 4992 | 2.7764 | 1
106 | Classroom | 237 | 15 |  | 720 | 16 | 15 | Unit Ventilator | 5760 | 2.4688 | 1
107 | Classroom | 458 | 30 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 4.7708 | 2
108 | Classroom | 115 | 7 |  | 600 | 13 | 7 | Unit Ventilator | 4800 | 1.4375 | 1
109 | Classroom | 186 | 12 |  | 744 | 16 | 12 | Unit Ventilator | 5952 | 1.875 | 1
110 | Classroom | 418 | 27 |  | 696 | 15 | 15 | Unit Ventilator | 5568 | 4.5043 | 2
111 | Classroom | 202 | 13 |  | 624 | 14 | 13 | Unit Ventilator | 4992 | 2.4279 | 1
112 | Classroom | 461 | 30 |  | 1032 | 23 | 23 | Unit Ventilator | 8256 | 3.3503 | 1
113 | Classroom | 211 | 14 |  | 720 | 16 | 14 | Unit Ventilator | 5760 | 2.1979 | 1
114 | Classroom | 377 | 25 |  | 644 | 14 | 14 | Unit Ventilator | 5152 | 4.3905 | 2
115 | Classroom | 271 | 18 |  | 620 | 14 | 14 | Unit Ventilator | 4960 | 3.2782 | 1
116 | Classroom | 395 | 26 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 2.9954 | 1
118 | Classroom | 384 | 25 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.1739 | 2
119 | Classroom | 320 | 21 |  | 624 | 14 | 14 | Unit Ventilator | 4992 | 3.8462 | 1
120 | Classroom | 311 | 20 |  | 1610 | 36 | 20 | Unit Ventilator | 12880 | 1.4488 | 1
200 | Classroom |  | 0 | Yes | 205 | 4 | 4 |  | 1640 | 0 | 0
201 | Classroom | 286 | 19 |  | 696 | 15 | 15 | Unit Ventilator | 5568 | 3.0819 | 1
202 | Classroom | 560 | 37 |  | 696 | 15 | 15 | Unit Ventilator | 5568 | 6.0345 | 2
203 | Classroom | 381 | 25 |  | 725 | 16 | 16 | Unit Ventilator | 5800 | 3.9414 | 1
204 | Classroom | 323 | 21 |  | 884 | 20 | 20 | Unit Ventilator | 7072 | 2.7404 | 1
205 | Classroom | 271 | 18 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.6058 | 1
206 | Classroom | 316 | 21 |  | 806 | 18 | 18 | Unit Ventilator | 6448 | 2.9404 | 1
207 | Classroom | 295 | 19 |  | 806 | 18 | 18 | Unit Ventilator | 6448 | 2.745 | 1
207A | Asst. Principal Office | 0 | 0 | Yes | 293 | 6 | 6 | Unit Ventilator | 2344 | 0 | 0
208 | Classroom | 305 | 20 |  | 528 | 12 | 12 | Unit Ventilator | 4224 | 4.3324 | 2
209 | Classroom | 560 | 37 |  | 884 | 20 | 20 | Unit Ventilator | 7072 | 4.7511 | 2
210 | Classroom | 290 | 19 |  | 1118 | 25 | 19 | Unit Ventilator | 8944 | 1.9454 | 1
211 | Classroom | 307 | 20 |  | 648 | 14 | 14 | Unit Ventilator | 5184 | 3.5532 | 1
212 | Classroom | 483 | 32 |  | 665 | 15 | 15 | Unit Ventilator | 5320 | 5.4474 | 2
213 | Classroom | 590 | 39 |  | 806 | 18 | 18 | Unit Ventilator | 6448 | 5.4901 | 2
214 | Classroom | 300 | 20 |  | 806 | 18 | 18 | Unit Ventilator | 6448 | 2.7916 | 1
215 | Classroom | 294 | 19 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 3.0288 | 1
216 | Classroom | 317 | 21 |  | 648 | 14 | 14 | Unit Ventilator | 5184 | 3.669 | 1
217 | Classroom | 350 | 23 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 3.3568 | 1
218 | Classroom | 271 | 18 |  | 621 | 14 | 14 | Unit Ventilator | 4968 | 3.2729 | 1
219 | Classroom | 137 | 9 |  | 648 | 14 | 9 | Unit Ventilator | 5184 | 1.5856 | 1
220 | Classroom | 235 | 15 |  | 648 | 14 | 14 | Unit Ventilator | 5184 | 2.7199 | 1
221 | Classroom | 325 | 21 |  | 744 | 16 | 16 | Unit Ventilator | 5952 | 3.2762 | 1
222 | Classroom | 180 | 12 |  | 648 | 14 | 12 | Unit Ventilator | 5184 | 2.0833 | 1
301 | Classroom | 325 | 21 |  | 720 | 16 | 16 | ERU | 5760 | 3.3854 | 1
302 | Classroom | 304 | 20 |  | 720 | 16 | 16 | ERU | 5760 | 3.1667 | 1
303 | Classroom | 270 | 18 |  | 720 | 16 | 16 | ERU | 5760 | 2.8125 | 1
304 | Classroom | 435 | 29 |  | 720 | 16 | 16 | ERU | 5760 | 4.5312 | 2
305 | Classroom | 453 | 30 |  | 720 | 16 | 16 | ERU | 5760 | 4.7188 | 2
306 | Classroom | 480 | 32 |  | 720 | 16 | 16 | ERU | 5760 | 5 | 2
401 | Classroom | 320 | 21 |  | 720 | 16 | 16 | ERU | 5760 | 3.3333 | 1
402 | Classroom | 282 | 18 |  | 720 | 16 | 16 | ERU | 5760 | 2.9375 | 1
403 | Classroom | 551 | 36 |  | 720 | 16 | 16 | ERU | 5760 | 5.7396 | 2
404 | Classroom | 412 | 27 |  | 720 | 16 | 16 | ERU | 5760 | 4.2917 | 2
405 | Classroom | 412 | 27 |  | 720 | 16 | 16 | ERU | 5760 | 4.2917 | 2
406 | Classroom | 406 | 27 |  | 720 | 16 | 16 | ERU | 5760 | 4.2292 | 2
510 | Classroom | 282 | 18 |  | 754 | 17 | 17 | ERU | 6032 | 2.805 | 1
511 | Classroom | 430 | 28 |  | 754 | 17 | 17 | ERU | 6032 | 4.2772 | 2
512 | Classroom | 447 | 29 |  | 754 | 17 | 17 | ERU | 6032 | 4.4463 | 2
513 | Classroom | 543 | 36 |  | 754 | 17 | 17 | ERU | 6032 | 5.4012 | 2
515 | Classroom | 652 | 43 |  | 754 | 17 | 17 | ERU | 6032 | 6.4854 | 2
516 | Classroom | 519 | 34 |  | 754 | 17 | 17 | ERU | 6032 | 5.1625 | 2
517 | Classroom | 605 | 40 |  | 754 | 17 | 17 | ERU | 6032 | 6.0179 | 2
520 | Classroom | 500 | 33 |  | 754 | 17 | 17 | ERU | 6032 | 4.9735 | 2
521 | Classroom | 548 | 36 |  | 754 | 17 | 17 | ERU | 6032 | 5.4509 | 2
522 | Classroom | 530 | 35 |  | 754 | 17 | 17 | ERU | 6032 | 5.2719 | 2
523 | Classroom | 509 | 33 |  | 754 | 17 | 17 | ERU | 6032 | 5.063 | 2
525 | Classroom | 676 | 45 |  | 754 | 17 | 17 | ERU | 6032 | 6.7241 | 2
526 | Classroom | 646 | 43 |  | 754 | 17 | 17 | ERU | 6032 | 6.4257 | 2
527 | Classroom | 568 | 37 |  | 774 | 17 | 17 | ERU | 6192 | 5.5039 | 2
- | Main Office |  | 0 | Yes | 493 | 11 | 11 |  | 3944 | 0 | 0
- | Counselor Office |  | 0 | Yes | 126 | 2 | 2 |  | 1008 | 0 | 0
- | Counselor Office |  | 0 | Yes | 231 | 5 | 5 |  | 1848 | 0 | 0
- | Principal Office |  | 0 | Yes | 196 | 4 | 4 |  | 1568 | 0 | 0
- | Special Education |  | 0 | Yes | 275 | 6 | 6 |  | 2200 | 0 | 0
- | Conference Room |  | 0 | Yes | 135 | 3 | 3 |  | 1080 | 0 | 0
- | Faculty Room |  | 0 | Yes | 171 | 3 | 3 |  | 1368 | 0 | 0
- | Nurse Office |  | 0 | Yes | 372 | 8 | 8 |  | 2976 | 0 | 0
- | Asst. Principal 1 |  | 0 | Yes | 86 | 1 | 1 |  | 688 | 0 | 0
- | Asst. Principal 2 |  | 0 | Yes | 97 | 2 | 2 |  | 776 | 0 | 0
- | Auditorium |  | 0 |  | 4920 | 111 | 0 | AHU | 39360 | 0 | 0
| Auditorium Room 1 |  | 0 | Yes | 263 | 5 | 5 |  | 2104 | 0 | 0
| Auditorium Room 2 |  | 0 | Yes | 254 | 5 | 5 |  | 2032 | 0 | 0
Music 1 | Room |  | 0 | Yes | 354 | 8 | 8 |  | 2832 | 0 | 0
Music 2 | Room |  | 0 | Yes | 711 | 16 | 16 |  | 5688 | 0 | 0
- | Cafeteria | 998 | 66 |  | 3257 | 74 | 66 | RTU | 26056 | 2.2981 | 1
- | Gym |  | 0 | Yes | 3982 | 90 | 90 | AHU | 31856 | 0 | 0
School Police | Office |  | 0 | Yes | 54 | 1 | 1 |  | 432 | 0 | 0
- | Nurse Office | 292 | 19 |  | 372 | 8 | 8 | Unit Ventilator | 2976 | 5.8871 | 2
1 | Mobile Classroom | 326 | 21 |  | 594 | 13 | 13 | AHU | 4752 | 4.1162 | 2
2 | Mobile Classroom | 328 | 21 |  | 594 | 13 | 13 | AHU | 4752 | 4.1414 | 2
3 | Mobile Classroom | 644 | 42 |  | 594 | 13 | 13 | AHU | 4752 | 8.1313 | 2
4 | Mobile Classroom | 451 | 30 |  | 594 | 13 | 13 | AHU | 4752 | 5.6944 | 2
5 | Mobile Classroom | 580 | 38 |  | 594 | 13 | 13 | AHU | 4752 | 7.3232 | 2
6 | Mobile Classroom | 438 | 29 |  | 594 | 13 | 13 | AHU | 4752 | 5.5303 | 2
7 | Mobile Classroom | 414 | 27 |  | 594 | 13 | 13 | AHU | 4752 | 5.2273 | 2
8 | Mobile Classroom | 574 | 38 |  | 594 | 13 | 13 | AHU | 4752 | 7.2475 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-06 | [7 empty] | 0 | 0 | 0
School: | General George A. McCall Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | 2nd Retest | 3rd Retest | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
0 | Classroom | 0 | 0 | Yes | 572 | 13 | 13 | N/A | 4576 | 0 | 0
1 | Classroom | 370 | 24 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 3.0032 | 1
2 | Music Room | 453 | 30 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 4.064 | 2
4 | Classroom | 1631 | 108 |  | 660 | 15 | 15 | AHU | 5280 | 18.5341 | 3
5 | Classroom | 478 | 31 |  | 1012 | 23 | 23 | AHU | 8096 | 3.5425 | 1
6 | Classroom | 535 | 35 |  | 1100 | 25 | 25 | AHU | 8800 | 3.6477 | 1
101 | Office | 0 | 0 | Yes | 276 | 6 | 6 | N/A | 2208 | 0 | 0
101A | Office | 182 | 12 | Yes | 440 | 10 | 10 | Unit Ventilator | 3520 | 3.1023 | 1
102 | Classroom | 332 | 22 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.9785 | 1
103 | Classroom | 283 | 18 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.4119 | 1
105 | Classroom | 278 | 18 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.3693 | 1
106 | Classroom | 340 | 22 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.7597 | 1
107 | Classroom | 292 | 19 | Yes | 968 | 22 | 22 | Unit Ventilator | 7744 | 2.2624 | 1
108 | Classroom | 303 | 20 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.7183 | 1
109 | Classroom | 375 | 25 |  | 880 | 20 | 20 | Unit Ventilator | 7040 | 3.196 | 1
110 | Classroom | 0 | 0 | Yes | 220 | 5 | 5 | N/A | 1760 | 0 | 0
110A | Office | 336 | 22 |  | 440 | 10 | 10 | Unit Ventilator | 3520 | 5.7273 | 2
209 | Classroom | 0 | 0 | Yes | 440 | 10 | 10 | Unit Ventilator | 3520 | 0 | 0
210 | Classroom | 273 | 18 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.3267 | 1
211 | Classroom | 293 | 19 | Yes | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.3782 | 1
212 | Classroom | 294 | 19 |  | 880 | 20 | 19 | Unit Ventilator | 7040 | 2.5057 | 1
213 | Classroom | 320 | 21 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.5974 | 1
214 | Classroom | 376 | 25 |  | 880 | 20 | 20 | Unit Ventilator | 7040 | 3.2045 | 1
216A | Office | 0 | 0 | Yes | 480 | 10 | 10 | N/A | 3840 | 0 | 0
217 | Classroom | 297 | 19 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.8125 | 1
218 | Classroom | 309 | 20 |  | 924 | 21 | 20 | Unit Ventilator | 7392 | 2.5081 | 1
219 | Classroom | 313 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.964 | 1
318 | Classroom | 172 | 11 | Yes | 748 | 17 | 17 | Unit Ventilator | 5984 | 1.7246 | 1
319 | Classroom | 368 | 24 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.987 | 1
320 | Classroom | 401 | 26 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 3.5975 | 1
321 | Classroom | 329 | 21 |  | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.804 | 1
322 | Classroom | 292 | 19 |  | 924 | 21 | 19 | Unit Ventilator | 7392 | 2.3701 | 1
323 | Classroom | 351 | 23 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.849 | 1
324 | Classroom | 284 | 18 |  | 880 | 20 | 18 | Unit Ventilator | 7040 | 2.4205 | 1
325 | Classroom | 396 | 26 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 3.2143 | 1
326 | Classroom | 309 | 20 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.7721 | 1
327 | Classroom | 345 | 23 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.267 | 1
327A | Classroom | 261 | 17 |  | 484 | 11 | 11 | Unit Ventilator | 3872 | 4.0444 | 2
- | Auditorium | 1451 | 96 |  | 4224 | 96 | 96 | AHU | 33792 | 2.5763 | 1
- | Gym/Cafeteria | 1279 | 85 |  | 3740 | 85 | 85 | AHU | 29920 | 2.5648 | 1
- | Main Office | 311 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.9451 | 1
- | Library | 492 | 32 |  | 1584 | 36 | 32 | Unit Ventilator | 12672 | 2.3295 | 1
- | Engineer Office | 0 | 0 |  | 432 | 9 | 0 | N/A | 3456 | 0 | 0
- | Gym Office | 0 | 0 |  | 110 | 2 | 0 | AHU | 880 | 0 | 0
- | Kitchen | 9 | 0 | Yes | 384 | 8 | 8 | AHU | 3072 | 0.17578 | 0
- | Principals Office | 0 | 0 | Yes | 493 | 11 | 11 | AHU | 3944 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-13 | [7 empty] | 0 | 0 | 0
School: | John F. McCloskey Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Part 2 | Part 3 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
2 | IMC |  | 0 | Yes | 1044 | 23 | 23 | Unit Ventilator | 8352 | 0 | 0
7 | Recovery. room |  | 0 | Yes | 180 | 4 | 4 | Convector | 1440 | 0 | 0
101 | Classroom | 229 | 15 |  | 936 | 21 | 15 | Unit Ventilator | 7488 | 1.8349 | 1
102 | Classroom | 192 | 12 |  | 936 | 21 | 12 | Unit Ventilator | 7488 | 1.5385 | 1
103 | Classroom | 394 | 26 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 3.1571 | 1
104 | Classroom | 155 | 10 | Yes | 1056 | 24 | 24 | Unit Ventilator | 8448 | 1.1009 | 1
105 | Classroom | 342 | 22 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 2.8595 | 1
106 | Classroom | 203 | 13 |  | 936 | 21 | 13 | Unit Ventilator | 7488 | 1.6266 | 1
107 | Classroom | 206 | 13 |  | 936 | 21 | 13 | Unit Ventilator | 7488 | 1.6506 | 1
108 | Classroom | 390 | 26 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 3.125 | 1
109 | Classroom | 282 | 18 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 2.8736 | 1
111 | Classroom | 356 | 23 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 3.6277 | 1
113 | Classroom | 320 | 21 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 3.2609 | 1
114 | Classroom | 319 | 21 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 3.2507 | 1
201 | Classroom |  | 0 |  | 916 | 20 | 0 | Unit Ventilator | 7328 | 0 | 0
202 | Classroom | 200 | 13 |  | 936 | 21 | 13 | Unit Ventilator | 7488 | 1.6026 | 1
203 | Classroom | 194 | 12 |  | 936 | 21 | 12 | Unit Ventilator | 7488 | 1.5545 | 1
204 | Classroom | 378 | 25 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 3.0288 | 1
205 | Classroom | 342 | 22 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 2.7404 | 1
206 | Classroom | 487 | 32 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 3.9022 | 1
208 | Classroom | 346 | 23 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 2.7724 | 1
209 | Classroom | 514 | 34 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 4.1186 | 2
210 | Classroom | 247 | 16 |  | 936 | 21 | 16 | Unit Ventilator | 7488 | 1.9792 | 1
211 | Classroom | 374 | 24 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 2.9968 | 1
- | Auditorium |  | 0 |  | 2700 | 61 | 0 | AHU | 21600 | 0 | 0
- | Computer Room | 40 | 2 |  | 1080 | 24 | 2 | Unit Ventilator | 8640 | 0.27778 | 0
- | Gym |  | 0 | Yes | 3744 | 85 | 85 | AHU | 29952 | 0 | 0
- | Main Office |  | 0 | Yes | 338 | 7 | 7 | Convector | 2704 | 0 | 0
- | Prin. Office |  | 0 | Yes | 312 | 7 | 7 | Convector | 2496 | 0 | 0
- | Nurse. Office |  | 0 | Yes | 225 | 5 | 5 | Convector | 1800 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | Alexander K. McClure Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Retest | 2nd Retest | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
0 | Building Engineer | 0 | 0 |  |  | 0 | 0 | N/A | 0 | 0 | 0
1 | Gym | 650 | 43 |  | 2486 | 56 | 43 | House Fan | 19888 | 1.961 | 1
6 | Art | 302 | 20 |  | 894 | 20 | 20 | House Fan | 7152 | 2.5336 | 1
7 | Classroom | 559 | 37 |  | 839 | 19 | 19 | House Fan | 6712 | 4.997 | 2
11 | Classroom | 523 | 34 |  | 821 | 18 | 18 | House Fan | 6568 | 4.7777 | 2
101 | Classroom | 603 | 40 |  | 887 | 20 | 20 | House Fan | 7096 | 5.0986 | 2
106 | Classroom | 419 | 27 |  | 927 | 21 | 21 | House Fan | 7416 | 3.39 | 1
106A | Asst. Principal | 0 | 0 | Yes | 104 | 2 | 2 | House Fan | 832 | 0 | 0
107 | Classroom | 505 | 33 |  | 753 | 17 | 17 | House Fan | 6024 | 5.0299 | 2
108 | Classroom | 329 | 21 |  | 849 | 19 | 19 | House Fan | 6792 | 2.9064 | 1
109 | Classroom | 454 | 30 |  | 791 | 17 | 17 | House Fan | 6328 | 4.3047 | 2
110 | Classroom | 603 | 40 |  | 725 | 16 | 16 | House Fan | 5800 | 6.2379 | 2
111 | Classroom | 537 | 35 |  | 699 | 15 | 15 | House Fan | 5592 | 5.7618 | 2
201 | Classroom | 585 | 39 |  | 847 | 19 | 19 | House Fan | 6776 | 5.18 | 2
202 | Classroom | 597 | 39 |  | 883 | 20 | 20 | House Fan | 7064 | 5.0708 | 2
203 | Classroom | 423 | 28 |  | 903 | 20 | 20 | House Fan | 7224 | 3.5133 | 1
204 | Classroom | 461 | 30 |  | 887 | 20 | 20 | House Fan | 7096 | 3.898 | 1
205 | Classroom | 482 | 32 |  | 945 | 21 | 21 | House Fan | 7560 | 3.8254 | 1
206 | Library | 431 | 28 |  | 890 | 20 | 20 | House Fan | 7120 | 3.632 | 1
206A | Nurse Office | 0 | 0 |  | 194 | 4 | 0 | N/A | 1552 | 0 | 0
206B | Nurse Exam | 0 | 0 | Yes | 362 | 8 | 8 | House Fan | 2896 | 0 | 0
207 | Classroom | 442 | 29 |  | 869 | 19 | 19 | House Fan | 6952 | 3.8147 | 1
208 | Classroom | 309 | 20 |  | 812 | 18 | 18 | House Fan | 6496 | 2.8541 | 1
209 | Classroom | 412 | 27 |  | 823 | 18 | 18 | House Fan | 6584 | 3.7546 | 1
210 | Classroom | 602 | 40 |  | 714 | 16 | 16 | House Fan | 5712 | 6.3235 | 2
211 | Classroom | 595 | 39 |  | 740 | 16 | 16 | House Fan | 5920 | 6.0304 | 2
301 | Classroom | 559 | 37 |  | 882 | 20 | 20 | House Fan | 7056 | 4.7534 | 2
302 | Classroom | 501 | 33 |  | 902 | 20 | 20 | House Fan | 7216 | 4.1657 | 2
303 | Classroom | 377 | 25 |  | 900 | 20 | 20 | House Fan | 7200 | 3.1417 | 1
304 | Classroom | 483 | 32 |  | 875 | 19 | 19 | House Fan | 7000 | 4.14 | 2
305 | Classroom | 469 | 31 |  | 910 | 20 | 20 | House Fan | 7280 | 3.8654 | 1
306 | Classroom | 402 | 26 |  | 894 | 20 | 20 | House Fan | 7152 | 3.3725 | 1
306A | Office | 0 | 0 | Yes | 185 | 4 | 4 | House Fan | 1480 | 0 | 0
307 | Classroom | 470 | 31 |  | 932 | 21 | 21 | House Fan | 7456 | 3.7822 | 1
308 | Classroom | 301 | 20 |  | 815 | 18 | 18 | House Fan | 6520 | 2.7699 | 1
309 | Classroom | 313 | 20 |  | 851 | 19 | 19 | House Fan | 6808 | 2.7585 | 1
310 | Classroom | 396 | 26 |  | 726 | 16 | 16 | House Fan | 5808 | 4.0909 | 2
311 | Classroom | 406 | 27 |  | 732 | 16 | 16 | House Fan | 5856 | 4.1598 | 2
312 | Classroom | 0 | 0 | Yes | 435 | 9 | 9 | N/A | 3480 | 0 | 0
- | 4th Floor Office N | 0 | 0 |  |  | 0 | 0 | N/A | 0 | 0 | 0
- | 4th Floor Office S | 0 | 0 |  |  | 0 | 0 | N/A | 0 | 0 | 0
- | Cafeteria | 1876 | 125 |  | 2974 | 67 | 67 | House Fan | 23792 | 4.731 | 2
- | Main Office | 0 | 0 | Yes | 262 | 5 | 5 | N/A | 2096 | 0 | 0
- | Principal Office | 0 | 0 | Yes | 194 | 4 | 4 | N/A | 1552 | 0 | 0
- | Portable Classroom | 289 | 19 |  | 1290 | 29 | 19 | Unit Ventilators | 10320 | 1.6802 | 1
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Delaplaine McDaniel Elementary-Middle School | [7 empty] | 0 | 0 | 0
| McDaniel Annex (St. Edmunds) | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
McDaniel Main | [8 empty] | 0 | 0 | 0
102 | Classroom | 865 | 57 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 9.8295 | 2
103 | Classroom | 250 | 16 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 2.8409 | 1
104 | Classroom | 340 | 22 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 3.0502 | 1
105 | Classroom | 275 | 18 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.125 | 1
107 | Classroom | 1025 | 68 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 11.6477 | 3
108 | Classroom |  | 0 | Yes | 464 | 10 | 10 |  | 3712 | 0 | 0
109 | Classroom | 550 | 36 |  | 1260 | 28 | 28 | Unit Ventilator | 10080 | 3.2738 | 1
200 | Classroom | 430 | 28 |  | 1260 | 28 | 28 | Unit Ventilator | 10080 | 2.5595 | 1
201 | Classroom | 0 | 0 |  | 396 | 9 | 0 | Unit Ventilator | 3168 | 0 | 0
203 | Classroom | 635 | 42 |  | 630 | 14 | 14 | Unit Ventilator | 5040 | 7.5595 | 2
204 | Computer Lab | 949 | 63 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 7.7029 | 2
205 | Classroom | 635 | 42 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 7.2159 | 2
206 | Classroom | 475 | 31 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 4.1521 | 2
207 | Classroom | 0 | 0 |  | 783 | 17 | 0 | Unit Ventilator | 6264 | 0 | 0
209 | Classroom | 0 | 0 |  | 777 | 17 | 0 | Unit Ventilator | 6216 | 0 | 0
300 | Classroom | 0 | 0 | Yes | 819 | 18 | 18 | Unit Ventilator | 6552 | 0 | 0
301 | Classroom | 0 | 0 |  | 691 | 15 | 0 | Unit Ventilator | 5528 | 0 | 0
303 | Classroom | 428 | 28 |  | 945 | 21 | 21 | Unit Ventilator | 7560 | 3.3968 | 1
304 | Classroom | 134 | 8 |  | 704 | 16 | 8 | Unit Ventilator | 5632 | 1.4276 | 1
305 | Classroom | 374 | 24 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 4.3966 | 2
306 | Classroom | 185 | 12 |  | 638 | 14 | 12 | Unit Ventilator | 5104 | 2.1748 | 1
307 | Classroom | 570 | 38 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 6.7006 | 2
308 | Classroom | 470 | 31 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 5.5251 | 2
309 | Classroom | 400 | 26 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 4.7022 | 2
310 | Classroom | 494 | 32 |  | 880 | 20 | 20 | Unit Ventilator | 7040 | 4.2102 | 2
311 | Classroom | 430 | 28 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 5.0549 | 2
313 | Classroom | 1099 | 73 |  | 814 | 18 | 18 | Unit Ventilator | 6512 | 10.1259 | 3
- | Gym | 0 | 0 | Yes | 3300 | 75 | 75 | AHU | 26400 | 0 | 0
- | Gym Office |  | 0 | Yes | 77 | 1 | 1 |  | 616 | 0 | 0
- | Nurse Office |  | 0 | Yes | 280 | 6 | 6 |  | 2240 | 0 | 0
- | Media Center | 700 | 46 |  | 1078 | 24 | 24 | Unit Ventilator | 8624 | 4.8701 | 2
- | Kitchen |  | 0 | Yes | 294 | 6 | 6 |  | 2352 | 0 | 0
- | School Police |  | 0 | Yes | 90 | 2 | 2 |  | 720 | 0 | 0
- | Counselor Office |  | 0 | Yes | 117 | 2 | 2 |  | 936 | 0 | 0
- | Principals Office |  | 0 | Yes | 196 | 4 | 4 |  | 1568 | 0 | 0
- | Vice Principal |  | 0 | Yes | 187 | 4 | 4 |  | 1496 | 0 | 0
- | Office | 0 | 0 | Yes | 392 | 8 | 8 | AHU | 3136 | 0 | 0
McDaniel Annex (St. Edmunds) | [8 empty] | 0 | 0 | 0
K-1 | Classroom | 269 | 17 |  | 516 | 11 | 11 | Unit Ventilator | 4128 | 3.9099 | 1
K-2 | Classroom | 449 | 29 |  | 616 | 14 | 14 | Unit Ventilator | 4928 | 5.4667 | 2
K-3 | Classroom | 407 | 27 |  | 616 | 14 | 14 | Unit Ventilator | 4928 | 4.9554 | 2
K-4 | Classroom | 348 | 23 |  | 516 | 11 | 11 | Unit Ventilator | 4128 | 5.0581 | 2
206 | Classroom | 350 | 23 |  | 616 | 14 | 14 | Unit Ventilator | 4928 | 4.2614 | 2
207 | Classroom | 530 | 35 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 5.0189 | 2
208 | Classroom | 632 | 42 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 7.1818 | 2
209 | Classroom | 495 | 33 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 5.625 | 2
210 | Classroom | 375 | 25 |  | 440 | 10 | 10 | Unit Ventilator | 3520 | 6.392 | 2
213 | Classroom | 447 | 29 |  | 440 | 10 | 10 | Unit Ventilator | 3520 | 7.6193 | 2
215 | Classroom | 640 | 42 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 6.0606 | 2
306 | Classroom | 525 | 35 |  | 616 | 14 | 14 | Unit Ventilator | 4928 | 6.392 | 2
307 | Classroom | 653 | 43 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 6.1837 | 2
308 | Classroom | 425 | 28 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 4.8295 | 2
309 | Classroom | 630 | 42 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 7.1591 | 2
310 | Classroom | 471 | 31 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 5.3523 | 2
312 | Classroom | 481 | 32 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 5.1243 | 2
313 | Classroom | 611 | 40 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 6.5092 | 2
- | Cafeteria / Gym | 14007 | 933 |  | 3960 | 90 | 90 | AHU | 31680 | 26.5284 | 4
- | Classroom | 15010 | 1000 |  | 1431 | 32 | 32 | AHU | 11448 | 78.6688 | 5
Sheet Last Modified: | 2021-04-06 | [7 empty] | 0 | 0 | 0
School: | William McKinley Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | A1/11 | 529 | 35 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 4.6241 | 2
- | A2/12 | 627 | 41 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 5.652 | 2
- | A3/13 | 298 | 19 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 2.6049 | 1
- | A4/14 | 512 | 34 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 4.4755 | 2
- | Autistic Support 8 | 231 | 15 |  | 726 | 16 | 15 | Unit Ventilator | 5808 | 2.3864 | 1
- | B1/21 | 711 | 47 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 6.733 | 2
- | B2/22 | 630 | 42 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 6.2666 | 2
- | B3/23 | 660 | 44 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 6.565 | 2
- | B4/24 | 538 | 35 |  | 744 | 16 | 16 | Unit Ventilator | 5952 | 5.4234 | 2
- | C1/31 | 604 | 40 |  | 726 | 16 | 16 | Unit Ventilator | 5808 | 6.2397 | 2
- | C2/32 | 271 | 18 |  | 675 | 15 | 15 | Unit Ventilator | 5400 | 3.0111 | 1
- | C3/33 | 605 | 40 |  | 700 | 15 | 15 | Unit Ventilator | 5600 | 6.4821 | 2
- | C4/34 | 669 | 44 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 6.9688 | 2
- | CCTC 11 | 1062 | 70 |  | 1215 | 27 | 27 | Unit Ventilator | 9720 | 6.5556 | 2
- | D1 | 426 | 28 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 3.7238 | 1
- | D2 | 553 | 36 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 5.3173 | 2
- | D3 | 290 | 19 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.7885 | 1
- | D4 | 310 | 20 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.9808 | 1
- | Gymnasium | 1525 | 101 |  | 2860 | 65 | 65 | AHU | 22880 | 3.9991 | 1
- | Kindergarten 1 | 355 | 23 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.8815 | 1
- | Kindergarten 2 | 290 | 19 | Yes | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.3539 | 1
- | Kindergarten 3 | 282 | 18 | Yes | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.289 | 1
- | Pre K 4 | 739 | 49 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 5.9984 | 2
- | Room 5 | 611 | 40 |  | 726 | 16 | 16 | Unit Ventilator | 5808 | 6.312 | 2
-- | Room 6 | 467 | 31 |  | 726 | 16 | 16 | Unit Ventilator | 5808 | 4.8244 | 2
- | Room 9 / Visual Arts | 748 | 49 |  | 726 | 16 | 16 | AHU | 5808 | 7.7273 | 2
- | Room 12 | 587 | 39 |  | 809 | 18 | 18 | AHU | 6472 | 5.4419 | 2
A-0 | Small Classroom | 37 | 2 |  | 150 | 3 | 2 | AHU | 1200 | 1.85 | 1
7 | Teachers Lounge | 59 | 3 | Yes | 351 | 7 | 7 | AHU | 2808 | 1.2607 | 1
- | Nurse Exam Large | 69 | 4 | Yes | 252 | 5 | 5 | AHU | 2016 | 2.0536 | 1
- | Nurse Office | 38 | 2 |  | 119 | 2 | 2 | AHU | 952 | 2.395 | 1
- | Nurse Exam | 59 | 3 |  | 153 | 3 | 3 | AHU | 1224 | 2.8922 | 1
- | Storage Large | 61 | 4 |  | 216 | 4 | 4 | AHU | 1728 | 2.1181 | 1
- | Storage | 24 | 1 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | Auditorium | 1667 | 111 |  | 2453 | 55 | 55 | AHU | 19624 | 5.0968 | 2
- | Music Room | 319 | 21 |  | 727 | 16 | 16 | AHU | 5816 | 3.2909 | 1
- | Library | 1047 | 69 |  | 3888 | 88 | 69 | AHU | 31104 | 2.0197 | 1
- | Cafeteria | 894 | 59 |  | 2331 | 52 | 52 | AHU | 18648 | 2.8764 | 1
D-0 | Small Classroom | 36 | 2 |  | 150 | 3 | 2 | AHU | 1200 | 1.8 | 1
C-0 | Small Classroom | 21 | 1 |  | 150 | 3 | 1 | AHU | 1200 | 1.05 | 1
B-0 | Small Classroom | 53 | 3 |  | 150 | 3 | 3 | AHU | 1200 | 2.65 | 1
10 | Small Classroom | 26 | 1 | Yes | 364 | 8 | 8 | AHU | 2912 | 0.53571 | 0
- | Main Office | 50 | 3 | Yes | 817 | 18 | 18 | AHU | 6536 | 0.459 | 0
- | Admin Office 1 | 52 | 3 |  | 128 | 2 | 2 | AHU | 1024 | 3.0469 | 1
- | Admin Office 2 | 73 | 4 |  | 128 | 2 | 2 | AHU | 1024 | 4.2773 | 2
- | Admin Office 3 | 43 | 2 |  | 128 | 2 | 2 | AHU | 1024 | 2.5195 | 1
- | Admin Office 5 | 50 | 3 |  | 160 | 3 | 3 | AHU | 1280 | 2.3438 | 1
- | Admin Office 6 | 49 | 3 |  | 285 | 6 | 3 | AHU | 2280 | 1.2895 | 1
- | Admin Office 7 | 22 | 1 | Yes | 120 | 2 | 2 | AHU | 960 | 1.375 | 1
- | Equip Storage | 0 | 0 |  | 120 | 2 | 0 | AHU | 960 | 0 | 0
- | Corridor | 35 | 2 |  | 440 | 10 | 2 | AHU | 3520 | 0.59659 | 0
- | Principals Office | 35 | 2 | Yes | 180 | 4 | 4 | AHU | 1440 | 1.4583 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Morton McMichael Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Part 2 | Part 3 | [5 empty] | 0 | 0 | 0
| Part 4 | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Staff Lounge | 125 | 8 |  | 468 | 10 | 8 | Unit Ventilator | 3744 | 2.0032 | 1
101 | Admin | 281 | 18 |  | 1056 | 24 | 18 | Unit Ventilator | 8448 | 1.9957 | 1
102 | Superintendants | 284 | 18 |  | 600 | 13 | 13 | Unit Ventilator | 4800 | 3.55 | 1
- | IT Office |  | 0 |  | 459 | 10 | 0 |  | 3672 | 0 | 0
104 | Small Conf/Assis. Super | 110 | 7 |  | 252 | 5 | 5 | Unit Ventilator | 2016 | 3.2738 | 1
105 | Large Conference | 319 | 21 |  | 1188 | 27 | 21 | Unit Ventilator | 9504 | 2.0139 | 1
108 | Classroom | 375 | 25 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.2552 | 1
110 | Classroom | 279 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4911 | 1
114 | Classroom | 284 | 18 |  | 576 | 13 | 13 | Unit Ventilator | 4608 | 3.6979 | 1
200 | Classroom | 340 | 22 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.0357 | 1
201 | Classroom | 328 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9286 | 1
201A | Classroom | 320 | 21 |  | 336 | 7 | 7 | Unit Ventilator | 2688 | 7.1429 | 2
202 | Classroom | 292 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6071 | 1
204 | Classroom | 272 | 18 |  | 2592 | 58 | 18 | Unit Ventilator | 20736 | 0.78704 | 0
205 | Classroom | 326 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9107 | 1
206 | Classroom | 275 | 18 |  | 2592 | 58 | 18 | Unit Ventilator | 20736 | 0.79572 | 0
207 | Classroom | 318 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.8393 | 1
208 | Classroom | 249 | 16 |  | 2592 | 58 | 16 | Unit Ventilator | 20736 | 0.72049 | 0
210 | Classroom | 351 | 23 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.1339 | 1
212 | Classroom | 363 | 24 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.2411 | 1
214 | Classroom | 282 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.5179 | 1
216 | Classroom | 262 | 17 |  | 864 | 19 | 17 | Unit Ventilator | 6912 | 2.2743 | 1
217 | Classroom | 368 | 24 |  | 1944 | 44 | 24 | Unit Ventilator | 15552 | 1.4198 | 1
218 | Classroom | 320 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.8571 | 1
219 | Classroom | 351 | 23 |  | 1944 | 44 | 23 | Unit Ventilator | 15552 | 1.3542 | 1
220 | Classroom | 403 | 26 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.5982 | 1
222 | Classroom | 280 | 18 |  | 504 | 11 | 11 | Unit Ventilator | 4032 | 4.1667 | 2
224 | Classroom |  | 0 |  | 840 | 19 | 0 | Unit Ventilator | 6720 | 0 | 0
226 | Classroom | 240 | 16 |  | 840 | 19 | 16 | Unit Ventilator | 6720 | 2.1429 | 1
300 | Classroom | 239 | 15 |  | 840 | 19 | 15 | Unit Ventilator | 6720 | 2.1339 | 1
301 | Classroom | 291 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.5982 | 1
302 | Classroom | 302 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6964 | 1
303 | Classroom | 288 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.5714 | 1
305 | Classroom | 317 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.8304 | 1
306 | Classroom | 546 | 36 |  | 1248 | 28 | 28 | Unit Ventilator | 9984 | 3.2812 | 1
307 | Classroom | 274 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4464 | 1
308 | Classroom | 273 | 18 |  | 864 | 19 | 18 | Unit Ventilator | 6912 | 2.3698 | 1
310 | Classroom | 272 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4286 | 1
312 | Classroom | 281 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.5089 | 1
314 | Classroom | 306 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7321 | 1
316 | Classroom | 315 | 21 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.7344 | 1
317 | Classroom | 392 | 26 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.5 | 1
318 | Classroom | 274 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4464 | 1
319 | Classroom | 276 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4643 | 1
320 | Classroom | 281 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.5089 | 1
322 | Classroom | 270 | 18 |  | 576 | 13 | 13 | Unit Ventilator | 4608 | 3.5156 | 1
323 | Classroom | 279 | 18 |  | 864 | 19 | 18 | Unit Ventilator | 6912 | 2.4219 | 1
324 | Classroom | 326 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9107 | 1
325 | Classroom | 285 | 19 |  | 888 | 20 | 19 | Unit Ventilator | 7104 | 2.4071 | 1
326 | Classroom | 262 | 17 |  | 864 | 19 | 17 | Unit Ventilator | 6912 | 2.2743 | 1
- | Auditorium | 520 | 34 |  | 4914 | 111 | 34 | AHU | 39312 | 0.79365 | 0
- | Cafe | 590 | 39 |  | 2485 | 56 | 39 | AHU | 19880 | 1.7807 | 1
- | Gym | 690 | 46 |  | 3621 | 82 | 46 | AHU | 28968 | 1.4292 | 1
- | Main Office |  | 0 | Yes | 1401 | 31 | 31 |  | 11208 | 0 | 0
- | Nurse Office |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-06 | [7 empty] | 0 | 0 | 0
School: | General George G. Meade Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
15 | Classroom | 378 | 25 | Yes | 644 | 14 | 14 | Unit Ventilator | 5152 | 4.4022 | 2
16 | Classroom | 336 | 22 |  | 833 | 18 | 18 | Unit Ventilator | 6664 | 3.0252 | 1
17 | Classroom | 184 | 12 |  | 330 | 7 | 7 | Unit Ventilator | 2640 | 4.1818 | 2
18 | Classroom | 686 | 45 | Yes | 1101 | 25 | 25 | Unit Ventilator | 8808 | 4.673 | 2
101 | Classroom | 294 | 19 |  | 892 | 20 | 19 | Unit Ventilator | 7136 | 2.472 | 1
102 | Classroom | 299 | 19 | Yes | 765 | 17 | 17 | Unit Ventilator | 6120 | 2.9314 | 1
103 | Classroom | 360 | 24 | Yes | 823 | 18 | 18 | Unit Ventilator | 6584 | 3.2807 | 1
104 | Classroom | 281 | 18 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 2.9894 | 1
105 | Classroom | 445 | 29 |  | 674 | 15 | 15 | Unit Ventilator | 5392 | 4.9518 | 2
106 | Classroom | 405 | 27 |  | 846 | 19 | 19 | Unit Ventilator | 6768 | 3.5904 | 1
107 | Classroom | 332 | 22 |  | 526 | 11 | 11 | Unit Ventilator | 4208 | 4.7338 | 2
108 | Classroom | 294 | 19 |  | 670 | 15 | 15 | Unit Ventilator | 5360 | 3.291 | 1
109 | Classroom | 279 | 18 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 2.9681 | 1
115 | Classroom | 640 | 42 | Yes | 865 | 19 | 19 | Unit Ventilator | 6920 | 5.5491 | 2
116 | Classroom | 325 | 21 | Yes | 413 | 9 | 9 | Unit Ventilator | 3304 | 5.9019 | 2
117 | Classroom | 433 | 28 | Yes | 837 | 19 | 19 | Unit Ventilator | 6696 | 3.8799 | 1
118 | Classroom | 664 | 44 | Yes | 849 | 19 | 19 | Unit Ventilator | 6792 | 5.8657 | 2
200 | Classroom | 193 | 12 |  | 349 | 7 | 7 | Unit Ventilator | 2792 | 4.1476 | 2
201 | Classroom | 414 | 27 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 4.6552 | 2
202 | Classroom | 53 | 3 |  | 673 | 15 | 3 | Unit Ventilator | 5384 | 0.59064 | 0
203 | Classroom | 275 | 18 |  | 666 | 15 | 15 | Unit Ventilator | 5328 | 3.0968 | 1
204 | Classroom | 360 | 24 |  | 669 | 15 | 15 | Unit Ventilator | 5352 | 4.0359 | 2
205 | Classroom | 343 | 22 |  | 701 | 15 | 15 | Unit Ventilator | 5608 | 3.6698 | 1
206 | Classroom | 280 | 18 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 2.9787 | 1
207 | Classroom | 303 | 20 |  | 671 | 15 | 15 | Unit Ventilator | 5368 | 3.3867 | 1
208 | Classroom | 259 | 17 |  | 576 | 13 | 13 | Unit Ventilator | 4608 | 3.3724 | 1
209 | Classroom | 0 | 0 |  | 540 | 12 | 0 | Unit Ventilator | 4320 | 0 | 0
210 | Classroom | 311 | 20 |  | 511 | 11 | 11 | Unit Ventilator | 4088 | 4.5646 | 2
211 | Classroom | 222 | 14 |  | 720 | 16 | 14 | Unit Ventilator | 5760 | 2.3125 | 1
215 | Classroom | 550 | 36 |  | 843 | 19 | 19 | Unit Ventilator | 6744 | 4.8932 | 2
216 | Classroom | 306 | 20 |  | 855 | 19 | 19 | Unit Ventilator | 6840 | 2.6842 | 1
217 | Classroom | 169 | 11 |  | 842 | 19 | 11 | Unit Ventilator | 6736 | 1.5053 | 1
218 | Classroom | 631 | 42 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 5.5546 | 2
285 | Classroom | 273 | 18 |  | 0 | 0 | 0 | Unit Ventilator | 0 | 0 | 0
301 | Classroom | 883 | 58 |  | 2031 | 46 | 46 | Unit Ventilator | 16248 | 3.2607 | 1
304 | Classroom | 276 | 18 |  | 670 | 15 | 15 | Unit Ventilator | 5360 | 3.0896 | 1
305 | Classroom | 346 | 23 |  | 702 | 15 | 15 | Unit Ventilator | 5616 | 3.6966 | 1
306 | Classroom | 319 | 21 |  | 706 | 16 | 16 | Unit Ventilator | 5648 | 3.3888 | 1
307 | Classroom | 347 | 23 |  | 670 | 15 | 15 | Unit Ventilator | 5360 | 3.8843 | 1
308 | Classroom | 112 | 7 |  | 852 | 19 | 7 | Unit Ventilator | 6816 | 0.98592 | 0
309 | Classroom | 333 | 22 |  | 309 | 7 | 7 | Unit Ventilator | 2472 | 8.0825 | 2
310 | Classroom | 247 | 16 |  | 510 | 11 | 11 | Unit Ventilator | 4080 | 3.6324 | 1
311 | Classroom | 351 | 23 |  | 706 | 16 | 16 | Unit Ventilator | 5648 | 3.7288 | 1
312 | Classroom | 305 | 20 |  | 514 | 11 | 11 | Unit Ventilator | 4112 | 4.4504 | 2
315 | Classroom | 289 | 19 |  | 838 | 19 | 19 | Unit Ventilator | 6704 | 2.5865 | 1
316 | Classroom | 285 | 19 |  | 855 | 19 | 19 | Unit Ventilator | 6840 | 2.5 | 1
317 | Classroom | 548 | 36 |  | 847 | 19 | 19 | Unit Ventilator | 6776 | 4.8524 | 2
318 | Classroom | 647 | 43 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 5.6954 | 2
- | Main Office |  | 0 | Yes | 305.08 | 6 | 6 |  | 2440.64 | 0 | 0
- | Nurse Office |  | 0 | Yes | 242.55 | 5 | 5 |  | 1940.4 | 0 | 0
- | 1st Floor Hall | 310 | 20 |  | 2688 | 61 | 20 | Unit Ventilator | 21504 | 0.86496 | 0
- | 1st Floor Nurse RR | 0 | 0 |  | 244 | 5 | 0 | N/A | 1952 | 0 | 0
- | 1st Floor Staff Womens RR | 0 | 0 |  | 393 | 8 | 0 | N/A | 3144 | 0 | 0
- | 2nd Floor Hall | 0 | 0 |  | 2066 | 46 | 0 | Unit Ventilator | 16528 | 0 | 0
- | 2nd Floor Mens RR | 99 | 6 |  | 355 | 8 | 6 | N/A | 2840 | 2.0915 | 1
- | 2nd Floor Womens RR | 236 | 15 |  | 328 | 7 | 7 | N/A | 2624 | 5.3963 | 2
- | 3rd Floor Hall | 289 | 19 |  | 2661 | 60 | 19 | Unit Ventilator | 21288 | 0.81454 | 0
- | 3rd Floor Mens RR | 95 | 6 |  | 259 | 5 | 5 | N/A | 2072 | 2.751 | 1
- | 3rd Floor Womens RR | 219 | 14 |  | 328 | 7 | 7 | N/A | 2624 | 5.0076 | 2
- | Cafeteria | 754 | 50 |  | 5223 | 118 | 50 | Unit Ventilator | 41784 | 1.0827 | 1
- | Bsmt: Boys RR | 0 | 0 |  | 765 | 17 | 0 | N/A | 6120 | 0 | 0
- | Bsmt: Grils RR | 0 | 0 |  | 697 | 15 | 0 | N/A | 5576 | 0 | 0
- | Staff Restroom: 1st Floor | 0 | 0 |  | 168 | 3 | 0 | N/A | 1344 | 0 | 0
- | Library | 0 | 0 |  | 2062.2 | 46 | 0 | Unit Ventilator | 16497.6 | 0 | 0
- | Staff Restroom: 2nd Floor | 0 | 0 |  | 305 | 6 | 0 | N/A | 2440 | 0 | 0
- | Staff Restroom: 3rd Floor | 0 | 0 |  | 308 | 7 | 0 | N/A | 2464 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-08 | [7 empty] | 0 | 0 | 0
School: | Austin Meehan Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
3 | Classroom | 280 | 18 |  | 1537 | 34 | 18 | Unit Ventilator | 12296 | 1.3663 | 1
111 | Classroom | 323 | 21 |  | 917 | 20 | 20 | Unit Ventilator | 7336 | 2.6418 | 1
112 | Classroom | 309 | 20 |  | 1490 | 33 | 20 | Unit Ventilator | 11920 | 1.5554 | 1
113 | Classroom | 287 | 19 |  | 208 | 4 | 4 | Unit Ventilator | 1664 | 10.3486 | 3
114 | Classroom | 307 | 20 |  | 1193 | 27 | 20 | Unit Ventilator | 9544 | 1.93 | 1
115 | Classroom | 274 | 18 |  | 1192 | 27 | 18 | Unit Ventilator | 9536 | 1.724 | 1
121 | Classroom | 0 | 0 |  | 944 | 21 | 0 | Unit Ventilator | 7552 | 0 | 0
122 | Classroom | 503 | 33 |  | 1085 | 24 | 24 | Unit Ventilator | 8680 | 3.477 | 1
123 | Classroom | 350 | 23 |  | 1175 | 26 | 23 | Unit Ventilator | 9400 | 2.234 | 1
124 | Classroom | 283 | 18 |  | 1123 | 25 | 18 | Unit Ventilator | 8984 | 1.89 | 1
125 | Classroom | 413 | 27 |  | 1156 | 26 | 26 | Unit Ventilator | 9248 | 2.6795 | 1
126 | Classroom | 400 | 26 |  | 1064 | 24 | 24 | Unit Ventilator | 8512 | 2.8195 | 1
127 | Classroom | 333 | 22 |  | 1198 | 27 | 22 | Unit Ventilator | 9584 | 2.0847 | 1
128 | Classroom | 343 | 22 |  | 933 | 21 | 21 | Unit Ventilator | 7464 | 2.7572 | 1
211 | Classroom | 327 | 21 |  | 867 | 19 | 19 | Unit Ventilator | 6936 | 2.8287 | 1
212 | Classroom | 382 | 25 |  | 1630 | 37 | 25 | Unit Ventilator | 13040 | 1.7577 | 1
213 | Classroom | 281 | 18 |  | 269 | 6 | 6 | Unit Ventilator | 2152 | 7.8346 | 2
214 | Classroom | 372 | 24 |  | 1317 | 29 | 24 | Unit Ventilator | 10536 | 2.1185 | 1
215 | Classroom | 396 | 26 |  | 1199 | 27 | 26 | Unit Ventilator | 9592 | 2.4771 | 1
221 | Classroom | 0 | 0 |  | 1054 | 23 | 0 | Unit Ventilator | 8432 | 0 | 0
222 | Classroom | 337 | 22 |  | 1286 | 29 | 22 | Unit Ventilator | 10288 | 1.9654 | 1
223 | Classroom | 343 | 22 |  | 1230 | 27 | 22 | Unit Ventilator | 9840 | 2.0915 | 1
224 | Classroom | 0 | 0 |  | 1091 | 24 | 0 | Unit Ventilator | 8728 | 0 | 0
225 | Classroom | 420 | 28 |  | 1151 | 26 | 26 | Unit Ventilator | 9208 | 2.7368 | 1
226 | Classroom | 397 | 26 |  | 1175 | 26 | 26 | Unit Ventilator | 9400 | 2.534 | 1
227 | Classroom | 327 | 21 |  | 1292 | 29 | 21 | Unit Ventilator | 10336 | 1.8982 | 1
228 | Classroom | 0 | 0 |  | 931 | 21 | 0 | Unit Ventilator | 7448 | 0 | 0
311 | Classroom | 310 | 20 |  | 1041 | 23 | 20 | Unit Ventilator | 8328 | 2.2334 | 1
312 | Classroom | 309 | 20 |  | 1602 | 36 | 20 | Unit Ventilator | 12816 | 1.4466 | 1
313 | Classroom | 0 | 0 |  | 756 | 17 | 0 | Unit Ventilator | 6048 | 0 | 0
314 | Classroom | 0 | 0 |  | 1279 | 29 | 0 | Unit Ventilator | 10232 | 0 | 0
315 | Classroom | 0 | 0 |  | 1219 | 27 | 0 | Unit Ventilator | 9752 | 0 | 0
321 | Classroom | 0 | 0 |  | 1064 | 24 | 0 | Unit Ventilator | 8512 | 0 | 0
322 | Classroom | 460 | 30 |  | 1199 | 27 | 27 | Unit Ventilator | 9592 | 2.8774 | 1
323 | Classroom | 0 | 0 |  | 1365 | 31 | 0 | Unit Ventilator | 10920 | 0 | 0
324 | Classroom | 377 | 25 |  | 1039 | 23 | 23 | Unit Ventilator | 8312 | 2.7214 | 1
325 | Classroom | 270 | 18 |  | 1247 | 28 | 18 | Unit Ventilator | 9976 | 1.6239 | 1
326 | Classroom | 493 | 32 |  | 1322 | 30 | 30 | Unit Ventilator | 10576 | 2.7969 | 1
327 | Classroom | 417 | 27 |  | 1184 | 26 | 26 | Unit Ventilator | 9472 | 2.6415 | 1
328 | Classroom | 397 | 26 |  | 955 | 21 | 21 | Unit Ventilator | 7640 | 3.1178 | 1
411 | Classroom | 576 | 38 |  | 947 | 21 | 21 | Unit Ventilator | 7576 | 4.5618 | 2
412 | Classroom | 352 | 23 |  | 1474 | 33 | 23 | Unit Ventilator | 11792 | 1.791 | 1
413 | Classroom | 307 | 20 |  | 208 | 4 | 4 | Unit Ventilator | 1664 | 11.0697 | 3
414 | Classroom | 313 | 20 |  | 1255 | 28 | 20 | Unit Ventilator | 10040 | 1.8705 | 1
415 | Classroom | 347 | 23 |  | 1215 | 27 | 23 | Unit Ventilator | 9720 | 2.142 | 1
421 | Classroom |  | 0 | Yes | 1058 | 24 | 24 | N/A | 8464 | 0 | 0
422 | Classroom | 463 | 30 |  | 1199 | 27 | 27 | Unit Ventilator | 9592 | 2.8962 | 1
423 | Classroom | 363 | 24 |  | 1327 | 30 | 24 | Unit Ventilator | 10616 | 2.0516 | 1
424 | Classroom | 300 | 20 |  | 1365 | 31 | 20 | Unit Ventilator | 10920 | 1.6484 | 1
425 | Classroom | 383 | 25 |  | 1350 | 30 | 25 | Unit Ventilator | 10800 | 2.1278 | 1
426 | Classroom | 450 | 30 |  | 1201 | 27 | 27 | Unit Ventilator | 9608 | 2.8102 | 1
427 | Classroom | 357 | 23 |  | 1242 | 28 | 23 | Unit Ventilator | 9936 | 2.1558 | 1
428 | Classroom | 390 | 26 |  | 1054 | 23 | 23 | Unit Ventilator | 8432 | 2.7751 | 1
A-01 A | Art | 599 | 39 |  | 1692 | 38 | 38 | Unit Ventilator | 13536 | 2.6551 | 1
A-02 | Art | 288 | 19 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
A-03 A | Art | 648 | 43 |  | 1692 | 38 | 38 | Unit Ventilator | 13536 | 2.8723 | 1
- | Boys Locker Room | 1404 | 93 |  | 700 | 15 | 15 | AHU | 5600 | 15.0429 | 3
- | Girls Locker Room | 1531 | 102 |  | 700 | 15 | 15 | AHU | 5600 | 16.4036 | 3
Ground Level Pod #1 | Auditorium Control room | 0 | 0 |  | 102 | 2 | 0 | AHU | 816 | 0 | 0
Ground Level Pod #1 | Center Core | 163 | 10 |  | 528 | 12 | 10 | AHU | 4224 | 2.3153 | 1
Ground Level Pod #1 | Center Core | 297 | 19 |  | 1012 | 23 | 19 | AHU | 8096 | 2.2011 | 1
Ground Level Pod #1 | Conference | 38 | 2 |  | 150 | 3 | 2 | AHU | 1200 | 1.9 | 1
Ground Level Pod #1 | Counselor | 0 | 0 |  | 80 | 1 | 0 | AHU | 640 | 0 | 0
Ground Level Pod #1 | Entryway | 0 | 0 |  | 238 | 5 | 0 | AHU | 1904 | 0 | 0
Ground Level Pod #1 | Entryway | 32 | 2 |  | 238 | 5 | 2 | AHU | 1904 | 1.0084 | 1
Ground Level Pod #1 | Lobby | 113 | 7 |  | 1625 | 36 | 7 | AHU | 13000 | 0.52154 | 0
Ground Level Pod #1 | Lobby Entryway | 55 | 3 |  | 238 | 5 | 3 | AHU | 1904 | 1.7332 | 1
Ground Level Pod #1 | Main Office - Waiting | 143 | 9 |  | 1550 | 35 | 9 | AHU | 12400 | 0.69194 | 0
Ground Level Pod #1 | Main Office 1 | 63 | 4 |  | 130 | 2 | 2 | AHU | 1040 | 3.6346 | 1
Ground Level Pod #1 | Main Office 2 | 74 | 4 |  | 231 | 5 | 4 | AHU | 1848 | 2.4026 | 1
Ground Level Pod #1 | Main Office 3 | 41 | 2 |  | 110 | 2 | 2 | AHU | 880 | 2.7955 | 1
Ground Level Pod #1 | Main Office 4 | 135 | 9 |  | 156 | 3 | 3 | AHU | 1248 | 6.4904 | 2
Ground Level Pod #1 | Office | 28 | 1 |  | 143 | 3 | 1 | AHU | 1144 | 1.4685 | 1
Ground Level Pod #1 | Office Floor | 0 | 0 |  | 500 | 11 | 0 | AHU | 4000 | 0 | 0
Ground Level Pod #1 | Ticket Booth | 0 | 0 |  |  | 0 | 0 | AHU | 0 | 0 | 0
Ground level Pod #2 | Cafeteria | 374 | 24 |  | 2900 | 65 | 24 | AHU | 23200 | 0.96724 | 0
Ground level Pod #2 | Center Core | 68 | 4 |  | 400 | 9 | 4 | AHU | 3200 | 1.275 | 1
Ground level Pod #2 | Entryway | 32 | 2 |  | 300 | 6 | 2 | AHU | 2400 | 0.8 | 0
Ground level Pod #2 | Office | 8 | 0 |  |  | 0 | 0 | AHU | 0 | 0 | 0
Ground level Pod #2 | Pod Center Core | 116 | 7 |  | 925 | 21 | 7 | AHU | 7400 | 0.94054 | 0
Ground Level Pod #3 | Cafeteria | 59 | 3 |  | 2900 | 65 | 3 | AHU | 23200 | 0.15259 | 0
Ground Level Pod #3 | Center Core | 272 | 18 |  | 425 | 9 | 9 | AHU | 3400 | 4.8 | 2
Ground Level Pod #3 | Entryway | 68 | 4 |  | 460 | 10 | 4 | AHU | 3680 | 1.1087 | 1
Ground Level Pod #3 | Pod Center Core | 174 | 11 |  | 900 | 20 | 11 | AHU | 7200 | 1.45 | 1
Ground Level Pod #3 | Pod Center Prep | 30 | 2 |  | 945 | 21 | 2 | AHU | 7560 | 0.2381 | 0
Ground level Pod #4 | Center Ring - Counselor | 34 | 2 |  | 110 | 2 | 2 | AHU | 880 | 2.3182 | 1
Ground level Pod #4 | Center Ring - Police | 0 | 0 |  | 187 | 4 | 0 | AHU | 1496 | 0 | 0
Ground level Pod #4 | Center Ring - Social Work | 36 | 2 |  | 110 | 2 | 2 | AHU | 880 | 2.4545 | 1
Ground Level Pod #4 | Mayfair Center Core | 63 | 4 |  | 425 | 9 | 4 | AHU | 3400 | 1.1118 | 1
Ground Level Pod #4 | Mayfair Conference | 27 | 1 |  | 156 | 3 | 1 | AHU | 1248 | 1.2981 | 1
Ground Level Pod #4 | Mayfair Entry way | 0 | 0 |  | 204 | 4 | 0 | AHU | 1632 | 0 | 0
Ground Level Pod #4 | Mayfair Nurse Office | 0 | 0 |  | 216 | 4 | 0 | AHU | 1728 | 0 | 0
Ground Level Pod #4 | Mayfair Office | 0 | 0 |  | 144 | 3 | 0 | AHU | 1152 | 0 | 0
Ground Level Pod #4 | Mayfair Pod Center Core | 21 | 1 |  | 969 | 22 | 1 | AHU | 7752 | 0.16254 | 0
Ground Level Pod #4 | Mayfair Pod Center Prep | 0 | 0 |  | 646 | 14 | 0 | AHU | 5168 | 0 | 0
Ground Level Pod #4 | Mayfair Principal Office | 0 | 0 |  | 190 | 4 | 0 | AHU | 1520 | 0 | 0
Ground Level Pod #4 | Nurse Exam | 62 | 4 |  | 54 | 1 | 1 | AHU | 432 | 8.6111 | 2
Ground Level Pod #4 | Nurse Office | 93 | 6 |  | 420 | 9 | 6 | AHU | 3360 | 1.6607 | 1
Ground Level Pod #4 | Roster Area Entry | 134 | 8 |  | 150 | 3 | 3 | AHU | 1200 | 6.7 | 2
Ground Level Pod #4 | Roster Room | 64 | 4 |  | 80 | 1 | 1 | AHU | 640 | 6 | 2
- | Gym | 3715 | 247 |  | 3700 | 84 | 84 | AHU | 29600 | 7.5304 | 2
Lower Level Pod #2 | M-1 Band - Ensemble | 60 | 4 |  | 459 | 10 | 4 | AHU | 3672 | 0.98039 | 0
Lower Level Pod #2 | M-1 Band - Office | 30 | 2 |  | 600 | 13 | 2 | AHU | 4800 | 0.375 | 0
Lower Level Pod #2 | M-1 Band - Practice 1 | 59 | 3 |  | 450 | 10 | 3 | AHU | 3600 | 0.98333 | 0
Lower Level Pod #2 | Math Rm - Office | 30 | 2 |  | 104 | 2 | 2 | AHU | 832 | 2.1635 | 1
Lower Level Pod #2 | Math Rm - Storage | 0 | 0 |  | 50 | 1 | 0 | AHU | 400 | 0 | 0
Lower Level Pod #2 | Storage | 0 | 0 |  |  | 0 | 0 | AHU | 0 | 0 | 0
Lower Level Pod #2 | Visual Com. Lab - Darkroom | 58 | 3 |  | 380 | 8 | 3 | AHU | 3040 | 1.1447 | 1
Lower Level Pod #4 | Center Core Art-01,02,03 | 60 | 4 |  | 1692 | 38 | 4 | AHU | 13536 | 0.26596 | 0
Lower Level Pod #4 | Center Core Storage | 21 | 1 |  |  | 0 | 0 | AHU | 0 | 0 | 0
Lower Level Pod #4 | Classroom #3 Office | 25 | 1 |  | 144 | 3 | 1 | AHU | 1152 | 1.3021 | 1
Lower Level Pod #4 | Classroom #3 Prep | 27 | 1 |  | 50 | 1 | 1 | AHU | 400 | 4.05 | 2
Lower Level Pod #4 | Classroom #3 Storage | 24 | 1 |  | 126 | 2 | 1 | AHU | 1008 | 1.4286 | 1
Lower Level Pod #4 | M-5 Band Rm Ensemble | 46 | 3 |  | 1734 | 39 | 3 | AHU | 13872 | 0.19896 | 0
Lower Level Pod #4 | M-5 Band Rm Office | 0 | 0 |  | 100 | 2 | 0 | AHU | 800 | 0 | 0
Lower Level Pod #4 | M-5 Band Rm Practice 1 | 0 | 0 |  | 40 | 0 | 0 | AHU | 320 | 0 | 0
Lower Level Pod #4 | M-5 Band Rm Practice 2 | 0 | 0 |  | 40 | 0 | 0 | AHU | 320 | 0 | 0
M-1 B | Band Room | 323 | 21 |  | 1178 | 26 | 21 | Unit Ventilator | 9424 | 2.0565 | 1
M-5 | Band Room | 0 | 0 |  | 1734 | 39 | 0 | Unit Ventilator | 13872 | 0 | 0
Math Lab | Classroom | 338 | 22 |  | 1337 | 30 | 22 | Unit Ventilator | 10696 | 1.896 | 1
S-01 A | Power Tech Lab | 312 | 20 |  | 1472 | 33 | 20 | Unit Ventilator | 11776 | 1.5897 | 1
S-02 A | Engineering Lab | 797 | 53 |  | 1985 | 45 | 45 | Unit Ventilator | 15880 | 3.0113 | 1
S-03 | Visual Comm. Lab | 321 | 21 |  | 1379 | 31 | 21 | Unit Ventilator | 11032 | 1.7458 | 1
Technology Lab | Classroom | 326 | 21 |  | 1025 | 23 | 21 | Unit Ventilator | 8200 | 2.3854 | 1
- | Auditorium | 4818 | 321 |  | 4485 | 101 | 101 | AHU | 35880 | 8.0569 | 2
Upper Level | Mayfair Multi-Purpose Room | 835 | 55 |  | 5781 | 131 | 55 | AHU | 46248 | 1.0833 | 1
129A | Upper Level Pod #1 Classroom | 264 | 17 |  | 731 | 16 | 16 | AHU | 5848 | 2.7086 | 1
Upper Level Pod #1 | Core | 309 | 20 |  | 540 | 12 | 12 | AHU | 4320 | 4.2917 | 2
Upper Level Pod #1 | Deans Office | 355 | 23 |  | 480 | 10 | 10 | AHU | 3840 | 5.5469 | 2
Upper Level Pod #1 | Pod Center Core | 0 | 0 |  | 616 | 14 | 0 | AHU | 4928 | 0 | 0
430 | Upper Level Multi-Purpose Mayfair Classroom | 90 | 6 | Yes | 1249 | 28 | 28 | AHU | 9992 | 0.54043 | 0
431 | Upper Level Multi-Purpose Mayfair Classroom | 136 | 9 | Yes | 789 | 17 | 17 | AHU | 6312 | 1.2928 | 1
Upper Level Pod #2 | Core | 0 | 0 |  | 425 | 9 | 0 | AHU | 3400 | 0 | 0
432 | Upper Level Pod #2 Lab B/C (Mayfair Room) | 212 | 14 | Yes | 928 | 21 | 21 | AHU | 7424 | 1.7134 | 1
433 | Upper Level Pod #2 Mayfair Kindergarten (Mayfair Room) | 184 | 12 | Yes | 1145 | 26 | 26 | AHU | 9160 | 1.2052 | 1
Upper Level Pod #2 | Pod Center Core | 0 | 0 |  | 2968 | 67 | 0 | AHU | 23744 | 0 | 0
Upper Level Pod #3 | Center Core | 0 | 0 |  | 616 | 14 | 0 | AHU | 4928 | 0 | 0
Upper Level Pod #3 | Lab C Classroom | 187 | 12 |  | 806 | 18 | 12 | AHU | 6448 | 1.7401 | 1
Upper Level Pod #3 | Lab Office | 28 | 1 |  | 120 | 2 | 1 | AHU | 960 | 1.75 | 1
Upper Level Pod #3 | Pod Center Core | 0 | 0 |  | 2968 | 67 | 0 | AHU | 23744 | 0 | 0
Upper Level Pod #4 | Mayfair Center Core | 174 | 11 |  | 4366 | 99 | 11 | AHU | 34928 | 0.2989 | 0
429 | Upper Level Pod #4 Mayfair Classroom | 263 | 17 |  | 1008 | 22 | 17 | AHU | 8064 | 1.9568 | 1
Upper Level Pod #4 | Mayfair Counselor Office | 79 | 5 |  | 132 | 3 | 3 | AHU | 1056 | 4.4886 | 2
Upper Level Pod #4 | Mayfair Multi-Purpose Room | 424 | 28 |  | 4662 | 105 | 28 | AHU | 37296 | 0.68211 | 0
Upper Level Pod #4 | Mayfair Principal Office | 83 | 5 |  | 180 | 4 | 4 | AHU | 1440 | 3.4583 | 1
Weight Room | Classroom | 107 | 7 |  | 210 | 4 | 4 | AHU | 1680 | 3.8214 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | William M. Meredith Elementary-Middle School | [7 empty] | 0 | 0 | 0
| William M. Meredith Elementary-Middle School Modular Building | [7 empty] | 0 | 0 | 0
Vendor: | Capital | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Main Building | [8 empty] | 0 | 0 | 0
B5 | Classroom |  | 0 | Yes | 696 | 15 | 15 |  | 5568 | 0 | 0
102 | Classroom |  | 0 | Yes | 690 | 15 | 15 |  | 5520 | 0 | 0
103 | Classroom |  | 0 | Yes | 690 | 15 | 15 |  | 5520 | 0 | 0
104 | Classroom |  | 0 | Yes | 690 | 15 | 15 |  | 5520 | 0 | 0
105 | Classroom |  | 0 | Yes | 920 | 20 | 20 |  | 7360 | 0 | 0
106 | Classroom |  | 0 | Yes | 816 | 18 | 18 |  | 6528 | 0 | 0
107 | Classroom |  | 0 | Yes | 664 | 15 | 15 |  | 5312 | 0 | 0
108 | Classroom |  | 0 | Yes | 664 | 15 | 15 |  | 5312 | 0 | 0
201 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
202 | Classroom |  | 0 | Yes | 690 | 15 | 15 |  | 5520 | 0 | 0
204.5 | Classroom |  | 0 | Yes | 425 | 9 | 9 |  | 3400 | 0 | 0
205 | Classroom |  | 0 | Yes | 782 | 17 | 17 |  | 6256 | 0 | 0
206 | Classroom |  | 0 | Yes | 759 | 17 | 17 |  | 6072 | 0 | 0
206A | Classroom |  | 0 | Yes | 368 | 8 | 8 |  | 2944 | 0 | 0
207 | Classroom |  | 0 | Yes | 506 | 11 | 11 |  | 4048 | 0 | 0
208 | Classroom |  | 0 | Yes | 664 | 15 | 15 |  | 5312 | 0 | 0
301 | Classroom |  | 0 | Yes | 696 | 15 | 15 |  | 5568 | 0 | 0
302 | Classroom |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | 0 | 0
303 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | 0 | 0
304 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
305 | Classroom |  | 0 | Yes | 1210 | 27 | 27 |  | 9680 | 0 | 0
306 | Classroom |  | 0 | Yes | 782 | 17 | 17 |  | 6256 | 0 | 0
307 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
308 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
309 | Classroom |  | 0 | Yes | 648 | 14 | 14 |  | 5184 | 0 | 0
309A | Classroom |  | 0 |  | 420 | 9 | 0 |  | 3360 | 0 | 0
- | Auditorium |  | 0 |  | 3185 | 72 | 0 |  | 25480 | 0 | 0
- | Counselors Office |  | 0 | Yes | 375 | 8 | 8 |  | 3000 | 0 | 0
- | Gym |  | 0 |  | 3723 | 84 | 0 |  | 29784 | 0 | 0
- | Library |  | 0 | Yes | 1298 | 29 | 29 |  | 10384 | 0 | 0
- | Lunchroom |  | 0 |  | 2250 | 51 | 0 |  | 18000 | 0 | 0
- | Main office |  | 0 | Yes | 368 | 8 | 8 |  | 2944 | 0 | 0
- | Nurses Office |  | 0 | Yes | 168 | 3 | 3 |  | 1344 | 0 | 0
- | Principals office |  | 0 | Yes | 256 | 5 | 5 |  | 2048 | 0 | 0
- | Psych Office #1 |  | 0 |  | 138 | 3 | 0 |  | 1104 | 0 | 0
- | Psych Office #2 |  | 0 |  | 88 | 2 | 0 |  | 704 | 0 | 0
- | Teachers Lounge |  | 0 |  | 322 | 7 | 0 |  | 2576 | 0 | 0
Modular Building | [8 empty] | 0 | 0 | 0
1 | Classroom | 368 | 24 |  | 720 | 16 | 16 | AHU | 5760 | 3.8333 | 1
2 | Classroom | 378 | 25 |  | 720 | 16 | 16 | AHU | 5760 | 3.9375 | 1
3 | Classroom | 381 | 25 |  | 720 | 16 | 16 | AHU | 5760 | 3.9688 | 1
4 | Classroom | 374 | 24 |  | 720 | 16 | 16 | AHU | 5760 | 3.8958 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | Thomas Mifflin Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | Part 2 | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 253 | 16 | Yes | 794 | 18 | 18 | Unit Ventilator | 6352 | 2.3898 | 1
102 | Classroom | 555 | 37 |  | 1040 | 23 | 23 | Unit Ventilator | 8320 | 4.0024 | 2
103 | Classroom | 288 | 19 |  | 375 | 8 | 8 | Unit Ventilator | 3000 | 5.76 | 2
104 | Classroom | 270 | 18 |  | 537 | 12 | 12 | Unit Ventilator | 4296 | 3.7709 | 1
105 | Classroom | 395 | 26 |  | 484 | 11 | 11 | Unit Ventilator | 3872 | 6.1209 | 2
106 | Classroom | 422 | 28 |  | 682 | 15 | 15 | Unit Ventilator | 5456 | 4.6408 | 2
107 | Classroom | 330 | 22 |  | 658 | 14 | 14 | Unit Ventilator | 5264 | 3.7614 | 1
108 | Classroom | 439 | 29 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.7717 | 2
109 | Classroom | 230 | 15 |  | 662 | 15 | 15 | Unit Ventilator | 5296 | 2.6057 | 1
110 | Classroom | 348 | 23 |  | 669 | 15 | 15 | Unit Ventilator | 5352 | 3.9013 | 1
111 | Classroom | 587 | 39 |  | 531 | 12 | 12 | Unit Ventilator | 4248 | 8.291 | 2
114 | Classroom | 0 | 0 | Yes | 630 | 14 | 14 | Unit Ventilator | 5040 | 0 | 0
115 | Classroom | 0 | 0 | Yes | 684 | 15 | 15 | Unit Ventilator | 5472 | 0 | 0
128 (117) | Counselor Office | 376 | 25 |  | 350 | 7 | 7 | Unit Ventilator | 2800 | 8.0571 | 2
201 | Classroom | 595 | 39 |  | 775 | 17 | 17 | Unit Ventilator | 6200 | 5.7581 | 2
202 | Classroom | 638 | 42 |  | 764 | 17 | 17 | Unit Ventilator | 6112 | 6.2631 | 2
203 | Classroom | 300 | 20 |  | 340 | 7 | 7 | Unit Ventilator | 2720 | 6.6176 | 2
204 | Classroom | 354 | 23 |  | 639 | 14 | 14 | Unit Ventilator | 5112 | 4.1549 | 2
205 | Classroom | 458 | 30 |  | 682 | 15 | 15 | Unit Ventilator | 5456 | 5.0367 | 2
206 | Classroom | 432 | 28 |  | 688 | 15 | 15 | Unit Ventilator | 5504 | 4.7093 | 2
207 | Classroom | 606 | 40 |  | 686 | 15 | 15 | Unit Ventilator | 5488 | 6.6254 | 2
209 | Classroom | 241 | 16 |  | 686 | 15 | 15 | Unit Ventilator | 5488 | 2.6348 | 1
210 | Classroom | 598 | 39 |  | 1380 | 31 | 31 | Unit Ventilator | 11040 | 3.25 | 1
211 | Classroom | 408 | 27 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.4348 | 2
212 | Meeting Room | 1055 | 70 |  | 312 | 7 | 7 | Unit Ventilator | 2496 | 25.3606 | 4
215 | Classroom |  | 0 | Yes | 323 | 7 | 7 | Unit Ventilator | 2584 | 0 | 0
- | Auditorium | 0 | 0 |  | 3837 | 87 | 0 | House Fan | 30696 | 0 | 0
- | Cafeteria | 270 | 18 | Yes | 2128 | 48 | 48 | Unit Ventilator | 17024 | 0.9516 | 0
- | Cafeteria Hall | 0 | 0 |  | 738 | 16 | 0 | Unit Ventilator | 5904 | 0 | 0
- | Library | 403 | 26 |  | 3024 | 68 | 26 | Unit Ventilator | 24192 | 0.9995 | 0
- | Music Room | 425 | 28 |  | 966 | 21 | 21 | Unit Ventilator | 7728 | 3.2997 | 1
Pre-K 3 | Classroom | 489 | 32 |  | 972 | 22 | 22 | Unit Ventilator | 7776 | 3.7731 | 1
Pre-K 4 | Classroom | 335 | 22 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 2.731 | 1
- | Main Office |  | 0 | Yes | 552 | 12 | 12 |  | 4416 | 0 | 0
- | Principal Office |  | 0 | Yes | 390 | 8 | 8 |  | 3120 | 0 | 0
- | Nurses Office |  | 0 | Yes | 192 | 4 | 4 |  | 1536 | 0 | 0
- | Gym | 4205 | 280 |  | 5280 | 120 | 120 | RTU | 42240 | 5.973 | 2
6 | Speech |  | 0 | Yes | 544 | 12 | 12 |  | 4352 | 0 | 0
8 | Classroom |  | 0 | Yes | 851 | 19 | 19 |  | 6808 | 0 | 0
20 | Special Needs |  | 0 | Yes | 661 | 15 | 15 |  | 5288 | 0 | 0
- | Spanish Classroom | 0 | 0 | Yes | 900 | 20 | 20 | Unit Ventilator | 7200 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-28 | [7 empty] | 0 | 0 | 0
School: | E. Spencer Miller- Philadelphia Learning Academy South (9-12) and Crossroads Acelerated Academy (7-8) | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
153 | Office | 0 | 0 |  | 187 | 4 | 0 |  | 1496 | 0 | 0
158 | School Police Office | 267 | 17 |  | 540 | 12 | 12 |  | 4320 | 3.7083 | 1
167 | Staff Lounge | 0 | 0 |  | 532 | 12 | 0 |  | 4256 | 0 | 0
170 | Office | 0 | 0 |  | 99 | 2 | 0 |  | 792 | 0 | 0
175 | Office | 0 | 0 |  | 154 | 3 | 0 |  | 1232 | 0 | 0
181 | Office | 49 | 3 |  | 344 | 7 | 3 |  | 2752 | 1.0683 | 1
183 | Office | 10 | 0 |  | 110 | 2 | 0 |  | 880 | 0.68182 | 0
184 | Office | 7 | 0 |  | 100 | 2 | 0 |  | 800 | 0.525 | 0
185 | Office | 17 | 1 |  | 220 | 5 | 1 |  | 1760 | 0.57955 | 0
186 | Office | 27 | 1 |  | 208 | 4 | 1 |  | 1664 | 0.97356 | 0
188 | Office | 201 | 13 |  | 77 | 1 | 1 |  | 616 | 19.5779 | 3
192 | Office | 289 | 19 |  | 111 | 2 | 2 |  | 888 | 19.527 | 3
245 | Office | 17 | 1 |  | 170 | 3 | 1 |  | 1360 | 0.75 | 0
246 | Office | 41 | 2 |  | 131 | 2 | 2 |  | 1048 | 2.3473 | 1
247 | Office | 33 | 2 |  | 167 | 3 | 2 |  | 1336 | 1.482 | 1
248 | Office | 0 | 0 |  | 152 | 3 | 0 |  | 1216 | 0 | 0
252 | Office | 0 | 0 |  | 516 | 11 | 0 |  | 4128 | 0 | 0
254 | Office | 166 | 11 |  | 231 | 5 | 5 |  | 1848 | 5.3896 | 2
255 | Office | 46 | 3 |  | 98 | 2 | 2 |  | 784 | 3.5204 | 1
256 | Office | 94 | 6 |  | 140 | 3 | 3 |  | 1120 | 5.0357 | 2
257 | Office | 396 | 26 |  | 120 | 2 | 2 |  | 960 | 24.75 | 4
258 | Office | 58 | 3 |  | 531 | 12 | 3 |  | 4248 | 0.81921 | 0
262 | Office | 111 | 7 |  | 102 | 2 | 2 |  | 816 | 8.1618 | 2
266 | Office | 762 | 50 |  | 381 | 8 | 8 |  | 3048 | 15 | 3
267 | Office | 949 | 63 |  | 437 | 9 | 9 |  | 3496 | 16.2872 | 3
274 | Office | 192 | 12 |  | 148 | 3 | 3 |  | 1184 | 9.7297 | 2
275 | Office | 130 | 8 |  | 117 | 2 | 2 |  | 936 | 8.3333 | 2
276 | Office | 72 | 4 |  | 101 | 2 | 2 |  | 808 | 5.3465 | 2
277 | Office | 176 | 11 |  | 147 | 3 | 3 |  | 1176 | 8.9796 | 2
278 | Office | 107 | 7 |  | 109 | 2 | 2 |  | 872 | 7.3624 | 2
279 | Office | 104 | 6 |  | 106 | 2 | 2 |  | 848 | 7.3585 | 2
280 | Office | 287 | 19 |  | 254 | 5 | 5 |  | 2032 | 8.4744 | 2
282 | Office | 311 | 20 |  | 272 | 6 | 6 |  | 2176 | 8.5754 | 2
286 | Office | 636 | 42 |  | 290 | 6 | 6 |  | 2320 | 16.4483 | 3
287 | Office | 104 | 6 |  | 107 | 2 | 2 |  | 856 | 7.2897 | 2
290 | Office | 108 | 7 |  | 132 | 3 | 3 |  | 1056 | 6.1364 | 2
291 | Office | 107 | 7 |  | 151 | 3 | 3 |  | 1208 | 5.3146 | 2
292 | Office | 210 | 14 |  | 150 | 3 | 3 |  | 1200 | 10.5 | 3
293 | Office | 186 | 12 |  | 153 | 3 | 3 |  | 1224 | 9.1176 | 2
- | 1st Flr Computer Room | 0 | 0 |  | 240 | 5 | 0 |  | 1920 | 0 | 0
- | 1st Flr Corrider by B & E Section | 0 | 0 |  | 320 | 7 | 0 |  | 2560 | 0 | 0
- | 1st Flr Kitchen | 8316 | 554 |  | 924 | 21 | 21 |  | 7392 | 67.5 | 5
- | 1st Flr Kitchen Dry Food Area | 171 | 11 |  | 187 | 4 | 4 |  | 1496 | 6.8583 | 2
- | 1st Flr Kitchen Freezer Area | 85 | 5 |  | 420 | 9 | 5 |  | 3360 | 1.5179 | 1
- | 1st Flr Mechanical Room | 19 | 1 |  | 336 | 7 | 1 |  | 2688 | 0.42411 | 0
- | 2nd Floor Conference Room | 359 | 23 |  | 216 | 4 | 4 |  | 1728 | 12.4653 | 3
- | 2nd Floor Corridor by Elevator | 363 | 24 |  | 463 | 10 | 10 |  | 3704 | 5.8801 | 2
- | 2nd Floor Meeting Room | 139 | 9 |  | 79 | 1 | 1 |  | 632 | 13.1962 | 3
- | 2nd Floor Mens Restroom by Elevator | 138 | 9 |  | 255 | 5 | 5 |  | 2040 | 4.0588 | 2
- | 2nd Floor Restroom Vestibule by Elevator | 157 | 10 |  | 73 | 1 | 1 |  | 584 | 16.1301 | 3
- | 2nd Floor Womans Restroom by Elevator | 114 | 7 |  | 167 | 3 | 3 |  | 1336 | 5.1198 | 2
- | 2nd Flr Corridor by Admin Office | 195 | 13 |  | 218 | 4 | 4 |  | 1744 | 6.7087 | 2
- | 2nd Flr Corridor by G Section | 45 | 3 |  | 458 | 10 | 3 |  | 3664 | 0.7369 | 0
- | 2nd Flr Reception Office | 170 | 11 |  | 116 | 2 | 2 |  | 928 | 10.9914 | 3
- | 1st Flr A - Common Area | 48 | 3 |  | 1251 | 28 | 3 |  | 10008 | 0.28777 | 0
A1 | Classroom | 58 | 3 |  | 960 | 21 | 3 |  | 7680 | 0.45312 | 0
A2 | Classroom | 66 | 4 |  | 990 | 22 | 4 |  | 7920 | 0.5 | 0
A3 | Classroom | 60 | 4 |  | 990 | 22 | 4 |  | 7920 | 0.45455 | 0
A4 | Classroom | 56 | 3 |  | 997 | 22 | 3 |  | 7976 | 0.42126 | 0
- | 1st Flr B - Common Area | 747 | 49 |  | 960 | 21 | 21 |  | 7680 | 5.8359 | 2
B1 | Classroom | 304 | 20 |  | 868 | 19 | 19 |  | 6944 | 2.6267 | 1
B2 | Classroom | 488 | 32 |  | 945 | 21 | 21 |  | 7560 | 3.873 | 1
B3 | Classroom | 942 | 62 |  | 980 | 22 | 22 |  | 7840 | 7.2092 | 2
B4 | Classroom | 961 | 64 |  | 910 | 20 | 20 |  | 7280 | 7.9203 | 2
- | C - Common Area 1st Flr | 1014 | 67 |  | 1285 | 29 | 29 |  | 10280 | 5.9183 | 2
C-1 | Classroom | 885 | 59 |  | 816 | 18 | 18 |  | 6528 | 8.1342 | 2
C-2 | Classroom | 1047 | 69 |  | 840 | 19 | 19 |  | 6720 | 9.3482 | 2
C-3 | Classroom | 1200 | 80 |  | 840 | 19 | 19 |  | 6720 | 10.7143 | 3
C-4 | Classroom | 828 | 55 |  | 868 | 19 | 19 |  | 6944 | 7.1544 | 2
- | Climate Masters Office | 150 | 10 |  | 821 | 18 | 10 |  | 6568 | 1.3703 | 1
- | Computer Support Specialist Office | 102 | 6 |  | 88 | 2 | 2 |  | 704 | 8.6932 | 2
- | Corridor 2nd Floor near office 252 | 0 | 0 |  | 376 | 8 | 0 |  | 3008 | 0 | 0
- | 1st Flr Corridor By B Section | 0 | 0 |  | 360 | 8 | 0 |  | 2880 | 0 | 0
- | Corridor by D Section | 713 | 47 |  | 438 | 9 | 9 |  | 3504 | 12.2089 | 3
- | Corridor by Main Office | 38 | 2 |  | 610 | 13 | 2 |  | 4880 | 0.46721 | 0
- | Corridor by Office 258 | 107 | 7 |  | 160 | 3 | 3 |  | 1280 | 5.0156 | 2
- | 2nd Flr D - Common Area | 202 | 13 |  | 910 | 20 | 13 |  | 7280 | 1.6648 | 1
D1 | Classroom | 206 | 13 |  | 960 | 21 | 13 |  | 7680 | 1.6094 | 1
D2 | Classroom | 132 | 8 |  | 901 | 20 | 8 |  | 7208 | 1.0988 | 1
D3 | Classroom | 268 | 17 |  | 1007 | 22 | 17 |  | 8056 | 1.996 | 1
D4 | Classroom | 209 | 13 |  | 972 | 22 | 13 |  | 7776 | 1.6127 | 1
- | Dr. Graham Principal Office | 111 | 7 |  | 823 | 18 | 7 |  | 6584 | 1.0115 | 1
- | 2nd Flr E - Common Area | 431 | 28 |  | 934 | 21 | 21 |  | 7472 | 3.4609 | 1
E1 | Classroom | 633 | 42 |  | 919 | 20 | 20 |  | 7352 | 5.1659 | 2
E2 | Classroom | 593 | 39 |  | 1021 | 23 | 23 |  | 8168 | 4.356 | 2
E3 | Classroom | 594 | 39 |  | 1046 | 23 | 23 |  | 8368 | 4.2591 | 2
E4 | Classroom | 647 | 43 |  | 984 | 22 | 22 |  | 7872 | 4.9314 | 2
- | 2nd Flr G - Common Area | 12 | 0 |  | 1214 | 27 | 0 |  | 9712 | 0.074135 | 0
G1 | Classroom | 40 | 2 |  | 862 | 19 | 2 |  | 6896 | 0.34803 | 0
G2 | Classroom | 29 | 1 |  | 878 | 19 | 1 |  | 7024 | 0.24772 | 0
G3 | Classroom | 26 | 1 |  | 884 | 20 | 1 |  | 7072 | 0.22059 | 0
G4 | Classroom | 33 | 2 |  | 872 | 19 | 2 |  | 6976 | 0.28383 | 0
- | 1 st Flr Gym | 5785 | 385 |  | 3888 | 88 | 88 |  | 31104 | 11.1593 | 3
- | Late Check Office | 0 | 0 |  | 96 | 2 | 0 |  | 768 | 0 | 0
- | Main Entrance | 5 | 0 |  | 64 | 1 | 0 |  | 512 | 0.58594 | 0
- | 1st Flr Media Room | 524 | 34 |  | 1539 | 34 | 34 |  | 12312 | 2.5536 | 1
- | Meeting Room | 21 | 1 |  | 90 | 2 | 1 |  | 720 | 1.75 | 1
- | Mens Restroom by Elevator | 26 | 1 |  | 190 | 4 | 1 |  | 1520 | 1.0263 | 1
- | Nurses Office | 584 | 38 |  | 412 | 9 | 9 |  | 3296 | 10.6311 | 3
- | Office Corridor | 228 | 15 |  | 702 | 15 | 15 |  | 5616 | 2.4359 | 1
- | Parking Lot Entry | 0 | 0 |  | 135 | 3 | 0 |  | 1080 | 0 | 0
- | Reception | 47 | 3 |  | 521 | 11 | 3 |  | 4168 | 0.67658 | 0
- | Restroom Vestibule Between A1/A2 | 6 | 0 |  | 56 | 1 | 0 |  | 448 | 0.80357 | 0
- | Restroom Vestibule Between A3/A4 | 4 | 0 |  | 56 | 1 | 0 |  | 448 | 0.53571 | 0
- | Restroom Vestibule Between B1/B2 | 83 | 5 |  | 63 | 1 | 1 |  | 504 | 9.881 | 2
- | Restroom Vestibule Between B3/B4 | 49 | 3 |  | 63 | 1 | 1 |  | 504 | 5.8333 | 2
- | Restroom Vestibule Between C1/C2 | 89 | 5 |  | 56 | 1 | 1 |  | 448 | 11.9196 | 3
- | Restroom Vestibule Between C3/C4 | 93 | 6 |  | 63 | 1 | 1 |  | 504 | 11.0714 | 3
- | Restroom Vestibule Between D1/D2 | 20 | 1 |  | 50 | 1 | 1 |  | 400 | 3 | 1
- | Restroom Vestibule Between D3/D4 | 27 | 1 |  | 51 | 1 | 1 |  | 408 | 3.9706 | 1
- | Restroom Vestibule Between E1/E2 | 55 | 3 |  | 51 | 1 | 1 |  | 408 | 8.0882 | 2
- | Restroom Vestibule Between E3/E4 | 54 | 3 |  | 51 | 1 | 1 |  | 408 | 7.9412 | 2
- | Restroom Vestibule Between G1/G2 | 3 | 0 |  | 50 | 1 | 0 |  | 400 | 0.45 | 0
- | Restroom Vestibule Between G3/G4 | 2 | 0 |  | 51 | 1 | 0 |  | 408 | 0.29412 | 0
- | 1st Flr Storage Room | 61 | 4 |  | 475 | 10 | 4 |  | 3800 | 0.96316 | 0
- | Truancy Office 1st Floor | 0 | 0 |  | 727 | 16 | 0 |  | 5816 | 0 | 0
- | Vestibule by stairs/Rooms 266 & 267 | 153 | 10 |  | 219 | 4 | 4 |  | 1752 | 5.2397 | 2
- | Vistibule by Meeting Room | 132 | 8 |  | 252 | 5 | 5 |  | 2016 | 3.9286 | 1
- | Womans Restroom by 1st Floor Elevator | 26 | 1 |  | 169 | 3 | 1 |  | 1352 | 1.1538 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-05-03 | [7 empty] | 0 | 0 | 0
School: | Mitchell Elementary School | [7 empty] | 0 | 0 | 0
| EMCOR | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
102 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
103 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
104 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
105 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
106 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
107 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
108 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
109 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
110 | Counselor's Office |  | 0 | Yes | 255 | 5 | 5 | House Fan | 2040 | 0 | 0
111 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
112 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
213 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
214 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
215 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
216 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
217 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
218 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
219 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
220 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
221 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
222 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
223 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
225 | Nurse |  | 0 | Yes | 378 | 8 | 8 | House Fan | 3024 | 0 | 0
324 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
325 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
326 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
327 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
328 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
329 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
330 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
331 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
332 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
333 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
334 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
B1 | Classroom |  | 0 | Yes | 756 | 17 | 17 | Unit Ventilator | 6048 | 0 | 0
B2 | B.E. Office |  | 0 | Yes | 200 | 4 | 4 |  | 1600 | 0 | 0
B3 | Classroom |  | 0 | Yes | 609 | 13 | 13 | Unit Ventilator | 4872 | 0 | 0
B4 | Classroom |  | 0 | Yes | 980 | 22 | 22 | Unit Ventilator | 7840 | 0 | 0
B6 | Classroom |  | 0 | Yes | 1344 | 30 | 30 | Unit Ventilator | 10752 | 0 | 0
- | SP Office |  | 0 | Yes | 88 | 2 | 2 |  | 704 | 0 | 0
- | Library |  | 0 | Yes | 1504 | 34 | 34 |  | 12032 | 0 | 0
- | Gym |  | 0 | Yes | 3495 | 79 | 79 | House Fan | 27960 | 0 | 0
- | Cafeteria Office |  | 0 | Yes | 134 | 3 | 3 |  | 1072 | 0 | 0
- | Cafeteria |  | 0 | Yes | 2452 | 55 | 55 | House Fan | 19616 | 0 | 0
- | Main Office |  | 0 | Yes | 494 | 11 | 11 | House Fan | 3952 | 0 | 0
- | Principal's Office |  | 0 | Yes | 216 | 4 | 4 | House Fan | 1728 | 0 | 0
110C | Vice Principal's Office |  | 0 | Yes | 101 | 2 | 2 |  | 808 | 0 | 0
110A | Administrative Assistant's Office |  | 0 | Yes | 191 | 4 | 4 |  | 1528 | 0 | 0
- | Teacher's Lounge/Multipurpose |  | 0 | Yes | 390 | 8 | 8 | House Fan | 3120 | 0 | 0
110B | Counselor's Office |  | 0 | Yes | 242 | 5 | 5 | House Fan | 1936 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-19 | [7 empty] | 0 | 0 | 0
School: | The Promise Academy @ Martin Luther King High School | [7 empty] | 0 | 0 | 0
Vendor: | Meehan (Auditorium) | Chadwick (Building) | Exhaust | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 464 | 30 |  | 828 | 18 | 18 |  | 6624 | 4.2029 | 2
102 | Classroom | 315 | 21 |  | 828 | 18 | 18 |  | 6624 | 2.8533 | 1
104 | Classroom | 260 | 17 |  | 900 | 20 | 17 |  | 7200 | 2.1667 | 1
105 | Classroom | 162 | 10 |  | 1050 | 23 | 10 |  | 8400 | 1.1571 | 1
106 | Classroom | 476 | 31 |  | 900 | 20 | 20 |  | 7200 | 3.9667 | 1
107 | Classroom | 229 | 15 |  | 864 | 19 | 15 |  | 6912 | 1.9878 | 1
108 | Classroom | 489 | 32 |  | 850 | 19 | 19 |  | 6800 | 4.3147 | 2
109 | Classroom | 304 | 20 |  | 896 | 20 | 20 |  | 7168 | 2.5446 | 1
110 | Classroom |  | 0 |  | 800 | 18 | 0 |  | 6400 | 0 | 0
116 | Classroom |  | 0 |  | 800 | 18 | 0 |  | 6400 | 0 | 0
117 | Classroom | 296 | 19 |  | 924 | 21 | 19 |  | 7392 | 2.4026 | 1
118 | Classroom | 278 | 18 |  | 864 | 19 | 18 |  | 6912 | 2.4132 | 1
120 | Classroom | 105 | 7 |  | 864 | 19 | 7 |  | 6912 | 0.91146 | 0
121 | Classroom | 176 | 11 |  | 864 | 19 | 11 |  | 6912 | 1.5278 | 1
122 | Classroom | 420 | 28 |  | 1152 | 26 | 26 |  | 9216 | 2.7344 | 1
123 | Classroom | 86 | 5 |  | 864 | 19 | 5 |  | 6912 | 0.74653 | 0
124 | Classroom | 252 | 16 |  | 900 | 20 | 16 |  | 7200 | 2.1 | 1
125 | Classroom | 203 | 13 |  | 864 | 19 | 13 |  | 6912 | 1.7622 | 1
201 | Classroom | 215 | 14 |  | 828 | 18 | 14 |  | 6624 | 1.9475 | 1
202 | Classroom | 201 | 13 |  | 864 | 19 | 13 |  | 6912 | 1.7448 | 1
204 | Classroom |  | 0 |  | 900 | 20 | 0 |  | 7200 | 0 | 0
205 | Classroom | 416 | 27 |  | 1050 | 23 | 23 |  | 8400 | 2.9714 | 1
206 | Classroom | 47 | 3 |  | 900 | 20 | 3 |  | 7200 | 0.39167 | 0
207 | Classroom | 90 | 6 |  | 864 | 19 | 6 |  | 6912 | 0.78125 | 0
208 | Classroom | 212 | 14 |  | 850 | 19 | 14 |  | 6800 | 1.8706 | 1
209 | Classroom | 360 | 24 |  | 896 | 20 | 20 |  | 7168 | 3.0134 | 1
210 | Classroom | 0 | 0 |  | 800 | 18 | 0 |  | 6400 | 0 | 0
216 | Classroom | 469 | 31 |  | 800 | 18 | 18 |  | 6400 | 4.3969 | 2
217 | Classroom | 130 | 8 |  | 924 | 21 | 8 |  | 7392 | 1.0552 | 1
218 | Classroom | 293 | 19 |  | 864 | 19 | 19 |  | 6912 | 2.5434 | 1
220 | Classroom | 318 | 21 |  | 864 | 19 | 19 |  | 6912 | 2.7604 | 1
221 | Classroom | 204 | 13 |  | 864 | 19 | 13 |  | 6912 | 1.7708 | 1
222 | Classroom | 210 | 14 |  | 1152 | 26 | 14 |  | 9216 | 1.3672 | 1
223 | Classroom | 170 | 11 |  | 864 | 19 | 11 |  | 6912 | 1.4757 | 1
224 | Classroom | 207 | 13 |  | 900 | 20 | 13 |  | 7200 | 1.725 | 1
225 | Classroom | 150 | 10 |  | 864 | 19 | 10 |  | 6912 | 1.3021 | 1
301 | Classroom | 161 | 10 |  | 828 | 18 | 10 |  | 6624 | 1.4583 | 1
302 | Classroom | 178 | 11 |  | 864 | 19 | 11 |  | 6912 | 1.5451 | 1
303 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | 0 | 0
304 | Classroom | 391 | 26 |  | 900 | 20 | 20 |  | 7200 | 3.2583 | 1
305 | Classroom | 244 | 16 |  | 1050 | 23 | 16 |  | 8400 | 1.7429 | 1
306 | Classroom | 347 | 23 |  | 900 | 20 | 20 |  | 7200 | 2.8917 | 1
307 | Classroom | 99 | 6 |  | 864 | 19 | 6 |  | 6912 | 0.85938 | 0
308 | Classroom | 217 | 14 |  | 850 | 19 | 14 |  | 6800 | 1.9147 | 1
309 | Classroom | 65 | 4 |  | 896 | 20 | 4 |  | 7168 | 0.54408 | 0
310 | Classroom | 347 | 23 |  | 800 | 18 | 18 |  | 6400 | 3.2531 | 1
313 | Classroom |  | 0 | Yes | 1368 | 31 | 31 |  | 10944 | 0 | 0
316 | Classroom | 297 | 19 |  | 800 | 18 | 18 |  | 6400 | 2.7844 | 1
317 | Classroom | 201 | 13 |  | 924 | 21 | 13 |  | 7392 | 1.6315 | 1
318 | Classroom | 275 | 18 |  | 864 | 19 | 18 |  | 6912 | 2.3872 | 1
320 | Classroom | 303 | 20 |  | 864 | 19 | 19 |  | 6912 | 2.6302 | 1
321 | Classroom | 85 | 5 |  | 864 | 19 | 5 |  | 6912 | 0.73785 | 0
322 | Classroom | 310 | 20 |  | 1152 | 26 | 20 |  | 9216 | 2.0182 | 1
323 | Classroom | 310 | 20 |  | 864 | 19 | 19 |  | 6912 | 2.691 | 1
324 | Classroom | 213 | 14 |  | 900 | 20 | 14 |  | 7200 | 1.775 | 1
325 | Classroom | 84 | 5 |  | 864 | 19 | 5 |  | 6912 | 0.72917 | 0
327 | Classroom |  | 0 | Yes | 1824 | 41 | 41 |  | 14592 | 0 | 0
- | Auditorium | 13590 | 906 |  | 4350 | 98 | 98 |  | 34800 | 23.431 | 3
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | John Moffet Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101A | Classroom | 97 | 6 |  | 360 | 8 | 6 | AHU | 2880 | 2.0208 | 1
104 | Classroom | 225 | 15 |  | 704 | 16 | 15 | Unit Ventilator | 5632 | 2.397 | 1
105 | Classroom | 205 | 13 |  | 575 | 13 | 13 | Unit Ventilator | 4600 | 2.6739 | 1
107 | Classroom | 271 | 18 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 2.5248 | 1
108 | Classroom | 327 | 21 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 3.1362 | 1
112 | Classroom | 524 | 34 |  | 896 | 20 | 20 | Unit Ventilator | 7168 | 4.3862 | 2
113 | Classroom | 293 | 19 |  | 928 | 21 | 19 | Unit Ventilator | 7424 | 2.368 | 1
114 | Classroom | 441 | 29 |  | 986 | 22 | 22 | Unit Ventilator | 7888 | 3.3545 | 1
115 | Classroom | 337 | 22 |  | 868 | 19 | 19 | Unit Ventilator | 6944 | 2.9119 | 1
119 | Nurse | 178 | 11 |  | 77 | 1 | 1 | AHU | 616 | 17.3377 | 3
201 | Classroom | 105 | 7 |  | 315 | 7 | 7 | Unit Ventilator | 2520 | 2.5 | 1
202 | Classroom | 745 | 49 |  | 891 | 20 | 20 | Unit Ventilator | 7128 | 6.271 | 2
203 | Classroom | 301 | 20 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 2.994 | 1
204 | Classroom | 357 | 23 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 3.5511 | 1
205 | Classroom | 267 | 17 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 3.0022 | 1
208 | Classroom | 183 | 12 |  | 924 | 21 | 12 | Unit Ventilator | 7392 | 1.4854 | 1
209 | Classroom | 542 | 36 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 6.0945 | 2
211 | Classroom | 543 | 36 |  | 648 | 14 | 14 | Unit Ventilator | 5184 | 6.2847 | 2
213 | Classroom | 114 | 7 |  | 352 | 8 | 7 | Unit Ventilator | 2816 | 2.429 | 1
214 | Classroom | 210 | 14 |  | 957 | 21 | 14 | Unit Ventilator | 7656 | 1.6458 | 1
215 | Classroom | 261 | 17 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 2.5962 | 1
216 | Classroom | 470 | 31 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 4.6751 | 2
217 | Classroom | 666 | 44 |  | 957 | 21 | 21 | Unit Ventilator | 7656 | 5.2194 | 2
218 | Classroom | 260 | 17 |  | 330 | 7 | 7 | Unit Ventilator | 2640 | 5.9091 | 2
219 | Classroom | 0 | 0 |  | 1100 | 25 | 0 | Unit Ventilator | 8800 | 0 | 0
221 | Classroom | 449 | 29 |  | 884 | 20 | 20 | Unit Ventilator | 7072 | 3.8094 | 1
223 | Classroom | 403 | 26 |  | 340 | 7 | 7 | AHU | 2720 | 8.8897 | 2
225 | Classroom | 266 | 17 |  | 858 | 19 | 17 | Unit Ventilator | 6864 | 2.3252 | 1
228A | Classroom | 60 | 4 |  | 252 | 5 | 4 | AHU | 2016 | 1.7857 | 1
229 | Classroom | 47 | 3 |  | 336 | 7 | 3 | AHU | 2688 | 1.0491 | 1
- | Auditorium | 773 | 51 |  | 2478 | 56 | 51 | AHU | 19824 | 2.3396 | 1
- | Faculty Lounge | 125 | 8 |  | 361 | 8 | 8 | Unit Ventilator | 2888 | 2.597 | 1
- | Library | 1025 | 68 |  | 1674 | 38 | 38 | AHU | 13392 | 4.5923 | 2
- | Office | 110 | 7 |  | 70 | 1 | 1 | AHU | 560 | 11.7857 | 3
- | Main Office | 87 | 5 |  | 496 | 11 | 5 | Unit Ventilator | 3968 | 1.3155 | 1
- | Principals Office | 140 | 9 |  | 294 | 6 | 6 | Unit Ventilator | 2352 | 3.5714 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | J. Hampton Moore Elementary School | [7 empty] | 0 | 0 | 0
| Mobile Classrooms | Main Building | Little School House | [5 empty] | 0 | 0 | 0
Vendor: | Devine | Main Retest | LSH Retest | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Moore Main | [8 empty] | 0 | 0 | 0
- | Auditorium | 224 | 14 |  | 3015 | 68 | 14 | AHU | 24120 | 0.55721 | 0
- | Gym | 145 | 9 | Yes | 4500 | 102 | 102 | AHU | 36000 | 0.24167 | 0
101 | Classroom | 518 | 34 |  | 1055 | 23 | 23 | Univent | 8440 | 3.6825 | 1
102 | Classroom | 504 | 33 |  | 1055 | 23 | 23 | Univent | 8440 | 3.5829 | 1
103 | Classroom | 364 | 24 |  | 624 | 14 | 14 | Univent | 4992 | 4.375 | 2
104 | Classroom | 116 | 7 | Yes | 458 | 10 | 10 | Univent | 3664 | 1.8996 | 1
105 | Classroom | 408 | 27 |  | 1082 | 24 | 24 | Univent | 8656 | 2.8281 | 1
106 | Classroom | 237 | 15 | Yes | 951 | 21 | 21 | Univent | 7608 | 1.8691 | 1
107 | Classroom | 535 | 35 |  | 951 | 21 | 21 | Univent | 7608 | 4.2192 | 2
108 | Classroom | 503 | 33 |  | 951 | 21 | 21 | Univent | 7608 | 3.9669 | 1
109 | Classroom | 220 | 14 | Yes | 951 | 21 | 21 | Univent | 7608 | 1.735 | 1
110 | Classroom | 113 | 7 | Yes | 951 | 21 | 21 | Univent | 7608 | 0.89117 | 0
110A | Classroom | 237 | 15 |  | 951 | 21 | 15 | Univent | 7608 | 1.8691 | 1
112 | Classroom | 325 | 21 |  | 951 | 21 | 21 | Univent | 7608 | 2.5631 | 1
113 | Classroom | 472 | 31 |  | 951 | 21 | 21 | Univent | 7608 | 3.7224 | 1
114 | Classroom | 487 | 32 |  | 951 | 21 | 21 | Univent | 7608 | 3.8407 | 1
115 | Classroom | 236 | 15 |  | 383 | 8 | 8 | Univent | 3064 | 4.6214 | 2
201 | Classroom | 480 | 32 |  | 976 | 22 | 22 | Univent | 7808 | 3.6885 | 1
202 | Classroom | 319 | 21 |  | 976 | 22 | 21 | Univent | 7808 | 2.4513 | 1
203 | Classroom | 251 | 16 | Yes | 951 | 21 | 21 | Univent | 7608 | 1.9795 | 1
203B | Classroom |  | 0 | Yes | 624 | 14 | 14 |  | 4992 | 0 | 0
204 | Classroom | 291 | 19 | Yes | 951 | 21 | 21 | Univent | 7608 | 2.295 | 1
205A | Classroom | 261 | 17 | Yes | 452 | 10 | 10 | Univent | 3616 | 4.3308 | 2
205B | Classroom | 130 | 8 | Yes | 642 | 14 | 14 | Univent | 5136 | 1.5187 | 1
206 | Classroom | 326 | 21 |  | 970 | 22 | 21 | Univent | 7760 | 2.5206 | 1
207 | Classroom | 424 | 28 |  | 951 | 21 | 21 | Univent | 7608 | 3.3438 | 1
207A | Classroom |  | 0 | Yes | 239 | 5 | 5 | N/A | 1912 | 0 | 0
208 | Classroom | 527 | 35 |  | 951 | 21 | 21 | Univent | 7608 | 4.1562 | 2
209 | Classroom | 399 | 26 |  | 951 | 21 | 21 | Univent | 7608 | 3.1467 | 1
210A | Classroom | 108 | 7 | Yes | 458 | 10 | 10 | Univent | 3664 | 1.7686 | 1
210B | Classroom | 335 | 22 | Yes | 458 | 10 | 10 | Univent | 3664 | 5.4858 | 2
211 | Classroom | 433 | 28 |  | 951 | 21 | 21 | Univent | 7608 | 3.4148 | 1
212 | Classroom | 244 | 16 | Yes | 951 | 21 | 21 | Univent | 7608 | 1.9243 | 1
213 | Classroom | 0 | 0 | Yes | 951 | 21 | 21 | Univent | 7608 | 0 | 0
214 | Classroom | 64 | 4 | Yes | 820 | 18 | 18 | Univent | 6560 | 0.58537 | 0
215 | Classroom | 454 | 30 |  | 951 | 21 | 21 | Univent | 7608 | 3.5804 | 1
216 | Classroom | 444 | 29 |  | 951 | 21 | 21 | Univent | 7608 | 3.5016 | 1
217 | Classroom | 520 | 34 |  | 951 | 21 | 21 | Univent | 7608 | 4.1009 | 2
218 | Classroom | 347 | 23 |  | 951 | 21 | 21 | Univent | 7608 | 2.7366 | 1
219 | Counselor Office |  | 0 | Yes | 170 | 3 | 3 |  | 1360 | 0 | 0
- | Principals Office | 0 | 0 | Yes | 400 | 9 | 9 |  | 3200 | 0 | 0
Assistant Principal | Office |  | 0 | Yes | 172 | 3 | 3 |  | 1376 | 0 | 0
Teachers Lounge | Room |  | 0 | Yes | 170 | 3 | 3 |  | 1360 | 0 | 0
2nd Floor Copy Room | Room |  | 0 | Yes | 172 | 3 | 3 |  | 1376 | 0 | 0
- | Nurse Office | 0 | 0 | Yes | 800 | 18 | 18 | Univent | 6400 | 0 | 0
Moore LSH | [8 empty] | 0 | 0 | 0
- | Office | 224 | 14 |  | 200 | 4 | 4 | FCU | 1600 | 8.4 | 2
- | Kitchen | 145 | 9 |  | 624 | 14 | 9 | FCU | 4992 | 1.7428 | 1
- | Faculty Lounge | 130 | 8 | Yes | 200 | 4 | 4 | FCU | 1600 | 4.875 | 2
P101 | Classroom |  | 0 | Yes | 120 | 2 | 2 |  | 960 | 0 | 0
P102 | Classroom |  | 0 | Yes | 120 | 2 | 2 |  | 960 | 0 | 0
P110 | Classroom | 361 | 24 |  | 950 | 21 | 21 | Univent | 7600 | 2.85 | 1
P111 | Classroom | 593 | 39 |  | 950 | 21 | 21 | Univent | 7600 | 4.6816 | 2
P112 | Classroom | 379 | 25 |  | 950 | 21 | 21 | Univent | 7600 | 2.9921 | 1
P113 | Classroom | 463 | 30 |  | 950 | 21 | 21 | Univent | 7600 | 3.6553 | 1
P114 | Classroom | 747 | 49 |  | 950 | 21 | 21 | Univent | 7600 | 5.8974 | 2
P114 | Hallway | 130 | 8 |  | 780 | 17 | 8 | FCU | 6240 | 1.25 | 1
P115 | Classroom | 361 | 24 |  | 950 | 21 | 21 | Univent | 7600 | 2.85 | 1
P116 | Classroom | 491 | 32 |  | 950 | 21 | 21 | Univent | 7600 | 3.8763 | 1
P117 | Classroom | 430 | 28 |  | 950 | 21 | 21 | Univent | 7600 | 3.3947 | 1
P124 | Classroom | 999 | 66 |  | 950 | 21 | 21 | Univent | 7600 | 7.8868 | 2
P124 | Hallway | 80 | 5 |  | 1122 | 25 | 5 | FCU | 8976 | 0.53476 | 0
P125 | Classroom | 476 | 31 |  | 950 | 21 | 21 | Univent | 7600 | 3.7579 | 1
P126 | Classroom | 304 | 20 |  | 950 | 21 | 20 | Univent | 7600 | 2.4 | 1
P127 | Classroom | 1009 | 67 |  | 950 | 21 | 21 | Univent | 7600 | 7.9658 | 2
Moore Modular | [8 empty] | 0 | 0 | 0
A-1 | Classroom | 568 | 37 |  | 781 | 17 | 17 | Univent | 6248 | 5.4545 | 2
A-2 | Classroom | 453 | 30 |  | 781 | 17 | 17 | Univent | 6248 | 4.3502 | 2
A-3 | Classroom | 441 | 29 |  | 781 | 17 | 17 | Univent | 6248 | 4.235 | 2
A-4 | Classroom | 360 | 24 |  | 781 | 17 | 17 | Univent | 6248 | 3.4571 | 1
A-5 | Classroom | 214 | 14 | Yes | 781 | 17 | 17 | Univent | 6248 | 2.0551 | 1
A-6 | Classroom | 125 | 8 | Yes | 781 | 17 | 17 | Univent | 6248 | 1.2004 | 1
A-7 | Classroom | 465 | 31 |  | 781 | 17 | 17 | Univent | 6248 | 4.4654 | 2
A-8 | Classroom | 629 | 41 |  | 781 | 17 | 17 | Univent | 6248 | 6.0403 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-12 | [7 empty] | 0 | 0 | 0
School: | Robert Morris Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 192 | 12 | Yes | 1284 | 29 | 29 | Univent | 10272 | 1.1215 | 1
101 | Classroom | 171 | 11 | Yes | 1410 | 32 | 32 | Univent | 11280 | 0.90957 | 0
200 | Classroom | 185 | 12 | Yes | 858 | 19 | 19 | Univent | 6864 | 1.6171 | 1
201 | Classroom | 72 | 4 | Yes | 603 | 13 | 13 | Univent | 4824 | 0.89552 | 0
202 | Classroom | 218 | 14 |  | 849 | 19 | 14 | Univent | 6792 | 1.9258 | 1
203 | Classroom | 200 | 13 | Yes | 821 | 18 | 18 | Univent | 6568 | 1.827 | 1
204 | Classroom | 163 | 10 | Yes | 846 | 19 | 19 | Univent | 6768 | 1.445 | 1
206 | Classroom | 85 | 5 |  | 847 | 19 | 5 | Univent | 6776 | 0.75266 | 0
208 | Classroom | 152 | 10 |  | 830 | 18 | 10 | Univent | 6640 | 1.3735 | 1
210 | Classroom | 0 | 0 |  | 837 | 19 | 0 | Univent | 6696 | 0 | 0
212 | Lunch Room | 137 | 9 |  | 876 | 19 | 9 | Univent | 7008 | 1.1729 | 1
213 | Classroom | 74 | 4 |  | 875 | 19 | 4 | Univent | 7000 | 0.63429 | 0
214 | Classroom | 125 | 8 |  | 848 | 19 | 8 | Univent | 6784 | 1.1055 | 1
215 | Classroom | 286 | 19 |  | 840 | 19 | 19 | Univent | 6720 | 2.5536 | 1
216 | Classroom | 94 | 6 |  | 848 | 19 | 6 | Univent | 6784 | 0.83137 | 0
217 | Classroom | 114 | 7 | Yes | 463 | 10 | 10 | Univent | 3704 | 1.8467 | 1
218 | Classroom | 283 | 18 |  | 1037 | 23 | 18 | Univent | 8296 | 2.0468 | 1
219 | Kitchen | 261 | 17 |  | 1204 | 27 | 17 | Univent | 9632 | 1.6258 | 1
300 | Classroom | 86 | 5 | Yes | 856 | 19 | 19 | Univent | 6848 | 0.7535 | 0
301 | Classroom | 273 | 18 |  | 601 | 13 | 13 | Univent | 4808 | 3.4068 | 1
302 | Classroom | 225 | 15 |  | 848 | 19 | 15 | Univent | 6784 | 1.99 | 1
303 | Classroom | 266 | 17 |  | 818 | 18 | 17 | Univent | 6544 | 2.4389 | 1
304 | Classroom | 86 | 5 |  | 843 | 19 | 5 | Univent | 6744 | 0.76512 | 0
306 | Classroom | 169 | 11 |  | 849 | 19 | 11 | Univent | 6792 | 1.4929 | 1
308 | Classroom | 129 | 8 | Yes | 828 | 18 | 18 | Univent | 6624 | 1.1685 | 1
310/312/314 | Library | 734 | 48 |  | 2102 | 47 | 47 | Univent | 16816 | 2.6189 | 1
313 | Classroom | 264 | 17 |  | 975 | 22 | 17 | Univent | 7800 | 2.0308 | 1
315 | Classroom | 217 | 14 |  | 1220 | 27 | 14 | Univent | 9760 | 1.334 | 1
316 | Classroom | 139 | 9 |  | 845 | 19 | 9 | Univent | 6760 | 1.2337 | 1
317 | Classroom | 152 | 10 | Yes | 462 | 10 | 10 | Univent | 3696 | 2.4675 | 1
319 | Art Room | 0 | 0 | Yes | 1042 | 23 | 23 | Univent | 8336 | 0 | 0
400 | Classroom | 58 | 3 |  | 857 | 19 | 3 | Univent | 6856 | 0.50758 | 0
401 | Classroom | 121 | 8 | Yes | 602 | 13 | 13 | Univent | 4816 | 1.5075 | 1
402 | Classroom | 169 | 11 |  | 846 | 19 | 11 | Univent | 6768 | 1.4982 | 1
403 | Classroom | 498 | 33 |  | 817 | 18 | 18 | Univent | 6536 | 4.5716 | 2
404 | Classroom | 92 | 6 |  | 848 | 19 | 6 | Univent | 6784 | 0.81368 | 0
406 | Classroom | 60 | 4 |  | 845 | 19 | 4 | Univent | 6760 | 0.53254 | 0
408 | Classroom | 55 | 3 | Yes | 829 | 18 | 18 | Univent | 6632 | 0.49759 | 0
410 | Classroom | 0 | 0 |  | 849 | 19 | 0 | Univent | 6792 | 0 | 0
412 | Lunch Room | 106 | 7 |  | 858 | 19 | 7 | Univent | 6864 | 0.92657 | 0
413 | Classroom | 313 | 20 |  | 871 | 19 | 19 | Univent | 6968 | 2.6952 | 1
414 | Classroom | 291 | 19 |  | 847 | 19 | 19 | Univent | 6776 | 2.5767 | 1
415 | Classroom | 147 | 9 | Yes | 836 | 19 | 19 | Univent | 6688 | 1.3188 | 1
416 | Classroom | 106 | 7 | Yes | 847 | 19 | 19 | Univent | 6776 | 0.93861 | 0
417 | Faculty | 158 | 10 |  | 446 | 10 | 10 | Univent | 3568 | 2.657 | 1
418 | Classroom | 34 | 2 | Yes | 1044 | 23 | 23 | Univent | 8352 | 0.24425 | 0
419 | Music Room | 511 | 34 |  | 1040 | 23 | 23 | Univent | 8320 | 3.6851 | 1
- | Auditorium | 1066 | 71 |  | 5308 | 120 | 71 | Univent | 42464 | 1.5062 | 1
- | Counselor's Office | 70 | 4 |  | 474 | 10 | 4 | Univent | 3792 | 1.1076 | 1
- | Gymnasium | 1100 | 73 |  | 3688 | 83 | 73 | Univent | 29504 | 2.237 | 1
- | Nurse's Office |  | 0 | Yes | 261 | 5 | 5 | N/A | 2088 | 0 | 0
- | Principal's Office |  | 0 | Yes | 294 | 6 | 6 | N/A | 2352 | 0 | 0
- | Main Office | 387 | 25 |  | 1373 | 31 | 25 | Univent | 10984 | 2.114 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | Andrew Morrison Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | EMCOR Retest 1-15-21 | Retest 2-22-21 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
5 | Music Rm |  | 0 | Yes | 813 | 18 | 18 | House Fan | 6504 | 0 | 0
8 | Art Rm |  | 0 | Yes | 886 | 20 | 20 | House Fan | 7088 | 0 | 0
101A | Nurse |  | 0 | Yes | 376 | 8 | 8 | House Fan | 3008 | 0 | 0
101B | Counselor |  | 0 |  | 341 | 7 | 0 | House Fan | 2728 | 0 | 0
102 | Classroom |  | 0 | Yes | 701 | 15 | 15 | House Fan | 5608 | 0 | 0
103 | Classroom |  | 0 | Yes | 734 | 16 | 16 | House Fan | 5872 | 0 | 0
104 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
106 | Lounge |  | 0 | Yes | 526 | 11 | 11 | House Fan | 4208 | 0 | 0
107 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
108 | Classroom |  | 0 | Yes | 566 | 12 | 12 | House Fan | 4528 | 0 | 0
109 | Classroom | 376 | 25 |  | 765 | 17 | 17 | Univent | 6120 | 3.6863 | 1
110 | Classroom | 427 | 28 |  | 792 | 18 | 18 | Univent | 6336 | 4.0436 | 2
111 | Classroom | 408 | 27 |  | 781 | 17 | 17 | Univent | 6248 | 3.9181 | 1
112 | Classroom | 469 | 31 |  | 792 | 18 | 18 | Univent | 6336 | 4.4413 | 2
113 | Classroom | 380 | 25 |  | 767 | 17 | 17 | Univent | 6136 | 3.7158 | 1
114 | Office / Classroom | 271 | 18 |  | 351 | 7 | 7 | Univent | 2808 | 5.7906 | 2
115 | Gym |  | 0 |  | 4693 | 106 | 0 | House Fan | 37544 | 0 | 0
200 | Office |  | 0 |  | 168 | 3 | 0 | House Fan | 1344 | 0 | 0
201 | Classroom |  | 0 |  | 726 | 16 | 0 | House Fan | 5808 | 0 | 0
202 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
203 | Classroom |  | 0 |  | 731 | 16 | 0 | House Fan | 5848 | 0 | 0
204 | Classroom |  | 0 |  | 718 | 16 | 0 | House Fan | 5744 | 0 | 0
204A | Office |  | 0 |  | 322 | 7 | 0 | House Fan | 2576 | 0 | 0
204B | Office |  | 0 | Yes | 150 | 3 | 3 | N/A | 1200 | 0 | 0
204C | Office |  | 0 |  | 84 | 1 | 0 | N/A | 672 | 0 | 0
205 | Classroom |  | 0 |  | 698 | 15 | 0 | House Fan | 5584 | 0 | 0
206 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
207 | Classroom |  | 0 |  | 698 | 15 | 0 | House Fan | 5584 | 0 | 0
208 | Classroom |  | 0 |  | 643 | 14 | 0 | House Fan | 5144 | 0 | 0
212 | Classroom | 48 | 3 |  | 398 | 9 | 3 | Univent | 3184 | 0.90452 | 0
213 | Classroom | 194 | 12 |  | 742 | 16 | 12 | Univent | 5936 | 1.9609 | 1
214 | Classroom | 197 | 13 |  | 864 | 19 | 13 | Univent | 6912 | 1.7101 | 1
215 | Office | 0 | 0 |  | 100 | 2 | 0 | Univent | 800 | 0 | 0
216 | Classroom | 411 | 27 |  | 762 | 17 | 17 | Univent | 6096 | 4.0453 | 2
217 | Classroom | 365 | 24 |  | 734 | 16 | 16 | Univent | 5872 | 3.7296 | 1
218 | Office / Classroom | 269 | 17 |  | 356 | 8 | 8 | Univent | 2848 | 5.6671 | 2
300 | Classroom |  | 0 |  | 644 | 14 | 0 | House Fan | 5152 | 0 | 0
301a | Office |  | 0 |  | 163 | 3 | 0 | House Fan | 1304 | 0 | 0
302 | Classroom |  | 0 |  | 688 | 15 | 0 | House Fan | 5504 | 0 | 0
303 | Classroom |  | 0 |  | 736 | 16 | 0 | House Fan | 5888 | 0 | 0
304 | Classroom |  | 0 |  | 666 | 15 | 0 | House Fan | 5328 | 0 | 0
306 | Classroom |  | 0 |  | 1085 | 24 | 0 | House Fan | 8680 | 0 | 0
306A | Library |  | 0 |  | 1166 | 26 | 0 | House Fan | 9328 | 0 | 0
307 | Classroom |  | 0 |  | 687 | 15 | 0 | House Fan | 5496 | 0 | 0
308 | Classroom |  | 0 |  | 798 | 18 | 0 | House Fan | 6384 | 0 | 0
312 | Classroom | 224 | 14 |  | 1070 | 24 | 14 | Rooftop Unit | 8560 | 1.5701 | 1
313 | Classroom | 0 | 0 |  | 944 | 21 | 0 | Rooftop Unit | 7552 | 0 | 0
314 | Classroom | 332 | 22 |  | 1117 | 25 | 22 | Rooftop Unit | 8936 | 2.2292 | 1
314 | Office | 0 | 0 |  | 372 | 8 | 0 | Univent | 2976 | 0 | 0
314A | Office |  | 0 |  | 372 | 8 | 0 | House Fan | 2976 | 0 | 0
315A | Teacher's Lounge | 0 | 0 |  | 294 | 6 | 0 | Univent | 2352 | 0 | 0
316 | Office / Classroom | 130 | 8 |  | 356 | 8 | 8 | Rooftop Unit | 2848 | 2.7388 | 1
- | Auditorium |  | 0 |  | 3657 | 83 | 0 | House Fan | 29256 | 0 | 0
- | Gym | 857 | 57 |  | 4693 | 106 | 57 | Univent | 37544 | 1.3696 | 1
- | Lunch Rm |  | 0 |  | 4331 | 98 | 0 | House Fan | 34648 | 0 | 0
- | Main Office |  | 0 | Yes | 395 | 8 | 8 | House Fan | 3160 | 0 | 0
- | Principals Office |  | 0 | Yes | 269 | 6 | 6 | House Fan | 2152 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Thomas G. Morton Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 0 | 0 | Yes | 988 | 22 | 22 | Univent | 7904 | 0 | 0
101 | Classroom | 0 | 0 | Yes | 875 | 19 | 19 | Univent | 7000 | 0 | 0
102 | Classroom | 374 | 24 |  | 792 | 18 | 18 | Air Coil Unit | 6336 | 3.5417 | 1
104B | Storage | 77 | 5 |  | 84 | 1 | 1 | Univent | 672 | 6.875 | 2
108A | Nurse Office | 125 | 8 |  | 90 | 2 | 2 | Univent | 720 | 10.4167 | 3
108B | Audio | 40 | 2 |  | 224 | 5 | 2 | Univent | 1792 | 1.3393 | 1
108C | Examination | 36 | 2 |  | 234 | 5 | 2 | Univent | 1872 | 1.1538 | 1
110 | Classroom | 0 | 0 |  | 513 | 11 | 0 | Univent | 4104 | 0 | 0
111 | Classroom | 309 | 20 | Yes | 252 | 5 | 5 | Univent | 2016 | 9.1964 | 2
200 | Classroom | 0 | 0 | Yes | 1071 | 24 | 24 | Univent | 8568 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 754 | 17 | 17 | Univent | 6032 | 0 | 0
202 | Classroom | 432 | 28 | Yes | 754 | 17 | 17 | Univent | 6032 | 4.2971 | 2
203 | Classroom | 475 | 31 |  | 8112 | 184 | 31 | Univent | 64896 | 0.43916 | 0
204 | Classroom | 399 | 26 |  | 438 | 9 | 9 | Univent | 3504 | 6.8322 | 2
205 | Classroom | 0 | 0 | Yes | 1015 | 23 | 23 | Univent | 8120 | 0 | 0
206 | Classroom | 0 | 0 | Yes | 1305 | 29 | 29 | Univent | 10440 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 1305 | 29 | 29 | Univent | 10440 | 0 | 0
208 | Classroom | 329 | 21 | Yes | 1015 | 23 | 23 | Univent | 8120 | 2.431 | 1
209 | Classroom | 280 | 18 | Yes | 408 | 9 | 9 | Univent | 3264 | 5.1471 | 2
210 | Classroom | 0 | 0 | Yes | 725 | 16 | 16 | Univent | 5800 | 0 | 0
211 | Classroom | 0 | 0 | Yes | 841 | 19 | 19 | Univent | 6728 | 0 | 0
212 | Classroom | 0 | 0 | Yes | 264 | 6 | 6 | Univent | 2112 | 0 | 0
213 | Classroom | 437 | 29 |  | 725 | 16 | 16 | Univent | 5800 | 4.5207 | 2
214A | Classroom | 94 | 6 |  | 190 | 4 | 4 | Univent | 1520 | 3.7105 | 1
214B | Classroom | 162 | 10 |  | 624 | 14 | 10 | Univent | 4992 | 1.9471 | 1
300 | Classroom | 309 | 20 |  | 780 | 17 | 17 | Univent | 6240 | 2.9712 | 1
301 | Classroom | 0 | 0 |  | 725 | 16 | 0 | Univent | 5800 | 0 | 0
302 | Classroom | 685 | 45 |  | 240 | 5 | 5 | Univent | 1920 | 21.4062 | 3
303 | Classroom | 486 | 32 |  | 754 | 17 | 17 | Univent | 6032 | 4.8342 | 2
304 | Classroom | 448 | 29 | Yes | 725 | 16 | 16 | Univent | 5800 | 4.6345 | 2
305 | Classroom | 291 | 19 |  | 312 | 7 | 7 | Univent | 2496 | 6.9952 | 2
306 | Classroom | 483 | 32 | Yes | 754 | 17 | 17 | Univent | 6032 | 4.8044 | 2
307 | Classroom | 415 | 27 | Yes | 756 | 17 | 17 | Univent | 6048 | 4.1171 | 2
308 | Library | 1124 | 74 |  | 2975 | 67 | 67 | Univent | 23800 | 2.8336 | 1
308 | Library Office | 0 | 0 |  | 462 | 10 | 0 | Univent | 3696 | 0 | 0
309 | Classroom | 283 | 18 | Yes | 806 | 18 | 18 | Univent | 6448 | 2.6334 | 1
310 | Classroom | 628 | 41 |  | 700 | 15 | 15 | Univent | 5600 | 6.7286 | 2
311 | Classroom | 294 | 19 |  | 754 | 17 | 17 | Univent | 6032 | 2.9244 | 1
312 | Classroom | 349 | 23 |  | 754 | 17 | 17 | Univent | 6032 | 3.4715 | 1
313 | Classroom | 547 | 36 |  | 486 | 11 | 11 | Univent | 3888 | 8.4414 | 2
315 | Classroom | 544 | 36 |  | 754 | 17 | 17 | Univent | 6032 | 5.4111 | 2
316 | Classroom | 324 | 21 |  | 754 | 17 | 17 | Univent | 6032 | 3.2228 | 1
317 | Classroom | 431 | 28 |  | 870 | 19 | 19 | Univent | 6960 | 3.7155 | 1
318 | Classroom | 305 | 20 |  | 312 | 7 | 7 | Univent | 2496 | 7.3317 | 2
319 | Classroom | 0 | 0 | Yes | 650 | 14 | 14 | Univent | 5200 | 0 | 0
320 | Classroom | 431 | 28 |  | 728 | 16 | 16 | Univent | 5824 | 4.4402 | 2
- | Auditorium | 5700 | 380 |  | 2646 | 60 | 60 | Air Coil Unit | 21168 | 16.1565 | 3
- | Cafeteria | 2196 | 146 | Yes | 2726 | 61 | 61 | Air Coil Unit | 21808 | 6.0418 | 2
- | Conference | 83 | 5 |  | 171 | 3 | 3 | Univent | 1368 | 3.6404 | 1
- | Counselors Office A | 87 | 5 |  | 99 | 2 | 2 | Univent | 792 | 6.5909 | 2
- | Counselors Office B | 91 | 6 |  | 128 | 2 | 2 | Univent | 1024 | 5.332 | 2
- | Counselors Office C | 148 | 9 |  | 100 | 2 | 2 | Univent | 800 | 11.1 | 3
- | Gym | 1927 | 128 |  | 4640 | 105 | 105 | Air Coil Unit | 37120 | 3.1148 | 1
- | Lounge | 311 | 20 |  | 351 | 7 | 7 | Univent | 2808 | 6.6453 | 2
- | Main Office | 285 | 19 |  | 380 | 8 | 8 | Univent | 3040 | 5.625 | 2
- | Copy Room | 53 | 3 |  | 60 | 1 | 1 | Univent | 480 | 6.625 | 2
- | Nurse | 83 | 5 |  | 123 | 2 | 2 | Univent | 984 | 5.061 | 2
- | Principal Office | 159 | 10 |  | 228 | 5 | 5 | Univent | 1824 | 5.2303 | 2
- | Vice Principal Office | 54 | 3 |  | 99 | 2 | 2 | Univent | 792 | 4.0909 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Motivation High School KIPP Turner West Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Capital | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Devine Part 2 | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
A-PreK Corridor | Corridor | 314 | 20 |  | 600 | 13 | 13 | Univent | 4800 | 3.925 | 1
A-PreK North Entrance-A | Corridor | 490 | 32 |  | 243 | 5 | 5 | Univent | 1944 | 15.1235 | 3
A-PreK North Entrance-B | Corridor | 548 | 36 |  | 480 | 10 | 10 | Univent | 3840 | 8.5625 | 2
A-PreK South Corridor | Corridor | 324 | 21 |  | 550 | 12 | 12 | Univent | 4400 | 4.4182 | 2
A-Wing Head Start Mech. Rm | Head Start PreK A169 & A170 | 349 | 23 |  | 1440 | 32 | 23 | Air Handling Unit | 11520 | 1.8177 | 1
A-Wing-Café Mech. Rm | 2nd & 3rd Flr. Staff Seminar Rms | 1734 | 115 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
A-Wing-Café Mech. Rm | 3rd Flr |  | 0 |  | 50 | 1 | 0 | Air Handling Unit | 400 | 0 | 0
A-Wing-Café Mech. Rm | 2nd Flr |  | 0 |  | 50 | 1 | 0 | Air Handling Unit | 400 | 0 | 0
A-Wing-Café Mech. Rm | Ground Flr. Administration | 351 | 23 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
A130 | Gym | 410 | 27 |  | 2552 | 58 | 27 | Heating Ventilation Unit | 20416 | 1.2049 | 1
A108 Locker Rm | A108 | 0 | 0 |  |  | 0 | 0 | Heating Ventilation Unit | 0 | 0 | 0
A152 Locker Rm | A152 | 1340 | 89 |  | 690 | 15 | 15 | Heating Ventilation Unit | 5520 | 14.5652 | 3
A162 Storage | A154 Corrective Gym | 306 | 20 |  | 5192 | 118 | 20 | Heating Ventilation Unit | 41536 | 0.44203 | 0
A165 | Storage | 0 | 0 |  | 5192 | 118 | 0 | Heating Ventilation Unit | 41536 | 0 | 0
B-157 | B-155 Fitness Rm | 1593 | 106 |  | 1150 | 26 | 26 | Univent | 9200 | 10.3891 | 3
MER Rm B146 | B-Wing | 555 | 37 |  | 1012 | 23 | 23 | Air Handling Unit | 8096 | 4.1131 | 2
B-Wing B137 | B-139 A, B, C, D | 2003 | 133 |  | 4134 | 93 | 93 | Air Handling Unit | 33072 | 3.6339 | 1
B101 Cafeteria | B-Wing Roof | 320 | 21 |  | 9405 | 213 | 21 | Air Handling Unit | 75240 | 0.25518 | 0
House Coord North 3rd & 2nd Flr | B-Wing Roof | 67 | 4 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
B318 | B-Wing Roof |  | 0 |  | 800 | 18 | 0 | Air Handling Unit | 6400 | 0 | 0
B218 | B-Wing Roof |  | 0 |  | 800 | 18 | 0 | Air Handling Unit | 6400 | 0 | 0
House Coord South 3rd & 2nd Flr | B-Wing Roof | 126 | 8 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
B306 | B-Wing Roof |  | 0 |  | 800 | 18 | 0 | Air Handling Unit | 6400 | 0 | 0
B206 | B-Wing Roof |  | 0 |  | 800 | 18 | 0 | Air Handling Unit | 6400 | 0 | 0
B325 IMC Library | B-Wing Roof | 7 | 0 |  | 851 | 19 | 0 | Air Handling Unit | 6808 | 0.061692 | 0
139A | Classroom |  | 0 |  | 880 | 20 | 0 |  | 7040 | 0 | 0
139B | Classroom |  | 0 |  | 987 | 22 | 0 |  | 7896 | 0 | 0
139C | Classroom |  | 0 |  | 884 | 20 | 0 |  | 7072 | 0 | 0
139D | Classroom |  | 0 |  | 1035 | 23 | 0 |  | 8280 | 0 | 0
151 | Classroom |  | 0 | Yes | 1824 | 41 | 41 |  | 14592 | 0 | 0
152 | Classroom |  | 0 | Yes | 1170 | 26 | 26 |  | 9360 | 0 | 0
B196 | Classroom | 376 | 25 |  | 567 | 12 | 12 | Univent | 4536 | 4.9735 | 2
B197 | Classroom | 755 | 50 |  | 962 | 21 | 21 | Univent | 7696 | 5.8862 | 2
B198 | Classroom | 739 | 49 |  | 792 | 18 | 18 | Univent | 6336 | 6.9981 | 2
B200 | Classroom | 1468 | 97 |  | 1564 | 35 | 35 | Univent | 12512 | 7.0396 | 2
B201 | Classroom | 673 | 44 |  | 850 | 19 | 19 | Univent | 6800 | 5.9382 | 2
B202 | Classroom | 172 | 11 |  | 748 | 17 | 11 | Univent | 5984 | 1.7246 | 1
B203 | Classroom | 673 | 44 |  | 748 | 17 | 17 | Univent | 5984 | 6.748 | 2
B204 | Classroom | 143 | 9 |  | 759 | 17 | 9 | Univent | 6072 | 1.413 | 1
B205 | Classroom | 555 | 37 |  | 720 | 16 | 16 | Univent | 5760 | 5.7812 | 2
B207 | Classroom | 629 | 41 |  | 748 | 17 | 17 | Univent | 5984 | 6.3068 | 2
B208 | Classroom | 640 | 42 |  | 759 | 17 | 17 | Univent | 6072 | 6.3241 | 2
B209 | Classroom | 108 | 7 |  | 816 | 18 | 7 | Univent | 6528 | 0.99265 | 0
B210 | Classroom | 630 | 42 |  | 720 | 16 | 16 | Univent | 5760 | 6.5625 | 2
B211 | Classroom | 350 | 23 |  | 720 | 16 | 16 | Univent | 5760 | 3.6458 | 1
B212 | Classroom | 538 | 35 |  | 1326 | 30 | 30 | Univent | 10608 | 3.043 | 1
B213 | Classroom | 244 | 16 |  | 759 | 17 | 16 | Univent | 6072 | 2.4111 | 1
B214 | Classroom | 0 | 0 |  | 759 | 17 | 0 | Univent | 6072 | 0 | 0
B215 | Classroom | 341 | 22 |  | 748 | 17 | 17 | Univent | 5984 | 3.4191 | 1
B216 | Classroom | 339 | 22 |  | 748 | 17 | 17 | Univent | 5984 | 3.3991 | 1
B217 | Classroom | 273 | 18 |  | 624 | 14 | 14 | Univent | 4992 | 3.2812 | 1
B219 | Classroom | 378 | 25 |  | 748 | 17 | 17 | Univent | 5984 | 3.7901 | 1
B220 | Classroom | 242 | 16 |  | 759 | 17 | 16 | Univent | 6072 | 2.3913 | 1
B221 | Classroom | 456 | 30 |  | 816 | 18 | 18 | Univent | 6528 | 4.1912 | 2
B222 | Classroom | 633 | 42 |  | 598 | 13 | 13 | Univent | 4784 | 7.939 | 2
B223 | Classroom | 642 | 42 |  | 690 | 15 | 15 | Univent | 5520 | 6.9783 | 2
B301 | Classroom | 200 | 13 |  | 850 | 19 | 13 | Univent | 6800 | 1.7647 | 1
B302 | Classroom | 129 | 8 |  | 748 | 17 | 8 | Univent | 5984 | 1.2934 | 1
B304 | Classroom | 630 | 42 |  | 1564 | 35 | 35 | Univent | 12512 | 3.0211 | 1
B305 | Classroom | 150 | 10 |  | 720 | 16 | 10 | Univent | 5760 | 1.5625 | 1
306 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0
B307 | Classroom | 193 | 12 |  | 748 | 17 | 12 | Univent | 5984 | 1.9352 | 1
B308 | Classroom | 110 | 7 |  | 759 | 17 | 7 | Univent | 6072 | 1.087 | 1
B309 | Classroom | 186 | 12 |  | 816 | 18 | 12 | Univent | 6528 | 1.7096 | 1
B310 | Classroom | 196 | 13 |  | 720 | 16 | 13 | Univent | 5760 | 2.0417 | 1
B311 | Classroom | 222 | 14 |  | 720 | 16 | 14 | Univent | 5760 | 2.3125 | 1
B312 | Classroom | 691 | 46 |  | 1326 | 30 | 30 | Univent | 10608 | 3.9084 | 1
B313 | Classroom | 264 | 17 |  | 759 | 17 | 17 | Univent | 6072 | 2.6087 | 1
B314 | Classroom | 436 | 29 |  | 759 | 17 | 17 | Univent | 6072 | 4.3083 | 2
B315 | Classroom | 198 | 13 |  | 748 | 17 | 13 | Univent | 5984 | 1.9853 | 1
B316 | Classroom | 160 | 10 |  | 748 | 17 | 10 | Univent | 5984 | 1.6043 | 1
B317 | Classroom | 198 | 13 |  | 624 | 14 | 13 | Univent | 4992 | 2.3798 | 1
318 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0
B319 | Classroom | 304 | 20 |  | 748 | 17 | 17 | Univent | 5984 | 3.0481 | 1
B320 | Classroom | 144 | 9 |  | 759 | 17 | 9 | Univent | 6072 | 1.4229 | 1
B321 | Classroom | 290 | 19 |  | 816 | 18 | 18 | Univent | 6528 | 2.6654 | 1
B322 | Classroom | 213 | 14 |  | 598 | 13 | 13 | Univent | 4784 | 2.6714 | 1
B323 | Classroom | 156 | 10 |  | 690 | 15 | 10 | Univent | 5520 | 1.6957 | 1
B324 | Classroom | 577 | 38 |  | 1435 | 32 | 32 | Univent | 11480 | 3.0157 | 1
Main Office | Main Office |  | 0 | Yes | 950 | 21 | 21 |  | 7600 | 0 | 0
Teachers Lounge | Lounge |  | 0 | Yes | 728 | 16 | 16 |  | 5824 | 0 | 0
Nurse | Office |  | 0 | Yes | 910 | 20 | 20 |  | 7280 | 0 | 0
C-Wing | Auditorium | 346 | 23 | Yes | 1476 | 33 | 33 | Air Handling Unit | 11808 | 1.7581 | 1
| Music Rm | [7 empty] | 0 | 0 | 0
C-Wing | Auditorium Comm. Rm. | 1811 | 120 |  | 7392 | 168 | 120 | Air Handling Unit | 59136 | 1.8375 | 1
C-Wing | Auditorium/ Auditorium Stage | 3862 | 257 |  | 1890 | 42 | 42 | Air Handling Unit | 15120 | 15.3254 | 3
Head Start | B110 Learning Lab & B104 Student Store | 457 | 30 |  | 81 | 1 | 1 | Air Handling Unit | 648 | 42.3148 | 4
Mech Rm. | [8 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-05-03 | [7 empty] | 0 | 0 | 0
School: | Luis Munoz – Marin Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100B | CORRIDOR | 149 | 9 |  | 618 | 14 | 9 | Air Handling Unit | 4944 | 1.8083 | 1
100E | CORRIDOR | 115 | 7 |  | 1780 | 40 | 7 | Air Handling Unit | 14240 | 0.48455 | 0
100F | CORRIDOR | 250 | 16 |  | 1210 | 27 | 16 | Air Handling Unit | 9680 | 1.5496 | 1
100G | CORRIDOR | 142 | 9 |  | 1404 | 31 | 9 | Air Handling Unit | 11232 | 0.75855 | 0
100H | CORRIDOR |  | 0 |  | 1780 | 40 | 0 | Air Handling Unit | 14240 | 0 | 0
102 | Classroom | 193 | 12 |  | 792 | 18 | 12 | Air Handling Unit | 6336 | 1.8277 | 1
104 | Classroom | 225 | 15 | Yes | 805 | 18 | 18 | Air Handling Unit | 6440 | 2.0963 | 1
105 | Classroom | 195 | 13 | Yes | 713 | 16 | 16 | Air Handling Unit | 5704 | 2.0512 | 1
106 | Classroom | 213 | 14 | Yes | 713 | 16 | 16 | Air Handling Unit | 5704 | 2.2405 | 1
107 | Classroom | 170 | 11 | Yes | 682 | 15 | 15 | Air Handling Unit | 5456 | 1.8695 | 1
108 | Classroom | 202 | 13 | Yes | 682 | 15 | 15 | Air Handling Unit | 5456 | 2.2214 | 1
109 | Classroom | 227 | 15 |  | 682 | 15 | 15 | Air Handling Unit | 5456 | 2.4963 | 1
110 | Classroom | 212 | 14 | Yes | 682 | 15 | 15 | Air Handling Unit | 5456 | 2.3314 | 1
111 | Classroom | 469 | 31 |  | 700 | 15 | 15 | Air Handling Unit | 5600 | 5.025 | 2
115 | LOBBY | 648 | 43 |  | 1368 | 31 | 31 | Air Handling Unit | 10944 | 3.5526 | 1
116 | - | 215 | 14 |  | 609 | 13 | 13 | Air Handling Unit | 4872 | 2.6478 | 1
118 | - | 177 | 11 | Yes | 672 | 15 | 15 | Air Handling Unit | 5376 | 1.9754 | 1
120 | - | 188 | 12 | Yes | 768 | 17 | 17 | Air Handling Unit | 6144 | 1.8359 | 1
121 | HEALTH | 87 | 5 |  | 816 | 18 | 5 | Air Handling Unit | 6528 | 0.79963 | 0
124A | OFFICE | 19 | 1 |  | 120 | 2 | 1 | Air Handling Unit | 960 | 1.1875 | 1
125 | SPE. | 17 | 1 | Yes | 336 | 7 | 7 | Air Handling Unit | 2688 | 0.37946 | 0
125 | OCC | 51 | 3 |  | 272 | 6 | 3 | Air Handling Unit | 2176 | 1.4062 | 1
126 | FAM MGMT | 272 | 18 |  | 1215 | 27 | 18 | Air Handling Unit | 9720 | 1.679 | 1
127 | CLASSROOM | 56 | 3 |  | 670 | 15 | 3 | Air Handling Unit | 5360 | 0.62687 | 0
127B |  | 15 |  |  | 39 |  | 0 | Air Handling Unit | 312 | 2.8846 | 1
127C |  | 18 |  |  | 149 |  | 0 | Air Handling Unit | 1192 | 0.90604 | 0
160 | Classroom | 27 | 1 |  | 39 | 0 | 0 | Air Handling Unit | 312 | 5.1923 | 2
161 | Classroom | 33 | 2 |  | 375 | 8 | 2 | Air Handling Unit | 3000 | 0.66 | 0
162 | Classroom | 55 | 3 |  | 114 | 2 | 2 | Air Handling Unit | 912 | 3.6184 | 1
163 | Classroom | 62 | 4 |  | 114 | 2 | 2 | Air Handling Unit | 912 | 4.0789 | 2
164 | Classroom | 33 | 2 |  | 117 | 2 | 2 | Air Handling Unit | 936 | 2.1154 | 1
166 | Classroom | 23 | 1 |  | 102 | 2 | 1 | Air Handling Unit | 816 | 1.6912 | 1
168 | Classroom | 33 | 2 |  | 109 | 2 | 2 | Air Handling Unit | 872 | 2.2706 | 1
169 | Classroom | 23 | 1 |  | 81 | 1 | 1 | Air Handling Unit | 648 | 2.1296 | 1
170 | Classroom | 35 | 2 |  | 134 | 3 | 2 | Air Handling Unit | 1072 | 1.959 | 1
171 | OFFICE | 223 | 14 |  | 148 | 3 | 3 | Air Handling Unit | 1184 | 11.3007 | 3
172 | - | 58 | 3 |  | 148 | 3 | 3 | Air Handling Unit | 1184 | 2.9392 | 1
173 | PRINCIPAL | 87 | 5 |  | 304 | 6 | 5 | Air Handling Unit | 2432 | 2.1464 | 1
176 | - | 114 | 7 |  | 148 | 3 | 3 | Air Handling Unit | 1184 | 5.777 | 2
177 | - | 69 | 4 |  | 134 | 3 | 3 | Air Handling Unit | 1072 | 3.8619 | 1
180 | CONFR | 54 | 3 |  | 244 | 5 | 3 | Air Handling Unit | 1952 | 1.6598 | 1
181 | ASS PRINC | 100 | 6 |  | 188 | 4 | 4 | Air Handling Unit | 1504 | 3.9894 | 1
181A | OFFICE | 42 | 2 |  | 125 | 2 | 2 | Air Handling Unit | 1000 | 2.52 | 1
182 | - | 42 | 2 |  | 131 | 2 | 2 | Air Handling Unit | 1048 | 2.4046 | 1
183 | - | 42 | 2 |  | 97 | 2 | 2 | Air Handling Unit | 776 | 3.2474 | 1
200A | CORRIDOR | 160 | 10 |  | 1780 | 40 | 10 | Air Handling Unit | 14240 | 0.67416 | 0
200C | CORRIDOR | 148 | 9 |  | 1780 | 40 | 9 | Air Handling Unit | 14240 | 0.6236 | 0
200D | CORRIDOR | 240 | 16 |  | 1359 | 30 | 16 | Air Handling Unit | 10872 | 1.3245 | 1
200E | CORRIDOR | 100 | 6 |  | 1404 | 31 | 6 | Air Handling Unit | 11232 | 0.53419 | 0
200F | - | 156 | 10 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 11.7 | 3
201 | Classroom | 204 | 13 | Yes | 714 | 16 | 16 | Univent and Air Handling Unit | 5712 | 2.1429 | 1
202 | Classroom | 94 | 6 | Yes | 713 | 16 | 16 | Univent and Air Handling Unit | 5704 | 0.98878 | 0
203 | Classroom | 68 | 4 | Yes | 704 | 16 | 16 | Univent and Air Handling Unit | 5632 | 0.72443 | 0
204 | Classroom | 418 | 27 |  | 764 | 17 | 17 | Univent and Air Handling Unit | 6112 | 4.1034 | 2
205 | Classroom | 152 | 10 | Yes | 764 | 17 | 17 | Univent and Air Handling Unit | 6112 | 1.4921 | 1
206 | Classroom | 241 | 16 | Yes | 764 | 17 | 17 | Univent and Air Handling Unit | 6112 | 2.3658 | 1
207 | Classroom | 148 | 9 |  | 648 | 14 | 9 | Univent and Air Handling Unit | 5184 | 1.713 | 1
208 | IMC | 338 | 22 |  | 1757 | 39 | 22 | Air Handling Unit | 14056 | 1.4428 | 1
209 | Classroom | 272 | 18 |  | 648 | 14 | 14 | Univent and Air Handling Unit | 5184 | 3.1481 | 1
213 | Classroom | 155 | 10 |  | 764 | 17 | 10 | Univent and Air Handling Unit | 6112 | 1.5216 | 1
214 | Classroom | 140 | 9 |  | 118 | 2 | 2 | Univent | 944 | 8.8983 | 2
214 | IMC | 311 | 20 |  | 1405 | 31 | 20 | Air Handling Unit | 11240 | 1.6601 | 1
214A | WORK | 32 | 2 |  | 118 | 2 | 2 | Air Handling Unit | 944 | 2.0339 | 1
215 | Classroom | 232 | 15 | Yes | 840 | 19 | 19 | Univent and Air Handling Unit | 6720 | 2.0714 | 1
216A | OFFICE | 64 | 4 |  | 165 | 3 | 3 | Air Handling Unit | 1320 | 2.9091 | 1
217 | Classroom | 200 | 13 |  | 782 | 17 | 13 | Univent and Air Handling Unit | 6256 | 1.9182 | 1
218 | Classroom | 120 | 8 |  | 374 | 8 | 8 | Univent | 2992 | 2.4064 | 1
218B | STR. | 65 | 4 | Yes | 2255 | 51 | 51 | Air Handling Unit | 18040 | 0.21619 | 0
218S | Classroom | 71 | 4 |  | 241 | 5 | 4 | Air Handling Unit | 1928 | 2.2095 | 1
219 | Classroom | 153 | 10 | Yes | 7825 | 177 | 177 | Univent and Air Handling Unit | 62600 | 0.14665 | 0
220 | Classroom | 117 | 7 | Yes | 648 | 14 | 14 | Univent and Air Handling Unit | 5184 | 1.3542 | 1
221 | Classroom | 253 | 16 | Yes | 764 | 17 | 17 | Univent and Air Handling Unit | 6112 | 2.4836 | 1
222 | OFFICE | 50 | 3 |  | 1105 | 25 | 3 | Air Handling Unit | 8840 | 0.33937 | 0
223 | Classroom | 188 | 12 | Yes | 690 | 15 | 15 | Univent and Air Handling Unit | 5520 | 2.0435 | 1
225 | Classroom | 73 | 4 | Yes | 870 | 19 | 19 | Univent | 6960 | 0.62931 | 0
225 | COMP. | 124 | 8 |  | 96 | 2 | 2 | Air Handling Unit | 768 | 9.6875 | 2
226 | TECH. | 94 | 6 | Yes | 906 | 20 | 20 | Air Handling Unit | 7248 | 0.77815 | 0
226 (right) | Classroom | 104 | 6 |  | 343 | 7 | 6 | Univent | 2744 | 2.2741 | 1
226(left) | Classroom | 191 | 12 |  | 104 | 2 | 2 | Univent | 832 | 13.774 | 3
226C | SHOP | 91 | 6 |  | 104 | 2 | 2 | Air Handling Unit | 832 | 6.5625 | 2
227 | Classroom | 150 | 10 |  | 660 | 15 | 10 | Univent and Air Handling Unit | 5280 | 1.7045 | 1
300b | Corridor | 191 | 12 |  | 1404 | 31 | 12 | Air Handling Unit | 11232 | 1.0203 | 1
300d | Corridor | 225 | 15 |  | 1359 | 30 | 15 | Air Handling Unit | 10872 | 1.2417 | 1
301 | Classroom | 224 | 14 | Yes | 714 | 16 | 16 | Univent and Air Handling Unit | 5712 | 2.3529 | 1
302 | Classroom | 229 | 15 | Yes | 757 | 17 | 17 | Univent and Air Handling Unit | 6056 | 2.2688 | 1
303 | Classroom | 188 | 12 | Yes | 704 | 16 | 16 | Univent and Air Handling Unit | 5632 | 2.0028 | 1
304 | Classroom | 194 | 12 | Yes | 757 | 17 | 17 | Univent and Air Handling Unit | 6056 | 1.9221 | 1
305 | Classroom | 232 | 15 | Yes | 704 | 16 | 16 | Univent and Air Handling Unit | 5632 | 2.4716 | 1
306 | Classroom | 243 | 16 | Yes | 757 | 17 | 17 | Univent and Air Handling Unit | 6056 | 2.4075 | 1
307 | Classroom | 139 | 9 | Yes | 648 | 14 | 14 | Univent and Air Handling Unit | 5184 | 1.6088 | 1
308 | Classroom | 86 | 5 |  | 734 | 16 | 5 | Univent and Air Handling Unit | 5872 | 0.87875 | 0
309 | Classroom | 120 | 8 | Yes | 648 | 14 | 14 | Univent and Air Handling Unit | 5184 | 1.3889 | 1
313 | Classroom | 156 | 10 | Yes | 1160 | 26 | 26 | Univent and Air Handling Unit | 9280 | 1.0086 | 1
314 | Classroom | 119 | 7 | Yes | 1163 | 26 | 26 | Univent and Air Handling Unit | 9304 | 0.76741 | 0
315 | Classroom | 107 | 7 | Yes | 713 | 16 | 16 | Univent and Air Handling Unit | 5704 | 1.1255 | 1
316 | Classroom | 49 | 3 | Yes | 782 | 17 | 17 | Univent and Air Handling Unit | 6256 | 0.46995 | 0
317 | Classroom | 99 | 6 | Yes | 782 | 17 | 17 | Univent and Air Handling Unit | 6256 | 0.94949 | 0
318 | Classroom | 118 | 7 | Yes | 684 | 15 | 15 | Univent and Air Handling Unit | 5472 | 1.2939 | 1
319 | Classroom | 358 | 23 |  | 782 | 17 | 17 | Univent and Air Handling Unit | 6256 | 3.4335 | 1
320 | Classroom | 252 | 16 |  | 648 | 14 | 14 | Univent and Air Handling Unit | 5184 | 2.9167 | 1
321 | Classroom | 454 | 30 |  | 648 | 14 | 14 | Univent and Air Handling Unit | 5184 | 5.2546 | 2
322 | OFFICE | 0 | 0 |  | 100 | 2 | 0 | Air Handling Unit | 800 | 0 | 0
- | AUDITORIUM | 2082 | 138 |  | 2938 | 66 | 66 | Air Handling Unit | 23504 | 5.3148 | 2
- | CAFETERIA | 251 | 16 | Yes | 4402 | 100 | 100 | Air Handling Unit | 35216 | 0.42765 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | George W. Nebinger Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom |  | 0 | Yes | 44 | 1 | 1 | House Fan | 352 | 0 | 0
102 | Classroom |  | 0 | Yes | 880 | 20 | 20 | House Fan | 7040 | 0 | 0
103 | Classroom |  | 0 |  | 644 | 14 | 0 | House Fan | 5152 | 0 | 0
104 | Classroom |  | 0 |  | 644 | 14 | 0 | House Fan | 5152 | 0 | 0
105 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | 0 | 0
106 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | 0 | 0
107 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
201 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
202 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
203 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | 0 | 0
204 | Classroom |  | 0 | Yes | 899 | 20 | 20 | House Fan | 7192 | 0 | 0
204A | Classroom |  | 0 | Yes | 285 | 6 | 6 | House Fan | 2280 | 0 | 0
205 | Classroom |  | 0 | Yes | 330 | 7 | 7 | House Fan | 2640 | 0 | 0
206 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | 0 | 0
207 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
208 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
301 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
302 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
303 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | 0 | 0
304 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | 0 | 0
305 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
305A | Classroom |  | 0 |  | 450 | 10 | 0 | House Fan | 3600 | 0 | 0
306 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | 0 | 0
307 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
308 | Classroom |  | 0 | Yes | 750 | 17 | 17 | House Fan | 6000 | 0 | 0
401 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
402 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
- | Gym |  | 0 |  | 2870 | 65 | 0 | House Fan | 22960 | 0 | 0
- | Main Office |  | 0 | Yes | 330 | 7 | 7 | House Fan | 2640 | 0 | 0
- | Principal's Office |  | 0 | Yes | 247 | 5 | 5 | House Fan | 1976 | 0 | 0
- | Health Room |  | 0 | Yes | 99 | 2 | 2 | House Fan | 792 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | Northeast High School | [7 empty] | 0 | 0 | 0
Vendor: | Capital Programs | Devine Brothers | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Devine Brothers Data | [8 empty] | 0 | 0 | 0
1 | Classroom | 591 | 39 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 6.2872 | 2
2 | Classroom | 520 | 34 |  | 619 | 14 | 14 | Unit Ventilator | 4952 | 6.3005 | 2
3 | Classroom | 546 | 36 |  | 759 | 17 | 17 | Unit Ventilator | 6072 | 5.3953 | 2
4 | Classroom | 545 | 36 |  | 749 | 17 | 17 | Unit Ventilator | 5992 | 5.4573 | 2
5 | Classroom | 586 | 39 |  | 807 | 18 | 18 | Unit Ventilator | 6456 | 5.4461 | 2
6 | Classroom | 564 | 37 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 5.4092 | 2
7 | Classroom | 572 | 38 |  | 761 | 17 | 17 | Unit Ventilator | 6088 | 5.6373 | 2
8 | Classroom | 539 | 35 |  | 775 | 17 | 17 | Unit Ventilator | 6200 | 5.2161 | 2
9 | Classroom | 280 | 18 |  | 762 | 17 | 17 | Unit Ventilator | 6096 | 2.7559 | 1
10 | Classroom | 271 | 18 |  | 749 | 17 | 17 | Unit Ventilator | 5992 | 2.7136 | 1
11 | Classroom | 337 | 22 |  | 770 | 17 | 17 | Unit Ventilator | 6160 | 3.2825 | 1
12 | Classroom | 633 | 42 |  | 1673 | 38 | 38 | Unit Ventilator | 13384 | 2.8377 | 1
13 | Classroom | 541 | 36 |  | 1744 | 39 | 36 | Unit Ventilator | 13952 | 2.3265 | 1
14 | Classroom | 334 | 22 |  | 1047 | 23 | 22 | Unit Ventilator | 8376 | 2.3926 | 1
15 | Classroom | 507 | 33 |  | 1526 | 34 | 33 | Unit Ventilator | 12208 | 2.4918 | 1
16A | Classroom | 238 | 15 |  | 731 | 16 | 15 | Unit Ventilator | 5848 | 2.4419 | 1
16B | Classroom | 264 | 17 |  | 885 | 20 | 17 | Unit Ventilator | 7080 | 2.2373 | 1
17A | Classroom | 380 | 25 |  | 661 | 15 | 15 | Unit Ventilator | 5288 | 4.3116 | 2
17B | Classroom | 419 | 27 |  | 853 | 19 | 19 | Unit Ventilator | 6824 | 3.6841 | 1
17C | Classroom | 259 | 17 |  | 1050 | 23 | 17 | Unit Ventilator | 8400 | 1.85 | 1
18B | Classroom | 0 | 0 |  | 962 | 21 | 0 | Unit Ventilator | 7696 | 0 | 0
18D | Classroom | 0 | 0 |  | 843 | 19 | 0 | Unit Ventilator | 6744 | 0 | 0
19B | Classroom | 374 | 24 |  | 862 | 19 | 19 | Unit Ventilator | 6896 | 3.2541 | 1
21 | Offices | 0 | 0 |  | 1233 | 28 | 0 | Vertical Fan Coil Unit | 9864 | 0 | 0
22 | Office | 230 | 15 |  | 172 | 3 | 3 | Unit Ventilator | 1376 | 10.0291 | 3
23 | Classroom | 260 | 17 |  | 741 | 16 | 16 | Unit Ventilator | 5928 | 2.6316 | 1
24 | Classroom | 129 | 8 |  | 370 | 8 | 8 | Unit Ventilator | 2960 | 2.6149 | 1
27 | Teacher's Lounge | 378 | 25 |  | 1205 | 27 | 25 | Unit Ventilator | 9640 | 2.3527 | 1
31 | Classroom | 0 | 0 |  | 562 | 12 | 0 | Unit Ventilator | 4496 | 0 | 0
32 | Classrm. Lab | 2251 | 150 |  | 824 | 18 | 18 | Unit Ventilator | 6592 | 20.4885 | 3
32A | Classrm. Lab | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0
34A | Office | 0 | 0 |  | 187 | 4 | 0 | Unit Ventilator | 1496 | 0 | 0
33 | Classroom | 499 | 33 |  | 571 | 12 | 12 | Unit Ventilator | 4568 | 6.5543 | 2
35 | Office | 0 | 0 |  | 459 | 10 | 0 | Unit Ventilator | 3672 | 0 | 0
105 | Offices | 517 | 34 |  | 519 | 11 | 11 | Unit Ventilator | 4152 | 7.4711 | 2
106 | Classroom | 748 | 49 |  | 1031 | 23 | 23 | Unit Ventilator | 8248 | 5.4413 | 2
108 | Classroom | 739 | 49 |  | 948 | 21 | 21 | Unit Ventilator | 7584 | 5.8465 | 2
109 | Classroom | 508 | 33 |  | 940 | 21 | 21 | Unit Ventilator | 7520 | 4.0532 | 2
110 | Library | 610 | 40 |  | 386 | 8 | 8 | Unit Ventilator | 3088 | 11.8523 | 3
111 | Classroom | 553 | 36 |  | 993 | 22 | 22 | Unit Ventilator | 7944 | 4.1767 | 2
112 | Classroom | 602 | 40 |  | 980 | 22 | 22 | Unit Ventilator | 7840 | 4.6071 | 2
113 | Classroom | 535 | 35 |  | 883 | 20 | 20 | Unit Ventilator | 7064 | 4.5442 | 2
114 | Classroom | 363 | 24 |  | 717 | 16 | 16 | Unit Ventilator | 5736 | 3.7971 | 1
115 | Room | 541 | 36 |  | 965 | 21 | 21 | Unit Ventilator | 7720 | 4.2047 | 2
116 | Classroom | 623 | 41 |  | 745 | 16 | 16 | Unit Ventilator | 5960 | 6.2718 | 2
117 | Classroom | 0 | 0 |  | 686 | 15 | 0 | Unit Ventilator | 5488 | 0 | 0
118 | Classroom | 543 | 36 |  | 842 | 19 | 19 | Unit Ventilator | 6736 | 4.8367 | 2
119 | Classroom | 436 | 29 |  | 766 | 17 | 17 | Unit Ventilator | 6128 | 4.2689 | 2
120 | Classroom | 370 | 24 |  | 741 | 16 | 16 | Unit Ventilator | 5928 | 3.7449 | 1
121 | Classroom | 370 | 24 |  | 767 | 17 | 17 | Unit Ventilator | 6136 | 3.618 | 1
122 | Classroom | 495 | 33 |  | 1571 | 35 | 33 | Unit Ventilator | 12568 | 2.3631 | 1
123 | Classroom | 403 | 26 |  | 738 | 16 | 16 | Unit Ventilator | 5904 | 4.0955 | 2
124 | Classroom | 458 | 30 |  | 1410 | 32 | 30 | Unit Ventilator | 11280 | 2.4362 | 1
125 | Classroom | 392 | 26 |  | 802 | 18 | 18 | Unit Ventilator | 6416 | 3.6658 | 1
126 | Classroom | 326 | 21 |  | 698 | 15 | 15 | Unit Ventilator | 5584 | 3.5029 | 1
127 | Classroom | 425 | 28 |  | 751 | 17 | 17 | Unit Ventilator | 6008 | 4.2443 | 2
130 | Classroom | 481 | 32 |  | 1091 | 24 | 24 | Unit Ventilator | 8728 | 3.3066 | 1
131 | Classroom | 409 | 27 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 4.3022 | 2
132 | Classroom | 726 | 48 |  | 1038 | 23 | 23 | Unit Ventilator | 8304 | 5.2457 | 2
133 | Classroom | 679 | 45 |  | 1627 | 36 | 36 | Unit Ventilator | 13016 | 3.13 | 1
133A | Office | 0 | 0 |  | 293 | 6 | 0 | Unit Ventilator | 2344 | 0 | 0
134 | Classroom | 181 | 12 |  | 402 | 9 | 9 | Unit Ventilator | 3216 | 3.3769 | 1
136 | Classroom | 712 | 47 |  | 1206 | 27 | 27 | Unit Ventilator | 9648 | 4.4279 | 2
137 | Classroom | 537 | 35 |  | 773 | 17 | 17 | Unit Ventilator | 6184 | 5.2102 | 2
138 | Classroom | 453 | 30 |  | 1240 | 28 | 28 | Unit Ventilator | 9920 | 2.7399 | 1
139 | Classroom | 601 | 40 |  | 798 | 18 | 18 | Unit Ventilator | 6384 | 5.6485 | 2
140 | Classroom | 356 | 23 |  | 694 | 15 | 15 | Unit Ventilator | 5552 | 3.8473 | 1
141 | Classroom | 510 | 34 |  | 773 | 17 | 17 | Unit Ventilator | 6184 | 4.9483 | 2
143 | Classroom | 368 | 24 |  | 778 | 17 | 17 | Unit Ventilator | 6224 | 3.5476 | 1
150 | Classroom | 118 | 7 |  | 845 | 19 | 7 | Unit Ventilator | 6760 | 1.0473 | 1
152 | Classroom | 127 | 8 |  | 881 | 20 | 8 | Unit Ventilator | 7048 | 1.0812 | 1
154 | Classroom | 0 | 0 |  | 874 | 19 | 0 | Unit Ventilator | 6992 | 0 | 0
156 | Classroom | 132 | 8 |  | 815 | 18 | 8 | Unit Ventilator | 6520 | 1.2147 | 1
158 | Classroom | 160 | 10 |  | 849 | 19 | 10 | Unit Ventilator | 6792 | 1.4134 | 1
160 | Classroom | 158 | 10 |  | 835 | 18 | 10 | Unit Ventilator | 6680 | 1.4192 | 1
162 | Classroom | 0 | 0 |  | 711 | 16 | 0 | Unit Ventilator | 5688 | 0 | 0
175 | Classroom | 480 | 32 |  | 1223 | 27 | 27 | Unit Ventilator | 9784 | 2.9436 | 1
200 | Classroom | 137 | 9 |  | 715 | 16 | 9 | Unit Ventilator | 5720 | 1.4371 | 1
201 | Classroom | 548 | 36 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 5.6456 | 2
202 | Classroom | 525 | 35 |  | 755 | 17 | 17 | Unit Ventilator | 6040 | 5.2152 | 2
203 | Classroom | 232 | 15 |  | 555 | 12 | 12 | Unit Ventilator | 4440 | 3.1351 | 1
203A | Classroom | 418 | 27 |  | 546 | 12 | 12 | Unit Ventilator | 4368 | 5.7418 | 2
204 | Classroom | 523 | 34 |  | 572 | 13 | 13 | Unit Ventilator | 4576 | 6.8575 | 2
205 | Classroom | 441 | 29 |  | 1073 | 24 | 24 | Unit Ventilator | 8584 | 3.0825 | 1
206 | Classroom | 463 | 30 |  | 677 | 15 | 15 | Unit Ventilator | 5416 | 5.1292 | 2
207 | Classroom | 790 | 52 |  | 651 | 14 | 14 | Unit Ventilator | 5208 | 9.1014 | 2
208 | Classroom | 704 | 46 |  | 724 | 16 | 16 | Unit Ventilator | 5792 | 7.2928 | 2
209 | Classroom | 769 | 51 |  | 1069 | 24 | 24 | Unit Ventilator | 8552 | 5.3952 | 2
210 | Classroom | 410 | 27 |  | 730 | 16 | 16 | Unit Ventilator | 5840 | 4.2123 | 2
211 | Classroom | 730 | 48 |  | 1069 | 24 | 24 | Unit Ventilator | 8552 | 5.1216 | 2
212 | Classroom | 504 | 33 |  | 662 | 15 | 15 | Unit Ventilator | 5296 | 5.71 | 2
213 | Classroom | 650 | 43 |  | 1100 | 25 | 25 | Unit Ventilator | 8800 | 4.4318 | 2
214 | Classroom | 522 | 34 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 5.4909 | 2
215 A&B | Offices | 842 | 56 |  | 410 | 9 | 9 | Unit Ventilator | 3280 | 15.4024 | 3
215 C&D | Offices | 833 | 55 |  | 410 | 9 | 9 | Unit Ventilator | 3280 | 15.2378 | 3
216 | Classroom | 552 | 36 |  | 678 | 15 | 15 | Unit Ventilator | 5424 | 6.1062 | 2
218 | Classroom | 527 | 35 |  | 677 | 15 | 15 | Unit Ventilator | 5416 | 5.8383 | 2
219A | Classroom | 313 | 20 |  | 607 | 13 | 13 | Unit Ventilator | 4856 | 3.8674 | 1
219B | Classroom | 322 | 21 |  | 446 | 10 | 10 | Unit Ventilator | 3568 | 5.4148 | 2
220 | Classroom | 534 | 35 |  | 662 | 15 | 15 | Unit Ventilator | 5296 | 6.0498 | 2
221A | Classroom | 307 | 20 |  | 717 | 16 | 16 | Unit Ventilator | 5736 | 3.2113 | 1
221B | Classroom | 334 | 22 |  | 391 | 8 | 8 | Unit Ventilator | 3128 | 6.4066 | 2
222 | Classroom | 547 | 36 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 5.1799 | 2
223A | Classroom | 267 | 17 |  | 598 | 13 | 13 | Unit Ventilator | 4784 | 3.3487 | 1
223C | Classroom | 426 | 28 |  | 373 | 8 | 8 | Unit Ventilator | 2984 | 8.5657 | 2
225 | Classroom | 708 | 47 |  | 1445 | 32 | 32 | Unit Ventilator | 11560 | 3.6747 | 1
227A | Classroom | 311 | 20 |  | 590 | 13 | 13 | Unit Ventilator | 4720 | 3.9534 | 1
227B | Classroom | 298 | 19 |  | 494 | 11 | 11 | Unit Ventilator | 3952 | 4.5243 | 2
228 | Classroom | 525 | 35 |  | 784 | 17 | 17 | Unit Ventilator | 6272 | 5.0223 | 2
229B | Classroom | 165 | 11 |  | 525 | 11 | 11 | Unit Ventilator | 4200 | 2.3571 | 1
229C | Classroom | 325 | 21 |  | 570 | 12 | 12 | Unit Ventilator | 4560 | 4.2763 | 2
230 | Classroom | 503 | 33 |  | 657 | 14 | 14 | Unit Ventilator | 5256 | 5.742 | 2
231 | Classroom | 562 | 37 |  | 751 | 17 | 17 | Unit Ventilator | 6008 | 5.6125 | 2
232 | Classroom | 592 | 39 |  | 691 | 15 | 15 | Unit Ventilator | 5528 | 6.4255 | 2
233 | Classroom | 557 | 37 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 5.9255 | 2
234 | Classroom | 532 | 35 |  | 703 | 15 | 15 | Unit Ventilator | 5624 | 5.6757 | 2
235 | Classroom | 458 | 30 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 4.8793 | 2
236 | Classroom | 405 | 27 |  | 701 | 15 | 15 | Unit Ventilator | 5608 | 4.3331 | 2
237 | Room | 148 | 9 |  | 384 | 8 | 8 | Unit Ventilator | 3072 | 2.8906 | 1
238 | Classroom | 389 | 25 |  | 675 | 15 | 15 | Unit Ventilator | 5400 | 4.3222 | 2
240 | Classroom | 411 | 27 |  | 685 | 15 | 15 | Unit Ventilator | 5480 | 4.5 | 2
242 | Classroom | 479 | 31 |  | 711 | 16 | 16 | Unit Ventilator | 5688 | 5.0527 | 2
244 | Classroom | 518 | 34 |  | 634 | 14 | 14 | Unit Ventilator | 5072 | 6.1278 | 2
1st Fl. Corridor | Corridor | 0 | 0 |  | 892 | 20 | 0 | Unit Ventilator | 7136 | 0 | 0
2nd Fl. Corr. | 2nd Fl. Corr. | 0 | 0 |  | 9100 | 206 | 0 | Unit Ventilator | 72800 | 0 | 0
- | Auditorium | 1799 | 119 |  | 12288 | 279 | 119 | Heating Ventilation Unit | 98304 | 1.098 | 1
- | Band Room | 254 | 16 |  | 1028 | 23 | 16 | Heating Ventilation Unit | 8224 | 1.8531 | 1
Boys Gym #1 | Gym | 336 | 22 |  | 3701 | 84 | 22 | Heating Ventilation Unit | 29608 | 0.6809 | 0
Boys Gym #1 | Gym | 307 | 20 |  | 3701 | 84 | 20 | Heating Ventilation Unit | 29608 | 0.62213 | 0
Boys Gym #2 | Gym | 2587 | 172 |  | 3701 | 84 | 84 | Heating Ventilation Unit | 29608 | 5.2425 | 2
Boys Gym #2 | Gym | 1367 | 91 |  | 3701 | 84 | 84 | Heating Ventilation Unit | 29608 | 2.7702 | 1
Boys Lckr. Rm. | Locker Rm. | 1229 | 81 |  | 5966 | 135 | 81 | Heating Ventilation Unit | 47728 | 1.545 | 1
Cafeteria | Cafeteria | 1685 | 112 |  | 12073 | 274 | 112 | Heating Ventilation Unit | 96584 | 1.0468 | 1
Girls Gym #1 | Gym | 317 | 21 |  | 3514 | 79 | 21 | Heating Ventilation Unit | 28112 | 0.67658 | 0
Girls Gym #1 | Gym | 397 | 26 |  | 3514 | 79 | 26 | Heating Ventilation Unit | 28112 | 0.84732 | 0
Girls Gym #2 | Gym | 187 | 12 |  | 3514 | 79 | 12 | Heating Ventilation Unit | 28112 | 0.39912 | 0
Girls Lckr. Rm. | Locker Rm. | 0 | 0 |  | 3920 | 89 | 0 | Heating Ventilation Unit | 31360 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0
Library | Library | 2751 | 183 |  | 1816 | 41 | 41 | Heating Ventilation Unit | 14528 | 11.3615 | 3
Library | Library | 453 | 30 |  | 454 | 10 | 10 | Unit Ventilator | 3632 | 7.4835 | 2
Library | Library | 525 | 35 |  | 454 | 10 | 10 | Unit Ventilator | 3632 | 8.6729 | 2
Library | Library | 509 | 33 |  | 454 | 10 | 10 | Unit Ventilator | 3632 | 8.4086 | 2
Library | Library | 477 | 31 |  | 454 | 10 | 10 | Unit Ventilator | 3632 | 7.88 | 2
Main office | Offices | 446 | 29 |  | 2450 | 55 | 29 | Unit Ventilator | 19600 | 1.3653 | 1
Stage | Stage | 235 | 15 |  | 1743 | 39 | 15 | Unit Ventilator | 13944 | 1.0112 | 1
Stage | Stage | 262 | 17 |  | 1743 | 39 | 17 | Unit Ventilator | 13944 | 1.1274 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Olney Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Main Building ABR | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Main Building | [8 empty] | 0 | 0 | 0
101 | Classroom | 180 | 12 |  | 520 | 11 | 11 | AIr Handling Unit | 4160 | 2.5962 | 1
102 | Classroom | 122 | 8 |  | 520 | 11 | 8 | AIr Handling Unit | 4160 | 1.7596 | 1
103 | Classroom | 142 | 9 |  | 520 | 11 | 9 | AIr Handling Unit | 4160 | 2.0481 | 1
104 | Classroom | 527 | 35 |  | 520 | 11 | 11 | AIr Handling Unit | 4160 | 7.601 | 2
107 | Classroom | 63 | 4 |  | 667 | 15 | 4 | Univent | 5336 | 0.7084 | 0
108 | Classroom | 235 | 15 |  | 840 | 19 | 15 | Univent | 6720 | 2.0982 | 1
111 | Classroom | 88 | 5 |  | 378 | 8 | 5 | Univent | 3024 | 1.746 | 1
201 | Classroom | 289 | 19 |  | 682 | 15 | 15 | Univent | 5456 | 3.1782 | 1
203 | Classroom | 327 | 21 |  | 928 | 21 | 21 | Univent | 7424 | 2.6428 | 1
204 | Classroom | 286 | 19 |  | 756 | 17 | 17 | Univent | 6048 | 2.8373 | 1
205 | Classroom | 303 | 20 |  | 784 | 17 | 17 | Univent | 6272 | 2.8986 | 1
206 | Classroom | 296 | 19 |  | 812 | 18 | 18 | Univent | 6496 | 2.734 | 1
207 | Classroom | 309 | 20 |  | 594 | 13 | 13 | Univent | 4752 | 3.9015 | 1
208 | Classroom | 324 | 21 |  | 748 | 17 | 17 | Univent | 5984 | 3.2487 | 1
209 | Classroom | 282 | 18 |  | 1232 | 28 | 18 | Univent | 9856 | 1.7167 | 1
210 | Classroom | 327 | 21 |  | 330 | 7 | 7 | Univent | 2640 | 7.4318 | 2
211 | Classroom | 326 | 21 |  | 756 | 17 | 17 | Univent | 6048 | 3.2341 | 1
301 | Classroom | 0 | 0 |  | 682 | 15 | 0 | Univent | 5456 | 0 | 0
302 | Classroom | 328 | 21 |  | 682 | 15 | 15 | Univent | 5456 | 3.607 | 1
303 | Classroom | 281 | 18 |  | 899 | 20 | 18 | Univent | 7192 | 2.3443 | 1
304 | Classroom | 280 | 18 |  | 729 | 16 | 16 | Univent | 5832 | 2.8807 | 1
305 | Classroom | 324 | 21 |  | 812 | 18 | 18 | Univent | 6496 | 2.9926 | 1
306 | Classroom | 285 | 19 |  | 783 | 17 | 17 | Univent | 6264 | 2.7299 | 1
307 | Classroom | 279 | 18 |  | 594 | 13 | 13 | Univent | 4752 | 3.5227 | 1
308 | Classroom | 291 | 19 |  | 782 | 17 | 17 | Univent | 6256 | 2.7909 | 1
309 | Classroom | 325 | 21 |  | 638 | 14 | 14 | Univent | 5104 | 3.8205 | 1
310 | Classroom | 328 | 21 |  | 638 | 14 | 14 | Univent | 5104 | 3.8558 | 1
311 | Classroom | 309 | 20 |  | 756 | 17 | 17 | Univent | 6048 | 3.0655 | 1
- | Main Office |  | 0 |  | 480 | 10 | 0 |  | 3840 | 0 | 0
- | Principal's Office | 173 | 11 |  | 396 | 9 | 9 | Univent | 3168 | 3.2765 | 1
- | Boys' Cafeteria |  | 0 | Yes | 1271 | 28 |  | Active Pure | 10168 | 0 | 0
- | Girls' Cafeteria |  | 0 | Yes | 943 | 21 |  | Active Pure | 7544 | 0 | 0
Annex | [8 empty] | 0 | 0 | 0
1 | Classroom |  | 0 | Yes | 684 | 15 | 15 |  | 5472 | 0 | 0
2 | Classroom |  | 0 | Yes | 1050 | 23 | 23 |  | 8400 | 0 | 0
3 | Classroom |  | 0 | Yes | 792 | 18 | 18 |  | 6336 | 0 | 0
4 | Classroom |  | 0 | Yes | 840 | 19 | 19 |  | 6720 | 0 | 0
5 | Classroom |  | 0 | Yes | 1104 | 25 | 25 |  | 8832 | 0 | 0
6 | Classroom |  | 0 | Yes | 700 | 15 | 15 |  | 5600 | 0 | 0
7 | Classroom |  | 0 | Yes | 1050 | 23 | 23 |  | 8400 | 0 | 0
8 | Classroom |  | 0 | Yes | 816 | 18 | 18 |  | 6528 | 0 | 0
9 | Classroom |  | 0 | Yes | 840 | 19 | 19 |  | 6720 | 0 | 0
10 | Classroom |  | 0 | Yes | 875 | 19 | 19 |  | 7000 | 0 | 0
- | Lobby |  | 0 | Yes | 180 | 4 | 4 |  | 1440 | 0 | 0
- | Counselor Office |  | 0 | Yes | 108 | 2 | 2 |  | 864 | 0 | 0
- | Asst Principal's Office |  | 0 | Yes | 89 | 2 | 2 |  | 712 | 0 | 0
- | Gym |  | 0 | Yes | 4328 | 98 | 98 | Hydroxyl Unit | 34624 | 0 | 0
- | Nurse Open area (Office D) and Early Lit |  | 0 | Yes | 547 | 12 | 12 |  | 4376 | 0 | 0
- | Conference room (medical waiting) |  | 0 | Yes | 141 | 3 | 3 |  | 1128 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | One Bright Ray- Elmwood | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 313 | 20 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
102 | Classroom | 189 | 12 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
103 | Classroom | 249 | 16 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
104 | Classroom | 215 | 14 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
105 | Classroom | 250 | 16 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
105 | Principal's Office | 58 | 3 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Dean of Students Office | 56 | 3 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Faculty Lounge | 69 | 4 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Foyer / Hallway | 147 | 9 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Open Space / Classroom | 475 | 31 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | SW Office | 48 | 3 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | Overbrook Educational Center Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | Retest | [6 empty] | 0 | 0 | 0
School: | Overbrook Education Center Annex | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Main Building | [8 empty] | 0 | 0 | 0
- | Boiler Room | 602 | 40 |  | 1496 | 34 | 34 | AHU | 11968 | 3.018 | 1
- | BE Office |  | 0 |  | 491 | 11 | 0 | AHU | 3928 | 0 | 0
- | Cafeteria | 233 | 15 | Yes | 1936 | 44 | 44 | AHU | 15488 | 0.90263 | 0
- | Corridor | 49 | 3 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | Kitchen | 53 | 3 |  | 440 | 10 | 3 | AHU | 3520 | 0.90341 | 0
- | Music Room | 204 | 13 |  | 748 | 17 | 13 | AHU | 5984 | 2.0455 | 1
- | Computer Room | 79 | 5 |  | 176 | 4 | 4 | AHU | 1408 | 3.3665 | 1
- | 1st Flr Entryway | 42 | 2 |  | 396 | 9 | 2 | AHU | 3168 | 0.79545 | 0
- | Exam Office | 32 | 2 |  | 176 | 4 | 2 | AHU | 1408 | 1.3636 | 1
- | Gym Office | 28 | 1 |  | 132 | 3 | 1 | AHU | 1056 | 1.5909 | 1
- | Gym /Stage | 1257 | 83 |  | 2332 | 53 | 53 | AHU | 18656 | 4.0427 | 2
- | Gym Lobby | 109 | 7 |  |  | 0 | 0 | AHU | 0 | 0 | 0
1st flr Hallway | Corridor | 20 | 1 |  |  | 0 | 0 | AHU | 0 | 0 | 0
1st flr Lobby | Main Lobby | 71 | 4 |  | 396 | 9 | 4 | AHU | 3168 | 1.3447 | 1
1st flr Main Office | Administration | 65 | 4 |  | 220 | 5 | 4 | AHU | 1760 | 2.2159 | 1
1st flr Nurse's Office | Medical | 38 | 2 |  | 264 | 6 | 2 | AHU | 2112 | 1.0795 | 1
1st flr Office | Principal | 49 | 3 |  | 220 | 5 | 3 | AHU | 1760 | 1.6705 | 1
1st flr Office | Copy Room | 19 | 1 |  | 88 | 2 | 1 | AHU | 704 | 1.6193 | 1
1st flr Office | Conference Room | 47 | 3 |  | 176 | 4 | 3 | AHU | 1408 | 2.0028 | 1
201 | Faculty Lounge | 161 | 10 |  | 220 | 5 | 5 | AHU | 1760 | 5.4886 | 2
204 | Office | 171 | 11 | Yes | 176 | 4 | 4 | RTU | 1408 | 7.2869 | 2
206 | Classroom | 370 | 24 |  | 660 | 15 | 15 | Univent | 5280 | 4.2045 | 2
207 | Classroom | 353 | 23 |  | 748 | 17 | 17 | Univent | 5984 | 3.5394 | 1
208 | Classroom | 446 | 29 |  | 748 | 17 | 17 | Univent | 5984 | 4.4719 | 2
209 | Classroom | 475 | 31 |  | 572 | 13 | 13 | Univent | 4576 | 6.2281 | 2
210 | Classroom | 425 | 28 |  | 660 | 15 | 15 | Univent | 5280 | 4.8295 | 2
211 | Classroom (Life Skills) | 536 | 35 |  | 748 | 17 | 17 | Univent | 5984 | 5.3743 | 2
2nd flr Library | Library | 344 | 22 |  | 1496 | 34 | 22 | AHU | 11968 | 1.7246 | 1
2nd flr Art | Classroom | 74 | 4 |  | 924 | 21 | 4 | AHU | 7392 | 0.60065 | 0
2nd Flr Hallway | Corridor | 197 | 13 |  |  | 0 | 0 | AAON unit | 0 | 0 | 0
2nd flr Science | Classroom | 84 | 5 |  | 836 | 19 | 5 | AHU | 6688 | 0.75359 | 0
301 | Classroom | 452 | 30 |  | 220 | 5 | 5 | RTU | 1760 | 15.4091 | 3
302 | Office | 284 | 18 |  | 176 | 4 | 4 | AHU | 1408 | 12.1023 | 3
304 | Classroom | 463 | 30 |  | 660 | 15 | 15 | Univent | 5280 | 5.2614 | 2
305 | Classroom | 517 | 34 |  | 748 | 17 | 17 | Univent | 5984 | 5.1838 | 2
306 | Classroom | 550 | 36 |  | 704 | 16 | 16 | Univent | 5632 | 5.8594 | 2
307 | Classroom | 596 | 39 |  | 572 | 13 | 13 | Univent | 4576 | 7.8147 | 2
308 | Classroom | 461 | 30 |  | 660 | 15 | 15 | Univent | 5280 | 5.2386 | 2
309 | Classroom | 1030 | 68 |  | 748 | 17 | 17 | Univent | 5984 | 10.3275 | 3
316 | Classroom |  | 0 | Yes | 695 | 15 | 15 |  | 5560 | 0 | 0
Annex Building | [8 empty] | 0 | 0 | 0
5 | Kitchen |  | 0 | Yes | 157 | 3 | 3 |  | 1256 | 0 | 0
6 | Office |  | 0 | Yes | 122 | 2 | 2 |  | 976 | 0 | 0
7 | Lobby |  | 0 |  | 890 | 20 | 0 |  | 7120 | 0 | 0
1 | Classroom |  | 0 | Yes | 1077 | 24 | 24 |  | 8616 | 0 | 0
2 | Classroom |  | 0 | Yes | 404 | 9 | 9 |  | 3232 | 0 | 0
25 | Classroom |  | 0 | Yes | 555 | 12 | 12 |  | 4440 | 0 | 0
24 | Office |  | 0 | Yes | 177 | 4 | 4 |  | 1416 | 0 | 0
22 | Classroom |  | 0 | Yes | 902 | 20 | 20 |  | 7216 | 0 | 0
21 | Classroom |  | 0 | Yes | 297 | 6 | 6 |  | 2376 | 0 | 0
31 | Classroom |  | 0 | Yes | 304 | 6 | 6 |  | 2432 | 0 | 0
32 | Classroom |  | 0 | Yes | 909 | 20 | 20 |  | 7272 | 0 | 0
34 | Classroom |  | 0 |  | 232 | 5 | 0 |  | 1856 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | Overbrook Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Classroom | 825 | 55 |  | 720 | 16 | 16 | House fan | 5760 | 8.5938 | 2
2 | Classroom | 798 | 53 |  | 720 | 16 | 16 | House fan | 5760 | 8.3125 | 2
3 | Classroom | 872 | 58 |  | 720 | 16 | 16 | House fan | 5760 | 9.0833 | 2
4 | Classroom | 838 | 55 |  | 528 | 12 | 12 | House fan | 4224 | 11.9034 | 3
5 | Classroom | 579 | 38 |  | 720 | 16 | 16 | House fan | 5760 | 6.0312 | 2
6 | Classroom | 499 | 33 |  | 720 | 16 | 16 | House fan | 5760 | 5.1979 | 2
7 | Classroom | 816 | 54 |  | 768 | 17 | 17 | House fan | 6144 | 7.9688 | 2
8 | Classroom | 614 | 40 |  | 768 | 17 | 17 | House fan | 6144 | 5.9961 | 2
9 | Classroom | 788 | 52 |  | 768 | 17 | 17 | House fan | 6144 | 7.6953 | 2
12 | Classroom | 522 | 34 |  | 720 | 16 | 16 | House fan | 5760 | 5.4375 | 2
13 | Classroom | 581 | 38 |  | 720 | 16 | 16 | House fan | 5760 | 6.0521 | 2
14 | Classroom | 472 | 31 |  | 720 | 16 | 16 | House fan | 5760 | 4.9167 | 2
15 | Classroom | 412 | 27 |  | 720 | 16 | 16 | House fan | 5760 | 4.2917 | 2
16 | Classroom | 505 | 33 |  | 720 | 16 | 16 | House fan | 5760 | 5.2604 | 2
17 | Classroom | 524 | 34 |  | 720 | 16 | 16 | House fan | 5760 | 5.4583 | 2
18 | Classroom | 508 | 33 |  | 768 | 17 | 17 | House fan | 6144 | 4.9609 | 2
19 | Classroom | 654 | 43 |  | 768 | 17 | 17 | House fan | 6144 | 6.3867 | 2
20 | Classroom | 498 | 33 |  | 768 | 17 | 17 | House fan | 6144 | 4.8633 | 2
- | Boys Bathroom | 826 | 55 |  | 736 | 16 | 16 | House fan | 5888 | 8.4171 | 2
- | Cafeteria | 1236 | 82 |  | 1560 | 35 | 35 | House fan | 12480 | 5.9423 | 2
- | Faculty bathroom | 40 | 2 |  | 64 | 1 | 1 | House fan | 512 | 4.6875 | 2
- | Girls Bathroom | 445 | 29 |  | 340 | 7 | 7 | House fan | 2720 | 9.8162 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | Overbrook High School | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
10 | - |  | 0 |  | 1041 | 23 | 0 |  | 8328 | 0 | 0
11 | - |  | 0 |  | 1450 | 32 | 0 |  | 11600 | 0 | 0
100 | Classroom |  | 0 |  | 1409 | 32 | 0 |  | 11272 | 0 | 0
100A | Classroom |  | 0 | Yes | 435 | 9 | 9 |  | 3480 | 0 | 0
100B | Classroom |  | 0 | Yes | 479 | 10 | 10 |  | 3832 | 0 | 0
100C | Classroom |  | 0 | Yes | 1407 | 31 | 31 |  | 11256 | 0 | 0
101 | Classroom |  | 0 | Yes | 832 | 18 | 18 |  | 6656 | 0 | 0
102 | Classroom |  | 0 |  | 742 | 16 | 0 |  | 5936 | 0 | 0
103 | Classroom |  | 0 |  | 692 | 15 | 0 |  | 5536 | 0 | 0
104 | Classroom |  | 0 |  | 649 | 14 | 0 |  | 5192 | 0 | 0
105 | Classroom |  | 0 |  | 990 | 22 | 0 |  | 7920 | 0 | 0
105A | Classroom |  | 0 |  | 228 | 5 | 0 |  | 1824 | 0 | 0
106A | Classroom |  | 0 |  | 535 | 12 | 0 |  | 4280 | 0 | 0
160B | Classroom |  | 0 |  | 534 | 12 | 0 |  | 4272 | 0 | 0
107 | Classroom |  | 0 |  | 703 | 15 | 0 |  | 5624 | 0 | 0
108 | Classroom |  | 0 |  | 677 | 15 | 0 |  | 5416 | 0 | 0
109A | Classroom |  | 0 |  | 551 | 12 | 0 |  | 4408 | 0 | 0
109B | Classroom |  | 0 |  | 507 | 11 | 0 |  | 4056 | 0 | 0
110 | Classroom |  | 0 |  | 931 | 21 | 0 |  | 7448 | 0 | 0
117 | Classroom |  | 0 |  | 515 | 11 | 0 |  | 4120 | 0 | 0
118 | Classroom |  | 0 |  | 556 | 12 | 0 |  | 4448 | 0 | 0
119 | Classroom |  | 0 |  | 753 | 17 | 0 |  | 6024 | 0 | 0
120 | Classroom |  | 0 |  | 1026 | 23 | 0 |  | 8208 | 0 | 0
121 | Classroom |  | 0 |  | 1048 | 23 | 0 |  | 8384 | 0 | 0
200 | Classroom |  | 0 |  | 304 | 6 | 0 |  | 2432 | 0 | 0
201 | Classroom |  | 0 |  | 496 | 11 | 0 |  | 3968 | 0 | 0
201 | Classroom |  | 0 |  | 490 | 11 | 0 |  | 3920 | 0 | 0
202 | Classroom |  | 0 |  | 486 | 11 | 0 |  | 3888 | 0 | 0
204 | Classroom |  | 0 |  | 881 | 20 | 0 |  | 7048 | 0 | 0
205 | Classroom |  | 0 |  | 733 | 16 | 0 |  | 5864 | 0 | 0
206 | Classroom |  | 0 |  | 1003 | 22 | 0 |  | 8024 | 0 | 0
207 | Classroom |  | 0 |  | 718 | 16 | 0 |  | 5744 | 0 | 0
209 | Classroom |  | 0 |  | 337 | 7 | 0 |  | 2696 | 0 | 0
210 | Classroom |  | 0 |  | 460 | 10 | 0 |  | 3680 | 0 | 0
211 | Classroom |  | 0 |  | 713 | 16 | 0 |  | 5704 | 0 | 0
212 | Classroom |  | 0 |  | 728 | 16 | 0 |  | 5824 | 0 | 0
213 | Classroom |  | 0 |  | 902 | 20 | 0 |  | 7216 | 0 | 0
214 | Classroom |  | 0 |  | 796 | 18 | 0 |  | 6368 | 0 | 0
215 | Classroom |  | 0 |  | 3413 | 77 | 0 |  | 27304 | 0 | 0
216 | Classroom |  | 0 |  | 850 | 19 | 0 |  | 6800 | 0 | 0
217 | Classroom |  | 0 |  | 712 | 16 | 0 |  | 5696 | 0 | 0
218 | Classroom |  | 0 |  | 700 | 15 | 0 |  | 5600 | 0 | 0
219 | Classroom |  | 0 |  | 719 | 16 | 0 |  | 5752 | 0 | 0
220 | Classroom |  | 0 |  | 359 | 8 | 0 |  | 2872 | 0 | 0
221 | Classroom |  | 0 |  | 877 | 19 | 0 |  | 7016 | 0 | 0
222 | Classroom |  | 0 |  | 877 | 19 | 0 |  | 7016 | 0 | 0
223 | Classroom |  | 0 |  | 729 | 16 | 0 |  | 5832 | 0 | 0
224 | Classroom |  | 0 |  | 731 | 16 | 0 |  | 5848 | 0 | 0
225 | Classroom |  | 0 |  | 694 | 15 | 0 |  | 5552 | 0 | 0
300 | Classroom |  | 0 |  | 747 | 16 | 0 |  | 5976 | 0 | 0
301 | Classroom |  | 0 |  | 724 | 16 | 0 |  | 5792 | 0 | 0
302 | Classroom |  | 0 |  | 737 | 16 | 0 |  | 5896 | 0 | 0
303 | Classroom |  | 0 |  | 907 | 20 | 0 |  | 7256 | 0 | 0
304 | Classroom |  | 0 |  | 941 | 21 | 0 |  | 7528 | 0 | 0
305 | Classroom |  | 0 |  | 724 | 16 | 0 |  | 5792 | 0 | 0
306 | Classroom |  | 0 |  | 738 | 16 | 0 |  | 5904 | 0 | 0
307 | Classroom |  | 0 |  | 739 | 16 | 0 |  | 5912 | 0 | 0
308 | Classroom |  | 0 |  | 834 | 18 | 0 |  | 6672 | 0 | 0
309 | Classroom |  | 0 |  | 733 | 16 | 0 |  | 5864 | 0 | 0
311 | Classroom |  | 0 |  | 721 | 16 | 0 |  | 5768 | 0 | 0
312 | Classroom |  | 0 |  | 704 | 16 | 0 |  | 5632 | 0 | 0
313 | Classroom |  | 0 |  | 491 | 11 | 0 |  | 3928 | 0 | 0
314 | Classroom |  | 0 |  | 669 | 15 | 0 |  | 5352 | 0 | 0
315 | Classroom |  | 0 |  | 673 | 15 | 0 |  | 5384 | 0 | 0
316 | Classroom |  | 0 | Yes | 762 | 17 | 17 |  | 6096 | 0 | 0
317 | Classroom |  | 0 | Yes | 917 | 20 | 20 |  | 7336 | 0 | 0
318 | Classroom |  | 0 |  | 669 | 15 | 0 |  | 5352 | 0 | 0
319 | Classroom |  | 0 |  | 681 | 15 | 0 |  | 5448 | 0 | 0
320 | Classroom |  | 0 |  | 724 | 16 | 0 |  | 5792 | 0 | 0
321 | Classroom |  | 0 |  | 712 | 16 | 0 |  | 5696 | 0 | 0
322 | Classroom |  | 0 |  | 499 | 11 | 0 |  | 3992 | 0 | 0
323 | Classroom |  | 0 |  | 437 | 9 | 0 |  | 3496 | 0 | 0
324 | Classroom |  | 0 |  | 801 | 18 | 0 |  | 6408 | 0 | 0
325 | Classroom |  | 0 |  | 936 | 21 | 0 |  | 7488 | 0 | 0
326 | Classroom |  | 0 |  | 690 | 15 | 0 |  | 5520 | 0 | 0
327 | Classroom |  | 0 |  | 191 | 4 | 0 |  | 1528 | 0 | 0
328 | Classroom |  | 0 |  | 683 | 15 | 0 |  | 5464 | 0 | 0
329 | Classroom |  | 0 |  | 711 | 16 | 0 |  | 5688 | 0 | 0
330 | Classroom |  | 0 |  | 690 | 15 | 0 |  | 5520 | 0 | 0
331 | Classroom |  | 0 |  | 204 | 4 | 0 |  | 1632 | 0 | 0
332 | Classroom |  | 0 |  | 687 | 15 | 0 |  | 5496 | 0 | 0
333 | Classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | 0 | 0
334 | Classroom |  | 0 |  | 817 | 18 | 0 |  | 6536 | 0 | 0
- | Main Office |  | 0 |  | 1057 | 24 | 0 |  | 8456 | 0 | 0
- | Principal Office |  | 0 |  | 562 | 12 | 0 |  | 4496 | 0 | 0
- | Auditorium Balcony |  | 0 |  | 1436 | 32 | 0 |  | 11488 | 0 | 0
- | Auditorium |  | 0 |  | 8711 | 197 | 0 |  | 69688 | 0 | 0
- | Teachers Lounge |  | 0 |  | 310 | 7 | 0 |  | 2480 | 0 | 0
- | Cafeteria A |  | 0 |  | 2778 | 63 | 0 |  | 22224 | 0 | 0
- | Cafeteria B |  | 0 |  | 4516 | 102 | 0 |  | 36128 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Academy @ Palumbo High School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
103 | Graphics Arts | 1248 | 83 |  | 1058 | 24 | 24 | Air Handling Unit | 8464 | 8.8469 | 2
104 | Fine Arts | 271 | 18 |  | 782 | 17 | 17 | Air Handling Unit | 6256 | 2.5991 | 1
118 | Conference Room | 1440 | 96 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 15.6522 | 3
129 | Main Office | 723 | 48 |  | 528 | 12 | 12 | Air Handling Unit | 4224 | 10.2699 | 3
132 | Mixed Choir | 736 | 49 |  | 966 | 21 | 21 | Air Handling Unit | 7728 | 5.7143 | 2
134 | Music Theory | 1170 | 78 |  | 946 | 21 | 21 | Air Handling Unit | 7568 | 9.2759 | 2
135 | Intro to Music | 1709 | 113 |  | 968 | 22 | 22 | Air Handling Unit | 7744 | 13.2412 | 3
136 | Music Equipment Storage | 609 | 40 |  | 396 | 9 | 9 | Air Handling Unit | 3168 | 11.5341 | 3
204 | Creative Writing | 843 | 56 |  | 660 | 15 | 15 | Air Handling Unit | 5280 | 9.5795 | 2
205 | Computer Lab | 653 | 43 |  | 768 | 17 | 17 | Air Handling Unit | 6144 | 6.377 | 2
206 | Environment Club | 713 | 47 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 7.75 | 2
207 | Language & Journalism | 1069 | 71 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 11.6196 | 3
212 | Visitor's Locker Room | 615 | 41 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 6.4062 | 2
221 | History | 618 | 41 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 6.7174 | 2
223 | Literature | 750 | 50 |  | 1104 | 25 | 25 | Air Handling Unit | 8832 | 5.0951 | 2
224 | English / History | 113 | 7 |  | 660 | 15 | 7 | Air Handling Unit | 5280 | 1.2841 | 1
231 | Office | 595 | 39 |  | 484 | 11 | 11 | Air Handling Unit | 3872 | 9.22 | 2
301 | Forensics / Algebra 2 | 604 | 40 |  | 528 | 12 | 12 | Air Handling Unit | 4224 | 8.5795 | 2
302 | Dean's Office | 1510 | 100 |  | 440 | 10 | 10 | Air Handling Unit | 3520 | 25.7386 | 4
305 | History | 257 | 17 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 2.7935 | 1
306 | Spanish | 554 | 36 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 6.0217 | 2
307 | American History | 282 | 18 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 3.0652 | 1
312 | Cardio & Weight Lifting | 615 | 41 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 6.4062 | 2
321 | Spanish | 666 | 44 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 7.2391 | 2
321 | History | 532 | 35 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 5.7826 | 2
322 | History | 1582 | 105 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 17.1957 | 3
323 | Spanish | 567 | 37 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 6.163 | 2
332 | Black History | 84 | 5 |  | 638 | 14 | 5 | Air Handling Unit | 5104 | 0.98746 | 0
333 | History | 1066 | 71 |  | 792 | 18 | 18 | Air Handling Unit | 6336 | 10.0947 | 3
334 | Psychologist | 0 | 0 |  | 567 | 12 | 0 | Air Handling Unit | 4536 | 0 | 0
336 | Spanish | 0 | 0 |  | 1058 | 24 | 0 | Air Handling Unit | 8464 | 0 | 0
403 | Physics Lab | 322 | 21 |  | 1056 | 24 | 21 | Air Handling Unit | 8448 | 2.2869 | 1
407 | Biology Lab | 587 | 39 |  | 1440 | 32 | 32 | Air Handling Unit | 11520 | 3.0573 | 1
411 | Chemistry | 651 | 43 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 6.7812 | 2
412 | Unknown | 668 | 44 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 6.9583 | 2
421 | Spanish | 117 | 7 |  | 690 | 15 | 7 | Air Handling Unit | 5520 | 1.2717 | 1
422 | Chinese | 965 | 64 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 10.4891 | 3
423 | English 1 | 628 | 41 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 6.8261 | 2
432 | Literature | 484 | 32 |  | 760 | 17 | 17 | Air Handling Unit | 6080 | 4.7763 | 2
433 | History | 142 | 9 |  | 760 | 17 | 9 | Air Handling Unit | 6080 | 1.4013 | 1
436 | Science | 769 | 51 |  | 1058 | 24 | 24 | Air Handling Unit | 8464 | 5.4513 | 2
437 | Geometry | 723 | 48 |  | 552 | 12 | 12 | Air Handling Unit | 4416 | 9.8234 | 2
501 | Algebra 2 | 677 | 45 |  | 768 | 17 | 17 | Air Handling Unit | 6144 | 6.6113 | 2
502 | Forensics / Algebra | 415 | 27 |  | 768 | 17 | 17 | Air Handling Unit | 6144 | 4.0527 | 2
503 | Statistics | 483 | 32 |  | 768 | 17 | 17 | Air Handling Unit | 6144 | 4.7168 | 2
504 | Algebra | 190 | 12 |  | 768 | 17 | 12 | Air Handling Unit | 6144 | 1.8555 | 1
506 | Algebra | 707 | 47 |  | 768 | 17 | 17 | Air Handling Unit | 6144 | 6.9043 | 2
507 | Computer Science | 420 | 28 |  | 768 | 17 | 17 | Air Handling Unit | 6144 | 4.1016 | 2
521 | Algebra | 190 | 12 |  | 690 | 15 | 12 | Air Handling Unit | 5520 | 2.0652 | 1
522 | Math | 2026 | 135 |  | 968 | 22 | 22 | Air Handling Unit | 7744 | 15.6973 | 3
524 | Algebra | 1222 | 81 |  | 770 | 17 | 17 | Air Handling Unit | 6160 | 11.9026 | 3
529 | Film | 493 | 32 |  | 660 | 15 | 15 | Air Handling Unit | 5280 | 5.6023 | 2
201A | Exercise | 323 | 21 |  | 23 | 0 | 0 | Air Handling Unit | 184 | 105.3261 | 5
201B | Exercise | 627 | 41 |  | 1771 | 40 | 40 | Air Handling Unit | 14168 | 2.6553 | 1
304A | Computer Lab | 571 | 38 |  | 500 | 11 | 11 | Air Handling Unit | 4000 | 8.565 | 2
304B | Computer Lab | 637 | 42 |  | 446 | 10 | 10 | Air Handling Unit | 3568 | 10.7119 | 3
329A | Admin. Office | 605 | 40 |  | 660 | 15 | 15 | Air Handling Unit | 5280 | 6.875 | 2
329B | Admin. Office | 196 | 13 |  | 660 | 15 | 13 | Air Handling Unit | 5280 | 2.2273 | 1
337A | Study Skills / AS | 860 | 57 |  | 337 | 7 | 7 | Air Handling Unit | 2696 | 19.1395 | 3
337B | Study Skills / AS | 975 | 65 |  | 552 | 12 | 12 | Air Handling Unit | 4416 | 13.2473 | 3
404A | Chemistry Lab | 230 | 15 |  | 720 | 16 | 15 | Air Handling Unit | 5760 | 2.3958 | 1
404B | Chemistry Lab | 2087 | 139 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 21.7396 | 3
409A | Office | 43 | 2 |  | 280 | 6 | 2 | Air Handling Unit | 2240 | 1.1518 | 1
409B | Office | 123 | 8 |  | 280 | 6 | 6 | Air Handling Unit | 2240 | 3.2946 | 1
429A | Robotics | 574 | 38 |  | 1320 | 30 | 30 | Air Handling Unit | 10560 | 3.2614 | 1
429B | Robotics | 652 | 43 |  | 429 | 9 | 9 | Air Handling Unit | 3432 | 11.3986 | 3
434A | Algebra | 541 | 36 |  | 434 | 9 | 9 | Air Handling Unit | 3472 | 9.3491 | 2
434B | Algebra | 276 | 18 |  | 1188 | 27 | 18 | Air Handling Unit | 9504 | 1.7424 | 1
B14 | Storage | 594 | 39 |  | 374 | 8 | 8 | Air Handling Unit | 2992 | 11.9118 | 3
B15 | Storage | 237 | 15 |  | 384 | 8 | 8 | Air Handling Unit | 3072 | 4.6289 | 2
B16 | Storage | 37 | 2 |  | 90 | 2 | 2 | Air Handling Unit | 720 | 3.0833 | 1
B17 | Storage | 326 | 21 |  | 364 | 8 | 8 | Air Handling Unit | 2912 | 6.717 | 2
B19 | Storage | 723 | 48 |  | 1013 | 23 | 23 | Air Handling Unit | 8104 | 5.3529 | 2
B24-A | Storage | 723 | 48 |  | 1013 | 23 | 23 | Air Handling Unit | 8104 | 5.3529 | 2
B24-B | Storage | 461 | 30 |  | 1013 | 23 | 23 | Air Handling Unit | 8104 | 3.4131 | 1
- | Auditorium | 16042 | 1069 |  | 12420 | 282 | 282 | Air Handling Unit | 99360 | 9.6872 | 2
- | Gyms and Cafeteria | 7343 | 489 |  | 21078 | 479 | 479 | Air Handling Unit | 168624 | 2.6128 | 1
- | Home Locker Room | 417 | 27 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 4.3438 | 2
- | Locker Room | 417 | 27 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 4.3438 | 2
- | Main Library | 1095 | 73 |  | 4608 | 104 | 73 | Air Handling Unit | 36864 | 1.7822 | 1
- | Library A | 1256 | 83 |  | 238 | 5 | 5 | Air Handling Unit | 1904 | 39.5798 | 4
- | Library B | 1078 | 71 |  | 238 | 5 | 5 | Air Handling Unit | 1904 | 33.9706 | 4
- | Library Storage | 917 | 61 |  | 288 | 6 | 6 | Air Handling Unit | 2304 | 23.8802 | 3
- | Men's Room | 50 | 3 |  | 252 | 5 | 3 | Air Handling Unit | 2016 | 1.4881 | 1
- | Ladies Room | 46 | 3 |  | 252 | 5 | 3 | Air Handling Unit | 2016 | 1.369 | 1
- | Safe Room | 1158 | 77 |  | 675 | 15 | 15 | Air Handling Unit | 5400 | 12.8667 | 3
B18 | Storage | 477 | 31 |  | 723 | 16 | 16 |  | 5784 | 4.9481 | 2
B20 | Storage | 461 | 30 |  | 1013 | 23 | 23 |  | 8104 | 3.4131 | 1
B21 | Storage | 736 | 49 |  | 966 | 21 | 21 |  | 7728 | 5.7143 | 2
B22 | Storage | 723 | 48 |  | 528 | 12 | 12 |  | 4224 | 10.2699 | 3
B23 | Storage | 323 | 21 |  | 23 | 0 | 0 |  | 184 | 105.3261 | 5
B24 | Storage | 627 | 41 |  | 1771 | 40 | 40 |  | 14168 | 2.6553 | 1
B25 | Storage | 843 | 56 |  | 660 | 15 | 15 |  | 5280 | 9.5795 | 2
B26 | Storage | 113 | 7 |  | 660 | 15 | 7 |  | 5280 | 1.2841 | 1
B27 | Storage | 595 | 39 |  | 484 | 11 | 11 |  | 3872 | 9.22 | 2
B28 | Storage | 604 | 40 |  | 528 | 12 | 12 |  | 4224 | 8.5795 | 2
B29 | Storage | 1510 | 100 |  | 440 | 10 | 10 |  | 3520 | 25.7386 | 4
B30 | Storage | 571 | 38 |  | 500 | 11 | 11 |  | 4000 | 8.565 | 2
B31 | Storage | 637 | 42 |  | 446 | 10 | 10 |  | 3568 | 10.7119 | 3
B32 | Storage | 666 | 44 |  | 690 | 15 | 15 |  | 5520 | 7.2391 | 2
B33 | Storage | 567 | 37 |  | 690 | 15 | 15 |  | 5520 | 6.163 | 2
B34 | Storage | 605 | 40 |  | 660 | 15 | 15 |  | 5280 | 6.875 | 2
B35 | Storage | 196 | 13 |  | 660 | 15 | 13 |  | 5280 | 2.2273 | 1
B36 | Storage | 84 | 5 |  | 638 | 14 | 5 |  | 5104 | 0.98746 | 0
B37 | Storage | 1066 | 71 |  | 792 | 18 | 18 |  | 6336 | 10.0947 | 3
B38 | Storage | 0 | 0 |  | 567 | 12 | 0 |  | 4536 | 0 | 0
B39 | Storage | 0 | 0 |  | 1058 | 24 | 0 |  | 8464 | 0 | 0
B40 | Storage | 860 | 57 |  | 337 | 7 | 7 |  | 2696 | 19.1395 | 3
B41 | Storage | 975 | 65 |  | 552 | 12 | 12 |  | 4416 | 13.2473 | 3
B42 | Storage | 322 | 21 |  | 1056 | 24 | 21 |  | 8448 | 2.2869 | 1
B43 | Storage | 230 | 15 |  | 720 | 16 | 15 |  | 5760 | 2.3958 | 1
B44 | Storage | 2087 | 139 |  | 720 | 16 | 16 |  | 5760 | 21.7396 | 3
B45 | Storage | 628 | 41 |  | 690 | 15 | 15 |  | 5520 | 6.8261 | 2
B46 | Storage | 574 | 38 |  | 1320 | 30 | 30 |  | 10560 | 3.2614 | 1
B47 | Storage | 652 | 43 |  | 429 | 9 | 9 |  | 3432 | 11.3986 | 3
B48 | Storage | 484 | 32 |  | 760 | 17 | 17 |  | 6080 | 4.7763 | 2
B49 | Storage | 142 | 9 |  | 760 | 17 | 9 |  | 6080 | 1.4013 | 1
B50 | Storage | 541 | 36 |  | 434 | 9 | 9 |  | 3472 | 9.3491 | 2
B51 | Storage | 276 | 18 |  | 1188 | 27 | 18 |  | 9504 | 1.7424 | 1
B52 | Storage | 769 | 51 |  | 1058 | 24 | 24 |  | 8464 | 5.4513 | 2
B53 | Storage | 723 | 48 |  | 552 | 12 | 12 |  | 4416 | 9.8234 | 2
B54 | Storage | 677 | 45 |  | 768 | 17 | 17 |  | 6144 | 6.6113 | 2
B55 | Storage | 415 | 27 |  | 768 | 17 | 17 |  | 6144 | 4.0527 | 2
B56 | Storage | 483 | 32 |  | 768 | 17 | 17 |  | 6144 | 4.7168 | 2
B57 | Storage | 1222 | 81 |  | 770 | 17 | 17 |  | 6160 | 11.9026 | 3
B58 | Storage | 493 | 32 |  | 660 | 15 | 15 |  | 5280 | 5.6023 | 2
B59 | Storage | 1158 | 77 |  |  | 0 | 0 |  | 0 | 0 | 0
B60 | Storage | 26166 | 1744 |  |  | 0 | 0 |  | 0 | 0 | 0
B61 | Storage | 594 | 39 |  | 374 | 8 | 8 |  | 2992 | 11.9118 | 3
B62 | Storage | 237 | 15 |  | 384 | 8 | 8 |  | 3072 | 4.6289 | 2
B63 | Storage | 37 | 2 |  | 90 | 2 | 2 |  | 720 | 3.0833 | 1
B64 | Storage | 1170 | 78 |  | 946 | 21 | 21 |  | 7568 | 9.2759 | 2
B65 | Storage | 1709 | 113 |  | 968 | 22 | 22 |  | 7744 | 13.2412 | 3
B66 | Storage | 609 | 40 |  | 396 | 9 | 9 |  | 3168 | 11.5341 | 3
B67 | Storage | 1248 | 83 |  | 1058 | 24 | 24 |  | 8464 | 8.8469 | 2
B68 | Storage | 271 | 18 |  | 782 | 17 | 17 |  | 6256 | 2.5991 | 1
B69 | Storage | 1440 | 96 |  | 690 | 15 | 15 |  | 5520 | 15.6522 | 3
B70 | Storage | 653 | 43 |  | 768 | 17 | 17 |  | 6144 | 6.377 | 2
B71 | Storage | 713 | 47 |  | 690 | 15 | 15 |  | 5520 | 7.75 | 2
B72 | Storage | 1069 | 71 |  | 690 | 15 | 15 |  | 5520 | 11.6196 | 3
B73 | Storage | 615 | 41 |  | 720 | 16 | 16 |  | 5760 | 6.4062 | 2
B74 | Storage | 417 | 27 |  | 720 | 16 | 16 |  | 5760 | 4.3438 | 2
B75 | Storage | 618 | 41 |  | 690 | 15 | 15 |  | 5520 | 6.7174 | 2
B76 | Storage | 750 | 50 |  | 1104 | 25 | 25 |  | 8832 | 5.0951 | 2
B77 | Storage | 257 | 17 |  | 690 | 15 | 15 |  | 5520 | 2.7935 | 1
B78 | Storage | 554 | 36 |  | 690 | 15 | 15 |  | 5520 | 6.0217 | 2
B79 | Storage | 282 | 18 |  | 690 | 15 | 15 |  | 5520 | 3.0652 | 1
B80 | Storage | 615 | 41 |  | 720 | 16 | 16 |  | 5760 | 6.4062 | 2
B81 | Storage | 532 | 35 |  | 690 | 15 | 15 |  | 5520 | 5.7826 | 2
B82 | Storage | 1582 | 105 |  | 690 | 15 | 15 |  | 5520 | 17.1957 | 3
B83 | Storage | 917 | 61 |  | N/A | 0 | 0 |  | #VALUE! | #VALUE! | #VALUE!
B84 | Storage | 1256 | 83 |  | N/A | 0 | 0 |  | #VALUE! | #VALUE! | #VALUE!
B85 | Storage | 1078 | 71 |  | N/A | 0 | 0 |  | #VALUE! | #VALUE! | #VALUE!
B86 | Storage | 587 | 39 |  | 1440 | 32 | 32 |  | 11520 | 3.0573 | 1
B87 | Storage | 651 | 43 |  | 720 | 16 | 16 |  | 5760 | 6.7812 | 2
B88 | Storage | 668 | 44 |  | 720 | 16 | 16 |  | 5760 | 6.9583 | 2
B89 | Storage | 117 | 7 |  | 690 | 15 | 7 |  | 5520 | 1.2717 | 1
B90 | Storage | 965 | 64 |  | 690 | 15 | 15 |  | 5520 | 10.4891 | 3
B91 | Storage | 417 | 27 |  |  | 0 | 0 |  | 0 | 0 | 0
B92 | Storage | 190 | 12 |  | 768 | 17 | 12 |  | 6144 | 1.8555 | 1
B93 | Storage | 707 | 47 |  | 768 | 17 | 17 |  | 6144 | 6.9043 | 2
B94 | Storage | 420 | 28 |  | 768 | 17 | 17 |  | 6144 | 4.1016 | 2
B95 | Storage | 190 | 12 |  | 690 | 15 | 12 |  | 5520 | 2.0652 | 1
B96 | Storage | 2026 | 135 |  | 968 | 22 | 22 |  | 7744 | 15.6973 | 3
B97 | Storage | 16042 | 1069 |  | 12420 | 282 | 282 |  | 99360 | 9.6872 | 2
B98 | Storage | 7343 | 489 |  | 21078 | 479 | 479 |  | 168624 | 2.6128 | 1
B99 | Storage | 1095 | 73 |  | 4608 | 104 | 73 |  | 36864 | 1.7822 | 1
B100 | Storage | 43 | 2 |  | 280 | 6 | 2 |  | 2240 | 1.1518 | 1
B101 | Storage | 123 | 8 |  | 280 | 6 | 6 |  | 2240 | 3.2946 | 1
B102 | Storage | 50 | 3 |  | 252 | 5 | 3 |  | 2016 | 1.4881 | 1
B103 | Storage | 46 | 3 |  | 252 | 5 | 3 |  | 2016 | 1.369 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | Parkway Northwest High School former Hill, JE (Hill-Freedman) | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | Goldner Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
108 | Room | 676 | 45 |  | 676 | 15 | 15 | Univent | 5408 | 7.5 | 2
109 | Room | 333 | 22 |  | 714 | 16 | 16 | Fan Coil Unit | 5712 | 3.4979 | 1
110 | Room | 168 | 11 |  | 1015 | 23 | 11 | Univent | 8120 | 1.2414 | 1
130 | Room | 564 | 37 |  | 630 | 14 | 14 | Univent | 5040 | 6.7143 | 2
131 | Room | 476 | 31 |  | 580 | 13 | 13 | Univent | 4640 | 6.1552 | 2
132 | Room | 528 | 35 |  | 580 | 13 | 13 | Univent | 4640 | 6.8276 | 2
133 | Room | 452 | 30 |  | 469 | 10 | 10 | Univent | 3752 | 7.2281 | 2
134 | Room | 496 | 33 |  | 1015 | 23 | 23 | Univent | 8120 | 3.665 | 1
135 | Room | 304 | 20 |  | 812 | 18 | 18 | Univent | 6496 | 2.8079 | 1
136 | Room | 424 | 28 |  | 424 | 9 | 9 | Univent | 3392 | 7.5 | 2
203 | Room | 409 | 27 |  | 600 | 13 | 13 | Univent | 4800 | 5.1125 | 2
204 | Room | 363 | 24 |  | 667 | 15 | 15 | Univent | 5336 | 4.0817 | 2
205 | Room | 376 | 25 |  | 720 | 16 | 16 | Univent | 5760 | 3.9167 | 1
206 | Room | 350 | 23 |  | 810 | 18 | 18 | Univent | 6480 | 3.2407 | 1
207 | Room | 371 | 24 |  | 783 | 17 | 17 | Univent | 6264 | 3.5536 | 1
210 | Room | 482 | 32 |  | 1116 | 25 | 25 | Fan Coil Unit | 8928 | 3.2392 | 1
211 | Room | 329 | 21 |  | 957 | 21 | 21 | Univent | 7656 | 2.5784 | 1
221 | Room | 300 | 20 |  | 580 | 13 | 13 | Univent | 4640 | 3.8793 | 1
222 | Room | 75 | 5 |  | 580 | 13 | 5 | Univent | 4640 | 0.96983 | 0
223 | Room | 523 | 34 |  | 580 | 13 | 13 | Univent | 4640 | 6.7629 | 2
224 | Room | 717 | 47 |  | 580 | 13 | 13 | Univent | 4640 | 9.2716 | 2
225 | Room | 250 | 16 |  | 580 | 13 | 13 | Univent | 4640 | 3.2328 | 1
226 | Room | 163 | 10 |  | 580 | 13 | 10 | Univent | 4640 | 2.1078 | 1
- | Auditurium | 912 | 60 |  | 1050 | 23 | 23 | Univent | 8400 | 6.5143 | 2
- | Gym | 969 | 64 |  | 2460 | 55 | 55 | Univent | 19680 | 2.9543 | 1
- | Main Office | 0 | 0 |  | 399 | 9 | 0 |  | 3192 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | #VALUE! | #VALUE! | #VALUE!
School: | John M. Patterson Elementary School | House fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine Brothers Retest | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Classroom |  | 0 | Yes | 648 | 14 | 14 | House Fan | 5184 | 0 | 0
2 | Classroom |  | 0 | Yes | 648 | 14 | 14 | House Fan | 5184 | 0 | 0
3 | Classroom |  | 0 | Yes | 648 | 14 | 14 | House Fan | 5184 | 0 | 0
100 | Office | 0 | 0 |  | 143 | 3 | 0 | House Fan | 1144 | 0 | 0
101 | Classroom | 659 | 43 |  | 704 | 16 | 16 | House Fan | 5632 | 7.0206 | 2
102 | Classroom | 568 | 37 |  | 616 | 14 | 14 | House Fan | 4928 | 6.9156 | 2
103 | Classroom | 403 | 26 |  | 616 | 14 | 14 | House Fan | 4928 | 4.9067 | 2
104 | Classroom | 663 | 44 |  | 616 | 14 | 14 | House Fan | 4928 | 8.0722 | 2
105 | Classroom | 518 | 34 |  | 616 | 14 | 14 | House Fan | 4928 | 6.3068 | 2
106 | Classroom | 639 | 42 |  | 616 | 14 | 14 | House Fan | 4928 | 7.78 | 2
107 | Classroom | 698 | 46 |  | 616 | 14 | 14 | House Fan | 4928 | 8.4984 | 2
108 | Classroom | 656 | 43 |  | 704 | 16 | 16 | House Fan | 5632 | 6.9886 | 2
109 | Classroom | 658 | 43 |  | 704 | 16 | 16 | House Fan | 5632 | 7.0099 | 2
110 | Classroom | 722 | 48 |  | 704 | 16 | 16 | House Fan | 5632 | 7.6918 | 2
200 | Classroom | 0 | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
200A | Counselor | 0 | 0 |  | 240 | 5 | 0 | House Fan | 1920 | 0 | 0
201 | Classroom | 373 | 24 |  | 704 | 16 | 16 | House Fan | 5632 | 3.9737 | 1
202 | Classroom | 578 | 38 |  | 703 | 15 | 15 | House Fan | 5624 | 6.1664 | 2
203 | Classroom | 504 | 33 |  | 616 | 14 | 14 | House Fan | 4928 | 6.1364 | 2
204 | Classroom | 474 | 31 |  | 616 | 14 | 14 | House Fan | 4928 | 5.7711 | 2
205 | Classroom | 421 | 28 |  | 616 | 14 | 14 | House Fan | 4928 | 5.1258 | 2
206 | Classroom | 541 | 36 |  | 616 | 14 | 14 | House Fan | 4928 | 6.5869 | 2
207 | Classroom | 637 | 42 |  | 616 | 14 | 14 | House Fan | 4928 | 7.7557 | 2
208 | Classroom | 209 | 13 |  | 704 | 16 | 13 | House Fan | 5632 | 2.2266 | 1
209 | Classroom | 585 | 39 |  | 704 | 16 | 16 | House Fan | 5632 | 6.2322 | 2
210 | Classroom | 583 | 38 |  | 410 | 9 | 9 | House Fan | 3280 | 10.6646 | 3
300 | Classroom | 394 | 26 |  | 704 | 16 | 16 | House Fan | 5632 | 4.1974 | 2
301 | Classroom | 530 | 35 |  | 704 | 16 | 16 | House Fan | 5632 | 5.6463 | 2
302 | Classroom | 511 | 34 |  | 704 | 16 | 16 | House Fan | 5632 | 5.4439 | 2
303 | Classroom | 576 | 38 |  | 704 | 16 | 16 | House Fan | 5632 | 6.1364 | 2
304 | Classroom | 359 | 23 |  | 616 | 14 | 14 | House Fan | 4928 | 4.3709 | 2
305 | Classroom | 561 | 37 |  | 616 | 14 | 14 | House Fan | 4928 | 6.8304 | 2
306 | Classroom | 604 | 40 |  | 616 | 14 | 14 | House Fan | 4928 | 7.3539 | 2
307 | Classroom | 103 | 6 |  | 616 | 14 | 6 | House Fan | 4928 | 1.2541 | 1
308 | Classroom | 418 | 27 |  | 704 | 16 | 16 | House Fan | 5632 | 4.4531 | 2
309 | Classroom | 101 | 6 |  | 704 | 16 | 6 | House Fan | 5632 | 1.076 | 1
310 | Classroom | 429 | 28 |  | 704 | 16 | 16 | House Fan | 5632 | 4.5703 | 2
- | Auditorium | 5125 | 341 |  | 2880 | 65 | 65 | House Fan | 23040 | 13.3464 | 3
- | Admin Office | 0 | 0 | Yes | 88 | 2 | 2 | House Fan | 704 | 0 | 0
- | Principal Office |  | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | 0 | 0
- | Book Room Storage | 0 | 0 |  | 230 | 5 | 0 | House Fan | 1840 | 0 | 0
- | Boiler Rm. | 22650 | 1510 |  | 1440 | 32 | 32 | House Fan | 11520 | 117.9688 | 5
- | Small Cafeteria | 689 | 45 |  | 1232 | 28 | 28 | House Fan | 9856 | 4.1944 | 2
- | Kitchen | 212 | 14 |  | 200 | 4 | 4 | House Fan | 1600 | 7.95 | 2
- | Gym/Cafeteria | 0 | 0 | Yes | 3762 | 85 | 85 | House Fan | 30096 | 0 | 0
- | Storage | 574 | 38 |  |  | 0 | 0 | House Fan | 0 | 0 | 0
- | Music | 375 | 25 |  | 560 | 12 | 12 | House Fan | 4480 | 5.0223 | 2
- | Nurse's Room | 0 | 0 | Yes | 336 | 7 | 7 | House Fan | 2688 | 0 | 0
- | Teacher's Lounge | 0 | 0 | Yes | 410 | 9 | 9 | House Fan | 3280 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-20 | [7 empty] | 0 | 0 | 0
School: | Penn Alexander Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Part 2 | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B24 | Classroom | 37 | 2 |  | 130 | 2 | 2 | Air Handling Unit | 1040 | 2.1346 | 1
B26 | Classroom | 120 | 8 |  | 216 | 4 | 4 | Air Handling Unit | 1728 | 4.1667 | 2
B28 | Classroom | 483 | 32 |  | 722 | 16 | 16 | Air Handling Unit | 5776 | 5.0173 | 2
106 | Classroom | 1065 | 71 |  | 806 | 18 | 18 | Air Handling Unit | 6448 | 9.91 | 2
108 | Classroom | 310 | 20 |  | 842 | 19 | 19 | Univent | 6736 | 2.7613 | 1
109 | Classroom | 311 | 20 |  | 759 | 17 | 17 | Univent | 6072 | 3.0731 | 1
110 | Classroom | 305 | 20 |  | 693 | 15 | 15 | Univent | 5544 | 3.3009 | 1
113 | Classroom | 220 | 14 |  | 222 | 5 | 5 | Air Handling Unit | 1776 | 7.4324 | 2
117 | Classroom | 285 | 19 |  | 741 | 16 | 16 | Univent | 5928 | 2.8846 | 1
118 | Classroom | 329 | 21 |  | 759 | 17 | 17 | Univent | 6072 | 3.251 | 1
119 | Classroom | 315 | 21 |  | 683 | 15 | 15 | Univent | 5464 | 3.459 | 1
123 | Classroom | 0 | 0 |  | 150 | 3 | 0 | Air Handling Unit | 1200 | 0 | 0
125 | Classroom | 73 | 4 |  | 209 | 4 | 4 | Air Handling Unit | 1672 | 2.6196 | 1
126 | Classroom | 13 | 0 |  | 99 | 2 | 0 | Air Handling Unit | 792 | 0.98485 | 0
127 | Classroom | 14 | 0 |  | 99 | 2 | 0 | Air Handling Unit | 792 | 1.0606 | 1
128 | Classroom | 10 | 0 | Yes | 99 | 2 | 2 | Air Handling Unit | 792 | 0.75758 | 0
129 | Classroom | 84 | 5 | Yes | 291 | 6 | 6 | Air Handling Unit | 2328 | 2.1649 | 1
131 | Classroom | 302 | 20 |  | 694 | 15 | 15 | Univent | 5552 | 3.2637 | 1
133 | Classroom | 0 | 0 | Yes | 644 | 14 | 14 | Univent | 5152 | 0 | 0
134 | Classroom | 330 | 22 |  | 683 | 15 | 15 | Univent | 5464 | 3.6237 | 1
201 | Classroom | 491 | 32 |  | 875 | 19 | 19 | Air Handling Unit | 7000 | 4.2086 | 2
202 | Classroom | 74 | 4 |  | 324 | 7 | 4 | Air Handling Unit | 2592 | 1.713 | 1
208 | Classroom | 0 | 0 | Yes | 842 | 19 | 19 | Univent | 6736 | 0 | 0
209 | Classroom | 0 | 0 | Yes | 759 | 17 | 17 | Univent | 6072 | 0 | 0
210 | Classroom | 0 | 0 | Yes | 693 | 15 | 15 | Univent | 5544 | 0 | 0
213 | Classroom | 75 | 5 |  | 222 | 5 | 5 | Air Handling Unit | 1776 | 2.5338 | 1
217 | Classroom | 0 | 0 | Yes | 741 | 16 | 16 | Univent | 5928 | 0 | 0
218 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | Univent | 5824 | 0 | 0
219 | Classroom | 0 | 0 | Yes | 683 | 15 | 15 | Univent | 5464 | 0 | 0
220 | Classroom | 241 | 16 |  | 224 | 5 | 5 | Air Handling Unit | 1792 | 8.0692 | 2
221 | Classroom | 0 | 0 | Yes | 96 | 2 | 2 | Air Handling Unit | 768 | 0 | 0
222 | Classroom | 0 | 0 |  | 169 | 3 | 0 | Air Handling Unit | 1352 | 0 | 0
225 | Classroom | 0 | 0 | Yes | 209 | 4 | 4 | Air Handling Unit | 1672 | 0 | 0
227 | Classroom | 0 | 0 |  | 99 | 2 | 0 | Air Handling Unit | 792 | 0 | 0
228 | Classroom | 0 | 0 |  | 154 | 3 | 0 | Air Handling Unit | 1232 | 0 | 0
229 | Classroom | 0 | 0 |  | 108 | 2 | 0 | Air Handling Unit | 864 | 0 | 0
230 | Classroom | 318 | 21 |  | 736 | 16 | 16 | Univent | 5888 | 3.2405 | 1
231 | Classroom | 301 | 20 |  | 840 | 19 | 19 | Univent | 6720 | 2.6875 | 1
233 | Classroom | 266 | 17 |  | 739 | 16 | 16 | Univent | 5912 | 2.6996 | 1
234 | Classroom | 328 | 21 |  | 671 | 15 | 15 | Univent | 5368 | 3.6662 | 1
301 | Classroom | 1176 | 78 |  | 1005 | 22 | 22 | Air Handling Unit | 8040 | 8.7761 | 2
302 | Classroom | 0 | 0 |  | 324 | 7 | 0 | Univent | 2592 | 0 | 0
308 | Classroom | 0 | 0 | Yes | 842 | 19 | 19 | Univent | 6736 | 0 | 0
309 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | Univent | 5704 | 0 | 0
310 | Classroom | 0 | 0 | Yes | 693 | 15 | 15 | Univent | 5544 | 0 | 0
317 | Classroom | 0 | 0 | Yes | 741 | 16 | 16 | Univent | 5928 | 0 | 0
318 | Classroom | 0 | 0 | Yes | 759 | 17 | 17 | Univent | 6072 | 0 | 0
319 | Classroom | 0 | 0 | Yes | 683 | 15 | 15 | Univent | 5464 | 0 | 0
320 | Classroom | 0 | 0 |  | 320 | 7 | 0 | Air Handling Unit | 2560 | 0 | 0
- | Cafeteria | 7801 | 520 |  | 3766 | 85 | 85 | Air Handling Unit | 30128 | 15.5357 | 3
- | GYM | 1362 | 90 |  | 4271 | 97 | 90 | Air Handling Unit | 34168 | 2.3917 | 1
- | Library | 550 | 36 |  | 2658 | 60 | 36 | Air Handling Unit | 21264 | 1.5519 | 1
- | Main Office | 205 | 13 |  | 1063 | 24 | 13 | Air Handling Unit | 8504 | 1.4464 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-28 | [7 empty] | 0 | 0 | 0
School: | Penn Treaty High School | [7 empty] | 0 | 0 | 0
Vendor: | Meehan | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | classroom |  | 0 | Yes | 624 | 14 | 14 | House Fan | 4992 | 0 | 0
102 | Administration |  | 0 | Yes | 336 | 7 | 7 | House Fan | 2688 | 0 | 0
102A | classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
104 | classroom |  | 0 | Yes | 1539 | 34 | 34 | House Fan | 12312 | 0 | 0
105 | classroom |  | 0 | Yes | 594 | 13 | 13 | House Fan | 4752 | 0 | 0
106 | classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan | 6912 | 0 | 0
107 | classroom |  | 0 | Yes | 920 | 20 | 20 | House Fan | 7360 | 0 | 0
108 | Administration |  | 0 | Yes | 780 | 17 | 17 | House Fan | 6240 | 0 | 0
109 | classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan | 6912 | 0 | 0
110 | classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | 0 | 0
110A | classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
111 | classroom |  | 0 |  | 650 | 14 | 0 | House Fan | 5200 | 0 | 0
115 | Auditorium |  | 0 |  | 3594 | 81 | 0 | House Fan | 28752 | 0 | 0
H11A | Main office |  | 0 |  | 560 | 12 | 0 | House Fan | 4480 | 0 | 0
H11b | Main office |  | 0 |  | 576 | 13 | 0 | House Fan | 4608 | 0 | 0
H12 | Main office |  | 0 |  | 1150 | 26 | 0 | House Fan | 9200 | 0 | 0
H13 | Main office |  | 0 |  | 792 | 18 | 0 | House Fan | 6336 | 0 | 0
H13a | Main office |  | 0 |  | 312 | 7 | 0 | House Fan | 2496 | 0 | 0
H13b | Main office |  | 0 |  | 814 | 18 | 0 | House Fan | 6512 | 0 | 0
H13c | Main office |  | 0 |  | 275 | 6 | 0 | House Fan | 2200 | 0 | 0
H13d | Main office |  | 0 |  | 1150 | 26 | 0 | House Fan | 9200 | 0 | 0
201 | classroom |  | 0 |  | 650 | 14 | 0 | House Fan | 5200 | 0 | 0
202 | classroom |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
203 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
203A | classroom |  | 0 |  | 253 | 5 | 0 | House Fan | 2024 | 0 | 0
204 | classroom |  | 0 |  | 130 | 2 | 0 | House Fan | 1040 | 0 | 0
204A | classroom |  | 0 |  | 552 | 12 | 0 | House Fan | 4416 | 0 | 0
205 | Nurse |  | 0 | Yes | 325 | 7 | 7 | House Fan | 2600 | 0 | 0
207 | Main office |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | 0 | 0
207A | Speech |  | 0 | Yes | 70 | 1 | 1 | House Fan | 560 | 0 | 0
207B | Office |  | 0 |  | 120 | 2 | 0 | House Fan | 960 | 0 | 0
207D | Principal Office |  | 0 | Yes | 300 | 6 | 6 | House Fan | 2400 | 0 | 0
207G | Conference Room |  | 0 | Yes | 144 | 3 | 3 | House Fan | 1152 | 0 | 0
208 | classroom |  | 0 |  | 1056 | 24 | 0 | House Fan | 8448 | 0 | 0
209 | classroom |  | 0 |  | 1032 | 23 | 0 | House Fan | 8256 | 0 | 0
210 | IMC |  | 0 | Yes | 2352 | 53 | 53 | House Fan | 18816 | 0 | 0
213 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
214 | classroom |  | 0 |  | 624 | 14 | 0 | House Fan | 4992 | 0 | 0
217 | Auditorium |  | 0 |  | 2304 | 52 | 0 | House Fan | 18432 | 0 | 0
301 | classroom |  | 0 |  | 650 | 14 | 0 | House Fan | 5200 | 0 | 0
301A | Administration |  | 0 |  | 375 | 8 | 0 | House Fan | 3000 | 0 | 0
303 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
303A | Admin |  | 0 |  | 275 | 6 | 0 | House Fan | 2200 | 0 | 0
304 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
305 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
305A | classroom |  | 0 |  | 912 | 20 | 0 | House Fan | 7296 | 0 | 0
307 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
308 | classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | 0 | 0
309 | classroom |  | 0 |  | 744 | 16 | 0 | House Fan | 5952 | 0 | 0
310 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
311 | classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0
312 | classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0
313 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
314 | classroom |  | 0 |  | 624 | 14 | 0 | House Fan | 4992 | 0 | 0
315 | Admin |  | 0 |  | 238 | 5 | 0 | House Fan | 1904 | 0 | 0
316 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | 0 | 0
317 | classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | 0 | 0
401 | classroom |  | 0 |  | 624 | 14 | 0 | House Fan | 4992 | 0 | 0
402A | Admin |  | 0 |  | 828 | 18 | 0 | House Fan | 6624 | 0 | 0
402 | classroom |  | 0 |  | 322 | 7 | 0 | House Fan | 2576 | 0 | 0
403 | classroom |  | 0 |  | 1032 | 23 | 0 | House Fan | 8256 | 0 | 0
404 | classroom |  | 0 |  | 984 | 22 | 0 | House Fan | 7872 | 0 | 0
405 | classroom |  | 0 |  | 984 | 22 | 0 | House Fan | 7872 | 0 | 0
406 | classroom |  | 0 |  | 984 | 22 | 0 | House Fan | 7872 | 0 | 0
407 | classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0
408 | classroom |  | 0 |  | 1008 | 22 | 0 | House Fan | 8064 | 0 | 0
409 | classroom |  | 0 |  | 1008 | 22 | 0 | House Fan | 8064 | 0 | 0
410 | classroom |  | 0 |  | 1008 | 22 | 0 | House Fan | 8064 | 0 | 0
412 | Admin |  | 0 |  | 506 | 11 | 0 | House Fan | 4048 | 0 | 0
412A | classroom |  | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
412b | classroom |  | 0 |  | 84 | 1 | 0 | House Fan | 672 | 0 | 0
412c | Admin |  | 0 |  | 484 | 11 | 0 | House Fan | 3872 | 0 | 0
413 | classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0
414 | classroom |  | 0 |  | 650 | 14 | 0 | House Fan | 5200 | 0 | 0
415 | Cafe |  | 0 |  | 2200 | 50 | 0 | House Fan | 17600 | 0 | 0
417 | Kitchen |  | 0 | Yes | 455 | 10 | 10 | House Fan | 3640 | 0 | 0
417A | kitchen |  | 0 |  | 700 | 15 | 0 | House Fan | 5600 | 0 | 0
419 | Cafe |  | 0 |  | 2150 | 48 | 0 | House Fan | 17200 | 0 | 0
- | boys gym |  | 0 |  | 4725 | 107 | 0 | House Fan | 37800 | 0 | 0
- | girls gym |  | 0 |  | 4725 | 107 | 0 | House Fan | 37800 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-24 | [7 empty] | 0 | 0 | 0
School: | Joseph Pennell Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | - | 0 | 0 | Yes | 1152 | 26 | 26 | Univent | 9216 | 0 | 0
2 | - | 0 | 0 | Yes | 1152 | 26 | 26 | Univent | 9216 | 0 | 0
101 | Classroom | 0 | 0 |  | 288 | 6 | 0 | Air Handling Unit | 2304 | 0 | 0
102 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | Air Handling Unit | 5760 | 0 | 0
103 | Classroom | 0 | 0 | Yes | 875 | 19 | 19 | Air Handling Unit | 7000 | 0 | 0
104 | Classroom | 0 | 0 | Yes | 175 | 3 | 3 | Air Handling Unit | 1400 | 0 | 0
104A | Classroom | 0 | 0 |  | 375 | 8 | 0 | Air Handling Unit | 3000 | 0 | 0
104B | Classroom | 0 | 0 |  | 175 | 3 | 0 | Air Handling Unit | 1400 | 0 | 0
104C | Classroom | 0 | 0 |  | 125 | 2 | 0 | Air Handling Unit | 1000 | 0 | 0
105 | Classroom | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit | 7200 | 0 | 0
106 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Air Handling Unit | 6528 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 1025 | 23 | 23 | Air Handling Unit | 8200 | 0 | 0
110 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | Air Handling Unit | 6960 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Air Handling Unit | 6528 | 0 | 0
202 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Air Handling Unit | 6528 | 0 | 0
203 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0
204 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0
205 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0
206 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Air Handling Unit | 6528 | 0 | 0
208 | Classroom | 0 | 0 | Yes | 984 | 22 | 22 | Air Handling Unit | 7872 | 0 | 0
209 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit | 6960 | 0 | 0
210 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit | 6960 | 0 | 0
211 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit | 6960 | 0 | 0
301 | Classroom | 0 | 0 |  | 816 | 18 | 0 | Air Handling Unit | 6528 | 0 | 0
302 | Classroom | 0 | 0 |  | 816 | 18 | 0 | Air Handling Unit | 6528 | 0 | 0
303 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0
304 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0
305 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0
306 | Classroom | 0 | 0 | Yes | 875 | 19 | 19 | Air Handling Unit | 7000 | 0 | 0
307 | Classroom | 0 | 0 |  | 816 | 18 | 0 | Air Handling Unit | 6528 | 0 | 0
308 | Classroom | 0 | 0 | Yes | 910 | 20 | 20 | Air Handling Unit | 7280 | 0 | 0
309 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit | 6960 | 0 | 0
310 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit | 6960 | 0 | 0
311 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit | 6960 | 0 | 0
- | Basement Boys Room | 0 | 0 |  | 650 | 14 | 0 | Air Handling Unit | 5200 | 0 | 0
- | Basement Corridor | 0 | 0 |  | 352 | 8 | 0 | Air Handling Unit | 2816 | 0 | 0
- | Gym | 0 | 0 | Yes | 5096 | 115 | 115 | Air Handling Unit | 40768 | 0 | 0
- | Library | 0 | 0 |  | 1593 | 36 | 0 | Air Handling Unit | 12744 | 0 | 0
- | Nurse | 0 | 0 | Yes | 384 | 8 | 8 | Air Handling Unit | 3072 | 0 | 0
- | Counselor Office |  | 0 |  | 384 | 8 | 0 |  | 3072 | 0 | 0
- | Office |  | 0 | Yes | 456 | 10 | 10 |  | 3648 | 0 | 0
- | Principal's Office |  | 0 | Yes | 234 | 5 | 5 |  | 1872 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | Samuel Pennypacker Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B2 | Classroom | 0 | 0 | Yes | 928 | 21 | 21 | House Fan | 7424 | 0 | 0
B3 | Classroom | 923 | 61 |  | 1160 | 26 | 26 | House Fan | 9280 | 5.9677 | 2
B4 | Classroom | 0 | 0 | Yes | 1260 | 28 | 28 | House Fan | 10080 | 0 | 0
B8 | Classroom | 488 | 32 |  | 576 | 13 | 13 | House Fan | 4608 | 6.3542 | 2
B9 | Classroom | 439 | 29 |  | 460 | 10 | 10 | House Fan | 3680 | 7.1576 | 2
B10 | Classroom | 425 | 28 |  | 576 | 13 | 13 | House Fan | 4608 | 5.5339 | 2
101 | Classroom | 545 | 36 |  | 1131 | 25 | 25 | House Fan | 9048 | 3.6141 | 1
102 | Classroom | 440 | 29 |  | 841 | 19 | 19 | House Fan | 6728 | 3.9239 | 1
103 | Classroom | 545 | 36 |  | 870 | 19 | 19 | House Fan | 6960 | 4.6983 | 2
104 | Classroom | 611 | 40 |  | 870 | 19 | 19 | House Fan | 6960 | 5.2672 | 2
105 | Classroom | 340 | 22 |  | 841 | 19 | 19 | House Fan | 6728 | 3.0321 | 1
106 | Classroom | 395 | 26 |  | 841 | 19 | 19 | House Fan | 6728 | 3.5226 | 1
107 | Classroom | 503 | 33 |  | 841 | 19 | 19 | House Fan | 6728 | 4.4857 | 2
108 | Classroom | 650 | 43 |  | 899 | 20 | 20 | House Fan | 7192 | 5.4227 | 2
109 | Classroom | 437 | 29 |  | 841 | 19 | 19 | House Fan | 6728 | 3.8971 | 1
110 | Classroom | 459 | 30 |  | 899 | 20 | 20 | House Fan | 7192 | 3.8293 | 1
201 | Classroom | 351 | 23 |  | 899 | 20 | 20 | House Fan | 7192 | 2.9283 | 1
202 | Classroom | 424 | 28 |  | 841 | 19 | 19 | House Fan | 6728 | 3.7812 | 1
203 | Classroom | 390 | 26 |  | 870 | 19 | 19 | House Fan | 6960 | 3.3621 | 1
204 | Classroom | 338 | 22 |  | 841 | 19 | 19 | House Fan | 6728 | 3.0143 | 1
205 | Classroom | 649 | 43 |  | 841 | 19 | 19 | House Fan | 6728 | 5.7878 | 2
208 | Classroom | 586 | 39 |  | 899 | 20 | 20 | House Fan | 7192 | 4.8888 | 2
209 | Classroom | 508 | 33 |  | 841 | 19 | 19 | House Fan | 6728 | 4.5303 | 2
210 | Classroom | 356 | 23 |  | 899 | 20 | 20 | House Fan | 7192 | 2.97 | 1
212 | Storage | 0 | 0 |  | 360 | 8 | 0 | House Fan | 2880 | 0 | 0
301 | Classroom | 382 | 25 |  | 899 | 20 | 20 | House Fan | 7192 | 3.1869 | 1
302 | Classroom | 653 | 43 |  | 841 | 19 | 19 | House Fan | 6728 | 5.8234 | 2
303 | Classroom | 355 | 23 |  | 870 | 19 | 19 | House Fan | 6960 | 3.0603 | 1
304 | Classroom | 407 | 27 |  | 841 | 19 | 19 | House Fan | 6728 | 3.6296 | 1
305 | Classroom | 583 | 38 |  | 841 | 19 | 19 | House Fan | 6728 | 5.1992 | 2
306 | Classroom | 554 | 36 |  | 870 | 19 | 19 | House Fan | 6960 | 4.7759 | 2
307 | Classroom | 513 | 34 |  | 841 | 19 | 19 | House Fan | 6728 | 4.5749 | 2
308 | Classroom | 515 | 34 |  | 899 | 20 | 20 | House Fan | 7192 | 4.2964 | 2
309 | Classroom | 676 | 45 |  | 841 | 19 | 19 | House Fan | 6728 | 6.0285 | 2
310 | Classroom | 422 | 28 |  | 899 | 20 | 20 | House Fan | 7192 | 3.5206 | 1
311 | Classroom | 550 | 36 |  | 720 | 16 | 16 | House Fan | 5760 | 5.7292 | 2
312 | Classroom | 0 | 0 | Yes | 138 | 3 | 3 | House Fan | 1104 | 0 | 0
- | Auditorium | 1967 | 131 |  | 4272 | 97 | 97 | House Fan | 34176 | 3.4533 | 1
- | Counselor's Office | 0 | 0 | Yes | 386 | 8 | 8 | House Fan | 3088 | 0 | 0
- | Gym/Café | 0 | 0 | Yes | 3608 | 82 | 82 | House Fan | 28864 | 0 | 0
- | Nurse | 0 | 0 | Yes | 361 | 8 | 8 | House Fan | 2888 | 0 | 0
- | Library | 928 | 61 |  | 1620 | 36 | 36 | House Fan | 12960 | 4.2963 | 2
- | Main Office | 0 | 0 | Yes | 342 | 7 | 7 | House Fan | 2736 | 0 | 0
- | Principals Office | 0 | 0 | Yes | 346 | 7 | 7 | House Fan | 2768 | 0 | 0
- | Teacher's Lounge | 0 | 0 |  | 105 | 2 | 0 | House Fan | 840 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Penrose Elementary School- Main Building | [7 empty] | 0 | 0 | 0
| Main Exhaust Report | [7 empty] | 0 | 0 | 0
School: | Penrose Little School House | [7 empty] | 0 | 0 | 0
| Penrose LSH Exhaust Report | LSH Part 2 and Exhaust | LSH Part 3 and Exhaust | [5 empty] | 0 | 0 | 0
School: | TB Read – former Motivation High School Building | [7 empty] | 0 | 0 | 0
| TB Read Exhaust Report | TB Read Exhaust Retest | [6 empty] | 0 | 0 | 0
Vendor: | Chadwick | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Penrose Main Building | [8 empty] | 0 | 0 | 0
101 | Classroom | 373 | 24 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.1646 | 1
102 | Classroom | 387 | 25 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.2834 | 1
103 | Classroom | 359 | 23 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.0458 | 1
104 | Classroom | 505 | 33 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 4.2845 | 2
105 | Classroom | 469 | 31 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.9791 | 1
106 | office | 119 | 7 |  | 315 | 7 | 7 | Rooftop Unit | 2520 | 2.8333 | 1
106a | principal | 26 | 1 |  | 72 | 1 | 1 | Rooftop Unit | 576 | 2.7083 | 1
106b | council | 36 | 2 |  | 176 | 4 | 2 | Rooftop Unit | 1408 | 1.5341 | 1
107 | Classroom | 99 | 6 |  | 884 | 20 | 6 | Rooftop Unit | 7072 | 0.83993 | 0
111 | Classroom | 233 | 15 |  | 884 | 20 | 15 | Rooftop Unit | 7072 | 1.9768 | 1
113 | Classroom | 256 | 17 |  | 884 | 20 | 17 | Rooftop Unit | 7072 | 2.1719 | 1
115 | Classroom | 287 | 19 |  | 884 | 20 | 19 | Rooftop Unit | 7072 | 2.435 | 1
116 | cafe | 330 | 22 |  | 1794 | 40 | 22 | Rooftop Unit | 14352 | 1.3796 | 1
116 | Classroom | 387 | 25 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.2834 | 1
117 | Classroom | 337 | 22 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 2.8592 | 1
118 | Classroom | 306 | 20 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 2.5962 | 1
119 | Classroom | 297 | 19 |  | 884 | 20 | 19 | Rooftop Unit | 7072 | 2.5198 | 1
121 | Classroom | 291 | 19 |  | 884 | 20 | 19 | Rooftop Unit | 7072 | 2.4689 | 1
201 | Classroom | 704 | 46 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 5.9729 | 2
202 | Classroom | 475 | 31 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 4.03 | 2
203 | Classroom | 697 | 46 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 5.9135 | 2
204 | Classroom | 457 | 30 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.8773 | 1
205 | Classroom | 292 | 19 |  | 884 | 20 | 19 | Rooftop Unit | 7072 | 2.4774 | 1
206 | Classroom | 399 | 26 |  | 496 | 11 | 11 | Rooftop Unit | 3968 | 6.0333 | 2
207 | Classroom | 574 | 38 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 4.8699 | 2
211 | Classroom | 423 | 28 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.5888 | 1
213 | Classroom | 159 | 10 |  | 884 | 20 | 10 | Rooftop Unit | 7072 | 1.349 | 1
214 | Classroom | 202 | 13 |  | 884 | 20 | 13 | Rooftop Unit | 7072 | 1.7138 | 1
215 | Classroom | 208 | 13 |  | 884 | 20 | 13 | Rooftop Unit | 7072 | 1.7647 | 1
216 | Classroom | 144 | 9 |  | 884 | 20 | 9 | Rooftop Unit | 7072 | 1.2217 | 1
217 | Classroom | 142 | 9 |  | 884 | 20 | 9 | Rooftop Unit | 7072 | 1.2048 | 1
218 | Classroom | 153 | 10 |  | 1768 | 40 | 10 | Rooftop Unit | 14144 | 0.64904 | 0
219 | Classroom | 131 | 8 |  | 884 | 20 | 8 | Rooftop Unit | 7072 | 1.1114 | 1
221 | Classroom | 151 | 10 |  | 884 | 20 | 10 | Rooftop Unit | 7072 | 1.2811 | 1
Penrose Little School House | [8 empty] | 0 | 0 | 0
1 | Classroom | 289 | 19 |  | 978 | 22 | 19 | Blower Coil Unit | 7824 | 2.2163 | 1
2 | Classroom | 340 | 22 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 2.6074 | 1
3 | Classroom | 289 | 19 |  | 978 | 22 | 19 | Blower Coil Unit | 7824 | 2.2163 | 1
4 | Classroom | 340 | 22 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 2.6074 | 1
5 | Classroom | 350 | 23 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 2.684 | 1
6 | Classroom | 374 | 24 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 2.8681 | 1
7 | Classroom | 374 | 24 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 2.8681 | 1
8 | Classroom | 493 | 32 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 3.7807 | 1
9 | Classroom | 311 | 20 |  | 978 | 22 | 20 | Blower Coil Unit | 7824 | 2.385 | 1
10 | Classroom | 493 | 32 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 3.7807 | 1
11 | Classroom | 311 | 20 |  | 978 | 22 | 20 | Blower Coil Unit | 7824 | 2.385 | 1
- | multipurpose | 2960 | 197 |  | 2067 | 46 | 46 | Blower Coil Unit | 16536 | 10.7402 | 3
- | Corridor | 58 | 3 |  | 684 | 15 | 3 | Blower Coil Unit | 5472 | 0.63596 | 0
- | Boy's Restroom | 59 | 3 |  | 200 | 4 | 3 | Blower Coil Unit | 1600 | 2.2125 | 1
- | Girl's Rest Room | 64 | 4 |  | 200 | 4 | 4 | Blower Coil Unit | 1600 | 2.4 | 1
- | General Office |  | 0 |  | 146 | 3 | 0 | Blower Coil Unit | 1168 | 0 | 0
- | Principal's Office |  | 0 |  | 72 | 1 | 0 | Blower Coil Unit | 576 | 0 | 0
- | Psychiastrist's Office |  | 0 |  | 72 | 1 | 0 | Blower Coil Unit | 576 | 0 | 0
TB Read | [8 empty] | 0 | 0 | 0
101 | Classroom | 324 | 21 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 3.0682 | 1
102 | Classroom | 101 | 6 | Yes | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 0.95644 | 0
103 | Classroom | 492 | 32 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 4.6591 | 2
104 | Classroom | 584 | 38 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 5.5303 | 2
105 | Classroom | 400 | 26 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 3.7879 | 1
201 | Classroom | 443 | 29 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 4.1951 | 2
202 | Classroom | 1636 | 109 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 15.4924 | 3
203 | Classroom | 717 | 47 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 6.7898 | 2
204 | Classroom | 948 | 63 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 8.9773 | 2
205 | Classroom | 397 | 26 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 3.7595 | 1
14 | Computer Lab | 473 | 31 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 4.4792 | 2
- | Corridor #1 | 795 | 53 |  | 1298 | 29 | 29 | Heating Ventilation Unit | 10384 | 4.5936 | 2
- | Corridor #2 | 413 | 27 |  | 1600 | 36 | 27 | Heating Ventilation Unit | 12800 | 1.9359 | 1
- | GYM | 7270 | 484 |  | 8969 | 203 | 203 | Heating Ventilation Unit | 71752 | 6.0793 | 2
- | Library | 442 | 29 |  | 874 | 19 | 19 | Heating Ventilation Unit | 6992 | 3.7929 | 1
Sheet Last Modified: | 2021-05-03 | [7 empty] | 0 | 0 | 0
School: | Philadelphia Learning Academy North/ Camelot Academy East/ Crossroads Academy at Hunting Park (former CEP Hunting Park) Alternative School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
3 | Room (Split Level South) | 25 | 1 |  | 86 | 1 | 1 | Rooftop Unit | 688 | 2.1802 | 1
5 | Room (Split Level South) | 141 | 9 |  | 396 | 9 | 9 | Rooftop Unit | 3168 | 2.6705 | 1
005A | Room (Split Level South) | 20 | 1 |  | 87 | 1 | 1 | Rooftop Unit | 696 | 1.7241 | 1
6 | Room | 27 | 1 |  | 83 | 1 | 1 | Rooftop Unit | 664 | 2.4398 | 1
006A | Room | 14 | 0 |  | 80 | 1 | 0 | Rooftop Unit | 640 | 1.3125 | 1
006B | Room | 13 | 0 |  | 79 | 1 | 0 | Rooftop Unit | 632 | 1.2342 | 1
10 | Room | 7 | 0 |  | 84 | 1 | 0 | Rooftop Unit | 672 | 0.625 | 0
010A | Room | 53 | 3 |  | 80 | 1 | 1 | Rooftop Unit | 640 | 4.9688 | 2
103 | Room | 20 | 1 |  | 87 | 1 | 1 | Rooftop Unit | 696 | 1.7241 | 1
104 | Room | 19 | 1 |  | 85 | 1 | 1 | Rooftop Unit | 680 | 1.6765 | 1
105 | Room | 27 | 1 |  | 81 | 1 | 1 | Rooftop Unit | 648 | 2.5 | 1
106 | Room | 22 | 1 |  | 83 | 1 | 1 | Rooftop Unit | 664 | 1.988 | 1
108 | Room | 14 | 0 |  | 89 | 2 | 0 | Rooftop Unit | 712 | 1.1798 | 1
109 | Room | 13 | 0 |  | 92 | 2 | 0 | Rooftop Unit | 736 | 1.0598 | 1
110 | Room | 15 | 0 |  | 269 | 6 | 0 | Rooftop Unit | 2152 | 0.41822 | 0
113 | Room (Split Level South) | 56 | 3 |  | 134 | 3 | 3 | Rooftop Unit | 1072 | 3.1343 | 1
114 | Room (Split Level South) | 26 | 1 |  | 136 | 3 | 1 | Rooftop Unit | 1088 | 1.4338 | 1
115 | Room (Split Level South) | 41 | 2 |  | 139 | 3 | 2 | Rooftop Unit | 1112 | 2.2122 | 1
116 | Room (Split Level South) | 25 | 1 |  | 139 | 3 | 1 | Rooftop Unit | 1112 | 1.3489 | 1
117 | Room (Split Level South) | 80 | 5 |  | 355 | 8 | 5 | Rooftop Unit | 2840 | 1.6901 | 1
120 | Admin Office | -231 | -15 |  | 92 | 2 | -15 | Rooftop Unit | 736 | -18.8315 | 0
121 | Admin Office | 145 | 9 |  | 396 | 9 | 9 | Rooftop Unit | 3168 | 2.7462 | 1
122 | Admin Office | 208 | 13 |  | 94 | 2 | 2 | Rooftop Unit | 752 | 16.5957 | 3
123 | Admin Office | 97 | 6 |  | 92 | 2 | 2 | Rooftop Unit | 736 | 7.9076 | 2
124 | Admin Office | -65 | -4 |  | 92 | 2 | -4 | Rooftop Unit | 736 | -5.2989 | 0
126 | Admin Office | 57 | 3 |  | 139 | 3 | 3 | Rooftop Unit | 1112 | 3.0755 | 1
127 | Admin Office | -417 | -27 |  | 95 | 2 | -27 | Rooftop Unit | 760 | -32.9211 | 0
129 | Admin Office | -65 | -4 |  | 355 | 8 | -4 | Rooftop Unit | 2840 | -1.3732 | 0
130 | Admin Office | -52 | -3 | Yes | 140 | 3 | 3 | Rooftop Unit | 1120 | -2.7857 | 0
133 | Admin Office | 104 | 6 |  | 266 | 6 | 6 | Rooftop Unit | 2128 | 2.9323 | 1
133A | Admin Office | 322 | 21 |  | 927 | 21 | 21 | Rooftop Unit | 7416 | 2.6052 | 1
133B | Admin Office | 316 | 21 |  | 927 | 21 | 21 | Rooftop Unit | 7416 | 2.5566 | 1
134 | Media Room | 195 | 13 |  | 1769 | 40 | 13 | Rooftop Unit | 14152 | 0.82674 | 0
135 | Admin Office | 253 | 16 |  | 709 | 16 | 16 | Rooftop Unit | 5672 | 2.6763 | 1
136 | Media Room | 465 | 31 |  | 407 | 9 | 9 | Rooftop Unit | 3256 | 8.5688 | 2
142 | Admin Office | 339 | 22 |  | 225 | 5 | 5 | Rooftop Unit | 1800 | 11.3 | 3
147 | AEP Office | 146 | 9 |  | 413 | 9 | 9 | Rooftop Unit | 3304 | 2.6513 | 1
148 | AEP Office | -245 | -16 |  | 92 | 2 | -16 | Rooftop Unit | 736 | -19.9728 | 0
149 | AEP Office | -104 | -6 |  | 94 | 2 | -6 | Rooftop Unit | 752 | -8.2979 | 0
150 | AEP Office | -38 | -2 |  | 136 | 3 | -2 | Rooftop Unit | 1088 | -2.0956 | 0
151 | AEP Office | 178 | 11 |  | 179 | 4 | 4 | Rooftop Unit | 1432 | 7.4581 | 2
152 | AEP Office | 10 | 0 |  | 91 | 2 | 0 | Rooftop Unit | 728 | 0.82418 | 0
153 | AEP Office | 36 | 2 |  | 92 | 2 | 2 | Rooftop Unit | 736 | 2.9348 | 1
154 | AEP Office | 69 | 4 |  | 96 | 2 | 2 | Rooftop Unit | 768 | 5.3906 | 2
155 | AEP Office | 179 | 11 |  | 184 | 4 | 4 | Rooftop Unit | 1472 | 7.2962 | 2
156 | AEP Office | -34 | -2 |  | 80 | 1 | -2 | Rooftop Unit | 640 | -3.1875 | 0
157 | AEP Office | 70 | 4 |  | 79 | 1 | 1 | Rooftop Unit | 632 | 6.6456 | 2
158 | AEP Office | 119 | 7 |  | 85 | 1 | 1 | Rooftop Unit | 680 | 10.5 | 3
159 | AEP Office | 21 | 1 |  | 84 | 1 | 1 | Rooftop Unit | 672 | 1.875 | 1
160 | AEP Office | 184 | 12 |  | 142 | 3 | 3 | Rooftop Unit | 1136 | 9.7183 | 2
161 | Library Office | -59 | -3 |  | 91 | 2 | -3 | Rooftop Unit | 728 | -4.8626 | 0
162 | Library Office | -99 | -6 |  | 269 | 6 | -6 | Rooftop Unit | 2152 | -2.7602 | 0
164 | Main Library | 980 | 65 |  | 973 | 22 | 22 | Rooftop Unit | 7784 | 7.554 | 2
174 | Office | -270 | -18 |  | 83 | 1 | -18 | Rooftop Unit | 664 | -24.3976 | 0
175 | Office | 80 | 5 |  | 82 | 1 | 1 | Rooftop Unit | 656 | 7.3171 | 2
180 | Office | 87 | 5 |  | 93 | 2 | 2 | Rooftop Unit | 744 | 7.0161 | 2
181 | Office | -31 | -2 |  | 92 | 2 | -2 | Rooftop Unit | 736 | -2.5272 | 0
182 | Office | 166 | 11 |  | 92 | 2 | 2 | Rooftop Unit | 736 | 13.5326 | 3
184 | Office | 122 | 8 |  | 93 | 2 | 2 | Rooftop Unit | 744 | 9.8387 | 2
185 | Office | 27 | 1 |  | 92 | 2 | 1 | Rooftop Unit | 736 | 2.2011 | 1
186A | Office | -272 | -18 |  | 449 | 10 | -18 | Rooftop Unit | 3592 | -4.5434 | 0
186B | Office | -47 | -3 |  | 449 | 10 | -3 | Rooftop Unit | 3592 | -0.78508 | 0
187 | Office | -182 | -12 |  | 94 | 2 | -12 | Rooftop Unit | 752 | -14.5213 | 0
188 | Office | 100 | 6 |  | 92 | 2 | 2 | Rooftop Unit | 736 | 8.1522 | 2
189 | Office | 78 | 5 |  | 227 | 5 | 5 | Rooftop Unit | 1816 | 2.5771 | 1
192 | Office | -269 | -17 |  | 72 | 1 | -17 | Rooftop Unit | 576 | -28.0208 | 0
193 | Office | 283 | 18 |  | 82 | 1 | 1 | Rooftop Unit | 656 | 25.8841 | 4
194 | Office | 106 | 7 |  | 48 | 1 | 1 | Rooftop Unit | 384 | 16.5625 | 3
195 | Office | 78 | 5 |  | 232 | 5 | 5 | Rooftop Unit | 1856 | 2.5216 | 1
196 | Classroom | 190 | 12 |  | 528 | 12 | 12 | Rooftop Unit | 4224 | 2.6989 | 1
201 | Classroom | 248 | 16 |  | 712 | 16 | 16 | Rooftop Unit | 5696 | 2.6124 | 1
204 | Electrical Closet | 13 | 0 |  | 80 | 1 | 0 | Rooftop Unit | 640 | 1.2188 | 1
205 | IT Room | -3 | 0 |  | 84 | 1 | 0 | Rooftop Unit | 672 | -0.26786 | 0
207 | Closet | 0 | 0 |  | 136 | 3 | 0 | Rooftop Unit | 1088 | 0 | 0
210 | Office | -127 | -8 |  | 96 | 2 | -8 | Rooftop Unit | 768 | -9.9219 | 0
211 | Office | -20 | -1 |  | 94 | 2 | -1 | Rooftop Unit | 752 | -1.5957 | 0
212 | Office | 0 | 0 |  | 96 | 2 | 0 | Rooftop Unit | 768 | 0 | 0
213 | Room |  | 0 | Yes | 880 | 20 | 20 |  | 7040 | 0 | 0
213A | Office | 63 | 4 |  | 180 | 4 | 4 | Rooftop Unit | 1440 | 2.625 | 1
213B | Office | 284 | 18 |  | 792 | 18 | 18 | Rooftop Unit | 6336 | 2.6894 | 1
214 | Office | -12 | 0 |  | 89 | 2 | 0 | Rooftop Unit | 712 | -1.0112 | 0
215 | Office | 0 | 0 |  | 92 | 2 | 0 | Rooftop Unit | 736 | 0 | 0
217 | Office | -31 | -2 |  | 96 | 2 | -2 | Rooftop Unit | 768 | -2.4219 | 0
218 | Office | -23 | -1 |  | 86 | 1 | -1 | Rooftop Unit | 688 | -2.0058 | 0
219 | Office | 0 | 0 |  | 93 | 2 | 0 | Rooftop Unit | 744 | 0 | 0
221 | IT Room | 13 | 0 |  | 52 | 1 | 0 | Rooftop Unit | 416 | 1.875 | 1
222 | Electrical Closet | 195 | 13 |  | 94 | 2 | 2 | Rooftop Unit | 752 | 15.5585 | 3
223 | Closet | 0 | 0 |  | 55 | 1 | 0 | Rooftop Unit | 440 | 0 | 0
303 | Room (Split Level South) | 45 | 2 |  | 86 | 1 | 1 | Rooftop Unit | 688 | 3.9244 | 1
304 | Room (Split Level South) | 124 | 8 |  | 231 | 5 | 5 | Rooftop Unit | 1848 | 4.026 | 2
307 | Room (Split Level South) | 118 | 7 |  | 312 | 7 | 7 | Rooftop Unit | 2496 | 2.8365 | 1
311 | Room (Split Level South) | 13 | 0 |  | 136 | 3 | 0 | Rooftop Unit | 1088 | 0.71691 | 0
311A | Room (Split Level South) | 20 | 1 |  | 63 | 1 | 1 | Rooftop Unit | 504 | 2.381 | 1
311B | Room (Split Level South) | 12 | 0 |  | 86 | 1 | 0 | Rooftop Unit | 688 | 1.0465 | 1
313 | Room | 20 | 1 |  | 98 | 2 | 1 | Rooftop Unit | 784 | 1.5306 | 1
314 | Room | 21 | 1 |  | 85 | 1 | 1 | Rooftop Unit | 680 | 1.8529 | 1
316 | Room | 62 | 4 |  | 449 | 10 | 4 | Rooftop Unit | 3592 | 1.0356 | 1
320 | Room | 19 | 1 |  | 87 | 1 | 1 | Rooftop Unit | 696 | 1.6379 | 1
321 | Room | 16 | 1 |  | 89 | 2 | 1 | Rooftop Unit | 712 | 1.3483 | 1
322 | Room | 17 | 1 |  | 87 | 1 | 1 | Rooftop Unit | 696 | 1.4655 | 1
H01 | Room (Split Level South) | 34 | 2 |  | 89 | 2 | 2 | Rooftop Unit | 712 | 2.8652 | 1
H01 | Room | 15 | 0 |  | 72 | 1 | 0 | Rooftop Unit | 576 | 1.5625 | 1
H21 | Room (Split Level South) | 159 | 10 |  | 446 | 10 | 10 | Rooftop Unit | 3568 | 2.6738 | 1
H21 | Room | 7 | 0 |  | 52 | 1 | 0 | Rooftop Unit | 416 | 1.0096 | 1
L4/L5 | Room | 84 | 5 |  | 225 | 5 | 5 | Rooftop Unit | 1800 | 2.8 | 1
A1 | Classroom | 594 | 39 | Yes | 794 | 18 | 18 | Rooftop Unit | 6352 | 5.6108 | 2
A2 | Classroom | 876 | 58 |  | 793 | 18 | 18 | Rooftop Unit | 6344 | 8.285 | 2
A3 | Classroom | 219 | 14 |  | 795 | 18 | 14 | Rooftop Unit | 6360 | 2.066 | 1
A4 | Classroom | 905 | 60 |  | 796 | 18 | 18 | Rooftop Unit | 6368 | 8.527 | 2
B1 | Classroom | 430 | 28 |  | 793 | 18 | 18 | Rooftop Unit | 6344 | 4.0668 | 2
B2 | Classroom | 1048 | 69 |  | 792 | 18 | 18 | Rooftop Unit | 6336 | 9.9242 | 2
B3 | Classroom | 84 | 5 |  | 794 | 18 | 5 | Rooftop Unit | 6352 | 0.79345 | 0
B4 | Classroom | 769 | 51 |  | 794 | 18 | 18 | Rooftop Unit | 6352 | 7.2639 | 2
C1 | Classroom | 551 | 36 |  | 797 | 18 | 18 | Rooftop Unit | 6376 | 5.1851 | 2
C2 | Classroom | 927 | 61 |  | 795 | 18 | 18 | Rooftop Unit | 6360 | 8.7453 | 2
C3 | Classroom | 115 | 7 |  | 794 | 18 | 7 | Rooftop Unit | 6352 | 1.0863 | 1
C4 | Classroom | 70 | 4 |  | 795 | 18 | 4 | Rooftop Unit | 6360 | 0.66038 | 0
D1 | Classroom | 587 | 39 |  | 797 | 18 | 18 | Rooftop Unit | 6376 | 5.5238 | 2
D2 | Classroom | 935 | 62 |  | 795 | 18 | 18 | Rooftop Unit | 6360 | 8.8208 | 2
D3 | Classroom | 14 | 0 |  | 793 | 18 | 0 | Rooftop Unit | 6344 | 0.13241 | 0
D4 | Classroom | 617 | 41 |  | 796 | 18 | 18 | Rooftop Unit | 6368 | 5.8134 | 2
E1 | Classroom | 312 | 20 | Yes | 794 | 18 | 18 | Rooftop Unit | 6352 | 2.9471 | 1
E2 | Classroom | 752 | 50 | Yes | 796 | 18 | 18 | Rooftop Unit | 6368 | 7.0854 | 2
E3 | Classroom | 269 | 17 |  | 793 | 18 | 17 | Rooftop Unit | 6344 | 2.5441 | 1
E4 | Classroom | 715 | 47 | Yes | 795 | 18 | 18 | Rooftop Unit | 6360 | 6.7453 | 2
G1 | Classroom | 66 | 4 | Yes | 794 | 18 | 18 | Rooftop Unit | 6352 | 0.62343 | 0
G2 | Classroom | 857 | 57 | Yes | 796 | 18 | 18 | Rooftop Unit | 6368 | 8.0747 | 2
G3 | Classroom | 197 | 13 | Yes | 793 | 18 | 18 | Rooftop Unit | 6344 | 1.8632 | 1
G4 | Classroom | 813 | 54 | Yes | 797 | 18 | 18 | Rooftop Unit | 6376 | 7.6506 | 2
Gym | Recreational Area 1 | 442 | 29 |  | 1276 | 29 | 29 | Rooftop Unit | 10208 | 2.598 | 1
Gym | Gym Cafeteria | 306 | 20 |  | 886 | 20 | 20 | Rooftop Unit | 7088 | 2.5903 | 1
Gym | Recreational Area 1 | 630 | 42 |  | 1848 | 42 | 42 | Rooftop Unit | 14784 | 2.5568 | 1
Gym | Gym 2A | 716 | 47 |  | 9196 | 209 | 47 | Rooftop Unit | 73568 | 0.58395 | 0
Gym | Gym 2B | 601 | 40 |  | 9196 | 209 | 40 | Rooftop Unit | 73568 | 0.49016 | 0
Gym | Vestibule | 0 | 0 |  | 176 | 4 | 0 | Rooftop Unit | 1408 | 0 | 0
H1 | Classroom | 807 | 53 |  | 796 | 18 | 18 | Rooftop Unit | 6368 | 7.6036 | 2
H17 | Hallway | 91 | 6 |  | 264 | 6 | 6 | Rooftop Unit | 2112 | 2.5852 | 1
H2 | Classroom | 706 | 47 |  | 794 | 18 | 18 | Rooftop Unit | 6352 | 6.6688 | 2
H3 | Classroom | -660 | -44 |  | 793 | 18 | -44 | Rooftop Unit | 6344 | -6.2421 | 0
H4 | Classroom | 11 | 0 |  | 795 | 18 | 0 | Rooftop Unit | 6360 | 0.10377 | 0
Hallway | Hallway (Split Level South) | 48 | 3 |  | 136 | 3 | 3 | Rooftop Unit | 1088 | 2.6471 | 1
Hunter | Office | 229 | 15 |  | 664 | 15 | 15 | Rooftop Unit | 5312 | 2.5866 | 1
Hunting Park | Lobby | 1738 | 115 |  | 5069 | 115 | 115 | Rooftop Unit | 40552 | 2.5715 | 1
J | Hallway | 0 | 0 |  | 616 | 14 | 0 | Rooftop Unit | 4928 | 0 | 0
J1 | Classroom | -493 | -32 | Yes | 529 | 12 | 12 | Rooftop Unit | 4232 | -6.9896 | 0
J2 | Classroom | 381 | 25 |  | 792 | 18 | 18 | Rooftop Unit | 6336 | 3.608 | 1
J3 | Classroom | 493 | 32 |  | 528 | 12 | 12 | Rooftop Unit | 4224 | 7.0028 | 2
J4 | Classroom | 1208 | 80 |  | 528 | 12 | 12 | Rooftop Unit | 4224 | 17.1591 | 3
K | Hallway | 0 | 0 |  | 616 | 14 | 0 | Rooftop Unit | 4928 | 0 | 0
K1 | Classroom | 189 | 12 |  | 792 | 18 | 12 | Rooftop Unit | 6336 | 1.7898 | 1
K2 | Classroom | 682 | 45 |  | 794 | 18 | 18 | Rooftop Unit | 6352 | 6.4421 | 2
K3 | Classroom | 130 | 8 | Yes | 796 | 18 | 18 | Rooftop Unit | 6368 | 1.2249 | 1
K4 | Classroom | 617 | 41 |  | 797 | 18 | 18 | Rooftop Unit | 6376 | 5.8061 | 2
Kitchen | Kitchen | 1953 | 130 |  | 880 | 20 | 20 | Rooftop Unit | 7040 | 16.6449 | 3
Kitchen | Lounge | -3 | 0 |  | 73 | 1 | 0 | Rooftop Unit | 584 | -0.30822 | 0
L | Hallway | 0 | 0 |  | 704 | 16 | 0 | Rooftop Unit | 5632 | 0 | 0
L1 | Classroom | 79 | 5 | Yes | 794 | 18 | 18 | Rooftop Unit | 6352 | 0.74622 | 0
L2 | Classroom | 636 | 42 |  | 793 | 18 | 18 | Rooftop Unit | 6344 | 6.0151 | 2
L3 | Classroom | 109 | 7 | Yes | 792 | 18 | 18 | Rooftop Unit | 6336 | 1.0322 | 1
L4 | Classroom | 707 | 47 |  | 797 | 18 | 18 | Rooftop Unit | 6376 | 6.6531 | 2
Lobby | Main Lobby North | 147 | 9 |  | 410 | 9 | 9 | Rooftop Unit | 3280 | 2.689 | 1
M | Hallway | 0 | 0 |  | 704 | 16 | 0 | Rooftop Unit | 5632 | 0 | 0
M1 | Classroom | 226 | 15 |  | 794 | 18 | 15 | Rooftop Unit | 6352 | 2.1348 | 1
M2 | Classroom | 855 | 57 |  | 796 | 18 | 18 | Rooftop Unit | 6368 | 8.0559 | 2
M3 | Classroom | 17 | 1 |  | 793 | 18 | 1 | Rooftop Unit | 6344 | 0.16078 | 0
M4 | Classroom | 684 | 45 |  | 795 | 18 | 18 | Rooftop Unit | 6360 | 6.4528 | 2
Men's Bathroom | Men's Bathroom | 0 | 0 |  | 132 | 3 | 0 | Rooftop Unit | 1056 | 0 | 0
MS0S1 | Office | 432 | 28 |  | 528 | 12 | 12 | Rooftop Unit | 4224 | 6.1364 | 2
MS0S2 | Office | 1153 | 76 |  | 880 | 20 | 20 | Rooftop Unit | 7040 | 9.8267 | 2
MS2 | MS2 (Woodshop) | 480 | 32 |  | 1408 | 32 | 32 | Rooftop Unit | 11264 | 2.5568 | 1
MS2 | MS2 (Woodshop) | 768 | 51 |  | 1408 | 32 | 32 | Rooftop Unit | 11264 | 4.0909 | 2
MS6 | Office | 107 | 7 |  | 176 | 4 | 4 | Rooftop Unit | 1408 | 4.5597 | 2
MS7 | Office | 0 | 0 |  | 132 | 3 | 0 | Rooftop Unit | 1056 | 0 | 0
N1 | Classroom | 612 | 40 |  | 794 | 18 | 18 | Rooftop Unit | 6352 | 5.7809 | 2
N2 | Classroom (with office) | 100 | 6 |  | 796 | 18 | 6 | Rooftop Unit | 6368 | 0.94221 | 0
N3 | Classroom (with office) | 1490 | 99 |  | 795 | 18 | 18 | Rooftop Unit | 6360 | 14.0566 | 3
N4 | Classroom | 781 | 52 |  | 796 | 18 | 18 | Rooftop Unit | 6368 | 7.3587 | 2
Office | Office | 12 | 0 |  | 132 | 3 | 0 | Rooftop Unit | 1056 | 0.68182 | 0
S11 | AEP Office | -244 | -16 |  | 396 | 9 | -16 | Rooftop Unit | 3168 | -4.6212 | 0
- | Staff Lounge | 243 | 16 |  | 528 | 12 | 12 | Rooftop Unit | 4224 | 3.4517 | 1
- | Women's Bathroom | 0 | 0 |  | 132 | 3 | 0 | Rooftop Unit | 1056 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Robert B. Pollock Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCORE Fluidics | Retest Report | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Classroom | 313 | 20 |  | 945 | 21 | 20 | Perimeter Heater | 7560 | 2.4841 | 1
2 | Classroom | 385 | 25 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 3.0556 | 1
3 | Classroom | 141 | 9 | Yes | 945 | 21 | 21 | Perimeter Heater | 7560 | 1.119 | 1
4 | Classroom | 406 | 27 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 3.2222 | 1
5 | Classroom | 222 | 14 | Yes | 945 | 21 | 21 | Perimeter Heater | 7560 | 1.7619 | 1
6 | Classroom | 278 | 18 |  | 720 | 16 | 16 | Perimeter Heater | 5760 | 2.8958 | 1
7 | Classroom | 270 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1429 | 1
8 | Classroom | 329 | 21 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 2.6111 | 1
9 | Classroom | 301 | 20 |  | 945 | 21 | 20 | Perimeter Heater | 7560 | 2.3889 | 1
10 | Classroom | 482 | 32 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 3.8254 | 1
11 | Classroom | 0 | 0 | Yes | 945 | 21 | 21 | Perimeter Heater | 7560 | 0 | 0
12 | Classroom | 369 | 24 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 2.9286 | 1
13 | Classroom | 282 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.2381 | 1
14 | Classroom | 338 | 22 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 2.6825 | 1
15 | Classroom | 275 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1825 | 1
16 | Classroom | 311 | 20 |  | 840 | 19 | 19 | Perimeter Heater | 6720 | 2.7768 | 1
17 | Classroom | 294 | 19 |  | 945 | 21 | 19 | Perimeter Heater | 7560 | 2.3333 | 1
101 | Classroom | 505 | 33 |  | 1450 | 32 | 32 | Perimeter Heater | 11600 | 2.6121 | 1
102 | Classroom | 280 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.2222 | 1
103 | Classroom | 305 | 20 |  | 945 | 21 | 20 | Perimeter Heater | 7560 | 2.4206 | 1
104 | Classroom | 277 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1984 | 1
105 | Classroom | 273 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1667 | 1
106 | Classroom | 707 | 47 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 5.6111 | 2
107 | Classroom |  | 0 | Yes | 945 | 21 | 21 |  | 7560 | 0 | 0
108 | Classroom | 315 | 21 |  | 594 | 13 | 13 | Perimeter Heater | 4752 | 3.9773 | 1
110 | Classroom | 301 | 20 | Yes | 945 | 21 | 21 | Perimeter Heater | 7560 | 2.3889 | 1
111 | Classroom | 276 | 18 |  | 480 | 10 | 10 | Perimeter Heater | 3840 | 4.3125 | 2
112 | Classroom | 276 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1905 | 1
113 | Classroom | 272 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1587 | 1
114 | Classroom | 277 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1984 | 1
115 | Classroom | 275 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1825 | 1
116 | Classroom | 289 | 19 |  | 945 | 21 | 19 | Perimeter Heater | 7560 | 2.2937 | 1
117A | Classroom | 579 | 38 |  | 1890 | 42 | 38 | Perimeter Heater | 15120 | 2.2976 | 1
118 | Classroom | 323 | 21 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 2.5635 | 1
- | Main Office |  | 0 | Yes | 674 | 15 | 15 |  | 5392 | 0 | 0
- | Principals Office |  | 0 | Yes | 96 | 2 | 2 |  | 768 | 0 | 0
- | Nurses Office |  | 0 | Yes | 96 | 2 | 2 |  | 768 | 0 | 0
- | Office |  | 0 | Yes | 108 | 2 | 2 |  | 864 | 0 | 0
- | Auditorium | 5528 | 368 |  | 4240 | 96 | 96 | Air Handling Unit | 33920 | 9.7783 | 2
- | Cafeteria | 5093 | 339 |  | 4032 | 91 | 91 | Air Handling Unit | 32256 | 9.4736 | 2
- | Confrence Room | 275 | 18 |  | 374 | 8 | 8 | Perimeter Heater | 2992 | 5.5147 | 2
- | Gym | 3930 | 262 |  | 3901 | 88 | 88 | Air Handling Unit | 31208 | 7.5558 | 2
- | Kindergarten Classroom | 438 | 29 |  | 1450 | 32 | 29 | Perimeter Heater | 11600 | 2.2655 | 1
- | First Flr Office | 0 | 0 |  | 674 | 15 | 0 | Perimeter Heater | 5392 | 0 | 0
- | P1 Bungalow Building | 527 | 35 |  | 1248 | 28 | 28 | Perimeter Heater | 9984 | 3.1671 | 1
- | P2 Bungalow Building | 298 | 19 |  | 806 | 18 | 18 | Perimeter Heater | 6448 | 2.773 | 1
- | P3 Bungalow Building | 385 | 25 |  | 1040 | 23 | 23 | Perimeter Heater | 8320 | 2.7764 | 1
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21 | [7 empty] | 0 | 0 | 0
School: | Potter Thomas Promise Academy Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | Retest | [6 empty] | 0 | 0 | 0
| Devine 2nd Retest 2-15-21 | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 322 | 21 |  | 1350 | 30 | 21 | Univent | 10800 | 1.7889 | 1
102 | Classroom | 387 | 25 |  | 1590 | 36 | 25 | Univent | 12720 | 1.8255 | 1
103 | Classroom | 374 | 24 |  | 1590 | 36 | 24 | Univent | 12720 | 1.7642 | 1
104 | Classroom | 817 | 54 |  | 1590 | 36 | 36 | Univent | 12720 | 3.8538 | 1
105 | Classroom | 296 | 19 |  | 1024 | 23 | 19 | Univent | 8192 | 2.168 | 1
106 | Music Room | 216 | 14 |  | 754 | 17 | 14 | Univent | 6032 | 2.1485 | 1
106 | Computer Lab | 149 | 9 | Yes | 1989 | 45 | 45 | Univent | 15912 | 0.56184 | 0
201 | Classroom | 245 | 16 |  | 812 | 18 | 16 | Univent | 6496 | 2.2629 | 1
202 | Classroom | 275 | 18 |  | 870 | 19 | 18 | Univent | 6960 | 2.3707 | 1
203 | Classroom | 329 | 21 |  | 870 | 19 | 19 | Univent | 6960 | 2.8362 | 1
204 | Classroom | 350 | 23 |  | 870 | 19 | 19 | Univent | 6960 | 3.0172 | 1
205 | Classroom | 356 | 23 |  | 870 | 19 | 19 | Univent | 6960 | 3.069 | 1
206 | Classroom | 338 | 22 |  | 783 | 17 | 17 | Univent | 6264 | 3.2375 | 1
207 | Classroom | 469 | 31 |  | 841 | 19 | 19 | Univent | 6728 | 4.1825 | 2
208 | Classroom | 397 | 26 |  | 870 | 19 | 19 | Univent | 6960 | 3.4224 | 1
209 | Classroom | 257 | 17 |  | 870 | 19 | 17 | Univent | 6960 | 2.2155 | 1
210 | Classroom | 368 | 24 |  | 870 | 19 | 19 | Univent | 6960 | 3.1724 | 1
211 | Classroom | 348 | 23 |  | 870 | 19 | 19 | Univent | 6960 | 3 | 1
212 | Classroom | 291 | 19 |  | 870 | 19 | 19 | Univent | 6960 | 2.5086 | 1
213 | Classroom | 280 | 18 |  | 870 | 19 | 18 | Univent | 6960 | 2.4138 | 1
214 | Classroom | 319 | 21 |  | 870 | 19 | 19 | Univent | 6960 | 2.75 | 1
215 | Classroom | 297 | 19 |  | 870 | 19 | 19 | Univent | 6960 | 2.5603 | 1
216 | Classroom | 286 | 19 |  | 870 | 19 | 19 | Univent | 6960 | 2.4655 | 1
217 | Classroom | 392 | 26 |  | 896 | 20 | 20 | Univent | 7168 | 3.2812 | 1
218 | Classroom | 296 | 19 |  | 870 | 19 | 19 | Univent | 6960 | 2.5517 | 1
219 | Classroom | 307 | 20 |  | 870 | 19 | 19 | Univent | 6960 | 2.6466 | 1
220 | Classroom | 235 | 15 |  | 870 | 19 | 15 | Univent | 6960 | 2.0259 | 1
221 | Classroom | 293 | 19 |  | 870 | 19 | 19 | Univent | 6960 | 2.5259 | 1
222 | Classroom | 312 | 20 |  | 783 | 17 | 17 | Univent | 6264 | 2.9885 | 1
223 | Classroom | 238 | 15 |  | 870 | 19 | 15 | Univent | 6960 | 2.0517 | 1
224 | Classroom | 300 | 20 |  | 870 | 19 | 19 | Univent | 6960 | 2.5862 | 1
226 | Classroom | 365 | 24 |  | 942 | 21 | 21 | Univent | 7536 | 2.9061 | 1
226A | - |  | 0 | Yes | 269 | 6 | 6 |  | 2152 | 0 | 0
228 | Classroom | 364 | 24 |  | 942 | 21 | 21 | Univent | 7536 | 2.8981 | 1
228A | - |  | 0 | Yes | 269 | 6 | 6 |  | 2152 | 0 | 0
- | Art room | 642 | 42 |  | 1800 | 40 | 40 | Univent | 14400 | 2.675 | 1
| Art Room B |  | 0 |  | 260 | 5 | 0 |  | 2080 | 0 | 0
- | Cafeteria/Theatre | 0 | 0 | Yes | 5280 | 120 | 120 | Air Handling Unit | 42240 | 0 | 0
| ESOL Suite |  | 0 | Yes | 119 | 2 | 2 |  | 952 | 0 | 0
- | Community Room | 239 | 15 |  | 839 | 19 | 15 | Univent | 6712 | 2.1365 | 1
- | Gym | 0 | 0 |  | 5016 | 114 | 0 | Air Handling Unit | 40128 | 0 | 0
- | Gym Offices | 0 | 0 | Yes | 200 | 4 | 4 | Air Handling Unit | 1600 | 0 | 0
- | Kitchen | 273 | 18 |  | 1332 | 30 | 18 | Air Handling Unit | 10656 | 1.5372 | 1
- | Library | 5562 | 370 |  | 1944 | 44 | 44 | Air Handling Unit | 15552 | 21.4583 | 3
Counselor | Office |  | 0 | Yes | 261 | 5 | 5 |  | 2088 | 0 | 0
- | Main Office | 1418 | 94 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | 5.9083 | 2
- | Faculty lounge |  | 0 |  | 840 | 19 | 0 |  | 6720 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Powel/SLAMS Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Capital Retest 3-31-2021 | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Report Classroom ID / Area ID Number | Posted Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | #VALUE! | #VALUE! | #VALUE!
26 | 26 | Electrical room |  | 0 |  | 502 | 11 | 0 | 0 | 0 | 0
21 | 21 | Lockers | 98 | 6 |  | 114 | 2 | 2 | 0 | 0 | 0
23 | 23 | Lockers | 101 | 6 |  | 149 | 3 | 3 | 0 | 0 | 0
17 | 17 | Storage | 203 | 13 |  | 330 | 7 | 7 | 0 | 0 | 0
18 | 18 | Workshop | 362 | 24 |  | 305 | 6 | 6 | 0 | 0 | 0
103 | 101 | Cafeteria | 3580 | 238 |  | 3579 | 81 | 81 | 0 | 0 | 0
104 | - | Corridor | 498 | 33 |  | 977 | 22 | 22 | 0 | 0 | 0
105 | 100 | Waiting Area | 241 | 16 |  | 404 | 9 | 9 | 0 | 0 | 0
112 | 100A | Conselor's Office | 15 | 1 |  | 104 | 2 | 1 | 0 | 0 | 0
113 | 100G | Office | 16 | 1 |  | 123 | 2 | 1 | 0 | 0 | 0
114 | 100B | Dean's Office | 16 | 1 |  | 104 | 2 | 1 | 0 | 0 | 0
115 | 100F | Records | 14 | 0 |  | 101 | 2 | 0 | 0 | 0 | 0
115 | - | Open Office Space | 29 | 1 |  | 332 | 7 | 1 | 0 | 0 | 0
116 | 100C | Principal's Office | 30 | 2 |  | 166 | 3 | 2 | 0 | 0 | 0
118 | 100D | Conference Room | 67 | 4 |  | 186 | 4 | 4 | 0 | 0 | 0
119 | 101F | Kitchen Storage | 36 | 2 |  | 152 | 3 | 2 | 0 | 0 | 0
121 | 101E | Kitchen | 535 | 35 |  | 841 | 19 | 19 | 0 | 0 | 0
123 | - | Servery | 270 | 18 |  | 486 | 11 | 11 | 0 | 0 | 0
124 | 101B | Office | 33 | 2 |  | 91 | 2 | 2 | 0 | 0 | 0
126 | - | Corridor | 251 | 16 |  | 2146 | 48 | 16 | 0 | 0 | 0
127 | 102 | Kindergarten Classroom | 314 | 20 |  | 1023 | 23 | 20 | 0 | 0 | 0
128 | 103 | Classroom | 302 | 20 |  | 853 | 19 | 19 | 0 | 0 | 0
129 | 104 | Kindergarten Classroom | 317 | 21 |  | 1022 | 23 | 21 | 0 | 0 | 0
130 | 105 | Classroom | 318 | 21 |  | 851 | 19 | 19 | 0 | 0 | 0
131 | 106 | Kindergarten Classroom | 321 | 21 |  | 1022 | 23 | 21 | 0 | 0 | 0
132 | 107 | Classroom | 322 | 21 |  | 853 | 19 | 19 | 0 | 0 | 0
133 | 108 | Special Education Classroom | 147 | 9 |  | 378 | 8 | 8 | 0 | 0 | 0
134 | 109 | Classroom | 314 | 20 |  | 853 | 19 | 19 | 0 | 0 | 0
135 | 110 | Classroom | 326 | 21 |  | 852 | 19 | 19 | 0 | 0 | 0
136 | 111 | Classroom | 322 | 21 |  | 853 | 19 | 19 | 0 | 0 | 0
137 | 112 | Classroom | 323 | 21 |  | 842 | 19 | 19 | 0 | 0 | 0
138 | 113 | Classroom | 310 | 20 |  | 842 | 19 | 19 | 0 | 0 | 0
139 | 114 | Classroom | 317 | 21 |  | 844 | 19 | 19 | 0 | 0 | 0
140 | 115 | Classroom | 318 | 21 |  | 844 | 19 | 19 | 0 | 0 | 0
141 | 116 | Classroom | 325 | 21 |  | 851 | 19 | 19 | 0 | 0 | 0
142 | 117 | Classroom | 313 | 20 |  | 853 | 19 | 19 | 0 | 0 | 0
143 | 118 | Special Education Classroom | 151 | 10 |  | 388 | 8 | 8 | 0 | 0 | 0
145 | 119 | Library | 546 | 36 |  | 1712 | 38 | 36 | 0 | 0 | 0
146 | 119B | Conference Room | 32 | 2 |  | 261 | 5 | 2 | 0 | 0 | 0
147 | 119A | Work Room | 19 | 1 |  | 270 | 6 | 1 | 0 | 0 | 0
148 | 120/121 | Art Classroom | 379 | 25 |  | 956 | 21 | 21 | 0 | 0 | 0
149 | 120A | Art Storage Room | 50 | 3 |  | 61 | 1 | 1 | 0 | 0 | 0
150 | 121/123 | Music Classroom | 200 | 13 |  | 1083 | 24 | 13 | 0 | 0 | 0
152 | 123A | Music Studio | 53 | 3 |  | 237 | 5 | 3 | 0 | 0 | 0
161 | - | Lobby | 208 | 13 |  | 475 | 10 | 10 | 0 | 0 | 0
162 | 122 | Gym | 4453 | 296 |  | 5236 | 119 | 119 | 0 | 0 | 0
163 | 125A | Office | 55 | 3 |  | 161 | 3 | 3 | 0 | 0 | 0
164 | 125B | Storage | 35 | 2 |  | 141 | 3 | 2 | 0 | 0 | 0
167 | - | Small Group | 1288 | 85 |  | 963 | 21 | 21 | 0 | 0 | 0
168 | - | Open Space/Corridor | 196 | 13 |  | 324 | 7 | 7 | 0 | 0 | 0
201 | - | Corridor | 472 | 31 |  | 563 | 12 | 12 | 0 | 0 | 0
212 | 200A | Conselor's Office | 22 | 1 |  | 104 | 2 | 1 | 0 | 0 | 0
214 | 200B | Principal's Office | 33 | 2 |  | 166 | 3 | 2 | 0 | 0 | 0
216 | 200C | Conference Room | 65 | 4 |  | 189 | 4 | 4 | 0 | 0 | 0
217 | 200D | Small Meeting Room | 20 | 1 |  | 96 | 2 | 1 | 0 | 0 | 0
218 | 200E | Small Meeting Room | 20 | 1 |  | 96 | 2 | 1 | 0 | 0 | 0
219 | 200F | Records | 8 | 0 |  | 180 | 4 | 0 | 0 | 0 | 0
202 | 201 | Nurse's Suite | 23 | 1 |  | 221 | 5 | 1 | 0 | 0 | 0
203 | 201D | Exam Room | 12 | 0 |  | 81 | 1 | 0 | 0 | 0 | 0
204 | 201A | Exam Room | 13 | 0 |  | 102 | 2 | 0 | 0 | 0 | 0
205 | 200 | Waiting Area | 161 | 10 |  | 359 | 8 | 8 | 0 | 0 | 0
213 | 201E | Building Storage | 44 | 2 |  | 494 | 11 | 2 | 0 | 0 | 0
215 | - | Open Office | 121 | 8 |  | 1263 | 28 | 8 | 0 | 0 | 0
220 | - | Corridor | 11 | 0 |  | 266 | 6 | 0 | 0 | 0 | 0
221 | 201H | Faculty Lounge | 126 | 8 |  | 419 | 9 | 8 | 0 | 0 | 0
226 | - | Corridor | 233 | 15 |  | 3096 | 70 | 15 | 0 | 0 | 0
227 | 202 | Classroom | 421 | 28 |  | 858 | 19 | 19 | 0 | 0 | 0
228 | 203 | Classroom | 446 | 29 |  | 860 | 19 | 19 | 0 | 0 | 0
229 | 204 | Classroom | 427 | 28 |  | 856 | 19 | 19 | 0 | 0 | 0
230 | 205 | Classroom | 416 | 27 |  | 858 | 19 | 19 | 0 | 0 | 0
231 | 206 | Classroom | 426 | 28 |  | 858 | 19 | 19 | 0 | 0 | 0
232 | 207 | Classroom | 417 | 27 |  | 860 | 19 | 19 | 0 | 0 | 0
233 | 208 | Special Education Classroom | 195 | 13 |  | 377 | 8 | 8 | 0 | 0 | 0
234 | 209 | Classroom | 438 | 29 |  | 860 | 19 | 19 | 0 | 0 | 0
235 | 210 | Art Classroom | 494 | 32 |  | 1235 | 28 | 28 | 0 | 0 | 0
237 | 210A | Storage | 18 | 1 |  | 48 | 1 | 1 | 0 | 0 | 0
239 | 210B | Storage | 33 | 2 |  | 113 | 2 | 2 | 0 | 0 | 0
236 | 211 | Classroom | 435 | 29 |  | 860 | 19 | 19 | 0 | 0 | 0
241 | 212 | Classroom | 450 | 30 |  | 852 | 19 | 19 | 0 | 0 | 0
238 | 213 | Classroom | 425 | 28 |  | 851 | 19 | 19 | 0 | 0 | 0
243 | 214 | Classroom | 447 | 29 |  | 859 | 19 | 19 | 0 | 0 | 0
240 | 215 | Classroom | 456 | 30 |  | 852 | 19 | 19 | 0 | 0 | 0
244 | 216 | Small Group Classroom | 119 | 7 |  | 388 | 8 | 7 | 0 | 0 | 0
242 | 217 | Pre-Eng. Classroom | 417 | 27 |  | 860 | 19 | 19 | 0 | 0 | 0
245 | 219 | Makerspace | 677 | 45 |  | 165 | 3 | 3 | 0 | 0 | 0
248 | 220 | Science Classroom | 1385 | 92 |  | 1289 | 29 | 29 | 0 | 0 | 0
249 | 220B | Prep Room | 739 | 49 |  | 403 | 9 | 9 | 0 | 0 | 0
250 | 221 | Classroom | 1356 | 90 |  | 1285 | 29 | 29 | 0 | 0 | 0
256 | 221C | Storage | 0 | 0 |  | 50 | 1 | 0 | 0 | 0 | 0
253 | 221C | Room | 489 | 32 |  | 632 | 14 | 14 | 0 | 0 | 0
254 | 225 | Office | 50 | 3 |  | 173 | 3 | 3 | 0 | 0 | 0
266 | - | West Hallway | 208 | 13 |  | 779 | 17 | 13 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-31 | [7 empty] | 0 | 0 | 0
School: | Anna B. Pratt Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Capital | Devine ABR | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
106 | Classroom / Swing Space | 597 | 39 |  | 936 | 21 | 21 | Univent | 7488 | 4.7837 | 2
109 | Classroom | 651 | 43 |  | 936 | 21 | 21 | Univent | 7488 | 5.2163 | 2
110 | Classroom | 327 | 21 |  | 936 | 21 | 21 | Univent | 7488 | 2.6202 | 1
111 | Classroom | 320 | 21 |  | 936 | 21 | 21 | Univent | 7488 | 2.5641 | 1
112 | Classroom | 393 | 26 |  | 936 | 21 | 21 | Univent | 7488 | 3.149 | 1
113 | Special Education | 453 | 30 |  | 936 | 21 | 21 | Univent | 7488 | 3.6298 | 1
114 | Classroom | 442 | 29 |  | 936 | 21 | 21 | Univent | 7488 | 3.5417 | 1
201 | Classroom / Swing Space | 473 | 31 |  | 936 | 21 | 21 | Univent | 7488 | 3.7901 | 1
200 / 202 | Library | 776 | 51 |  | 1848 | 42 | 42 | Univent | 14784 | 3.1494 | 1
208 | Classroom | 367 | 24 |  | 936 | 21 | 21 | Univent | 7488 | 2.9407 | 1
209 | Classroom | 489 | 32 |  | 936 | 21 | 21 | Univent | 7488 | 3.9183 | 1
210 | Technology Classroom | 422 | 28 |  | 936 | 21 | 21 | Univent | 7488 | 3.3814 | 1
211 | Classroom | 313 | 20 |  | 936 | 21 | 20 | Univent | 7488 | 2.508 | 1
212 | Classroom | 526 | 35 |  | 936 | 21 | 21 | Univent | 7488 | 4.2147 | 2
213 | Classroom | 468 | 31 |  | 936 | 21 | 21 | Univent | 7488 | 3.75 | 1
214 | Data Room | 433 | 28 |  | 399 | 9 | 9 | Univent | 3192 | 8.1391 | 2
301 | Music Room | 327 | 21 |  | 936 | 21 | 21 | Univent | 7488 | 2.6202 | 1
302 | Classroom | 311 | 20 |  | 936 | 21 | 20 | Univent | 7488 | 2.492 | 1
308 | Classroom | 386 | 25 |  | 936 | 21 | 21 | Univent | 7488 | 3.0929 | 1
309 | Special Education | 459 | 30 |  | 936 | 21 | 21 | Univent | 7488 | 3.6779 | 1
310 | Special Education | 447 | 29 |  | 936 | 21 | 21 | Univent | 7488 | 3.5817 | 1
311 | Classroom | 430 | 28 |  | 936 | 21 | 21 | Univent | 7488 | 3.4455 | 1
312 | Classroom | 615 | 41 |  | 936 | 21 | 21 | Univent | 7488 | 4.9279 | 2
313 | Classroom | 330 | 22 |  | 936 | 21 | 21 | Univent | 7488 | 2.6442 | 1
314 | Classroom | 522 | 34 |  | 936 | 21 | 21 | Univent | 7488 | 4.1827 | 2
315 | Staff Room | 361 | 24 |  | 399 | 9 | 9 | Univent | 3192 | 6.7857 | 2
- | Main Office |  | 0 | Yes | 352 | 8 | 8 |  | 2816 | 0 | 0
- | Principal Office |  | 0 | Yes | 228 | 5 | 5 |  | 1824 | 0 | 0
- | AS Office |  | 0 | Yes | 192 | 4 | 4 |  | 1536 | 0 | 0
- | Nurses Office |  | 0 | Yes | 156 | 3 | 3 |  | 1248 | 0 | 0
- | Climate Office |  | 0 | Yes | 156 | 3 | 3 |  | 1248 | 0 | 0
- | Counselors Office |  | 0 | Yes | 156 | 3 | 3 |  | 1248 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Prince Hall Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Retest | Gymnasium | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
1 | Classroom | 380 | 25 |  | 1200 | 27 | 25 | Univent | 9600 | 2.375 | 1
2 | Classroom | 321 | 21 |  | 1200 | 27 | 21 | Univent | 9600 | 2.0063 | 1
3 | Classroom | 387 | 25 |  | 1200 | 27 | 25 | Univent | 9600 | 2.4188 | 1
4 | Classroom | 304 | 20 |  | 1200 | 27 | 20 | Univent | 9600 | 1.9 | 1
5 | Classroom | 313 | 20 |  | 900 | 20 | 20 | Univent | 7200 | 2.6083 | 1
6 | Classroom | 268 | 17 | Yes | 900 | 20 | 20 | Univent | 7200 | 2.2333 | 1
7 | Classroom | 351 | 23 |  | 836 | 19 | 19 | Univent | 6688 | 3.1489 | 1
8 | Classroom | 334 | 22 |  | 874 | 19 | 19 | Univent | 6992 | 2.8661 | 1
9 | Classroom | 235 | 15 | Yes | 1050 | 23 | 23 | Univent | 8400 | 1.6786 | 1
10 | Classroom | 375 | 25 |  | 888 | 20 | 20 | Univent | 7104 | 3.1672 | 1
11 | Classroom | 242 | 16 | Yes | 1066 | 24 | 24 | Univent | 8528 | 1.7026 | 1
12 | Classroom | 234 | 15 | Yes | 1134 | 25 | 25 | Univent | 9072 | 1.5476 | 1
13 | Classroom | 227 | 15 | Yes | 1100 | 25 | 25 | Univent | 8800 | 1.5477 | 1
103 | Classroom | 601 | 40 |  | 1280 | 29 | 29 | Univent | 10240 | 3.5215 | 1
104 | Classroom | 696 | 46 |  | 1280 | 29 | 29 | Univent | 10240 | 4.0781 | 2
105 | Classroom | 664 | 44 |  | 1360 | 30 | 30 | Univent | 10880 | 3.6618 | 1
106 | Classroom | 739 | 49 |  | 1280 | 29 | 29 | Univent | 10240 | 4.3301 | 2
112 | Classroom |  | 0 | Yes | 1360 | 30 | 30 |  | 10880 | 0 | 0
116 | Classroom | 279 | 18 |  | 400 | 9 | 9 | Univent | 3200 | 5.2313 | 2
117 | Classroom | 322 | 21 |  | 700 | 15 | 15 | Univent | 5600 | 3.45 | 1
201 | Classroom | 418 | 27 |  | 1200 | 27 | 27 | Univent | 9600 | 2.6125 | 1
202 | Classroom | 292 | 19 | Yes | 1200 | 27 | 27 | Univent | 9600 | 1.825 | 1
203 | Classroom | 311 | 20 |  | 1200 | 27 | 20 | Univent | 9600 | 1.9438 | 1
204 | Classroom | 259 | 17 | Yes | 1200 | 27 | 27 | Univent | 9600 | 1.6187 | 1
205 | Classroom | 377 | 25 |  | 900 | 20 | 20 | Univent | 7200 | 3.1417 | 1
206 | Classroom | 338 | 22 |  | 900 | 20 | 20 | Univent | 7200 | 2.8167 | 1
207 | Classroom | 238 | 15 |  | 836 | 19 | 15 | Univent | 6688 | 2.1352 | 1
208 | Classroom | 312 | 20 |  | 874 | 19 | 19 | Univent | 6992 | 2.6773 | 1
209 | Classroom | 244 | 16 | Yes | 1050 | 23 | 23 | Univent | 8400 | 1.7429 | 1
210 | Classroom | 240 | 16 |  | 888 | 20 | 16 | Univent | 7104 | 2.027 | 1
211 | Classroom | 263 | 17 |  | 1066 | 24 | 17 | Univent | 8528 | 1.8504 | 1
212 | Classroom | 332 | 22 |  | 1170 | 26 | 22 | Univent | 9360 | 2.1282 | 1
213 | Classroom | 614 | 40 |  | 988 | 22 | 22 | Univent | 7904 | 4.6609 | 2
- | AUDITORIUM | 1185 | 79 |  | 3363 | 76 | 76 | Air Handling Unit | 26904 | 2.6427 | 1
- | Admin. Main Office | 56 | 3 |  | 255 | 5 | 3 | Univent | 2040 | 1.6471 | 1
- | Admin. Office | 28 | 1 |  | 126 | 2 | 1 | Univent | 1008 | 1.6667 | 1
- | Main Office | 301 | 20 |  | 720 | 16 | 16 | Univent | 5760 | 3.1354 | 1
- | Principal's Office |  | 0 | Yes | 255 | 5 | 5 |  | 2040 | 0 | 0
- | Copy Room Office | 16 | 1 |  | 98 | 2 | 1 | Univent | 784 | 1.2245 | 1
- | Counselor's Office | 107 | 7 |  | 416 | 9 | 7 | Univent | 3328 | 1.9291 | 1
- | Computer Room Classroom | 380 | 25 |  | 1600 | 36 | 25 | Univent | 12800 | 1.7812 | 1
- | IMC Classroom | 1021 | 68 |  | 4335 | 98 | 68 | Univent | 34680 | 1.7664 | 1
- | Gym | 0 | 0 |  | 4800 | 109 | 0 | Air Handling Unit | 38400 | 0 | 0
- | Gym Locker Rooms | 335 | 22 |  | 403 | 9 | 9 | Air Handling Unit | 3224 | 6.2345 | 2
- | Main Entrance | 68 | 4 |  | 150 | 3 | 3 | Univent | 1200 | 3.4 | 1
- | Multi-Purpose/Cafe | 2016 | 134 |  | 2760 | 62 | 62 | Air Handling Unit | 22080 | 5.4783 | 2
- | Nurse's Office 1 | 50 | 3 |  | 90 | 2 | 2 | Univent | 720 | 4.1667 | 2
- | Nurse's Office 2 | 40 | 2 |  | 110 | 2 | 2 | Univent | 880 | 2.7273 | 1
- | Nurse's Office | 71 | 4 | Yes | 160 | 3 | 3 | Univent | 1280 | 3.3281 | 1
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | A. Philip Randolph Career and Technical High School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
20 | Classroom | 1172 | 78 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
21 | Classroom | 1124 | 74 |  | 600 | 13 | 13 | Air Coil Unit | 4800 | 14.05 | 3
23 | Classroom | 1177 | 78 |  | 720 | 16 | 16 | Air Coil Unit | 5760 | 12.2604 | 3
24 | Classroom | 889 | 59 |  | 792 | 18 | 18 | Air Coil Unit | 6336 | 8.4186 | 2
36 | Classroom | 93 | 6 |  |  | 0 | 0 | Rooftop Unit | 0 | 0 | 0
37 | Classroom | 176 | 11 |  | 704 | 16 | 11 | Rooftop Unit | 5632 | 1.875 | 1
38 | DENTAL SHOP | 236 | 15 |  | 1596 | 36 | 15 | Rooftop Unit | 12768 | 1.109 | 1
38 | DENTAL IMAGE ROOM | 8 | 0 |  |  | 0 | 0 | Rooftop Unit | 0 | 0 | 0
38 | DENTAL X-RAY ROOM | 12 | 0 |  |  | 0 | 0 | Rooftop Unit | 0 | 0 | 0
39 | Classroom | 73 | 4 |  |  | 0 | 0 | Rooftop Unit | 0 | 0 | 0
50 | Art Room | 694 | 46 |  | 1008 | 22 | 22 | Air Coil Unit | 8064 | 5.1637 | 2
51 | Classroom | 199 | 13 |  | 510 | 11 | 11 | Air Coil Unit | 4080 | 2.9265 | 1
52 | Classroom | 435 | 29 |  | 420 | 9 | 9 | Air Coil Unit | 3360 | 7.7679 | 2
53 | Classroom | 483 | 32 |  | 612 | 13 | 13 | Air Coil Unit | 4896 | 5.9191 | 2
54 | Classroom | 784 | 52 |  | 798 | 18 | 18 | Air Coil Unit | 6384 | 7.3684 | 2
55 | Classroom | 149 | 9 |  | 660 | 15 | 9 | Air Coil Unit | 5280 | 1.6932 | 1
56 | Classroom | 570 | 38 |  | 1190 | 27 | 27 | Air Coil Unit | 9520 | 3.5924 | 1
57 | Classroom | 505 | 33 |  | 522 | 11 | 11 | Air Coil Unit | 4176 | 7.2557 | 2
71 | Room | 262 | 17 |  | 480 | 10 | 10 | Air Coil Unit | 3840 | 4.0938 | 2
72 | Room | 289 | 19 |  | 510 | 11 | 11 | Air Coil Unit | 4080 | 4.25 | 2
73 | Classroom | 0 | 0 |  | 616 | 14 | 0 | Air Coil Unit | 4928 | 0 | 0
74 | Room | 0 | 0 |  | 572 | 13 | 0 | Air Coil Unit | 4576 | 0 | 0
75 | Classroom | 0 | 0 |  | 660 | 15 | 0 | Air Coil Unit | 5280 | 0 | 0
76 | Classroom | 0 | 0 |  | 600 | 13 | 0 | Air Coil Unit | 4800 | 0 | 0
94 | Room | 88 | 5 |  | 72 | 1 | 1 | Air Coil Unit | 576 | 9.1667 | 2
100 | Classroom | 197 | 13 |  | 396 | 9 | 9 | Air Coil Unit | 3168 | 3.7311 | 1
- | Automotive | 80 | 5 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
- | AV storage | 96 | 6 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
- | BEHAVIORAL THERAPIST OFFICE | 26 | 1 |  |  | 0 | 0 | Rooftop Unit | 0 | 0 | 0
- | Boys Bathroom | 0 | 0 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
- | Break Room | 168 | 11 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
- | CAFETERIA | 2027 | 135 |  | 3828 | 87 | 87 | Rooftop Unit | 30624 | 3.9714 | 1
- | Cafeteria | 2027 | 135 |  | 704 | 16 | 16 | Air Coil Unit | 5632 | 21.5945 | 3
- | Classrooms | 392 | 26 |  | 600 | 13 | 13 | Air Coil Unit | 4800 | 4.9 | 2
- | Classrooms | 5734 | 382 |  | 720 | 16 | 16 | Air Coil Unit | 5760 | 59.7292 | 5
- | Classrooms | 4521 | 301 |  | 792 | 18 | 18 | Air Coil Unit | 6336 | 42.8125 | 4
- | Classrooms | 0 | 0 |  | 572 | 13 | 0 | Air Coil Unit | 4576 | 0 | 0
- | COUNSELORS OFFICE | 19 | 1 |  |  | 0 | 0 | Rooftop Unit | 0 | 0 | 0
- | Engineers Office | 238 | 15 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
- | Girls Bathroom | 0 | 0 |  | 200 | 4 | 0 | Air Coil Unit | 1600 | 0 | 0
- | Hallway | 245 | 16 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
- | IMC side area | 657 | 43 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
- | IMC area | 118 | 7 |  | 1664 | 37 | 7 | Air Coil Unit | 13312 | 0.53185 | 0
- | INSPECTORS OFFICE | 0 | 0 |  |  | 0 | 0 | Rooftop Unit | 0 | 0 | 0
- | IT ROOM | 40 | 2 |  |  | 0 | 0 | Rooftop Unit | 0 | 0 | 0
- | kitchen | 1766 | 117 |  | 722 | 16 | 16 | Air Coil Unit | 5776 | 18.3449 | 3
- | Kitchen | 3575 | 238 |  | 722 | 16 | 16 | Air Coil Unit | 5776 | 37.1364 | 4
- | Kitchen Dining | 93 | 6 |  | 252 | 5 | 5 | Air Coil Unit | 2016 | 2.7679 | 1
- | Library | 29 | 1 |  | 1664 | 37 | 1 | Air Coil Unit | 13312 | 0.13071 | 0
- | MAIL ROOM | 50 | 3 |  | 384 | 8 | 3 | Rooftop Unit | 3072 | 0.97656 | 0
- | MAIN OFFICE | 113 | 7 |  | 134 | 3 | 3 | Rooftop Unit | 1072 | 6.3246 | 2
- | CONFERENCE ROOM | 23 | 1 |  | 247 | 5 | 1 | Rooftop Unit | 1976 | 0.69838 | 0
Main office, classrooms | Main office, classrooms | 1328 | 88 |  | 285 | 6 | 6 | Air Coil Unit | 2280 | 34.9474 | 4
- | Ms. SMALLEY OFFICE | 7 | 0 |  | 120 | 2 | 0 | Rooftop Unit | 960 | 0.4375 | 0
- | NURSES OFFICE | 156 | 10 |  | 196 | 4 | 4 | Rooftop Unit | 1568 | 5.9694 | 2
- | office next to electrical room | 136 | 9 |  | 140 | 3 | 3 | Air Coil Unit | 1120 | 7.2857 | 2
office diffuser s1 | office | 223 | 14 |  | 140 | 3 | 3 | Air Coil Unit | 1120 | 11.9464 | 3
- | kitchen office | 21 | 1 |  | 320 | 7 | 1 | Air Coil Unit | 2560 | 0.49219 | 0
- | VP office | 0 | 0 |  | 130 | 2 | 0 | Air Coil Unit | 1040 | 0 | 0
office Diffuser S6 | office | 0 | 0 |  | 192 | 4 | 0 | Air Coil Unit | 1536 | 0 | 0
office Diffuser S1 | office | 0 | 0 |  | 320 | 7 | 0 | Air Coil Unit | 2560 | 0 | 0
office diffuser s18 | office | 78 | 5 |  | 120 | 2 | 2 | Air Coil Unit | 960 | 4.875 | 2
office diffuser s17 | office | 84 | 5 |  | 308 | 7 | 5 | Air Coil Unit | 2464 | 2.0455 | 1
office diffuser s16 | office | 108 | 7 |  | 280 | 6 | 6 | Air Coil Unit | 2240 | 2.8929 | 1
OFFICE IN BACK OF MAIN OFFICE | OFFICE IN BACK OF MAIN OFFICE | 0 | 0 |  | 110 | 2 | 0 | Rooftop Unit | 880 | 0 | 0
OFFICE NEXT TO RM 39 | OFFICE NEXT TO RM 39 | 23 | 1 |  | 216 | 4 | 1 | Rooftop Unit | 1728 | 0.79861 | 0
- | Paint shop | 0 | 0 |  | 320 | 7 | 0 | H2-7 | 2560 | 0 | 0
- | Paint shop | 0 | 0 |  |  | 0 | 0 | H2-8 | 0 | 0 | 0
PRINCIPLE OFFICE | PRINCIPLE OFFICE | 49 | 3 |  | 16 | 0 | 0 | Rooftop Unit | 128 | 22.9688 | 3
security | office diffuser s4 | 180 | 12 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
- | Shop area | 408 | 27 |  |  | 0 | 0 | H2-5 | 0 | 0 | 0
- | Shop area | 1346 | 89 |  |  | 0 | 0 | H1-4 | 0 | 0 | 0
- | Shop area | 591 | 39 |  |  | 0 | 0 | H1-3 | 0 | 0 | 0
- | Shop area | 450 | 30 |  |  | 0 | 0 | H4-14 | 0 | 0 | 0
- | Shop area | 0 | 0 |  |  | 0 | 0 | H4-13 | 0 | 0 | 0
- | Shop area | 0 | 0 |  |  | 0 | 0 | H4-12 | 0 | 0 | 0
- | Shop area | 0 | 0 |  |  | 0 | 0 | H3-10 | 0 | 0 | 0
- | Shop area | 0 | 0 |  |  | 0 | 0 | H3-11 | 0 | 0 | 0
- | Shop Classrooms | 2065 | 137 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
- | SPEECH THERAPIST NEXT TO PRINCIPLE OFFICE | 60 | 4 |  |  | 0 | 0 | Rooftop Unit | 0 | 0 | 0
- | SPEECH THERAPIST OFFICE | 20 | 1 |  |  | 0 | 0 | Rooftop Unit | 0 | 0 | 0
storage diffuser s11 | storage | 53 | 3 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
storage diffuser s10 | storage | 192 | 12 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
storage diffuser s9 | storage | 170 | 11 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
storage diffuser s2 | storage | 120 | 8 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
storage diffuser s1 | storage | 115 | 7 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
storage diffuser S19 | storage | 0 | 0 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
storage diffuser S17 | storage | 0 | 0 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
storage diffuser S16 | storage | 0 | 0 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
Storage Diffuser S5 | Storage | 0 | 0 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
storage diffuser s6 | storage | 76 | 5 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
storage diffuser s4 | storage | 64 | 4 |  |  | 0 | 0 | Air Coil Unit | 0 | 0 | 0
- | STORAGE ROOM IN MAIN OFFICE | 16 | 1 |  |  | 0 | 0 | Rooftop Unit | 0 | 0 | 0
teacher lounge diffuser S19 | teachers lounge | 37 | 2 |  | 572 | 13 | 2 | Air Coil Unit | 4576 | 0.48514 | 0
- | TOM MCLAUGHLIN OFFICE | 29 | 1 |  | 572 | 13 | 1 | Rooftop Unit | 4576 | 0.38024 | 0
- | vending machine shop | 0 | 0 |  |  | 0 | 0 | H1-1 | 0 | 0 | 0
- | welding shop | 0 | 0 |  |  | 0 | 0 | H2-9 | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-07 | [7 empty] | 0 | 0 | 0
School: | Rhawnhurst Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Part 2 | Part 3 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 301 | 20 |  | 1485 | 33 | 20 | Univent | 11880 | 1.5202 | 1
101 | Classroom | 341 | 22 |  | 1056 | 24 | 22 | Univent | 8448 | 2.4219 | 1
102 | Classroom | 296 | 19 |  | 1056 | 24 | 19 | Univent | 8448 | 2.1023 | 1
102B | Office |  | 0 | Yes | 110 | 2 | 2 | Univent | 880 | 0 | 0
103 | Classroom | 297 | 19 |  | 1056 | 24 | 19 | Univent | 8448 | 2.1094 | 1
104 | Classroom | 335 | 22 |  | 1056 | 24 | 22 | Univent | 8448 | 2.3793 | 1
105 | Classroom | 307 | 20 |  | 1073 | 24 | 20 | Univent | 8584 | 2.1459 | 1
106 | Classroom | 624 | 41 |  | 1020 | 23 | 23 | Univent | 8160 | 4.5882 | 2
107 | Classroom | 321 | 21 |  | 1056 | 24 | 21 | Univent | 8448 | 2.2798 | 1
108 | Classroom | 313 | 20 |  | 1056 | 24 | 20 | Univent | 8448 | 2.223 | 1
109 | Classroom | 302 | 20 |  | 1056 | 24 | 20 | Univent | 8448 | 2.1449 | 1
110 | Classroom | 301 | 20 |  | 1056 | 24 | 20 | Univent | 8448 | 2.1378 | 1
200 | Classroom | 520 | 34 |  | 1056 | 24 | 24 | Univent | 8448 | 3.6932 | 1
201 | Classroom | 259 | 17 |  | 1056 | 24 | 17 | Univent | 8448 | 1.8395 | 1
202 | Classroom | 306 | 20 |  | 1056 | 24 | 20 | Univent | 8448 | 2.1733 | 1
203 | Classroom | 586 | 39 |  | 1056 | 24 | 24 | Univent | 8448 | 4.1619 | 2
203A | Office |  | 0 | Yes | 275 | 6 | 6 | Univent | 2200 | 0 | 0
203B | Office |  | 0 | Yes | 198 | 4 | 4 | Univent | 1584 | 0 | 0
204 | Classroom | 452 | 30 |  | 1056 | 24 | 24 | Univent | 8448 | 3.2102 | 1
Annex 301 | Classroom | 246 | 16 |  | 792 | 18 | 16 | Univent | 6336 | 2.3295 | 1
Annex 302 | Classroom | 291 | 19 |  | 792 | 18 | 18 | Univent | 6336 | 2.7557 | 1
Annex 303 | Classroom | 303 | 20 |  | 792 | 18 | 18 | Univent | 6336 | 2.8693 | 1
Annex 304 | Classroom | 198 | 13 | Yes | 792 | 18 | 18 | Univent | 6336 | 1.875 | 1
Annex 305 | Classroom | 248 | 16 |  | 792 | 18 | 16 | Univent | 6336 | 2.3485 | 1
Annex 306 | Classroom | 216 | 14 | Yes | 792 | 18 | 18 | Univent | 6336 | 2.0455 | 1
- | Main Office |  | 0 | Yes | 240 | 5 | 5 | Univent | 1920 | 0 | 0
Principal | Office |  | 0 | Yes | 264 | 6 | 6 | Univent | 2112 | 0 | 0
- | Nurses Office |  | 0 | Yes | 460 | 10 | 10 | Univent | 3680 | 0 | 0
- | Special Education Office |  | 0 | Yes | 360 | 8 | 8 | Univent | 2880 | 0 | 0
- | Counselor Office |  | 0 | Yes | 241 | 5 | 5 | Univent | 1928 | 0 | 0
- | Auditorium | 2049 | 136 |  | 3431 | 77 | 77 | Air Handling Unit | 27448 | 4.479 | 2
- | Cafeteria | 362 | 24 |  | 2814 | 63 | 24 | Univent | 22512 | 0.96482 | 0
- | Gym | 116 | 7 |  | 3969 | 90 | 7 | Air Handling Unit | 31752 | 0.2192 | 0
- | Library | 140 | 9 | Yes | 1134 | 25 | 25 | Univent | 9072 | 0.92593 | 0
- | Trailer | 286 | 19 |  | 649 | 14 | 14 | Air Handling Unit | 5192 | 3.3051 | 1
A1 | Annex | 75 | 5 |  | 792 | 18 | 5 | Univent | 6336 | 0.71023 | 0
A2 | Annex | 95 | 6 |  | 792 | 18 | 6 | Univent | 6336 | 0.89962 | 0
A3 | Annex | 54 | 3 |  | 792 | 18 | 3 | Univent | 6336 | 0.51136 | 0
A4 | Annex | 62 | 4 |  | 792 | 18 | 4 | Univent | 6336 | 0.58712 | 0
A5 | Annex | 63 | 4 |  | 792 | 18 | 4 | Univent | 6336 | 0.59659 | 0
A6 | Annex | 70 | 4 |  | 792 | 18 | 4 | Univent | 6336 | 0.66288 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-15 | [7 empty] | 0 | 0 | 0
School: | James Rhoads Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 122 | 8 |  | 552 | 12 | 8 | Univent | 4416 | 1.6576 | 1
102 | Classroom | 87 | 5 | Yes | 968 | 22 | 22 | Univent | 7744 | 0.67407 | 0
104 | Classroom | 136 | 9 | Yes | 968 | 22 | 22 | Univent | 7744 | 1.0537 | 1
200 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0
201 | Classroom | 190 | 12 | Yes | 805 | 18 | 18 | Univent | 6440 | 1.7702 | 1
202 | Classroom | 237 | 15 |  | 805 | 18 | 15 | Univent | 6440 | 2.2081 | 1
203 | Classroom | 212 | 14 | Yes | 805 | 18 | 18 | Univent | 6440 | 1.9752 | 1
204 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent | 6440 | 0 | 0
205 | Classroom | 162 | 10 | Yes | 805 | 18 | 18 | Univent | 6440 | 1.5093 | 1
206 | Classroom | 201 | 13 | Yes | 805 | 18 | 18 | Univent | 6440 | 1.8727 | 1
207 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0
208 | Classroom | 236 | 15 |  | 805 | 18 | 15 | Univent | 6440 | 2.1988 | 1
209 | Classroom | 174 | 11 | Yes | 805 | 18 | 18 | Univent | 6440 | 1.6211 | 1
210 | Classroom | 212 | 14 |  | 805 | 18 | 14 | Univent | 6440 | 1.9752 | 1
300 | Classroom | 318 | 21 |  | 805 | 18 | 18 | Univent | 6440 | 2.9627 | 1
301 | Classroom | 202 | 13 |  | 805 | 18 | 13 | Univent | 6440 | 1.882 | 1
302 | Classroom | 197 | 13 |  | 805 | 18 | 13 | Univent | 6440 | 1.8354 | 1
303 | Classroom | 300 | 20 |  | 805 | 18 | 18 | Univent | 6440 | 2.795 | 1
304 | Classroom | 203 | 13 |  | 805 | 18 | 13 | Univent | 6440 | 1.8913 | 1
305 | Classroom | 205 | 13 |  | 805 | 18 | 13 | Univent | 6440 | 1.9099 | 1
306 | Classroom | 169 | 11 |  | 805 | 18 | 11 | Univent | 6440 | 1.5745 | 1
307 | Classroom | 233 | 15 |  | 805 | 18 | 15 | Univent | 6440 | 2.1708 | 1
308 | Classroom | 201 | 13 |  | 805 | 18 | 13 | Univent | 6440 | 1.8727 | 1
309 | Classroom | 174 | 11 |  | 805 | 18 | 11 | Univent | 6440 | 1.6211 | 1
310 | Classroom | 342 | 22 |  | 805 | 18 | 18 | Univent | 6440 | 3.1863 | 1
400 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0
401 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0
402 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0
403 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0
404 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent | 6440 | 0 | 0
405 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent | 6440 | 0 | 0
406 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent | 6440 | 0 | 0
407 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent | 6440 | 0 | 0
408 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0
409 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent | 6440 | 0 | 0
410 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0
- | Main Office |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | 0 | 0
- | Principal Office |  | 0 | Yes | 300 | 6 | 6 |  | 2400 | 0 | 0
- | Nurse Office |  | 0 | Yes | 120 | 2 | 2 |  | 960 | 0 | 0
- | Auditorium | 0 | 0 |  | 1800 | 40 | 0 | Air Handling Unit | 14400 | 0 | 0
- | Café/Gym | 0 | 0 |  | 6480 | 147 | 0 | Air Handling Unit | 51840 | 0 | 0
- | IMC | 0 | 0 |  | 897 | 20 | 0 | Univent | 7176 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-08 | [7 empty] | 0 | 0 | 0
School: | E. Washington Rhodes Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | 1ST/2ND FLR A&B POD AREAS | 0 | 0 |  | 1829 | 41 | 0 | Air Handling Unit | 14632 | 0 | 0
- | 1ST/2ND FLR C&D POD AREAS | 0 | 0 |  | 1829 | 41 | 0 | Air Handling Unit | 14632 | 0 | 0
A1 | CLASSROOM | 365 | 24 |  | 850 | 19 | 19 | Univent | 6800 | 3.2206 | 1
A2 | CLASSROOM | 326 | 21 |  | 850 | 19 | 19 | Univent | 6800 | 2.8765 | 1
A3 | CLASSROOM | 0 | 0 |  | 850 | 19 | 0 | Univent | 6800 | 0 | 0
A4 | CLASSROOM | 0 | 0 |  | 1085 | 24 | 0 | Univent | 8680 | 0 | 0
A5 | CLASSROOM | 289 | 19 |  | 720 | 16 | 16 | Univent | 5760 | 3.0104 | 1
A6 | CLASSROOM | 308 | 20 |  | 890 | 20 | 20 | Univent | 7120 | 2.5955 | 1
A7 | CLASSROOM | 0 | 0 |  | 0 | 0 | 0 | Univent | 0 | 0 | 0
A101 | CLASSROOM | 283 | 18 |  | 850 | 19 | 18 | Univent | 6800 | 2.4971 | 1
A102 | CLASSROOM | 369 | 24 |  | 850 | 19 | 19 | Univent | 6800 | 3.2559 | 1
A103 | CLASSROOM | 279 | 18 |  | 816 | 18 | 18 | Univent | 6528 | 2.5643 | 1
A104 | CLASSROOM | 238 | 15 |  | 1120 | 25 | 15 | Univent | 8960 | 1.5938 | 1
A105 | CLASSROOM | 296 | 19 |  | 744 | 16 | 16 | Univent | 5952 | 2.9839 | 1
A106 | CLASSROOM | 227 | 15 |  | 1100 | 25 | 15 | Univent | 8800 | 1.5477 | 1
B1 | CLASSROOM | 275 | 18 |  | 850 | 19 | 18 | Univent | 6800 | 2.4265 | 1
B2 | CLASSROOM | 308 | 20 |  | 850 | 19 | 19 | Univent | 6800 | 2.7176 | 1
B3 | CLASSROOM | 338 | 22 |  | 850 | 19 | 19 | Univent | 6800 | 2.9824 | 1
B4 | CLASSROOM | 300 | 20 |  | 1085 | 24 | 20 | Univent | 8680 | 2.0737 | 1
B5 | CLASSROOM | 233 | 15 |  | 720 | 16 | 15 | Univent | 5760 | 2.4271 | 1
B6 | CLASSROOM | 296 | 19 |  | 890 | 20 | 19 | Univent | 7120 | 2.4944 | 1
B101 | CLASSROOM | 237 | 15 |  | 850 | 19 | 15 | Univent | 6800 | 2.0912 | 1
B102 | CLASSROOM | 325 | 21 |  | 850 | 19 | 19 | Univent | 6800 | 2.8676 | 1
B103 | CLASSROOM | 275 | 18 |  | 816 | 18 | 18 | Univent | 6528 | 2.5276 | 1
B104 | CLASSROOM | 307 | 20 |  | 1120 | 25 | 20 | Univent | 8960 | 2.0558 | 1
B105 | CLASSROOM | 301 | 20 |  | 744 | 16 | 16 | Univent | 5952 | 3.0343 | 1
B106 | CLASSROOM | 297 | 19 |  | 1100 | 25 | 19 | Univent | 8800 | 2.025 | 1
C1 | CLASSROOM | 297 | 19 |  | 850 | 19 | 19 | Univent | 6800 | 2.6206 | 1
C2 | CLASSROOM | 0 | 0 | Yes | 850 | 19 | 19 | Univent | 6800 | 0 | 0
C3 | CLASSROOM | 0 | 0 | Yes | 850 | 19 | 19 | Univent | 6800 | 0 | 0
C4 | CLASSROOM | 367 | 24 |  | 1085 | 24 | 24 | Univent | 8680 | 2.5369 | 1
C5 | CLASSROOM | 368 | 24 |  | 720 | 16 | 16 | Univent | 5760 | 3.8333 | 1
C6 | CLASSROOM | 333 | 22 |  | 890 | 20 | 20 | Univent | 7120 | 2.8062 | 1
C7 | CLASSROOM | 293 | 19 |  | 0 | 0 | 0 | Univent | 0 | 0 | 0
C101 | CLASSROOM | 253 | 16 |  | 850 | 19 | 16 | Univent | 6800 | 2.2324 | 1
C102 | CLASSROOM | 404 | 26 |  | 850 | 19 | 19 | Univent | 6800 | 3.5647 | 1
C103 | CLASSROOM | 230 | 15 |  | 816 | 18 | 15 | Univent | 6528 | 2.114 | 1
C104 | CLASSROOM | 353 | 23 |  | 1120 | 25 | 23 | Univent | 8960 | 2.3638 | 1
C105 | CLASSROOM | 290 | 19 |  | 744 | 16 | 16 | Univent | 5952 | 2.9234 | 1
C106 | CLASSROOM | 241 | 16 |  | 1100 | 25 | 16 | Univent | 8800 | 1.6432 | 1
D1 | CLASSROOM | 274 | 18 |  | 850 | 19 | 18 | Univent | 6800 | 2.4176 | 1
D2 | CLASSROOM | 449 | 29 |  | 850 | 19 | 19 | Univent | 6800 | 3.9618 | 1
D3 | CLASSROOM | 314 | 20 |  | 850 | 19 | 19 | Univent | 6800 | 2.7706 | 1
D4 | CLASSROOM | 293 | 19 |  | 1085 | 24 | 19 | Univent | 8680 | 2.0253 | 1
D5 | CLASSROOM | 273 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.8438 | 1
D6 | CLASSROOM | 405 | 27 |  | 890 | 20 | 20 | Univent | 7120 | 3.4129 | 1
D101 | CLASSROOM | 283 | 18 |  | 850 | 19 | 18 | Univent | 6800 | 2.4971 | 1
D102 | CLASSROOM | 304 | 20 |  | 850 | 19 | 19 | Univent | 6800 | 2.6824 | 1
D103 | CLASSROOM | 326 | 21 |  | 816 | 18 | 18 | Univent | 6528 | 2.9963 | 1
D104 | CLASSROOM | 244 | 16 |  | 1120 | 25 | 16 | Univent | 8960 | 1.6339 | 1
D105 | CLASSROOM | 235 | 15 |  | 744 | 16 | 15 | Univent | 5952 | 2.369 | 1
D106 | CLASSROOM | 0 | 0 |  | 1100 | 25 | 0 | Univent | 8800 | 0 | 0
D200 | MUSIC CLASSROOM 2 | 729 | 48 |  | 1600 | 36 | 36 | Univent | 12800 | 3.4172 | 1
D205 | MUSIC CLASSROOM 1 | 620 | 41 |  | 1600 | 36 | 36 | Univent | 12800 | 2.9062 | 1
E12 | SCIENCE CLASSROOM | 0 | 0 |  | 1232 | 28 | 0 | Univent | 9856 | 0 | 0
E-147 | BREAK ROOM, OFFICE AREA | 0 | 0 |  | 120 | 2 | 0 | Univent | 960 | 0 | 0
E-148 | VICE PRINCIPAL OFFICE | 0 | 0 |  | 120 | 2 | 0 | Univent | 960 | 0 | 0
E-149 | CONFERENCE AREA | 47 | 3 |  | 260 | 5 | 3 | Univent | 2080 | 1.3558 | 1
E-150 | PRINCIPAL OFFICE | 36 | 2 |  | 225 | 5 | 2 | Univent | 1800 | 1.2 | 1
E204 | EARLY CHILDROOM ED CLASSROOM | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
E205 | CREATIVE WRITING CLASSROOM (LEFT) | 577 | 38 |  |  | 0 | 0 | Univent | 0 | 0 | 0
E207 | COMPUTER LAB | 3 | 0 |  | 2070 | 47 | 0 | Univent | 16560 | 0.01087 | 0
- | GIRLS GYM | 0 | 0 |  | 4897 | 111 | 0 | Air Handling Unit | 39176 | 0 | 0
- | BOYS GYM | 0 | 0 |  | 4897 | 111 | 0 | Air Handling Unit | 39176 | 0 | 0
- | IMC - LIBRARY | 0 | 0 |  | 3985 | 90 | 0 | Air Handling Unit | 31880 | 0 | 0
- | INDUSTRIAL ART (WOODSHOP) | 0 | 0 |  | 1564 | 35 | 0 | Air Handling Unit | 12512 | 0 | 0
- | SWIMMING POOL | 0 | 0 |  | 10200 | 231 | 0 | Air Handling Unit | 81600 | 0 | 0
- | ADMIN + HEALTH OFFICE | 0 | 0 |  | 130 | 2 | 0 | Air Handling Unit | 1040 | 0 | 0
- | ART STUDIOS | 0 | 0 |  | 3860 | 87 | 0 | Air Handling Unit | 30880 | 0 | 0
- | AUDITORIUM + STAGE | 0 | 0 |  | 12450 | 282 | 0 | Air Handling Unit | 99600 | 0 | 0
- | CLASSROOM (YMCA 2) | 0 | 0 |  | 704 | 16 | 0 | Air Handling Unit | 5632 | 0 | 0
- | CLASSROOM (YMCA OST1) | 0 | 0 |  | 544 | 12 | 0 | Air Handling Unit | 4352 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-05 | [7 empty] | 0 | 0 | 0
School: | Richmond Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
3 | - |  | 0 |  | 1000 | 22 | 0 | Radiators/House fan | 8000 | 0 | 0
8 | - |  | 0 |  | 1200 | 27 | 0 | Radiators/House fan | 9600 | 0 | 0
101 | Classroom |  | 0 | Yes | 759 | 17 | 17 | Radiators/House fan | 6072 | 0 | 0
102 | Classroom |  | 0 | Yes | 759 | 17 | 17 | Radiators/House fan | 6072 | 0 | 0
102A | Nurse |  | 0 | Yes | 216 | 4 | 4 | Radiators/House fan | 1728 | 0 | 0
103 | Classroom |  | 0 | Yes | 812 | 18 | 18 | Radiators/House fan | 6496 | 0 | 0
104 | Classroom |  | 0 | Yes | 812 | 18 | 18 | Radiators/House fan | 6496 | 0 | 0
105 | Main Office |  | 0 | Yes | 416 | 9 | 9 | Radiators/House fan | 3328 | 0 | 0
106 | Classroom |  | 0 | Yes | 762 | 17 | 17 | Radiators/House fan | 6096 | 0 | 0
107 | Classroom |  | 0 | Yes | 742 | 16 | 16 | Radiators/House fan | 5936 | 0 | 0
108 | Faculty Lounge |  | 0 |  | 440 | 10 | 0 | Radiators/House fan | 3520 | 0 | 0
109 | Classroom |  | 0 | Yes | 1180 | 26 | 26 | Radiators/House fan | 9440 | 0 | 0
201 | Classroom |  | 0 | Yes | 759 | 17 | 17 | Radiators/House fan | 6072 | 0 | 0
202 | Classroom |  | 0 | Yes | 759 | 17 | 17 | Radiators/House fan | 6072 | 0 | 0
203 | Classroom |  | 0 | Yes | 960 | 21 | 21 | Radiators/House fan | 7680 | 0 | 0
203A | Counselor Office |  | 0 |  | 167 | 3 | 0 | Radiators/House fan | 1336 | 0 | 0
204 | Classroom |  | 0 | Yes | 960 | 21 | 21 | Radiators/House fan | 7680 | 0 | 0
205 | Classroom |  | 0 | Yes | 896 | 20 | 20 | Radiators/House fan | 7168 | 0 | 0
206 | - |  | 0 |  | 896 | 20 | 0 | Radiators/House fan | 7168 | 0 | 0
207 | - |  | 0 | Yes | 792 | 18 | 18 | Radiators/House fan | 6336 | 0 | 0
208 | - |  | 0 |  | 792 | 18 | 0 | Radiators/House fan | 6336 | 0 | 0
209 | - |  | 0 | Yes | 841 | 19 | 19 | Radiators/House fan | 6728 | 0 | 0
210 | - |  | 0 |  | 202 | 4 | 0 | Radiators/House fan | 1616 | 0 | 0
301 | - |  | 0 |  | 792 | 18 | 0 | Radiators/House fan | 6336 | 0 | 0
302 | Classroom |  | 0 |  | 792 | 18 | 0 | Radiators/House fan | 6336 | 0 | 0
303 | - |  | 0 |  | 840 | 19 | 0 | Radiators/House fan | 6720 | 0 | 0
303A | - |  | 0 |  | 390 | 8 | 0 | Radiators/House fan | 3120 | 0 | 0
304 | - |  | 0 |  | 900 | 20 | 0 | Radiators/House fan | 7200 | 0 | 0
305 | - |  | 0 |  | 840 | 19 | 0 | Radiators/House fan | 6720 | 0 | 0
306 | Classroom |  | 0 |  | 870 | 19 | 0 | Radiators/House fan | 6960 | 0 | 0
307 | - |  | 0 |  | 850 | 19 | 0 | Radiators/House fan | 6800 | 0 | 0
308 | - |  | 0 |  | 850 | 19 | 0 | Radiators/House fan | 6800 | 0 | 0
309 | - |  | 0 |  | 900 | 20 | 0 | Radiators/House fan | 7200 | 0 | 0
310 | - |  | 0 |  | 202 | 4 | 0 | Radiators/House fan | 1616 | 0 | 0
- | Principal's Office |  | 0 |  | 448 | 10 | 0 | Radiators/House fan | 3584 | 0 | 0
- | Gym |  | 0 |  | 2760 | 62 | 0 | Heating Ventalation Unit | 22080 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-01 | [7 empty] | 0 | 0 | 0
School: | Rivera (Bright Futures) Early Childhood Center | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Basement | Cafeteria | 1016 | 67 |  | 4000 | 90 | 67 | Air Handling Unit | 32000 | 1.905 | 1
Basement | VVT's in the small Building | 138 | 9 |  | 247 | 5 | 5 | Air Handling Unit | 1976 | 4.1903 | 2
2nd floor | Common area vvt's(tall Building) | 131 | 8 |  | 247 | 5 | 5 | Air Handling Unit | 1976 | 3.9777 | 1
4th for upper building | Zoned AH for 5 zone floor | 0 | 0 |  | 247 | 5 | 0 | Air Handling Unit | 1976 | 0 | 0
5th floor upper building | Zoned AH for 6 zone floor | 1 | 0 |  | 247 | 5 | 0 | Air Handling Unit | 1976 | 0.030364 | 0
- | Zone1( group learning room) | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit | 1080 | 0 | 0
- | Zone2 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit | 1080 | 0 | 0
- | Zone3 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit | 1080 | 0 | 0
- | Zone4 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit | 1080 | 0 | 0
- | Zone5 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit | 1080 | 0 | 0
- | Zone6 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit | 1080 | 0 | 0
Zone1 | Group learning open area 1 | 804 | 53 |  | 280 | 6 | 6 | Air Handling Unit | 2240 | 21.5357 | 3
Zone 1 | Group learning open area 2 | 0 | 0 |  | 270 | 6 | 0 | Air Handling Unit | 2160 | 0 | 0
Zone 1 | Group learning office | 0 | 0 |  | 276 | 6 | 0 | Air Handling Unit | 2208 | 0 | 0
Zone 1 | Large storage | 0 | 0 |  | 112 | 2 | 0 | Air Handling Unit | 896 | 0 | 0
Zone 1 | Small storage | 21 | 1 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 1.9688 | 1
Zone 2 | Office 1 | 85 | 5 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 7.9688 | 2
Zone 2 | Office 2 | 72 | 4 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 6.75 | 2
Zone 2 | Office 3 | 37 | 2 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 3.4688 | 1
Zone 2 | Spare room | 83 | 5 |  | 85 | 1 | 1 | Air Handling Unit | 680 | 7.3235 | 2
Zone 2 | Hallway | 0 | 0 |  | 110 | 2 | 0 | Air Handling Unit | 880 | 0 | 0
Zone 2 | Copy room | 38 | 2 |  | 84 | 1 | 1 | Air Handling Unit | 672 | 3.3929 | 1
Zone 3 | Conference room vent 1 | 314 | 20 |  | 1344 | 30 | 20 | Air Handling Unit | 10752 | 1.7522 | 1
Zone 3 | Conference room vent 2 | 0 | 0 |  | 1344 | 30 | 0 | Air Handling Unit | 10752 | 0 | 0
Zone 3 | Conference room vent 3 | 0 | 0 |  | 1344 | 30 | 0 | Air Handling Unit | 10752 | 0 | 0
Zone 4 | Admin open area 1 | 307 | 20 |  | 182 | 4 | 4 | Air Handling Unit | 1456 | 12.6511 | 3
Zone 4 | Admin open area 2 | 0 | 0 |  | 182 | 4 | 0 | Air Handling Unit | 1456 | 0 | 0
Zone 4 | copy room | 57 | 3 |  | 84 | 1 | 1 | Air Handling Unit | 672 | 5.0893 | 2
Zone 4 | elevator hallway | 0 | 0 |  | 144 | 3 | 0 | Air Handling Unit | 1152 | 0 | 0
Zone 4 | admin waiting area | 0 | 0 |  | 380 | 8 | 0 | Air Handling Unit | 3040 | 0 | 0
Zone 4 | Vacant office 1 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 4 | Vacant office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 4 | Supply Room | 0 | 0 |  | 110 | 2 | 0 | Air Handling Unit | 880 | 0 | 0
Zone 5 | Office 1 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 5 | Office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 5 | Zone 5 meeting Room 1 | 42 | 2 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 3.9375 | 1
Zone 5 | Zone 5 meeting Room 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 6 | Storage | 110 | 7 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 10.3125 | 3
Zone 6 | Office 1 | 272 | 18 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 25.5 | 4
Zone 6 | Office 2 | 121 | 8 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 11.3438 | 3
Zone 6 | Office 3 | 115 | 7 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 10.7812 | 3
Zone 6 | Office 4 | 198 | 13 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 18.5625 | 3
Zone 6 | Office 5 | 147 | 9 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 13.7812 | 3
- | Zone 1 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Zone 2 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Zone 3 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Zone 4 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Zone 5 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
Zone 1 | Group learning area. Diffuser 1 | 91 | 6 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
Zone 1 | Group learning area. Diffuser 2 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
Zone 1 | Group learning area. Diffuser 3 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
Zone 1 | Group learning area. Diffuser 4 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
Zone 1 | Group learning area. Diffuser 5 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
Zone 1 | Office 1 | 18 | 1 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 1.6875 | 1
Zone 1 | Office 2 | 19 | 1 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 1.7812 | 1
Zone 1 | Office 3 | 12 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 1.125 | 1
Zone 2 | Elevator lobby | 0 | 0 |  | 144 | 3 | 0 | Air Handling Unit | 1152 | 0 | 0
Zone 2 | Reception diffuser 1 | 34 | 2 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
Zone 2 | Reception diffuser 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 2 | Office 1 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 2 | Office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 3 | Office 1 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 3 | Office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 3 | Office 3 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 3 | Kitchen 1 | 0 | 0 |  | 214 | 4 | 0 | Air Handling Unit | 1712 | 0 | 0
Zone 3 | Kitchen 2 | 0 | 0 |  | 214 | 4 | 0 | Air Handling Unit | 1712 | 0 | 0
Zone 3 | Hallway 1 | 0 | 0 |  | 276 | 6 | 0 | Air Handling Unit | 2208 | 0 | 0
Zone 3 | Hallway 2 | 0 | 0 |  | 168 | 3 | 0 | Air Handling Unit | 1344 | 0 | 0
Zone 4 | Office 411 | 0 | 0 |  | 75 | 1 | 0 | Air Handling Unit | 600 | 0 | 0
Zone 4 | Office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 4 | Office 3 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 4 | Storage 415 | 0 | 0 |  | 39 | 0 | 0 | Air Handling Unit | 312 | 0 | 0
Zone 4 | Hallway | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 4 | Assistant Superintendent | 0 | 0 |  | 460 | 10 | 0 | Air Handling Unit | 3680 | 0 | 0
Zone 4 | Assistant Superintendent | 0 | 0 |  | 460 | 10 | 0 | Air Handling Unit | 3680 | 0 | 0
Zone 4 | Assistant Superintendent | 0 | 0 |  | 460 | 10 | 0 | Air Handling Unit | 3680 | 0 | 0
Zone 4 | Storage 408 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 5 | Office 403 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 5 | Office 403 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 5 | Office 404 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 5 | Office | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 5 | Office | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 5 | Conference room 406 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 5 | Conference room 406 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
Zone 5 | Office 407 | 0 | 0 |  | 142 | 3 | 0 | Air Handling Unit | 1136 | 0 | 0
Zone 5 | Office 409 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0
3rd floor. VVT#11 | Commons area total | 50 | 3 |  | 247 | 5 | 3 | Air Handling Unit | 1976 | 1.5182 | 1
- | Elevator hall | 9 | 0 |  | 400 | 9 | 0 | Air Handling Unit | 3200 | 0.16875 | 0
- | Elevator hall | 0 | 0 |  | 602 | 13 | 0 | Air Handling Unit | 4816 | 0 | 0
- | Commons Area Diffuser | 11 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Commons Area Diffuser | 11 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Commons Area Diffuser | 11 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Commons Area Diffuser | 12 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Commons Area Office | 2 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
2nd floor. VVT#8 | Commons Are Total | 58 | 3 |  | 247 | 5 | 3 | Air Handling Unit | 1976 | 1.7611 | 1
- | Elevator hall | 2 | 0 |  | 400 | 9 | 0 | Air Handling Unit | 3200 | 0.0375 | 0
- | Commons Area Diffuser | 14 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Commons Area Diffuser | 14 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Commons Area Diffuser | 12 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Commons Area Diffuser | 8 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Commons area office | 3 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Class bathroom | 3 | 0 |  | 75 | 1 | 0 | Air Handling Unit | 600 | 0.3 | 0
- | Staff Bathroom | 2 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Elevator hall | 2 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
1st floor VVT#4 | 1st floor Commons Area Total | 46 | 3 |  | 247 | 5 | 3 | Air Handling Unit | 1976 | 1.3968 | 1
- | elevator hall | 14 | 0 |  | 480 | 10 | 0 | Air Handling Unit | 3840 | 0.21875 | 0
- | elevator hall | 7 | 0 |  | 700 | 15 | 0 | Air Handling Unit | 5600 | 0.075 | 0
- | Commons area diffuser | 7 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Commons area diffuser | 8 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Commons area diffuser | 2 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Commons area diffuser | 4 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Commons area office | 3 | 0 |  | 126 | 2 | 0 | Air Handling Unit | 1008 | 0.17857 | 0
- | Class bathroom | 0 | 0 |  | 75 | 1 | 0 | Air Handling Unit | 600 | 0 | 0
- | Staff bathroom | 2 | 0 |  | 48 | 1 | 0 | Air Handling Unit | 384 | 0.3125 | 0
Room110 | Classroom | 400 | 26 |  | 900 | 20 | 20 | Univent | 7200 | 3.3333 | 1
Room 111 | Classroom | 335 | 22 |  | 900 | 20 | 20 | Univent | 7200 | 2.7917 | 1
Room 112 | Classroom | 410 | 27 |  | 900 | 20 | 20 | Univent | 7200 | 3.4167 | 1
Room 113 | Classroom | 375 | 25 |  | 900 | 20 | 20 | Univent | 7200 | 3.125 | 1
205A | Office space | 290 | 19 |  | 480 | 10 | 10 | Univent | 3840 | 4.5312 | 2
205B | Office space | 484 | 32 |  | 613 | 13 | 13 | Univent | 4904 | 5.9217 | 2
Room 212 | Classroom | 259 | 17 |  | 900 | 20 | 17 | Univent | 7200 | 2.1583 | 1
Room 213 | Classroom | 502 | 33 |  | 900 | 20 | 20 | Univent | 7200 | 4.1833 | 2
Room 214 | Classroom | 277 | 18 |  | 900 | 20 | 18 | Univent | 7200 | 2.3083 | 1
Room 215 | Classroom | 544 | 36 |  | 900 | 20 | 20 | Univent | 7200 | 4.5333 | 2
Room303 | Office space | 482 | 32 |  | 1414 | 32 | 32 | Univent | 11312 | 2.5566 | 1
Room 303B | Office space | 256 | 17 |  | 360 | 8 | 8 | Univent | 2880 | 5.3333 | 2
Room 309 | Classroom | 517 | 34 |  | 1110 | 25 | 25 | Univent | 8880 | 3.4932 | 1
Room 310 | Classroom | 290 | 19 |  | 900 | 20 | 19 | Univent | 7200 | 2.4167 | 1
Room 311 | Classroom | 326 | 21 |  | 900 | 20 | 20 | Univent | 7200 | 2.7167 | 1
Room 312 | Classroom | 394 | 26 |  | 900 | 20 | 20 | Univent | 7200 | 3.2833 | 1
VVT 9 | Total | 10 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Office | 3 | 0 |  | 144 | 3 | 0 | Air Handling Unit | 1152 | 0.15625 | 0
- | Office | 4 | 0 |  | 144 | 3 | 0 | Air Handling Unit | 1152 | 0.20833 | 0
- | Hallway | 4 | 0 |  | 688 | 15 | 0 | Air Handling Unit | 5504 | 0.043605 | 0
VVT 10 | Total | 43 | 2 |  | 688 | 15 | 2 | Air Handling Unit | 5504 | 0.46875 | 0
- | Teachers Lounge | 16 | 1 |  | 390 | 8 | 1 | Air Handling Unit | 3120 | 0.30769 | 0
- | Bathroom | 4 | 0 |  | 48 | 1 | 0 | Air Handling Unit | 384 | 0.625 | 0
- | Women's Room | 8 | 0 |  | 112 | 2 | 0 | Air Handling Unit | 896 | 0.53571 | 0
- | Men's Room | 3 | 0 |  | 112 | 2 | 0 | Air Handling Unit | 896 | 0.20089 | 0
- | Hallway | 11 | 0 |  | 688 | 15 | 0 | Air Handling Unit | 5504 | 0.11991 | 0
VVT 6 | Total | 18 | 1 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | office | 6 | 0 |  | 100 | 2 | 0 | Air Handling Unit | 800 | 0.45 | 0
- | Office | 5 | 0 |  | 100 | 2 | 0 | Air Handling Unit | 800 | 0.375 | 0
- | Office | 5 | 0 |  | 100 | 2 | 0 | Air Handling Unit | 800 | 0.375 | 0
- | Hallway | 2 | 0 |  | 688 | 15 | 0 | Air Handling Unit | 5504 | 0.021802 | 0
VVT 7 | Total | 32 | 2 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Men's room | 7 | 0 |  | 112 | 2 | 0 | Air Handling Unit | 896 | 0.46875 | 0
- | Women's room | 11 | 0 |  | 112 | 2 | 0 | Air Handling Unit | 896 | 0.73661 | 0
- | Staff bathroom | 4 | 0 |  | 52 | 1 | 0 | Air Handling Unit | 416 | 0.57692 | 0
- | Hallway | 4 | 0 |  | 688 | 15 | 0 | Air Handling Unit | 5504 | 0.043605 | 0
- | Hallway | 4 | 0 |  | 688 | 15 | 0 | Air Handling Unit | 5504 | 0.043605 | 0
VVT1 | Total | 29 | 1 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | kitchen | 6 | 0 |  | 288 | 6 | 0 | Air Handling Unit | 2304 | 0.15625 | 0
- | Storage | 4 | 0 |  | 450 | 10 | 0 | Air Handling Unit | 3600 | 0.066667 | 0
- | Men's room | 4 | 0 |  | 77 | 1 | 0 | Air Handling Unit | 616 | 0.38961 | 0
- | Women's room | 6 | 0 |  | 77 | 1 | 0 | Air Handling Unit | 616 | 0.58442 | 0
- | Unisex bathroom | 3 | 0 |  | 77 | 1 | 0 | Air Handling Unit | 616 | 0.29221 | 0
VVT 3 | Total | 0 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | storage | 0 | 0 |  | 328 | 7 | 0 | Air Handling Unit | 2624 | 0 | 0
- | storage | 0 | 0 |  | 450 | 10 | 0 | Air Handling Unit | 3600 | 0 | 0
- | storage | 0 | 0 |  | 250 | 5 | 0 | Air Handling Unit | 2000 | 0 | 0
- | storage | 0 | 0 |  | 175 | 3 | 0 | Air Handling Unit | 1400 | 0 | 0
VVT 5 | Total | 41 | 2 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | hallway | 7 | 0 |  | 425 | 9 | 0 | Air Handling Unit | 3400 | 0.12353 | 0
- | Lobby | 11 | 0 |  | 375 | 8 | 0 | Air Handling Unit | 3000 | 0.22 | 0
- | Guard office | 8 | 0 |  | 120 | 2 | 0 | Air Handling Unit | 960 | 0.5 | 0
- | Staff lockers | 4 | 0 |  | 450 | 10 | 0 | Air Handling Unit | 3600 | 0.066667 | 0
- | Hallway | 4 | 0 |  | 800 | 18 | 0 | Air Handling Unit | 6400 | 0.0375 | 0
- | Hallway | 8 | 0 |  | 168 | 3 | 0 | Air Handling Unit | 1344 | 0.35714 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | Paul Robeson High School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B-2 | Classroom | 0 | 0 |  | 1073 | 24 | 0 | Fan Coil Unit | 8584 | 0 | 0
100 | Classroom | 380 | 25 |  | 940 | 21 | 21 | Univent | 7520 | 3.0319 | 1
106 | Classroom | 470 | 31 |  | 840 | 19 | 19 | Univent | 6720 | 4.1964 | 2
108 | Classroom | 11 | 0 |  | 828 | 18 | 0 | Univent | 6624 | 0.099638 | 0
200 | Classroom | 89 | 5 |  | 696 | 15 | 5 | Univent | 5568 | 0.95905 | 0
202 | Classroom | 231 | 15 |  | 696 | 15 | 15 | Univent | 5568 | 2.4892 | 1
204 | Classroom | 301 | 20 |  | 696 | 15 | 15 | Univent | 5568 | 3.2435 | 1
205 | Classroom | 304 | 20 |  | 672 | 15 | 15 | Univent | 5376 | 3.3929 | 1
206 | Classroom | 200 | 13 |  | 696 | 15 | 13 | Univent | 5568 | 2.1552 | 1
207 | Classroom | 191 | 12 |  | 696 | 15 | 12 | Univent | 5568 | 2.0582 | 1
208 | Classroom | 125 | 8 |  | 696 | 15 | 8 | Univent | 5568 | 1.347 | 1
209 | Classroom | 178 | 11 |  | 384 | 8 | 8 | Univent | 3072 | 3.4766 | 1
210 | Classroom | 200 | 13 |  | 690 | 15 | 13 | Univent | 5520 | 2.1739 | 1
211 | Classroom | 262 | 17 |  | 851 | 19 | 17 | Univent | 6808 | 2.309 | 1
212 | Classroom | 280 | 18 |  | 875 | 19 | 18 | Univent | 7000 | 2.4 | 1
213 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Univent | 7000 | 0 | 0
- | AUDITORIUM | 0 | 0 |  | 2793 | 63 | 0 | Air Handling Unit | 22344 | 0 | 0
- | Cafeteria | 862 | 57 |  | 2343 | 53 | 53 | Univent | 18744 | 2.7593 | 1
- | GYM | 812 | 54 |  | 3478 | 79 | 54 | Air Handling Unit | 27824 | 1.751 | 1
- | MAIN OFFICE | 0 | 0 |  | 552 | 12 | 0 | Univent | 4416 | 0 | 0
- | Student Lounge | 64 | 4 |  | 552 | 12 | 4 | Univent | 4416 | 0.86957 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-05-03 | [7 empty] | 0 | 0 | 0
School: | Roosevelt Elementary School | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom |  | 0 | Yes | 1035 | 23 | 23 | House Fan | 8280 | 0 | 0
102 | Classroom |  | 0 | Yes | 1012 | 23 | 23 | House Fan | 8096 | 0 | 0
103 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | 0 | 0
104 | Main Office |  | 0 | Yes | 1225 | 27 | 27 | House Fan | 9800 | 0 | 0
105 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0
106 & 106a | Classroom |  | 0 | Yes | 1298 | 29 | 29 | House Fan | 10384 | 0 | 0
107 | Parent Liason |  | 0 | Yes | 550 | 12 | 12 | House Fan | 4400 | 0 | 0
108 | Classroom |  | 0 | Yes | 814 | 18 | 18 | House Fan | 6512 | 0 | 0
109 | Classroom |  | 0 | Yes | 1104 | 25 | 25 | House Fan | 8832 | 0 | 0
110 | Classroom |  | 0 | Yes | 960 | 21 | 21 | House Fan | 7680 | 0 | 0
- | Lunchroom A |  | 0 | Yes | 2881 | 65 | 65 | House Fan | 23048 | 0 | 0
- | Lunchroom B |  | 0 | Yes | 2898 | 65 | 65 | House Fan | 23184 | 0 | 0
200A | Counselor |  | 0 | Yes | 342 | 7 | 7 | House Fan | 2736 | 0 | 0
200B | Counselor |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | 0 | 0
200C | Counselor |  | 0 | Yes | 342 | 7 | 7 | House Fan | 2736 | 0 | 0
201 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
202 | Classroom |  | 0 | Yes | 638 | 14 | 14 | House Fan | 5104 | 0 | 0
203 | Classroom |  | 0 | Yes | 748 | 17 | 17 | House Fan | 5984 | 0 | 0
205 | IMC |  | 0 | Yes | 1320 | 30 | 30 | House Fan | 10560 | 0 | 0
206A | Counselor |  | 0 | Yes | 140 | 3 | 3 | House Fan | 1120 | 0 | 0
206B | Counselor |  | 0 | Yes | 116 | 2 | 2 | House Fan | 928 | 0 | 0
206C | Counselor |  | 0 | Yes | 115 | 2 | 2 | House Fan | 920 | 0 | 0
206D | Counselor |  | 0 | Yes | 142 | 3 | 3 | House Fan | 1136 | 0 | 0
206E | Counselor |  | 0 | Yes | 126 | 2 | 2 | House Fan | 1008 | 0 | 0
207A | Room |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | 0 | 0
207B | Room |  | 0 |  | 145 | 3 | 0 | House Fan | 1160 | 0 | 0
207C | Room |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | 0 | 0
207D | Room |  | 0 |  | 103 | 2 | 0 | House Fan | 824 | 0 | 0
207E | Room |  | 0 | Yes | 132 | 3 | 3 | House Fan | 1056 | 0 | 0
208 | Art Room |  | 0 | Yes | 1152 | 26 | 26 | House Fan | 9216 | 0 | 0
209 | Faculty Lounge |  | 0 | Yes | 696 | 15 | 15 | House Fan | 5568 | 0 | 0
- | Principal Office |  | 0 | Yes | 629 | 14 | 14 | House Fan | 5032 | 0 | 0
- | Nurse Suite |  | 0 | Yes | 552 | 12 | 12 | House Fan | 4416 | 0 | 0
210 | Science Lab |  | 0 | Yes | 700 | 15 | 15 | House Fan | 5600 | 0 | 0
211 | Music |  | 0 | Yes | 858 | 19 | 19 | House Fan | 6864 | 0 | 0
212 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
213 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
214 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
215 | Classroom |  | 0 | Yes | 572 | 13 | 13 | House Fan | 4576 | 0 | 0
216 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
217 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
218 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
219 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0
220 | Classroom |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | 0 | 0
221A | Classroom |  | 0 | Yes | 342 | 7 | 7 | House Fan | 2736 | 0 | 0
221B | Classroom |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | 0 | 0
221C | Classroom |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | 0 | 0
222 | Classroom |  | 0 |  | 336 | 7 | 0 | House Fan | 2688 | 0 | 0
300A | Counselor // Storage |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | 0 | 0
300B | Counselor // Storage |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | 0 | 0
300C | Counselor // Storage |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | 0 | 0
301 | Vice Principals Office |  | 0 | Yes | 629 | 14 | 14 | House Fan | 5032 | 0 | 0
302 | Classroom |  | 0 | Yes | 735 | 16 | 16 | House Fan | 5880 | 0 | 0
303 | Classroom |  | 0 | Yes | 789 | 17 | 17 | House Fan | 6312 | 0 | 0
304 | Classroom |  | 0 | Yes | 734 | 16 | 16 | House Fan | 5872 | 0 | 0
305 | Classroom |  | 0 | Yes | 789 | 17 | 17 | House Fan | 6312 | 0 | 0
306 | Classroom |  | 0 |  | 1170 | 26 | 0 | House Fan | 9360 | 0 | 0
307 | Classroom |  | 0 | Yes | 936 | 21 | 21 | House Fan | 7488 | 0 | 0
308 | Classroom |  | 0 | Yes | 735 | 16 | 16 | House Fan | 5880 | 0 | 0
309 | Classroom |  | 0 |  | 952 | 21 | 0 | House Fan | 7616 | 0 | 0
310 | Classroom |  | 0 | Yes | 840 | 19 | 19 | House Fan | 6720 | 0 | 0
311 | Classroom |  | 0 |  | 836 | 19 | 0 | House Fan | 6688 | 0 | 0
312 | Classroom |  | 0 |  | 792 | 18 | 0 | House Fan | 6336 | 0 | 0
313 | Classroom |  | 0 |  | 920 | 20 | 0 | House Fan | 7360 | 0 | 0
314 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan | 5704 | 0 | 0
315 | Classroom |  | 0 |  | 667 | 15 | 0 | House Fan | 5336 | 0 | 0
316 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan | 5704 | 0 | 0
317 | Classroom |  | 0 |  | 638 | 14 | 0 | House Fan | 5104 | 0 | 0
318 | Classroom |  | 0 |  | 868 | 19 | 0 | House Fan | 6944 | 0 | 0
319 | Classroom |  | 0 | Yes | 868 | 19 | 19 | House Fan | 6944 | 0 | 0
320 | Classroom |  | 0 | Yes | 868 | 19 | 19 | House Fan | 6944 | 0 | 0
324A | Counselor, School Police |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | 0 | 0
324B | Counselor, School Police |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | 0 | 0
324C | Counselor, School Police |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | 0 | 0
322 | Classroom |  | 0 | Yes | 868 | 19 | 19 | House Fan | 6944 | 0 | 0
321 | Classroom |  | 0 | Yes | 861 | 19 | 19 | House Fan | 6888 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | William Rowen Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | EMCOR Part 2 | Devine | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Auditorium | 0 | 0 |  | 4256 | 96 | 0 | House Fan | 34048 | 0 | 0
- | Cafeteria/Gym | 0 | 0 | Yes | 5220 | 118 | 118 | Univent | 41760 | 0 | 0
- | Library | 328 | 21 |  | 1456 | 33 | 21 | Univent | 11648 | 1.6896 | 1
101 | Classroom | 457 | 30 |  | 1128 | 25 | 25 | Univent | 9024 | 3.0386 | 1
102 | Classroom | 545 | 36 |  | 1128 | 25 | 25 | Univent | 9024 | 3.6237 | 1
103 | Classroom | 42 | 2 | Yes | 266 | 6 | 6 | Univent | 2128 | 1.1842 | 1
104 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Univent | 6528 | 0 | 0
105 | Classroom | 304 | 20 |  | 816 | 18 | 18 | Univent | 6528 | 2.7941 | 1
106 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Univent | 6528 | 0 | 0
107 | Classroom | 299 | 19 |  | 816 | 18 | 18 | Univent | 6528 | 2.7482 | 1
108 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | Univent | 5760 | 0 | 0
109 | Classroom | 234 | 15 |  | 720 | 16 | 15 | Univent | 5760 | 2.4375 | 1
110 | Classroom | 399 | 26 |  | 720 | 16 | 16 | Univent | 5760 | 4.1562 | 2
111 | Classroom | 440 | 29 |  | 720 | 16 | 16 | Univent | 5760 | 4.5833 | 2
112 | Classroom | 68 | 4 |  | 720 | 16 | 4 | Univent | 5760 | 0.70833 | 0
113 | Classroom | 235 | 15 |  | 720 | 16 | 15 | Univent | 5760 | 2.4479 | 1
- | Nurse's Office | 235 | 15 |  | 192 | 4 | 4 | Univent | 1536 | 9.1797 | 2
201 | Classroom | 373 | 24 |  | 920 | 20 | 20 | Univent | 7360 | 3.0408 | 1
202 | Classroom | 396 | 26 |  | 920 | 20 | 20 | Univent | 7360 | 3.2283 | 1
203 | Classroom | 307 | 20 |  | 442 | 10 | 10 | Univent | 3536 | 5.2093 | 2
204 | Classroom | 299 | 19 |  | 384 | 8 | 8 | Univent | 3072 | 5.8398 | 2
205 | Classroom | 309 | 20 |  | 720 | 16 | 16 | Univent | 5760 | 3.2188 | 1
206 | Classroom | 230 | 15 |  | 720 | 16 | 15 | Univent | 5760 | 2.3958 | 1
207 | Classroom | 327 | 21 |  | 720 | 16 | 16 | Univent | 5760 | 3.4062 | 1
208 | Classroom | 272 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.8333 | 1
209 | Classroom | 324 | 21 |  | 720 | 16 | 16 | Univent | 5760 | 3.375 | 1
210 | Classroom | 276 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.875 | 1
211 | Classroom | 336 | 22 |  | 720 | 16 | 16 | Univent | 5760 | 3.5 | 1
212 | Classroom | 272 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.8333 | 1
213 | Classroom | 284 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.9583 | 1
214 | Classroom | 271 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.8229 | 1
215 | Classroom | 280 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.9167 | 1
216 | Classroom | 300 | 20 |  | 744 | 16 | 16 | Univent | 5952 | 3.0242 | 1
- | Main Office |  | 0 | Yes | 552 | 12 | 12 |  | 4416 | 0 | 0
- | Principal |  | 0 | Yes | 270 | 6 | 6 |  | 2160 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Roxborough High School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
114 | Classroom | 0 | 0 |  | 857 | 19 | 0 | Univent | 6856 | 0 | 0
115 | Classroom | 30 | 2 |  | 870 | 19 | 2 | Univent | 6960 | 0.25862 | 0
116 | Classroom | 45 | 3 |  | 690 | 15 | 3 | Univent | 5520 | 0.48913 | 0
117 | Weight Room | 30 | 2 |  | 814 | 18 | 2 | Univent | 6512 | 0.27641 | 0
118 | Classroom | 55 | 3 |  | 702 | 15 | 3 | Univent | 5616 | 0.58761 | 0
119 | Classroom | 270 | 18 |  | 877 | 19 | 18 | Univent | 7016 | 2.309 | 1
120 | Classroom | 85 | 5 |  | 694 | 15 | 5 | Univent | 5552 | 0.91859 | 0
121 | Classroom | 40 | 2 |  | 1207 | 27 | 2 | Univent | 9656 | 0.24855 | 0
124A-1 | Classroom | 55 | 3 |  | 621 | 14 | 3 | Univent | 4968 | 0.66425 | 0
124B-1 | Classroom | 30 | 2 |  | 672 | 15 | 2 | Univent | 5376 | 0.33482 | 0
126 | Classroom | 0 | 0 |  | 1841 | 41 | 0 | Univent | 14728 | 0 | 0
128 | Classroom | 50 | 3 |  | 1501 | 34 | 3 | Univent | 12008 | 0.24983 | 0
203 | Classroom |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | 0 | 0
205 | Classroom |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | 0 | 0
215 | Classroom | 0 | 0 |  | 829 | 18 | 0 | Univent | 6632 | 0 | 0
216 | Classroom | 50 | 3 |  | 834 | 18 | 3 | Univent | 6672 | 0.44964 | 0
217 | Classroom | 0 | 0 |  | 686 | 15 | 0 | Univent | 5488 | 0 | 0
218 | Classroom | 0 | 0 |  | 724 | 16 | 0 | Univent | 5792 | 0 | 0
219 | Classroom | 55 | 3 |  | 842 | 19 | 3 | Univent | 6736 | 0.4899 | 0
220 | Classroom | 60 | 4 |  | 616 | 14 | 4 | Univent | 4928 | 0.73052 | 0
221 | Classroom | 35 | 2 |  | 845 | 19 | 2 | Univent | 6760 | 0.31065 | 0
223 | Classroom | 55 | 3 |  | 1072 | 24 | 3 | Univent | 8576 | 0.38479 | 0
224 | Classroom | 55 | 3 |  | 1010 | 22 | 3 | Univent | 8080 | 0.40842 | 0
235 | Classroom |  | 0 | Yes | 839 | 19 | 19 |  | 6712 | 0 | 0
309 | Classroom |  | 0 | Yes | 997 | 22 | 22 |  | 7976 | 0 | 0
312 | Classroom |  | 0 | Yes | 1071 | 24 | 24 |  | 8568 | 0 | 0
319 | Classroom | 40 | 2 |  | 644 | 14 | 2 | Univent | 5152 | 0.46584 | 0
320 | Classroom | 40 | 2 |  | 721 | 16 | 2 | Univent | 5768 | 0.41609 | 0
321 | Classroom | 55 | 3 |  | 924 | 21 | 3 | Univent | 7392 | 0.44643 | 0
322 | Classroom | 30 | 2 |  | 723 | 16 | 2 | Univent | 5784 | 0.3112 | 0
323 | Classroom | 60 | 4 |  | 777 | 17 | 4 | Univent | 6216 | 0.57915 | 0
324 | Classroom | 55 | 3 |  | 942 | 21 | 3 | Univent | 7536 | 0.4379 | 0
325 | Classroom | 45 | 3 | Yes | 325 | 7 | 7 | Univent | 2600 | 1.0385 | 1
326 | Classroom | 55 | 3 |  | 1000 | 22 | 3 | Univent | 8000 | 0.4125 | 0
- | Gymnasium | 740 | 49 |  | 11475 | 260 | 49 | Air Handling Unit | 91800 | 0.48366 | 0
- | Library | 2335 | 155 |  | 2622 | 59 | 59 | Air Handling Unit | 20976 | 6.6791 | 2
East Office | Office | 75 | 5 |  |  | 0 | 0 |  | 0 | 0 | 0
West Office | Office | 110 | 7 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Alumni Room | 255 | 17 |  | 377 | 8 | 8 | Air Handling Unit | 3016 | 5.0729 | 2
- | Computer Lab | 1285 | 85 |  | 870 | 19 | 19 | Air Handling Unit | 6960 | 11.0776 | 3
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | Arts Academy @ Benjamin Rush High School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | Devine Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
103 | Lab Classroom | 465 | 31 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 4.6624 | 2
103 | Lab Classroom | 465 | 31 |  |  | 0 | 0 | Univent & Air Handling Unit | 0 | 0 | 0
104 | GraphicArts Classroom | 928 | 61 |  | 1840 | 41 | 41 | Univent & Air Handling Unit | 14720 | 3.7826 | 1
104 | Graphic Arts Classroom | 946 | 63 |  |  | 0 | 0 | Univent & Air Handling Unit | 0 | 0 | 0
105 | IMC Classroom | 2959 | 197 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
105D | Student Property Office | 281 | 18 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
105E | IMC Copy Office | 960 | 64 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
105F | Cart Storage | 368 | 24 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
105G | Tech Equip Office | 255 | 17 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
105H | IMC Office | 201 | 13 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
105J | IMC Storage room | 252 | 16 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
105K | IMC Conference Rm | 312 | 20 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
106 | Art Studio Classroom | 1326 | 88 |  | 1020 | 23 | 23 | Air Handling Unit | 8160 | 9.75 | 2
107 | storage room | 275 | 18 |  | 280 | 6 | 6 | Air Handling Unit | 2240 | 7.3661 | 2
122 | Art Studio Classroom | 1689 | 112 |  | 1496 | 34 | 34 | Air Handling Unit | 11968 | 8.4676 | 2
123 | Production Studio Classroom | 2228 | 148 |  | 1254 | 28 | 28 | Air Handling Unit | 10032 | 13.3254 | 3
126A | Boys Locker Room | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
127A | Girls Locker Room | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
129 | Production Booth Classroom | 842 | 56 |  | 264 | 6 | 6 | Air Handling Unit | 2112 | 23.9205 | 3
131A | Changing Room Classroom | 238 | 15 |  | 72 | 1 | 1 | Air Handling Unit | 576 | 24.7917 | 4
131B | Changing Room Classroom | 175 | 11 |  | 192 | 4 | 4 | Air Handling Unit | 1536 | 6.8359 | 2
133 | Storage Room | 428 | 28 |  | 580 | 13 | 13 | Air Handling Unit | 4640 | 5.5345 | 2
134 | Music Classroom | 1076 | 71 |  | 748 | 17 | 17 | Air Handling Unit | 5984 | 10.7888 | 3
135 | Music Classroom | 1097 | 73 |  | 748 | 17 | 17 | Air Handling Unit | 5984 | 10.9993 | 3
136 | Practice Classroom | 113 | 7 |  | 36 | 0 | 0 | Air Handling Unit | 288 | 23.5417 | 3
137 | Practice Classroom | 116 | 7 |  | 36 | 0 | 0 | Air Handling Unit | 288 | 24.1667 | 4
138 | Library | 88 | 5 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
140 | Vocal Music Classroom | 3597 | 239 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
141 | Scene Shop Classroom | 994 | 66 |  |  | 0 | 0 | Univent & Air Handling Unit | 0 | 0 | 0
142 | Vocal Theory Classroom | 347 | 23 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 3.4793 | 1
143 | Music Theory Classroom | 963 | 64 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 9.6557 | 2
144 | Music Tech Lab Classroom | 699 | 46 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.0087 | 2
145A | Clerical Office | 362 | 24 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 3.7708 | 1
145B | Roster Office | 161 | 10 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 15.0938 | 3
145D | Copier Office | 219 | 14 |  | 75 | 1 | 1 | Air Handling Unit | 600 | 21.9 | 3
145E | Conference Office | 341 | 22 |  | 128 | 2 | 2 | Air Handling Unit | 1024 | 19.9805 | 3
145F | Principal Office | 328 | 21 |  | 247 | 5 | 5 | Air Handling Unit | 1976 | 9.9595 | 2
145J | Asset Princ.Office | 114 | 7 |  | 272 | 6 | 6 | Air Handling Unit | 2176 | 3.1434 | 1
145K | Asset Princ.Office | 67 | 4 |  | 180 | 4 | 4 | Air Handling Unit | 1440 | 2.7917 | 1
146A | Clinic Office | 45 | 3 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 2.8125 | 1
146B | ClinicWaitingoffice | 506 | 33 |  | 221 | 5 | 5 | Air Handling Unit | 1768 | 17.1719 | 3
146D | Exam Room | 328 | 21 |  | 60 | 1 | 1 | Air Handling Unit | 480 | 41 | 4
147 | Counselor Waiting Area | 450 | 30 |  | 288 | 6 | 6 | Air Handling Unit | 2304 | 11.7188 | 3
147B | Counselor Office | 149 | 9 |  | 221 | 5 | 5 | Air Handling Unit | 1768 | 5.0566 | 2
147D | Counselor's Office | 283 | 18 |  | 60 | 1 | 1 | Air Handling Unit | 480 | 35.375 | 4
147E | Counselor Office | 157 | 10 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 9.8125 | 2
147F | Counselor Conference Office | 311 | 20 |  | 169 | 3 | 3 | Air Handling Unit | 1352 | 13.8018 | 3
147G | Counselor's Office | 383 | 25 |  | 180 | 4 | 4 | Air Handling Unit | 1440 | 15.9583 | 3
148A | Camera office | 565 | 37 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 35.3125 | 4
148B | Storage Room | 121 | 8 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
148C | Records Office | 118 | 7 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
148D | Security Office | 125 | 8 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
148E | Operations Office | 372 | 24 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
200 | General Classroom | 649 | 43 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.5074 | 2
201 | General Classroom | 532 | 35 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 5.3342 | 2
202 | General Classroom | 692 | 46 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.9385 | 2
204 | General Classroom | 447 | 29 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 4.482 | 2
205 | General Classroom | 566 | 37 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 5.6751 | 2
209 | Social Ed. Classroom | 779 | 51 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.8108 | 2
210 | General Classroom | 662 | 44 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.6377 | 2
211 | General Classroom | 562 | 37 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 5.635 | 2
212 | General Classroom | 423 | 28 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 4.2413 | 2
213 | General Classroom | 597 | 39 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 5.986 | 2
214 | General Classroom | 868 | 57 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 8.7032 | 2
215 | General Classroom | 442 | 29 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit | 0 | 0 | 0
216 | Physical Science Classroom | 970 | 64 |  | 1344 | 30 | 30 | Fan Coil Unit & Air Handling Unit | 10752 | 5.4129 | 2
217 | Prep Classroom | 299 | 19 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit | 0 | 0 | 0
219 | Physics Classroom | 630 | 42 |  | 1344 | 30 | 30 | Fan Coil Unit & Air Handling Unit | 10752 | 3.5156 | 1
220 | Storage room | 418 | 27 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
221 | General Classroom | 324 | 21 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit | 0 | 0 | 0
221B | Storage Room | 135 | 9 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
221C | Storage Room | 130 | 8 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
222 | Biology Classroom | 633 | 42 |  | 1764 | 40 | 40 | Fan Coil Unit & Air Handling Unit | 14112 | 2.6913 | 1
223 | Prep Classroom | 322 | 21 |  | 312 | 7 | 7 | Fan Coil Unit & Air Handling Unit | 2496 | 7.7404 | 2
224 | Chemistry Classroom | 616 | 41 |  | 1716 | 39 | 39 | Fan Coil Unit & Air Handling Unit | 13728 | 2.6923 | 1
224A | Storage Room | 135 | 9 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
225 | Instructional Room | 483 | 32 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit | 0 | 0 | 0
234 | Lab Classroom | 1107 | 73 |  | 850 | 19 | 19 | Fan Coil Unit & Air Handling Unit | 6800 | 9.7676 | 2
235 | Lab Classroom | 595 | 39 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit | 0 | 0 | 0
235 | Lab Classroom | 465 | 31 |  |  | 0 | 0 | Univent & Air Handling Unit | 0 | 0 | 0
236 | Multipurpose Classroom | 636 | 42 |  | 1156 | 26 | 26 | Fan Coil Unit & Air Handling Unit | 9248 | 4.1263 | 2
237 | Foreign Language Classroom | 613 | 40 |  | 1156 | 26 | 26 | Fan Coil Unit & Air Handling Unit | 9248 | 3.9771 | 1
240 | Commercial Art Classroom | 845 | 56 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit | 0 | 0 | 0
241 | General Classroom | 664 | 44 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit | 0 | 0 | 0
242 | Instructional Room | 551 | 36 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit | 0 | 0 | 0
243 | General Classroom | 518 | 34 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit | 0 | 0 | 0
244 | General Classroom | 737 | 49 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.3897 | 2
245 | General Classroom | 586 | 39 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 5.8757 | 2
246 | General Classroom | 719 | 47 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.2092 | 2
247 | General Classroom | 705 | 47 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.0689 | 2
248 | General Classroom | 909 | 60 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 9.1143 | 2
249 | General Classroom | 779 | 51 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.8108 | 2
251 | General Classroom | 671 | 44 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.7279 | 2
252 | General Classroom | 876 | 58 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 8.7834 | 2
253 | General Classroom | 608 | 40 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.0963 | 2
254 | General Classroom | 633 | 42 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.3469 | 2
255 | General Classroom | 738 | 49 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.3997 | 2
256 | General Classroom | 684 | 45 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.8583 | 2
- | Auditorium | 18527 | 1235 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Cafeteria | 10458 | 697 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Studios Area and Assoc. Corridors, fresh air vent in rooms | 18369 | 1224 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Instrumental Music Area | 14678 | 978 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Gym | 8904 | 593 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | ICM Classroom Area | 11044 | 736 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | Walter Biddle Saul High School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
A1 | A1 | 732 | 48 |  | 864 | 19 | 19 | Air Handling Unit | 6912 | 6.3542 | 2
A1/A2 | Storage | 288 | 19 |  | 255 | 5 | 5 | Air Handling Unit | 2040 | 8.4706 | 2
A2 | A2 | 703 | 46 |  | 864 | 19 | 19 | Air Handling Unit | 6912 | 6.1024 | 2
A3 | A3 | 395 | 26 |  | 792 | 18 | 18 | Univent | 6336 | 3.7405 | 1
A5 | A5 | 1123 | 74 |  | 740 | 16 | 16 | Univent | 5920 | 11.3818 | 3
A21 | A21 | 0 | 0 |  | 570 | 12 | 0 | Air Handling Unit | 4560 | 0 | 0
A22 | A22 | 487 | 32 |  | 620 | 14 | 14 | Univent | 4960 | 5.8911 | 2
A23 | A23 | 699 | 46 |  | 888 | 20 | 20 | Univent | 7104 | 5.9037 | 2
A24 | A24 | 1147 | 76 |  | 888 | 20 | 20 | Univent | 7104 | 9.6875 | 2
A25 | A25 | 878 | 58 |  | 888 | 20 | 20 | Univent | 7104 | 7.4155 | 2
A26 | A26 | 449 | 29 |  | 888 | 20 | 20 | Univent | 7104 | 3.7922 | 1
A29 | A29 |  | 0 | Yes | 864 | 19 | 19 |  | 6912 | 0 | 0
1 | 1 | 240 | 16 |  | 864 | 19 | 19 | Univent | 6912 | 2.0833 | 1
2 | 2 | 70 | 4 |  | 551 | 12 | 12 | Univent | 4408 | 0.95281 | 0
3 | 3 | 900 | 60 |  | 1134 | 25 | 25 | Univent | 9072 | 5.9524 | 2
4 | 4 | 0 | 0 |  | 896 | 20 | 0 | Univent | 7168 | 0 | 0
100 | 100 | 215 | 14 |  | 620 | 14 | 14 | Univent | 4960 | 2.6008 | 1
102 | 102 | 342 | 22 |  | 620 | 14 | 14 | Univent | 4960 | 4.1371 | 2
103 | 103 | 206 | 13 |  | 780 | 17 | 17 | Univent | 6240 | 1.9808 | 1
104 | 104 | 265 | 17 |  | 640 | 14 | 14 | Univent | 5120 | 3.1055 | 1
200 | 200 | 258 | 17 |  | 620 | 14 | 14 | Univent | 4960 | 3.121 | 1
201 | 201 | 244 | 16 |  | 620 | 14 | 14 | Univent | 4960 | 2.9516 | 1
202 | 202 | 251 | 16 |  | 620 | 14 | 14 | Univent | 4960 | 3.0363 | 1
203 | 203 | 173 | 11 |  | 620 | 14 | 14 | Univent | 4960 | 2.0927 | 1
204 | 204 | 226 | 15 |  | 620 | 14 | 14 | Univent | 4960 | 2.7339 | 1
205 | 205 | 468 | 31 |  | 660 | 15 | 15 | Univent | 5280 | 5.3182 | 2
206 | 206 | 560 | 37 |  | 110 | 2 | 2 | Univent | 880 | 38.1818 | 4
208 | 208 | 232 | 15 |  | 600 | 13 | 13 | Univent | 4800 | 2.9 | 1
210 | 210 | 244 | 16 |  | 465 | 10 | 10 | Univent | 3720 | 3.9355 | 1
Food Science | Laboratory |  | 0 |  | 560 | 12 | 12 |  | 4480 | 0 | 0
- | Nurse | 316 | 21 |  | 260 | 5 | 5 | Univent | 2080 | 9.1154 | 2
- | Staff Lounge | 0 | 0 |  | 384 | 8 | 0 | Univent | 3072 | 0 | 0
Sheet Last Modified: | 2021-05-03 | [7 empty] | 0 | 0 | 0
School: | William L. Sayre High School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 518 | 34 |  | 720 | 16 | 16 | Univent | 5760 | 5.3958 | 2
102 | Lounge | 229 | 15 |  | 408 | 9 | 9 | Univent | 3264 | 4.2096 | 2
103 | Music | 327 | 21 |  | 1260 | 28 | 28 | Univent | 10080 | 1.9464 | 1
104 | Office | 0 | 0 |  | 360 | 8 | 0 | Univent | 2880 | 0 | 0
105 | Classroom | 375 | 25 |  | 1504 | 34 | 34 | Univent | 12032 | 1.87 | 1
106 | Classroom | 389 | 25 |  | 768 | 17 | 17 | Univent | 6144 | 3.7988 | 1
107 | Classroom | 517 | 34 |  | 1408 | 32 | 32 | Univent | 11264 | 2.7539 | 1
108 | Classroom | 0 | 0 |  | 768 | 17 | 0 | Univent | 6144 | 0 | 0
109 | Classroom | 0 | 0 | Yes | 1120 | 25 | 25 | Univent | 8960 | 0 | 0
110 | Classroom | 351 | 23 |  | 768 | 17 | 17 | Univent | 6144 | 3.4277 | 1
111 | Classroom | 638 | 42 |  | 1363 | 30 | 30 | Univent | 10904 | 3.5106 | 1
115 | Classroom | 369 | 24 |  | 896 | 20 | 20 | Univent | 7168 | 3.0887 | 1
117 | Classroom | 0 | 0 | Yes | 756 | 17 | 17 | Univent | 6048 | 0 | 0
119 | Classroom | 192 | 12 |  | 868 | 19 | 19 | Univent | 6944 | 1.659 | 1
131 | Classroom | 402 | 26 |  | 729 | 16 | 16 | Univent | 5832 | 4.1358 | 2
133 | Office | 357 | 23 |  | 288 | 6 | 6 | Univent | 2304 | 9.2969 | 2
135 | Boy's Infirmary | 287 | 19 |  | 132 | 3 | 3 | Univent | 1056 | 16.3068 | 3
137 | Girl's Infirmary | 142 | 9 |  | 285 | 6 | 6 | Univent | 2280 | 3.7368 | 1
139 | Classroom | 202 | 13 |  | 1024 | 23 | 23 | Univent | 8192 | 1.4795 | 1
141 | Classroom | 384 | 25 |  | 1188 | 27 | 27 | Univent | 9504 | 2.4242 | 1
200 | Youth Court | 693 | 46 |  | 744 | 16 | 16 | Univent | 5952 | 6.9859 | 2
200 | Classroom | 410 | 27 |  | 592 | 13 | 13 | Univent | 4736 | 5.1943 | 2
203 | Classroom | 808 | 53 |  | 1504 | 34 | 34 | Univent | 12032 | 4.0293 | 2
204 | Classroom | 294 | 19 |  | 744 | 16 | 16 | Univent | 5952 | 2.9637 | 1
205 | Classroom | 762 | 50 |  | 1504 | 34 | 34 | Univent | 12032 | 3.7999 | 1
206 | Classroom | 473 | 31 |  | 696 | 15 | 15 | Univent | 5568 | 5.097 | 2
207 | Classroom | 702 | 46 |  | 1280 | 29 | 29 | Univent | 10240 | 4.1133 | 2
208 | Classroom | 548 | 36 |  | 744 | 16 | 16 | Univent | 5952 | 5.5242 | 2
210 | Classroom | 246 | 16 |  | 744 | 16 | 16 | Univent | 5952 | 2.4798 | 1
211 | Classroom | 835 | 55 |  | 1344 | 30 | 30 | Univent | 10752 | 4.6596 | 2
212 | Classroom | 367 | 24 |  | 744 | 16 | 16 | Univent | 5952 | 3.6996 | 1
215 | Classroom | 0 | 0 |  | 621 | 14 | 0 | Univent | 4968 | 0 | 0
216 | Classroom | 731 | 48 |  | 864 | 19 | 19 | Univent | 6912 | 6.3455 | 2
217 | Classroom | 81 | 5 |  | 990 | 22 | 22 | Univent | 7920 | 0.61364 | 0
219 | Classroom | 0 | 0 |  | 1008 | 22 | 0 | Univent | 8064 | 0 | 0
220 | Classroom | 301 | 20 |  | 744 | 16 | 16 | Univent | 5952 | 3.0343 | 1
221 | Classroom | 92 | 6 |  | 987 | 22 | 22 | Univent | 7896 | 0.69909 | 0
222 | Classroom | 623 | 41 |  | 744 | 16 | 16 | Univent | 5952 | 6.2802 | 2
223 | Classroom | 0 | 0 |  | 902 | 20 | 0 | Univent | 7216 | 0 | 0
224 | Classroom | 419 | 27 |  | 744 | 16 | 16 | Univent | 5952 | 4.2238 | 2
225 | Classroom | 264 | 17 |  | 725 | 16 | 16 | Univent | 5800 | 2.731 | 1
226 | Classroom | 0 | 0 |  | 744 | 16 | 0 | Univent | 5952 | 0 | 0
228 | Classroom | 202 | 13 |  | 840 | 19 | 19 | Univent | 6720 | 1.8036 | 1
229 | Classroom | 401 | 26 |  | 1458 | 33 | 33 | Univent | 11664 | 2.0628 | 1
230 | Classroom | 797 | 53 |  | 792 | 18 | 18 | Univent | 6336 | 7.5473 | 2
231 | Classroom | 509 | 33 |  | 999 | 22 | 22 | Univent | 7992 | 3.8213 | 1
232 | Classroom | 1571 | 104 |  | 960 | 21 | 21 | Univent | 7680 | 12.2734 | 3
234 | Classroom | 1041 | 69 |  | 816 | 18 | 18 | Univent | 6528 | 9.568 | 2
235 | Classroom | 778 | 51 |  | 1400 | 31 | 31 | Univent | 11200 | 4.1679 | 2
236 | Classroom | 809 | 53 |  | 744 | 16 | 16 | Univent | 5952 | 8.1552 | 2
240 | Classroom | 683 | 45 |  | 696 | 15 | 15 | Univent | 5568 | 7.3599 | 2
242 | Classroom | 274 | 18 |  | 912 | 20 | 20 | Univent | 7296 | 2.2533 | 1
244 | Classroom | 0 | 0 |  | 768 | 17 | 0 | Univent | 6144 | 0 | 0
246 | Classroom | 415 | 27 |  | 936 | 21 | 21 | Univent | 7488 | 3.3253 | 1
248 | Classroom | 0 | 0 |  | 666 | 15 | 0 | Univent | 5328 | 0 | 0
- | Auditorium | 0 | 0 |  | 10250 | 232 | 0 | House Fan | 82000 | 0 | 0
- | Cafeteria | 0 | 0 |  | 10540 | 239 | 0 | House Fan | 84320 | 0 | 0
- | Counseling Office | 234 | 15 |  | 187 | 4 | 4 | Univent | 1496 | 9.385 | 2
- | Girls Gym | 0 | 0 | Yes | 7630 | 173 | 173 | House Fan | 61040 | 0 | 0
- | Boys Gym | 0 | 0 | Yes | 7630 | 173 | 173 | House Fan | 61040 | 0 | 0
- | Handball Court | 0 | 0 |  | 800 | 18 | 0 | Air Handling Unit | 6400 | 0 | 0
- | Library | 0 | 0 |  | 3432 | 78 | 0 | Univent | 27456 | 0 | 0
- | IMC Computer | 0 | 0 |  | 744 | 16 | 0 | Univent | 5952 | 0 | 0
- | Kitchen Cooler room | 0 | 0 |  | 182 | 4 | 0 | Univent | 1456 | 0 | 0
- | Locker room | 0 | 0 |  | 180 | 4 | 0 | Air Handling Unit & Univent | 1440 | 0 | 0
- | Boys Locker Rm | 0 | 0 |  | 7470 | 169 | 0 | Whole House | 59760 | 0 | 0
[8 empty] | Return Air Fan & Air Handling Unit | 0 | 0 | 0
- | Girls Locker Rm | 0 | 0 |  | 7470 | 169 | 0 | Whole House | 59760 | 0 | 0
[8 empty] | Return Air Fan & Air Handling Unit | 0 | 0 | 0
- | Main Office | 153 | 10 |  | 1128 | 25 | 25 | Univent | 9024 | 1.0173 | 1
- | Office | 0 | 0 |  | 198 | 4 | 0 | Univent | 1584 | 0 | 0
- | Rec Room | 0 | 0 |  | 9780 | 222 | 0 | House Fan | 78240 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | High School of the Future | [7 empty] | 0 | 0 | 0
Vendor: | Meehan | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Auditorium | 4278 | 285 |  | 4935 | 112 | 112 | Air Handling Unit | 39480 | 6.5015 | 2
10 | Mens Room | 139 | 9 |  | 205 | 4 | 4 | Air Handling Unit | 1640 | 5.0854 | 2
12 | Womens Room | 88 | 5 |  | 215 | 4 | 4 | Air Handling Unit | 1720 | 3.0698 | 1
14 | Storage | 26 | 1 |  | 275 | 6 | 6 | Air Handling Unit | 2200 | 0.70909 | 0
16 | IDF | 15 | 1 |  | 165 | 3 | 3 | Air Handling Unit | 1320 | 0.68182 | 0
17 | Electrical room | 40 | 2 |  | 75 | 1 | 1 | Air Handling Unit | 600 | 4 | 1
19 | Music Library | 30 | 2 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 1.875 | 1
21 | Instrument stroage | 96 | 6 |  | 370 | 8 | 8 | Air Handling Unit | 2960 | 1.9459 | 1
22 | Uniform Room | 49 | 3 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 3.675 | 1
23 | Practice room | 41 | 2 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 3.075 | 1
24 | Practice room | 42 | 2 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 3.15 | 1
25 | Practice room | 43 | 2 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 3.225 | 1
26 | Vocal Music Room | 184 | 12 |  | 1400 | 31 | 31 | Air Handling Unit | 11200 | 0.98571 | 0
27 | Practice Room | 27 | 1 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 2.025 | 1
28 | Practice Room | 36 | 2 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 2.7 | 1
29 | Practice Room | 41 | 2 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 3.075 | 1
30 | Dressing Room | 45 | 3 |  | 1300 | 29 | 29 | Air Handling Unit | 10400 | 0.25962 | 0
31 | Music Intrrument room | 966 | 64 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | 4.025 | 2
32 | Dressing Room | 104 | 6 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.86667 | 0
33 | Dressing Room | 45 | 3 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | 1.125 | 1
34 | Scene shop | 537 | 35 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 3.3563 | 1
58 | Kitchen |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
101 | Vestibule | 102 | 6 |  | 555 | 12 | 12 | Air Handling Unit | 4440 | 1.3784 | 1
103 | Camera Room | 49 | 3 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 3.675 | 1
104 | Security Room | 59 | 3 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 2.2125 | 1
105 | Corridor |  | 0 |  | 50 | 1 | 1 | Air Handling Unit | 400 | 0 | 0
106 | Electric room | 63 | 4 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 3.5 | 1
107 | Equipment room | 55 | 3 |  | 205 | 4 | 4 | Air Handling Unit | 1640 | 2.0122 | 1
110 | waiting room | 101 | 6 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 3.7875 | 1
112 | clerical office | 315 | 21 |  | 635 | 14 | 14 | Air Handling Unit | 5080 | 3.7205 | 1
113 | work/ conf room | 97 | 6 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 3.6375 | 1
114 | Admin conf room | 81 | 5 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 3.0375 | 1
115 | Principal office | 80 | 5 |  | 255 | 5 | 5 | Air Handling Unit | 2040 | 2.3529 | 1
115A | Principal bathroom | 8 | 0 |  | 60 | 1 | 1 | Air Handling Unit | 480 | 1 | 0
117 | Operations office | 24 | 1 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 1.5 | 1
118 | vault room | 25 | 1 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 0.9375 | 0
119 | supply room | 12 | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 0.75 | 0
121 | Nurse | 38 | 2 |  | 95 | 2 | 2 | Air Handling Unit | 760 | 3 | 1
121 | Waiting room | 17 | 1 |  | 95 | 2 | 2 | Air Handling Unit | 760 | 1.3421 | 1
123 | Nurse office | 14 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
125 | Exam room B | 14 | 0 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 1.05 | 1
125 | Exam room A | 13 | 0 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 0.975 | 0
130 | Parent volunteer room | 13 | 0 |  | 480 | 10 | 10 | Air Handling Unit | 3840 | 0.20312 | 0
130 | Parent volunteer room | 13 | 0 |  | 480 | 10 | 10 | Air Handling Unit | 3840 | 0.20312 | 0
131 | Plasma screen room | 9 | 0 |  | 45 | 1 | 1 | Air Handling Unit | 360 | 1.5 | 1
131 | Janitor closet |  | 0 |  | 30 | 0 | 0 | Air Handling Unit | 240 | 0 | 0
132 | Womens room | 25 | 1 |  | 220 | 5 | 5 | Air Handling Unit | 1760 | 0.85227 | 0
132 | Womens Room | 20 | 1 |  | 220 | 5 | 5 | Air Handling Unit | 1760 | 0.68182 | 0
132 | Womens room |  | 0 |  | 220 | 5 | 5 | Air Handling Unit | 1760 | 0 | 0
132 | Womens room |  | 0 |  | 220 | 5 | 5 | Air Handling Unit | 1760 | 0 | 0
133 | Mens room | 49 | 3 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | 1.5 | 1
133 | Mens room | 38 | 2 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | 1.1633 | 1
135 | Mens Room |  | 0 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | 0 | 0
135 | Mens Room |  | 0 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | 0 | 0
139 | Mens locker | 14 | 0 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0.28 | 0
139 | Mens Locker | 14 | 0 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0.28 | 0
139 | Mens Locker | 15 | 1 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0.3 | 0
139 | Mens Locker | 15 | 1 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0.3 | 0
139 | Mens Locker room |  | 0 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0 | 0
139 | Mens locaker room |  | 0 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0 | 0
140 | office | 48 | 3 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | 1.2 | 1
140 | office |  | 0 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | 0 | 0
141 | toilet room | 9 | 0 |  | 90 | 2 | 2 | Air Handling Unit | 720 | 0.75 | 0
141 | toilet room |  | 0 |  | 90 | 2 | 2 | Air Handling Unit | 720 | 0 | 0
142 | Training room | 20 | 1 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0.4 | 0
142 | Training room | 22 | 1 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0.44 | 0
142 | training room |  | 0 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0 | 0
143 | Womens Locker | 14 | 0 |  | 750 | 17 | 14 | Air Handling Unit | 6000 | 0.14 | 0
143 | Womens Locker | 14 | 0 |  | 750 | 17 | 14 | Air Handling Unit | 6000 | 0.14 | 0
143 | Womens Locker | 15 | 1 |  | 750 | 17 | 15 | Air Handling Unit | 6000 | 0.15 | 0
143 | Womens LOcker | 16 | 1 |  | 750 | 17 | 16 | Air Handling Unit | 6000 | 0.16 | 0
143 | Womens locker room |  | 0 |  | 750 | 17 | 17 | Air Handling Unit | 6000 | 0 | 0
143 | Womens locker room |  | 0 |  | 750 | 17 | 17 | Air Handling Unit | 6000 | 0 | 0
144 | Office | 44 | 2 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | 1.1 | 1
144 | office |  | 0 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | 0 | 0
145 | Toilet Room | 9 | 0 |  | 65 | 1 | 1 | Air Handling Unit | 520 | 1.0385 | 1
145 | toilet room |  | 0 |  | 65 | 1 | 1 | Air Handling Unit | 520 | 0 | 0
146 | Corridor | 6 | 0 |  | 150 | 3 | 3 | Air Handling Unit | 1200 | 0.3 | 0
146 | corridor |  | 0 |  | 150 | 3 | 3 | Air Handling Unit | 1200 | 0 | 0
147 | Fitness center | 44 | 2 |  | 1545 | 35 | 35 | Air Handling Unit | 12360 | 0.21359 | 0
147 | Fitness center | 62 | 4 |  | 1545 | 35 | 35 | Air Handling Unit | 12360 | 0.30097 | 0
147 | Fitness center | 47 | 3 |  | 1545 | 35 | 35 | Air Handling Unit | 12360 | 0.22816 | 0
147 | Fitness center |  | 0 |  | 1545 | 35 | 35 | Air Handling Unit | 12360 | 0 | 0
147 | Fitness center |  | 0 |  | 1545 | 35 | 35 | Air Handling Unit | 12360 | 0 | 0
147 | Fitness center |  | 0 |  | 1545 | 35 | 35 | Air Handling Unit | 12360 | 0 | 0
148 | Visitor locker room | 39 | 2 |  | 485 | 11 | 11 | Air Handling Unit | 3880 | 0.60309 | 0
148 | Visitor locker room | 44 | 2 |  | 485 | 11 | 11 | Air Handling Unit | 3880 | 0.68041 | 0
148 | visitor locaker room |  | 0 |  | 485 | 11 | 11 | Air Handling Unit | 3880 | 0 | 0
148 | Visitor locaker room |  | 0 |  | 485 | 11 | 11 | Air Handling Unit | 3880 | 0 | 0
148 | visitor locker room |  | 0 |  | 485 | 11 | 11 | Air Handling Unit | 3880 | 0 | 0
149 | IDF | 15 | 1 |  | 50 | 1 | 1 | Air Handling Unit | 400 | 2.25 | 1
149 | IDF |  | 0 |  | 50 | 1 | 1 | Air Handling Unit | 400 | 0 | 0
150 | work shop |  | 0 |  | 155 | 3 | 3 | Air Handling Unit | 1240 | 0 | 0
151 | Custodial office |  | 0 |  | 155 | 3 | 3 | Air Handling Unit | 1240 | 0 | 0
152 | Corridor | 34 | 2 |  | 2055 | 46 | 34 | Air Handling Unit | 16440 | 0.12409 | 0
152 | Corridor | 28 | 1 |  | 2055 | 46 | 28 | Air Handling Unit | 16440 | 0.10219 | 0
152 | Corridor | 28 | 1 |  | 2055 | 46 | 28 | Air Handling Unit | 16440 | 0.10219 | 0
155 | Corridor |  | 0 |  | 145 | 3 | 3 | Air Handling Unit | 1160 | 0 | 0
156 | Locker room |  | 0 |  | 60 | 1 | 1 | Air Handling Unit | 480 | 0 | 0
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | 0 | 0
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | 0 | 0
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | 0 | 0
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | 0 | 0
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | 0 | 0
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | 0 | 0
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | 0 | 0
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | 0 | 0
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | 0 | 0
158 | Dishwashing |  | 0 |  | 390 | 8 | 8 | Air Handling Unit | 3120 | 0 | 0
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | 0 | 0
160 | Dishwashing |  | 0 |  | 390 | 8 | 8 | Air Handling Unit | 3120 | 0 | 0
161 | Serving |  | 0 |  | 695 | 15 | 15 | Air Handling Unit | 5560 | 0 | 0
161 | Serving |  | 0 |  | 695 | 15 | 15 | Air Handling Unit | 5560 | 0 | 0
161 | Serving |  | 0 |  | 695 | 15 | 15 | Air Handling Unit | 5560 | 0 | 0
162 | Kitchen office |  | 0 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | 0 | 0
164 | Faculty dining |  | 0 |  | 610 | 13 | 13 | Air Handling Unit | 4880 | 0 | 0
164 | Faculty dining |  | 0 |  | 610 | 13 | 13 | Air Handling Unit | 4880 | 0 | 0
166 | Mens Room | 71 | 4 |  | 220 | 5 | 5 | Air Handling Unit | 1760 | 2.4205 | 1
167 | Womens Room | 50 | 3 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | 1.5306 | 1
170 | Special Education | 24 | 1 |  | 1205 | 27 | 24 | Air Handling Unit | 9640 | 0.14938 | 0
170 | Special Education | 21 | 1 |  | 1205 | 27 | 21 | Air Handling Unit | 9640 | 0.13071 | 0
170 | Special Education | 31 | 2 |  | 1205 | 27 | 27 | Air Handling Unit | 9640 | 0.19295 | 0
170 | Special Education | 30 | 2 |  | 1205 | 27 | 27 | Air Handling Unit | 9640 | 0.18672 | 0
173 | Driver education lab | 70 | 4 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0.4375 | 0
173 | Driver education lab | 70 | 4 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0.4375 | 0
173 | Driver education lab | 69 | 4 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0.43125 | 0
173 | Driver education lab | 65 | 4 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0.40625 | 0
174 | Science Prep | 59 | 3 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 2.2125 | 1
175 | Science Lab | 55 | 3 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.27409 | 0
175 | Science LAB | 54 | 3 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.2691 | 0
175 | science lab | 47 | 3 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.23422 | 0
175 | science lab | 41 | 2 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.20432 | 0
175 | science lab | 59 | 3 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.29402 | 0
175 | science lab | 63 | 4 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.31395 | 0
177 | table storage | 0 | 0 |  | 610 | 13 | 0 | Air Handling Unit | 4880 | 0 | 0
177 | table storage | 0 | 0 |  | 610 | 13 | 0 | Air Handling Unit | 4880 | 0 | 0
178 | teacher storage | 0 | 0 |  | 125 | 2 | 0 | Air Handling Unit | 1000 | 0 | 0
179 | services room | 0 | 0 |  | 160 | 3 | 0 | Air Handling Unit | 1280 | 0 | 0
180 | IDF closet | 0 | 0 |  | 155 | 3 | 0 | Air Handling Unit | 1240 | 0 | 0
181 | School store | 0 | 0 |  | 200 | 4 | 0 | Air Handling Unit | 1600 | 0 | 0
183 | Computer lab |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0 | 0
183 | Computer lab | 374 | 24 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 3.1167 | 1
183 | Computer lab | 362 | 24 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 3.0167 | 1
183 | Computer lab | 477 | 31 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 3.975 | 1
183 | Computer lab | 477 | 31 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 3.975 | 1
184 | Interactive learning center | 667 | 44 |  | 2800 | 63 | 63 | Air Handling Unit | 22400 | 1.7866 | 1
184 | Interactive learning center | 473 | 31 |  | 2800 | 63 | 63 | Air Handling Unit | 22400 | 1.267 | 1
184 | Interactive learning center | 570 | 38 |  | 2800 | 63 | 63 | Air Handling Unit | 22400 | 1.5268 | 1
184 | Interactive learning center | 536 | 35 |  | 2800 | 63 | 63 | Air Handling Unit | 22400 | 1.4357 | 1
184 | Interactive learning center | 417 | 27 |  | 2800 | 63 | 63 | Air Handling Unit | 22400 | 1.117 | 1
185 | Individual reading | 37 | 2 |  | 390 | 8 | 8 | Air Handling Unit | 3120 | 0.71154 | 0
185 | Individual reading | 32 | 2 |  | 390 | 8 | 8 | Air Handling Unit | 3120 | 0.61538 | 0
185 | Individual reading | 27 | 1 |  | 390 | 8 | 8 | Air Handling Unit | 3120 | 0.51923 | 0
185 | Individual reading | 31 | 2 |  | 390 | 8 | 8 | Air Handling Unit | 3120 | 0.59615 | 0
186 | Literacy Nook | 35 | 2 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.29167 | 0
186 | Literacy Nook | 28 | 1 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.23333 | 0
186 | Literacy Nook | 20 | 1 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.16667 | 0
186 | Literacy Nook | 20 | 1 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.16667 | 0
186 | Literacy Nook | 20 | 1 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.16667 | 0
186 | Literacy Nook | 20 | 1 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.16667 | 0
186 | Literacy Nook | 30 | 2 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.25 | 0
186 | Literacy Nook | 14 | 0 |  | 900 | 20 | 14 | Air Handling Unit | 7200 | 0.11667 | 0
187 | Copy Room | 111 | 7 |  | 250 | 5 | 5 | Air Handling Unit | 2000 | 3.33 | 1
187 | Copy Room | 86 | 5 |  | 250 | 5 | 5 | Air Handling Unit | 2000 | 2.58 | 1
188 | Conference room | 87 | 5 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 3.2625 | 1
188 | Conferenceroom | 90 | 6 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 3.375 | 1
189 | Visitor room | 165 | 11 |  | 605 | 13 | 13 | Air Handling Unit | 4840 | 2.0455 | 1
189 | Visitor room | 202 | 13 |  | 605 | 13 | 13 | Air Handling Unit | 4840 | 2.5041 | 1
189 | Visitor room | 177 | 11 |  | 605 | 13 | 13 | Air Handling Unit | 4840 | 2.1942 | 1
190 | ILC office | 120 | 8 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 6.6667 | 2
191 | storage | 112 | 7 |  | 170 | 3 | 3 | Air Handling Unit | 1360 | 4.9412 | 2
192 |  | 1210 |  |  |  |  | 1210 | Air Handling Unit | 0 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | 0 | 0
201 | Computer tech |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0 | 0
201 | Computer tech |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0 | 0
201 | Computer tech |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0 | 0
203 | Teachers Copy center |  | 0 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | 0 | 0
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit | 9520 | 0 | 0
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit | 9520 | 0 | 0
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit | 9520 | 0 | 0
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit | 9520 | 0 | 0
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit | 9520 | 0 | 0
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit | 9520 | 0 | 0
205 | Storage |  | 0 |  | 150 | 3 | 3 | Air Handling Unit | 1200 | 0 | 0
207 | Clerical |  | 0 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 0 | 0
207 | Clerical |  | 0 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 0 | 0
208 | Office |  | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 0 | 0
209 | Roster Room |  | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 0 | 0
210 |  |  |  |  | 200 |  | 0 | Air Handling Unit | 1600 | 0 | 0
211 |  |  |  |  | 200 |  | 0 | Air Handling Unit | 1600 | 0 | 0
212 | Staff Room |  | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 0 | 0
213 | Staff Room |  | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 0 | 0
214 | Assistant Principle office |  | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 0 | 0
215 |  |  |  |  | 120 |  | 0 | Air Handling Unit | 960 | 0 | 0
216 | Rest Room |  | 0 |  | 50 | 1 | 1 | Air Handling Unit | 400 | 0 | 0
217 | Records |  | 0 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | 0 | 0
218 |  |  |  |  | 120 |  | 0 | Air Handling Unit | 960 | 0 | 0
219 | PE Director |  | 0 |  | 150 | 3 | 3 | Air Handling Unit | 1200 | 0 | 0
220 |  |  |  |  | 150 |  | 0 | Air Handling Unit | 1200 | 0 | 0
221 |  |  |  |  | 120 |  | 0 | Air Handling Unit | 960 | 0 | 0
222 |  |  |  |  | 120 |  | 0 | Air Handling Unit | 960 | 0 | 0
223 | Counselor office |  | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 0 | 0
224 | Success center |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0 | 0
224 | Success center |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0 | 0
224 | Success center |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0 | 0
224 | Success center |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0 | 0
225 |  |  |  |  | 450 |  | 0 | Air Handling Unit | 3600 | 0 | 0
225 |  |  |  |  | 450 |  | 0 | Air Handling Unit | 3600 | 0 | 0
226 | Computer flex lab |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0 | 0
226 | Computer flex lab |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0 | 0
226 | Computer flex lab |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0 | 0
226 | Computer flex lab |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0 | 0
227 | General classroom |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0 | 0
227 | General Classroom |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0 | 0
227 | General Classroom |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0 | 0
227 | General Classroom |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0 | 0
228 | Art Storage |  | 0 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 0 | 0
229 | [6 empty] | 0 | Air Handling Unit | 0 | 0 | 0
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | 0 | 0
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | 0 | 0
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | 0 | 0
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | 0 | 0
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | 0 | 0
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | 0 | 0
231A | [6 empty] | 0 | Air Handling Unit | 0 | 0 | 0
231A | [6 empty] | 0 | Air Handling Unit | 0 | 0 | 0
231B | Special education |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0 | 0
231B | Special education |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0 | 0
237 | Mens Room | 57 | 3 |  | 250 | 5 | 5 | Air Handling Unit | 2000 | 1.71 | 1
240 | Womens Room | 76 | 5 |  | 255 | 5 | 5 | Air Handling Unit | 2040 | 2.2353 | 1
241 | Storage | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit | 7200 | 0 | 0
241 | Storage | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit | 7200 | 0 | 0
241 | Storage | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit | 7200 | 0 | 0
241 | Storage | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit | 7200 | 0 | 0
242 | chemistry classroom | 53 | 3 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0.265 | 0
242 | chemistry classroom | 47 | 3 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0.235 | 0
242 | chemistry classroom | 51 | 3 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0.255 | 0
242 | chemistry classroom | 56 | 3 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0.28 | 0
242 | chemistry classroom | 56 | 3 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0.28 | 0
242 | chemistry classroom | 41 | 2 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0.205 | 0
243 | Storage | 84 | 5 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 3.15 | 1
244 | Planning | 72 | 4 |  | 290 | 6 | 6 | Air Handling Unit | 2320 | 1.8621 | 1
245 | Biology class | 97 | 6 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | 2.9694 | 1
245 | Biology class | 97 | 6 |  | 1290 | 29 | 29 | Air Handling Unit | 10320 | 0.56395 | 0
245 | Biology class | 78 | 5 |  | 1290 | 29 | 29 | Air Handling Unit | 10320 | 0.45349 | 0
245 | Biology class | 83 | 5 |  | 1290 | 29 | 29 | Air Handling Unit | 10320 | 0.48256 | 0
245 | Biology class | 93 | 6 |  | 1290 | 29 | 29 | Air Handling Unit | 10320 | 0.5407 | 0
245 | Biology class | 51 | 3 |  | 1290 | 29 | 29 | Air Handling Unit | 10320 | 0.29651 | 0
246 | General classroom | 67 | 4 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.55833 | 0
246 | General classroom | 50 | 3 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.41667 | 0
246 | General classroom | 66 | 4 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.55 | 0
246 | General classroom | 63 | 4 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.525 | 0
247 | General classroom | 68 | 4 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.56667 | 0
247 | General classroom | 72 | 4 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.6 | 0
247 | General classroom | 69 | 4 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.575 | 0
247 | General classroom | 81 | 5 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.675 | 0
248 | N/A | 107 | 7 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 5.9444 | 2
249 | General classroom | 59 | 3 |  | 745 | 16 | 16 | Air Handling Unit | 5960 | 0.59396 | 0
249 | General classroom | 62 | 4 |  | 745 | 16 | 16 | Air Handling Unit | 5960 | 0.62416 | 0
249 | General classroom | 90 | 6 |  | 745 | 16 | 16 | Air Handling Unit | 5960 | 0.90604 | 0
249 | General classroom | 77 | 5 |  | 745 | 16 | 16 | Air Handling Unit | 5960 | 0.77517 | 0
250 | General classroom | 68 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.64151 | 0
250 | General classroom | 60 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.56604 | 0
250 | General classroom | 80 | 5 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.75472 | 0
250 | General classroom | 83 | 5 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.78302 | 0
251 | N/A | 173 | 11 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
252 | General classroom | 57 | 3 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.53438 | 0
252 | General classroom | 56 | 3 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.525 | 0
252 | General classroom | 88 | 5 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.825 | 0
252 | General classroom | 79 | 5 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.74062 | 0
253 | Corridor | 26 | 1 |  | 6010 | 136 | 26 | Air Handling Unit | 48080 | 0.032446 | 0
253 | Corridor | 25 | 1 |  | 6010 | 136 | 25 | Air Handling Unit | 48080 | 0.031198 | 0
253 | Corridor | 28 | 1 |  | 6010 | 136 | 28 | Air Handling Unit | 48080 | 0.034942 | 0
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
301 | General classroom |  | 0 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | 0 | 0
301 | General classroom |  | 0 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | 0 | 0
301 | General classroom |  | 0 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | 0 | 0
301 | General classroom |  | 0 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | 0 | 0
302 | SPR |  | 0 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0 | 0
305 | SPR |  | 0 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 0 | 0
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0 | 0
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0 | 0
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0 | 0
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0 | 0
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0 | 0
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0 | 0
308 | Teacher storage |  | 0 |  | 90 | 2 | 2 | Air Handling Unit | 720 | 0 | 0
309 | Resource room |  | 0 |  | 645 | 14 | 14 | Air Handling Unit | 5160 | 0 | 0
309 | Resource room |  | 0 |  | 645 | 14 | 14 | Air Handling Unit | 5160 | 0 | 0
309 | Resource room |  | 0 |  | 645 | 14 | 14 | Air Handling Unit | 5160 | 0 | 0
309 | Resource room |  | 0 |  | 645 | 14 | 14 | Air Handling Unit | 5160 | 0 | 0
315 | Electrical room | 27 | 1 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 1.6875 | 1
316 | IDF closet | 29 | 1 |  | 170 | 3 | 3 | Air Handling Unit | 1360 | 1.2794 | 1
317 | Deans Office | 32 | 2 |  | 140 | 3 | 3 | Air Handling Unit | 1120 | 1.7143 | 1
318 | Mens room | 107 | 7 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | 3.2755 | 1
321 | Womens Room | 110 | 7 |  | 250 | 5 | 5 | Air Handling Unit | 2000 | 3.3 | 1
322 | General classroom | 102 | 6 |  | 815 | 18 | 18 | Air Handling Unit | 6520 | 0.93865 | 0
322 | General classroom | 105 | 7 |  | 815 | 18 | 18 | Air Handling Unit | 6520 | 0.96626 | 0
322 | General classroom | 65 | 4 |  | 815 | 18 | 18 | Air Handling Unit | 6520 | 0.59816 | 0
322 | General classroom | 73 | 4 |  | 815 | 18 | 18 | Air Handling Unit | 6520 | 0.67178 | 0
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit | 12600 | 0 | 0
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit | 12600 | 0 | 0
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit | 12600 | 0 | 0
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit | 12600 | 0 | 0
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit | 12600 | 0 | 0
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit | 12600 | 0 | 0
324 | Science Prep | 54 | 3 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 2.025 | 1
324 | Science Prep | 53 | 3 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 1.9875 | 1
325 | Physics classroom | 16 | 1 |  | 1505 | 34 | 16 | Air Handling Unit | 12040 | 0.079734 | 0
325 | Physics classroom | 116 | 7 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.57807 | 0
325 | Physics classroom | 14 | 0 |  | 1505 | 34 | 14 | Air Handling Unit | 12040 | 0.069767 | 0
325 | Physics classroom | 13 | 0 |  | 1505 | 34 | 13 | Air Handling Unit | 12040 | 0.064784 | 0
325 | Physics classroom | 13 | 0 |  | 1505 | 34 | 13 | Air Handling Unit | 12040 | 0.064784 | 0
325 | Physics classroom | 14 | 0 |  | 1505 | 34 | 14 | Air Handling Unit | 12040 | 0.069767 | 0
326 | General classroom | 86 | 5 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | 0.78182 | 0
326 | General classroom | 85 | 5 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | 0.77273 | 0
326 | General classroom | 99 | 6 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | 0.9 | 0
326 | General classroom | 47 | 3 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | 0.42727 | 0
327 | General classroom | 64 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.60377 | 0
327 | General classroom | 58 | 3 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.54717 | 0
327 | General classroom | 62 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.58491 | 0
327 | General classroom | 43 | 2 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.40566 | 0
328 | N/A | 159 | 10 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 8.8333 | 2
329 | General classroom | 64 | 4 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.6 | 0
329 | General classroom | 59 | 3 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.55312 | 0
329 | General classroom | 65 | 4 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 3.6111 | 1
329 | General classroom | 68 | 4 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.6375 | 0
330 | General classroom | 70 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.66038 | 0
330 | General classroom | 64 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.60377 | 0
330 | General classroom | 74 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.69811 | 0
330 | General classroom | 81 | 5 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.76415 | 0
331 | General classroom | 62 | 4 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 3.4444 | 1
331 | General classroom | 69 | 4 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 3.8333 | 1
331 | General classroom | 73 | 4 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 4.0556 | 2
331 | General classroom | 73 | 4 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 4.0556 | 2
333 | Corridor | 79 | 5 |  | 5535 | 125 | 79 | Air Handling Unit | 44280 | 0.10705 | 0
333 | Corridor | 66 | 4 |  | 5535 | 125 | 66 | Air Handling Unit | 44280 | 0.089431 | 0
333 | Corridor | 81 | 5 |  | 5535 | 125 | 81 | Air Handling Unit | 44280 | 0.10976 | 0
360 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
360 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
360 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Corridor | 9 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Vending machines |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Corridor | 28 | 1 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Corridor | 11 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Kitchen storage |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Gymnasium | 5058 | 337 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Storage |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Fitness center |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Fitness center |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
Sheet Last Modified: | 2021-04-22 | [7 empty] | 0 | 0 | 0
School: | George W. Sharswood Elementary School | House fan Abated | [6 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Building Engineer | 0 | 0 |  | 1288 | 29 | 0 | House Fan | 10304 | 0 | 0
- | Cafeteria | 0 | 0 | Yes | 2000 | 45 | 45 | House Fan | 16000 | 0 | 0
- | Kitchen Storage | 0 | 0 |  | 121 | 2 | 0 | House Fan | 968 | 0 | 0
- | Art Room | 1817 | 121 |  | 1242 | 28 | 28 | House Fan | 9936 | 10.9722 | 3
B9A & B9B | Classroom | 2017 | 134 |  | 1242 | 28 | 28 | House Fan | 9936 | 12.18 | 3
- | Gym | 2219 | 147 |  | 2160 | 49 | 49 | House Fan | 17280 | 7.7049 | 2
- | Main Office | 0 | 0 | Yes | 552 | 12 | 12 | House Fan | 4416 | 0 | 0
- | Nurse Office | 0 | 0 | Yes | 550 | 12 | 12 | House Fan | 4400 | 0 | 0
- | Nurse Exam | 0 | 0 | Yes | 299 | 6 | 6 | House Fan | 2392 | 0 | 0
- | Principal's Office | 0 | 0 | Yes | 288 | 6 | 6 | House Fan | 2304 | 0 | 0
101 | Classroom | 1018 | 67 |  | 550 | 12 | 12 | House Fan | 4400 | 13.8818 | 3
102 | Classroom | 932 | 62 |  | 550 | 12 | 12 | House Fan | 4400 | 12.7091 | 3
103 | Classroom | 484 | 32 |  | 550 | 12 | 12 | House Fan | 4400 | 6.6 | 2
104 | Classroom |  | 0 | Yes | 276 | 6 | 6 | House Fan | 2208 | 0 | 0
105 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | House Fan | 6720 | 0 | 0
106 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | House Fan | 5824 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | House Fan | 5824 | 0 | 0
108 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | House Fan | 5824 | 0 | 0
109 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0
114 | Classroom | 0 | 0 | Yes | 748 | 17 | 17 | House Fan | 5984 | 0 | 0
- | Auditorium | 0 | 0 |  | 2350 | 53 | 0 | House Fan | 18800 | 0 | 0
216 | Music Rm | 0 | 0 | Yes | 1500 | 34 | 34 | House Fan | 12000 | 0 | 0
- | Teacher's Lounge | 0 | 0 |  | 440 | 10 | 0 | House Fan | 3520 | 0 | 0
217 | Classroom | 0 | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | 0 | 0
219 | Classroom | 0 | 0 | Yes | 744 | 16 | 16 | House Fan | 5952 | 0 | 0
223 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0
224 | Classroom | 0 | 0 | Yes | 684 | 15 | 15 | House Fan | 5472 | 0 | 0
225 | Classroom | 695 | 46 |  | 684 | 15 | 15 | House Fan | 5472 | 7.6206 | 2
226 | Classroom | 881 | 58 |  | 684 | 15 | 15 | House Fan | 5472 | 9.6601 | 2
227 | Classroom | 429 | 28 |  | 684 | 15 | 15 | House Fan | 5472 | 4.7039 | 2
228 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | House Fan | 5456 | 0 | 0
329 | Classroom | 281 | 18 |  | 696 | 15 | 15 | House Fan | 5568 | 3.028 | 1
329A | Office | 0 | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | 0 | 0
330 | Classroom | 811 | 54 |  | 696 | 15 | 15 | House Fan | 5568 | 8.7392 | 2
331 | Classroom | 276 | 18 |  | 696 | 15 | 15 | House Fan | 5568 | 2.9741 | 1
332 | Classroom | 0 | 0 | Yes | 576 | 13 | 13 | House Fan | 4608 | 0 | 0
333 | Classroom | 0 | 0 | Yes | 775 | 17 | 17 | House Fan | 6200 | 0 | 0
334 | Classroom | 0 | 0 | Yes | 783 | 17 | 17 | House Fan | 6264 | 0 | 0
335 | Classroom | 0 | 0 | Yes | 783 | 17 | 17 | House Fan | 6264 | 0 | 0
336 | Classroom | 0 | 0 | Yes | 783 | 17 | 17 | House Fan | 6264 | 0 | 0
337 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
338 | Classroom | 0 | 0 | Yes | 552 | 12 | 12 | House Fan | 4416 | 0 | 0
339 | Classroom | 368 | 24 |  | 672 | 15 | 15 | House Fan | 5376 | 4.1071 | 2
340 | Classroom | 326 | 21 |  | 576 | 13 | 13 | House Fan | 4608 | 4.2448 | 2
341 | Classroom | 156 | 10 |  | 576 | 13 | 10 | House Fan | 4608 | 2.0312 | 1
341A | Classroom | 0 | 0 |  | 120 | 2 | 0 | House Fan | 960 | 0 | 0
342A | Classroom | 0 | 0 |  | 288 | 6 | 0 | House Fan | 2304 | 0 | 0
342B | Classroom | 0 | 0 | Yes | 432 | 9 | 9 | House Fan | 3456 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | Shawmont Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | Retest | 2nd Retest | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | CLASS | 0 | 0 | Yes | 1033 | 23 | 23 | Univent | 8264 | 0 | 0
103 | CLASS | 323 | 21 |  | 687 | 15 | 15 | Univent | 5496 | 3.5262 | 1
104 | CLASS | 337 | 22 |  | 568 | 12 | 12 | Univent | 4544 | 4.4498 | 2
105 | Office | 0 | 0 | Yes | 359 | 8 | 8 |  | 2872 | 0 | 0
106 | CLASS | 336 | 22 |  | 687 | 15 | 15 | Univent | 5496 | 3.6681 | 1
107 | CLASS | 327 | 21 |  | 705 | 16 | 16 | Univent | 5640 | 3.4787 | 1
108 | CLASS | 308 | 20 |  | 750 | 17 | 17 | Univent | 6000 | 3.08 | 1
201 | CLASS | 312 | 20 |  | 670 | 15 | 15 | Univent | 5360 | 3.4925 | 1
202 | CLASS | 323 | 21 |  | 536 | 12 | 12 | Univent | 4288 | 4.5196 | 2
203 | CLASS | 372 | 24 |  | 794 | 18 | 18 | Univent | 6352 | 3.5139 | 1
204 | CLASS | 273 | 18 |  | 794 | 18 | 18 | Univent | 6352 | 2.5787 | 1
205 | Therapy | 340 | 22 |  | 370 | 8 | 8 | Univent | 2960 | 6.8919 | 2
206 | CLASS | 325 | 21 |  | 670 | 15 | 15 | Univent | 5360 | 3.6381 | 1
207 | CLASS | 222 | 14 | Yes | 675 | 15 | 15 | Univent | 5400 | 2.4667 | 1
208 | CLASS | 272 | 18 |  | 675 | 15 | 15 | Univent | 5400 | 3.0222 | 1
209 | CLASS | 252 | 16 |  | 670 | 15 | 15 | Univent | 5360 | 2.8209 | 1
300 | CLASS | 281 | 18 |  | 503 | 11 | 11 | Univent | 4024 | 4.1899 | 2
301 | CLASS | 312 | 20 |  | 690 | 15 | 15 | Univent | 5520 | 3.3913 | 1
302 | CLASS | 287 | 19 |  | 704 | 16 | 16 | Univent | 5632 | 3.0575 | 1
303 | CLASS | 276 | 18 |  | 695 | 15 | 15 | Univent | 5560 | 2.9784 | 1
304 | CLASS | 371 | 24 |  | 797 | 18 | 18 | Univent | 6376 | 3.4912 | 1
305 | Office | 96 | 6 | Yes | 448 | 10 | 10 | Univent | 3584 | 1.6071 | 1
305-A | Classroom | 313 | 20 |  | 814 | 18 | 18 | Univent | 6512 | 2.8839 | 1
306 | CLASS | 296 | 19 |  | 675 | 15 | 15 | Univent | 5400 | 3.2889 | 1
307 | CLASS | 279 | 18 |  | 675 | 15 | 15 | Univent | 5400 | 3.1 | 1
308 | CLASS | 0 | 0 | Yes | 695 | 15 | 15 | Univent | 5560 | 0 | 0
309 | CLASS | 370 | 24 |  | 690 | 15 | 15 | Univent | 5520 | 4.0217 | 2
310 | CLASS | 275 | 18 | Yes | 1103 | 25 | 25 | Univent | 8824 | 1.8699 | 1
311 | CLASS | 292 | 19 |  | 935 | 21 | 19 | Univent | 7480 | 2.3422 | 1
312 | CLASS | 0 | 0 | Yes | 1039 | 23 | 23 | Univent | 8312 | 0 | 0
313 | CLASS | 0 | 0 | Yes | 1036 | 23 | 23 | Univent | 8288 | 0 | 0
314 | CLASS | 433 | 28 |  | 1012 | 23 | 23 | Univent | 8096 | 3.209 | 1
315 | CLASS | 388 | 25 |  | 1184 | 26 | 25 | Univent | 9472 | 2.4578 | 1
- | AUDITORIUM | 1331 | 88 |  | 3193 | 72 | 72 | Air Handling Unit | 25544 | 3.1264 | 1
- | BAND RM | 0 | 0 | Yes | 934 | 21 | 21 | Univent | 7472 | 0 | 0
- | COMPUTER LAB | 0 | 0 | Yes | 1103 | 25 | 25 | Univent | 8824 | 0 | 0
- | GYM | 5749 | 383 | Yes | 2610 | 59 | 59 | Air Handling Unit | 20880 | 16.5201 | 3
- | LIBRARY | 750 | 50 |  | 1804 | 41 | 41 | Univent | 14432 | 3.1181 | 1
B-1 | Strings Room | 343 | 22 |  | 641 | 14 | 14 | Univent | 5128 | 4.0133 | 2
B-2 | Music Room | 0 | 0 | Yes | 518 | 11 | 11 | Univent | 4144 | 0 | 0
B-3 | Band Room | 396 | 26 |  | 153 | 3 | 3 | Univent | 1224 | 19.4118 | 3
B-4 | Band Room | 281 | 18 |  | 940 | 21 | 18 | Univent | 7520 | 2.242 | 1
B-6 | Classroom | 395 | 26 |  | 803 | 18 | 18 | Univent | 6424 | 3.6893 | 1
- | Cafeteria | 1132 | 75 |  | 4090 | 92 | 75 | Univent | 32720 | 2.0758 | 1
- | Staff Lounge | 0 | 0 | Yes | 364 | 8 | 8 | Univent | 2912 | 0 | 0
- | Nurse |  | 0 | Yes | 287 | 6 | 6 |  | 2296 | 0 | 0
- | Principal's Office |  | 0 | Yes | 210 | 4 | 4 |  | 1680 | 0 | 0
- | Main Office |  | 0 | Yes | 379 | 8 | 8 |  | 3032 | 0 | 0
Sheet Last Modified: | 2021-04-06 | [7 empty] | 0 | 0 | 0
School: | Isaac A. Sheppard Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 661 | 44 |  | 768 | 17 | 17 | House Fan | 6144 | 6.4551 | 2
101 | Classroom | 894 | 59 |  | 682 | 15 | 15 | House Fan | 5456 | 9.8314 | 2
102 | Classroom | 910 | 60 |  | 682 | 15 | 15 | House Fan | 5456 | 10.0073 | 3
103 | Classroom | 578 | 38 |  | 682 | 15 | 15 | House Fan | 5456 | 6.3563 | 2
200 | Classroom | 665 | 44 |  | 704 | 16 | 16 | House Fan | 5632 | 7.0845 | 2
201 | Classroom | 595 | 39 |  | 704 | 16 | 16 | House Fan | 5632 | 6.3388 | 2
202 | Classroom | 1004 | 66 |  | 682 | 15 | 15 | House Fan | 5456 | 11.0411 | 3
203 | Classroom | 951 | 63 |  | 682 | 15 | 15 | House Fan | 5456 | 10.4582 | 3
204 | Classroom | 949 | 63 |  | 682 | 15 | 15 | House Fan | 5456 | 10.4362 | 3
205 | Classroom | 661 | 44 |  | 682 | 15 | 15 | House Fan | 5456 | 7.2691 | 2
206 | Classroom | 844 | 56 |  | 704 | 16 | 16 | House Fan | 5632 | 8.9915 | 2
300 | Classroom | 840 | 56 |  | 875 | 19 | 19 | House Fan | 7000 | 7.2 | 2
301 | Classroom | 717 | 47 |  | 875 | 19 | 19 | House Fan | 7000 | 6.1457 | 2
302 | Classroom | 963 | 64 |  | 836 | 19 | 19 | House Fan | 6688 | 8.6394 | 2
303 | Classroom | 762 | 50 |  | 836 | 19 | 19 | House Fan | 6688 | 6.8361 | 2
304 | Classroom | 998 | 66 |  | 704 | 16 | 16 | House Fan | 5632 | 10.6321 | 3
305 | Classroom | 847 | 56 |  | 704 | 16 | 16 | House Fan | 5632 | 9.0234 | 2
306 | Classroom | 636 | 42 |  | 704 | 16 | 16 | House Fan | 5632 | 6.7756 | 2
- | Auditorium | 1843 | 122 |  | 1176 | 26 | 26 | House Fan | 9408 | 11.7538 | 3
Main Office | Office |  | 0 | Yes | 255 | 5 | 5 | Air Purifier | 2040 | 0 | 0
Nurse Office | Office |  | 0 | Yes | 122 | 2 | 2 | Air Purifier | 976 | 0 | 0
Principal Office | Office |  | 0 | Yes | 183 | 4 | 4 | Air Purifier | 1464 | 0 | 0
- | Library | 1317 | 87 |  | 851 | 19 | 19 | House Fan | 6808 | 11.6069 | 3
- | Lunch Room/Cafeteria | 1498 | 99 |  | 1311 | 29 | 29 | House Fan | 10488 | 8.5698 | 2
- | Server Room | 0 | 0 |  | 0 | 0 | 0 | Minisplit Air Handling Unit | 0 | 0 | 0
Sheet Last Modified: | 2021-04-07 | [7 empty] | 0 | 0 | 0
School: | Philip Sheridan Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Meehan | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Room | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
102 | Room | 1116 | 74 |  | 768 | 17 | 17 | House Fan | 6144 | 10.8984 | 3
103 | Room | 921 | 61 |  | 768 | 17 | 17 | House Fan | 6144 | 8.9941 | 2
104 | Room | 749 | 49 |  | 720 | 16 | 16 | House Fan | 5760 | 7.8021 | 2
105 | Room | 693 | 46 |  | 720 | 16 | 16 | House Fan | 5760 | 7.2188 | 2
106 | Classroom | 1006 | 67 |  | 768 | 17 | 17 | House Fan | 6144 | 9.8242 | 2
107 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
108 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
109 | Classroom | 861 | 57 |  | 768 | 17 | 17 | House Fan | 6144 | 8.4082 | 2
110 | Classroom | 376 | 25 |  | 768 | 17 | 17 | House Fan | 6144 | 3.6719 | 1
Main Office | Office |  | 0 | Yes | 448 | 10 | 10 | House Fan | 3584 | 0 | 0
110 | Principal office | 597 | 39 |  | 216 | 4 | 4 | House Fan | 1728 | 20.7292 | 3
111 | Nurse | 0 | 0 | Yes | 312 | 7 | 7 | House Fan | 2496 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
202 | Classroom | 877 | 58 |  | 768 | 17 | 17 | House Fan | 6144 | 8.5645 | 2
203 | Classroom | 981 | 65 |  | 720 | 16 | 16 | House Fan | 5760 | 10.2188 | 3
204 | Classroom | 760 | 50 |  | 720 | 16 | 16 | House Fan | 5760 | 7.9167 | 2
205 | Classroom | 737 | 49 |  | 720 | 16 | 16 | House Fan | 5760 | 7.6771 | 2
206 | Classroom | 999 | 66 |  | 768 | 17 | 17 | House Fan | 6144 | 9.7559 | 2
207 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
208 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
209 | Classroom | 1162 | 77 |  | 768 | 17 | 17 | House Fan | 6144 | 11.3477 | 3
209.5 | Office |  | 0 | Yes | 220 | 5 | 5 | House Fan | 1760 | 0 | 0
210 | Classroom | 926 | 61 |  | 768 | 17 | 17 | House Fan | 6144 | 9.043 | 2
210.5 | Office |  | 0 |  | 220 | 5 | 0 | House Fan | 1760 | 0 | 0
211 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
301 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
302 | Classroom | 1253 | 83 |  | 768 | 17 | 17 | House Fan | 6144 | 12.2363 | 3
303 | Classroom | 1038 | 69 |  | 720 | 16 | 16 | House Fan | 5760 | 10.8125 | 3
304 | Classroom | 746 | 49 |  | 720 | 16 | 16 | House Fan | 5760 | 7.7708 | 2
305 | Classroom | 811 | 54 |  | 720 | 16 | 16 | House Fan | 5760 | 8.4479 | 2
306 | Classroom | 1007 | 67 |  | 768 | 17 | 17 | House Fan | 6144 | 9.834 | 2
307 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
308 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
309 | Classroom | 894 | 59 |  | 768 | 17 | 17 | House Fan | 6144 | 8.7305 | 2
310 | Classroom | 1334 | 88 |  | 768 | 17 | 17 | House Fan | 6144 | 13.0273 | 3
311 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
- | Basement East Side |  | 0 |  | 567 | 12 | 0 | House Fan | 4536 | 0 | 0
- | Basement West Side |  | 0 |  | 567 | 12 | 0 | House Fan | 4536 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-19 | [7 empty] | 0 | 0 | 0
School: | SLA @ Beeber | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom |  | 0 |  | 1200 | 27 | 0 |  | 9600 | 0 | 0
101 | Classroom |  | 0 |  | 1150 | 26 | 0 |  | 9200 | 0 | 0
102 | Classroom |  | 0 |  | 925 | 21 | 0 |  | 7400 | 0 | 0
102A | Classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | 0 | 0
103 | Classroom |  | 0 |  | 1636 | 37 | 0 |  | 13088 | 0 | 0
104 | Classroom |  | 0 |  | 875 | 19 | 0 |  | 7000 | 0 | 0
105 | Classroom |  | 0 |  | 909 | 20 | 0 |  | 7272 | 0 | 0
106 | Classroom |  | 0 | Yes | 966 | 21 | 21 |  | 7728 | 0 | 0
106A | Classroom |  | 0 | Yes | 610 | 13 | 13 |  | 4880 | 0 | 0
107 | Classroom |  | 0 |  | 912 | 20 | 0 |  | 7296 | 0 | 0
107A | Classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | 0 | 0
107B | Classroom |  | 0 |  | 360 | 8 | 0 |  | 2880 | 0 | 0
108 | Classroom |  | 0 |  | 912 | 20 | 0 |  | 7296 | 0 | 0
109 | Classroom |  | 0 |  | 700 | 15 | 0 |  | 5600 | 0 | 0
200 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | 0 | 0
201 | Office |  | 0 | Yes | 187 | 4 | 4 |  | 1496 | 0 | 0
202 | Classroom |  | 0 | Yes | 1128 | 25 | 25 |  | 9024 | 0 | 0
203 | Classroom |  | 0 |  | 1128 | 25 | 0 |  | 9024 | 0 | 0
203A | Classroom |  | 0 | Yes | 720 | 16 | 16 |  | 5760 | 0 | 0
203B | Classroom |  | 0 | Yes | 360 | 8 | 8 |  | 2880 | 0 | 0
204 | Classroom |  | 0 | Yes | 664 | 15 | 15 |  | 5312 | 0 | 0
204A | Nurse office |  | 0 |  | 187 | 4 | 0 |  | 1496 | 0 | 0
205 | Office |  | 0 | Yes | 360 | 8 | 8 |  | 2880 | 0 | 0
206-208 | Office |  | 0 |  | 996 | 22 | 0 |  | 7968 | 0 | 0
- | Main Office |  | 0 | Yes | 335 | 7 | 7 |  | 2680 | 0 | 0
- | Principal Office |  | 0 |  | 660 | 15 | 0 |  | 5280 | 0 | 0
Secretary | Office |  | 0 | Yes |  | 0 | 0 |  | 0 | 0 | 0
Conference Room | Conference Room |  | 0 | Yes |  | 0 | 0 |  | 0 | 0 | 0
Cafeteria | Cafeteria |  | 0 |  | 7014 | 159 | 0 |  | 56112 | 0 | 0
209-210 | Library |  | 0 | Yes | 1872 | 42 | 42 |  | 14976 | 0 | 0
211 | Classroom |  | 0 |  | 984 | 22 | 0 |  | 7872 | 0 | 0
212 | Classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | 0 | 0
213-214 | Classroom |  | 0 |  | 1518 | 34 | 0 |  | 12144 | 0 | 0
214A-B | Classroom |  | 0 |  | 1021 | 23 | 0 |  | 8168 | 0 | 0
215 | Office |  | 0 |  | 187 | 4 | 0 |  | 1496 | 0 | 0
216 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
217 | Classroom |  | 0 |  | 816 | 18 | 0 |  | 6528 | 0 | 0
218 | Classroom |  | 0 | Yes | 744 | 16 | 16 |  | 5952 | 0 | 0
219 | Classroom |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | 0 | 0
220 | Classroom |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | 0 | 0
221 | Classroom |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | 0 | 0
222 | Classroom |  | 0 | Yes | 816 | 18 | 18 |  | 6528 | 0 | 0
223 | Classroom |  | 0 | Yes |  | 0 | 0 |  | 0 | 0 | 0
224 | Classroom |  | 0 | Yes |  | 0 | 0 |  | 0 | 0 | 0
316 | Office |  | 0 |  | 187 | 4 | 0 |  | 1496 | 0 | 0
317 | Classroom |  | 0 |  | 665 | 15 | 0 |  | 5320 | 0 | 0
318 | Classroom |  | 0 |  | 836 | 19 | 0 |  | 6688 | 0 | 0
319-320 | Classroom |  | 0 |  | 1488 | 33 | 0 |  | 11904 | 0 | 0
321 | Classroom |  | 0 |  | 749 | 17 | 0 |  | 5992 | 0 | 0
322 | Classroom |  | 0 |  | 766 | 17 | 0 |  | 6128 | 0 | 0
323 | Classroom |  | 0 |  | 808 | 18 | 0 |  | 6464 | 0 | 0
324 | Classroom |  | 0 |  | 668 | 15 | 0 |  | 5344 | 0 | 0
300 | Office |  | 0 |  | 187 | 4 | 0 |  | 1496 | 0 | 0
301-303 | Classroom |  | 0 | Yes | 2072 | 47 | 47 |  | 16576 | 0 | 0
302 | Classroom |  | 0 | Yes | 720 | 16 | 16 |  | 5760 | 0 | 0
303A-B | Classroom |  | 0 | Yes | 1072 | 24 | 24 |  | 8576 | 0 | 0
304 | Classroom |  | 0 | Yes | 1009 | 22 | 22 |  | 8072 | 0 | 0
305 | Classroom |  | 0 |  | 989 | 22 | 0 |  | 7912 | 0 | 0
306 | Classroom |  | 0 |  | 1001 | 22 | 0 |  | 8008 | 0 | 0
307 | Classroom |  | 0 |  | 1361 | 30 | 0 |  | 10888 | 0 | 0
308 | Office |  | 0 |  | 200 | 4 | 0 |  | 1600 | 0 | 0
309-310 | Classroom |  | 0 | Yes | 2085 | 47 | 47 |  | 16680 | 0 | 0
311 | Office |  | 0 | Yes | 651 | 14 | 14 |  | 5208 | 0 | 0
312 | Office |  | 0 |  | 300 | 6 | 0 |  | 2400 | 0 | 0
313-315 | Classroom |  | 0 |  | 2227 | 50 | 0 |  | 17816 | 0 | 0
314A | Classroom |  | 0 |  | 1126 | 25 | 0 |  | 9008 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | Solis-Cohen Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Main Exhaust | Main Exhaust Part 2 | [5 empty] | 0 | 0 | 0
School: | Solis-Cohen Elementary School- Little School House | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Chadwick Part 2 | Chadwick Part 3 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Solis-Cohen Main Building | [8 empty] | 0 | 0 | 0
- | Main Office |  | 0 |  | 120 | 2 | 0 | N/A | 960 | 0 | 0
1 | classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | 0 | 0
2 | classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | 0 | 0
3 | Classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | 0 | 0
4 | classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | 0 | 0
5 | classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | 0 | 0
6 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | 0 | 0
7 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | 0 | 0
8 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | 0 | 0
9 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | 0 | 0
9A | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | 0 | 0
10 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | 0 | 0
11 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | 0 | 0
12 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | 0 | 0
13 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | 0 | 0
14 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | 0 | 0
26 | Classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | 0 | 0
27 | Classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | 0 | 0
- | Esol Room |  | 0 |  | 806 | 18 | 0 | N/A | 6448 | 0 | 0
- | Nurses Office |  | 0 |  | 1116 | 25 | 0 | N/A | 8928 | 0 | 0
- | Gym |  | 0 |  | 5355 | 121 | 0 | N/A | 42840 | 0 | 0
- | Cafeteria |  | 0 |  | 2660 | 60 | 0 | N/A | 21280 | 0 | 0
- | Auditorium |  | 0 |  | 5036 | 114 | 0 | N/A | 40288 | 0 | 0
- | Counselors Office A |  | 0 |  | 352 | 8 | 0 | N/A | 2816 | 0 | 0
- | Counselors Office B |  | 0 |  | 352 | 8 | 0 | N/A | 2816 | 0 | 0
Solis-Cohen LSH | [8 empty] | 0 | 0 | 0
100B | Lobby | 88 | 5 |  | 196 | 4 | 4 | Air Handling Unit | 1568 | 3.3673 | 1
101A | Reception Office | 30 | 2 |  | 256 | 5 | 2 | Air Handling Unit | 2048 | 0.87891 | 0
101B | Clerical Office | 56 | 3 |  | 336 | 7 | 3 | Air Handling Unit | 2688 | 1.25 | 1
101C | Asst. Principals Office | 32 | 2 |  | 598 | 13 | 2 | Air Handling Unit | 4784 | 0.40134 | 0
101D | Nurses Office | 32 | 2 |  | 256 | 5 | 2 | Air Handling Unit | 2048 | 0.9375 | 0
102 | Classroom | 287 | 19 |  | 858 | 19 | 19 | Univent | 6864 | 2.5087 | 1
103 | Classroom | 276 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.4126 | 1
104 | Classroom | 276 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.4126 | 1
105 | Classroom | 292 | 19 |  | 858 | 19 | 19 | Univent | 6864 | 2.5524 | 1
106 | Classroom | 280 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.4476 | 1
107 | Classroom | 274 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.3951 | 1
108 | Classroom | 275 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.4038 | 1
110 | Faculty Dining | 45 | 3 |  | 640 | 14 | 3 | Air Handling Unit | 5120 | 0.52734 | 0
121 | Classroom | 282 | 18 |  | 1092 | 24 | 18 | Univent | 8736 | 1.9368 | 1
122 | Classroom | 289 | 19 |  | 1092 | 24 | 19 | Univent | 8736 | 1.9849 | 1
123 | Classroom | 290 | 19 |  | 1092 | 24 | 19 | Univent | 8736 | 1.9918 | 1
124 | Classroom | 292 | 19 |  | 1092 | 24 | 19 | Univent | 8736 | 2.0055 | 1
125 | Classroom | 320 | 21 |  | 598 | 13 | 13 | Univent | 4784 | 4.0134 | 2
126 | Classroom | 287 | 19 |  | 1092 | 24 | 19 | Univent | 8736 | 1.9712 | 1
- | Lunch Room |  | 0 | Yes | 2160 | 49 | 49 | Air Handling Unit | 17280 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | South Philly HS | [7 empty] | 0 | 0 | 0
Vendor: | Meehan (Auditoriums) | EMCOR (School) | Chadwick Retest | [5 empty] | 0 | 0 | 0
Vendor: | EMCOR (Gym) | EMCOR Retest 2 | EMCOR Retest 3 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Pre Engineering Shop Class A | 0 | 0 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
- | Pre Engineering Shop Class B | 281 | 18 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
- | Computer Lab | 296 | 19 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
004A | Engineering Tech. | 308 | 20 |  | 1716 | 39 | 20 | Nesbitt Unit Ventilator | 13728 | 1.3462 | 1
004B | Engineering Tech. | 0 | 0 |  | 880 | 20 | 0 | Nesbitt Unit Ventilator | 7040 | 0 | 0
004C | Engineering Tech. | 313 | 20 |  | 2640 | 60 | 20 | Nesbitt Unit Ventilator | 21120 | 0.8892 | 0
- | Cafeteria | 7225 | 481 |  | 11200 | 254 | 254 | Nesbitt Unit Ventilator | 89600 | 4.8382 | 2
- | Cafeteria | 5887 | 392 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Culinary Kitchen Hood MAU | 0 | 0 |  |  | 0 | 0 | Make-up Air Unit | 0 | 0 | 0
- | Cafeteria Kitchen Hood | 4929 | 328 |  |  | 0 | 0 | Cafeteria Kitchen Hood | 0 | 0 | 0
005A | Room | 0 | 0 |  | 2204 | 50 | 0 | Nesbitt Unit Ventilator | 17632 | 0 | 0
005B | Room | 0 | 0 |  | 984 | 22 | 0 | Nesbitt Unit Ventilator | 7872 | 0 | 0
- | General Office A | 461 | 30 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
- | General Office B | 394 | 26 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
100 | Room | 384 | 25 |  | 1100 | 25 | 25 | Nesbitt Unit Ventilator | 8800 | 2.6182 | 1
101 | Room | 345 | 23 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 5520 | 3.75 | 1
104 | Room | 276 | 18 |  | 620 | 14 | 14 | Nesbitt Unit Ventilator | 4960 | 3.3387 | 1
105A | Room | 0 | 0 |  | 2709 | 61 | 0 | Nesbitt Unit Ventilator | 21672 | 0 | 0
105B | Room | 207 | 13 |  | 260 | 5 | 5 | Nesbitt Unit Ventilator | 2080 | 5.9712 | 2
106 | Room | 400 | 26 |  | 667 | 15 | 15 | Nesbitt Unit Ventilator | 5336 | 4.4978 | 2
108A | Room | 0 | 0 |  | 2280 | 51 | 0 | Nesbitt Unit Ventilator | 18240 | 0 | 0
108B | Room | 386 | 25 |  | 528 | 12 | 12 | Nesbitt Unit Ventilator | 4224 | 5.483 | 2
108C | Room | 417 | 27 |  | 276 | 6 | 6 | Nesbitt Unit Ventilator | 2208 | 11.3315 | 3
109 | Room | 0 | 0 |  | 812 | 18 | 0 | Nesbitt Unit Ventilator | 6496 | 0 | 0
- | Studio 1 | 308 | 20 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
- | Studio 2 | 419 | 27 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
- | Community Closet | 352 | 23 |  | 899 | 20 | 20 | Nesbitt Unit Ventilator | 7192 | 2.9366 | 1
200 | Room | 371 | 24 |  | 840 | 19 | 19 |  | 6720 | 3.3125 | 1
201 | Room | 363 | 24 |  | 1008 | 22 | 22 | Nesbitt Unit Ventilator | 8064 | 2.7009 | 1
202 | Room | 465 | 31 |  | 1247 | 28 | 28 | Nesbitt Unit Ventilator | 9976 | 2.7967 | 1
203 | Room | 278 | 18 |  | 579 | 13 | 13 | Nesbitt Unit Ventilator | 4632 | 3.601 | 1
204 | Room | 549 | 36 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 5520 | 5.9674 | 2
205A | Room | 0 | 0 |  | 86.25 | 1 | 0 | Nesbitt Unit Ventilator | 690 | 0 | 0
205B | Room | 415 | 27 |  | 150 | 3 | 3 | Nesbitt Unit Ventilator | 1200 | 20.75 | 3
206 | Room | 479 | 31 |  | 705 | 16 | 16 | Nesbitt Unit Ventilator | 5640 | 5.0957 | 2
207 | Room | 426 | 28 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 5520 | 4.6304 | 2
208 | Room | 373 | 24 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 5520 | 4.0543 | 2
209 | Room | 419 | 27 |  | 242 | 5 | 5 | Nesbitt Unit Ventilator | 1936 | 12.9855 | 3
210 | Room | 297 | 19 |  | 900 | 20 | 19 | Nesbitt Unit Ventilator | 7200 | 2.475 | 1
211 | Room | 320 | 21 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 5520 | 3.4783 | 1
214A | Music Room | 350 | 23 |  | 2142 | 48 | 23 | Nesbitt Unit Ventilator | 17136 | 1.2255 | 1
214B | Music Room | 323 | 21 |  | 170 | 3 | 3 | Nesbitt Unit Ventilator | 1360 | 14.25 | 3
217A | Room | 382 | 25 |  | 2560 | 58 | 25 | Nesbitt Unit Ventilator | 20480 | 1.1191 | 1
217B | Room | 411 | 27 |  | 1312 | 29 | 27 | Nesbitt Unit Ventilator | 10496 | 2.3495 | 1
219A | Room | 367 | 24 |  | 899 | 20 | 20 | Nesbitt Unit Ventilator | 7192 | 3.0617 | 1
220 | Room | 380 | 25 |  | 667 | 15 | 15 | Nesbitt Unit Ventilator | 5336 | 4.2729 | 2
221A | Room | 320 | 21 |  | 1984 | 45 | 21 | Nesbitt Unit Ventilator | 15872 | 1.2097 | 1
221B | Room | 279 | 18 |  | 127.5 | 2 | 2 | Nesbitt Unit Ventilator | 1020 | 16.4118 | 3
222A | Room | 329 | 21 |  | 1705 | 38 | 21 | Nesbitt Unit Ventilator | 13640 | 1.4472 | 1
222B | Room | 286 | 19 |  | 110.5 | 2 | 2 | Nesbitt Unit Ventilator | 884 | 19.4118 | 3
223A | Room | 259 | 17 |  | 1519 | 34 | 17 | Nesbitt Unit Ventilator | 12152 | 1.2788 | 1
223B | Room | 217 | 14 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
- | Culinary Arts A | 0 | 0 |  | 130.5 | 2 | 0 | Nesbitt Unit Ventilator | 1044 | 0 | 0
- | Culinary Arts B | 0 | 0 |  | 215 | 4 | 0 | Nesbitt Unit Ventilator | 1720 | 0 | 0
300A | Room | 0 | 0 |  | 112 | 2 | 0 | Nesbitt Unit Ventilator | 896 | 0 | 0
300B | Room | 367 | 24 |  | 149 | 3 | 3 | Nesbitt Unit Ventilator | 1192 | 18.4732 | 3
301 | Room | 416 | 27 |  | 1207 | 27 | 27 | Nesbitt Unit Ventilator | 9656 | 2.5849 | 1
302 | Room | 393 | 26 |  | 1167 | 26 | 26 | Nesbitt Unit Ventilator | 9336 | 2.5257 | 1
303 | Room | 338 | 22 |  | 875 | 19 | 19 | Nesbitt Unit Ventilator | 7000 | 2.8971 | 1
304A | Room | 413 | 27 |  | 193 | 4 | 4 | Nesbitt Unit Ventilator | 1544 | 16.0492 | 3
304B | Room | 427 | 28 |  | 1027 | 23 | 23 | Nesbitt Unit Ventilator | 8216 | 3.1183 | 1
305A | Room | 371 | 24 |  | 259 | 5 | 5 | Nesbitt Unit Ventilator | 2072 | 10.7432 | 3
305B | Room | 365 | 24 |  | 140 | 3 | 3 | Nesbitt Unit Ventilator | 1120 | 19.5536 | 3
306A | Room | 358 | 23 |  | 193 | 4 | 4 | Nesbitt Unit Ventilator | 1544 | 13.9119 | 3
306B | Room | 310 | 20 |  | 948 | 21 | 20 | Nesbitt Unit Ventilator | 7584 | 2.4525 | 1
307A | Room | 298 | 19 |  | 959 | 21 | 19 | Nesbitt Unit Ventilator | 7672 | 2.3306 | 1
308 | Library A | 322 | 21 |  | 6124 | 139 | 21 | Nesbitt Unit Ventilator | 48992 | 0.39435 | 0
308 | Library B | 429 | 28 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
308 | Library C | 381 | 25 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
308 | Library Office | 361 | 24 |  | 84 | 1 | 1 | Nesbitt Unit Ventilator | 672 | 32.2321 | 4
308 | Library Archive Room | 0 | 0 |  | 360 | 8 | 0 | Nesbitt Unit Ventilator | 2880 | 0 | 0
311A | Room | 347 | 23 |  | 973 | 22 | 22 | Nesbitt Unit Ventilator | 7784 | 2.6747 | 1
311B | Room | 374 | 24 |  | 1054 | 23 | 23 | Nesbitt Unit Ventilator | 8432 | 2.6613 | 1
313B | Room | 0 | 0 |  | 526 | 11 | 0 | Nesbitt Unit Ventilator | 4208 | 0 | 0
316 | Room | 686 | 45 |  | 722 | 16 | 16 | Nesbitt Unit Ventilator | 5776 | 7.126 | 2
400A | Room | 314 | 20 |  | 203 | 4 | 4 | Nesbitt Unit Ventilator | 1624 | 11.601 | 3
400B | Room | 208 | 13 |  | 1092 | 24 | 13 | Nesbitt Unit Ventilator | 8736 | 1.4286 | 1
401A | Room | 342 | 22 |  | 878 | 19 | 19 | Nesbitt Unit Ventilator | 7024 | 2.9214 | 1
401B | Room | 318 | 21 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
402A | Room | 0 | 0 |  | 894 | 20 | 0 | Nesbitt Unit Ventilator | 7152 | 0 | 0
402B | Room | 296 | 19 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
403A | Room | 0 | 0 |  | 994 | 22 | 0 | Nesbitt Unit Ventilator | 7952 | 0 | 0
403B | Room | 307 | 20 |  | 458 | 10 | 10 |  | 3664 | 5.0273 | 2
404A | Room | 0 | 0 |  | 952 | 21 | 0 | Nesbitt Unit Ventilator | 7616 | 0 | 0
404B | Room | 297 | 19 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
405A | Room | 306 | 20 |  | 893 | 20 | 20 | Nesbitt Unit Ventilator | 7144 | 2.57 | 1
405B | Room | 0 | 0 |  |  | 0 | 0 | Nesbitt Unit Ventilator | 0 | 0 | 0
406 | Room | 339 | 22 |  | 708 | 16 | 16 | Nesbitt Unit Ventilator | 5664 | 3.5911 | 1
407 | Room | 298 | 19 |  | 715 | 16 | 16 | Nesbitt Unit Ventilator | 5720 | 3.1259 | 1
408 | Room | 321 | 21 |  | 708 | 16 | 16 | Nesbitt Unit Ventilator | 5664 | 3.4004 | 1
409 | Room | 278 | 18 |  | 675 | 15 | 15 | Nesbitt Unit Ventilator | 5400 | 3.0889 | 1
410 | Room | 288 | 19 |  | 694 | 15 | 15 | Nesbitt Unit Ventilator | 5552 | 3.1124 | 1
411 | Room | 333 | 22 |  | 707 | 16 | 16 | Nesbitt Unit Ventilator | 5656 | 3.5325 | 1
412 | Room | 276 | 18 |  | 701 | 15 | 15 | Nesbitt Unit Ventilator | 5608 | 2.9529 | 1
412A | Room | 222 | 14 |  | 471 | 10 | 10 | Nesbitt Unit Ventilator | 3768 | 3.535 | 1
413 | Room | 284 | 18 |  | 711 | 16 | 16 | Nesbitt Unit Ventilator | 5688 | 2.9958 | 1
414 | Room | 0 | 0 |  | 580 | 13 | 0 | Nesbitt Unit Ventilator | 4640 | 0 | 0
415 | Room | 416 | 27 |  | 691 | 15 | 15 | Nesbitt Unit Ventilator | 5528 | 4.5152 | 2
416 | Room | 337 | 22 |  | 660 | 15 | 15 | Nesbitt Unit Ventilator | 5280 | 3.8295 | 1
417 | Room | 349 | 23 |  | 694 | 15 | 15 | Nesbitt Unit Ventilator | 5552 | 3.7716 | 1
418 | Room | 343 | 22 |  | 698 | 15 | 15 | Nesbitt Unit Ventilator | 5584 | 3.6855 | 1
418A | Room | 277 | 18 |  | 341 | 7 | 7 | Nesbitt Unit Ventilator | 2728 | 6.0924 | 2
419A | Room | 0 | 0 |  | 1126 | 25 | 0 | Nesbitt Unit Ventilator | 9008 | 0 | 0
419B | Room | 0 | 0 |  | 135 | 3 | 0 | Nesbitt Unit Ventilator | 1080 | 0 | 0
420A | Room | 322 | 21 |  | 1082 | 24 | 21 | Nesbitt Unit Ventilator | 8656 | 2.232 | 1
420B | Room | 337 | 22 |  | 85 | 1 | 1 | Nesbitt Unit Ventilator | 680 | 29.7353 | 4
421 | Room | 328 | 21 |  | 673 | 15 | 15 | Nesbitt Unit Ventilator | 5384 | 3.6553 | 1
422 | Room | 343 | 22 |  | 673 | 15 | 15 | Nesbitt Unit Ventilator | 5384 | 3.8224 | 1
423 | Room | 322 | 21 |  | 673 | 15 | 15 | Nesbitt Unit Ventilator | 5384 | 3.5884 | 1
424 | Room | 272 | 18 |  | 705 | 16 | 16 | Nesbitt Unit Ventilator | 5640 | 2.8936 | 1
425 | Room | 310 | 20 |  | 706 | 16 | 16 | Nesbitt Unit Ventilator | 5648 | 3.2932 | 1
426 | Room | 285 | 19 |  | 681 | 15 | 15 | Nesbitt Unit Ventilator | 5448 | 3.1388 | 1
427 | Room | 295 | 19 |  | 670 | 15 | 15 | Nesbitt Unit Ventilator | 5360 | 3.3022 | 1
428 | Room | 400 | 26 |  | 681 | 15 | 15 | Nesbitt Unit Ventilator | 5448 | 4.4053 | 2
429 | Room | 309 | 20 |  | 716 | 16 | 16 | Nesbitt Unit Ventilator | 5728 | 3.2367 | 1
432 | Room | 972 | 64 |  | 664 | 15 | 15 | Nesbitt Unit Ventilator | 5312 | 10.9789 | 3
433 | Room | 401 | 26 |  | 705 | 16 | 16 | Nesbitt Unit Ventilator | 5640 | 4.266 | 2
434 | Room | 544 | 36 |  | 677 | 15 | 15 | Nesbitt Unit Ventilator | 5416 | 6.0266 | 2
435 | Room | 503 | 33 |  | 705 | 16 | 16 | Nesbitt Unit Ventilator | 5640 | 5.3511 | 2
500 | Classroom | 0 | 0 |  | 937 | 21 | 0 | Nesbitt Unit Ventilator | 7496 | 0 | 0
500A | Classroom | 0 | 0 |  | 36 | 0 | 0 | Univent | 288 | 0 | 0
500B | Classroom | 158 | 10 |  |  | 0 | 0 | Univent | 0 | 0 | 0
501 A | Classroom | 0 | 0 |  | 845 | 19 | 0 | Univent | 6760 | 0 | 0
501 B | Classroom | 351 | 23 |  |  | 0 | 0 | Univent | 0 | 0 | 0
502 A | Classroom | 208 | 13 |  | 969 | 22 | 13 | Univent | 7752 | 1.6099 | 1
502 B | Classroom | 266 | 17 |  |  | 0 | 0 | Univent | 0 | 0 | 0
503 A | Classroom | 157 | 10 |  | 1035 | 23 | 10 | Univent | 8280 | 1.1377 | 1
503 B | Classroom | 67 | 4 |  | 200 | 4 | 4 | Univent | 1600 | 2.5125 | 1
504 A | Classroom | 330 | 22 |  | 982 | 22 | 22 | Univent | 7856 | 2.5204 | 1
504 B | Classroom | 160 | 10 |  |  | 0 | 0 | Univent | 0 | 0 | 0
505 A | Classroom |  | 0 |  | 942 | 21 | 0 | Univent | 7536 | 0 | 0
505 B | Classroom |  | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
506 | Classroom | 320 | 21 |  | 690 | 15 | 15 | Univent | 5520 | 3.4783 | 1
507 | Classroom | 212 | 14 |  | 690 | 15 | 14 | Univent | 5520 | 2.3043 | 1
508 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Univent | 5520 | 0 | 0
509 | Classroom | 192 | 12 |  | 690 | 15 | 12 | Univent | 5520 | 2.087 | 1
510 A | Classroom | 183 | 12 |  | 990 | 22 | 12 | Univent | 7920 | 1.3864 | 1
510 B | Classroom | 353 | 23 |  | 102 | 2 | 2 | Univent | 816 | 25.9559 | 4
511 | Classroom | 286 | 19 |  | 690 | 15 | 15 | Univent | 5520 | 3.1087 | 1
512 | Classroom | 159 | 10 |  | 690 | 15 | 10 | Univent | 5520 | 1.7283 | 1
513 | Classroom | 183 | 12 |  | 690 | 15 | 12 | Univent | 5520 | 1.9891 | 1
514 | Classroom | 182 | 12 |  | 690 | 15 | 12 | Univent | 5520 | 1.9783 | 1
515 | Classroom | 205 | 13 |  | 690 | 15 | 13 | Univent | 5520 | 2.2283 | 1
516 | Classroom | 65 | 4 |  | 713 | 16 | 4 | Univent | 5704 | 0.68373 | 0
517 | Classroom | 334 | 22 |  | 552 | 12 | 12 | Univent | 4416 | 4.538 | 2
518 | Classroom | 0 | 0 |  | 713 | 16 | 0 | Univent | 5704 | 0 | 0
519 | Classroom | 177 | 11 |  | 616 | 14 | 11 | Univent | 4928 | 2.155 | 1
520 | Classroom | 196 | 13 |  | 616 | 14 | 13 | Univent | 4928 | 2.3864 | 1
521 | Classroom | 155 | 10 |  | 616 | 14 | 10 | Univent | 4928 | 1.8872 | 1
522 | Classroom | 0 | 0 |  | 616 | 14 | 0 | Univent | 4928 | 0 | 0
523 | Classroom | 153 | 10 |  | 705 | 16 | 10 | Univent | 5640 | 1.6277 | 1
524 | Classroom | 63 | 4 |  | 690 | 15 | 4 | Univent | 5520 | 0.68478 | 0
525 | Classroom | 76 | 5 |  | 690 | 15 | 5 | Univent | 5520 | 0.82609 | 0
526 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Univent | 5520 | 0 | 0
527 | Classroom | 167 | 11 |  | 690 | 15 | 11 | Univent | 5520 | 1.8152 | 1
528 | Classroom | 223 | 14 |  | 690 | 15 | 14 | Univent | 5520 | 2.4239 | 1
529 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Univent | 5520 | 0 | 0
530 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Univent | 5520 | 0 | 0
531 | Classroom | 4 | 0 |  | 690 | 15 | 0 | Univent | 5520 | 0.043478 | 0
532 | Classroom | 0 | 0 |  | 705 | 16 | 0 | Univent | 5640 | 0 | 0
533 | Classroom | 163 | 10 |  | 705 | 16 | 10 | Univent | 5640 | 1.734 | 1
534 | Classroom | 0 | 0 |  | 705 | 16 | 0 | Univent | 5640 | 0 | 0
535 | Classroom | 380 | 25 |  | 705 | 16 | 16 | Univent | 5640 | 4.0426 | 2
- | Auditorium | 10918 | 727 |  | 11536 | 262 | 262 | Nesbitt Unit Ventilator | 92288 | 7.0982 | 2
- | Gym | 24019 | 1601 |  | 20384 | 463 | 463 | Air Handling Unit | 163072 | 8.8374 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-05-03 | [7 empty] | 0 | 0 | 0
School: | Southwark Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B4 | Office | 0 | 0 | Yes | 952 | 21 | 21 | House Fan | 7616 | 0 | 0
B5 | Music Room | 1241 | 82 |  | 1800 | 40 | 40 | House Fan | 14400 | 5.1708 | 2
B20 | Basement | 584 | 38 |  | 960 | 21 | 21 | House Fan | 7680 | 4.5625 | 2
B21 | Basement | 515 | 34 |  | 1728 | 39 | 34 | House Fan | 13824 | 2.2352 | 1
102 | First Floor | 532 | 35 |  | 528 | 12 | 12 | House Fan | 4224 | 7.5568 | 2
103 | First Floor | 268 | 17 |  | 660 | 15 | 15 | House Fan | 5280 | 3.0455 | 1
107 | First Floor | 739 | 49 |  | 704 | 16 | 16 | House Fan | 5632 | 7.8729 | 2
112 | Classroom | 579 | 38 |  | 864 | 19 | 19 | House Fan | 6912 | 5.026 | 2
113 | First Floor | 679 | 45 |  | 704 | 16 | 16 | House Fan | 5632 | 7.2337 | 2
114 | Classroom | 716 | 47 |  | 864 | 19 | 19 | House Fan | 6912 | 6.2153 | 2
115 | First Floor | 417 | 27 |  | 792 | 18 | 18 | House Fan | 6336 | 3.9489 | 1
116 | Classroom | 575 | 38 |  | 864 | 19 | 19 | House Fan | 6912 | 4.9913 | 2
117 | Classroom |  | 0 | Yes | 414 | 9 | 9 | House Fan | 3312 | 0 | 0
201 | Second Floor | 772 | 51 |  | 748 | 17 | 17 | House Fan | 5984 | 7.7406 | 2
202 | Classroom | 486 | 32 |  | 864 | 19 | 19 | House Fan | 6912 | 4.2188 | 2
203 | Classroom | 297 | 19 |  | 704 | 16 | 16 | House Fan | 5632 | 3.1641 | 1
204 | Library |  | 0 | Yes | 696 | 15 | 15 | House Fan | 5568 | 0 | 0
205 | Library |  | 0 | Yes | 696 | 15 | 15 | House Fan | 5568 | 0 | 0
206 | Second Floor | 615 | 41 |  | 704 | 16 | 16 | House Fan | 5632 | 6.5518 | 2
207 | Classroom | 633 | 42 |  | 864 | 19 | 19 | House Fan | 6912 | 5.4948 | 2
208 | Second Floor | 332 | 22 |  | 792 | 18 | 18 | House Fan | 6336 | 3.1439 | 1
209 | Classroom | 990 | 66 |  | 864 | 19 | 19 | House Fan | 6912 | 8.5938 | 2
210 | Second Floor | 236 | 15 |  | 660 | 15 | 15 | House Fan | 5280 | 2.6818 | 1
211 | Classroom |  | 0 | Yes | 792 | 18 | 18 | House Fan | 6336 | 0 | 0
212 | Classroom | 1033 | 68 |  | 864 | 19 | 19 | House Fan | 6912 | 8.967 | 2
213 | Second Floor | 675 | 45 |  | 792 | 18 | 18 | House Fan | 6336 | 6.392 | 2
214 | Classroom | 453 | 30 |  | 864 | 19 | 19 | House Fan | 6912 | 3.9323 | 1
215 | Second Floor | 532 | 35 |  | 748 | 17 | 17 | House Fan | 5984 | 5.3342 | 2
216 | Classroom | 562 | 37 |  | 864 | 19 | 19 | House Fan | 6912 | 4.8785 | 2
217 | Room |  | 0 | Yes | 272 | 6 | 6 | House Fan | 2176 | 0 | 0
300 | Classroom |  | 0 | Yes | 480 | 10 | 10 | House Fan | 3840 | 0 | 0
301 | Classroom |  | 0 | Yes | 800 | 18 | 18 | House Fan | 6400 | 0 | 0
302 | Third Floor | 415 | 27 |  | 748 | 17 | 17 | House Fan | 5984 | 4.1611 | 2
303 | Classroom | 291 | 19 |  | 864 | 19 | 19 | House Fan | 6912 | 2.526 | 1
304 | Room |  | 0 | Yes | 336 | 7 | 7 | House Fan | 2688 | 0 | 0
305 | Third Floor | 589 | 39 |  | 704 | 16 | 16 | House Fan | 5632 | 6.2749 | 2
306 | Classroom | 276 | 18 |  | 864 | 19 | 18 | House Fan | 6912 | 2.3958 | 1
307 | Classroom |  | 0 | Yes | 480 | 10 | 10 | House Fan | 3840 | 0 | 0
308 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
309 | Third Floor | 98 | 6 | Yes | 704 | 16 | 16 | House Fan | 5632 | 1.044 | 1
310 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
311 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
312 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
313 | Third Floor | 66 | 4 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0.70312 | 0
314 | Classroom |  | 0 | Yes | 800 | 18 | 18 | House Fan | 6400 | 0 | 0
315 | Classroom | 214 | 14 | Yes | 864 | 19 | 19 | House Fan | 6912 | 1.8576 | 1
316 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
- | Auditorium | 1586 | 105 |  | 1584 | 36 | 36 | House Fan | 12672 | 7.5095 | 2
- | Boy's Bathroom | 541 | 36 |  | 792 | 18 | 18 | House Fan | 6336 | 5.1231 | 2
- | Girl's Bathroom | 582 | 38 |  | 704 | 16 | 16 | House Fan | 5632 | 6.2003 | 2
- | Music Room | 1241 | 82 |  | 1496 | 34 | 34 | House Fan | 11968 | 6.2216 | 2
- | Nurses | 1184 | 78 |  | 150 | 3 | 3 | House Fan | 1200 | 59.2 | 5
- | Gym | 1915 | 127 |  | 1560 | 35 | 35 | House Fan | 12480 | 9.2067 | 2
- | Main Office | 0 | 0 | Yes | 416 | 9 | 9 | House Fan | 3328 | 0 | 0
- | Principal's Office |  | 0 | Yes | 294 | 6 | 6 | House Fan | 2352 | 0 | 0
- | Cafeteria |  | 0 | Yes | 1890 | 42 | 42 | House Fan | 15120 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | Spring Garden | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom |  | 0 | Yes | 475 | 10 | 10 |  | 3800 | 0 | 0
102 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | 0 | 0
103 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | 0 | 0
104A | storage |  | 0 |  | 50 | 1 | 0 |  | 400 | 0 | 0
104B | office |  | 0 | Yes | 80 | 1 | 1 |  | 640 | 0 | 0
104C | office |  | 0 | Yes | 110 | 2 | 2 |  | 880 | 0 | 0
104D | office |  | 0 | Yes | 99 | 2 | 2 |  | 792 | 0 | 0
105A | Classroom |  | 0 | Yes | 483 | 10 | 10 |  | 3864 | 0 | 0
105B | Classroom |  | 0 | Yes | 420 | 9 | 9 |  | 3360 | 0 | 0
201 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | 0 | 0
202 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | 0 | 0
203 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | 0 | 0
204 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | 0 | 0
205 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | 0 | 0
206 | Classroom |  | 0 | Yes | 483 | 10 | 10 |  | 3864 | 0 | 0
207 | Classroom |  | 0 | Yes | 572 | 13 | 13 |  | 4576 | 0 | 0
301 | Classroom |  | 0 | Yes | 741 | 16 | 16 |  | 5928 | 0 | 0
303 | Classroom |  | 0 | Yes | 532 | 12 | 12 |  | 4256 | 0 | 0
304 | Classroom |  | 0 | Yes | 578 | 13 | 13 |  | 4624 | 0 | 0
305 | Classroom |  | 0 | Yes | 720 | 16 | 16 |  | 5760 | 0 | 0
306 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | 0 | 0
307 | Classroom |  | 0 | Yes | 608 | 13 | 13 |  | 4864 | 0 | 0
308 | IMC |  | 0 | Yes | 874 | 19 | 19 |  | 6992 | 0 | 0
310 | Classroom |  | 0 | Yes | 380 | 8 | 8 |  | 3040 | 0 | 0
- | Auditorium |  | 0 | Yes | 2265 | 51 | 51 |  | 18120 | 0 | 0
- | Gym |  | 0 | Yes | 1800 | 40 | 40 |  | 14400 | 0 | 0
- | Lunchroom |  | 0 | Yes | 1520 | 34 | 34 |  | 12160 | 0 | 0
- | Main office |  | 0 | Yes | 231 | 5 | 5 |  | 1848 | 0 | 0
- | Nurses Office |  | 0 | Yes | 189 | 4 | 4 |  | 1512 | 0 | 0
- | Principal Office |  | 0 | Yes | 210 | 4 | 4 |  | 1680 | 0 | 0
- | Staff lounge |  | 0 | Yes | 168 | 3 | 3 |  | 1344 | 0 | 0
- | Teachers lounge |  | 0 | Yes | 195 | 4 | 4 |  | 1560 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-19 | [7 empty] | 0 | 0 | 0
School: | Gilbert Spruance Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | [7 empty] | 0 | 0 | 0
School: | Gilbert Spruance Little School House | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | Chadwick | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Spruance Main Building | [8 empty] | 0 | 0 | 0
100 | Room | 108 | 7 |  | 728 | 16 | 7 | Unit Ventilator | 5824 | 1.1126 | 1
101 & 101B | Room | 208 | 13 |  | 1180 | 26 | 13 | Unit Ventilator | 9440 | 1.322 | 1
102 | Room | 112 | 7 |  | 756 | 17 | 7 | Unit Ventilator | 6048 | 1.1111 | 1
Outside 102 | Hallway | 0 | 0 |  | 370 | 8 | 0 | Unit Ventilator | 2960 | 0 | 0
103 | Room | 188 | 12 |  | 756 | 17 | 12 | Unit Ventilator | 6048 | 1.8651 | 1
104 | Room | 101 | 6 |  | 756 | 17 | 6 | Unit Ventilator | 6048 | 1.002 | 1
105 | Room | 83 | 5 |  | 756 | 17 | 5 | Unit Ventilator | 6048 | 0.82341 | 0
106 | Room | 106 | 7 |  | 756 | 17 | 7 | Unit Ventilator | 6048 | 1.0516 | 1
107 | Room | 119 | 7 | Yes | 756 | 17 | 17 | Unit Ventilator | 6048 | 1.1806 | 1
108 | Room | 115 | 7 |  | 756 | 17 | 7 | Unit Ventilator | 6048 | 1.1409 | 1
109 | Room | 160 | 10 |  | 756 | 17 | 10 | Unit Ventilator | 6048 | 1.5873 | 1
110 | Room | 97 | 6 |  | 756 | 17 | 6 | Unit Ventilator | 6048 | 0.9623 | 0
111 | Room | 145 | 9 |  | 996 | 22 | 9 | Unit Ventilator | 7968 | 1.0919 | 1
112 | Room | 208 | 13 |  | 996 | 22 | 13 | Unit Ventilator | 7968 | 1.5663 | 1
113 | Room | 110 | 7 |  | 996 | 22 | 7 | Unit Ventilator | 7968 | 0.82831 | 0
Outside of 113 | Hallway | 0 | 0 |  | 3700 | 84 | 0 | Unit Ventilator | 29600 | 0 | 0
114 | Room | 240 | 16 |  | 996 | 22 | 16 | Unit Ventilator | 7968 | 1.8072 | 1
115 | Room | 150 | 10 |  | 996 | 22 | 10 | Unit Ventilator | 7968 | 1.1295 | 1
116 | Room | 334 | 22 |  | 719 | 16 | 16 | Unit Ventilator | 5752 | 3.484 | 1
117 | Room | 240 | 16 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 2.4457 | 1
118 | Room | 145 | 9 |  | 1075 | 24 | 9 | Unit Ventilator | 8600 | 1.0116 | 1
118A | Room | 183 | 12 |  | 486 | 11 | 11 | Unit Ventilator | 3888 | 2.8241 | 1
119 | Room | 241 | 16 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 2.4558 | 1
120 | Room | 225 | 15 |  | 1062 | 24 | 15 | Unit Ventilator | 8496 | 1.589 | 1
122 | Room | 248 | 16 |  | 851 | 19 | 16 | Unit Ventilator | 6808 | 2.1857 | 1
124 | Room | 58 | 3 | Yes | 756 | 17 | 17 | Unit Ventilator | 6048 | 0.5754 | 0
- | Auditorium/Gym | 0 | 0 |  | 4620 | 105 | 0 | Unit Ventilator | 36960 | 0 | 0
- | Adjustment Room | 73 | 4 |  | 435 | 9 | 4 | Unit Ventilator | 3480 | 1.2586 | 1
200 | Room | 148 | 9 |  | 756 | 17 | 9 | Unit Ventilator | 6048 | 1.4683 | 1
201 | Room | 136 | 9 |  | 756 | 17 | 9 | Unit Ventilator | 6048 | 1.3492 | 1
202 | Room | 179 | 11 |  | 690 | 15 | 11 | Unit Ventilator | 5520 | 1.9457 | 1
Outside of 202 | Hallway | 0 | 0 |  | 3700 | 84 | 0 | Unit Ventilator | 29600 | 0 | 0
203 | Room | 134 | 8 |  | 756 | 17 | 8 | Unit Ventilator | 6048 | 1.3294 | 1
204 | Room | 114 | 7 |  | 756 | 17 | 7 | Unit Ventilator | 6048 | 1.131 | 1
205 | Room | 97 | 6 |  | 756 | 17 | 6 | Unit Ventilator | 6048 | 0.9623 | 0
206 | Room | 83 | 5 |  | 756 | 17 | 5 | Unit Ventilator | 6048 | 0.82341 | 0
207 | Room | 102 | 6 |  | 756 | 17 | 6 | Unit Ventilator | 6048 | 1.0119 | 1
208 | Room | 139 | 9 |  | 756 | 17 | 9 | Unit Ventilator | 6048 | 1.379 | 1
209 | Room | 121 | 8 |  | 756 | 17 | 8 | Unit Ventilator | 6048 | 1.2004 | 1
210 | Room | 90 | 6 |  | 756 | 17 | 6 | Unit Ventilator | 6048 | 0.89286 | 0
211 | Room | 199 | 13 |  | 756 | 17 | 13 | Unit Ventilator | 6048 | 1.9742 | 1
212 | Room | 134 | 8 |  | 756 | 17 | 8 | Unit Ventilator | 6048 | 1.3294 | 1
213A | Room | 103 | 6 |  | 420 | 9 | 6 | Unit Ventilator | 3360 | 1.8393 | 1
Outside of Room 213A | Hallway | 0 | 0 |  | 756 | 17 | 0 | Unit Ventilator | 6048 | 0 | 0
213B | Room | 267 | 17 |  | 548 | 12 | 12 | Unit Ventilator | 4384 | 3.6542 | 1
214 | Room | 114 | 7 |  | 755 | 17 | 7 | Unit Ventilator | 6040 | 1.1325 | 1
214A | Room | 0 | 0 |  | 756 | 17 | 0 | Unit Ventilator | 6048 | 0 | 0
215 | Room | 53 | 3 |  | 756 | 17 | 3 | Unit Ventilator | 6048 | 0.52579 | 0
216 | Room | 122 | 8 |  | 756 | 17 | 8 | Unit Ventilator | 6048 | 1.2103 | 1
217 | Room | 83 | 5 |  | 756 | 17 | 5 | Unit Ventilator | 6048 | 0.82341 | 0
Outside of Room 217 | Hallway | 0 | 0 |  | 1850 | 42 | 0 | Unit Ventilator | 14800 | 0 | 0
218 | Room | 139 | 9 |  | 718 | 16 | 9 | Unit Ventilator | 5744 | 1.4519 | 1
220 | Room | 131 | 8 |  | 724 | 16 | 8 | Unit Ventilator | 5792 | 1.357 | 1
- | Cafeteria | 263 | 17 | Yes | 4550 | 103 | 103 | Unit Ventilator | 36400 | 0.43352 | 0
- | Main Office | 315 | 21 |  | 456 | 10 | 10 |  | 3648 | 5.1809 | 2
- | Principal | 240 | 16 |  | 241 | 5 | 5 |  | 1928 | 7.4689 | 2
- | Nurse | 374 | 24 |  | 374 | 8 | 8 |  | 2992 | 7.5 | 2
- | Main Entrance Lobby | 1498 | 99 |  | 1498 | 34 | 34 | Unit Ventilator | 11984 | 7.5 | 2
Little School House | [8 empty] | 0 | 0 | 0
1 | Room | 1072 | 71 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 7.6136 | 2
2 | Room | 938 | 62 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 6.6619 | 2
3 | Room | 741 | 49 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 5.2628 | 2
4 | Room | 1188 | 79 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 8.4375 | 2
5 | Room | 682 | 45 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 4.8438 | 2
6 | Room | 713 | 47 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 5.0639 | 2
7 | Room | 554 | 36 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 3.9347 | 1
8 | Room | 690 | 46 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 4.9006 | 2
9 | Room | 1558 | 103 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 11.0653 | 3
10 | Room | 853 | 56 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 6.0582 | 2
11 | Room | 1512 | 100 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 10.7386 | 3
12 | Room | 946 | 63 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 6.7188 | 2
- | CLI Office | 159 | 10 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 9.9375 | 2
- | Entrance/Lobby | 0 | 0 |  | 210 | 4 | 0 | Air Handling Unit | 1680 | 0 | 0
- | Hallway | 0 | 0 |  | 1950 | 44 | 0 | Air Handling Unit | 15600 | 0 | 0
- | Main Office | 165 | 11 |  | 315 | 7 | 7 | Air Handling Unit | 2520 | 3.9286 | 1
- | Office | 158 | 10 |  | 126 | 2 | 2 | Air Handling Unit | 1008 | 9.4048 | 2
- | Storage | 0 | 0 |  | 215 | 4 | 0 | Air Handling Unit | 1720 | 0 | 0
- | Teachers Lounge | 331 | 22 |  | 72 | 1 | 1 | Air Handling Unit | 576 | 34.4792 | 4
- | Therapy Room | 0 | 0 |  | 72 | 1 | 0 | Air Handling Unit | 576 | 0 | 0
- | Girl's RR | 0 | 0 |  | 272 | 6 | 0 | Air Handling Unit | 2176 | 0 | 0
- | Boy's RR | 0 | 0 |  | 272 | 6 | 0 | Air Handling Unit | 2176 | 0 | 0
- | Men's RR | 0 | 0 |  | 77 | 1 | 0 | Air Handling Unit | 616 | 0 | 0
- | Women's RR | 0 | 0 |  | 131 | 2 | 0 | Air Handling Unit | 1048 | 0 | 0
- | Multi-purpose Room | 2808 | 187 |  | 1998 | 45 | 45 | Fan Coil Unit | 15984 | 10.5405 | 3
Sheet Last Modified: | 2021-04-29 | [7 empty] | 0 | 0 | 0
School: | Edwin M. Stanton Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Meehan | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Main Office | 0 | 0 | Yes | 375 | 8 | 8 | House Fan | 3000 | 0 | 0
101 | Classroom | 829 | 55 |  | 870 | 19 | 19 | House Fan | 6960 | 7.1466 | 2
102 | Classroom | 598 | 39 |  | 870 | 19 | 19 | House Fan | 6960 | 5.1552 | 2
103 | Classroom | 630 | 42 |  | 899 | 20 | 20 | House Fan | 7192 | 5.2558 | 2
104 | Classroom | 635 | 42 |  | 864 | 19 | 19 | House Fan | 6912 | 5.5122 | 2
105 | Classroom | 639 | 42 |  | 870 | 19 | 19 | House Fan | 6960 | 5.5086 | 2
106 | Classroom | 764 | 50 |  | 870 | 19 | 19 | House Fan | 6960 | 6.5862 | 2
107 | Classroom | 836 | 55 |  | 1450 | 32 | 32 | House Fan | 11600 | 4.3241 | 2
201 | Classroom | 697 | 46 |  | 870 | 19 | 19 | House Fan | 6960 | 6.0086 | 2
202 | Classroom | 500 | 33 |  | 870 | 19 | 19 | House Fan | 6960 | 4.3103 | 2
203 | Classroom | 526 | 35 |  | 870 | 19 | 19 | House Fan | 6960 | 4.5345 | 2
204 | Classroom | 527 | 35 |  | 870 | 19 | 19 | House Fan | 6960 | 4.5431 | 2
205 | Library | 907 | 60 |  | 1363 | 30 | 30 | House Fan | 10904 | 4.9908 | 2
206 | Classroom | 531 | 35 |  | 870 | 19 | 19 | House Fan | 6960 | 4.5776 | 2
207 | Classroom | 706 | 47 |  | 870 | 19 | 19 | House Fan | 6960 | 6.0862 | 2
208 | Classroom | 806 | 53 |  | 870 | 19 | 19 | House Fan | 6960 | 6.9483 | 2
301 | Gym | 61 | 4 |  | 870 | 19 | 4 | House Fan | 6960 | 0.52586 | 0
302 | Gym | 432 | 28 |  | 870 | 19 | 19 | House Fan | 6960 | 3.7241 | 1
302 | Classroom | 560 | 37 |  | 870 | 19 | 19 | House Fan | 6960 | 4.8276 | 2
304 | Classroom | 715 | 47 |  | 870 | 19 | 19 | House Fan | 6960 | 6.1638 | 2
305 | Classroom | 833 | 55 |  | 1316 | 29 | 29 | House Fan | 10528 | 4.7473 | 2
306 | Classroom | 525 | 35 |  | 870 | 19 | 19 | House Fan | 6960 | 4.5259 | 2
307 | Classroom | 988 | 65 |  | 870 | 19 | 19 | House Fan | 6960 | 8.5172 | 2
308 | Classroom | 230 | 15 |  | 870 | 19 | 15 | House Fan | 6960 | 1.9828 | 1
Counselor | Office |  | 0 | Yes | 240 | 5 | 5 | House Fan | 1920 | 0 | 0
- | Cafeteria | 0 | 0 | Yes | 2400 | 54 | 54 | House Fan | 19200 | 0 | 0
- | Nurse Office | 0 | 0 | Yes | 200 | 4 | 4 | House Fan | 1600 | 0 | 0
- | Principal Office | 0 | 0 | Yes | 256 | 5 | 5 | House Fan | 2048 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-15 | [7 empty] | 0 | 0 | 0
School: | Allen M. Stearne Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | EMCOR Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | classroom | 529 | 35 |  | 730 | 16 | 16 | Perimeter Heater | 5840 | 5.4349 | 2
100A | First Floor | 30 | 2 |  | 222 | 5 | 2 | Perimeter Heater | 1776 | 1.0135 | 1
101 | classroom | 316 | 21 |  | 1197 | 27 | 21 | Perimeter Heater | 9576 | 1.9799 | 1
102 | classroom | 452 | 30 |  | 753 | 17 | 17 | Perimeter Heater | 6024 | 4.502 | 2
102A | First Floor | 284 | 18 |  | 401 | 9 | 9 | Perimeter Heater | 3208 | 5.3117 | 2
103 | classroom | 569 | 37 |  | 1175 | 26 | 26 | Perimeter Heater | 9400 | 3.6319 | 1
104 | classroom | 224 | 14 |  | 716 | 16 | 14 | Perimeter Heater | 5728 | 2.3464 | 1
105 | Classroom |  | 0 |  | 319 | 7 | 0 | Perimeter Heater | 2552 | 0 | 0
106 | classroom | 189 | 12 |  | 730 | 16 | 12 | Perimeter Heater | 5840 | 1.9418 | 1
108A | First Floor | 276 | 18 |  | 810 | 18 | 18 | Perimeter Heater | 6480 | 2.5556 | 1
108B | First Floor | 59 | 3 |  | 129 | 2 | 2 | Perimeter Heater | 1032 | 3.4302 | 1
108C | First Floor | 109 | 7 |  | 146 | 3 | 3 | Perimeter Heater | 1168 | 5.5993 | 2
108D | First Floor | 54 | 3 |  | 86 | 1 | 1 | Perimeter Heater | 688 | 4.7093 | 2
108E | First Floor | 87 | 5 |  | 75 | 1 | 1 | Perimeter Heater | 600 | 8.7 | 2
108F | First Floor | 62 | 4 |  | 94 | 2 | 2 | Perimeter Heater | 752 | 4.9468 | 2
200 | classroom | 274 | 18 |  | 740 | 16 | 16 | Perimeter Heater | 5920 | 2.777 | 1
201 | classroom | 322 | 21 |  | 717 | 16 | 16 | Perimeter Heater | 5736 | 3.3682 | 1
202 | classroom | 313 | 20 |  | 705 | 16 | 16 | Perimeter Heater | 5640 | 3.3298 | 1
203 | classroom | 337 | 22 |  | 739 | 16 | 16 | Perimeter Heater | 5912 | 3.4202 | 1
204 | classroom | 329 | 21 |  | 737 | 16 | 16 | Perimeter Heater | 5896 | 3.348 | 1
205 | classroom | 325 | 21 |  | 756 | 17 | 17 | Perimeter Heater | 6048 | 3.2242 | 1
206 | classroom | 334 | 22 |  | 745 | 16 | 16 | Perimeter Heater | 5960 | 3.3624 | 1
207 | classroom | 0 | 0 | Yes | 386 | 8 | 8 | Perimeter Heater | 3088 | 0 | 0
208 | classroom | 328 | 21 |  | 882 | 20 | 20 | Perimeter Heater | 7056 | 2.7891 | 1
209 | classroom | 109 | 7 | Yes | 639 | 14 | 14 | Perimeter Heater | 5112 | 1.2793 | 1
209A | classroom | 80 | 5 |  | 152 | 3 | 3 | Perimeter Heater | 1216 | 3.9474 | 1
209B | classroom | 0 | 0 |  | 125 | 2 | 0 | Perimeter Heater | 1000 | 0 | 0
210 | classroom | 549 | 36 |  | 1185 | 26 | 26 | Perimeter Heater | 9480 | 3.4747 | 1
211 | classroom | 845 | 56 |  | 728 | 16 | 16 | Perimeter Heater | 5824 | 8.7054 | 2
212 | classroom | 116 | 7 |  | 434 | 9 | 7 | Perimeter Heater | 3472 | 2.0046 | 1
213 | classroom | 131 | 8 |  | 224 | 5 | 5 | Perimeter Heater | 1792 | 4.3862 | 2
300 | classroom | 532 | 35 |  | 763 | 17 | 17 | Perimeter Heater | 6104 | 5.2294 | 2
300A | classroom | 395 | 26 |  | 224 | 5 | 5 | Perimeter Heater | 1792 | 13.2254 | 3
301 | classroom | 350 | 23 |  | 755 | 17 | 17 | Perimeter Heater | 6040 | 3.4768 | 1
302 | classroom | 289 | 19 |  | 746 | 16 | 16 | Perimeter Heater | 5968 | 2.9055 | 1
303 | classroom | 447 | 29 |  | 722 | 16 | 16 | Perimeter Heater | 5776 | 4.6434 | 2
304 | classroom | 434 | 28 |  | 745 | 16 | 16 | Perimeter Heater | 5960 | 4.3691 | 2
305 | classroom | 360 | 24 |  | 747 | 16 | 16 | Perimeter Heater | 5976 | 3.6145 | 1
306 | classroom | 534 | 35 |  | 715 | 16 | 16 | Perimeter Heater | 5720 | 5.6014 | 2
307 | Classroom |  | 0 |  | 790 | 17 | 0 | Perimeter Heater | 6320 | 0 | 0
308 | classroom | 278 | 18 |  | 717 | 16 | 16 | Perimeter Heater | 5736 | 2.9079 | 1
- | Auditorium | 0 | 0 |  | 2919 | 66 | 0 | AHU | 23352 | 0 | 0
- | Cafeteria/Gym | 0 | 0 | Yes | 3719 | 84 | 84 | AHU | 29752 | 0 | 0
- | Dean's Office (Temple) | 72 | 4 |  | 106 | 2 | 2 | Perimter Heater | 848 | 5.0943 | 2
- | Health Office | 274 | 18 |  | 294 | 6 | 6 | Perimter Heater | 2352 | 6.9898 | 2
- | Office | 300 | 20 |  | 984 | 22 | 20 | Perimter Heater | 7872 | 2.2866 | 1
- | Principal | 187 | 12 |  | 321 | 7 | 7 | Perimter Heater | 2568 | 4.3692 | 2
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | Edward Steel Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCORE Fluidics | Exhaust Report | [6 empty] | 0 | 0 | 0
| 2-15-2021 Retest | 2-22-21 Retest | 4-12-21 Retest | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Storeroom | 0 | 0 | Yes | 323 | 7 | 7 | Air Coil Unit | 2584 | 0 | 0
101A - C | Office | 0 | 0 | Yes | 356 | 8 | 8 | Air Coil Unit | 2848 | 0 | 0
102 | Main Office- open office | 0 | 0 | Yes | 512 | 11 | 11 | Air Coil Unit | 4096 | 0 | 0
102 | Main Office- admin ofc | 0 | 0 |  | 121 | 2 | 0 | Air Coil Unit | 968 | 0 | 0
102 | Main Office- asst principals ofc | 0 | 0 | Yes | 121 | 2 | 2 | Air Coil Unit | 968 | 0 | 0
102 | Main Office- principals ofc | 0 | 0 | Yes | 143 | 3 | 3 | Air Coil Unit | 1144 | 0 | 0
102 | Main Office- conf rm | 0 | 0 | Yes | 204 | 4 | 4 | Air Coil Unit | 1632 | 0 | 0
103 | Lounge | 0 | 0 | Yes | 676 | 15 | 15 | Air Coil Unit | 5408 | 0 | 0
104 | counselors ofc | 0 | 0 | Yes | 385 | 8 | 8 | Air Coil Unit | 3080 | 0 | 0
105 | Classroom | 46 | 3 | Yes | 660 | 15 | 15 | Air Handling Unit | 5280 | 0.52273 | 0
106 | data room | 0 | 0 | Yes | 1364 | 31 | 31 | Air Coil Unit | 10912 | 0 | 0
107 | Classroom | 363 | 24 | Yes | 1364 | 31 | 31 | Air Handling Unit | 10912 | 1.996 | 1
109 | Classroom | 257 | 17 | Yes | 1364 | 31 | 31 | Air Handling Unit | 10912 | 1.4131 | 1
110 | nurse str | 0 | 0 | Yes | 886 | 20 | 20 | Air Coil Unit | 7088 | 0 | 0
- | Nurse Waiting Area |  | 0 | Yes | 208 | 4 | 4 |  | 1664 | 0 | 0
111 | Classroom | 450 | 30 | Yes | 1364 | 31 | 31 | Air Handling Unit | 10912 | 2.4743 | 1
113 | Classroom | 338 | 22 | Yes | 1364 | 31 | 31 | Air Handling Unit | 10912 | 1.8585 | 1
- | AUDITORIUM | 475 | 31 | Yes | 2482 | 56 | 56 | Air Coil Unit | 19856 | 1.4353 | 1
- | CAFETERIA | 0 | 0 | Yes | 3478 | 79 | 79 | Air Coil Unit | 27824 | 0 | 0
- | Cafeteria Office |  | 0 | Yes | 300 | 6 | 6 |  | 2400 | 0 | 0
- | IMC | 2021 | 134 |  | 3283 | 74 | 74 | Air Coil Unit | 26264 | 4.617 | 2
201 | Classroom | 163 | 10 | Yes | 1330 | 30 | 30 | Air Handling Unit | 10640 | 0.91917 | 0
202 | Classroom | 250 | 16 | Yes | 1330 | 30 | 30 | Air Handling Unit | 10640 | 1.4098 | 1
203 | Classroom | 188 | 12 | Yes | 1147 | 26 | 26 | Air Handling Unit | 9176 | 1.2293 | 1
204 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0
205 | Classroom | 194 | 12 | Yes | 1147 | 26 | 26 | Air Handling Unit | 9176 | 1.2685 | 1
206 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0
207 | Classroom | 144 | 9 | Yes | 1147 | 26 | 26 | Air Handling Unit | 9176 | 0.94159 | 0
208 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0
209 | Classroom | 186 | 12 | Yes | 1147 | 26 | 26 | Air Handling Unit | 9176 | 1.2162 | 1
210 | Classroom | 196 | 13 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 1.2816 | 1
211 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0
212 | Classroom | 287 | 19 | Yes | 1130 | 25 | 25 | Air Coil Unit | 9040 | 1.9049 | 1
213 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | Air Coil Unit | 6960 | 0 | 0
214 | Classroom |  | 0 | Yes | 870 | 19 | 19 | Air Coil Unit | 6960 | 0 | 0
215 | Office | 0 | 0 | Yes | 345 | 7 | 7 | Air Coil Unit | 2760 | 0 | 0
216 | Classroom | 0 | 0 | Yes | 588 | 13 | 13 | Air Coil Unit | 4704 | 0 | 0
219 | Classroom |  | 0 | Yes | 462 | 10 | 10 | Air Coil Unit | 3696 | 0 | 0
220 | team office | 0 | 0 | Yes | 462 | 10 | 10 | Air Coil Unit | 3696 | 0 | 0
301 | Classroom | 0 | 0 | Yes | 1330 | 30 | 30 | Air Coil Unit | 10640 | 0 | 0
302 | Classroom | 0 | 0 | Yes | 1330 | 30 | 30 | Air Coil Unit | 10640 | 0 | 0
303 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0
304 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0
305 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0
306 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0
307 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0
308 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0
309 | Classroom | 0 | 0 | Yes | 1155 | 26 | 26 | Air Coil Unit | 9240 | 0 | 0
310 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0
311 | Classroom | 0 | 0 | Yes | 1330 | 30 | 30 | Air Coil Unit | 10640 | 0 | 0
312 | Classroom | 482 | 32 |  | 1330 | 30 | 30 | Air Coil Unit | 10640 | 2.718 | 1
313 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | Air Coil Unit | 6960 | 0 | 0
314 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | Air Coil Unit | 6960 | 0 | 0
315 | Staff Lounge |  | 0 | Yes | 330 | 7 | 7 | Air Coil Unit | 2640 | 0 | 0
319 | Classroom |  | 0 | Yes | 462 | 10 | 10 | Air Coil Unit | 3696 | 0 | 0
320 | team office |  | 0 | Yes | 462 | 10 | 10 | Air Coil Unit | 3696 | 0 | 0
- | imc office | 105 | 7 | Yes | 3283 | 74 | 74 | Air Coil Unit | 26264 | 0.23987 | 0
- | imc storage | 70 | 4 |  | 255 | 5 | 4 | Air Coil Unit | 2040 | 2.0588 | 1
- | material production | 210 | 14 | Yes | 625 | 14 | 14 | Air Coil Unit | 5000 | 2.52 | 1
- | open library | 1180 | 78 |  | 3360 | 76 | 76 | Air Coil Unit | 26880 | 2.6339 | 1
- | Gym Office |  | 0 | Yes | 168 | 3 | 3 |  | 1344 | 0 | 0
- | Gym | 7824 | 521 |  | 4860 | 110 | 110 |  | 38880 | 12.0741 | 3
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | Parkway Center City Middle College @ Stoddart Fleisher | [7 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | kitchen |  | 0 |  | 837 | 19 | 0 |  | 6696 | 0 | 0
- | lunchroom |  | 0 |  | 3822 | 86 | 0 |  | 30576 | 0 | 0
- | art room |  | 0 |  | 782 | 17 | 0 |  | 6256 | 0 | 0
506 | art room |  | 0 |  | 851 | 19 | 0 |  | 6808 | 0 | 0
505B | office |  | 0 |  | 528 | 12 | 0 |  | 4224 | 0 | 0
505 | classroom |  | 0 |  | 1078 | 24 | 0 |  | 8624 | 0 | 0
504 | classroom |  | 0 |  | 1144 | 26 | 0 |  | 9152 | 0 | 0
503A | office |  | 0 |  | 96 | 2 | 0 |  | 768 | 0 | 0
503B | shop |  | 0 |  | 252 | 5 | 0 |  | 2016 | 0 | 0
- | teacher's lounge |  | 0 |  | 621 | 14 | 0 |  | 4968 | 0 | 0
502 | classroom |  | 0 |  | 552 | 12 | 0 |  | 4416 | 0 | 0
501 | classroom |  | 0 |  | 640 | 14 | 0 |  | 5120 | 0 | 0
411 | classroom |  | 0 |  | 770 | 17 | 0 |  | 6160 | 0 | 0
410 | classroom |  | 0 |  | 805 | 18 | 0 |  | 6440 | 0 | 0
409 | classroom |  | 0 |  | 713 | 16 | 0 |  | 5704 | 0 | 0
408 | classroom |  | 0 |  | 716 | 16 | 0 |  | 5728 | 0 | 0
407 | classroom |  | 0 |  | 748 | 17 | 0 |  | 5984 | 0 | 0
406 | classroom |  | 0 |  | 704 | 16 | 0 |  | 5632 | 0 | 0
405B | counselor |  | 0 |  | 135 | 3 | 0 |  | 1080 | 0 | 0
405A | VP office |  | 0 |  | 506 | 11 | 0 |  | 4048 | 0 | 0
404 | classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | 0 | 0
403 | classroom |  | 0 |  | 621 | 14 | 0 |  | 4968 | 0 | 0
402 | classroom |  | 0 |  | 598 | 13 | 0 |  | 4784 | 0 | 0
401 | classroom |  | 0 |  | 640 | 14 | 0 |  | 5120 | 0 | 0
310 | classroom |  | 0 |  | 704 | 16 | 0 |  | 5632 | 0 | 0
309 | weight room |  | 0 |  | 920 | 20 | 0 |  | 7360 | 0 | 0
308 | classroom |  | 0 |  | 897 | 20 | 0 |  | 7176 | 0 | 0
307 | classroom |  | 0 |  | 858 | 19 | 0 |  | 6864 | 0 | 0
306 | storage room |  | 0 |  | 682 | 15 | 0 |  | 5456 | 0 | 0
305 | classroom |  | 0 |  | 660 | 15 | 0 |  | 5280 | 0 | 0
304 | classroom |  | 0 |  | 726 | 16 | 0 |  | 5808 | 0 | 0
303A | office |  | 0 |  | 161 | 3 | 0 |  | 1288 | 0 | 0
303 | classroom |  | 0 |  | 713 | 16 | 0 |  | 5704 | 0 | 0
302 | classroom |  | 0 |  | 682 | 15 | 0 |  | 5456 | 0 | 0
301A | computer office |  | 0 |  | 184 | 4 | 0 |  | 1472 | 0 | 0
301 | classroom |  | 0 |  | 640 | 14 | 0 |  | 5120 | 0 | 0
- | Boys locker room |  | 0 |  | 360 | 8 | 0 |  | 2880 | 0 | 0
- | Gym |  | 0 |  | 3300 | 75 | 0 |  | 26400 | 0 | 0
- | Girls Locker room |  | 0 |  | 324 | 7 | 0 |  | 2592 | 0 | 0
- | Nurses office |  | 0 |  | 240 | 5 | 0 |  | 1920 | 0 | 0
- | Exam Room |  | 0 |  | 150 | 3 | 0 |  | 1200 | 0 | 0
208 | classroom |  | 0 |  | 598 | 13 | 0 |  | 4784 | 0 | 0
207 | classroom |  | 0 |  | 598 | 13 | 0 |  | 4784 | 0 | 0
206 | classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | 0 | 0
205 | Library |  | 0 |  | 1081 | 24 | 0 |  | 8648 | 0 | 0
- | Main Office Area |  | 0 |  | 285 | 6 | 0 |  | 2280 | 0 | 0
- | Main Office Waiting area |  | 0 |  | 150 | 3 | 0 |  | 1200 | 0 | 0
- | Principal's office |  | 0 |  | 280 | 6 | 0 |  | 2240 | 0 | 0
204 | classroom |  | 0 |  | 616 | 14 | 0 |  | 4928 | 0 | 0
203 | classroom |  | 0 |  | 621 | 14 | 0 |  | 4968 | 0 | 0
202 | classroom |  | 0 |  | 598 | 13 | 0 |  | 4784 | 0 | 0
201 | counselor's Sitting area |  | 0 |  | 200 | 4 | 0 |  | 1600 | 0 | 0
201A | counselor's A |  | 0 |  | 96 | 2 | 0 |  | 768 | 0 | 0
201B | counselor's B |  | 0 |  | 132 | 3 | 0 |  | 1056 | 0 | 0
201C | counselor's C |  | 0 |  | 121 | 2 | 0 |  | 968 | 0 | 0
201D | counsel's D |  | 0 |  | 121 | 2 | 0 |  | 968 | 0 | 0
105 | conferance room |  | 0 |  | 598 | 13 | 0 |  | 4784 | 0 | 0
104A | classroom |  | 0 |  | 247 | 5 | 0 |  | 1976 | 0 | 0
104B | office |  | 0 |  | 117 | 2 | 0 |  | 936 | 0 | 0
104C | office |  | 0 |  | 112 | 2 | 0 |  | 896 | 0 | 0
104D | office |  | 0 |  | 90 | 2 | 0 |  | 720 | 0 | 0
104E | office |  | 0 |  | 99 | 2 | 0 |  | 792 | 0 | 0
- | Regional office |  | 0 |  | No Access | 0 | 0 |  | #VALUE! | #VALUE! | #VALUE!
- | Data room |  | 0 |  | 484 | 11 | 0 |  | 3872 | 0 | 0
102A | classroom |  | 0 |  | 693 | 15 | 0 |  | 5544 | 0 | 0
102C | office |  | 0 |  | 195 | 4 | 0 |  | 1560 | 0 | 0
102E | classroom |  | 0 |  | 513 | 11 | 0 |  | 4104 | 0 | 0
102D | office |  | 0 |  | 635 | 14 | 0 |  | 5080 | 0 | 0
102B | office |  | 0 |  | 195 | 4 | 0 |  | 1560 | 0 | 0
101 | counselor |  | 0 |  | 306 | 6 | 0 |  | 2448 | 0 | 0
- | Auditorium |  | 0 |  | 4539 | 103 | 0 |  | 36312 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | Strawberry Mansion High School | [7 empty] | 0 | 0 | 0
School: | Leslie P. Hill Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Strawberry Mansion | [8 empty] | 0 | 0 | 0
101 | Music Rm. | 0 | 0 |  | 1288 | 29 | 0 | Heating Unit Ventilator | 10304 | 0 | 0
102 | Classroom | 542 | 36 |  | 768 | 17 | 17 | Univent | 6144 | 5.293 | 2
103 | Music Rm. | 78 | 5 |  | 1288 | 29 | 5 | Heating Unit Ventilator | 10304 | 0.45419 | 0
104 | Classroom | 427 | 28 |  | 888 | 20 | 20 | Univent | 7104 | 3.6064 | 1
108 | Classroom | 0 | 0 |  | 888 | 20 | 0 | Univent | 7104 | 0 | 0
109A & 109B | Classroom | 620 | 41 |  | 1288 | 29 | 29 | Heating Unit Ventilator | 10304 | 3.6102 | 1
110 | Classroom | 695 | 46 |  | 888 | 20 | 20 | Univent | 7104 | 5.8699 | 2
111 | Classroom | 444 | 29 |  | 288 | 6 | 6 | Univent | 2304 | 11.5625 | 3
112 | Classroom | 0 | 0 |  | 888 | 20 | 0 | Univent | 7104 | 0 | 0
200 | Classroom | 0 | 0 |  | 1056 | 24 | 0 | Univent | 8448 | 0 | 0
201 | Classroom | 416 | 27 |  | 805 | 18 | 18 | Univent | 6440 | 3.8758 | 1
202 | Classroom | 357 | 23 |  | 1152 | 26 | 23 | Univent | 9216 | 2.3242 | 1
203 | Classroom | 607 | 40 |  | 782 | 17 | 17 | Univent | 6256 | 5.8216 | 2
206 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0
207 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
208 | Classroom | 512 | 34 |  | 1104 | 25 | 25 | Univent | 8832 | 3.4783 | 1
209 | Computer Lab | 859 | 57 |  | 1012 | 23 | 23 | Air Handling Unit | 8096 | 6.3661 | 2
212 | Classroom | 382 | 25 |  | 851 | 19 | 19 | Univent | 6808 | 3.3666 | 1
214 | Classroom | 301 | 20 |  | 851 | 19 | 19 | Univent | 6808 | 2.6528 | 1
216 | Classroom | 350 | 23 |  | 851 | 19 | 19 | Univent | 6808 | 3.0846 | 1
217 | Classroom | 516 | 34 |  | 1012 | 23 | 23 | Univent | 8096 | 3.8241 | 1
219 | Classroom | 0 | 0 |  | 960 | 21 | 0 | Univent | 7680 | 0 | 0
220 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
222 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
224 | Classroom | 0 | 0 |  | 782 | 17 | 0 | Univent | 6256 | 0 | 0
300 | Classroom | 464 | 30 |  | 782 | 17 | 17 | Univent | 6256 | 4.4501 | 2
301 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0
302 | Classroom | 401 | 26 |  | 782 | 17 | 17 | Univent | 6256 | 3.8459 | 1
303 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0
304 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
306 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
307 | Classroom | 442 | 29 |  | 851 | 19 | 19 | Univent | 6808 | 3.8954 | 1
308 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
309 | Classroom | 335 | 22 |  | 851 | 19 | 19 | Univent | 6808 | 2.9524 | 1
310 | Classroom | 430 | 28 |  | 851 | 19 | 19 | Univent | 6808 | 3.7897 | 1
311 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
312 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
314 | Classroom | 446 | 29 |  | 851 | 19 | 19 | Univent | 6808 | 3.9307 | 1
315 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
316 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
317 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
319 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
320 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
322 | Classroom | 459 | 30 |  | 851 | 19 | 19 | Univent | 6808 | 4.0452 | 2
323 | Classroom | 601 | 40 |  | 851 | 19 | 19 | Univent | 6808 | 5.2967 | 2
324 | Classroom | 466 | 31 |  | 782 | 17 | 17 | Univent | 6256 | 4.4693 | 2
325 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
400A&B | Classroom | 0 | 0 |  | 598 | 13 | 0 | Univent | 4784 | 0 | 0
401A | Classroom | 488 | 32 |  | 345 | 7 | 7 | Univent | 2760 | 10.6087 | 3
402 | Classroom | 465 | 31 |  | 1288 | 29 | 29 | Univent | 10304 | 2.7077 | 1
403 | Classroom | 250 | 16 |  | 299 | 6 | 6 | Univent | 2392 | 6.2709 | 2
404 | Classroom | 434 | 28 |  | 1196 | 27 | 27 | Univent | 9568 | 2.7216 | 1
405 | Classroom | 503 | 33 |  | 987 | 22 | 22 | Univent | 7896 | 3.8222 | 1
406 | Classroom | 239 | 15 |  | 666 | 15 | 15 | Univent | 5328 | 2.6914 | 1
407 | Classroom | 236 | 15 |  | 375 | 8 | 8 | Univent | 3000 | 4.72 | 2
408 | Classroom | 456 | 30 |  | 851 | 19 | 19 | Univent | 6808 | 4.0188 | 2
409 | Classroom | 0 | 0 |  | 1288 | 29 | 0 | Univent | 10304 | 0 | 0
410 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
412 | Classroom | 431 | 28 |  | 851 | 19 | 19 | Univent | 6808 | 3.7985 | 1
413 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
414 | Classroom | 467 | 31 |  | 851 | 19 | 19 | Univent | 6808 | 4.1157 | 2
415 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
417 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
418 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
420 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
421 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
422 | Classroom | 0 | 0 |  | 782 | 17 | 0 | Univent | 6256 | 0 | 0
423 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0
500 | Classroom | 280 | 18 |  | 800 | 18 | 18 | Univent | 6400 | 2.625 | 1
500B | Classroom | 264 | 17 |  | 375 | 8 | 8 | Univent | 3000 | 5.28 | 2
502 | Classroom | 442 | 29 |  | 300 | 6 | 6 | Univent | 2400 | 11.05 | 3
505 | Classroom | 0 | 0 |  | 1300 | 29 | 0 | Univent | 10400 | 0 | 0
506 | Classroom | 0 | 0 |  | 925 | 21 | 0 | Univent | 7400 | 0 | 0
507 | Classroom | 0 | 0 |  | 425 | 9 | 0 | Univent | 3400 | 0 | 0
508 | Classroom | 487 | 32 |  | 1250 | 28 | 28 | Univent | 10000 | 2.922 | 1
509 | Classroom | 0 | 0 |  | 1100 | 25 | 0 | Univent | 8800 | 0 | 0
513 | Classroom | 489 | 32 |  | 325 | 7 | 7 | Univent | 2600 | 11.2846 | 3
516 | Classroom | 0 | 0 |  | 1327 | 30 | 0 | Univent | 10616 | 0 | 0
517 | Classroom | 0 | 0 |  | 1162 | 26 | 0 | Univent | 9296 | 0 | 0
518 | Classroom | 0 | 0 |  | 1375 | 31 | 0 | Univent | 11000 | 0 | 0
519 | Classroom | 292 | 19 |  | 570 | 12 | 12 | Univent | 4560 | 3.8421 | 1
520 | Classroom | 683 | 45 |  | 1447 | 32 | 32 | Univent | 11576 | 3.5401 | 1
522 | Classroom | 0 | 0 |  | 1471 | 33 | 0 | Univent | 11768 | 0 | 0
- | Library | 1247 | 83 |  | 1863 | 42 | 42 | Air Handling Unit | 14904 | 5.0201 | 2
- | Culinary Arts area | 1077 | 71 |  | 6536 | 148 | 71 | Air Handling Unit | 52288 | 1.2358 | 1
- | Book Strg. Rm. Security office | 0 | 0 |  | 1733 | 39 | 0 | Air Handling Unit | 13864 | 0 | 0
- | DOS office | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
- | EST office | 513 | 34 |  |  | 0 | 0 | Univent | 0 | 0 | 0
| Serves unknown | 0 | 0 |  |  | 0 | 0 | Heating Unit Ventilator | 0 | 0 | 0
- | Auditorium | 7054 | 470 |  | 9936 | 225 | 225 | Heating Unit Ventilator | 79488 | 5.3246 | 2
- | Cafeteria | 1912 | 127 |  | 10725 | 243 | 127 | Heating Unit Ventilator | 85800 | 1.3371 | 1
- | Aud. Stage | 2999 | 199 |  | 2668 | 60 | 60 | Heating Unit Ventilator | 21344 | 8.4305 | 2
- | Unknown location and what it serves |  | 0 |  |  | 0 | 0 | Heating Unit Ventilator | 0 | 0 | 0
- | Maintenance office, Lobby | 317 | 21 |  |  | 0 | 0 | Heating Unit Ventilator | 0 | 0 | 0
- | Girls Locker Room | 1759 | 117 |  |  | 0 | 0 | Heating Unit Ventilator | 0 | 0 | 0
- | Girls Gym | 885 | 59 |  | 5808 | 132 | 59 | Heating Unit Ventilator | 46464 | 1.1428 | 1
- | Boys Locker Room | 126 | 8 |  |  | 0 | 0 | Heating Unit Ventilator | 0 | 0 | 0
- | Boys Gym | 6081 | 405 |  | 5808 | 132 | 132 | Heating Unit Ventilator | 46464 | 7.8525 | 2
- | Unknown location and what it serves |  | 0 |  |  | 0 | 0 | Heating Unit Ventilator | 0 | 0 | 0
- | Music Prac. Rms. & Office | 607 | 40 |  |  | 0 | 0 | Heating Unit Ventilator | 0 | 0 | 0
- | Nurses area, Admin areas | 796 | 53 |  |  | 0 | 0 | Heating Unit Ventilator | 0 | 0 | 0
- | Unknown |  | 0 |  |  | 0 | 0 | Heating Unit Ventilator | 0 | 0 | 0
- | Unknown |  | 0 |  |  | 0 | 0 | Heating Unit Ventilator | 0 | 0 | 0
LP Hill Building | [8 empty] | 0 | 0 | 0
1 | Office | 0 | 0 |  | 870.365 | 19 | 0 | Vertical ACU | 6962.92 | 0 | 0
4 | Office | 0 | 0 |  | 409.462 | 9 | 0 | Vertical Air Coil Unit and Univent | 3275.696 | 0 | 0
5 | Classroom | 0 | 0 |  |  | 0 | 0 | Vertical Air Coil Unit and Univent | 0 | 0 | 0
7 | Classroom | 0 | 0 |  |  | 0 | 0 | Vertical Air Coil Unit and Univent | 0 | 0 | 0
7 | Conference Rm. | 0 | 0 |  | 1111.66 | 25 | 0 | Vertical Air Coil Unit and Univent | 8893.28 | 0 | 0
10 | Storage Room | 0 | 0 |  | 454.88 | 10 | 0 | Vertical Air Coil Unit | 3639.04 | 0 | 0
12 | Truency Court | 0 | 0 |  | 988.792 | 22 | 0 | Vertical Air Coil Unit | 7910.336 | 0 | 0
14 | Truency Court | 0 | 0 |  | 715.596 | 16 | 0 | Univent | 5724.768 | 0 | 0
15 | General Room | 0 | 0 |  | 734.479 | 16 | 0 | Vertical Air Coil Unit and Univent | 5875.832 | 0 | 0
100 | Classroom | 0 | 0 |  | 982.127 | 22 | 0 | Vertical Air Coil Unit and Univent | 7857.016 | 0 | 0
101 | Classroom | 0 | 0 |  | 1041.52 | 23 | 0 | Vertical Air Coil Unit and Univent | 8332.16 | 0 | 0
102 | Classroom | 0 | 0 |  | 973.903 | 22 | 0 | Univent | 7791.224 | 0 | 0
103 | Classroom | 0 | 0 |  | 1054.8 | 23 | 0 | Vertical Air Coil Unit and Univent | 8438.4 | 0 | 0
104 | Classroom | 0 | 0 |  | 1022.271 | 23 | 0 | Univent | 8178.168 | 0 | 0
105 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Univent | 7000 | 0 | 0
106 | Classroom | 160 | 10 |  | 933.66 | 21 | 10 | Univent | 7469.28 | 1.2853 | 1
107 | Classroom | 15 | 1 |  | 1492.29 | 33 | 1 | Univent | 11938.32 | 0.075387 | 0
108 | Classroom | 224 | 14 |  | 1492.29 | 33 | 14 | Univent | 11938.32 | 1.1258 | 1
200 | Office | 0 | 0 |  | 917.724 | 20 | 0 | Univent | 7341.792 | 0 | 0
202 | Office | 294 | 19 |  | 1034 | 23 | 19 | Univent | 8272 | 2.1325 | 1
203 | Office | 0 | 0 |  | 833.94 | 18 | 0 | Univent | 6671.52 | 0 | 0
204 | Office | 50 | 3 |  | 1034 | 23 | 3 | Univent | 8272 | 0.36267 | 0
205 | Office | 0 | 0 |  | 1033.59 | 23 | 0 | Univent | 8268.72 | 0 | 0
206 | Office | 0 | 0 |  | 951.5 | 21 | 0 | Univent | 7612 | 0 | 0
207 | Office | 31 | 2 |  | 1033.59 | 23 | 2 | Univent | 8268.72 | 0.22494 | 0
209 | Office | 119 | 7 |  | 1031.06 | 23 | 7 | Univent | 8248.48 | 0.86561 | 0
210 | Office | 0 | 0 |  | 1009.73 | 22 | 0 | Univent | 8077.84 | 0 | 0
212 | Office | 169 | 11 |  | 882.972 | 20 | 11 | Univent | 7063.776 | 1.4355 | 1
213 | Office | 0 | 0 |  | 940.62 | 21 | 0 | Univent | 7524.96 | 0 | 0
214 | Waiting area | 0 | 0 |  | 912.502 | 20 | 0 | Univent | 7300.016 | 0 | 0
215 | Waiting area | 0 | 0 |  | 1025.81 | 23 | 0 | Univent | 8206.48 | 0 | 0
300 | Classroom | 216 | 14 |  | 922.898 | 20 | 14 | Univent | 7383.184 | 1.7553 | 1
301 | Classroom | 0 | 0 |  | 921.33 | 20 | 0 | Univent | 7370.64 | 0 | 0
302 | Classroom | 0 | 0 |  | 1010.47 | 22 | 0 | Univent | 8083.76 | 0 | 0
303 | Classroom | 0 | 0 |  | 912.38 | 20 | 0 | Univent | 7299.04 | 0 | 0
304 | Classroom | 0 | 0 |  | 986.631 | 22 | 0 | Univent | 7893.048 | 0 | 0
305 | Classroom | 25 | 1 |  | 618.57 | 14 | 1 | Univent | 4948.56 | 0.30312 | 0
306 | Classroom | 0 | 0 |  | 932.119 | 21 | 0 | Univent | 7456.952 | 0 | 0
307 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
309 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
310 | Classroom | 280 | 18 |  | 1009.5 | 22 | 18 | Univent | 8076 | 2.0802 | 1
312 | Classroom | 0 | 0 |  | 992.166 | 22 | 0 | Univent | 7937.328 | 0 | 0
313 | Classroom | 0 | 0 |  | 978.97 | 22 | 0 | Univent | 7831.76 | 0 | 0
314 | Classroom | 0 | 0 |  | 911.255 | 20 | 0 | Univent | 7290.04 | 0 | 0
315 | Classroom |  | 0 |  | 863.91 | 19 | 0 | Univent | 6911.28 | 0 | 0
400 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
401 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
402 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
403 | Classroom | 194 | 12 |  |  | 0 | 0 | Univent | 0 | 0 | 0
404 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
405 | Classroom | 92 | 6 |  |  | 0 | 0 | Univent | 0 | 0 | 0
406 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
407 | Classroom | 131 | 8 |  |  | 0 | 0 | Univent | 0 | 0 | 0
409 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
410 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
411/413 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
412 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
414 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
415 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
- | Faculty Rm. | 0 | 0 |  |  | 0 | 0 | Univent | 0 | 0 | 0
- | Main office | 0 | 0 |  | 1107.41 | 25 | 0 | Univent | 8859.28 | 0 | 0
- | Princ. Office | 682 | 45 |  | 355.756 | 8 | 8 | Univent | 2846.048 | 14.3778 | 3
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | James J. Sullivan Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B7 | Classroom |  | 0 | Yes | 610 | 13 | 13 | House Fan | 4880 | 0 | 0
B2 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
- | Library |  | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | 0 | 0
B9 | Classroom |  | 0 |  | 506 | 11 | 0 | House Fan | 4048 | 0 | 0
- | Kitchen |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | 0 | 0
101 | Classroom |  | 0 | Yes | 920 | 20 | 20 | House Fan | 7360 | 0 | 0
102 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
103 | Classroom |  | 0 |  | 736 | 16 | 0 | House Fan | 5888 | 0 | 0
104 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
105 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
106 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
107 | Classroom |  | 0 | Yes | 275 | 6 | 6 |  | 2200 | 0 | 0
107a | office |  | 0 | Yes | 115 | 2 | 2 | House Fan | 920 | 0 | 0
107b | office |  | 0 | Yes | 115 | 2 | 2 | House Fan | 920 | 0 | 0
107c | office |  | 0 | Yes | 115 | 2 | 2 | House Fan | 920 | 0 | 0
108 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
109 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
110 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
- | Main Office |  | 0 | Yes | 336 | 7 | 7 | House Fan | 2688 | 0 | 0
- | Principal's Office |  | 0 | Yes | 210 | 4 | 4 | House Fan | 1680 | 0 | 0
201 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
202 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
203 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
204 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
205 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
206 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
207 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
208 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
209 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
210 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
211 | Classroom |  | 0 | Yes | 192 | 4 | 4 | House Fan | 1536 | 0 | 0
214 | Classroom |  | 0 | Yes | 384 | 8 | 8 | House Fan | 3072 | 0 | 0
215 | Office |  | 0 | Yes | 195 | 4 | 4 | House Fan | 1560 | 0 | 0
- | Nurses Office |  | 0 | Yes | 264 | 6 | 6 | House Fan | 2112 | 0 | 0
300 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0
301 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
302 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
303 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
304 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
305 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
306 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
307 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0
307B | Classroom |  | 0 | Yes | 119 | 2 | 2 |  | 952 | 0 | 0
308 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
309 | Computer Room |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0
310 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | 0 | 0
311 | Office |  | 0 | Yes | 192 | 4 | 4 | House Fan | 1536 | 0 | 0
- | Cafe/Gym |  | 0 | Yes | 3432 | 78 | 78 | Hydroxyl Unit | 27456 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27 | [7 empty] | 0 | 0 | 0
School: | Parkway West High School @ Sulzberger | [7 empty] | 0 | 0 | 0
Vendor: | [8 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | - |  | 0 |  | 483 | 10 | 0 |  | 3864 | 0 | 0
101 | - |  | 0 |  | 575 | 13 | 0 |  | 4600 | 0 | 0
102 | - |  | 0 |  | 851 | 19 | 0 |  | 6808 | 0 | 0
106 | - |  | 0 |  | 920 | 20 | 0 |  | 7360 | 0 | 0
107 | - |  | 0 | Yes | 943 | 21 | 21 |  | 7544 | 0 | 0
108 | - |  | 0 | Yes | 874 | 19 | 19 |  | 6992 | 0 | 0
109 | - |  | 0 |  | 920 | 20 | 0 |  | 7360 | 0 | 0
201 | - |  | 0 |  | 682 | 15 | 0 |  | 5456 | 0 | 0
202 | - |  | 0 |  | 660 | 15 | 0 |  | 5280 | 0 | 0
203 | - |  | 0 | Yes | 528 | 12 | 12 |  | 4224 | 0 | 0
203A | - |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | 0 | 0
204 | Nurses Office |  | 0 | Yes | 460 | 10 | 10 |  | 3680 | 0 | 0
205 | - |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | 0 | 0
206 | Counselors Office |  | 0 | Yes | 690 | 15 | 15 |  | 5520 | 0 | 0
Principal | Office |  | 0 | Yes | 322 | 7 | 7 |  | 2576 | 0 | 0
208 | Main Office |  | 0 | Yes | 825 | 18 | 18 |  | 6600 | 0 | 0
210 | - |  | 0 |  | 836 | 19 | 0 |  | 6688 | 0 | 0
211 | - |  | 0 | Yes | 864 | 19 | 19 |  | 6912 | 0 | 0
212 | - |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | 0 | 0
212A | - |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | 0 | 0
213 | - |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | 0 | 0
215 | - |  | 0 |  | 816 | 18 | 0 |  | 6528 | 0 | 0
216 | - |  | 0 | Yes | 748 | 17 | 17 |  | 5984 | 0 | 0
217 | - |  | 0 | Yes | 736 | 16 | 16 |  | 5888 | 0 | 0
218 | - |  | 0 | Yes | 704 | 16 | 16 |  | 5632 | 0 | 0
219 | - |  | 0 | Yes | 704 | 16 | 16 |  | 5632 | 0 | 0
220 | - |  | 0 | Yes | 704 | 16 | 16 |  | 5632 | 0 | 0
221 | - |  | 0 |  | 805 | 18 | 0 |  | 6440 | 0 | 0
222 | - |  | 0 |  | 690 | 15 | 0 |  | 5520 | 0 | 0
301-302 | - |  | 0 | Yes | 1012 | 23 | 23 |  | 8096 | 0 | 0
303 | - |  | 0 | Yes | 1176 | 26 | 26 |  | 9408 | 0 | 0
304 | - |  | 0 | Yes | 966 | 21 | 21 |  | 7728 | 0 | 0
305 | - |  | 0 |  | 858 | 19 | 0 |  | 6864 | 0 | 0
306 | - |  | 0 | Yes | 770 | 17 | 17 |  | 6160 | 0 | 0
307 | - |  | 0 |  | 770 | 17 | 0 |  | 6160 | 0 | 0
308 | - |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0
309 | - |  | 0 |  | 880 | 20 | 0 |  | 7040 | 0 | 0
310 | - |  | 0 |  | 880 | 20 | 0 |  | 7040 | 0 | 0
311 | - |  | 0 |  | 924 | 21 | 0 |  | 7392 | 0 | 0
312 | - |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | 0 | 0
313 | - |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | 0 | 0
314 | - |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | 0 | 0
315 | - |  | 0 |  | 330 | 7 | 0 |  | 2640 | 0 | 0
316 | - |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | 0 | 0
317 | - |  | 0 |  | 748 | 17 | 0 |  | 5984 | 0 | 0
318 | - |  | 0 | Yes | 736 | 16 | 16 |  | 5888 | 0 | 0
319 | - |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | 0 | 0
320 | - |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | 0 | 0
321 | - |  | 0 |  | 704 | 16 | 0 |  | 5632 | 0 | 0
322 | - |  | 0 | Yes | 748 | 17 | 17 |  | 5984 | 0 | 0
323 | - |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
- | 3rd Flr. Computer Lab |  | 0 |  | 1035 | 23 | 0 |  | 8280 | 0 | 0
- | Auditorium |  | 0 |  | 3390 | 77 | 0 |  | 27120 | 0 | 0
- | North Caf. |  | 0 |  | 2680 | 60 | 0 |  | 21440 | 0 | 0
- | South Caf. |  | 0 | Yes | 2720 | 61 | 61 |  | 21760 | 0 | 0
- | South Gym |  | 0 |  | 4186 | 95 | 0 |  | 33488 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | Swenson Arts & Technology High School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
49 | Classroom |  | 0 | Yes | 308 | 7 | 7 |  | 2464 | 0 | 0
50 | Classroom |  | 0 |  | 308 | 7 | 0 |  | 2464 | 0 | 0
51 | Classroom |  | 0 | Yes | 308 | 7 | 7 |  | 2464 | 0 | 0
53 | Classroom |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | 0 | 0
4 | Classroom |  | 0 | Yes | 532 | 12 | 12 |  | 4256 | 0 | 0
5 | Classroom |  | 0 | Yes | 528 | 12 | 12 |  | 4224 | 0 | 0
6 | Classroom |  | 0 |  | 132 | 3 | 0 |  | 1056 | 0 | 0
100 | Classroom | 242 | 16 |  | 1278 | 29 | 16 | Rooftop Unit | 10224 | 1.4202 | 1
101 | Classroom | 143 | 9 |  | 228 | 5 | 5 | Rooftop Unit | 1824 | 4.7039 | 2
102 | Classroom | 76 | 5 |  | 149 | 3 | 3 | Rooftop Unit | 1192 | 3.8255 | 1
103 | Classroom | 82 | 5 |  | 151 | 3 | 3 | Rooftop Unit | 1208 | 4.0728 | 2
104 | Classroom | 116 | 7 |  | 144 | 3 | 3 | Rooftop Unit | 1152 | 6.0417 | 2
105 | Classroom | 40 | 2 |  | 110 | 2 | 2 | Rooftop Unit | 880 | 2.7273 | 1
105 | Classroom | 55 | 3 |  | 200 | 4 | 3 | Rooftop Unit | 1600 | 2.0625 | 1
106 | Classroom | 75 | 5 |  | 178 | 4 | 4 | Rooftop Unit | 1424 | 3.1601 | 1
109 | Classroom | 93 | 6 |  | 306 | 6 | 6 | Rooftop Unit | 2448 | 2.2794 | 1
110 | Classroom | 70 | 4 |  | 159 | 3 | 3 | Rooftop Unit | 1272 | 3.3019 | 1
111 | Classroom | 42 | 2 |  | 146 | 3 | 2 | Rooftop Unit | 1168 | 2.1575 | 1
112 | Classroom | 24 | 1 |  | 100 | 2 | 1 | Rooftop Unit | 800 | 1.8 | 1
113 | Classroom | 21 | 1 | Yes | 105 | 2 | 2 | Rooftop Unit | 840 | 1.5 | 1
114 | Classroom | 135 | 9 |  | 602 | 13 | 9 | Rooftop Unit | 4816 | 1.6819 | 1
128 | Classroom | 612 | 40 |  | 1275 | 28 | 28 | Rooftop Unit | 10200 | 3.6 | 1
129 | Classroom | 39 | 2 |  | 144 | 3 | 2 | Rooftop Unit | 1152 | 2.0312 | 1
130 | Classroom | 536 | 35 |  | 960 | 21 | 21 | Rooftop Unit | 7680 | 4.1875 | 2
138 | Classroom | 305 | 20 | Yes | 1125 | 25 | 25 | Rooftop Unit | 9000 | 2.0333 | 1
140 | Classroom | 675 | 45 |  | 1085 | 24 | 24 | Rooftop Unit | 8680 | 4.6659 | 2
144 | Classroom | 1497 | 99 |  | 1734 | 39 | 39 | Rooftop Unit | 13872 | 6.4749 | 2
146 | Classroom | 650 | 43 |  | 700 | 15 | 15 | Rooftop Unit | 5600 | 6.9643 | 2
150 | Classroom | 618 | 41 |  | 308 | 7 | 7 | Rooftop Unit | 2464 | 15.0487 | 3
164 | Classroom | 305 | 20 |  | 899 | 20 | 20 | Rooftop Unit | 7192 | 2.5445 | 1
170 | Classroom | 188 | 12 |  | 351 | 7 | 7 | Rooftop Unit | 2808 | 4.0171 | 2
171 | Classroom | 526 | 35 |  | 1461 | 33 | 33 | Rooftop Unit | 11688 | 2.7002 | 1
172 | Classroom |  | 0 | Yes | 126 | 2 | 2 |  | 1008 | 0 | 0
176 | Classroom |  | 0 | Yes | 452 | 10 | 10 |  | 3616 | 0 | 0
180 | Classroom | 93 | 6 |  | 209 | 4 | 4 | Rooftop Unit | 1672 | 3.3373 | 1
182 | Classroom | 251 | 16 | Yes | 1059 | 24 | 24 | Rooftop Unit | 8472 | 1.7776 | 1
184 | Classroom | 228 | 15 | Yes | 1628 | 37 | 37 | Rooftop Unit | 13024 | 1.0504 | 1
195 | Classroom | 439 | 29 |  | 1566 | 35 | 29 | Rooftop Unit | 12528 | 2.1025 | 1
196 | Classroom | 68 | 4 |  | 272 | 6 | 4 | Rooftop Unit | 2176 | 1.875 | 1
200 | Classroom | 344 | 22 |  | 1624 | 36 | 22 | Rooftop Unit | 12992 | 1.5887 | 1
201 & 201A | Classroom | 211 | 14 | Yes | 660 | 15 | 15 | Rooftop Unit | 5280 | 2.3977 | 1
202 | Classroom | 181 | 12 | Yes | 836 | 19 | 19 | Rooftop Unit | 6688 | 1.6238 | 1
203 | Classroom | 190 | 12 |  | 760 | 17 | 12 | Rooftop Unit | 6080 | 1.875 | 1
204 | Classroom |  | 0 | Yes | 1584 | 36 | 36 | Rooftop Unit | 12672 | 0 | 0
205 | Classroom | 328 | 21 | Yes | 1925 | 43 | 43 | Rooftop Unit | 15400 | 1.2779 | 1
207 | Classroom | 994 | 66 |  | 2300 | 52 | 52 | Rooftop Unit | 18400 | 3.2413 | 1
210 | Classroom | 1278 | 85 |  | 1020 | 23 | 23 | Rooftop Unit | 8160 | 9.3971 | 2
213 | Classroom |  | 0 | Yes | 748 | 17 | 17 | Rooftop Unit | 5984 | 0 | 0
214 | Classroom |  | 0 | Yes | 126 | 2 | 2 |  | 1008 | 0 | 0
216 | Classroom | 410 | 27 |  | 1597 | 36 | 27 | Rooftop Unit | 12776 | 1.9255 | 1
216 | Classroom | 1578 | 105 |  | 1597 | 36 | 36 | Rooftop Unit | 12776 | 7.4108 | 2
227 | Classroom | 225 | 15 | Yes | 840 | 19 | 19 | Rooftop Unit | 6720 | 2.0089 | 1
228 | Classroom | 135 | 9 | Yes | 930 | 21 | 21 | Rooftop Unit | 7440 | 1.0887 | 1
229 | Classroom | 174 | 11 | Yes | 1008 | 22 | 22 | Rooftop Unit | 8064 | 1.2946 | 1
230/231 | Classroom | 87 | 5 | Yes | 522 | 11 | 11 | Rooftop Unit | 4176 | 1.25 | 1
231 | Classroom | 43 | 2 |  | 100 | 2 | 2 | Rooftop Unit | 800 | 3.225 | 1
232 | Classroom |  | 0 | Yes | 968 | 22 | 22 |  | 7744 | 0 | 0
232B | Classroom | 46 | 3 | Yes | 348 | 7 | 7 | Rooftop Unit | 2784 | 0.99138 | 0
234 | Classroom | 192 | 12 | Yes | 900 | 20 | 20 | Rooftop Unit | 7200 | 1.6 | 1
236 | Classroom | 293 | 19 |  | 1240 | 28 | 19 | Rooftop Unit | 9920 | 1.7722 | 1
237 | Classroom | 186 | 12 | Yes | 969 | 22 | 22 | Rooftop Unit | 7752 | 1.4396 | 1
238 | Classroom | 442 | 29 |  | 888 | 20 | 20 | Rooftop Unit | 7104 | 3.7331 | 1
245 | Classroom | 281 | 18 |  | 675 | 15 | 15 | Rooftop Unit | 5400 | 3.1222 | 1
247 | Classroom | 140 | 9 |  | 448 | 10 | 9 | Rooftop Unit | 3584 | 2.3438 | 1
249 & 249 A-B | Classroom | 520 | 34 |  | 414 | 9 | 9 | Rooftop Unit | 3312 | 9.4203 | 2
250 | Classroom | 303 | 20 |  | 900 | 20 | 20 | Rooftop Unit | 7200 | 2.525 | 1
253 | Classroom | 655 | 43 |  | 186 | 4 | 4 | Rooftop Unit | 1488 | 26.4113 | 4
257 | Classroom | 341 | 22 |  | 756 | 17 | 17 | Rooftop Unit | 6048 | 3.3829 | 1
258 | Classroom | 357 | 23 |  | 1050 | 23 | 23 | Rooftop Unit | 8400 | 2.55 | 1
259 | Classroom | 242 | 16 |  | 1225 | 27 | 16 | Rooftop Unit | 9800 | 1.4816 | 1
260 and 260 A-C | Classroom | 579 | 38 |  | 561 | 12 | 12 | Rooftop Unit | 4488 | 7.7406 | 2
261 | Classroom | 375 | 25 |  | 1050 | 23 | 23 | Rooftop Unit | 8400 | 2.6786 | 1
262 | Classroom | 678 | 45 |  | 2373 | 53 | 45 | Rooftop Unit | 18984 | 2.1429 | 1
263 | Classroom |  | 0 | Yes | 2373 | 53 | 53 |  | 18984 | 0 | 0
264 | Classroom | 333 | 22 |  | 870 | 19 | 19 | Rooftop Unit | 6960 | 2.8707 | 1
265 | Classroom | 307 | 20 |  | 928 | 21 | 20 | Rooftop Unit | 7424 | 2.4811 | 1
1750b | Room | 108 | 7 |  | 374 | 8 | 7 | Rooftop Unit | 2992 | 2.1658 | 1
1775A | - |  | 0 | Yes | 528 | 12 | 12 |  | 4224 | 0 | 0
- | Baking Room | 525 | 34 |  | 1981 | 45 | 34 | Rooftop Unit | 15848 | 1.9876 | 1
- | Dark Room | 59 | 3 |  | 104 | 2 | 2 | Rooftop Unit | 832 | 4.2548 | 2
- | Corridor | 109 | 7 |  | 355 | 8 | 7 | Rooftop Unit | 2840 | 2.3028 | 1
- | Hallway | 640 | 42 |  | 730 | 16 | 16 | Rooftop Unit | 5840 | 6.5753 | 2
- | Corridor | 54 | 3 |  | 162 | 3 | 3 | Rooftop Unit | 1296 | 2.5 | 1
- | Corridor | 53 | 3 |  | 152 | 3 | 3 | Rooftop Unit | 1216 | 2.6151 | 1
- | Corridor | 167 | 11 |  | 286 | 6 | 6 | Rooftop Unit | 2288 | 4.3794 | 2
- | Corridor | 70 | 4 |  | 344 | 7 | 4 | Rooftop Unit | 2752 | 1.5262 | 1
- | Hallway Diffuser s31 | 25 | 1 |  | 258 | 5 | 1 | Rooftop Unit | 2064 | 0.72674 | 0
- | Kitchen | 1391 | 92 |  | 205 | 4 | 4 | Rooftop Unit | 1640 | 50.8902 | 5
- | Nurse's Office/Medical | 165 | 11 |  | 591 | 13 | 11 | Rooftop Unit | 4728 | 2.0939 | 1
- | Office | 35 | 2 |  | 287 | 6 | 2 | Rooftop Unit | 2296 | 0.91463 | 0
- | Office | 77 | 5 |  | 1435 | 32 | 5 | Rooftop Unit | 11480 | 0.40244 | 0
- | Office | 54 | 3 |  | 157 | 3 | 3 | Rooftop Unit | 1256 | 2.5796 | 1
- | Office | 598 | 39 |  | 94 | 2 | 2 | Rooftop Unit | 752 | 47.7128 | 4
- | Classroom | 313 | 20 |  | 1769 | 40 | 20 | Rooftop Unit | 14152 | 1.327 | 1
S1 | Classroom | 309 | 20 |  | 336 | 7 | 7 | Rooftop Unit | 2688 | 6.8973 | 2
S2 | Classroom | 318 | 21 |  | 336 | 7 | 7 | Rooftop Unit | 2688 | 7.0982 | 2
S3 | Classroom | 52 | 3 |  | 336 | 7 | 3 | Rooftop Unit | 2688 | 1.1607 | 1
S3 | Office | 232 | 15 |  | 306 | 6 | 6 | Rooftop Unit | 2448 | 5.6863 | 2
S4 | Office | 14 | 0 |  | 20 | 0 | 0 | Rooftop Unit | 160 | 5.25 | 2
S5 | Storage | 33 | 2 |  | 270 | 6 | 2 | Rooftop Unit | 2160 | 0.91667 | 0
S6 | School Police | 207 | 13 |  | 515 | 11 | 11 | Rooftop Unit | 4120 | 3.0146 | 1
S8 | Classroom | 104 | 6 |  | 560 | 12 | 6 | Rooftop Unit | 4480 | 1.3929 | 1
- | School Store | 386 | 25 |  | 455 | 10 | 10 | Rooftop Unit | 3640 | 6.3626 | 2
- | Second Floor Hallway | 95 | 6 |  | 1846 | 41 | 6 | Rooftop Unit | 14768 | 0.38597 | 0
- | Storage | 33 | 2 |  | 590 | 13 | 2 | Rooftop Unit | 4720 | 0.41949 | 0
- | Storage | 107 | 7 |  | 35 | 0 | 0 | Rooftop Unit | 280 | 22.9286 | 3
- | Storage | 73 | 4 |  | 134 | 3 | 3 | Rooftop Unit | 1072 | 4.0858 | 2
- | Storage | 44 | 2 |  | 94 | 2 | 2 | Rooftop Unit | 752 | 3.5106 | 1
- | Storage | 45 | 3 |  | 91 | 2 | 2 | Rooftop Unit | 728 | 3.7088 | 1
- | Storage/Closet | 237 | 15 |  | 50 | 1 | 1 | Rooftop Unit | 400 | 35.55 | 4
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | John H. Taggart Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | [8 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
102-A | Classroom |  | 0 |  | 372 | 8 | 0 |  | 2976 | 0 | 0
102-B | Classroom |  | 0 |  | 230 | 5 | 0 |  | 1840 | 0 | 0
103 | Classroom |  | 0 |  | 506 | 11 | 0 |  | 4048 | 0 | 0
104 | Classroom |  | 0 | Yes | 594 | 13 | 13 |  | 4752 | 0 | 0
107 | Classroom |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | 0 | 0
108 | Nurse's Office |  | 0 | Yes | 176 | 4 | 4 |  | 1408 | 0 | 0
- | 2nd Floor Dean of Student's Office |  | 0 |  | 144 | 3 | 0 |  | 1152 | 0 | 0
200 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
201 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
202 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
203 | Classroom |  | 0 |  | 136 | 3 | 0 |  | 1088 | 0 | 0
204 | Computer Lab |  | 0 | Yes | 924 | 21 | 21 |  | 7392 | 0 | 0
205 | Classroom |  | 0 |  | 414 | 9 | 0 |  | 3312 | 0 | 0
206 | Classroom |  | 0 | Yes | 736 | 16 | 16 |  | 5888 | 0 | 0
207 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
208 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | 0 | 0
209 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | 0 | 0
- | 3rd Floor Men's Room |  | 0 |  | 56 | 1 | 0 |  | 448 | 0 | 0
300 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | 0 | 0
301 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
302 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
303 | Classroom |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | 0 | 0
304 | Classroom |  | 0 | Yes | 594 | 13 | 13 |  | 4752 | 0 | 0
305-306 | Library |  | 0 | Yes | 1320 | 30 | 30 |  | 10560 | 0 | 0
307 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | 0 | 0
308 | Classroom |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | 0 | 0
309 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | 0 | 0
400 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
401 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
402 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
403 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | 0 | 0
404 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
405 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
406 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
407 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
408 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | 0 | 0
409 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | 0 | 0
410 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | 0 | 0
500 | Classroom |  | 0 | Yes | 132 | 3 | 3 |  | 1056 | 0 | 0
- | Gym |  | 0 | Yes | 3555 | 80 | 80 | Hydroxyl Unit | 28440 | 0 | 0
- | Building Engineer's Office |  | 0 |  | 286 | 6 | 0 |  | 2288 | 0 | 0
- | Main Office |  | 0 | Yes | 286 | 6 | 6 |  | 2288 | 0 | 0
- | Principal's Office |  | 0 | Yes | 154 | 3 | 3 |  | 1232 | 0 | 0
- | Teacher's Lounge |  | 0 |  | 322 | 7 | 0 |  | 2576 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | Bayard Taylor Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Main Building Test 10-29-20 | [7 empty] | 0 | 0 | 0
Vendor: | Devine Main Building Retest 2-7-21 | [7 empty] | 0 | 0 | 0
School: | Bayard Taylor Annex (Our Lady of Pompeii) | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | EMCOR Retest 2-18-21 | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Taylor Main Building | [8 empty] | 0 | 0 | 0
B1 | Classroom | 210 | 14 |  | 780 | 17 | 14 | Univent | 6240 | 2.0192 | 1
B1B and B1B North & South. | B1 and B1 North & South. | 325 | 21 |  | 760 | 17 | 17 | Univent | 6080 | 3.2072 | 1
B2A & B2B | Classroom | 0 | 0 |  | 600 | 13 | 0 | Univent | 4800 | 0 | 0
B4 | Classroom | 299 | 19 |  | 1444 | 32 | 19 | Univent | 11552 | 1.553 | 1
B5 | Classroom | 316 | 21 |  | 1410 | 32 | 21 | Univent | 11280 | 1.6809 | 1
101 | Classroom | 362 | 24 |  | 1159 | 26 | 24 | Univent | 9272 | 2.3425 | 1
102 | Classroom |  | 0 | Yes | 1148 | 26 | 26 | Univent | 9184 | 0 | 0
103 | Classroom | 328 | 21 |  | 1149 | 26 | 21 | Univent | 9192 | 2.141 | 1
104 | Classroom | 387 | 25 |  | 1107 | 25 | 25 | Univent | 8856 | 2.622 | 1
105 | Classroom | 387 | 25 |  | 1394 | 31 | 25 | Univent | 11152 | 2.0821 | 1
201 | Classroom | 342 | 22 |  | 1101 | 25 | 22 | Univent | 8808 | 2.3297 | 1
202 | Classroom | 423 | 28 |  | 1097 | 24 | 24 | Univent | 8776 | 2.892 | 1
203 | Classroom |  | 0 | Yes | 1163 | 26 | 26 | Univent | 9304 | 0 | 0
204 | Classroom | 444 | 29 |  | 1099 | 24 | 24 | Univent | 8792 | 3.03 | 1
205 | Classroom | 470 | 31 |  | 1098 | 24 | 24 | Univent | 8784 | 3.2104 | 1
206 | Classroom | 408 | 27 |  | 1052 | 23 | 23 | Univent | 8416 | 2.9087 | 1
301 | Classroom |  | 0 | Yes | 1066 | 24 | 24 | Univent | 8528 | 0 | 0
302 | Classroom | 299 | 19 |  | 1065 | 24 | 19 | Univent | 8520 | 2.1056 | 1
303 | Classroom | 317 | 21 |  | 1127 | 25 | 21 | Univent | 9016 | 2.1096 | 1
304 | Classroom | 344 | 22 |  | 1133 | 25 | 22 | Univent | 9064 | 2.2771 | 1
305 | Classroom | 73 | 4 | Yes | 1109 | 25 | 25 | Univent | 8872 | 0.49369 | 0
306 | Classroom | 483 | 32 |  | 1107 | 25 | 25 | Univent | 8856 | 3.2724 | 1
- | IMC Library | 353 | 23 |  | 1641 | 37 | 23 | Univent | 13128 | 1.6133 | 1
- | Music Classroom | 162 | 10 |  | 780 | 17 | 10 | Univent | 6240 | 1.5577 | 1
- | Main Office | 303 | 20 |  | 889 | 20 | 20 | Univent | 7112 | 2.5562 | 1
- | Principal | 359 | 23 |  | 479 | 10 | 10 | Univent | 3832 | 5.6211 | 2
- | Lounge | 232 | 15 |  | 300 | 6 | 6 | Univent | 2400 | 5.8 | 2
- | Nurse | 148 | 9 |  | 300 | 6 | 6 | Univent | 2400 | 3.7 | 1
- | Art Classroom | 123 | 8 |  | 1107 | 25 | 8 | Univent | 8856 | 0.83333 | 0
Taylor Annex | [8 empty] | 0 | 0 | 0
222 | Classroom |  | 0 |  | 750 | 17 | 0 | N/A | 6000 | 0 | 0
223 | Classroom |  | 0 |  | 625 | 14 | 0 | N/A | 5000 | 0 | 0
224 | Classroom |  | 0 |  | 675 | 15 | 0 | N/A | 5400 | 0 | 0
231 | Classroom |  | 0 |  | 700 | 15 | 0 | N/A | 5600 | 0 | 0
331 | Classroom |  | 0 |  | 700 | 15 | 0 | N/A | 5600 | 0 | 0
332 | Classroom |  | 0 |  | 750 | 17 | 0 | N/A | 6000 | 0 | 0
333 | Classroom |  | 0 |  | 675 | 15 | 0 | N/A | 5400 | 0 | 0
334 | Classroom |  | 0 |  | 625 | 14 | 0 | N/A | 5000 | 0 | 0
- | Auditorium/Gym/Ca |  | 0 |  | 2516 | 57 | 0 | N/A | 20128 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | Tilden Middle School | [7 empty] | 0 | 0 | 0
Vendor: | [8 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom |  | 0 |  | 576 | 13 | 0 | House Fan | 4608 | 0 | 0
101 | Classroom |  | 0 |  | 624 | 14 | 0 | House Fan | 4992 | 0 | 0
103 | Classroom |  | 0 | Yes | 960 | 21 | 21 | House Fan | 7680 | 0 | 0
104 | Classroom |  | 0 |  | 1248 | 28 | 0 | House Fan | 9984 | 0 | 0
105 | Classroom |  | 0 | Yes | 1248 | 28 | 28 | House Fan | 9984 | 0 | 0
106 | Classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan | 6912 | 0 | 0
107 | Classroom |  | 0 | Yes | 792 | 18 | 18 | House Fan | 6336 | 0 | 0
109 | Classroom |  | 0 | Yes | 792 | 18 | 18 | House Fan | 6336 | 0 | 0
109A | Classroom |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | 0 | 0
110 | Classroom |  | 0 | Yes | 616 | 14 | 14 | House Fan | 4928 | 0 | 0
202 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
203 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | 0 | 0
203A | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan | 8448 | 0 | 0
204 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | 0 | 0
205 | Nurse's office |  | 0 | Yes | 384 | 8 | 8 | House Fan | 3072 | 0 | 0
207A | Principal's Office |  | 0 | Yes | 560 | 12 | 12 | House Fan | 4480 | 0 | 0
207C | Counselor's Suite |  | 0 |  | 120 | 2 | 0 | House Fan | 960 | 0 | 0
207D | Counselor's Suite |  | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | 0 | 0
207F | Counselor's Suite |  | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | 0 | 0
207G | Counselor's Suite |  | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | 0 | 0
207H | Counselor's Suite |  | 0 |  | 120 | 2 | 0 | House Fan | 960 | 0 | 0
208 | Main Office |  | 0 | Yes | 560 | 12 | 12 | House Fan | 4480 | 0 | 0
209 | IMC |  | 0 | Yes | 1728 | 39 | 39 | House Fan | 13824 | 0 | 0
211 | Classroom |  | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | 0 | 0
212 | Classroom |  | 0 | Yes | 1152 | 26 | 26 | House Fan | 9216 | 0 | 0
213 | Classroom |  | 0 |  | 616 | 14 | 0 | House Fan | 4928 | 0 | 0
214 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | 0 | 0
214A | Classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan | 6912 | 0 | 0
215 | Classroom |  | 0 | Yes | 576 | 13 | 13 | House Fan | 4608 | 0 | 0
301 | Classroom |  | 0 |  | 576 | 13 | 0 | House Fan | 4608 | 0 | 0
302 | Carson Valley |  | 0 |  | 288 | 6 | 0 | House Fan | 2304 | 0 | 0
303 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | 0 | 0
303A | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | 0 | 0
304 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | 0 | 0
305 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | 0 | 0
306 | Classroom |  | 0 |  | 616 | 14 | 0 | House Fan | 4928 | 0 | 0
307 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | 0 | 0
308 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | 0 | 0
310 | Classroom |  | 0 |  | 480 | 10 | 0 | House Fan | 3840 | 0 | 0
311 | Classroom |  | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0
312 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | 0 | 0
313 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | 0 | 0
314 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | 0 | 0
315 | Dean of Students |  | 0 | Yes | 216 | 4 | 4 | House Fan | 1728 | 0 | 0
316 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0
318 | Classroom |  | 0 |  | 792 | 18 | 0 | House Fan | 6336 | 0 | 0
319 | Classroom |  | 0 |  | 832 | 18 | 0 | House Fan | 6656 | 0 | 0
401 | Classroom |  | 0 | Yes | 625 | 14 | 14 | House Fan | 5000 | 0 | 0
403A | Faculty Lounge |  | 0 | Yes | 792 | 18 | 18 | House Fan | 6336 | 0 | 0
404 | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan | 8448 | 0 | 0
404A | Classroom |  | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | 0 | 0
405 | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan | 8448 | 0 | 0
406 | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan | 8448 | 0 | 0
407 | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan | 8448 | 0 | 0
408 | Classroom |  | 0 | Yes | 792 | 18 | 18 | House Fan | 6336 | 0 | 0
410B | Staff Conference |  | 0 | Yes | 1232 | 28 | 28 | House Fan | 9856 | 0 | 0
411 | Classroom |  | 0 | Yes | 769 | 17 | 17 | House Fan | 6152 | 0 | 0
412 | Classroom |  | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | 0 | 0
414 | Classroom |  | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | 0 | 0
415 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | 0 | 0
416 | Classroom |  | 0 | Yes | 392 | 8 | 8 | House Fan | 3136 | 0 | 0
- | Cafeteria |  | 0 | Yes | 5150 | 117 | 117 | House Fan | 41200 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-30 | [7 empty] | 0 | 0 | 0
School: | Trinidad Center | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
- | Adult Restroom | 13 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Assistant Director's Office | 16 | 1 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Boy's Restroom | 16 | 1 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Computer Room | 31 | 2 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Front Entrance | 34 | 2 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Girl's Restroom | 18 | 1 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Gym |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Hallway |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Head Receptionist's Office | 21 | 1 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Kitchen | 50 | 3 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Library |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Main Corridor (Hallway) | 0 | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Maintenance Office | 22 | 1 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Rear Entrance | 19 | 1 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
1 | Classroom | 101 | 6 | Yes | 610 | 13 | 13 | Air Handling Unit | 4880 | 1.2418 | 1
2 | Classroom | 95 | 6 | Yes | 610 | 13 | 13 | Air Handling Unit | 4880 | 1.168 | 1
3 | Classroom | 100 | 6 | Yes | 575 | 13 | 13 | Air Handling Unit | 4600 | 1.3043 | 1
4 | Classroom | 112 | 7 | Yes | 575 | 13 | 13 | Air Handling Unit | 4600 | 1.4609 | 1
5 | Classroom | 132 | 8 |  | 590 | 13 | 8 | Air Handling Unit | 4720 | 1.678 | 1
6 | Classroom |  | 0 | Yes | 629 | 14 | 14 | Air Handling Unit | 5032 | 0 | 0
7 | Storage |  | 0 | Yes | 609 | 13 | 13 | Air Handling Unit | 4872 | 0 | 0
8 | Storage |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
9 | Storage |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
10 | Roof Access |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Stairway |  | 0 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [7 empty] | 0 | 0 | 0
School: | The U School at Ferguson | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
B10 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0
B11 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0
B12 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0
110 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0
111 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0
112 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0
113 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0
114 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0
115 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0
210 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0
211 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0
212 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0
213 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0
214 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0
215 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0
310 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0
311 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0
312 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0
313 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0
314 | Classroom | 0 | 0 |  | 442 | 10 | 0 | Unit Ventilator | 3536 | 0 | 0
315 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-06 | [7 empty] | 0 | 0 | 0
School: | Vare-Washington Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | EMCOR Retest | Devine Retest | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | classroom | 478 | 31 |  | 1040 | 23 | 23 | Unit Ventilator | 8320 | 3.4471 | 1
102 | classroom | 251 | 16 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | 2.0112 | 1
103 | classroom | 267 | 17 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.5673 | 1
104 | classroom | 331 | 22 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.1827 | 1
105 | classroom | 297 | 19 |  | 936 | 21 | 19 | Unit Ventilator | 7488 | 2.3798 | 1
106 | classroom | 390 | 26 |  | 1040 | 23 | 23 | Unit Ventilator | 8320 | 2.8125 | 1
107 | classroom | 210 | 14 | Yes | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.0192 | 1
108 | classroom | 319 | 21 |  | 767 | 17 | 17 | Unit Ventilator | 6136 | 3.1193 | 1
109 | classroom | 313 | 20 |  | 767 | 17 | 17 | Unit Ventilator | 6136 | 3.0606 | 1
110 | classroom | 594 | 39 |  | 1482 | 33 | 33 | Unit Ventilator | 11856 | 3.0061 | 1
201 | Counselor | 380 | 25 |  | 684 | 15 | 15 | Unit Ventilator | 5472 | 4.1667 | 2
202 | classroom | 326 | 21 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.9387 | 1
203 | 4-6 Autistic Supp. | 316 | 21 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.8486 | 1
204 | classroom | 310 | 20 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.7945 | 1
205 | K-2 Autistic Supp. | 210 | 14 | Yes | 832 | 18 | 18 | Unit Ventilator | 6656 | 1.893 | 1
206 | classroom | 417 | 27 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 3.759 | 1
207 | classroom | 227 | 15 |  | 832 | 18 | 15 | Unit Ventilator | 6656 | 2.0463 | 1
208A | 3-4 Autistic Supp. | 293 | 19 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.6412 | 1
208B | K-2 Emotional Support | 297 | 19 |  | 725 | 16 | 16 | Unit Ventilator | 5800 | 3.0724 | 1
210 | ESOL | 234 | 15 |  | 575 | 13 | 13 | Unit Ventilator | 4600 | 3.0522 | 1
211 | ESOL/SBTL | 251 | 16 |  | 628 | 14 | 14 | Unit Ventilator | 5024 | 2.9976 | 1
213 | classroom | 405 | 27 |  | 1092 | 24 | 24 | Unit Ventilator | 8736 | 2.7816 | 1
214 | classroom | 322 | 21 |  | 468 | 10 | 10 | Unit Ventilator | 3744 | 5.1603 | 2
301 | classroom | 258 | 17 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.4808 | 1
302 | classroom | 291 | 19 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.7981 | 1
303 | classroom | 217 | 14 | Yes | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.0865 | 1
304 | classroom | 234 | 15 |  | 780 | 17 | 15 | Unit Ventilator | 6240 | 2.25 | 1
305 | classroom | 287 | 19 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.7596 | 1
306 | classroom | 323 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5109 | 1
307 | classroom | 217 | 14 | Yes | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.0865 | 1
308 | classroom | 269 | 17 |  | 988 | 22 | 17 | Unit Ventilator | 7904 | 2.042 | 1
309 | Psychologist / Climate Liaison | 185 | 12 |  | 598 | 13 | 12 | Unit Ventilator | 4784 | 2.3202 | 1
310 | Math Interventionist | 211 | 14 |  | 624 | 14 | 14 | Unit Ventilator | 4992 | 2.5361 | 1
311 | classroom | 189 | 12 | Yes | 624 | 14 | 14 | Unit Ventilator | 4992 | 2.2716 | 1
312A | classroom | 295 | 19 |  | 1014 | 23 | 19 | Unit Ventilator | 8112 | 2.182 | 1
313 | classroom | 166 | 11 |  | 494 | 11 | 11 | Unit Ventilator | 3952 | 2.5202 | 1
- | Gym | 305 | 20 |  | 4352 | 98 | 20 | Unit Ventilator | 34816 | 0.52562 | 0
- | Library | 208 | 13 |  | 578 | 13 | 13 | Unit Ventilator | 4624 | 2.699 | 1
- | Lunch Room | 146 | 9 | Yes | 1292 | 29 | 29 | Unit Ventilator | 10336 | 0.84752 | 0
- | Music | 748 | 49 |  | 1098 | 24 | 24 | Unit Ventilator | 8784 | 5.1093 | 2
- | Main Office |  | 0 | Yes | 396 | 9 | 9 | Active Pure Unit | 3168 | 0 | 0
- | Princpal's Office |  | 0 | Yes | 350 | 7 | 7 | Active Pure Unit | 2800 | 0 | 0
- | Nurse's Office |  | 0 | Yes | 264 | 6 | 6 | Active Pure Unit | 2112 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-12 | [7 empty] | 0 | 0 | 0
School: | EH Vare | [7 empty] | 0 | 0 | 0
Vendor: | [8 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
109 | - |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
110 | - |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21 | [7 empty] | 0 | 0 | 0
School: | General Louis Wagner Middle School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | Exhaust Report | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101A | classroom | 312 | 20 |  | 552 | 12 | 12 | Air Handling Unit | 4416 | 4.2391 | 2
101B | classroom | 376 | 25 |  | 506 | 11 | 11 | Air Handling Unit | 4048 | 5.5731 | 2
102 | classroom | 644 | 42 |  | 888 | 20 | 20 | Air Handling Unit | 7104 | 5.4392 | 2
103A | classroom | 1312 | 87 |  | 1344 | 30 | 30 | Air Handling Unit | 10752 | 7.3214 | 2
105 | classroom | 527 | 35 |  | 878 | 19 | 19 | Air Handling Unit | 7024 | 4.5017 | 2
106 | classroom | 713 | 47 |  | 883 | 20 | 20 | Air Handling Unit | 7064 | 6.0561 | 2
107 | classroom | 635 | 42 |  | 705 | 16 | 16 | Air Handling Unit | 5640 | 6.7553 | 2
108 | classroom | 586 | 39 |  | 916 | 20 | 20 | Air Handling Unit | 7328 | 4.798 | 2
111 | classroom | 536 | 35 |  | 360 | 8 | 8 | Air Handling Unit | 2880 | 11.1667 | 3
112 | classroom | 585 | 39 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 6.0938 | 2
201 | classroom | 973 | 64 |  | 711 | 16 | 16 | Air Handling Unit | 5688 | 10.2637 | 3
202 | classroom | 907 | 60 |  | 677 | 15 | 15 | Air Handling Unit | 5416 | 10.048 | 3
203 | classroom | 306 | 20 |  | 697 | 15 | 15 | Air Handling Unit | 5576 | 3.2927 | 1
204 | classroom | 600 | 40 |  | 657 | 14 | 14 | Air Handling Unit | 5256 | 6.8493 | 2
205A | Counselor Office | 597 | 39 |  | 306 | 6 | 6 | Air Handling Unit | 2448 | 14.6324 | 3
205B | Counselor Office | 690 | 46 |  | 306 | 6 | 6 | Air Handling Unit | 2448 | 16.9118 | 3
209A | classroom | 496 | 33 |  | 2064 | 46 | 33 | Air Handling Unit | 16512 | 1.8023 | 1
209B | classroom | 763 | 50 |  | 336 | 7 | 7 | Air Handling Unit | 2688 | 17.0312 | 3
209C | classroom | 995 | 66 |  | 336 | 7 | 7 | Air Handling Unit | 2688 | 22.2098 | 3
212 | classroom | 1030 | 68 |  | 859 | 19 | 19 | Air Handling Unit | 6872 | 8.993 | 2
213 | classroom | 870 | 58 |  | 656 | 14 | 14 | Air Handling Unit | 5248 | 9.9466 | 2
214 | classroom | 446 | 29 |  | 714 | 16 | 16 | Air Handling Unit | 5712 | 4.6849 | 2
215 | classroom | 240 | 16 |  | 659 | 14 | 14 | Air Handling Unit | 5272 | 2.7314 | 1
216 | classroom | 2170 | 144 |  | 777 | 17 | 17 | Air Handling Unit | 6216 | 20.9459 | 3
217 | classroom | 1626 | 108 |  | 743 | 16 | 16 | Air Handling Unit | 5944 | 16.4132 | 3
218 | classroom | 197 | 13 |  | 645 | 14 | 13 | Air Handling Unit | 5160 | 2.2907 | 1
219 | classroom | 1463 | 97 |  | 643 | 14 | 14 | Air Handling Unit | 5144 | 17.0645 | 3
220 | classroom | 731 | 48 |  | 563 | 12 | 12 | Air Handling Unit | 4504 | 9.738 | 2
221 | classroom | 1653 | 110 |  | 779 | 17 | 17 | Air Handling Unit | 6232 | 15.9146 | 3
222 | classroom | 667 | 44 |  | 670 | 15 | 15 | Air Handling Unit | 5360 | 7.4664 | 2
225 | Dean | 272 | 18 |  | 348 | 7 | 7 | Air Handling Unit | 2784 | 5.8621 | 2
226 | classroom | 671 | 44 |  | 654 | 14 | 14 | Air Handling Unit | 5232 | 7.695 | 2
301 | classroom | 1282 | 85 |  | 714 | 16 | 16 | Air Handling Unit | 5712 | 13.4664 | 3
302 | classroom | 2224 | 148 |  | 670 | 15 | 15 | Air Handling Unit | 5360 | 24.8955 | 4
303 | classroom | 2929 | 195 |  | 671 | 15 | 15 | Air Handling Unit | 5368 | 32.7385 | 4
304A | classroom | 1335 | 89 |  | 984 | 22 | 22 | Air Handling Unit | 7872 | 10.1753 | 3
305 | classroom | 3981 | 265 |  | 956 | 21 | 21 | Air Handling Unit | 7648 | 31.2317 | 4
306 | classroom | 3461 | 230 |  | 783 | 17 | 17 | Air Handling Unit | 6264 | 33.1513 | 4
307 | classroom | 996 | 66 |  | 912 | 20 | 20 | Air Handling Unit | 7296 | 8.1908 | 2
308 | classroom | 1202 | 80 |  | 928 | 21 | 21 | Air Handling Unit | 7424 | 9.7144 | 2
309 | classroom | 2171 | 144 |  | 847 | 19 | 19 | Air Handling Unit | 6776 | 19.2237 | 3
310 | classroom | 2047 | 136 |  | 881 | 20 | 20 | Air Handling Unit | 7048 | 17.4262 | 3
311A | classroom | 990 | 66 |  | 929 | 21 | 21 | Air Handling Unit | 7432 | 7.9925 | 2
312 | classroom | 211 | 14 |  | 716 | 16 | 14 | Air Handling Unit | 5728 | 2.2102 | 1
313 | classroom | 868 | 57 |  | 672 | 15 | 15 | Air Handling Unit | 5376 | 9.6875 | 2
314 | classroom | 350 | 23 |  | 719 | 16 | 16 | Air Handling Unit | 5752 | 3.6509 | 1
315 | classroom | 83 | 5 |  | 662 | 15 | 5 | Air Handling Unit | 5296 | 0.94033 | 0
316 | classroom | 1078 | 71 |  | 778 | 17 | 17 | Air Handling Unit | 6224 | 10.392 | 3
317 | classroom | 1382 | 92 |  | 604 | 13 | 13 | Air Handling Unit | 4832 | 17.1606 | 3
318 | classroom | 1811 | 120 |  | 610 | 13 | 13 | Air Handling Unit | 4880 | 22.2664 | 3
319 | classroom | 3185 | 212 |  | 644 | 14 | 14 | Air Handling Unit | 5152 | 37.0924 | 4
320 | classroom | 4504 | 300 |  | 738 | 16 | 16 | Air Handling Unit | 5904 | 45.7724 | 4
321 | classroom | 3538 | 235 |  | 786 | 17 | 17 | Air Handling Unit | 6288 | 33.7595 | 4
322 | classroom | 82 | 5 |  | 660 | 15 | 5 | Air Handling Unit | 5280 | 0.93182 | 0
323 | classroom | 1074 | 71 |  | 324 | 7 | 7 | Air Handling Unit | 2592 | 24.8611 | 4
324 | classroom | 909 | 60 |  | 659 | 14 | 14 | Air Handling Unit | 5272 | 10.3452 | 3
325 | classroom | 1021 | 68 |  | 346 | 7 | 7 | Air Handling Unit | 2768 | 22.1315 | 3
326 | classroom | 481 | 32 |  | 659 | 14 | 14 | Air Handling Unit | 5272 | 5.4742 | 2
326 | Counselor Office | 513 | 34 |  | 306 | 6 | 6 | Air Handling Unit | 2448 | 12.5735 | 3
- | Auditorium | 0 | 0 |  | 5460 | 124 | 0 | Air Handling Unit | 43680 | 0 | 0
- | Boy's Gym | 14624 | 974 |  | 4350 | 98 | 98 | Air Handling Unit | 34800 | 25.2138 | 4
- | Cafeteria | 498 | 33 |  | 408 | 9 | 9 | Air Handling Unit | 3264 | 9.1544 | 2
- | Computer Lab | 446 | 29 |  | 657 | 14 | 14 | Air Handling Unit | 5256 | 5.0913 | 2
- | Conf. Room | 884 | 58 |  | 336 | 7 | 7 | Air Handling Unit | 2688 | 19.7321 | 3
- | Kitchen | 5749 | 383 |  | 816 | 18 | 18 | Air Handling Unit | 6528 | 52.8401 | 5
- | Kitchen- Freezer/Cooler Condenser Fan | 0 | 0 |  | 144 | 3 | 0 | Air Handling Unit | 1152 | 0 | 0
- | Lunch Room | 175 | 11 |  | 2040 | 46 | 11 | Air Handling Unit | 16320 | 0.64338 | 0
- | Main Office | 632 | 42 |  | 531 | 12 | 12 | Air Handling Unit | 4248 | 8.9266 | 2
Principal | Office |  | 0 | Yes | 259 | 5 | 5 |  | 2072 | 0 | 0
Nurse | Office |  | 0 | Yes | 249 | 5 | 5 |  | 1992 | 0 | 0
- | MEDIA LAB A | 304 | 20 |  | 60 | 1 | 1 | Air Handling Unit | 480 | 38 | 4
- | MEDIA LAB B | 564 | 37 |  | 60 | 1 | 1 | Air Handling Unit | 480 | 70.5 | 5
- | Staff Lounge | 421 | 28 |  | 657 | 14 | 14 | Air Handling Unit | 5256 | 4.8059 | 2
- | VP Office | 1325 | 88 |  | 232 | 5 | 5 | Air Handling Unit | 1856 | 42.8341 | 4
- | Gym- Weight Room A | 1230 | 82 |  | 181 | 4 | 4 | Air Handling Unit | 1448 | 50.9669 | 5
- | Gym- Weight Room B | 1164 | 77 |  | 181 | 4 | 4 | Air Handling Unit | 1448 | 48.232 | 4
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26 | [7 empty] | 0 | 0 | 0
School: | Laura W. Waring Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | EMCOR Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 188 | 12 | Yes | 430 | 9 | 9 | Nesbitt Unit Ventilator | 3440 | 3.2791 | 1
102 | Classroom | 118 | 7 | Yes | 872 | 19 | 19 | Nesbitt Unit Ventilator | 6976 | 1.0149 | 1
103 | Classroom | 150 | 10 | Yes | 872 | 19 | 19 | Nesbitt Unit Ventilator | 6976 | 1.2901 | 1
105 | Classroom | 180 | 12 | Yes | 789 | 17 | 17 | Nesbitt Unit Ventilator | 6312 | 1.711 | 1
106 | Classroom | 171 | 11 | Yes | 850 | 19 | 19 | Nesbitt Unit Ventilator | 6800 | 1.5088 | 1
107 | Classroom | 226 | 15 |  | 850 | 19 | 15 | Nesbitt Unit Ventilator | 6800 | 1.9941 | 1
108 | Classroom | 165 | 11 | Yes | 750 | 17 | 17 | Nesbitt Unit Ventilator | 6000 | 1.65 | 1
200 | Counselor's Room | 0 | 0 |  | 300 | 6 | 0 | Nesbitt Unit Ventilator | 2400 | 0 | 0
201 | Computer Room | 0 | 0 | Yes | 925 | 21 | 21 | Nesbitt Unit Ventilator | 7400 | 0 | 0
202 | Classroom | 87 | 5 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator | 7104 | 0.7348 | 0
203 | Classroom | 274 | 18 |  | 888 | 20 | 18 | Nesbitt Unit Ventilator | 7104 | 2.3142 | 1
204 | Classroom | 276 | 18 |  | 888 | 20 | 18 | Nesbitt Unit Ventilator | 7104 | 2.3311 | 1
205 | Classroom | 311 | 20 |  | 850 | 19 | 19 | Nesbitt Unit Ventilator | 6800 | 2.7441 | 1
206 | Classroom | 193 | 12 | Yes | 850 | 19 | 19 | Nesbitt Unit Ventilator | 6800 | 1.7029 | 1
207 | Classroom | 152 | 10 | Yes | 850 | 19 | 19 | Nesbitt Unit Ventilator | 6800 | 1.3412 | 1
208 | Classroom | 209 | 13 | Yes | 750 | 17 | 17 | Nesbitt Unit Ventilator | 6000 | 2.09 | 1
300 | Classroom | 0 | 0 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator | 7104 | 0 | 0
301 | Classroom | 212 | 14 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator | 7104 | 1.7905 | 1
302 | Classroom | 105 | 7 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator | 7104 | 0.88682 | 0
303 | Classroom | 133 | 8 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator | 7104 | 1.1233 | 1
304 | Classroom | 255 | 17 |  | 888 | 20 | 17 | Nesbitt Unit Ventilator | 7104 | 2.1537 | 1
305 | Classroom | 93 | 6 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator | 7104 | 0.78547 | 0
306/307 | Classroom | 266 | 17 |  | 1850 | 42 | 17 | Nesbitt Unit Ventilator | 14800 | 1.0784 | 1
308 | Classroom | 220 | 14 | Yes | 896 | 20 | 20 | Nesbitt Unit Ventilator | 7168 | 1.8415 | 1
311 | Dining Room | 120 | 8 |  | 242 | 5 | 5 | Nesbitt Unit Ventilator | 1936 | 3.719 | 1
- | Cafeteria | 0 | 0 |  | 3477 | 79 | 0 | Nesbitt Unit Ventilator | 27816 | 0 | 0
- | Vestibule left of office | 0 | 0 |  | 96 | 2 | 0 | Nesbitt Unit Ventilator | 768 | 0 | 0
- | Nurse |  | 0 |  | 231 | 5 | 0 | Nesbitt Unit Ventilator | 1848 | 0 | 0
- | Faculty Lounge | 57 | 3 |  | 228 | 5 | 3 | Nesbitt Unit Ventilator | 1824 | 1.875 | 1
- | Health Office | 0 | 0 | Yes | 231 | 5 | 5 | Nesbitt Unit Ventilator | 1848 | 0 | 0
- | Multi-Purpose Room | 457 | 30 |  | 1820 | 41 | 30 | Nesbitt Unit Ventilator | 14560 | 1.8832 | 1
- | Main Office | 0 | 0 | Yes | 378 | 8 | 8 | Nesbitt Unit Ventilator | 3024 | 0 | 0
- | Principal's Office | 69 | 4 | Yes | 381 | 8 | 8 | Nesbitt Unit Ventilator | 3048 | 1.3583 | 1
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | George Washington High School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | Meehan (Auditorium) | [6 empty] | 0 | 0 | 0
School: | George Washington High School Annex | [7 empty] | 0 | 0 | 0
Vendor: | [8 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Main Building | [8 empty] | 0 | 0 | 0
1 | - | 370 | 24 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.6133 | 1
2 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
3 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0
4 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
5 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0
6 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
7 | - | 348 | 23 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.3984 | 1
8 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
9 | - | 412 | 27 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.0234 | 2
10 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
11 | - | 451 | 30 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.4043 | 2
12 | - | 0 | 0 |  | 775 | 17 | 0 | Carrier / Perimeter Heater | 6200 | 0 | 0
13 | - | 414 | 27 |  | 1209 | 27 | 27 | Carrier / Perimeter Heater | 9672 | 2.5682 | 1
14 | - | 374 | 24 |  | 1209 | 27 | 24 | Carrier / Perimeter Heater | 9672 | 2.3201 | 1
15 | - | 403 | 26 |  | 1209 | 27 | 26 | Carrier / Perimeter Heater | 9672 | 2.5 | 1
16 | - | 849 | 56 |  | 1911 | 43 | 43 | Carrier / Perimeter Heater | 15288 | 3.332 | 1
17 | - | 0 | 0 |  | 1240 | 28 | 0 | Carrier / Perimeter Heater | 9920 | 0 | 0
18 | - | 763 | 50 |  | 1911 | 43 | 43 | Carrier / Perimeter Heater | 15288 | 2.9945 | 1
19 | - | 0 | 0 |  | 1302 | 29 | 0 | Carrier / Perimeter Heater | 10416 | 0 | 0
20 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
21 | - | 451 | 30 |  | 1240 | 28 | 28 | Carrier / Perimeter Heater | 9920 | 2.7278 | 1
22 | - | 421 | 28 |  | 1209 | 27 | 27 | Carrier / Perimeter Heater | 9672 | 2.6117 | 1
23 | - | 0 | 0 |  | 1240 | 28 | 0 | Carrier / Perimeter Heater | 9920 | 0 | 0
24 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
25 | - | 419 | 27 |  | 912 | 20 | 20 | Carrier / Perimeter Heater | 7296 | 3.4457 | 1
26 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
27 | - | 0 | 0 |  | 912 | 20 | 0 | Carrier / Perimeter Heater | 7296 | 0 | 0
28 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
29 | - | 355 | 23 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.4668 | 1
30 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
31 | - | 413 | 27 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.0332 | 2
32 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
33 | - | 338 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.3008 | 1
34 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
35 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0
36 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
37 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0
38 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
39 | - | 403 | 26 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.9355 | 1
100 | - | 334 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.2617 | 1
102 | - | 335 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.2715 | 1
104 | Health Room |  | 0 |  | 1488 | 33 | 0 |  | 11904 | 0 | 0
107 | - | 495 | 33 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
108 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
109 | - | 357 | 23 |  | 744 | 16 | 16 | Carrier / Perimeter Heater | 5952 | 3.5988 | 1
110 | - | 413 | 27 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
111 | - | 370 | 24 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.6133 | 1
112 | - | 398 | 26 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.8867 | 1
113 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
114 | - | 427 | 28 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.1699 | 2
115 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
116 | - | 368 | 24 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.5938 | 1
117 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
118 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0
119 | - | 368 | 24 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
120 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0
121 | - | 381 | 25 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.7207 | 1
122 | - | 408 | 27 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 3.8636 | 1
123 | - | 465 | 31 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.541 | 2
124 | - | 436 | 29 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.2578 | 2
125 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
126 | - | 336 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.2812 | 1
127 | - | 416 | 27 |  | 1102 | 25 | 25 | Carrier / Perimeter Heater | 8816 | 2.8312 | 1
128 | - | 0 | 0 |  | 1280 | 29 | 0 | Carrier / Perimeter Heater | 10240 | 0 | 0
129 | - | 366 | 24 |  | 1073 | 24 | 24 | Carrier / Perimeter Heater | 8584 | 2.5582 | 1
130 | - | 0 | 0 |  | 1280 | 29 | 0 | Carrier / Perimeter Heater | 10240 | 0 | 0
131 | - | 388 | 25 |  | 1160 | 26 | 25 | Carrier / Perimeter Heater | 9280 | 2.5086 | 1
132 | - | 610 | 40 |  | 1092 | 24 | 24 | Carrier / Perimeter Heater | 8736 | 4.1896 | 2
133 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
134 | - | 732 | 48 |  | 1092 | 24 | 24 | Carrier / Perimeter Heater | 8736 | 5.0275 | 2
135 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
136 | - | 325 | 21 |  | 1092 | 24 | 21 | Carrier / Perimeter Heater | 8736 | 2.2321 | 1
137 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
138 | - | 408 | 27 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
139 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
140 | - | 424 | 28 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
141 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
142 | - | 865 | 57 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
143 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
144 | - | 308 | 20 |  | 832 | 18 | 18 | Carrier / Perimeter Heater | 6656 | 2.7764 | 1
145 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
146 | - | 0 | 0 |  | 775 | 17 | 0 | Carrier / Perimeter Heater | 6200 | 0 | 0
147 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
148 | - | 242 | 16 |  | 775 | 17 | 16 | Carrier / Perimeter Heater | 6200 | 2.3419 | 1
149 -155 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
156 | - | 926 | 61 |  | 814 | 18 | 18 | Carrier / Perimeter Heater | 6512 | 8.5319 | 2
157 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
158 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
159 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
160 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
161 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
162 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
164 | - | 695 | 46 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
200 | - | 485 | 32 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.7363 | 2
201 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
202 | - | 417 | 27 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.0723 | 2
203 | - | 397 | 26 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.877 | 1
204 | - | 337 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.291 | 1
205 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0
206 | - | 424 | 28 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
207 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0
208 | - | 536 | 35 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.2344 | 2
209 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
210 | - | 575 | 38 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.6152 | 2
211 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
212 | - | 514 | 34 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.0195 | 2
213 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
214 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0
215 | - | 547 | 36 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.3418 | 2
216 | - | 519 | 34 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.0684 | 2
217 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
218 | - | 521 | 34 |  | 1536 | 34 | 34 | Carrier / Perimeter Heater | 12288 | 2.5439 | 1
219 | - | 0 | 0 |  | 1536 | 34 | 0 | Carrier / Perimeter Heater | 12288 | 0 | 0
220 | - | 0 | 0 |  | 1536 | 34 | 0 | Carrier / Perimeter Heater | 12288 | 0 | 0
221 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0
222 | - | 569 | 37 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.5566 | 2
223 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
224 | - | 533 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.0473 | 2
225 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
226 | - | 536 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.0758 | 2
227 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
228 | - | 543 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.142 | 2
229 | - | 508 | 33 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 4.8106 | 2
230 | - | 563 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.3314 | 2
231 | - | 492 | 32 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 4.6591 | 2
232 | - | 563 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.3314 | 2
233 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
234 | - | 539 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.1042 | 2
235 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
236 | - | 544 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.1515 | 2
237 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
238 | - | 399 | 26 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 3.7784 | 1
239 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
240 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0
241 | - | 344 | 22 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 3.2576 | 1
242 | - | 450 | 30 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.3945 | 2
243 | - | 455 | 30 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 4.3087 | 2
244 | - | 428 | 28 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 4.053 | 2
245 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
246 | - | 423 | 28 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 4.0057 | 2
300 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
301 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
302 | - | 542 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.1326 | 2
303 | - | 539 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.1042 | 2
304 | - | 591 | 39 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.5966 | 2
305 | - | 556 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.2652 | 2
306 | - | 561 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.3125 | 2
307 | - | 592 | 39 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.6061 | 2
308 | - | 263 | 17 |  | 792 | 18 | 17 | Carrier / Perimeter Heater | 6336 | 2.4905 | 1
309 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
310 | - | 602 | 40 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.7008 | 2
311 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
312 | - | 599 | 39 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.6723 | 2
313 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
314 | - | 539 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.1042 | 2
315 | - | 530 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.0189 | 2
316 | - | 557 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.2746 | 2
317 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
318 | - | 580 | 38 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.6641 | 2
319 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
320 | - | 610 | 40 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.957 | 2
321 | - | 551 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.2178 | 2
322 | - | 554 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.2462 | 2
323 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
324 | - | 591 | 39 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 4.6172 | 2
325 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
326 | - | 533 | 35 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 4.1641 | 2
327 | - | 554 | 36 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 4.3281 | 2
328 | - | 561 | 37 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 4.3828 | 2
329 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
330 | - | 572 | 38 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 4.4688 | 2
331 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
332 | - | 576 | 38 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.4545 | 2
333 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
334 | - | 506 | 33 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 3.9531 | 1
335 | - | 605 | 40 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
336 | - | 559 | 37 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 4.3672 | 2
337 | - | 0 | 0 |  | 792 | 18 | 0 | Carrier / Perimeter Heater | 6336 | 0 | 0
338 | - | 0 | 0 |  | 792 | 18 | 0 | Carrier / Perimeter Heater | 6336 | 0 | 0
339 | - | 0 | 0 |  | 792 | 18 | 0 | Carrier / Perimeter Heater | 6336 | 0 | 0
Gymnasium | Gymnasium |  | 0 |  |  | 0 | 0 |  | 0 | 0 | 0
Auditorium | Auditorium | 17891 | 1192 |  | 10800 | 245 | 245 | Air Handling Unit | 86400 | 12.4243 | 3
- | Beacon Left | 311 | 20 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
- | Beacon Right | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
- | Cafeteria | 17015 | 1134 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
Center | - | 438 | 29 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
Dean's Office | - | 437 | 29 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
Library Left | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
Main Office | - | 394 | 26 |  | 2332 | 53 | 26 | Carrier / Perimeter Heater | 18656 | 1.2672 | 1
Principle | - | 0 | 0 |  | 615 | 13 | 0 | Carrier / Perimeter Heater | 4920 | 0 | 0
Right | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
- | Roster | 426 | 28 |  |  | 0 | 0 | Carrier / Perimeter Heater | 0 | 0 | 0
- | Staff Cafeteria | 1328 | 88 |  |  | 0 | 0 | Make-up Air Unit | 0 | 0 | 0
- | Student Cafeteria | 8507 | 567 |  | 12000 | 272 | 272 | Make-up Air Unit | 96000 | 5.3169 | 2
Annex | [8 empty] | 0 | 0 | 0
408 Annex | Classroom |  | 0 | Yes | 858 | 19 | 19 | Air Handling Unit | 6864 | 0 | 0
409 Annex | Classroom |  | 0 | Yes | 858 | 19 | 19 | Air Handling Unit | 6864 | 0 | 0
410 Annex | Classroom |  | 0 | Yes | 858 | 19 | 19 | Air Handling Unit | 6864 | 0 | 0
412 Annex | Classroom |  | 0 | Yes |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
Kitchen Annex | Kitchen |  | 0 | Yes |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
Recceration room | - |  | 0 |  | 3780 | 85 | 85 |  | 30240 | 0 | 0
Health Suite/ 11 rms | - |  | 0 |  | 77 | 1 | 1 |  | 616 | 0 | 0
Health Suite/ 2 rms | - |  | 0 |  | 80 | 1 | 1 |  | 640 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-14 | [7 empty] | 0 | 0 | 0
School: | Grover Washington Jr. Middle School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | CLASSROOM | 288 | 19 |  | 700 | 15 | 15 | Fan Coil Unit | 5600 | 3.0857 | 1
101 | CLASSROOM | 207 | 13 | Yes | 700 | 15 | 15 | Fan Coil Unit | 5600 | 2.2179 | 1
102 | CLASSROOM | 164 | 10 | Yes | 698 | 15 | 15 | Fan Coil Unit | 5584 | 1.7622 | 1
102A | CLASSROOM | 185 | 12 |  | 160 | 3 | 3 | Fan Coil Unit | 1280 | 8.6719 | 2
103 | CLASSROOM | 476 | 31 |  | 858 | 19 | 19 | Univent | 6864 | 4.1608 | 2
104 | CLASSROOM | 595 | 39 |  | 783 | 17 | 17 | Univent | 6264 | 5.6992 | 2
105 | CLASSROOM | 935 | 62 |  | 726 | 16 | 16 | Univent | 5808 | 9.6591 | 2
106 | CLASSROOM | 421 | 28 |  | 726 | 16 | 16 | Univent | 5808 | 4.3492 | 2
107 | CLASSROOM | 274 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.3951 | 1
108 | CLASSROOM | 395 | 26 |  | 858 | 19 | 19 | Univent | 6864 | 3.4528 | 1
109 | CLASSROOM | 573 | 38 |  | 858 | 19 | 19 | Univent | 6864 | 5.0087 | 2
110 | CLASSROOM | 310 | 20 |  | 858 | 19 | 19 | Univent | 6864 | 2.7098 | 1
112 | CLASSROOM | 377 | 25 |  | 858 | 19 | 19 | Univent | 6864 | 3.2955 | 1
113 | CLASSROOM | 392 | 26 |  | 312 | 7 | 7 | Univent | 2496 | 9.4231 | 2
114 | CLASSROOM | 361 | 24 |  | 858 | 19 | 19 | Univent | 6864 | 3.1556 | 1
115 | CLASSROOM | 292 | 19 |  | 726 | 16 | 16 | Univent | 5808 | 3.0165 | 1
116 | CLASSROOM | 749 | 49 |  | 726 | 16 | 16 | Univent | 5808 | 7.7376 | 2
117 | CLASSROOM | 763 | 50 |  | 726 | 16 | 16 | Univent | 5808 | 7.8822 | 2
118 | CLASSROOM | 757 | 50 |  | 726 | 16 | 16 | Univent | 5808 | 7.8202 | 2
119 | CLASSROOM | 396 | 26 |  | 858 | 19 | 19 | Univent | 6864 | 3.4615 | 1
120 | CLASSROOM | 304 | 20 |  | 858 | 19 | 19 | Univent | 6864 | 2.6573 | 1
121 | CLASSROOM | 370 | 24 |  | 858 | 19 | 19 | Univent | 6864 | 3.2343 | 1
122 | CLASSROOM | 314 | 20 |  | 858 | 19 | 19 | Univent | 6864 | 2.7448 | 1
201 | 2ND FLOOR C WING OFFICE | 211 | 14 |  | 312 | 7 | 7 | Univent | 2496 | 5.0721 | 2
202 | CLASSROOM | 601 | 40 |  | 858 | 19 | 19 | Univent | 6864 | 5.2535 | 2
203 | CLASSROOM | 580 | 38 |  | 858 | 19 | 19 | Univent | 6864 | 5.0699 | 2
204 | CLASSROOM | 304 | 20 |  | 858 | 19 | 19 | Univent | 6864 | 2.6573 | 1
205 | CLASSROOM | 285 | 19 |  | 858 | 19 | 19 | Univent | 6864 | 2.4913 | 1
206 | CLASSROOM | 406 | 27 |  | 783 | 17 | 17 | Univent | 6264 | 3.8889 | 1
207 | CLASSROOM | 456 | 30 |  | 726 | 16 | 16 | Univent | 5808 | 4.7107 | 2
208 | CLASSROOM | 561 | 37 |  | 1584 | 36 | 36 | Univent | 12672 | 2.6562 | 1
209 | CLASSROOM | 320 | 21 |  | 858 | 19 | 19 | Univent | 6864 | 2.7972 | 1
210 | CLASSROOM | 388 | 25 |  | 858 | 19 | 19 | Univent | 6864 | 3.3916 | 1
211 | CLASSROOM | 348 | 23 |  | 858 | 19 | 19 | Univent | 6864 | 3.042 | 1
212 | CLASSROOM | 318 | 21 |  | 858 | 19 | 19 | Univent | 6864 | 2.7797 | 1
213 | CLASSROOM | 307 | 20 |  | 1248 | 28 | 20 | Univent | 9984 | 1.845 | 1
214 | CLASSROOM | 286 | 19 | Yes | 1144 | 26 | 26 | Univent | 9152 | 1.875 | 1
215 | CLASSROOM | 693 | 46 |  | 1170 | 26 | 26 | Univent | 9360 | 4.4423 | 2
216 | CLASSROOM | 370 | 24 |  | 783 | 17 | 17 | Univent | 6264 | 3.5441 | 1
217 | CLASSROOM | 306 | 20 |  | 726 | 16 | 16 | Univent | 5808 | 3.1612 | 1
218 | CLASSROOM | 314 | 20 |  | 783 | 17 | 17 | Univent | 6264 | 3.0077 | 1
219 | CLASSROOM | 332 | 22 |  | 858 | 19 | 19 | Univent | 6864 | 2.9021 | 1
220 | CLASSROOM | 407 | 27 |  | 858 | 19 | 19 | Univent | 6864 | 3.5577 | 1
221 | 2ND FLOOR D WING OFFICE | 181 | 12 |  | 312 | 7 | 7 | Univent | 2496 | 4.351 | 2
301 | CLASSROOM | 112 | 7 | Yes | 858 | 19 | 19 | Fan Coil Unit | 6864 | 0.97902 | 0
302 | CLASSROOM | 339 | 22 |  | 858 | 19 | 19 | Univent | 6864 | 2.9633 | 1
303 | CLASSROOM | 0 | 0 | Yes | 858 | 19 | 19 | Univent | 6864 | 0 | 0
304 | CLASSROOM | 231 | 15 |  | 858 | 19 | 15 | Univent | 6864 | 2.0192 | 1
305 | CLASSROOM | 385 | 25 |  | 858 | 19 | 19 | Univent | 6864 | 3.3654 | 1
306 | CLASSROOM | 353 | 23 |  | 783 | 17 | 17 | Univent | 6264 | 3.3812 | 1
307 | CLASSROOM | 316 | 21 |  | 726 | 16 | 16 | Univent | 5808 | 3.2645 | 1
308 | CLASSROOM | 306 | 20 |  | 1584 | 36 | 20 | Univent | 12672 | 1.4489 | 1
309 | CLASSROOM | 486 | 32 |  | 858 | 19 | 19 | Univent | 6864 | 4.2483 | 2
310 | CLASSROOM | 283 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.4738 | 1
311 | CLASSROOM | 265 | 17 |  | 858 | 19 | 17 | Univent | 6864 | 2.3164 | 1
312 | CLASSROOM | 389 | 25 |  | 858 | 19 | 19 | Univent | 6864 | 3.4003 | 1
313 | CLASSROOM | 355 | 23 |  | 858 | 19 | 19 | Univent | 6864 | 3.1031 | 1
314 | CLASSROOM | 305 | 20 | Yes | 1144 | 26 | 26 | Univent | 9152 | 1.9996 | 1
315 | CLASSROOM | 1003 | 66 |  | 1170 | 26 | 26 | Univent | 9360 | 6.4295 | 2
316 | CLASSROOM | 363 | 24 |  | 783 | 17 | 17 | Univent | 6264 | 3.477 | 1
317 | CLASSROOM | 81 | 5 | Yes | 858 | 19 | 19 | Univent | 6864 | 0.70804 | 0
318 | CLASSROOM | 510 | 34 | Yes | 858 | 19 | 19 | Univent | 6864 | 4.458 | 2
319 | CLASSROOM | 463 | 30 |  | 858 | 19 | 19 | Univent | 6864 | 4.0472 | 2
320 | CLASSROOM | 0 | 0 | Yes | 858 | 19 | 19 | Univent | 6864 | 0 | 0
- | GYMNASIUM | 900 | 60 |  | 6370 | 144 | 60 | Rooftop Unit | 50960 | 1.0597 | 1
- | CAFETERIA | 3339 | 222 |  | 5160 | 117 | 117 | Rooftop Unit | 41280 | 4.8532 | 2
- | AUDITORIUM | 2146 | 143 |  | 7008 | 159 | 143 | Rooftop Unit | 56064 | 2.2967 | 1
- | KITCHEN HOOD | 8665 | 577 |  | 1584 | 36 | 36 | Rooftop Unit | 12672 | 41.0275 | 4
- | 1ST FLOOR BACK CORR. | 255 | 17 |  | 800 | 18 | 17 | Fan Coil Unit | 6400 | 2.3906 | 1
- | 1ST FLOOR CIRCLE HALL | 220 | 14 |  | 1246 | 28 | 14 | Fan Coil Unit | 9968 | 1.3242 | 1
- | 1ST FLOOR CORR INFRONT OF CAFÉ | 209 | 13 |  | 1008 | 22 | 13 | Fan Coil Unit | 8064 | 1.5551 | 1
- | 1ST FLOOR D WING OFFICE | 149 | 9 |  | 312 | 7 | 7 | Fan Coil Unit | 2496 | 3.5817 | 1
- | 1ST FLOOR ENTRANCE CORR. | 360 | 24 |  | 1053 | 23 | 23 | Fan Coil Unit | 8424 | 2.5641 | 1
- | 1ST FLOOR FRONT CORR. | 1074 | 71 |  | 1008 | 22 | 22 | Fan Coil Unit | 8064 | 7.9911 | 2
- | 1ST FLOOR FRONT HALL | 562 | 37 |  | 1540 | 35 | 35 | Fan Coil Unit | 12320 | 2.737 | 1
- | 1ST FLOOR OFFICES | 493 | 32 |  | 1888 | 42 | 32 | Fan Coil Unit | 15104 | 1.9584 | 1
- | 2ND / 1ST FLOOR D WING CORR | 380 | 25 |  | 1616 | 36 | 25 | Fan Coil Unit | 12928 | 1.7636 | 1
- | 2ND FLOOR C WING CLUSTER OFFICE | 1861 | 124 |  | 888 | 20 | 20 | Fan Coil Unit | 7104 | 15.7179 | 3
- | 2ND FLOOR C WING CONF. ROOM | 107 | 7 |  | 810 | 18 | 7 | Fan Coil Unit | 6480 | 0.99074 | 0
- | 2ND FLOOR CIRCLE HALL | 136 | 9 |  | 1246 | 28 | 9 | Fan Coil Unit | 9968 | 0.81862 | 0
- | 2ND FLOOR D WING SHOP | 97 | 6 |  | 408 | 9 | 6 | Fan Coil Unit | 3264 | 1.7831 | 1
- | 3RD FLOOR C WING CORR. | 660 | 44 |  | 1616 | 36 | 36 | Fan Coil Unit | 12928 | 3.0631 | 1
- | 3RD FLOOR CIRCLE HALL | 137 | 9 |  | 1246 | 28 | 9 | Fan Coil Unit | 9968 | 0.82464 | 0
- | 3RD FLOOR D WING CORR. | 501 | 33 |  | 1616 | 36 | 33 | Fan Coil Unit | 12928 | 2.3252 | 1
- | 3RD FLOOR D WING OFFICE | 167 | 11 |  | 312 | 7 | 7 | Fan Coil Unit | 2496 | 4.0144 | 2
- | 3RD FLOOR SHOP | 81 | 5 |  | 408 | 9 | 5 | Fan Coil Unit | 3264 | 1.489 | 1
- | BUILDING ENGINEER | 79 | 5 |  | 156 | 3 | 3 | Fan Coil Unit | 1248 | 3.7981 | 1
- | FACULTY BREAK ROOM | 188 | 12 |  | 648 | 14 | 12 | Fan Coil Unit | 5184 | 2.1759 | 1
- | GYM LOCKER ROOMS | 254 | 16 |  | 532 | 12 | 12 | Fan Coil Unit | 4256 | 3.5808 | 1
- | GYM TEACHER | 144 | 9 |  | 280 | 6 | 6 | Fan Coil Unit | 2240 | 3.8571 | 1
- | INSTRUMENT MUSIC | 0 | 0 | Yes | 1147 | 26 | 26 | Fan Coil Unit | 9176 | 0 | 0
- | IT Room | 268 | 17 |  | 396 | 9 | 9 | Fan Coil Unit | 3168 | 5.0758 | 2
- | KITCHEN OFFICE | 164 | 10 |  | 156 | 3 | 3 | Fan Coil Unit | 1248 | 7.8846 | 2
- | LIBRARY | 769 | 51 |  | 3864 | 87 | 51 | Fan Coil Unit | 30912 | 1.4926 | 1
- | LIBRARY STORAGE | 184 | 12 |  | 396 | 9 | 9 | Fan Coil Unit | 3168 | 3.4848 | 1
- | MUSIC PRACTICE B | 174 | 11 |  | 135 | 3 | 3 | Fan Coil Unit | 1080 | 9.6667 | 2
- | MUSIC PRACTICE C | 272 | 18 |  | 135 | 3 | 3 | Fan Coil Unit | 1080 | 15.1111 | 3
- | MUSIC PRATICE A | 126 | 8 |  | 135 | 3 | 3 | Fan Coil Unit | 1080 | 7 | 2
- | VOCAL MUSIC | 0 | 0 | Yes | 1221 | 27 | 27 | Fan Coil Unit | 9768 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-22 | [7 empty] | 0 | 0 | 0
School: | Martha Washington Elementary-Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Meehan | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 808 | 53 |  | 782 | 17 | 17 | House Fan | 6256 | 7.7494 | 2
102 | Classroom | 1564 | 104 |  | 920 | 20 | 20 | House Fan | 7360 | 12.75 | 3
103 | Classroom | 540 | 36 |  | 667 | 15 | 15 | House Fan | 5336 | 6.072 | 2
104 | Classroom | 250 | 16 |  | 667 | 15 | 15 | House Fan | 5336 | 2.8111 | 1
106 | Classroom | 529 | 35 |  | 667 | 15 | 15 | House Fan | 5336 | 5.9483 | 2
107 | Classroom | 370 | 24 |  | 690 | 15 | 15 | House Fan | 5520 | 4.0217 | 2
108 | Classroom | 279 | 18 |  | 667 | 15 | 15 | House Fan | 5336 | 3.1372 | 1
109 | Classroom | 525 | 35 |  | 667 | 15 | 15 | House Fan | 5336 | 5.9033 | 2
110 | - |  | 0 |  | 667 | 15 | 0 | Univent | 5336 | 0 | 0
111 | - |  | 0 | Yes | 667 | 15 | 15 | Univent | 5336 | 0 | 0
112 | - |  | 0 | Yes | 667 | 15 | 15 | Univent | 5336 | 0 | 0
113 | Classroom |  | 0 | Yes | 667 | 15 | 15 | Univent | 5336 | 0 | 0
201 | Classroom | 1290 | 86 |  | 667 | 15 | 15 | House Fan | 5336 | 14.5052 | 3
202 | Classroom | 990 | 66 |  | 667 | 15 | 15 | House Fan | 5336 | 11.1319 | 3
203 | Classroom | 425 | 28 |  | 759 | 17 | 17 | House Fan | 6072 | 4.1996 | 2
204 | Classroom | 442 | 29 |  | 713 | 16 | 16 | House Fan | 5704 | 4.6494 | 2
205 | Classroom | 345 | 23 |  | 621 | 14 | 14 | House Fan | 4968 | 4.1667 | 2
206 | Classroom | 829 | 55 |  | 667 | 15 | 15 | House Fan | 5336 | 9.3216 | 2
207 | Classroom | 479 | 31 |  | 660 | 15 | 15 | House Fan | 5280 | 5.4432 | 2
208 | Classroom | 489 | 32 |  | 667 | 15 | 15 | House Fan | 5336 | 5.4985 | 2
209 | Classroom | 394 | 26 |  | 667 | 15 | 15 | House Fan | 5336 | 4.4303 | 2
211 | - |  | 0 | Yes | 667 | 15 | 15 | Univent | 5336 | 0 | 0
212 | - |  | 0 | Yes | 667 | 15 | 15 | Univent | 5336 | 0 | 0
301 | Classroom | 551 | 36 |  | 667 | 15 | 15 | House Fan | 5336 | 6.1957 | 2
302 | Classroom | 850 | 56 |  | 667 | 15 | 15 | House Fan | 5336 | 9.5577 | 2
303 | Classroom | 453 | 30 |  | 667 | 15 | 15 | House Fan | 5336 | 5.0937 | 2
304 | Classroom | 236 | 15 |  | 1215 | 27 | 15 | House Fan | 9720 | 1.4568 | 1
305 | Classroom | 62 | 4 |  | 644 | 14 | 4 | House Fan | 5152 | 0.72205 | 0
306 | Classroom | 807 | 53 |  | 667 | 15 | 15 | House Fan | 5336 | 9.0742 | 2
307 | Classroom | 649 | 43 |  | 667 | 15 | 15 | House Fan | 5336 | 7.2976 | 2
308 | Classroom | 506 | 33 |  | 667 | 15 | 15 | House Fan | 5336 | 5.6897 | 2
309 | Classroom | 826 | 55 |  | 667 | 15 | 15 | House Fan | 5336 | 9.2879 | 2
310 | Classroom | 139 | 9 |  | 667 | 15 | 9 | House Fan | 5336 | 1.563 | 1
- | Main Office |  | 0 | Yes | 420 | 9 | 9 | Radiator | 3360 | 0 | 0
- | Principal's Office |  | 0 | Yes | 234 | 5 | 5 | Radiator | 1872 | 0 | 0
- | Nurse's Office |  | 0 | Yes | 180 | 4 | 4 | Radiator | 1440 | 0 | 0
- | BE's Office | 543 | 36 |  | 782 | 17 | 17 | House Fan | 6256 | 5.2078 | 2
- | Lunch Room A | 1542 | 102 |  | 792 | 18 | 18 | House Fan | 6336 | 14.6023 | 3
- | Lunch Room B | 1570 | 104 |  | 1540 | 35 | 35 | House Fan | 12320 | 7.6461 | 2
G2 | - |  | 0 | Yes | 667 | 15 | 15 | Univent | 5336 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [7 empty] | 0 | 0 | 0
School: | John H. Webster Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Devine Retest | [6 empty] | 0 | 0 | 0
School: | John H. Webster Elementary School- Little School House | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Webster Main Building | [8 empty] | 0 | 0 | 0
100 | Classroom | 1169 | 77 |  | 656 | 14 | 14 | Univent | 5248 | 13.3651 | 3
101 | Classroom | 593 | 39 |  | 1263 | 28 | 28 | Univent | 10104 | 3.5214 | 1
102 | Classroom | 435 | 29 |  | 721 | 16 | 16 | Univent | 5768 | 4.525 | 2
103 | Classroom | 1197 | 79 |  | 1062 | 24 | 24 | Univent | 8496 | 8.4534 | 2
104 | Classroom | 251 | 16 |  | 897 | 20 | 16 | Univent | 7176 | 2.0987 | 1
105 | Classroom | 310 | 20 |  | 531 | 12 | 12 | Univent | 4248 | 4.3785 | 2
106 | Classroom | 477 | 31 |  | 949 | 21 | 21 | Univent | 7592 | 3.7698 | 1
108 | Office | 49 | 3 |  | 226 | 5 | 3 | Air Handling Unit | 1808 | 1.6261 | 1
110 | Classroom | 358 | 23 |  | 1365 | 31 | 23 | Air Handling Unit | 10920 | 1.967 | 1
111 | Classroom | 312 | 20 |  | 1160 | 26 | 20 | Air Handling Unit | 9280 | 2.0172 | 1
112 | STS Classroom | 449 | 29 |  | 141 | 3 | 3 | Air Handling Unit | 1128 | 23.883 | 3
113 | Classroom | 280 | 18 |  | 1157 | 26 | 18 | Air Handling Unit | 9256 | 1.815 | 1
114 | Classroom | 290 | 19 |  | 1418 | 32 | 19 | Air Handling Unit | 11344 | 1.5339 | 1
200 | Classroom | 503 | 33 |  | 761 | 17 | 17 | Univent | 6088 | 4.9573 | 2
201 | Classroom | 369 | 24 |  | 597 | 13 | 13 | Univent | 4776 | 4.6357 | 2
202 | Classroom | 403 | 26 |  | 475 | 10 | 10 | Univent | 3800 | 6.3632 | 2
203 | Classroom | 444 | 29 |  | 772 | 17 | 17 | Univent | 6176 | 4.3135 | 2
204 | Classroom | 285 | 19 |  | 532 | 12 | 12 | Univent | 4256 | 4.0179 | 2
205 | Classroom | 329 | 21 |  | 823 | 18 | 18 | Univent | 6584 | 2.9982 | 1
206 | Classroom | 438 | 29 |  | 480 | 10 | 10 | Univent | 3840 | 6.8438 | 2
207 | Classroom | 108 | 7 | Yes | 648 | 14 | 14 | Univent | 5184 | 1.25 | 1
208 | Classroom | 352 | 23 |  | 540 | 12 | 12 | Univent | 4320 | 4.8889 | 2
209 | Classroom | 387 | 25 |  | 537 | 12 | 12 | Univent | 4296 | 5.405 | 2
300 | Classroom | 161 | 10 |  | 789 | 17 | 10 | Univent | 6312 | 1.5304 | 1
301 | Classroom | 313 | 20 |  | 729 | 16 | 16 | Univent | 5832 | 3.2202 | 1
302 | Classroom | 447 | 29 |  | 473 | 10 | 10 | Univent | 3784 | 7.0877 | 2
303 | Classroom | 137 | 9 | Yes | 690 | 15 | 15 | Univent | 5520 | 1.4891 | 1
304 | Classroom | 324 | 21 |  | 667 | 15 | 15 | Univent | 5336 | 3.6432 | 1
305 | Classroom | 321 | 21 |  | 794 | 18 | 18 | Univent | 6352 | 3.0321 | 1
306 | Classroom | 223 | 14 |  | 559 | 12 | 12 | Univent | 4472 | 2.9919 | 1
307 | Classroom | 171 | 11 |  | 790 | 17 | 11 | Univent | 6320 | 1.6234 | 1
308 | Classroom | 265 | 17 |  | 662 | 15 | 15 | Univent | 5296 | 3.0023 | 1
309 | Classroom | 360 | 24 |  | 567 | 12 | 12 | Univent | 4536 | 4.7619 | 2
311 | Classroom | 0 | 0 | Yes | 775 | 17 | 17 | Univent | 6200 | 0 | 0
312 | Classroom | 397 | 26 |  | 573 | 13 | 13 | Univent | 4584 | 5.1963 | 2
- | 2nd & 3rd corridors | 251 | 16 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Administration | 637 | 42 |  | 244 | 5 | 5 | Air Handling Unit | 1952 | 19.5799 | 3
- | Auditorium | 2708 | 180 |  | 3216 | 73 | 73 | Air Handling Unit | 25728 | 6.3153 | 2
- | Cafeteria | 2800 | 186 |  | 3216 | 73 | 73 | Air Handling Unit | 25728 | 6.5299 | 2
- | Child Care | 1704 | 113 |  | 1115 | 25 | 25 | Air Handling Unit | 8920 | 11.4619 | 3
- | Conference Office | 98 | 6 |  | 236 | 5 | 5 | Air Handling Unit | 1888 | 3.1144 | 1
- | Copy Room Office | 44 | 2 |  | 178 | 4 | 2 | Air Handling Unit | 1424 | 1.8539 | 1
- | Gym | 0 | 0 |  | 4403 | 100 | 0 | Air Handling Unit | 35224 | 0 | 0
- | IMC |  | 0 | Yes | 1363 | 30 | 30 | Univent | 10904 | 0 | 0
- | Kitchen Make Up | 1547 | 103 |  | 352 | 8 | 8 | Air Handling Unit | 2816 | 32.9616 | 4
- | Main Office | 201 | 13 |  | 244 | 5 | 5 | Air Handling Unit | 1952 | 6.1783 | 2
- | Mrs. Freeland's Office | 30 | 2 |  | 123 | 2 | 2 | Air Handling Unit | 984 | 1.8293 | 1
- | Music Room | 1406 | 93 |  | 696 | 15 | 15 | Air Handling Unit | 5568 | 15.1509 | 3
- | Nurse's Office | 87 | 5 |  | 412 | 9 | 5 | Air Handling Unit | 3296 | 1.5837 | 1
- | Principal's Office | 65 | 4 |  | 270 | 6 | 4 | Air Handling Unit | 2160 | 1.8056 | 1
- | Vice Principal's Office | 54 | 3 |  | 130 | 2 | 2 | Air Handling Unit | 1040 | 3.1154 | 1
Webster LSH | [8 empty] | 0 | 0 | 0
1 | Classroom | 441 | 29 |  | 971 | 22 | 22 | Blower Coil Unit | 7768 | 3.4063 | 1
2 | Classroom | 189 | 12 | Yes | 1012 | 23 | 23 | Blower Coil Unit | 8096 | 1.4007 | 1
3 | Classroom | 449 | 29 |  | 1016 | 23 | 23 | Blower Coil Unit | 8128 | 3.3145 | 1
4 | Classroom | 195 | 13 | Yes | 1017 | 23 | 23 | Blower Coil Unit | 8136 | 1.4381 | 1
5 | Classroom |  | 0 | Yes | 914 | 20 | 20 | Blower Coil Unit | 7312 | 0 | 0
6 | Classroom |  | 0 | Yes | 1040 | 23 | 23 | Blower Coil Unit | 8320 | 0 | 0
7 | Classroom |  | 0 | Yes | 1003 | 22 | 22 | Blower Coil Unit | 8024 | 0 | 0
8 | Classroom |  | 0 | Yes | 1024 | 23 | 23 | Blower Coil Unit | 8192 | 0 | 0
9 | Classroom | 162 | 10 | Yes | 975 | 22 | 22 | Blower Coil Unit | 7800 | 1.2462 | 1
10 | Classroom | 164 | 10 | Yes | 982 | 22 | 22 | Blower Coil Unit | 7856 | 1.2525 | 1
11 | Classroom | 188 | 12 | Yes | 1012 | 23 | 23 | Blower Coil Unit | 8096 | 1.3933 | 1
- | Student Toilets | 171 | 11 |  | 292 | 6 | 6 | Blower Coil Unit | 2336 | 4.3921 | 2
- | Custodial Closet |  | 0 |  | 58 | 1 | 0 | Fan Coil Unit | 464 | 0 | 0
- | Faculty Room |  | 0 |  | 156 | 3 | 0 | Fan Coil Unit | 1248 | 0 | 0
- | Multi Purpose Room | 2361 | 157 |  | 1714 | 38 | 38 | Blower Coil Unit | 13712 | 10.3311 | 3
- | Office Area | 409 | 27 |  | 274 | 6 | 6 | Blower Coil Unit | 2192 | 11.1953 | 3
- | Staff Toilets |  | 0 |  | 58 | 1 | 0 | Blower Coil Unit | 464 | 0 | 0
- | Storage & Closet |  | 0 |  | 200 | 4 | 0 | Blower Coil Unit | 1600 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-13 | [7 empty] | 0 | 0 | 0
School: | John Welsh Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine Brothers | Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 573 | 38 |  | 1122 | 25 | 25 | Univent | 8976 | 3.8302 | 1
102 | Classroom | 641 | 42 |  | 1030 | 23 | 23 | Univent | 8240 | 4.6675 | 2
103 | Classroom | 311 | 20 |  | 650 | 14 | 14 | Univent | 5200 | 3.5885 | 1
104 | Faculty Lounge | 774 | 51 |  | 750 | 17 | 17 | Univent | 6000 | 7.74 | 2
105 | Classroom | 307 | 20 |  | 586 | 13 | 13 | Univent | 4688 | 3.9292 | 1
106 | Classroom | 674 | 44 |  | 760 | 17 | 17 | Univent | 6080 | 6.6513 | 2
200 | Classroom | 301 | 20 |  | 825 | 18 | 18 | Univent | 6600 | 2.7364 | 1
201 | Classroom | 336 | 22 |  | 825 | 18 | 18 | Univent | 6600 | 3.0545 | 1
202 | Classroom | 333 | 22 |  | 825 | 18 | 18 | Univent | 6600 | 3.0273 | 1
203 | Classroom | 574 | 38 |  | 825 | 18 | 18 | Univent | 6600 | 5.2182 | 2
204 | Classroom | 356 | 23 |  | 825 | 18 | 18 | Univent | 6600 | 3.2364 | 1
205 | Classroom | 380 | 25 |  | 825 | 18 | 18 | Univent | 6600 | 3.4545 | 1
206 | Classroom | 405 | 27 |  | 825 | 18 | 18 | Univent | 6600 | 3.6818 | 1
209 | Classroom | 330 | 22 |  | 825 | 18 | 18 | Univent | 6600 | 3 | 1
210 | Library | 642 | 42 |  | 1218 | 27 | 27 | Univent | 9744 | 3.9532 | 1
211 | Classroom | 320 | 21 |  | 825 | 18 | 18 | Univent | 6600 | 2.9091 | 1
212 | Classroom | 610 | 40 |  | 825 | 18 | 18 | Univent | 6600 | 5.5455 | 2
300 | Classroom | 858 | 57 |  | 830 | 18 | 18 | Univent | 6640 | 7.753 | 2
301A | Classroom | 341 | 22 |  | 393 | 8 | 8 | Univent | 3144 | 6.5076 | 2
301B | Classroom |  | 0 | Yes | 393 | 8 | 8 | Univent | 3144 | 0 | 0
302 | Classroom | 887 | 59 |  | 830 | 18 | 18 | Univent | 6640 | 8.0151 | 2
303 | Classroom | 341 | 22 |  | 830 | 18 | 18 | Univent | 6640 | 3.0813 | 1
304 | Classroom | 790 | 52 |  | 830 | 18 | 18 | Univent | 6640 | 7.1386 | 2
305 | Classroom | 885 | 59 |  | 830 | 18 | 18 | Univent | 6640 | 7.997 | 2
306 | Classroom | 590 | 39 |  | 423 | 9 | 9 | Univent | 3384 | 10.461 | 3
308 | Classroom | 420 | 28 |  | 411 | 9 | 9 | Univent | 3288 | 7.6642 | 2
309 | Classroom | 454 | 30 |  | 830 | 18 | 18 | Univent | 6640 | 4.1024 | 2
310 | Classroom | 705 | 47 |  | 830 | 18 | 18 | Univent | 6640 | 6.3705 | 2
311 | Classroom | 890 | 59 |  | 830 | 18 | 18 | Univent | 6640 | 8.0422 | 2
312 | Classroom | 798 | 53 |  | 830 | 18 | 18 | Univent | 6640 | 7.2108 | 2
400 | Classroom | 346 | 23 |  | 825 | 18 | 18 | Univent | 6600 | 3.1455 | 1
401 | Classroom | 874 | 58 |  | 825 | 18 | 18 | Univent | 6600 | 7.9455 | 2
402 | Classroom | 801 | 53 |  | 825 | 18 | 18 | Univent | 6600 | 7.2818 | 2
403 | Classroom | 852 | 56 |  | 825 | 18 | 18 | Univent | 6600 | 7.7455 | 2
404 | Classroom | 368 | 24 |  | 825 | 18 | 18 | Univent | 6600 | 3.3455 | 1
405 | Classroom | 820 | 54 |  | 825 | 18 | 18 | Univent | 6600 | 7.4545 | 2
406 | Classroom | 328 | 21 |  | 425 | 9 | 9 | Univent | 3400 | 5.7882 | 2
408 | Classroom | 426 | 28 |  | 410 | 9 | 9 | Univent | 3280 | 7.7927 | 2
409 | Classroom | 417 | 27 |  | 825 | 18 | 18 | Univent | 6600 | 3.7909 | 1
410 | Classroom | 558 | 37 |  | 825 | 18 | 18 | Univent | 6600 | 5.0727 | 2
411 | Classroom | 897 | 59 |  | 825 | 18 | 18 | Univent | 6600 | 8.1545 | 2
412 | Classroom | 0 | 0 |  | 403 | 9 | 0 | Univent | 3224 | 0 | 0
412A | Classroom | 820 | 54 |  | 403 | 9 | 9 | Univent | 3224 | 15.2605 | 3
- | Main Office | 438 | 29 |  | 1038 | 23 | 23 | Univent | 8304 | 3.1647 | 1
- | Auditorium | 0 | 0 |  | 3868 | 87 | 0 | Air Handling Unit | 30944 | 0 | 0
- | Gym | 4931 | 328 |  | 3509 | 79 | 79 | Air Handling Unit | 28072 | 10.5393 | 3
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | New West Philadelphia High School | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
107 | Nurse Office |  | 0 |  | 264 | 6 | 0 | Air Handing Unit | 2112 | 0 | 0
107A | Nurse Exam Room |  | 0 |  | 149 | 3 | 0 | Air Handing Unit | 1192 | 0 | 0
107B | Nurse Suite |  | 0 |  | 100 | 2 | 0 | Air Handing Unit | 800 | 0 | 0
107C | Nurse Suite |  | 0 |  | 110 | 2 | 0 | Air Handing Unit | 880 | 0 | 0
101C | Maker Room |  | 0 | Yes | 1268 | 28 | 28 | Air Handing Unit | 10144 | 0 | 0
200 | - | 145 | 9 |  | 875 | 19 | 9 | Univent | 7000 | 1.2429 | 1
201 | Classroom | 190 | 12 |  | 539 | 12 | 12 | Univent | 4312 | 2.6438 | 1
202 | - | 308 | 20 |  | 895 | 20 | 20 | Univent | 7160 | 2.581 | 1
203 | - | 165 | 11 |  | 899 | 20 | 11 | Univent | 7192 | 1.3765 | 1
204 | - | 398 | 26 |  | 900 | 20 | 20 | Univent | 7200 | 3.3167 | 1
205 | - | 105 | 7 |  | 877 | 19 | 7 | Univent | 7016 | 0.89795 | 0
206 | - | 344 | 22 |  | 898 | 20 | 20 | Univent | 7184 | 2.8731 | 1
207 | - | 315 | 21 |  | 877 | 19 | 19 | Univent | 7016 | 2.6938 | 1
208 | - | 281 | 18 |  | 937 | 21 | 18 | Univent | 7496 | 2.2492 | 1
216 | - | 176 | 11 |  | 1330 | 30 | 11 | Univent | 10640 | 0.99248 | 0
300 | - | 210 | 14 |  | 878 | 19 | 14 | Univent | 7024 | 1.7938 | 1
301 | - | 0 | 0 |  | 544 | 12 | 0 | Univent | 4352 | 0 | 0
302 | - | 470 | 31 |  | 898 | 20 | 20 | Univent | 7184 | 3.9254 | 1
303 | - | 205 | 13 |  | 900 | 20 | 13 | Univent | 7200 | 1.7083 | 1
304 | - | 235 | 15 |  | 900 | 20 | 15 | Univent | 7200 | 1.9583 | 1
305 | - |  | 0 |  | 874 | 19 | 0 | Univent | 6992 | 0 | 0
306 | - | 190 | 12 |  | 896 | 20 | 12 | Univent | 7168 | 1.5904 | 1
307 | Classroom |  | 0 | Yes | 1387 | 31 | 31 | Univent | 11096 | 0 | 0
308 | - | 230 | 15 |  | 897 | 20 | 15 | Univent | 7176 | 1.9231 | 1
309 | Classroom |  | 0 | Yes | 1357 | 30 | 30 | Univent | 10856 | 0 | 0
310 | - | 115 | 7 |  | 898 | 20 | 7 | Univent | 7184 | 0.96047 | 0
311 | - |  | 0 |  | 900 | 20 | 0 | Univent | 7200 | 0 | 0
312 | - | 625 | 41 |  | 872 | 19 | 19 | Univent | 6976 | 5.3756 | 2
313 | - |  | 0 |  | 877 | 19 | 0 | Univent | 7016 | 0 | 0
315 | - | 425 | 28 |  | 876 | 19 | 19 | Univent | 7008 | 3.6387 | 1
316 | - | 190 | 12 |  | 399 | 9 | 9 | Univent | 3192 | 3.5714 | 1
317 | - | 205 | 13 |  | 902 | 20 | 13 | Univent | 7216 | 1.7045 | 1
318 | - | 365 | 24 |  | 1274 | 28 | 24 | Univent | 10192 | 2.1487 | 1
319 | - | 195 | 13 |  | 899 | 20 | 13 | Univent | 7192 | 1.6268 | 1
320 | - |  | 0 |  | 876 | 19 | 0 | Univent | 7008 | 0 | 0
321 | - | 425 | 28 |  | 894 | 20 | 20 | Univent | 7152 | 3.5654 | 1
Gymnasium | Gymnasium | 0 | 0 |  | 6370 | 144 | 0 | Univent | 50960 | 0 | 0
Gymnasium | Gymnasium | 0 | 0 | Yes | 10648 | 242 | 242 | Univent | 85184 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-13 | [7 empty] | 0 | 0 | 0
School: | Widener Memorial Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
2 | - | 1283 | 85 |  | 2800 | 63 | 63 | Carrier / Perimeter Heater | 22400 | 3.4366 | 1
3 | - | 500 | 33 |  | 1344 | 30 | 30 | Carrier / Perimeter Heater | 10752 | 2.7902 | 1
4 | - | 70 | 4 |  | 1332 | 30 | 4 | Carrier / Perimeter Heater | 10656 | 0.39414 | 0
5 | - | 146 | 9 |  | 527 | 11 | 9 | Carrier / Perimeter Heater | 4216 | 2.0778 | 1
6 | - | 38 | 2 |  | 744 | 16 | 2 | Carrier / Perimeter Heater | 5952 | 0.38306 | 0
7 | - | 70 | 4 |  | 912 | 20 | 4 | Carrier / Perimeter Heater | 7296 | 0.57566 | 0
8 | - | 317 | 21 |  | 460 | 10 | 10 | Carrier / Perimeter Heater | 3680 | 5.1685 | 2
9 | - | 311 | 20 |  | 480 | 10 | 10 | Carrier / Perimeter Heater | 3840 | 4.8594 | 2
10 | - | 291 | 19 |  | 504 | 11 | 11 | Carrier / Perimeter Heater | 4032 | 4.3304 | 2
11 | - | 290 | 19 |  | 504 | 11 | 11 | Carrier / Perimeter Heater | 4032 | 4.3155 | 2
12 | - | 292 | 19 |  | 744 | 16 | 16 | Carrier / Perimeter Heater | 5952 | 2.9435 | 1
13 | - | 210 | 14 |  | 759.5 | 17 | 14 | Carrier / Perimeter Heater | 6076 | 2.0737 | 1
14 | - | 244 | 16 |  | 759.5 | 17 | 16 | Carrier / Perimeter Heater | 6076 | 2.4095 | 1
15 | - | 224 | 14 |  | 759.5 | 17 | 14 | Carrier / Perimeter Heater | 6076 | 2.212 | 1
16 | - | 225 | 15 |  | 759.5 | 17 | 15 | Carrier / Perimeter Heater | 6076 | 2.2219 | 1
17 | - | 260 | 17 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 2.5675 | 1
18 | - | 304 | 20 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 3.002 | 1
19 | - | 0 | 0 | Yes | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 0 | 0
20 | - | 356 | 23 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 3.5155 | 1
21 | - | 271 | 18 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 2.6761 | 1
22 | - | 282 | 18 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 2.7847 | 1
23 | - | 275 | 18 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 2.7156 | 1
24 | - | 0 | 0 | Yes | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 0 | 0
25 | - | 192 | 12 |  | 1014 | 23 | 12 | Carrier / Perimeter Heater | 8112 | 1.4201 | 1
26 | - | 2008 | 133 |  | 891 | 20 | 20 | Air Handling Unit | 7128 | 16.9024 | 3
27 | - | 416 | 27 |  | 619.5 | 14 | 14 | Air Handling Unit | 4956 | 5.0363 | 2
28 | - | 416 | 27 |  | 925 | 21 | 21 | Air Handling Unit | 7400 | 3.373 | 1
31A | - | 0 | 0 | Yes | 190 | 4 | 4 | Carrier / Perimeter Heater | 1520 | 0 | 0
31B | Nurse's Office | 0 | 0 | Yes | 196 | 4 | 4 | Carrier / Perimeter Heater | 1568 | 0 | 0
32 | - | 0 | 0 |  | 272 | 6 | 0 | Carrier / Perimeter Heater | 2176 | 0 | 0
33 | - | 396 | 26 |  | 1271 | 28 | 26 | Carrier / Perimeter Heater | 10168 | 2.3367 | 1
34 | - | 622 | 41 |  | 1470 | 33 | 33 | Carrier / Perimeter Heater | 11760 | 3.1735 | 1
35A | - | 265 | 17 |  | 720 | 16 | 16 | Carrier / Perimeter Heater | 5760 | 2.7604 | 1
35B | - | 222 | 14 |  | 1107 | 25 | 14 | Carrier / Perimeter Heater | 8856 | 1.5041 | 1
35C | - | 0 | 0 | Yes | 364 | 8 | 8 | Carrier / Perimeter Heater | 2912 | 0 | 0
36 | - | 0 | 0 |  | 1288 | 29 | 0 | Carrier / Perimeter Heater | 10304 | 0 | 0
37 | - | 235 | 15 |  | 600 | 13 | 13 | Carrier / Perimeter Heater | 4800 | 2.9375 | 1
38 | - | 257 | 17 |  | 600 | 13 | 13 | Carrier / Perimeter Heater | 4800 | 3.2125 | 1
39 | - | 88 | 5 |  | 462 | 10 | 5 | Carrier / Perimeter Heater | 3696 | 1.4286 | 1
40 | - | 115 | 7 |  | 472 | 10 | 7 | Carrier / Perimeter Heater | 3776 | 1.8273 | 1
41 | - | 235 | 15 |  | 702 | 15 | 15 | Carrier / Perimeter Heater | 5616 | 2.5107 | 1
46 | Small Cafeteria | 182 | 12 |  | 1347 | 30 | 12 | Carrier / Perimeter Heater | 10776 | 1.0134 | 1
47 | - | 75 | 5 | Yes | 315 | 7 | 7 | Carrier / Perimeter Heater | 2520 | 1.7857 | 1
48 | - | 90 | 6 |  | 817 | 18 | 6 | Carrier / Perimeter Heater | 6536 | 0.82619 | 0
103 | - | 290 | 19 |  | 840 | 19 | 19 | Carrier / Perimeter Heater | 6720 | 2.5893 | 1
104 | - | 310 | 20 |  | 840 | 19 | 19 | Carrier / Perimeter Heater | 6720 | 2.7679 | 1
105 | - | 410 | 27 |  | 810 | 18 | 18 | Carrier / Perimeter Heater | 6480 | 3.7963 | 1
106 | - | 300 | 20 |  | 868 | 19 | 19 | Carrier / Perimeter Heater | 6944 | 2.5922 | 1
107 | - | 530 | 35 |  | 850 | 19 | 19 | Carrier / Perimeter Heater | 6800 | 4.6765 | 2
108 | - | 489 | 32 |  | 840 | 19 | 19 | Carrier / Perimeter Heater | 6720 | 4.3661 | 2
109 | - | 40 | 2 | Yes | 840 | 19 | 19 | Carrier / Perimeter Heater | 6720 | 0.35714 | 0
110 | - | 550 | 36 |  | 840 | 19 | 19 | Carrier / Perimeter Heater | 6720 | 4.9107 | 2
101 | - | 430 | 28 |  | 1271 | 28 | 28 | Carrier / Perimeter Heater | 10168 | 2.5374 | 1
102A | - | 124 | 8 |  | 140 | 3 | 3 | Carrier / Perimeter Heater | 1120 | 6.6429 | 2
102B | - | 165 | 11 |  | 140 | 3 | 3 | Carrier / Perimeter Heater | 1120 | 8.8393 | 2
111A | - | 98 | 6 |  | 140 | 3 | 3 | Carrier / Perimeter Heater | 1120 | 5.25 | 2
111B | - | 110 | 7 |  | 140 | 3 | 3 | Carrier / Perimeter Heater | 1120 | 5.8929 | 2
112 | - | 905 | 60 |  | 1271 | 28 | 28 | Carrier / Perimeter Heater | 10168 | 5.3403 | 2
- | Auditorium | 1042 | 69 |  | 4087 | 92 | 69 | Air Handling Unit | 32696 | 1.9122 | 1
- | Cafeteria | 918 | 61 |  | 2720 | 61 | 61 | Carrier / Perimeter Heater | 21760 | 2.5312 | 1
- | Computer Lab | 320 | 21 | Yes | 943 | 21 | 21 | Air Handling Unit | 7544 | 2.5451 | 1
- | Food Service "A & B" | 0 | 0 |  | 1320 | 30 | 0 | Carrier / Perimeter Heater | 10560 | 0 | 0
- | Game Room | 577 | 38 |  | 675 | 15 | 15 | Carrier / Perimeter Heater | 5400 | 6.4111 | 2
- | GYM | 174 | 11 |  | 3721 | 84 | 11 | Air Handling Unit | 29768 | 0.35071 | 0
- | Kitchen | 3011 | 200 |  | 1191 | 27 | 27 | Make-Up Air Unit | 9528 | 18.961 | 3
- | Music Room | 2765 | 184 |  | 2040 | 46 | 46 | Air Handling Unit | 16320 | 10.1654 | 3
- | Pool | 0 | 0 |  | 7467 | 169 | 0 | Air Handling Unit | 59736 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | Frances E. Willard Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Devine | Main Building Retest | [6 empty] | 0 | 0 | 0
School: | Willard Annex | [7 empty] | 0 | 0 | 0
Vendor: | EMCOR Fluidics | EMCOR Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
Willard Main Building | [8 empty] | 0 | 0 | 0
100A | OFFICE | 39 | 2 |  | 181 | 4 | 2 | Air Handling Unit | 1448 | 1.616 | 1
100B | OFFICE | 31 | 2 |  | 121 | 2 | 2 | Air Handling Unit | 968 | 1.9215 | 1
100C | OFFICE | 39 | 2 |  | 43 | 0 | 0 | Air Handling Unit | 344 | 6.8023 | 2
100D | OFFICE | 37 | 2 |  | 121 | 2 | 2 | Air Handling Unit | 968 | 2.2934 | 1
100E | OFFICE | 35 | 2 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 2.1875 | 1
100F | OFFICE | 51 | 3 |  | 345 | 7 | 3 | Air Handling Unit | 2760 | 1.1087 | 1
100G | Conference | 85 | 5 |  | 279 | 6 | 5 | Air Handling Unit | 2232 | 2.2849 | 1
100H | BREAK ROOM | 70 | 4 |  | 145 | 3 | 3 | Air Handling Unit | 1160 | 3.6207 | 1
100I | OFFICE | 76 | 5 |  | 210 | 4 | 4 | Air Handling Unit | 1680 | 2.7143 | 1
101 | Classroom | 310 | 20 |  | 984 | 22 | 20 | Univent and Air Handling Unit | 7872 | 2.3628 | 1
102 | Classroom | 304 | 20 |  | 1059 | 24 | 20 | Univent and Air Handling Unit | 8472 | 2.153 | 1
103 | Classroom | 321 | 21 |  | 889 | 20 | 20 | Univent and Air Handling Unit | 7112 | 2.7081 | 1
104 | Classroom | 282 | 18 |  | 1086 | 24 | 18 | Univent and Air Handling Unit | 8688 | 1.9475 | 1
105 | Classroom | 295 | 19 |  | 677 | 15 | 15 | Univent and Air Handling Unit | 5416 | 3.2681 | 1
106 | Classroom | 331 | 22 |  | 800 | 18 | 18 | Univent and Air Handling Unit | 6400 | 3.1031 | 1
107 | Nurse OFFICE | 35 | 2 |  | 277 | 6 | 2 | Fan Coil | 2216 | 0.94765 | 0
107A | OFFICE | 45 | 3 |  | 161 | 3 | 3 | Fan Coil | 1288 | 2.0963 | 1
107C | OFFICE | 14 | 0 |  | 150 | 3 | 0 | Air Handling Unit | 1200 | 0.7 | 0
107D | OFFICE | 26 | 1 |  | 103 | 2 | 1 | Air Handling Unit | 824 | 1.8932 | 1
107G | COMPUTER LAB | 298 | 19 |  | 1033 | 23 | 19 | Univent | 8264 | 2.1636 | 1
109 | Classroom | 282 | 18 |  | 802 | 18 | 18 | Univent and Air Handling Unit | 6416 | 2.6372 | 1
110 | Classroom | 282 | 18 |  | 818 | 18 | 18 | Univent and Air Handling Unit | 6544 | 2.5856 | 1
111 | Classroom | 295 | 19 |  | 818 | 18 | 18 | Univent and Air Handling Unit | 6544 | 2.7048 | 1
112 | Classroom | 306 | 20 |  | 813 | 18 | 18 | Univent and Air Handling Unit | 6504 | 2.8229 | 1
113 | Classroom | 305 | 20 |  | 813 | 18 | 18 | Univent and Air Handling Unit | 6504 | 2.8137 | 1
114 | Classroom | 280 | 18 |  | 815 | 18 | 18 | Univent and Air Handling Unit | 6520 | 2.5767 | 1
115 | Classroom | 293 | 19 |  | 815 | 18 | 18 | Univent and Air Handling Unit | 6520 | 2.6963 | 1
116 | Classroom | 302 | 20 |  | 813 | 18 | 18 | Univent and Air Handling Unit | 6504 | 2.786 | 1
117 | Classroom | 295 | 19 |  | 813 | 18 | 18 | Univent and Air Handling Unit | 6504 | 2.7214 | 1
121 | Classroom | 381 | 25 |  | 1059 | 24 | 24 | Univent and Air Handling Unit | 8472 | 2.6983 | 1
122 | Music Room | 328 | 21 |  | 1189 | 27 | 21 | Univent | 9512 | 2.069 | 1
123 | Classroom | 392 | 26 |  | 1061 | 24 | 24 | Univent and Air Handling Unit | 8488 | 2.771 | 1
126 | Staff Lounge | 397 | 26 |  | 419 | 9 | 9 | Univent and Air Handling Unit | 3352 | 7.1062 | 2
128 | Workroom | 154 | 10 |  | 285 | 6 | 6 | Air Handling Unit | 2280 | 4.0526 | 2
132 | BE Office | 78 | 5 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 4.3333 | 2
200E | IMC | 60 | 4 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 5.625 | 2
200F | CONF ROOM | 325 | 21 |  | 352 | 8 | 8 | Univent | 2816 | 6.9247 | 2
201 | Classsroom | 425 | 28 |  | 814 | 18 | 18 | Univent and Air Handling Unit | 6512 | 3.9158 | 1
202 | Classsroom | 530 | 35 |  | 814 | 18 | 18 | Univent and Air Handling Unit | 6512 | 4.8833 | 2
203 | Classsroom | 394 | 26 |  | 814 | 18 | 18 | Univent and Air Handling Unit | 6512 | 3.6302 | 1
204 | Classsroom | 517 | 34 |  | 814 | 18 | 18 | Univent and Air Handling Unit | 6512 | 4.7635 | 2
205 | Classsroom | 432 | 28 |  | 810 | 18 | 18 | Univent and Air Handling Unit | 6480 | 4 | 1
206 | Classsroom | 407 | 27 |  | 812 | 18 | 18 | Univent and Air Handling Unit | 6496 | 3.7592 | 1
207 | Classsroom | 368 | 24 |  | 685 | 15 | 15 | Univent and Air Handling Unit | 5480 | 4.0292 | 2
208 | ART | 479 | 31 |  | 1059 | 24 | 24 | Univent | 8472 | 3.3924 | 1
209 | Classsroom | 379 | 25 |  | 807 | 18 | 18 | Univent and Air Handling Unit | 6456 | 3.5223 | 1
210 | Classsroom | 382 | 25 |  | 820 | 18 | 18 | Univent and Air Handling Unit | 6560 | 3.4939 | 1
211 | Classsroom | 389 | 25 |  | 821 | 18 | 18 | Univent and Air Handling Unit | 6568 | 3.5536 | 1
212 | Classsroom | 375 | 25 |  | 814 | 18 | 18 | Univent and Air Handling Unit | 6512 | 3.4552 | 1
213 | Classsroom | 392 | 26 |  | 814 | 18 | 18 | Univent and Air Handling Unit | 6512 | 3.6118 | 1
214 | Classsroom | 382 | 25 |  | 811 | 18 | 18 | Univent and Air Handling Unit | 6488 | 3.5327 | 1
215 | Classsroom | 420 | 28 |  | 811 | 18 | 18 | Univent and Air Handling Unit | 6488 | 3.8841 | 1
216 | Classsroom | 301 | 20 |  | 811 | 18 | 18 | Univent and Air Handling Unit | 6488 | 2.7836 | 1
217 | Classsroom | 411 | 27 |  | 811 | 18 | 18 | Univent and Air Handling Unit | 6488 | 3.8009 | 1
221 | Classroom | 301 | 20 |  | 658 | 14 | 14 | Univent | 5264 | 3.4309 | 1
223 | Classroom | 357 | 23 |  | 887 | 20 | 20 | Univent and Air Handling Unit | 7096 | 3.0186 | 1
224 | Classroom | 585 | 39 |  | 1410 | 32 | 32 | Univent and Air Handling Unit | 11280 | 3.1117 | 1
225 | Classroom | 175 | 11 |  | 1267 | 28 | 11 | Univent and Air Handling Unit | 10136 | 1.0359 | 1
- | Auditorium | 3411 | 227 |  | 2755 | 62 | 62 | Air Handling Unit | 22040 | 9.2858 | 2
- | Cafeteria | 2559 | 170 |  | 5041 | 114 | 114 | Air Handling Unit | 40328 | 3.8073 | 1
- | Gym | 2627 | 175 |  | 5960 | 135 | 135 | Air Handling Unit | 47680 | 3.3058 | 1
- | LIBRARY | 514 | 34 |  | 2639 | 59 | 34 | Air Handling Unit | 21112 | 1.4608 | 1
- | Lobby | 1166 | 77 |  | 3402 | 77 | 77 | Air Handling Unit | 27216 | 2.5705 | 1
- | Main Office | 236 | 15 |  | 1165 | 26 | 15 | Air Handling Unit | 9320 | 1.5193 | 1
Willard Annex | [8 empty] | 0 | 0 | 0
#1 | Classroom | 334 | 22 |  | 828 | 18 | 18 | Rooftop Unit | 6624 | 3.0254 | 1
#2 | Classroom | 534 | 35 |  | 828 | 18 | 18 | Rooftop Unit | 6624 | 4.837 | 2
#3 | Classroom | 667 | 44 |  | 828 | 18 | 18 | Rooftop Unit | 6624 | 6.0417 | 2
#4 | Classroom | 595 | 39 |  | 828 | 18 | 18 | Rooftop Unit | 6624 | 5.3895 | 2
#5 | Classroom | 453 | 30 |  | 828 | 18 | 18 | Rooftop Unit | 6624 | 4.1033 | 2
#6 | Classroom | 1118 | 74 |  | 828 | 18 | 18 | Rooftop Unit | 6624 | 10.1268 | 3
- | Admin Desk/Office | 402 | 26 |  | 180 | 4 | 4 | Rooftop Unit | 1440 | 16.75 | 3
- | Entrance Hallway | 93 | 6 |  | N/A | 0 | 0 | Rooftop Unit | #VALUE! | #VALUE! | #VALUE!
- | Kitchen | 123 | 8 |  | 180 | 4 | 4 | Rooftop Unit | 1440 | 5.125 | 2
- | Office Space | 29 | 1 |  | 200 | 4 | 1 | Rooftop Unit | 1600 | 1.0875 | 1
- | Play Area | 2452 | 163 |  | 1228 | 27 | 27 | Rooftop Unit | 9824 | 14.9756 | 3
- | Principals Office | 257 | 17 |  | 120 | 2 | 2 | Rooftop Unit | 960 | 16.0625 | 3
- | BE Office | 362 | 24 |  | 195 | 4 | 4 | Rooftop Unit | 1560 | 13.9231 | 3
- | Health/Teachers Lounge | 0 | 0 |  | 240 | 5 | 0 | Univent | 1920 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | Woodrow Wilson Middle School | [7 empty] | 0 | 0 | 0
Vendor: | Capital | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Classroom | 693 | 46 |  | 1080 | 24 | 24 | Air Handling Unit | 8640 | 4.8125 | 2
102 | Classroom | 429 | 28 |  | 853 | 19 | 19 | Air Handling Unit | 6824 | 3.772 | 1
103 | Classroom | 962 | 64 |  | 672 | 15 | 15 | Air Handling Unit | 5376 | 10.7366 | 3
104 | Room |  | 0 |  | 616 | 14 | 0 | Air Handling Unit | 4928 | 0 | 0
105 | Classroom | 540 | 36 |  | 1038 | 23 | 23 | Air Handling Unit | 8304 | 3.9017 | 1
107 | Classroom | 882 | 58 |  | 968 | 22 | 22 | Air Handling Unit | 7744 | 6.8337 | 2
108 | Room |  | 0 |  | 352 | 8 | 0 | Air Handling Unit | 2816 | 0 | 0
109 | Classroom | 506 | 33 |  | 374 | 8 | 8 | Air Handling Unit | 2992 | 10.1471 | 3
110 | Room |  | 0 |  | 660 | 15 | 0 | Air Handling Unit | 5280 | 0 | 0
111 | Classroom | 277 | 18 |  | 812 | 18 | 18 | Air Handling Unit | 6496 | 2.5585 | 1
112 | Classroom | 271 | 18 |  | 954 | 21 | 18 | Air Handling Unit | 7632 | 2.1305 | 1
116 | Classroom | 143 | 9 |  | 697 | 15 | 9 | Air Handling Unit | 5576 | 1.5387 | 1
117 | Classroom | 191 | 12 |  | 697 | 15 | 12 | Air Handling Unit | 5576 | 2.0552 | 1
118 | Classroom | 146 | 9 |  | 697 | 15 | 9 | Air Handling Unit | 5576 | 1.571 | 1
119 | Classroom | 98 | 6 |  | 349 | 7 | 6 | Air Handling Unit | 2792 | 2.106 | 1
201 | Classroom | 0 | 0 | Yes | 727 | 16 | 16 | Air Handling Unit | 5816 | 0 | 0
202 | Classroom | 338 | 22 |  | 687 | 15 | 15 | Air Handling Unit | 5496 | 3.69 | 1
203 | Classroom | 451 | 30 |  | 726 | 16 | 16 | Air Handling Unit | 5808 | 4.6591 | 2
204 | Office |  | 0 | Yes | 160 | 3 | 3 | Air Handling Unit | 1280 | 0 | 0
205 | Classroom | 311 | 20 |  | 348 | 7 | 7 | Air Handling Unit | 2784 | 6.7026 | 2
206 | Classroom | 452 | 30 |  | 324 | 7 | 7 | Air Handling Unit | 2592 | 10.463 | 3
207 | Room |  | 0 |  | 308 | 7 | 0 | Air Handling Unit | 2464 | 0 | 0
208-C | Main Office |  | 0 |  | 572 | 13 | 0 | Air Handling Unit | 4576 | 0 | 0
209 | Classroom | 765 | 51 |  | 901 | 20 | 20 | Air Handling Unit | 7208 | 6.3679 | 2
210 | Classroom | 394 | 26 |  | 1034 | 23 | 23 | Air Handling Unit | 8272 | 2.8578 | 1
211 | Classroom | 356 | 23 |  | 849 | 19 | 19 | Air Handling Unit | 6792 | 3.1449 | 1
212 | Classroom | 318 | 21 |  | 867 | 19 | 19 | Air Handling Unit | 6936 | 2.7509 | 1
213 | Classroom | 213 | 14 |  | 687 | 15 | 14 | Air Handling Unit | 5496 | 2.3253 | 1
214 | Classroom | 596 | 39 |  | 727 | 16 | 16 | Air Handling Unit | 5816 | 6.1486 | 2
215 | Classroom | 1059 | 70 |  | 668 | 15 | 15 | Air Handling Unit | 5344 | 11.89 | 3
216 | Classroom | 1311 | 87 |  | 791 | 17 | 17 | Air Handling Unit | 6328 | 12.4305 | 3
217 | Classroom | 1097 | 73 |  | 682 | 15 | 15 | Air Handling Unit | 5456 | 12.0638 | 3
218 | Classroom | 810 | 54 |  | 702 | 15 | 15 | Air Handling Unit | 5616 | 8.6538 | 2
219 | Classroom | 1352 | 90 |  | 700 | 15 | 15 | Air Handling Unit | 5600 | 14.4857 | 3
220 | Classroom | 1207 | 80 |  | 682 | 15 | 15 | Air Handling Unit | 5456 | 13.2735 | 3
221 | Classroom | 897 | 59 |  | 791 | 17 | 17 | Air Handling Unit | 6328 | 8.5051 | 2
222 | Classroom | 608 | 40 |  | 668 | 15 | 15 | Air Handling Unit | 5344 | 6.8263 | 2
223 | Classroom | 305 | 20 |  | 347 | 7 | 7 | Air Handling Unit | 2776 | 6.5922 | 2
224 | Room |  | 0 |  | 308 | 7 | 0 | Air Handling Unit | 2464 | 0 | 0
226 | Classroom | 86 | 5 |  | 216 | 4 | 4 | Air Handling Unit | 1728 | 2.9861 | 1
227 | Classroom | 163 | 10 |  | 347 | 7 | 7 | Air Handling Unit | 2776 | 3.5231 | 1
228 | Classroom | 208 | 13 |  | 694 | 15 | 13 | Air Handling Unit | 5552 | 2.2478 | 1
245 | Room |  | 0 | Yes | 87 | 1 | 1 | Air Handling Unit | 696 | 0 | 0
246 | Room |  | 0 | Yes | 82 | 1 | 1 | Air Handling Unit | 656 | 0 | 0
247 | Room |  | 0 | Yes | 110 | 2 | 2 | Air Handling Unit | 880 | 0 | 0
301 | Classroom | 813 | 54 |  | 727 | 16 | 16 | Air Handling Unit | 5816 | 8.3872 | 2
302 | Classroom | 439 | 29 |  | 684 | 15 | 15 | Air Handling Unit | 5472 | 4.8136 | 2
303 | Classroom | 605 | 40 |  | 697 | 15 | 15 | Air Handling Unit | 5576 | 6.51 | 2
304 | Classroom | 552 | 36 |  | 972 | 22 | 22 | Air Handling Unit | 7776 | 4.2593 | 2
305 | Classroom | 518 | 34 |  | 914 | 20 | 20 | Air Handling Unit | 7312 | 4.2505 | 2
306 | Classroom | 497 | 33 |  | 898 | 20 | 20 | Air Handling Unit | 7184 | 4.1509 | 2
307 | Classroom | 781 | 52 |  | 965 | 21 | 21 | Air Handling Unit | 7720 | 6.0699 | 2
308 | Classroom | 466 | 31 |  | 833 | 18 | 18 | Air Handling Unit | 6664 | 4.1957 | 2
309 | Classroom | 735 | 49 |  | 894 | 20 | 20 | Air Handling Unit | 7152 | 6.1661 | 2
309-A | Room |  | 0 |  | 220 | 5 | 0 | Air Handling Unit | 1760 | 0 | 0
310 | Classroom | 765 | 51 |  | 924 | 21 | 21 | Air Handling Unit | 7392 | 6.2094 | 2
311 | Classroom | 1322 | 88 |  | 958 | 21 | 21 | Air Handling Unit | 7664 | 10.3497 | 3
312 | Classroom | 660 | 44 |  | 728 | 16 | 16 | Air Handling Unit | 5824 | 6.7995 | 2
313 | Classroom | 403 | 26 |  | 313 | 7 | 7 | Air Handling Unit | 2504 | 9.6565 | 2
2021-11-09 | Classroom | 1020 | 68 |  | 314 | 7 | 7 | Air Handling Unit | 2512 | 24.3631 | 4
315 | Classroom | 1082 | 72 |  | 668 | 15 | 15 | Air Handling Unit | 5344 | 12.1482 | 3
316 | Classroom | 1750 | 116 |  | 791 | 17 | 17 | Air Handling Unit | 6328 | 16.5929 | 3
317 | Classroom | 2057 | 137 |  | 685 | 15 | 15 | Air Handling Unit | 5480 | 22.5219 | 3
318 | Classroom | 1824 | 121 |  | 699 | 15 | 15 | Air Handling Unit | 5592 | 19.5708 | 3
319 | Classroom | 1263 | 84 |  | 699 | 15 | 15 | Air Handling Unit | 5592 | 13.5515 | 3
320 | Classroom | 642 | 42 |  | 684 | 15 | 15 | Air Handling Unit | 5472 | 7.0395 | 2
321 | Classroom | 658 | 43 |  | 791 | 17 | 17 | Air Handling Unit | 6328 | 6.2389 | 2
322 | Classroom | 508 | 33 |  | 668 | 15 | 15 | Air Handling Unit | 5344 | 5.7036 | 2
323 | Classroom | 282 | 18 |  | 347 | 7 | 7 | Air Handling Unit | 2776 | 6.0951 | 2
324 | Classroom | 127 | 8 |  | 694 | 15 | 8 | Air Handling Unit | 5552 | 1.3725 | 1
327 | Room |  | 0 |  | 264 | 6 | 0 | Air Handling Unit | 2112 | 0 | 0
328 | Classroom | 107 | 7 |  | 694 | 15 | 7 | Air Handling Unit | 5552 | 1.1563 | 1
401 | Room |  | 0 |  | 264 | 6 | 0 | Rooftop Unit | 2112 | 0 | 0
401A | Room |  | 0 |  | 572 | 13 | 0 | Rooftop Unit | 4576 | 0 | 0
402 | Room |  | 0 |  | 836 | 19 | 0 | Rooftop Unit | 6688 | 0 | 0
403 | Room |  | 0 |  | 1056 | 24 | 0 | Rooftop Unit | 8448 | 0 | 0
404 | Room |  | 0 |  | 1188 | 27 | 0 | Rooftop Unit | 9504 | 0 | 0
406 | Room |  | 0 |  | 44 | 1 | 0 | Rooftop Unit | 352 | 0 | 0
407 | Room |  | 0 |  | 44 | 1 | 0 | Rooftop Unit | 352 | 0 | 0
408 | Room |  | 0 |  | 44 | 1 | 0 | Rooftop Unit | 352 | 0 | 0
409 | Room |  | 0 |  | 132 | 3 | 0 | Rooftop Unit | 1056 | 0 | 0
410 | Counselor's Office |  | 0 | Yes | 165 | 3 | 3 | Rooftop Unit | 1320 | 0 | 0
- | Auditorium |  | 0 |  | 3740 | 85 | 0 | Air Handling Unit | 29920 | 0 | 0
- | Gym 1 |  | 0 |  | 2816 | 64 | 0 | Air Handling Unit | 22528 | 0 | 0
- | Gym 2 |  | 0 |  | 2816 | 64 | 0 | Air Handling Unit | 22528 | 0 | 0
- | Lunchroom 1 |  | 0 |  | 2640 | 60 | 0 | Air Handling Unit | 21120 | 0 | 0
- | Lunchroom 2 |  | 0 |  | 2596 | 59 | 0 | Air Handling Unit | 20768 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-29 | [7 empty] | 0 | 0 | 0
School: | Wister Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Mastery Charter Property Management | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Classroom | 307 | 20 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
101 | Classroom | 319 | 21 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
103 | Classroom | 148 | 9 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
106 | Lounge | 202 | 13 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
107A | Main Office | 0 | 0 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
108 | Classroom | 316 | 21 |  | 1134 | 25 | 21 | Unit Ventilator | 9072 | 2.0899 | 1
109 | Classroom | 313 | 20 |  | 1094 | 24 | 20 | Unit Ventilator | 8752 | 2.1458 | 1
110 | Storage | 215 | 14 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
111 | Classroom | 339 | 22 |  | 1414 | 32 | 22 | Unit Ventilator | 11312 | 1.7981 | 1
200 | Classroom | 309 | 20 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
201 | Office | 162 | 10 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
202 | Classroom | 138 | 9 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
203 | Classroom | 311 | 20 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
204 | Classroom | 271 | 18 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
205 | Classroom | 144 | 9 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
206 | Classroom | 304 | 20 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
207 | Classroom | 304 | 20 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
208 | Classroom | 308 | 20 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
209C | Classroom | 337 | 22 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
210 | Classroom | 319 | 21 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
211 | Classroom | 302 | 20 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
212 | Classroom | 313 | 20 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
213 | Classroom | 331 | 22 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
214 | Classroom | 349 | 23 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
300 | Classroom | 299 | 19 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
301 | Office | 129 | 8 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
302 | Classroom | 153 | 10 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
303 | Classroom | 308 | 20 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
304 | Classroom | 330 | 22 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
305 | Classroom | 332 | 22 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
306 | Classroom | 311 | 20 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
307 | Classroom | 312 | 20 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
- | Auditorium | 2036 | 135 |  |  | 0 | 0 | AHU | 0 | 0 | 0
- | Gym | 1544 | 102 |  |  | 0 | 0 | AHU | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-03-17 | [7 empty] | 0 | 0 | 0
School: | Sustainability Workshop School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | [7 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
101 | Corridor | 7 | 0 |  | 533 | 12 | 0 | VAV | 4264 | 0.098499 | 0
102 | Closet | 6 | 0 |  | 45 | 1 | 0 | VAV | 360 | 1 | 0
105 | Nurses Office / Classroom |  | 0 |  | 150 | 3 | 0 | HU | 1200 | 0 | 0
106 | Woodshop | 43 | 2 |  | 1003 | 22 | 2 | HU | 8024 | 0.32154 | 0
110 | Classroom | 23 | 1 |  | 884 | 20 | 1 | VAV | 7072 | 0.19514 | 0
111 | Auto Service | 0 | 0 |  | 1761 | 40 | 0 | HU and Univent | 14088 | 0 | 0
111 | Classroom |  | 0 |  | 756 | 17 | 0 | Univent | 6048 | 0 | 0
112 | Training Classroom | 0 | 0 |  | 459 | 10 | 0 | HU and Univent | 3672 | 0 | 0
114 | Tool Storage | 0 | 0 |  | 450 | 10 | 0 | HU and Univent | 3600 | 0 | 0
117 | Body Shop | 0 | 0 |  | 2944 | 66 | 0 | HU | 23552 | 0 | 0
121 | Classroom |  | 0 |  | 729 | 16 | 0 | Univent | 5832 | 0 | 0
200 | Corridor | 33 | 2 |  | 1868 | 42 | 2 | VAV | 14944 | 0.13249 | 0
201 | Classroom | 42 | 2 |  | 740 | 16 | 2 | VAV | 5920 | 0.42568 | 0
206 | Main Office | 7 | 0 |  | 234 | 5 | 0 | VAV | 1872 | 0.22436 | 0
207 | Office | 6 | 0 |  | 192 | 4 | 0 | VAV | 1536 | 0.23438 | 0
208 | Principle Office | 5 | 0 |  | 80 | 1 | 0 | VAV | 640 | 0.46875 | 0
209 | Copy Room | 12 | 0 |  | 132 | 3 | 0 | VAV | 1056 | 0.68182 | 0
210 | Classroom | 25 | 1 |  | 748 | 17 | 1 | VAV | 5984 | 0.25067 | 0
210-C | Counselors office in front of classroom 210 | 2 | 0 |  | NA | 0 | 0 | VAV | #VALUE! | #VALUE! | #VALUE!
212 | Mechanical room |  | 0 |  | 620 | 14 | 0 | AHU | 4960 | 0 | 0
212 | Classroom | 366 | 24 |  | 720 | 16 | 16 | VAV | 5760 | 3.8125 | 1
213 | Classroom | 1829 | 121 |  | 691 | 15 | 15 | VAV | 5528 | 19.8517 | 3
214 | Classroom | 837 | 55 |  | 761 | 17 | 17 | VAV | 6088 | 8.249 | 2
215 | Classroom | 839 | 55 |  | 961 | 21 | 21 | VAV | 7688 | 6.5479 | 2
215A | Classroom | 96 | 6 |  | NA | 0 | 0 | VAV | #VALUE! | #VALUE! | #VALUE!
216 | Classroom | 655 | 43 |  | 1012 | 23 | 23 | VAV | 8096 | 4.8542 | 2
219 | Corridor Bathroom | 40 | 2 |  | 48 | 1 | 1 | VAV | 384 | 6.25 | 2
- | Automotive Classroom | 0 | 0 |  | NA | 0 | 0 | HU and Univent | #VALUE! | #VALUE! | #VALUE!
- | Body Shop Classroom | 0 | 0 |  | NA | 0 | 0 | Univent | #VALUE! | #VALUE! | #VALUE!
- | Cafeteria Bathroom | 41 | 2 |  | 49 | 1 | 1 | VAV | 392 | 6.2755 | 2
- | Cafeteria | 402 | 26 |  | 2550 | 57 | 26 | RTU | 20400 | 1.1824 | 1
- | Computer Lab | 60 | 4 |  | 312 | 7 | 4 | HU | 2496 | 1.4423 | 1
- | Kitchen | 0 | 0 |  | 504 | 11 | 0 | MUA | 4032 | 0 | 0
- | Mr. Boyd Office | 185 | 12 |  | 152 | 3 | 3 | VAV and RETURN DUCT | 1216 | 9.1283 | 2
- | Mr. Tobias Office | 185 | 12 |  | 80 | 1 | 1 | VAV | 640 | 17.3438 | 3
- | Mrs. Walker Office | 138 | 9 |  | 80 | 1 | 1 | VAV | 640 | 12.9375 | 3
- | Ms. Phoebe Office | 188 | 12 |  | 91 | 2 | 2 | VAV | 728 | 15.4945 | 3
- | Nurse Room | 0 | 0 |  | NA | 0 | 0 | HU and Univent | #VALUE! | #VALUE! | #VALUE!
- | Storage / Office | 15 | 1 |  | 120 | 2 | 1 | RTU | 960 | 0.9375 | 0
- | Woodshop Office | 43 | 2 |  | NA | 0 | 0 | HU | #VALUE! | #VALUE! | #VALUE!
- | Woodshop Saw | 24 | 1 |  | NA | 0 | 0 | HU | #VALUE! | #VALUE! | #VALUE!
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [7 empty] | 0 | 0 | 0
School: | Richard R. Wright Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Goldner | Goldner Retest | [6 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
100 | Art Room | 280 | 18 | Yes | 1400 | 31 | 31 | Unit Ventilator | 11200 | 1.5 | 1
108-A | 1st Floor Gymnasium Office | 5 | 0 |  | 100 | 2 | 0 | Air Handling Unit | 800 | 0.375 | 0
112-A | 1st Floor Music Practice | 10 | 0 |  | 100 | 2 | 0 | Air Handling Unit | 800 | 0.75 | 0
112-B | 1st Floor Music Practice | 19 | 1 |  | 100 | 2 | 1 | Air Handling Unit | 800 | 1.425 | 1
114 | Classroom | 334 | 22 | Yes | 1360 | 30 | 30 | Unit Ventilator | 10880 | 1.8419 | 1
115 | Classroom | 358 | 23 | Yes | 1360 | 30 | 30 | Unit Ventilator | 10880 | 1.9743 | 1
118 | Nurse area | 0 | 0 | Yes | 378 | 8 | 8 | Unit Ventilator | 3024 | 0 | 0
119 | Nurse area | 0 | 0 | Yes | 216 | 4 | 4 | Unit Ventilator | 1728 | 0 | 0
120 | Classroom | 273 | 18 | Yes | 1360 | 30 | 30 | Unit Ventilator | 10880 | 1.5055 | 1
121 | Classroom | 435 | 29 |  | 1360 | 30 | 29 | Unit Ventilator | 10880 | 2.3989 | 1
122 | Classroom | 273 | 18 | Yes | 1360 | 30 | 30 | Unit Ventilator | 10880 | 1.5055 | 1
201 | Classroom | 342 | 22 | Yes | 1610 | 36 | 36 | Unit Ventilator | 12880 | 1.5932 | 1
202 | Classroom | 634 | 42 |  | 1702 | 38 | 38 | Unit Ventilator | 13616 | 2.7938 | 1
203 | Classroom | 349 | 23 | Yes | 1120 | 25 | 25 | Unit Ventilator | 8960 | 2.3371 | 1
204 | Classroom | 358 | 23 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
205 | Classroom | 482 | 32 |  | 870 | 19 | 19 | Unit Ventilator | 6960 | 4.1552 | 2
206 | Classroom | 499 | 33 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 4.609 | 2
207 | Classroom | 460 | 30 |  | 870 | 19 | 19 | Unit Ventilator | 6960 | 3.9655 | 1
208 | Classroom | 232 | 15 | Yes | 841 | 19 | 19 | Unit Ventilator | 6728 | 2.069 | 1
209 | Classroom | 341 | 22 |  |  | 0 | 0 | Unit Ventilator | 0 | 0 | 0
210 | Classroom | 413 | 27 |  | 899 | 20 | 20 | Unit Ventilator | 7192 | 3.4455 | 1
211 | Classroom | 270 | 18 | Yes | 1715 | 38 | 38 | Unit Ventilator | 13720 | 1.1808 | 1
212 | Classroom | 434 | 28 | Yes | 1911 | 43 | 43 | Unit Ventilator | 15288 | 1.7033 | 1
213 | Classroom | 310 | 20 | Yes | 1715 | 38 | 38 | Unit Ventilator | 13720 | 1.3557 | 1
214 | Classroom | 799 | 53 |  | 1786 | 40 | 40 | Unit Ventilator | 14288 | 3.3553 | 1
215 | Classroom | 325 | 21 |  | 870 | 19 | 19 | Unit Ventilator | 6960 | 2.8017 | 1
216 | Classroom | 296 | 19 | Yes | 930 | 21 | 21 | Unit Ventilator | 7440 | 2.3871 | 1
217 | Classroom | 568 | 37 |  | 870 | 19 | 19 | Unit Ventilator | 6960 | 4.8966 | 2
218 | Classroom | 415 | 27 |  | 870 | 19 | 19 | Unit Ventilator | 6960 | 3.5776 | 1
219 | Classroom | 289 | 19 |  | 870 | 19 | 19 | Unit Ventilator | 6960 | 2.4914 | 1
220 | Classroom | 278 | 18 |  | 870 | 19 | 18 | Unit Ventilator | 6960 | 2.3966 | 1
221 | Classroom | 339 | 22 |  | 899 | 20 | 20 | Unit Ventilator | 7192 | 2.8281 | 1
222 | Classroom | 372 | 24 |  | 784 | 17 | 17 | Unit Ventilator | 6272 | 3.5587 | 1
223 | Classroom | 369 | 24 | Yes | 1739 | 39 | 39 | Unit Ventilator | 13912 | 1.5914 | 1
224 | Classroom | 284 | 18 | Yes | 1739 | 39 | 39 | Unit Ventilator | 13912 | 1.2248 | 1
225 | Room | 211 | 14 |  | 196 | 4 | 4 | Air Handling Unit | 1568 | 8.074 | 2
227 | Room | 119 | 7 |  | 196 | 4 | 4 | Air Handling Unit | 1568 | 4.5536 | 2
- | 1st Floor Conference Room | 89 | 5 |  | 108 | 2 |  | Air Handling Unit | 864 | 6.1806 | 2
- | 1st Floor Counselor's Office | 17 | 1 |  | 100 | 2 |  | Air Handling Unit | 800 | 1.275 | 1
- | 1st Floor Engineer's Office | 30 | 2 |  | 36 | 0 |  | Air Handling Unit | 288 | 6.25 | 2
- | 1st Floor Entry Hallway | 79 | 5 |  | 140 | 3 |  | Air Handling Unit | 1120 | 4.2321 | 2
- | 1st Floor CSC Office | 4 | 0 |  | 100 | 2 |  | Air Handling Unit | 800 | 0.3 | 0
- | 1st Floor IT Room | 10 | 0 |  | 100 | 2 |  | Air Handling Unit | 800 | 0.75 | 0
- | 1st Floor Main Office | 98 | 6 |  | 144 | 3 |  | Air Handling Unit | 1152 | 5.1042 | 2
- | 1st Floor Office Storage | 0 | 0 |  | 160 | 3 |  | Air Handling Unit | 1280 | 0 | 0
- | 1st Floor Prinicpal's Office | 23 | 1 |  | 140 | 3 |  | Air Handling Unit | 1120 | 1.2321 | 1
- | 1st Floor Psychologist's Office | 14 | 0 |  | 140 | 3 |  | Air Handling Unit | 1120 | 0.75 | 0
- | 1st Floor Small Kitchen | 56 | 3 |  | 84 | 1 |  | Air Handling Unit | 672 | 5 | 2
- | 1st Floor Staff Lounge | 447 | 29 |  | 1556 | 35 | 29 | Unit Ventilator | 12448 | 2.1546 | 1
- | 2nd Floor Computer Storage | 44 | 2 |  | 196 | 4 | 2 | Air Handling Unit | 1568 | 1.6837 | 1
- | 2nd Floor Library | 2489 | 165 |  | 556 | 12 | 12 | Air Handling Unit | 4448 | 33.5746 | 4
- | 2nd Floor Library Lounge | 131 | 8 |  | 192 | 4 | 4 | Air Handling Unit | 1536 | 5.1172 | 2
- | 2nd Floor Library Storage | 109 | 7 |  | 336 | 7 | 7 | Air Handling Unit | 2688 | 2.433 | 1
- | 2nd Floor Office space | 250 | 16 |  | 216 | 4 | 4 | Unit Ventilator | 1728 | 8.6806 | 2
- | 2nd Floor Storage space | 358 | 23 |  | 432 | 9 | 9 | Unit Ventilator | 3456 | 6.2153 | 2
- | Cafetorium | 4622 | 308 |  | 4730 | 107 | 107 | Air Handling Unit | 37840 | 7.3288 | 2
- | Gym | 890 | 59 |  | 5644 | 128 | 59 | Air Handling Unit | 45152 | 1.1827 | 1
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
[9 empty] | 0 | 0 | 0
Sheet Last Modified: | 2021-05-03 | [7 empty] | 0 | 0 | 0
School: | William H. Ziegler Elementary School | [7 empty] | 0 | 0 | 0
Vendor: | Chadwick | Chadwick Part 2 | Chadwick Part 3 | [5 empty] | 0 | 0 | 0
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [8 empty] | 0 | 0 | 0
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | #VALUE! | #VALUE! | #VALUE!
102 | Classroom | 147 | 9 |  | 140 | 3 | 3 | Unit Ventilator | 1120 | 7.875 | 2
103 | Classroom | 309 | 20 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.7721 | 1
104 | Classroom | 346 | 23 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 3.1041 | 1
105 | Classroom | 296 | 19 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.6555 | 1
106 | Office/Classroom |  | 0 | Yes | 322 | 7 | 7 | Unit Ventilator | 2576 | 0 | 0
107 | Classroom | 161 | 10 | Yes | 638 | 14 | 14 | Unit Ventilator | 5104 | 1.8926 | 1
108 | Nurse |  | 0 | Yes | 171 | 3 | 3 | Unit Ventilator | 1368 | 0 | 0
109 | Classroom |  | 0 | Yes | 696 | 15 | 15 | Unit Ventilator | 5568 | 0 | 0
111 | Classroom | 331 | 22 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.64 | 1
112 | Classroom | 300 | 20 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.2991 | 1
113 | Classroom | 338 | 22 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.717 | 1
114 | Classroom | 301 | 20 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.3101 | 1
115 | Classroom | 312 | 20 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.4311 | 1
116 | Classroom | 318 | 21 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.4971 | 1
117 | Classroom | 318 | 21 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.4971 | 1
125 | Classroom | 294 | 19 |  | 600 | 13 | 13 | Energy Recovery Unit | 4800 | 3.675 | 1
201 | Classroom | 398 | 26 |  | 598 | 13 | 13 | Unit Ventilator | 4784 | 4.9916 | 2
202 | Classroom | 511 | 34 |  | 644 | 14 | 14 | Unit Ventilator | 5152 | 5.9511 | 2
203 | Classroom |  | 0 | Yes | 390 | 8 | 8 | Unit Ventilator | 3120 | 0 | 0
204 | Classroom | 417 | 27 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 4.0096 | 2
205 | Classroom | 315 | 21 |  | 962 | 21 | 21 | Unit Ventilator | 7696 | 2.4558 | 1
206 | Classroom | 110 | 7 | Yes | 644 | 14 | 14 | Unit Ventilator | 5152 | 1.2811 | 1
207 | Classroom |  | 0 | Yes | 243 | 5 | 5 | Unit Ventilator | 1944 | 0 | 0
208 | Teacher's Lounge |  | 0 | Yes | 280 | 6 | 6 | Unit Ventilator | 2240 | 0 | 0
210 | Classroom | 147 | 9 | Yes | 644 | 14 | 14 | Unit Ventilator | 5152 | 1.712 | 1
212 | Classroom | 534 | 35 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 6.0045 | 2
213 | Classroom | 332 | 22 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.651 | 1
214 | Classroom | 166 | 11 | Yes | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 1.8255 | 1
215 | Classroom | 281 | 18 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.0902 | 1
216 | Classroom | 265 | 17 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 2.9142 | 1
217 | Classroom | 261 | 17 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 2.8702 | 1
218 | Classroom | 275 | 18 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.0242 | 1
220 | Classroom | 269 | 17 |  | 748 | 17 | 17 | Energy Recovery Unit | 5984 | 2.6972 | 1
- | Cafeteria | 2750 | 183 |  | 2736 | 62 | 62 | Air Handling Unit | 21888 | 7.5384 | 2
- | Gymasium | 1073 | 71 |  | 3498 | 79 | 71 | Air Handling Unit | 27984 | 2.3006 | 1
- | Hallway | 105 | 7 |  |  | 0 | 0 | Air Handling Unit | 0 | 0 | 0
- | Library/IMC | 983 | 65 |  | 1953 | 44 | 44 | Air Handling Unit | 15624 | 3.775 | 1
- | Main Office |  | 0 | Yes | 456 | 10 | 10 | Unit Ventilator | 3648 | 0 | 0
- | Principal's Office |  | 0 | Yes | 198 | 4 | 4 | Unit Ventilator | 1584 | 0 | 0
- | Science Lab | 228 | 15 |  | 968 | 22 | 15 | Energy Recovery Unit | 7744 | 1.7665 | 1