## Coversheet
Contagion Mitigation System Certification of Buildings
By Walter Sobkiw
2021-05-05
05/01/2020 origination
This research is not associated with any institution.
It is ongoing and part of a broader set of COVID-19 systems oriented research areas.
www.cassbeth.com/covid-19
Copyright 2021. This spreadsheet may be freely distributed and referenced as long as the author is clearly identified. When using this information product for critical review or significant public meetings the author must be contacted and made aware of the events. Any commercial publication or other works that will collect money from part or all of this content must contact the author to arrange for release.

## Philadelphia Schools
[5 empty] | AUC Range | Cert Level | Number of Rooms |  | Mitigation Number of Rooms
[5 empty] | 120+ | 6 | 1 |  | 1
[5 empty] | 50-100 | 5 | 25 |  | 25
[5 empty] | 24 | 4 | 73 |  | 101
Sheet Last Modified: | 2021-03-22 |  |  | 2503 | 10 to 24 | 3 | 462 |  | 2935 | 0 | 0 | 0 | 0 | Min
School: | Alexander Adaire Elementary School | House Fan Abated/Final Report |  |  | 4 to 10 | 2 | 2574 |  | 2547 | 1.0003 | 1.0003 | 1.0003 | 1.0003 | Min > 0
Vendor: | Chadwick | Devine | Devine Retest |  | 1 to 4 | 1 | 4554 |  | 4166 | 327.3333 | 6 | 327.3333 | 6 | Max
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. |  |  |  |  | 0 - 1 | 0 | 2476 |  | 1721 | 3.7864 | 1 | 7.7009 | 2 | Average
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | cu-ft | AUC | Cert Level | Mitigation AUC | Mitigation Cert Level
8 ft ceiling
- | Auditorium | 2417 | 161 |  | 3234 | 73 | 73 | Air Handling Unit | 25872 | 5.6053 | 2 | 5.6053 | 2
- | Gym/Cafeteria | 322 | 21 |  | 3432 | 78 | 21 | Air Handling Unit | 27456 | 0.70367 | 0 | 0.70367 | 0
- | Main Ofiice | 161 | 10 |  | 468 | 10 | 10 | Unit Ventilator | 3744 | 2.5801 | 1 | 2.5801 | 1
100 | Classroom | 452 | 30 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.5312 | 1 | 3.5312 | 1
101 | Classroom | 480 | 32 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.75 | 1 | 3.75 | 1
102 | Classroom | 509 | 33 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.9766 | 1 | 3.9766 | 1
103 | Classroom | 409 | 27 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.1953 | 1 | 3.1953 | 1
104 | Classroom | 514 | 34 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.0156 | 2 | 4.0156 | 2
105 | Classroom | 523 | 34 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.0859 | 2 | 4.0859 | 2
106 | Classroom | 125 | 8 | Yes | 782 | 17 | 17 | Unit Ventilator | 6256 | 1.1988 | 1 | 21.1988 | 3
107 | Classroom | 272 | 18 |  | 380 | 8 | 8 | Unit Ventilator | 3040 | 5.3684 | 2 | 5.3684 | 2
108 | Faculty Room | 0 | 0 |  | 104 | 2 | 0 | Unit Ventilator | 832 | 0 | 0 | 0 | 0
109 | Classroom | 485 | 32 |  | 1470 | 33 | 32 | Unit Ventilator | 11760 | 2.4745 | 1 | 2.4745 | 1
200 | Classroom | 546 | 36 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 4.4901 | 2 | 4.4901 | 2
201 | Classroom | 607 | 40 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 4.9918 | 2 | 4.9918 | 2
202 | Classroom | 613 | 40 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 4.9119 | 2 | 4.9119 | 2
203 | Library | 593 | 39 |  | 1080 | 24 | 24 | Unit Ventilator | 8640 | 4.1181 | 2 | 4.1181 | 2
204 | Classroom | 480 | 32 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 3.9474 | 1 | 3.9474 | 1
205 | Classroom | 182 | 12 | Yes | 960 | 21 | 21 | Unit Ventilator | 7680 | 1.4219 | 1 | 21.4219 | 3
206 | Classroom | 317 | 21 |  | 984 | 22 | 21 | Unit Ventilator | 7872 | 2.4162 | 1 | 2.4162 | 1
207 | Classroom | 798 | 53 |  | 456 | 10 | 10 | Unit Ventilator | 3648 | 13.125 | 3 | 13.125 | 3
208 | Classroom | 577 | 38 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.5078 | 2 | 4.5078 | 2
209 | Classroom | 458 | 30 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 3.5781 | 1 | 3.5781 | 1
210 | Classroom | 519 | 34 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.0547 | 2 | 4.0547 | 2
211 | Classroom | 534 | 35 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 3.9732 | 1 | 3.9732 | 1
212 | Classroom | 1568 | 104 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 12.25 | 3 | 12.25 | 3
214 | Classroom | 340 | 22 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 2.6562 | 1 | 2.6562 | 1
216 | Classroom | 617 | 41 |  | 456 | 10 | 10 | Unit Ventilator | 3648 | 10.148 | 3 | 10.148 | 3
218 | Classroom | 424 | 28 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 4.0665 | 2 | 4.0665 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-24 | [8 empty] | unk | unk | unk | unk
School: | Ethan Allen Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
B1 | Classroom | 545 | 36 |  | 736 | 16 | 16 | House Fan | 5888 | 5.5537 | 2 | 5.5537 | 2
B2 | Classroom | 708 | 47 |  | 352 | 8 | 8 | House Fan | 2816 | 15.0852 | 3 | 15.0852 | 3
B3 | Classroom | 421 | 28 |  | 506 | 11 | 11 | House Fan | 4048 | 6.2401 | 2 | 6.2401 | 2
B4 | Classroom | 453 | 30 |  | 452 | 10 | 10 | House Fan | 3616 | 7.5166 | 2 | 7.5166 | 2
- | Auditorium | 2183 | 145 |  | 3432 | 78 | 78 | House Fan | 27456 | 4.7705 | 2 | 4.7705 | 2
- | Boys Basement Restroom | 130 | 8 |  | 383 | 8 | 8 | AC Bathroom | 3064 | 2.5457 | 1 | 2.5457 | 1
- | Girls Basement Restroom | 787 | 52 |  | 524 | 11 | 11 | AC Bathroom | 4192 | 11.2643 | 3 | 11.2643 | 3
101 | Classroom | 600 | 40 |  | 920 | 20 | 20 | House Fan | 7360 | 4.8913 | 2 | 4.8913 | 2
102 | Classroom | 405 | 27 |  | 690 | 15 | 15 | House Fan | 5520 | 4.4022 | 2 | 4.4022 | 2
103 | Classroom | 190 | 12 | Yes | 736 | 16 | 16 | House Fan | 5888 | 1.9361 | 1 | 21.9361 | 3
104 | Classroom | 505 | 33 |  | 690 | 15 | 15 | House Fan | 5520 | 5.4891 | 2 | 5.4891 | 2
105 | Classroom | 1216 | 81 |  | 690 | 15 | 15 | House Fan | 5520 | 13.2174 | 3 | 13.2174 | 3
106 | Classroom | 1055 | 70 |  | 690 | 15 | 15 | House Fan | 5520 | 11.4674 | 3 | 11.4674 | 3
107 | Classroom | 1312 | 87 |  | 690 | 15 | 15 | House Fan | 5520 | 14.2609 | 3 | 14.2609 | 3
108 | Classroom | 1307 | 87 |  | 736 | 16 | 16 | House Fan | 5888 | 13.3186 | 3 | 13.3186 | 3
109 | Classroom | 874 | 58 |  | 690 | 15 | 15 | House Fan | 5520 | 9.5 | 2 | 9.5 | 2
110 | Classroom | 1349 | 89 |  | 736 | 16 | 16 | House Fan | 5888 | 13.7466 | 3 | 13.7466 | 3
210 | Classroom | 1375 | 91 |  | 736 | 16 | 16 | House Fan | 5888 | 14.0115 | 3 | 14.0115 | 3
202 | Classroom | 298 | 19 |  | 690 | 15 | 15 | House Fan | 5520 | 3.2391 | 1 | 3.2391 | 1
203 | Classroom | 209 | 13 |  | 736 | 16 | 13 | House Fan | 5888 | 2.1298 | 1 | 2.1298 | 1
204 | Classroom | 373 | 24 |  | 690 | 15 | 15 | House Fan | 5520 | 4.0543 | 2 | 4.0543 | 2
205 | Classroom | 574 | 38 |  | 690 | 15 | 15 | House Fan | 5520 | 6.2391 | 2 | 6.2391 | 2
206 | Classroom | 580 | 38 |  | 690 | 15 | 15 | House Fan | 5520 | 6.3043 | 2 | 6.3043 | 2
207 | Classroom | 919 | 61 |  | 690 | 15 | 15 | House Fan | 5520 | 9.9891 | 2 | 9.9891 | 2
208 | Classroom | 1175 | 78 |  | 736 | 16 | 16 | House Fan | 5888 | 11.9735 | 3 | 11.9735 | 3
209 | Classroom | 753 | 50 |  | 690 | 15 | 15 | House Fan | 5520 | 8.1848 | 2 | 8.1848 | 2
210 | Classroom | 1638 | 109 |  | 736 | 16 | 16 | House Fan | 5888 | 16.6916 | 3 | 16.6916 | 3
214 | Classroom |  | 0 | Yes | 341 | 7 | 7 | House Fan | 2728 | unk | unk | 20 | 3
301 | Classroom | 880 | 58 |  | 736 | 16 | 16 | House Fan | 5888 | 8.9674 | 2 | 8.9674 | 2
302 | Classroom | 319 | 21 |  | 690 | 15 | 15 | House Fan | 5520 | 3.4674 | 1 | 3.4674 | 1
303 | Classroom | 74 | 4 |  | 736 | 16 | 4 | House Fan | 5888 | 0.75408 | 0 | 0.75408 | 0
304 | Classroom | 141 | 9 |  | 690 | 15 | 9 | House Fan | 5520 | 1.5326 | 1 | 1.5326 | 1
305 | Classroom | 151 | 10 |  | 690 | 15 | 10 | House Fan | 5520 | 1.6413 | 1 | 1.6413 | 1
306 | Classroom | 268 | 17 |  | 690 | 15 | 15 | House Fan | 5520 | 2.913 | 1 | 2.913 | 1
307 | Classroom | 921 | 61 |  | 690 | 15 | 15 | House Fan | 5520 | 10.0109 | 3 | 10.0109 | 3
308 | Classroom | 520 | 34 |  | 736 | 16 | 16 | House Fan | 5888 | 5.2989 | 2 | 5.2989 | 2
309 | Classroom | 121 | 8 |  | 690 | 15 | 8 | House Fan | 5520 | 1.3152 | 1 | 1.3152 | 1
310 | Classroom | 290 | 19 |  | 736 | 16 | 16 | House Fan | 5888 | 2.9552 | 1 | 2.9552 | 1
314 | Classroom | 421 | 28 |  | 720 | 16 | 16 | House Fan | 5760 | 4.3854 | 2 | 4.3854 | 2
- | Main Office |  | 0 | Yes | 309 | 7 | 7 | House Fan | 2472 | unk | unk | 20 | 3
- | Prinicipal Office |  | 0 | Yes | 177 | 4 | 4 | House Fan | 1416 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 186 | 4 | 4 | House Fan | 1488 | unk | unk | 20 | 3
- | Conselor Office |  | 0 | Yes | 177 | 4 | 4 | House Fan | 1416 | unk | unk | 20 | 3
- | Pyschologist Office |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | unk | unk | 20 | 3
- | Gym |  | 0 | Yes | 3422 | 77 | 77 | Hydroxyl Unit | 27376 | unk | unk | 20 | 3
Sheet Last Modified: | 2021-03-16 | [8 empty] | unk | unk | unk | unk
School: | Dr. Ethel Allen Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Chadwick Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
101-A | Classroom | 528 | 35 |  | 896 | 20 | 20 | Unit Ventilator | 7168 | 4.4196 | 2 | 4.4196 | 2
101-B | Classroom | 100 | 6 |  | 1036 | 23 | 6 | Unit Ventilator | 8288 | 0.72394 | 0 | 0.72394 | 0
102-A | Classroom | 70 | 4 |  | 1110 | 25 | 4 | Unit Ventilator | 8880 | 0.47297 | 0 | 0.47297 | 0
102-B | Classroom | 485 | 32 |  | 1110 | 25 | 25 | Unit Ventilator | 8880 | 3.277 | 1 | 3.277 | 1
102-C | Classroom | 0 | 0 |  | 1110 | 25 | 0 | Unit Ventilator | 8880 | 0 | 0 | 0 | 0
102-D | Classroom |  | 0 |  | 1110 | 25 | 0 | Unit Ventilator | 8880 | unk | unk | unk | unk
103 | Classroom | 1233 | 82 | Yes | 2277 | 51 | 51 | Unit Ventilator | 18216 | 4.0613 | 2 | 24.0613 | 4
103-A | Classroom | 76 | 5 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
104 | Classroom | 419 | 27 |  | 1260 | 28 | 27 | Unit Ventilator | 10080 | 2.494 | 1 | 2.494 | 1
105 | Classroom | 472 | 31 |  | 1260 | 28 | 28 | Unit Ventilator | 10080 | 2.8095 | 1 | 2.8095 | 1
106 | Classroom | 152 | 10 |  | 1184 | 26 | 10 | Unit Ventilator | 9472 | 0.96284 | 0 | 0.96284 | 0
107 | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | unk | unk | unk | unk
109 | Classroom | 172 | 11 | Yes | 1260 | 28 | 28 | Unit Ventilator | 10080 | 1.0238 | 1 | 21.0238 | 3
110 | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | unk | unk | unk | unk
112 | Classroom | 29 | 1 |  | 1056 | 24 | 1 | Unit Ventilator | 8448 | 0.20597 | 0 | 0.20597 | 0
113 | Classroom | 26 | 1 |  | 1056 | 24 | 1 | Unit Ventilator | 8448 | 0.18466 | 0 | 0.18466 | 0
114 | Classroom | 380 | 25 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.6989 | 1 | 2.6989 | 1
200 | Classroom | 511 | 34 |  | 1500 | 34 | 34 | Unit Ventilator | 12000 | 2.555 | 1 | 2.555 | 1
200C | Classroom | 0 | 0 | Yes | 784 | 17 | 17 | Unit Ventilator | 6272 | 0 | 0 | 20 | 3
201B | Classroom |  | 0 |  | 840 | 19 | 0 | Unit Ventilator | 6720 | unk | unk | unk | unk
202 | Classroom | 367 | 24 |  | 983 | 22 | 22 | Unit Ventilator | 7864 | 2.8001 | 1 | 2.8001 | 1
202 | Classroom |  | 0 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
203A | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | unk | unk | unk | unk
203B | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | unk | unk | unk | unk
203C | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | unk | unk | unk | unk
203D | Classroom |  | 0 |  | 1036 | 23 | 0 | Unit Ventilator | 8288 | unk | unk | unk | unk
204 | Classroom | 525 | 35 |  | 980 | 22 | 22 | Unit Ventilator | 7840 | 4.0179 | 2 | 4.0179 | 2
206 | Classroom | 194 | 12 |  | 1200 | 27 | 12 | Unit Ventilator | 9600 | 1.2125 | 1 | 1.2125 | 1
206 | Classroom | 170 | 11 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
207A | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | unk | unk | unk | unk
207B | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | unk | unk | unk | unk
208A | Classroom | 108 | 7 |  | 1260 | 28 | 7 | Unit Ventilator | 10080 | 0.64286 | 0 | 0.64286 | 0
208B | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | unk | unk | unk | unk
208C | Classroom |  | 0 |  | 1260 | 28 | 0 | Unit Ventilator | 10080 | unk | unk | unk | unk
209 | Classroom | 907 | 60 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Add B. Anderson Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Part 2 | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
- | Auditorium | 5840 | 389 |  | 2589 | 58 | 58 | Air Handling Unit | 20712 | 16.9177 | 3 | 16.9177 | 3
- | Gym | 2392 | 159 |  | 2200 | 50 | 50 | Air Handling Unit | 17600 | 8.1545 | 2 | 8.1545 | 2
- | Main Office | 84 | 5 | Yes | 451 | 10 | 10 | Unit Ventilator | 3608 | 1.3969 | 1 | 21.3969 | 3
- | Principal's Office |  | 0 | Yes | 350 | 7 | 7 | Convector | 2800 | unk | unk | 20 | 3
- | Nurse's Office |  | 0 | Yes | 350 | 7 | 7 | Convector | 2800 | unk | unk | 20 | 3
- | Stage | 2534 | 168 |  | 1008 | 22 | 22 | Air Handling Unit | 8064 | 18.8542 | 3 | 18.8542 | 3
100 | Classroom | 281 | 18 |  | 467 | 10 | 10 | Unit Ventilator | 3736 | 4.5128 | 2 | 4.5128 | 2
101 | Classroom | 32 | 2 |  | 355 | 8 | 2 | Unit Ventilator | 2840 | 0.67606 | 0 | 0.67606 | 0
102 | Classroom | 102 | 6 | Yes | 540 | 12 | 12 | Unit Ventilator | 4320 | 1.4167 | 1 | 21.4167 | 3
103 | Classroom | 40 | 2 | Yes | 628 | 14 | 14 | Unit Ventilator | 5024 | 0.47771 | 0 | 20.4777 | 3
104 | Classroom | 287 | 19 |  | 395 | 8 | 8 | Unit Ventilator | 3160 | 5.4494 | 2 | 5.4494 | 2
105 | Classroom | 295 | 19 |  | 521 | 11 | 11 | Unit Ventilator | 4168 | 4.2466 | 2 | 4.2466 | 2
106 | Classroom | 290 | 19 |  | 446 | 10 | 10 | Unit Ventilator | 3568 | 4.8767 | 2 | 4.8767 | 2
108 | Classroom | 283 | 18 |  | 405 | 9 | 9 | Unit Ventilator | 3240 | 5.2407 | 2 | 5.2407 | 2
200 | Classroom | 82 | 5 | Yes | 476 | 10 | 10 | Unit Ventilator | 3808 | 1.292 | 1 | 21.292 | 3
201 | Classroom | 128 | 8 | Yes | 627 | 14 | 14 | Unit Ventilator | 5016 | 1.5311 | 1 | 21.5311 | 3
202 | Classroom | 408 | 27 |  | 576 | 13 | 13 | Unit Ventilator | 4608 | 5.3125 | 2 | 5.3125 | 2
204 | Classroom | 323 | 21 |  | 683 | 15 | 15 | Unit Ventilator | 5464 | 3.5469 | 1 | 3.5469 | 1
205 | Classroom | 80 | 5 | Yes | 658 | 14 | 14 | Unit Ventilator | 5264 | 0.91185 | 0 | 20.9119 | 3
206 | Classroom | 329 | 21 |  | 637 | 14 | 14 | Unit Ventilator | 5096 | 3.8736 | 1 | 3.8736 | 1
207 | Classroom | 82 | 5 | Yes | 587 | 13 | 13 | Unit Ventilator | 4696 | 1.0477 | 1 | 21.0477 | 3
208 | Classroom | 129 | 8 | Yes | 720 | 16 | 16 | Unit Ventilator | 5760 | 1.3438 | 1 | 21.3438 | 3
209 | Classroom | 305 | 20 |  | 629 | 14 | 14 | Unit Ventilator | 5032 | 3.6367 | 1 | 3.6367 | 1
210 | Classroom | 41 | 2 |  | 241 | 5 | 2 | Unit Ventilator | 1928 | 1.2759 | 1 | 1.2759 | 1
211 | Classroom | 56 | 3 |  | 385 | 8 | 3 | Unit Ventilator | 3080 | 1.0909 | 1 | 1.0909 | 1
212 | Classroom | 319 | 21 |  | 603 | 13 | 13 | Unit Ventilator | 4824 | 3.9677 | 1 | 3.9677 | 1
213 | Classroom | 49 | 3 | Yes | 290 | 6 | 6 | Unit Ventilator | 2320 | 1.2672 | 1 | 21.2672 | 3
214 | Classroom | 112 | 7 | Yes | 741 | 16 | 16 | Unit Ventilator | 5928 | 1.1336 | 1 | 21.1336 | 3
300 | Classroom | 35 | 2 | Yes | 947 | 21 | 21 | Unit Ventilator | 7576 | 0.27719 | 0 | 20.2772 | 3
301 | Classroom | 63 | 4 | Yes | 900 | 20 | 20 | Unit Ventilator | 7200 | 0.525 | 0 | 20.525 | 3
302 | Classroom | 87 | 5 | Yes | 588 | 13 | 13 | Unit Ventilator | 4704 | 1.1097 | 1 | 21.1097 | 3
303 | Classroom | 85 | 5 | Yes | 571 | 12 | 12 | Unit Ventilator | 4568 | 1.1165 | 1 | 21.1165 | 3
304 | Classroom | 293 | 19 |  | 431 | 9 | 9 | Unit Ventilator | 3448 | 5.0986 | 2 | 5.0986 | 2
305 | Classroom | 58 | 3 | Yes | 504 | 11 | 11 | Unit Ventilator | 4032 | 0.8631 | 0 | 20.8631 | 3
306 | Classroom | 286 | 19 |  | 415 | 9 | 9 | Unit Ventilator | 3320 | 5.1687 | 2 | 5.1687 | 2
307 | Classroom | 97 | 6 | Yes | 501 | 11 | 11 | Unit Ventilator | 4008 | 1.4521 | 1 | 21.4521 | 3
308 | Classroom | 79 | 5 | Yes | 686 | 15 | 15 | Unit Ventilator | 5488 | 0.8637 | 0 | 20.8637 | 3
310 | Classroom | 106 | 7 | Yes | 592 | 13 | 13 | Unit Ventilator | 4736 | 1.3429 | 1 | 21.3429 | 3
311 | Classroom | 53 | 3 | Yes | 441 | 10 | 10 | Unit Ventilator | 3528 | 0.90136 | 0 | 20.9014 | 3
312 | Classroom | 18 | 1 | Yes | 465 | 10 | 10 | Unit Ventilator | 3720 | 0.29032 | 0 | 20.2903 | 3
313 | Classroom | 72 | 4 | Yes | 463 | 10 | 10 | Unit Ventilator | 3704 | 1.1663 | 1 | 21.1663 | 3
314 | Classroom | 61 | 4 | Yes | 533 | 12 | 12 | Unit Ventilator | 4264 | 0.85835 | 0 | 20.8583 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | Chester A. Arthur Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Retest | Devine 3rd Retest | [7 empty] | unk | unk | unk | unk
| Devine 4th Retest | Devine 5th Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
B001 | Classroom | 380 | 25 |  | 551 | 12 | 12 | Unit Ventilator | 4408 | 5.1724 | 2 | 5.1724 | 2
B002 | Classroom | 0 | 0 |  | 100 | 2 | 0 | N/A | 800 | 0 | 0 | 0 | 0
100 | Classroom | 309 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.9261 | 1 | 2.9261 | 1
102 | Classroom | 335 | 22 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.1723 | 1 | 3.1723 | 1
104 | Classroom | 295 | 19 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.7936 | 1 | 2.7936 | 1
106 | Classroom | 346 | 23 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.2765 | 1 | 3.2765 | 1
107A | Teacher's Lounge |  | 0 | Yes | 448 | 10 | 10 | Unit Ventilator | 3584 | unk | unk | 20 | 3
200 | Classroom | 335 | 22 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.1723 | 1 | 3.1723 | 1
201 | Classroom | 304 | 20 |  | 364 | 8 | 8 | Unit Ventilator | 2912 | 6.2637 | 2 | 6.2637 | 2
202 | Classroom | 320 | 21 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.0303 | 1 | 3.0303 | 1
203 | Classroom | 299 | 19 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.5955 | 1 | 2.5955 | 1
204 | Classroom | 333 | 22 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.1534 | 1 | 3.1534 | 1
205 | Classroom | 374 | 24 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.2465 | 1 | 3.2465 | 1
206 | Classroom | 280 | 18 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.6515 | 1 | 2.6515 | 1
207 | Classroom | 341 | 22 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.9601 | 1 | 2.9601 | 1
207A | Classroom |  | 0 | Yes | 425 | 9 | 9 | Unit Ventilator | 3400 | unk | unk | 20 | 3
209 | Classroom | 311 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.9451 | 1 | 2.9451 | 1
300 | Classroom | 293 | 19 |  | 857 | 19 | 19 | Unit Ventilator | 6856 | 2.5642 | 1 | 2.5642 | 1
301 | Classroom | 273 | 18 |  | 364 | 8 | 8 | Unit Ventilator | 2912 | 5.625 | 2 | 5.625 | 2
302 | Classroom | 355 | 23 |  | 857 | 19 | 19 | Unit Ventilator | 6856 | 3.1068 | 1 | 3.1068 | 1
303 | Classroom | 328 | 21 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.8472 | 1 | 2.8472 | 1
304 | Classroom | 350 | 23 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.3144 | 1 | 3.3144 | 1
305 | Classroom | 274 | 18 |  | 900 | 20 | 18 | Unit Ventilator | 7200 | 2.2833 | 1 | 2.2833 | 1
306 | Classroom | 304 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.8788 | 1 | 2.8788 | 1
307 | Classroom | 350 | 23 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.0382 | 1 | 3.0382 | 1
307A | Classroom |  | 0 | Yes | 425 | 9 | 9 | Unit Ventilator | 3400 | unk | unk | 20 | 3
309 | Classroom | 331 | 22 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.1345 | 1 | 3.1345 | 1
- | Auditorium | 753 | 50 |  | 4335 | 98 | 50 | HV Unit | 34680 | 1.3028 | 1 | 1.3028 | 1
- | Gym | 2466 | 164 |  | 3055 | 69 | 69 | HV Unit | 24440 | 6.054 | 2 | 6.054 | 2
- | IMC | 383 | 25 |  | 1472 | 33 | 25 | Unit Ventilator | 11776 | 1.9514 | 1 | 1.9514 | 1
- | Resource Room/Storage | 0 | 0 | Yes | 300 | 6 | 6 | Unit Ventilator | 2400 | 0 | 0 | 20 | 3
- | Main Office | 401 | 26 |  | 1104 | 25 | 25 | Unit Ventilator | 8832 | 2.7242 | 1 | 2.7242 | 1
- | BE Office | 63 | 4 |  | 240 | 5 | 4 | Unit Ventilator | 1920 | 1.9688 | 1 | 1.9688 | 1
- | Nurse Office | 0 | 0 | Yes | 276 | 6 | 6 |  | 2208 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 240 | 5 | 5 |  | 1920 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | Alexander D. Bache Elementary School | Bache Part 2 | [7 empty] | unk | unk | unk | unk
School: | W.E. Martin Building | Martin Part 2 | [7 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Bache Building | [9 empty] | unk | unk | unk | unk
1 | Classroom | 274 | 18 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.6758 | 1 | 2.6758 | 1
2 | Classroom | 295 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8809 | 1 | 2.8809 | 1
3 | Classroom | 305 | 20 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.9785 | 1 | 2.9785 | 1
4 | Classroom | 289 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8223 | 1 | 2.8223 | 1
5 | Classroom | 330 | 22 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.2227 | 1 | 3.2227 | 1
6 | Classroom | 273 | 18 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.666 | 1 | 2.666 | 1
7 | Classroom | 312 | 20 |  | 528 | 12 | 12 | Unit Ventilator | 4224 | 4.4318 | 2 | 4.4318 | 2
8 | Classroom | 406 | 27 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.9648 | 1 | 3.9648 | 1
9 | Classroom | 455 | 30 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 4.4434 | 2 | 4.4434 | 2
10 | Classroom | 400 | 26 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.9062 | 1 | 3.9062 | 1
11 | Classroom | 346 | 23 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.3789 | 1 | 3.3789 | 1
12 | Classroom | 388 | 25 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.7891 | 1 | 3.7891 | 1
13 | Teacher's Lounge | 339 | 22 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.3105 | 1 | 3.3105 | 1
14 | Classroom | 288 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8125 | 1 | 2.8125 | 1
15 | Classroom | 424 | 28 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 4.1406 | 2 | 4.1406 | 2
16 | Library | 296 | 19 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 3.0833 | 1 | 3.0833 | 1
17 | Library | 294 | 19 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 3.0625 | 1 | 3.0625 | 1
18 | Classroom | 338 | 22 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.3008 | 1 | 3.3008 | 1
19 | Classroom | 114 | 7 | Yes | 768 | 17 | 17 | Unit Ventilator | 6144 | 1.1133 | 1 | 21.1133 | 3
20 | Classroom | 302 | 20 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 3.1458 | 1 | 3.1458 | 1
21 | Classroom | 278 | 18 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 2.9616 | 1 | 2.9616 | 1
22 | Classroom | 328 | 21 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.7273 | 1 | 3.7273 | 1
23 | Classroom | 360 | 24 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 3.8352 | 1 | 3.8352 | 1
24 | Classroom | 347 | 23 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.9432 | 1 | 3.9432 | 1
25 | Classroom | 377 | 25 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.6816 | 1 | 3.6816 | 1
26 | Classroom | 381 | 25 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 3.9688 | 1 | 3.9688 | 1
27 | Classroom | 436 | 29 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 4.2578 | 2 | 4.2578 | 2
- | Cafeteria | 0 | 0 | Yes | 1891 | 42 | 42 | Unit Ventilator | 15128 | 0 | 0 | 20 | 3
Martin Building | 0 | [8 empty] | unk | unk | unk | unk
101 | Classroom | 405 | 27 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 4.2602 | 2 | 4.2602 | 2
102 | Classroom | 415 | 27 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 4.3654 | 2 | 4.3654 | 2
103 | Classroom | 308 | 20 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.5 | 1 | 3.5 | 1
104 | Classroom | 289 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8223 | 1 | 2.8223 | 1
105 | Classroom | 355 | 23 |  | 570 | 12 | 12 | Unit Ventilator | 4560 | 4.6711 | 2 | 4.6711 | 2
106 | Classroom | 339 | 22 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 3.9851 | 1 | 3.9851 | 1
107A | Classroom | 317 | 21 |  | 900 | 20 | 20 | Unit Ventilator | 7200 | 2.6417 | 1 | 2.6417 | 1
107B | Classroom | 0 | 0 | Yes | 736 | 16 | 16 | Unit Ventilator | 5888 | 0 | 0 | 20 | 3
108 | Classroom |  | 0 | Yes | 420 | 9 | 9 |  | 3360 | unk | unk | 20 | 3
110 | Classroom | 518 | 34 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 4.968 | 2 | 4.968 | 2
111 | Classroom | 354 | 23 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 3.9805 | 1 | 3.9805 | 1
112 | Classroom | 328 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5652 | 1 | 3.5652 | 1
113 | Classroom | 389 | 25 |  | 1092 | 24 | 24 | Unit Ventilator | 8736 | 2.6717 | 1 | 2.6717 | 1
114 | Classroom | 663 | 44 |  | 1036 | 23 | 23 | Unit Ventilator | 8288 | 4.7997 | 2 | 4.7997 | 2
115 | Classroom | 422 | 28 |  | 814 | 18 | 18 | Unit Ventilator | 6512 | 3.8882 | 1 | 3.8882 | 1
117 | Classroom | 536 | 35 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 5.1407 | 2 | 5.1407 | 2
119 | Classroom | 480 | 32 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 5.0491 | 2 | 5.0491 | 2
120 | Classroom | 277 | 18 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.0109 | 1 | 3.0109 | 1
121 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | Unit Ventilator | 5760 | 0 | 0 | 20 | 3
122 | Classroom | 0 | 0 |  | 744 | 16 | 0 | Unit Ventilator | 5952 | 0 | 0 | 0 | 0
124 | Classroom | 273 | 18 |  | 759 | 17 | 17 | Unit Ventilator | 6072 | 2.6976 | 1 | 2.6976 | 1
127 | Classroom |  | 0 | Yes | 690 | 15 | 15 | N/A | 5520 | unk | unk | 20 | 3
128 | Homemaking | 288 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8125 | 1 | 2.8125 | 1
129 | Classroom | 280 | 18 |  | 500 | 11 | 11 | Unit Ventilator | 4000 | 4.2 | 2 | 4.2 | 2
130 | Classroom | 321 | 21 |  | 644 | 14 | 14 | Unit Ventilator | 5152 | 3.7384 | 1 | 3.7384 | 1
131 | Classroom | 283 | 18 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 3.3268 | 1 | 3.3268 | 1
133 | Classroom | 337 | 22 |  | 403 | 9 | 9 | Unit Ventilator | 3224 | 6.2717 | 2 | 6.2717 | 2
134 | Counselor office | 279 | 18 |  | 512 | 11 | 11 | Unit Ventilator | 4096 | 4.0869 | 2 | 4.0869 | 2
135 | Custodial supply room | 0 | 0 |  | 512 | 11 | 0 | Unit Ventilator | 4096 | 0 | 0 | 0 | 0
136 | Classroom | 276 | 18 |  | 403 | 9 | 9 | Unit Ventilator | 3224 | 5.1365 | 2 | 5.1365 | 2
- | Main Office |  | 0 | Yes | 529 | 12 | 12 |  | 4232 | unk | unk | 20 | 3
- | Principals Office |  | 0 | Yes | 221 | 5 | 5 |  | 1768 | unk | unk | 20 | 3
- | Nurses Office |  | 0 | Yes | 308 | 7 | 7 |  | 2464 | unk | unk | 20 | 3
- | Auditorium | 109 | 7 |  | 1702 | 38 | 7 | Unit Ventilator | 13616 | 0.48032 | 0 | 0.48032 | 0
- | Cafe | 642 | 42 |  | 2451 | 55 | 42 | Unit Ventilator | 19608 | 1.9645 | 1 | 1.9645 | 1
- | Gym | 364 | 24 |  | 1914 | 43 | 24 | Unit Ventilator | 15312 | 1.4263 | 1 | 1.4263 | 1
- | Hallway | 157 | 10 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
- | Staff Lounge |  | 0 |  | 525 | 11 | 0 |  | 4200 | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-28 | [8 empty] | unk | unk | unk | unk
School: | Charles Carmine Antonio Baldi Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
22 | Classroom | 903 | 60 |  | 799 | 18 | 18 | Air Handling Unit | 6392 | 8.4762 | 2 | 8.4762 | 2
23 | Classroom | 552 | 36 |  | 844 | 19 | 19 | Unit Ventilator | 6752 | 4.9052 | 2 | 4.9052 | 2
24 | Classroom | 670 | 44 |  | 853 | 19 | 19 | Unit Ventilator | 6824 | 5.891 | 2 | 5.891 | 2
26B | Classroom | 383 | 25 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 3.5116 | 1 | 3.5116 | 1
27A | Classroom | 444 | 29 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 4.0709 | 2 | 4.0709 | 2
28 | Science Lab | 1347 | 89 |  | 1213 | 27 | 27 | Unit Ventilator | 9704 | 8.3285 | 2 | 8.3285 | 2
29 | Room | 733 | 48 |  | 1280 | 29 | 29 | Unit Ventilator | 10240 | 4.2949 | 2 | 4.2949 | 2
30 | Science Lab | 1295 | 86 |  | 1213 | 27 | 27 | Unit Ventilator | 9704 | 8.007 | 2 | 8.007 | 2
31A | Classroom | 696 | 46 |  | 831 | 18 | 18 | Unit Ventilator | 6648 | 6.2816 | 2 | 6.2816 | 2
31B | Classroom | 772 | 51 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 7.0782 | 2 | 7.0782 | 2
32A | Classroom | 1064 | 70 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 9.3662 | 2 | 9.3662 | 2
32B | Classroom | 395 | 26 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 3.6216 | 1 | 3.6216 | 1
33A | Classroom | 1195 | 79 |  | 853 | 19 | 19 | Unit Ventilator | 6824 | 10.507 | 3 | 10.507 | 3
34a | Classroom | 310 | 20 |  | 844 | 19 | 19 | Unit Ventilator | 6752 | 2.7547 | 1 | 2.7547 | 1
34b | Classroom | 232 | 15 |  | 799 | 18 | 15 | Unit Ventilator | 6392 | 2.1777 | 1 | 2.1777 | 1
35 | Science Lab | 433 | 28 |  | 1227 | 27 | 27 | Unit Ventilator | 9816 | 2.6467 | 1 | 2.6467 | 1
35 | Lounge | 133 | 8 |  | 435 | 9 | 8 | Unit Ventilator | 3480 | 2.2931 | 1 | 2.2931 | 1
38 | Lounge | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0 | 0 | 0
39 | Lounge | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0 | 0 | 0
40 | Seminar Room | 1766 | 117 |  | 411 | 9 | 9 | Unit Ventilator | 3288 | 32.2263 | 4 | 32.2263 | 4
40 | Classroom | 353 | 23 |  | 411 | 9 | 9 | Unit Ventilator | 3288 | 6.4416 | 2 | 6.4416 | 2
42 | SGI Room | 205 | 13 |  | 435 | 9 | 9 | Unit Ventilator | 3480 | 3.5345 | 1 | 3.5345 | 1
43 | SGI Room | 226 | 15 |  | 485 | 11 | 11 | Unit Ventilator | 3880 | 3.4948 | 1 | 3.4948 | 1
44A | Classroom | 243 | 16 |  | 854 | 19 | 16 | Unit Ventilator | 6832 | 2.1341 | 1 | 2.1341 | 1
44B | Classroom | 194 | 12 |  | 847 | 19 | 12 | Unit Ventilator | 6776 | 1.7178 | 1 | 1.7178 | 1
45 | Teachers IPO Room | 0 | 0 |  | 980 | 22 | 0 | Unit Ventilator | 7840 | 0 | 0 | 0 | 0
46 | Conf. Room | 56 | 3 |  | 980 | 22 | 3 | Unit Ventilator | 7840 | 0.42857 | 0 | 0.42857 | 0
46 | IPO Materials Room | 76 | 5 |  | 980 | 22 | 5 | Unit Ventilator | 7840 | 0.58163 | 0 | 0.58163 | 0
47 | Faculty Lounge Room | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0 | 0 | 0
47a | Classroom | 195 | 13 |  | 841 | 19 | 13 | Air Handling Unit | 6728 | 1.739 | 1 | 1.739 | 1
47b | Classroom | 191 | 12 |  | 844 | 19 | 12 | Air Handling Unit | 6752 | 1.6973 | 1 | 1.6973 | 1
48 | Science Lab | 858 | 57 |  | 1227 | 27 | 27 | Unit Ventilator | 9816 | 5.2445 | 2 | 5.2445 | 2
B4 | Room |  | 0 |  | 853 | 19 | 0 |  | 6824 | unk | unk | unk | unk
G5 | Room |  | 0 |  | 853 | 19 | 0 |  | 6824 | unk | unk | unk | unk
G100 | Classroom |  | 0 | Yes | 565 | 12 | 12 |  | 4520 | unk | unk | 20 | 3
G101 | Classroom |  | 0 |  | 1227 | 27 | 0 |  | 9816 | unk | unk | unk | unk
G102 | Classroom |  | 0 |  | 799 | 18 | 0 |  | 6392 | unk | unk | unk | unk
G103 | Classroom |  | 0 |  | 844 | 19 | 0 |  | 6752 | unk | unk | unk | unk
G104 | Classroom |  | 0 |  | 853 | 19 | 0 |  | 6824 | unk | unk | unk | unk
G105 | Classroom |  | 0 |  | 853 | 19 | 0 |  | 6824 | unk | unk | unk | unk
Y3 | Room |  | 0 |  | 818 | 18 | 0 |  | 6544 | unk | unk | unk | unk
Y5 | Room |  | 0 |  | 852 | 19 | 0 |  | 6816 | unk | unk | unk | unk
Y104 | Room |  | 0 |  | 818 | 18 | 0 |  | 6544 | unk | unk | unk | unk
Y105 | Room |  | 0 |  | 852 | 19 | 0 |  | 6816 | unk | unk | unk | unk
100 | Common Area | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0 | 0 | 0
127 | Art Lab | 0 | 0 | Yes | 2279 | 51 | 51 | Unit Ventilator | 18232 | 0 | 0 | 20 | 3
128 | Art Lab | 0 | 0 | Yes | 2184 | 49 | 49 | Unit Ventilator | 17472 | 0 | 0 | 20 | 3
129 | Faculty Dining Room | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0 | 0 | 0
137 | Classroom | 1440 | 96 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 13.2029 | 3 | 13.2029 | 3
138 | Classroom | 1218 | 81 |  | 831 | 18 | 18 | Unit Ventilator | 6648 | 10.9928 | 3 | 10.9928 | 3
139 | Lab | 2473 | 164 |  | 1213 | 27 | 27 | Unit Ventilator | 9704 | 15.2906 | 3 | 15.2906 | 3
140 | Large Group Room | 1508 | 100 |  | 1280 | 29 | 29 | Unit Ventilator | 10240 | 8.8359 | 2 | 8.8359 | 2
141 | Science Lab | 1291 | 86 |  | 1213 | 27 | 27 | Unit Ventilator | 9704 | 7.9823 | 2 | 7.9823 | 2
142 | Classroom | 1844 | 122 |  | 831 | 18 | 18 | Unit Ventilator | 6648 | 16.6426 | 3 | 16.6426 | 3
143 | Classroom | 1560 | 104 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 14.3032 | 3 | 14.3032 | 3
144 | Classroom | 391 | 26 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 3.585 | 1 | 3.585 | 1
145 | Classroom | 619 | 41 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 5.4489 | 2 | 5.4489 | 2
146 | Classroom | 265 | 17 |  | 853 | 19 | 17 | Unit Ventilator | 6824 | 2.33 | 1 | 2.33 | 1
147 | Classroom | 562 | 37 |  | 853 | 19 | 19 | Unit Ventilator | 6824 | 4.9414 | 2 | 4.9414 | 2
148 | Classroom | 592 | 39 |  | 844 | 19 | 19 | Unit Ventilator | 6752 | 5.2607 | 2 | 5.2607 | 2
149 | Classroom | 385 | 25 |  | 799 | 18 | 18 | Unit Ventilator | 6392 | 3.6139 | 1 | 3.6139 | 1
150 | Science Lab | 611 | 40 |  | 1233 | 28 | 28 | Unit Ventilator | 9864 | 3.7165 | 1 | 3.7165 | 1
200 | Classroom |  | 0 | Yes | 566 | 12 | 12 |  | 4528 | unk | unk | 20 | 3
200 Office | Office |  | 0 | Yes | 374 | 8 | 8 |  | 2992 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 1085 | 24 | 24 |  | 8680 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 893 | 20 | 20 |  | 7144 | unk | unk | 20 | 3
203 | Classroom |  | 0 |  | 1029 | 23 | 0 |  | 8232 | unk | unk | unk | unk
205 | Classroom |  | 0 | Yes | 1575 | 35 | 35 |  | 12600 | unk | unk | 20 | 3
211 | Classroom |  | 0 | Yes | 930 | 21 | 21 |  | 7440 | unk | unk | 20 | 3
212 | Classroom |  | 0 | Yes | 600 | 13 | 13 |  | 4800 | unk | unk | 20 | 3
213 | Classroom |  | 0 | Yes | 870 | 19 | 19 |  | 6960 | unk | unk | 20 | 3
214 | Classroom |  | 0 | Yes | 1326 | 30 | 30 |  | 10608 | unk | unk | 20 | 3
215 | Classroom |  | 0 |  | 980 | 22 | 0 |  | 7840 | unk | unk | unk | unk
225 | Library | 0 | 0 |  | 1230 | 27 | 0 | Unit Ventilator | 9840 | 0 | 0 | 0 | 0
226 | Study Area | 0 | 0 |  | 3510 | 79 | 0 | Unit Ventilator | 28080 | 0 | 0 | 0 | 0
227 | Computer Lab | 0 | 0 |  | 980 | 22 | 0 | Unit Ventilator | 7840 | 0 | 0 | 0 | 0
228 | Mech. Room | 0 | 0 |  | 411 | 9 | 0 | Unit Ventilator | 3288 | 0 | 0 | 0 | 0
155A | Teachers Office | 0 | 0 |  | 948 | 21 | 0 | Unit Ventilator | 7584 | 0 | 0 | 0 | 0
156A | Teachers Office | 0 | 0 |  | 948 | 21 | 0 | Unit Ventilator | 7584 | 0 | 0 | 0 | 0
225A | Office | 0 | 0 |  | 948 | 21 | 0 | Unit Ventilator | 7584 | 0 | 0 | 0 | 0
225B | Office | 0 | 0 |  | 1029 | 23 | 0 | Unit Ventilator | 8232 | 0 | 0 | 0 | 0
225C | Storage | 0 | 0 |  | 1000 | 22 | 0 | Unit Ventilator | 8000 | 0 | 0 | 0 | 0
225D | Office | 0 | 0 |  | 299 | 6 | 0 | Unit Ventilator | 2392 | 0 | 0 | 0 | 0
Computer Lab A | Lab |  | 0 |  | 2640 | 60 | 0 |  | 21120 | unk | unk | unk | unk
Computer Lab B | Lab |  | 0 |  | 2067 | 46 | 0 |  | 16536 | unk | unk | unk | unk
Computer Lab C | Lab |  | 0 |  | 2262 | 51 | 0 |  | 18096 | unk | unk | unk | unk
Main Office | Office |  | 0 | Yes | 875 | 19 | 19 |  | 7000 | unk | unk | 20 | 3
Principal | Office |  | 0 | Yes | 270 | 6 | 6 | Mobile Mini | 2160 | unk | unk | 20 | 3
Vice Principal | Office |  | 0 | Yes | 144 | 3 | 3 | Mobile Mini | 1152 | unk | unk | 20 | 3
Vice Principal | Office |  | 0 | Yes | 144 | 3 | 3 | Mobile Mini | 1152 | unk | unk | 20 | 3
Vice Principal | Office |  | 0 | Yes | 153 | 3 | 3 | Mobile Mini | 1224 | unk | unk | 20 | 3
- | Boys Gym | 0 | 0 |  | 5418 | 123 | 0 | Unit Ventilator | 43344 | 0 | 0 | 0 | 0
- | Boys Locker Room | 0 | 0 |  | 1824 | 41 | 0 | Unit Ventilator | 14592 | 0 | 0 | 0 | 0
- | Corridor/Hall | 1107 | 73 |  | 435 | 9 | 9 | Unit Ventilator | 3480 | 19.0862 | 3 | 19.0862 | 3
Cafeteria 1 | Dining | 0 | 0 |  | 2179 | 49 | 0 | Unit Ventilator | 17432 | 0 | 0 | 0 | 0
Cafeteria 2 | Dining |  | 0 |  | 2179 | 49 | 0 |  | 17432 | unk | unk | unk | unk
Cafeteria 3 | Dining |  | 0 |  | 2179 | 49 | 0 |  | 17432 | unk | unk | unk | unk
Cafeteria 4 | Dining |  | 0 |  | 2179 | 49 | 0 |  | 17432 | unk | unk | unk | unk
- | Girls Gym | 4087 | 272 | Yes | 5418 | 123 | 123 | Air Handling Unit | 43344 | 5.6575 | 2 | 25.6575 | 4
- | IPO Bathrooms | 129 | 8 |  | 411 | 9 | 8 | Unit Ventilator | 3288 | 2.354 | 1 | 2.354 | 1
- | IPO Office 1 |  | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | unk | unk | unk | unk
- | IPO Office 1 | 40 | 2 |  | 435 | 9 | 2 | Unit Ventilator | 3480 | 0.68966 | 0 | 0.68966 | 0
- | IPO Office 3 | 46 | 3 |  | 435 | 9 | 3 | Unit Ventilator | 3480 | 0.7931 | 0 | 0.7931 | 0
- | Lounge | 104 | 6 |  | 485 | 11 | 6 | Unit Ventilator | 3880 | 1.6082 | 1 | 1.6082 | 1
Sheet Last Modified: | 2021-03-12 | [8 empty] | unk | unk | unk | unk
School: | New Commodore John Barry Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | Exhaust | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Room |  | 0 | Yes | 425 | 9 | 9 | Rooftop Unit | 3400 | unk | unk | 20 | 3
104 | Room | 116 | 7 | Yes | 1008 | 22 | 22 | Rooftop Unit | 8064 | 0.8631 | 0 | 20.8631 | 3
105 | Room | 133 | 8 | Yes | 1134 | 25 | 25 | Rooftop Unit | 9072 | 0.87963 | 0 | 20.8796 | 3
106 | Room |  | 0 | Yes | 1140 | 25 | 25 | Rooftop Unit | 9120 | unk | unk | 20 | 3
107 | Room | 308 | 20 |  | 1118 | 25 | 20 | Rooftop Unit | 8944 | 2.0662 | 1 | 2.0662 | 1
108 | Room | 303 | 20 |  | 1140 | 25 | 20 | Rooftop Unit | 9120 | 1.9934 | 1 | 1.9934 | 1
109 | Room | 1254 | 83 |  | 2100 | 47 | 47 | Rooftop Unit | 16800 | 4.4786 | 2 | 4.4786 | 2
116 | Room | 125 | 8 |  |  | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
202 | Room | 147 | 9 | Yes | 551 | 12 | 12 | Rooftop Unit | 4408 | 2.0009 | 1 | 22.0009 | 3
203 | Room | 148 | 9 | Yes | 551 | 12 | 12 | Rooftop Unit | 4408 | 2.0145 | 1 | 22.0145 | 3
204 | Room | 139 | 9 | Yes | 418 | 9 | 9 | Rooftop Unit | 3344 | 2.494 | 1 | 22.494 | 3
205 | Room | 202 | 13 | Yes | 551 | 12 | 12 | Rooftop Unit | 4408 | 2.7495 | 1 | 22.7495 | 3
206 | Room | 145 | 9 | Yes | 728 | 16 | 16 | Rooftop Unit | 5824 | 1.4938 | 1 | 21.4938 | 3
207 | Room | 185 | 12 | Yes | 728 | 16 | 16 | Rooftop Unit | 5824 | 1.9059 | 1 | 21.9059 | 3
208 | Room | 139 | 9 | Yes | 728 | 16 | 16 | Rooftop Unit | 5824 | 1.432 | 1 | 21.432 | 3
209 | Room | 313 | 20 |  | 728 | 16 | 16 | Rooftop Unit | 5824 | 3.2246 | 1 | 3.2246 | 1
210 | Room | 272 | 18 |  | 630 | 14 | 14 | Rooftop Unit | 5040 | 3.2381 | 1 | 3.2381 | 1
211 | Room | 192 | 12 |  | 756 | 17 | 12 | Rooftop Unit | 6048 | 1.9048 | 1 | 1.9048 | 1
212 | Room | 154 | 10 | Yes | 900 | 20 | 20 | Rooftop Unit | 7200 | 1.2833 | 1 | 21.2833 | 3
213 | Room | 130 | 8 | Yes | 900 | 20 | 20 | Rooftop Unit | 7200 | 1.0833 | 1 | 21.0833 | 3
214 | Room | 268 | 17 |  | 812 | 18 | 17 | Rooftop Unit | 6496 | 2.4754 | 1 | 2.4754 | 1
215 | Room | 219 | 14 | Yes | 756 | 17 | 17 | Rooftop Unit | 6048 | 2.1726 | 1 | 22.1726 | 3
216 | Room | 223 | 14 | Yes | 756 | 17 | 17 | Rooftop Unit | 6048 | 2.2123 | 1 | 22.2123 | 3
301 | Room | 210 | 14 |  | 630 | 14 | 14 | Rooftop Unit | 5040 | 2.5 | 1 | 2.5 | 1
302A | Room |  | 0 |  | 104 | 2 | 0 | Rooftop Unit | 832 | unk | unk | unk | unk
302B | Room |  | 0 |  | 117 | 2 | 0 | Rooftop Unit | 936 | unk | unk | unk | unk
302C | Room |  | 0 |  | 104 | 2 | 0 | Rooftop Unit | 832 | unk | unk | unk | unk
303 | Room | 99 | 6 |  | 651 | 14 | 6 | Rooftop Unit | 5208 | 1.1406 | 1 | 1.1406 | 1
304 | Room |  | 0 |  | 110 | 2 | 0 | Rooftop Unit | 880 | unk | unk | unk | unk
305 | Room | 237 | 15 |  | 756 | 17 | 15 | Rooftop Unit | 6048 | 2.3512 | 1 | 2.3512 | 1
306 | Room | 156 | 10 |  | 756 | 17 | 10 | Rooftop Unit | 6048 | 1.5476 | 1 | 1.5476 | 1
307 | Room | 265 | 17 |  | 784 | 17 | 17 | Rooftop Unit | 6272 | 2.5351 | 1 | 2.5351 | 1
308 | Room | 192 | 12 | Yes | 864 | 19 | 19 | Rooftop Unit | 6912 | 1.6667 | 1 | 21.6667 | 3
309 | Room | 208 | 13 |  | 810 | 18 | 13 | Rooftop Unit | 6480 | 1.9259 | 1 | 1.9259 | 1
310 | Room | 296 | 19 |  | 810 | 18 | 18 | Rooftop Unit | 6480 | 2.7407 | 1 | 2.7407 | 1
311 | Room | 249 | 16 |  | 812 | 18 | 16 | Rooftop Unit | 6496 | 2.2999 | 1 | 2.2999 | 1
312 | Room | 210 | 14 |  | 840 | 19 | 14 | Rooftop Unit | 6720 | 1.875 | 1 | 1.875 | 1
313 | Room | 96 | 6 |  | 810 | 18 | 6 | Rooftop Unit | 6480 | 0.88889 | 0 | 0.88889 | 0
314 | Room | 219 | 14 |  | 810 | 18 | 14 | Rooftop Unit | 6480 | 2.0278 | 1 | 2.0278 | 1
315 | Room | 105 | 7 |  | 812 | 18 | 7 | Rooftop Unit | 6496 | 0.96983 | 0 | 0.96983 | 0
316 | Room | 143 | 9 |  | 812 | 18 | 9 | Rooftop Unit | 6496 | 1.3208 | 1 | 1.3208 | 1
320 | Room | 212 | 14 |  | 620 | 14 | 14 | Rooftop Unit | 4960 | 2.5645 | 1 | 2.5645 | 1
323 | Room | 230 | 15 |  | 620 | 14 | 14 | Rooftop Unit | 4960 | 2.7823 | 1 | 2.7823 | 1
401 | Room | 215 | 14 | Yes | 1260 | 28 | 28 | Rooftop Unit | 10080 | 1.2798 | 1 | 21.2798 | 3
403A | Room |  | 0 |  | 240 | 5 | 0 | Rooftop Unit | 1920 | unk | unk | unk | unk
403B | Room |  | 0 |  | 210 | 4 | 0 | Rooftop Unit | 1680 | unk | unk | unk | unk
403C | Room |  | 0 |  | 240 | 5 | 0 | Rooftop Unit | 1920 | unk | unk | unk | unk
404 | Room |  | 0 | Yes | 1024 | 23 | 23 | Rooftop Unit | 8192 | unk | unk | 20 | 3
405 | Room | 382 | 25 |  | 1476 | 33 | 25 | Rooftop Unit | 11808 | 1.9411 | 1 | 1.9411 | 1
406 | Room |  | 0 |  | 1462 | 33 | 0 | Rooftop Unit | 11696 | unk | unk | unk | unk
407 | Room |  | 0 |  | 1054 | 23 | 0 | Rooftop Unit | 8432 | unk | unk | unk | unk
408 | Room | 561 | 37 |  | 1280 | 29 | 29 | Rooftop Unit | 10240 | 3.2871 | 1 | 3.2871 | 1
409 | Room | 213 | 14 |  | 1160 | 26 | 14 | Rooftop Unit | 9280 | 1.3772 | 1 | 1.3772 | 1
- | Café | 593 | 39 |  | 4800 | 109 | 39 | Rooftop Unit | 38400 | 0.92656 | 0 | 0.92656 | 0
- | Gym |  | 0 | Yes | 6240 | 141 | 141 | Rooftop Unit | 49920 | unk | unk | 20 | 3
- | Library |  | 0 | Yes | 1961 | 44 | 44 | Rooftop Unit | 15688 | unk | unk | 20 | 3
- | Main Office |  | 0 |  | 924 | 21 | 0 | Rooftop Unit | 7392 | unk | unk | unk | unk
- | Nurse's Office |  | 0 |  | 143 | 3 | 0 | Rooftop Unit | 1144 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-16 | [8 empty] | unk | unk | unk | unk
School: | Clara Barton | [8 empty] | unk | unk | unk | unk
Vendor: | [9 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B7 | Classroom | 0 | 0 | Yes | 601 | 13 | 13 | House Fan | 4808 | 0 | 0 | 20 | 3
B8 | Classroom | 0 | 0 | Yes | 848 | 19 | 19 | House Fan | 6784 | 0 | 0 | 20 | 3
B10 | Classroom | 0 | 0 |  | 686 | 15 | 0 | House Fan | 5488 | 0 | 0 | 0 | 0
B11 | Classroom | 0 | 0 |  | 806 | 18 | 0 | House Fan | 6448 | 0 | 0 | 0 | 0
100 | Classroom | 0 | 0 | Yes | 742 | 16 | 16 | House Fan | 5936 | 0 | 0 | 20 | 3
101 | Classroom | 0 | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | 0 | 0 | 20 | 3
102 | Office | 0 | 0 | Yes | 452 | 10 | 10 | House Fan | 3616 | 0 | 0 | 20 | 3
102 A | Classroom | 0 | 0 |  | 70 | 1 | 0 | House Fan | 560 | 0 | 0 | 0 | 0
102 B | Office | 0 | 0 |  | 122 | 2 | 0 | House Fan | 976 | 0 | 0 | 0 | 0
103 C | Office | 0 | 0 |  | 90 | 2 | 0 | House Fan | 720 | 0 | 0 | 0 | 0
103 | Classroom | 0 | 0 | Yes | 627 | 14 | 14 | House Fan | 5016 | 0 | 0 | 20 | 3
104 | Library | 0 | 0 | Yes | 645 | 14 | 14 | House Fan | 5160 | 0 | 0 | 20 | 3
105 | Library | 0 | 0 | Yes | 658 | 14 | 14 | House Fan | 5264 | 0 | 0 | 20 | 3
106 | Library | 0 | 0 | Yes | 653 | 14 | 14 | House Fan | 5224 | 0 | 0 | 20 | 3
107 | Classroom | 0 | 0 | Yes | 632 | 14 | 14 | House Fan | 5056 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 640 | 14 | 14 | House Fan | 5120 | 0 | 0 | 20 | 3
109 | Classroom | 0 | 0 | Yes | 694 | 15 | 15 | House Fan | 5552 | 0 | 0 | 20 | 3
110 | Classroom | 0 | 0 | Yes | 683 | 15 | 15 | House Fan | 5464 | 0 | 0 | 20 | 3
111 | Classroom | 0 | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | 0 | 0 | 20 | 3
112 | Nurse's Office | 0 | 0 | Yes | 118 | 2 | 2 | House Fan | 944 | 0 | 0 | 20 | 3
- | Main Office | 0 | 0 | Yes | 297 | 6 | 6 | House Fan | 2376 | 0 | 0 | 20 | 3
- | Principal's Office | 0 | 0 | Yes | 159 | 3 | 3 | House Fan | 1272 | 0 | 0 | 20 | 3
200 | Classroom | 0 | 0 | Yes | 663 | 15 | 15 | House Fan | 5304 | 0 | 0 | 20 | 3
200 A | Office | 0 | 0 | Yes | 226 | 5 | 5 | House Fan | 1808 | 0 | 0 | 20 | 3
200 B | Classroom | 0 | 0 | Yes | 158 | 3 | 3 | House Fan | 1264 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 635 | 14 | 14 | House Fan | 5080 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0 | 20 | 3
203 | Classroom | 0 | 0 | Yes | 645 | 14 | 14 | House Fan | 5160 | 0 | 0 | 20 | 3
204 | Classroom | 0 | 0 | Yes | 624 | 14 | 14 | House Fan | 4992 | 0 | 0 | 20 | 3
205 | Classroom | 0 | 0 | Yes | 624 | 14 | 14 | House Fan | 4992 | 0 | 0 | 20 | 3
206 | Classroom | 0 | 0 | Yes | 653 | 14 | 14 | House Fan | 5224 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 664 | 15 | 15 | House Fan | 5312 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 638 | 14 | 14 | House Fan | 5104 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 | Yes | 662 | 15 | 15 | House Fan | 5296 | 0 | 0 | 20 | 3
210 | Classroom | 0 | 0 | Yes | 694 | 15 | 15 | House Fan | 5552 | 0 | 0 | 20 | 3
211 | Classroom | 0 | 0 | Yes | 616 | 14 | 14 | House Fan | 4928 | 0 | 0 | 20 | 3
211 A | Office | 0 | 0 |  | 115 | 2 | 0 | House Fan | 920 | 0 | 0 | 0 | 0
- | Teacher Lounge | 0 | 0 | Yes | 340 | 7 | 7 | House Fan | 2720 | 0 | 0 | 20 | 3
215 | Classroom |  | 0 | Yes | 345 | 7 | 7 | house Fan | 2760 | unk | unk | 20 | 3
300 | Classroom | 0 | 0 | Yes | 640 | 14 | 14 | House Fan | 5120 | 0 | 0 | 20 | 3
300A | Office |  | 0 | Yes | 264 | 6 | 6 | House Fan | 2112 | unk | unk | 20 | 3
301 | Classroom | 0 | 0 | Yes | 668 | 15 | 15 | House Fan | 5344 | 0 | 0 | 20 | 3
301 A | Office | 0 | 0 |  | 203 | 4 | 0 | House Fan | 1624 | 0 | 0 | 0 | 0
302 | Classroom | 0 | 0 | Yes | 639 | 14 | 14 | House Fan | 5112 | 0 | 0 | 20 | 3
303 | Classroom | 0 | 0 | Yes | 692 | 15 | 15 | House Fan | 5536 | 0 | 0 | 20 | 3
304 | Classroom | 0 | 0 | Yes | 627 | 14 | 14 | House Fan | 5016 | 0 | 0 | 20 | 3
305 | Classroom | 0 | 0 | Yes | 655 | 14 | 14 | House Fan | 5240 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 664 | 15 | 15 | House Fan | 5312 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 | Yes | 642 | 14 | 14 | House Fan | 5136 | 0 | 0 | 20 | 3
308 | Classroom | 0 | 0 | Yes | 663 | 15 | 15 | House Fan | 5304 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 | Yes | 605 | 13 | 13 | House Fan | 4840 | 0 | 0 | 20 | 3
310 | Classroom | 0 | 0 | Yes | 673 | 15 | 15 | House Fan | 5384 | 0 | 0 | 20 | 3
311 | Classroom | 0 | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | 0 | 0 | 20 | 3
312 | Classroom | 0 | 0 |  | 634 | 14 | 0 | House Fan | 5072 | 0 | 0 | 0 | 0
312 A | Office | 0 | 0 |  | 112 | 2 | 0 | House Fan | 896 | 0 | 0 | 0 | 0
- | Counselor Office |  | 0 | Yes | 152 | 3 | 3 | House Fan | 1216 | unk | unk | 20 | 3
- | Gym | 0 | 0 | Yes | 3436 | 78 | 78 | N/A | 27488 | 0 | 0 | 20 | 3
- | Kitchen | 0 | 0 | Yes | 1140 | 25 | 25 | House Fan | 9120 | 0 | 0 | 20 | 3
- | Cafeteria | 0 | 0 | Yes | 1478 | 33 | 33 | House Fan | 11824 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | John Bartram High School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Part 2 | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 590 | 39 |  | 1196 | 27 | 27 | Unit Ventilator | 9568 | 3.6998 | 1 | 3.6998 | 1
102 | Classroom | 359 | 23 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 3.1639 | 1 | 3.1639 | 1
103 | Classroom | 759 | 50 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 6.875 | 2 | 6.875 | 2
104 | Classroom | 646 | 43 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.2663 | 2 | 5.2663 | 2
105 | Classroom | 582 | 38 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 5.1293 | 2 | 5.1293 | 2
106 | Classroom | 696 | 46 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 5.2781 | 2 | 5.2781 | 2
107 | Classroom | 980 | 65 |  | 946 | 21 | 21 | Unit Ventilator | 7568 | 7.7696 | 2 | 7.7696 | 2
108 | Classroom | 575 | 38 |  | 1012 | 23 | 23 | Unit Ventilator | 8096 | 4.2614 | 2 | 4.2614 | 2
110 | Office | 0 | 0 |  | 238 | 5 | 0 | Unit Ventilator | 1904 | 0 | 0 | 0 | 0
111 | Classroom | 418 | 27 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 3.8944 | 1 | 3.8944 | 1
112 | Room | 416 | 27 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 3.3913 | 1 | 3.3913 | 1
113 | Classroom | 416 | 27 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.5217 | 2 | 4.5217 | 2
115 | Classroom | 343 | 22 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.7283 | 1 | 3.7283 | 1
116 | Classroom | 467 | 31 |  | 1357 | 30 | 30 | Unit Ventilator | 10856 | 2.5811 | 1 | 2.5811 | 1
117 | Classroom | 352 | 23 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.8261 | 1 | 3.8261 | 1
118 | Classroom | 325 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5326 | 1 | 3.5326 | 1
119 | Classroom | 346 | 23 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.7609 | 1 | 3.7609 | 1
120 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Unit Ventilator | 5520 | 0 | 0 | 0 | 0
121 | Office | 0 | 0 | Yes | 227 | 5 | 5 | Unit Ventilator | 1816 | 0 | 0 | 20 | 3
123 | Room | 498 | 33 |  | 1242 | 28 | 28 | Unit Ventilator | 9936 | 3.0072 | 1 | 3.0072 | 1
124 | Office | 0 | 0 | Yes | 309 | 7 | 7 | Unit Ventilator | 2472 | 0 | 0 | 20 | 3
124A | Office | 0 | 0 | Yes | 218 | 4 | 4 | Unit Ventilator | 1744 | 0 | 0 | 20 | 3
125 | Room | 356 | 23 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.8696 | 1 | 3.8696 | 1
126 | Room | 339 | 22 |  | 276 | 6 | 6 | Unit Ventilator | 2208 | 9.212 | 2 | 9.212 | 2
127 | Room | 349 | 23 |  | 644 | 14 | 14 | Unit Ventilator | 5152 | 4.0644 | 2 | 4.0644 | 2
127a | Room | 331 | 22 |  | 345 | 7 | 7 | Unit Ventilator | 2760 | 7.1957 | 2 | 7.1957 | 2
128 | Office | 0 | 0 |  | 230 | 5 | 0 | Unit Ventilator | 1840 | 0 | 0 | 0 | 0
130 | Room | 288 | 19 |  | 375 | 8 | 8 | Unit Ventilator | 3000 | 5.76 | 2 | 5.76 | 2
130A | Office | 0 | 0 |  | 236 | 5 | 0 | Unit Ventilator | 1888 | 0 | 0 | 0 | 0
131 | Office | 0 | 0 | Yes | 237 | 5 | 5 | Unit Ventilator | 1896 | 0 | 0 | 20 | 3
133 | Office | 0 | 0 | Yes | 333 | 7 | 7 | Unit Ventilator | 2664 | 0 | 0 | 20 | 3
134 | Main Office | 593 | 39 |  | 1656 | 37 | 37 | Unit Ventilator | 13248 | 2.6857 | 1 | 2.6857 | 1
201 | Classroom | 617 | 41 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 4.679 | 2 | 4.679 | 2
202 | Classroom | 282 | 18 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 2.6273 | 1 | 2.6273 | 1
203 | Classroom | 632 | 42 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 4.7927 | 2 | 4.7927 | 2
204 | Classroom | 309 | 20 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.3587 | 1 | 3.3587 | 1
205 | Classroom | 516 | 34 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 3.913 | 1 | 3.913 | 1
206 | Classroom | 324 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5217 | 1 | 3.5217 | 1
207 | Classroom | 363 | 24 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 2.7528 | 1 | 2.7528 | 1
208 | Classroom | 291 | 19 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.163 | 1 | 3.163 | 1
209 | Classroom | 0 | 0 | Yes | 309 | 7 | 7 | Unit Ventilator | 2472 | 0 | 0 | 20 | 3
210 | Classroom | 297 | 19 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.2283 | 1 | 3.2283 | 1
211 | Room | 0 | 0 | Yes | 321 | 7 | 7 | Unit Ventilator | 2568 | 0 | 0 | 20 | 3
211A | copy Room | 0 | 0 |  | 227 | 5 | 0 | Unit Ventilator | 1816 | 0 | 0 | 0 | 0
214 | Classroom | 370 | 24 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.0217 | 2 | 4.0217 | 2
215 | Classroom | 337 | 22 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.663 | 1 | 3.663 | 1
216 | Classroom | 327 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5543 | 1 | 3.5543 | 1
217 | Classroom | 282 | 18 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.0652 | 1 | 3.0652 | 1
218 | Classroom | 563 | 37 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 6.1196 | 2 | 6.1196 | 2
219 | Office | 0 | 0 | Yes | 272 | 6 | 6 | Unit Ventilator | 2176 | 0 | 0 | 20 | 3
220A | Office | 0 | 0 | Yes | 169 | 3 | 3 | Unit Ventilator | 1352 | 0 | 0 | 20 | 3
221 | Classroom | 97 | 6 | Yes | 851 | 19 | 19 | Unit Ventilator | 6808 | 0.85488 | 0 | 20.8549 | 3
222 | Classroom | 320 | 21 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 2.8202 | 1 | 2.8202 | 1
223 | Classroom | 329 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5761 | 1 | 3.5761 | 1
224 | Classroom | 302 | 20 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.2826 | 1 | 3.2826 | 1
225 | Classroom | 437 | 29 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.75 | 2 | 4.75 | 2
226 | Classroom | 315 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.4239 | 1 | 3.4239 | 1
227 | Classroom | 299 | 19 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.25 | 1 | 3.25 | 1
228 | Classroom | 302 | 20 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.2826 | 1 | 3.2826 | 1
229 | Classroom | 407 | 27 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.4239 | 2 | 4.4239 | 2
230 | Classroom | 290 | 19 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.1522 | 1 | 3.1522 | 1
231 | Classroom | 331 | 22 |  | 322 | 7 | 7 | Unit Ventilator | 2576 | 7.7096 | 2 | 7.7096 | 2
232 | Classroom | 0 | 0 | Yes | 690 | 15 | 15 | Unit Ventilator | 5520 | 0 | 0 | 20 | 3
234 | Office | 0 | 0 | Yes | 298 | 6 | 6 | Unit Ventilator | 2384 | 0 | 0 | 20 | 3
236 | Office | 0 | 0 | Yes | 299 | 6 | 6 | Unit Ventilator | 2392 | 0 | 0 | 20 | 3
236A | Copy room | 0 | 0 |  | 203 | 4 | 0 | Unit Ventilator | 1624 | 0 | 0 | 0 | 0
301 | Classroom |  | 0 |  | 816 | 18 | 0 | Air Handling Unit | 6528 | unk | unk | unk | unk
302 | Classroom |  | 0 |  | 816 | 18 | 0 | Air Handling Unit | 6528 | unk | unk | unk | unk
305 | Classroom |  | 0 |  | 1000 | 22 | 0 | Air Handling Unit | 8000 | unk | unk | unk | unk
306 | Classroom |  | 0 |  | 136 | 3 | 0 | Air Handling Unit | 1088 | unk | unk | unk | unk
307 | Classroom |  | 0 |  | 696 | 15 | 0 | Air Handling Unit | 5568 | unk | unk | unk | unk
309 | Classroom |  | 0 |  | 225 | 5 | 0 | Air Handling Unit | 1800 | unk | unk | unk | unk
313 | Faculty | 309 | 20 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.7855 | 1 | 2.7855 | 1
320 | Classroom | 618 | 41 |  | 1080 | 24 | 24 | Unit Ventilator | 8640 | 4.2917 | 2 | 4.2917 | 2
321 | Classroom | 574 | 38 |  | 1100 | 25 | 25 | Unit Ventilator | 8800 | 3.9136 | 1 | 3.9136 | 1
324 | Classroom | 553 | 36 |  | 945 | 21 | 21 | Unit Ventilator | 7560 | 4.3889 | 2 | 4.3889 | 2
325 | Classroom | 394 | 26 |  | 1080 | 24 | 24 | Unit Ventilator | 8640 | 2.7361 | 1 | 2.7361 | 1
328 | Room | 0 | 0 | Yes | 169 | 3 | 3 | Unit Ventilator | 1352 | 0 | 0 | 20 | 3
331 | Classroom | 351 | 23 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 3.2702 | 1 | 3.2702 | 1
332 | Classroom | 361 | 24 |  | 1081 | 24 | 24 | Unit Ventilator | 8648 | 2.5046 | 1 | 2.5046 | 1
333 | Classroom | 321 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.4891 | 1 | 3.4891 | 1
334 | Classroom | 284 | 18 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.087 | 1 | 3.087 | 1
335 | Classroom | 286 | 19 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 3.2159 | 1 | 3.2159 | 1
336 | Classroom | 295 | 19 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.2065 | 1 | 3.2065 | 1
337 | Classroom | 86 | 5 | Yes | 690 | 15 | 15 | Unit Ventilator | 5520 | 0.93478 | 0 | 20.9348 | 3
338 | Classroom | 280 | 18 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 3.1484 | 1 | 3.1484 | 1
339 | Classroom | 366 | 24 |  | 506 | 11 | 11 | Unit Ventilator | 4048 | 5.4249 | 2 | 5.4249 | 2
340 | Classroom | 274 | 18 |  | 484 | 11 | 11 | Unit Ventilator | 3872 | 4.2459 | 2 | 4.2459 | 2
341 | Classroom | 356 | 23 |  | 484 | 11 | 11 | Unit Ventilator | 3872 | 5.5165 | 2 | 5.5165 | 2
342 | Classroom | 289 | 19 |  | 529 | 12 | 12 | Unit Ventilator | 4232 | 4.0974 | 2 | 4.0974 | 2
344 | Room | 0 | 0 | Yes | 233 | 5 | 5 | Unit Ventilator | 1864 | 0 | 0 | 20 | 3
346 | Classroom | 291 | 19 |  | 675 | 15 | 15 | Unit Ventilator | 5400 | 3.2333 | 1 | 3.2333 | 1
B12 | Room | 0 | 0 |  | 383 | 8 | 0 | Unit Ventilator | 3064 | 0 | 0 | 0 | 0
B13 | BE Office | 0 | 0 |  | 238 | 5 | 0 | Unit Ventilator | 1904 | 0 | 0 | 0 | 0
B17 | Room | 0 | 0 |  | 209 | 4 | 0 | Unit Ventilator | 1672 | 0 | 0 | 0 | 0
Bc | Room | 0 | 0 | Yes | 244 | 5 | 5 | Unit Ventilator | 1952 | 0 | 0 | 20 | 3
C1 | Classroom | 398 | 26 |  | 1000 | 22 | 22 | Unit Ventilator | 8000 | 2.985 | 1 | 2.985 | 1
C2 | Classroom | 0 | 0 |  | 1000 | 22 | 0 | Unit Ventilator | 8000 | 0 | 0 | 0 | 0
C3 | Classroom | 1212 | 80 |  | 1000 | 22 | 22 | Unit Ventilator | 8000 | 9.09 | 2 | 9.09 | 2
C4 | Classroom | 0 | 0 |  | 1000 | 22 | 0 | Unit Ventilator | 8000 | 0 | 0 | 0 | 0
C5 | Classroom | 0 | 0 |  | 1000 | 22 | 0 | Unit Ventilator | 8000 | 0 | 0 | 0 | 0
C7 | Classroom | 881 | 58 |  | 968 | 22 | 22 | Unit Ventilator | 7744 | 6.8259 | 2 | 6.8259 | 2
C7A | Classroom | 0 | 0 |  | 909 | 20 | 0 | Unit Ventilator | 7272 | 0 | 0 | 0 | 0
- | School police | 0 | 0 | Yes | 192 | 4 | 4 | Unit Ventilator | 1536 | 0 | 0 | 20 | 3
- | 3rd Floor C Wing | 0 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Auditorium | 0 | 0 |  | 11625 | 264 | 0 | Air Handling Unit | 93000 | 0 | 0 | 0 | 0
- | Boys Gym | 5931 | 395 |  | 5280 | 120 | 120 | Air Handling Unit | 42240 | 8.4247 | 2 | 8.4247 | 2
- | Library | 866 | 57 |  | 4526 | 102 | 57 | Unit Ventilator | 36208 | 1.435 | 1 | 1.435 | 1
- | Corridor | 0 | 0 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
- | Girls Gym | 6806 | 453 |  | 5280 | 120 | 120 | Air Handling Unit | 42240 | 9.6676 | 2 | 9.6676 | 2
- | Nurse Area | 255 | 17 |  | 936 | 21 | 17 | Unit Ventilator | 7488 | 2.0433 | 1 | 2.0433 | 1
- | Cafeteria | 0 | 0 | Yes | 6262 | 142 | 142 | Unit Ventilator | 50096 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-05 | [8 empty] | unk | unk | unk | unk
School: | Mary McLeod Bethune School | [8 empty] | unk | unk | unk | unk
Vendor: | Capital | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Classroom | 300 | 20 |  | 1350 | 30 | 20 | Unit Ventilator | 10800 | 1.6667 | 1 | 1.6667 | 1
2 | Classroom | 278 | 18 |  | 1350 | 30 | 18 | Unit Ventilator | 10800 | 1.5444 | 1 | 1.5444 | 1
3 | Classroom | 395 | 26 |  | 1350 | 30 | 26 | Unit Ventilator | 10800 | 2.1944 | 1 | 2.1944 | 1
4 | Classroom | 425 | 28 |  | 1296 | 29 | 28 | Unit Ventilator | 10368 | 2.4595 | 1 | 2.4595 | 1
5 | Classroom | 314 | 20 |  | 1296 | 29 | 20 | Unit Ventilator | 10368 | 1.8171 | 1 | 1.8171 | 1
100 | Classroom | 614 | 40 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 4.7969 | 2 | 4.7969 | 2
101 | Classroom | 597 | 39 |  | 1024 | 23 | 23 | Unit Ventilator | 8192 | 4.3726 | 2 | 4.3726 | 2
101A | Instructional Storage | 0 | 0 |  |  | 0 | 0 | HUV |  | unk | unk | unk | unk
102 | Classroom | 560 | 37 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 6.087 | 2 | 6.087 | 2
103 | Classroom | 555 | 37 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 6.0326 | 2 | 6.0326 | 2
104 | Classroom | 575 | 38 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 6.25 | 2 | 6.25 | 2
105 | Classroom | 618 | 41 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 6.7174 | 2 | 6.7174 | 2
106 | Class Area | 163 | 10 |  | 625 | 14 | 10 | Unit Ventilator | 5000 | 1.956 | 1 | 1.956 | 1
106A | IT room | 280 | 18 |  | 304 | 6 | 6 | Unit Ventilator | 2432 | 6.9079 | 2 | 6.9079 | 2
107 | Class Area | 155 | 10 |  | 1050 | 23 | 10 | Unit Ventilator | 8400 | 1.1071 | 1 | 1.1071 | 1
108 | Class Area | 141 | 9 |  | 1050 | 23 | 9 | Unit Ventilator | 8400 | 1.0071 | 1 | 1.0071 | 1
109 | Class Area | 143 | 9 |  | 625 | 14 | 9 | Unit Ventilator | 5000 | 1.716 | 1 | 1.716 | 1
110 | Class Area | 159 | 10 |  | 690 | 15 | 10 | Unit Ventilator | 5520 | 1.7283 | 1 | 1.7283 | 1
111 | Class Area | 164 | 10 |  | 690 | 15 | 10 | Unit Ventilator | 5520 | 1.7826 | 1 | 1.7826 | 1
112 | Class Area | 142 | 9 |  | 690 | 15 | 9 | Unit Ventilator | 5520 | 1.5435 | 1 | 1.5435 | 1
113 | Class Area | 149 | 9 |  | 690 | 15 | 9 | Unit Ventilator | 5520 | 1.6196 | 1 | 1.6196 | 1
114 | Class Area | 137 | 9 |  | 690 | 15 | 9 | Unit Ventilator | 5520 | 1.4891 | 1 | 1.4891 | 1
114A | Team Planning | 0 | 0 |  | 360 | 8 | 0 | HUV | 2880 | 0 | 0 | 0 | 0
115 | Class | 141 | 9 |  | 690 | 15 | 9 | Unit Ventilator | 5520 | 1.5326 | 1 | 1.5326 | 1
118D | Main Office | 0 | 0 |  | 150 | 3 | 0 | Unit Ventilator | 1200 | 0 | 0 | 0 | 0
119A | Instructional Storage | 0 | 0 |  |  | 0 | 0 | HUV |  | unk | unk | unk | unk
119B | Building Engineer's Office | 305 | 20 |  | 450 | 10 | 10 | Unit Ventilator | 3600 | 5.0833 | 2 | 5.0833 | 2
120 | Instructional Materials Center | 303 | 20 |  | 2520 | 57 | 20 | Unit Ventilator | 20160 | 0.90179 | 0 | 0.90179 | 0
122 | Main Office | 394 | 26 |  | 600 | 13 | 13 | Unit Ventilator | 4800 | 4.925 | 2 | 4.925 | 2
122C | Main Office | 301 | 20 |  | 130 | 2 | 2 | Unit Ventilator | 1040 | 17.3654 | 3 | 17.3654 | 3
122D | Principal's Office | 383 | 25 |  | 216 | 4 | 4 | Unit Ventilator | 1728 | 13.2986 | 3 | 13.2986 | 3
123 | Teacher's Dining | 355 | 23 |  | 594 | 13 | 13 | Unit Ventilator | 4752 | 4.4823 | 2 | 4.4823 | 2
123A | Teacher's Lounge | 298 | 19 |  | 270 | 6 | 6 | Unit Ventilator | 2160 | 8.2778 | 2 | 8.2778 | 2
127 | Corridor | 0 | 0 |  |  | 0 | 0 | HUV |  | unk | unk | unk | unk
150 | Storage | 163 | 10 |  | 360 | 8 | 8 | Unit Ventilator | 2880 | 3.3958 | 1 | 3.3958 | 1
153 | Corridor | 0 | 0 |  |  | 0 | 0 | HUV |  | unk | unk | unk | unk
165 | Gym Office | 152 | 10 |  | 130 | 2 | 2 | Unit Ventilator | 1040 | 8.7692 | 2 | 8.7692 | 2
184 | Examination | 153 | 10 |  | 130 | 2 | 2 | Unit Ventilator | 1040 | 8.8269 | 2 | 8.8269 | 2
200 | Classroom | 622 | 41 |  | 1350 | 30 | 30 | Unit Ventilator | 10800 | 3.4556 | 1 | 3.4556 | 1
201 | Classroom | 530 | 35 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.7609 | 2 | 5.7609 | 2
201A | Instructional Storage | 0 | 0 |  |  | 0 | 0 | HUV |  | unk | unk | unk | unk
202 | Classroom | 519 | 34 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.6413 | 2 | 5.6413 | 2
203 | Classroom | 434 | 28 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.7174 | 2 | 4.7174 | 2
204 | Classroom | 550 | 36 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.9783 | 2 | 5.9783 | 2
205 | Classroom | 436 | 29 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.7391 | 2 | 4.7391 | 2
206 | Classroom | 500 | 33 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.4348 | 2 | 5.4348 | 2
206A | Team Planning | 149 | 9 |  | 270 | 6 | 6 | Unit Ventilator | 2160 | 4.1389 | 2 | 4.1389 | 2
207 | Classroom | 327 | 21 |  | 945 | 21 | 21 | Unit Ventilator | 7560 | 2.5952 | 1 | 2.5952 | 1
208 | Corridor | 0 | 0 |  |  | 0 | 0 | HUV |  | unk | unk | unk | unk
208 | Classroom | 509 | 33 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.5326 | 2 | 5.5326 | 2
209 | Classroom | 552 | 36 |  | 625 | 14 | 14 | Unit Ventilator | 5000 | 6.624 | 2 | 6.624 | 2
210 | Classroom | 694 | 46 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 7.5435 | 2 | 7.5435 | 2
211 | Classroom | 531 | 35 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.7717 | 2 | 5.7717 | 2
212 | Classroom | 379 | 25 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.1196 | 2 | 4.1196 | 2
213 | Classroom | 688 | 45 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 7.4783 | 2 | 7.4783 | 2
214 | Classroom | 382 | 25 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.1522 | 2 | 4.1522 | 2
214A | Instructional Storage | 0 | 0 |  |  | 0 | 0 | HUV |  | unk | unk | unk | unk
215 | Classroom | 370 | 24 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.3036 | 1 | 3.3036 | 1
216 | Classroom | 388 | 25 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 3.6149 | 1 | 3.6149 | 1
217 | Classroom | 413 | 27 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.911 | 1 | 3.911 | 1
218 | Classroom | 328 | 21 |  | 625 | 14 | 14 | Unit Ventilator | 5000 | 3.936 | 1 | 3.936 | 1
218C | Classroom | 286 | 19 |  | 960 | 21 | 19 | Unit Ventilator | 7680 | 2.2344 | 1 | 2.2344 | 1
219 | Classroom | 862 | 57 |  | 1800 | 40 | 40 | Unit Ventilator | 14400 | 3.5917 | 1 | 3.5917 | 1
220 | Classroom | 980 | 65 |  | 1350 | 30 | 30 | Unit Ventilator | 10800 | 5.4444 | 2 | 5.4444 | 2
221 | Classroom | 342 | 22 |  | 625 | 14 | 14 | Unit Ventilator | 5000 | 4.104 | 2 | 4.104 | 2
234 | Corridor | 0 | 0 |  |  | 0 | 0 | HUV |  | unk | unk | unk | unk
244 | Counselor | 0 | 0 |  |  | 0 | 0 | HUV |  | unk | unk | unk | unk
- | Nurse's Office | 279 | 18 |  | 150 | 3 | 3 | Unit Ventilator | 1200 | 13.95 | 3 | 13.95 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | James G. Blaine Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers Retest | 2nd Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Gym / Cafe. | 1104 | 73 |  | 3749 | 85 | 73 | Air Handling Unit | 29992 | 2.2086 | 1 | 2.2086 | 1
- | Auditorium | 577 | 38 |  | 3161 | 71 | 38 | Air Handling Unit | 25288 | 1.369 | 1 | 1.369 | 1
100 | Classroom | 437 | 29 |  | 1415 | 32 | 29 | Unit Ventilator | 11320 | 2.3163 | 1 | 2.3163 | 1
101 | Classroom | 684 | 45 |  | 1476 | 33 | 33 | Unit Ventilator | 11808 | 3.4756 | 1 | 3.4756 | 1
102 | Classroom | 625 | 41 |  | 1460 | 33 | 33 | Unit Ventilator | 11680 | 3.2106 | 1 | 3.2106 | 1
103 | Classroom | 461 | 30 |  | 1465 | 33 | 30 | Unit Ventilator | 11720 | 2.3601 | 1 | 2.3601 | 1
104 | Classroom | 319 | 21 |  | 856 | 19 | 19 | Unit Ventilator | 6848 | 2.795 | 1 | 2.795 | 1
105 | Classroom | 306 | 20 |  | 655 | 14 | 14 | Unit Ventilator | 5240 | 3.5038 | 1 | 3.5038 | 1
106 | Classroom | 452 | 30 |  | 921 | 20 | 20 | Unit Ventilator | 7368 | 3.6808 | 1 | 3.6808 | 1
107 | Classroom | 274 | 18 |  | 970 | 22 | 18 | Unit Ventilator | 7760 | 2.1186 | 1 | 2.1186 | 1
108 | Custodial | 251 | 16 |  | 835 | 18 | 16 | Unit Ventilator | 6680 | 2.2545 | 1 | 2.2545 | 1
110 | Nurse |  | 0 | Yes | 452 | 10 | 10 | Unit Ventilator | 3616 | unk | unk | 20 | 3
200 | Classroom | 297 | 19 |  | 947 | 21 | 19 | Unit Ventilator | 7576 | 2.3522 | 1 | 2.3522 | 1
201 | Classroom | 246 | 16 |  | 649 | 14 | 14 | Unit Ventilator | 5192 | 2.8428 | 1 | 2.8428 | 1
202 | Classroom | 414 | 27 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 3.3173 | 1 | 3.3173 | 1
203 | Classroom | 230 | 15 |  | 937 | 21 | 15 | Unit Ventilator | 7496 | 1.841 | 1 | 1.841 | 1
204 | Classroom | 359 | 23 |  | 958 | 21 | 21 | Unit Ventilator | 7664 | 2.8105 | 1 | 2.8105 | 1
205 | Classroom | 286 | 19 |  | 937 | 21 | 19 | Unit Ventilator | 7496 | 2.2892 | 1 | 2.2892 | 1
206 | Classroom | 447 | 29 |  | 952 | 21 | 21 | Unit Ventilator | 7616 | 3.5215 | 1 | 3.5215 | 1
207 | Classroom | 291 | 19 |  | 956 | 21 | 19 | Unit Ventilator | 7648 | 2.2829 | 1 | 2.2829 | 1
208 | Classroom | 314 | 20 |  | 968 | 22 | 20 | Unit Ventilator | 7744 | 2.4329 | 1 | 2.4329 | 1
209 | Classroom | 349 | 23 |  | 975 | 22 | 22 | Unit Ventilator | 7800 | 2.6846 | 1 | 2.6846 | 1
210 | Classroom | 236 | 15 |  | 931 | 21 | 15 | Unit Ventilator | 7448 | 1.9012 | 1 | 1.9012 | 1
211 | Classroom | 287 | 19 |  | 982 | 22 | 19 | Unit Ventilator | 7856 | 2.192 | 1 | 2.192 | 1
212 | Classroom | 362 | 24 |  | 953 | 21 | 21 | Unit Ventilator | 7624 | 2.8489 | 1 | 2.8489 | 1
213 | Classroom | 296 | 19 |  | 957 | 21 | 19 | Unit Ventilator | 7656 | 2.3197 | 1 | 2.3197 | 1
214 | Classroom | 378 | 25 |  | 956 | 21 | 21 | Unit Ventilator | 7648 | 2.9655 | 1 | 2.9655 | 1
215 | Classroom | 288 | 19 |  | 603 | 13 | 13 | Unit Ventilator | 4824 | 3.5821 | 1 | 3.5821 | 1
216 | Classroom | 406 | 27 |  | 942 | 21 | 21 | Unit Ventilator | 7536 | 3.2325 | 1 | 3.2325 | 1
217 | Classroom | 407 | 27 |  | 656 | 14 | 14 | Unit Ventilator | 5248 | 4.6532 | 2 | 4.6532 | 2
300 | Classroom | 332 | 22 |  | 956 | 21 | 21 | Unit Ventilator | 7648 | 2.6046 | 1 | 2.6046 | 1
301 | Classroom | 333 | 22 |  | 601 | 13 | 13 | Unit Ventilator | 4808 | 4.1556 | 2 | 4.1556 | 2
302 | Classroom | 249 | 16 |  | 864 | 19 | 16 | Unit Ventilator | 6912 | 2.1615 | 1 | 2.1615 | 1
303 | Classroom | 341 | 22 |  | 859 | 19 | 19 | Unit Ventilator | 6872 | 2.9773 | 1 | 2.9773 | 1
304 | Classroom | 270 | 18 |  | 863 | 19 | 18 | Unit Ventilator | 6904 | 2.3465 | 1 | 2.3465 | 1
305 | Classroom | 286 | 19 |  | 862 | 19 | 19 | Unit Ventilator | 6896 | 2.4884 | 1 | 2.4884 | 1
306 | Classroom | 254 | 16 |  | 861 | 19 | 16 | Unit Ventilator | 6888 | 2.2125 | 1 | 2.2125 | 1
307 | Classroom | 348 | 23 |  | 865 | 19 | 19 | Unit Ventilator | 6920 | 3.0173 | 1 | 3.0173 | 1
308 | Classroom | 334 | 22 |  | 859 | 19 | 19 | Unit Ventilator | 6872 | 2.9162 | 1 | 2.9162 | 1
309 | Classroom | 287 | 19 |  | 972 | 22 | 19 | Unit Ventilator | 7776 | 2.2145 | 1 | 2.2145 | 1
310 | Classroom | 324 | 21 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 2.8521 | 1 | 2.8521 | 1
311 | Classroom | 306 | 20 |  | 958 | 21 | 20 | Unit Ventilator | 7664 | 2.3956 | 1 | 2.3956 | 1
312 | Classroom | 483 | 32 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 3.8132 | 1 | 3.8132 | 1
313 | Classroom | 460 | 30 |  | 944 | 21 | 21 | Unit Ventilator | 7552 | 3.6547 | 1 | 3.6547 | 1
314 | Classroom | 238 | 15 |  | 951 | 21 | 15 | Unit Ventilator | 7608 | 1.877 | 1 | 1.877 | 1
315 | Classroom | 359 | 23 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 4.0367 | 2 | 4.0367 | 2
316 | Classroom | 315 | 21 |  | 952 | 21 | 21 | Unit Ventilator | 7616 | 2.4816 | 1 | 2.4816 | 1
317 | Classroom | 288 | 19 |  | 651 | 14 | 14 | Unit Ventilator | 5208 | 3.318 | 1 | 3.318 | 1
- | Main Office |  | 0 | Yes | 1235 | 28 | 28 | Unit Ventilator | 9880 | unk | unk | 20 | 3
- | Principal |  | 0 | Yes | 361 | 8 | 8 | Unit Ventilator | 2888 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-20 | [8 empty] | unk | unk | unk | unk
School: | Randolph Blankenburg Elementary-Middle School | House fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
K-1 | Classroom | 906 | 60 |  | 704 | 16 | 16 | House Fan | 5632 | 9.652 | 2 | 9.652 | 2
K-4 | Classroom | 828 | 55 |  | 704 | 16 | 16 | House Fan | 5632 | 8.821 | 2 | 8.821 | 2
B27 | Classroom | 517 | 34 |  | 1047 | 23 | 23 | House Fan | 8376 | 3.7034 | 1 | 3.7034 | 1
10A | Vice Principal | 0 | 0 | Yes | 176 | 4 | 4 | N/A | 1408 | 0 | 0 | 20 | 3
29 | Classroom | 594 | 39 |  | 704 | 16 | 16 | House Fan | 5632 | 6.3281 | 2 | 6.3281 | 2
30 | Classroom | 930 | 62 |  | 836 | 19 | 19 | House Fan | 6688 | 8.3433 | 2 | 8.3433 | 2
101 | Classroom | 890 | 59 |  | 704 | 16 | 16 | House Fan | 5632 | 9.4815 | 2 | 9.4815 | 2
102 | Classroom | 63 | 4 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0.67116 | 0 | 20.6712 | 3
103 | Classroom | 954 | 63 |  | 704 | 16 | 16 | House Fan | 5632 | 10.1634 | 3 | 10.1634 | 3
105 | Classroom | 907 | 60 |  | 704 | 16 | 16 | House Fan | 5632 | 9.6626 | 2 | 9.6626 | 2
106 | Classroom | 988 | 65 |  | 704 | 16 | 16 | House Fan | 5632 | 10.5256 | 3 | 10.5256 | 3
107 | Classroom | 959 | 63 |  | 704 | 16 | 16 | House Fan | 5632 | 10.2166 | 3 | 10.2166 | 3
208 | Classroom | 620 | 41 |  | 704 | 16 | 16 | House Fan | 5632 | 6.6051 | 2 | 6.6051 | 2
208A | Nurse's Office | 0 | 0 |  | 176 | 4 | 0 | N/A | 1408 | 0 | 0 | 0 | 0
209 | Classroom | 695 | 46 |  | 704 | 16 | 16 | House Fan | 5632 | 7.4041 | 2 | 7.4041 | 2
210 | Classroom | 930 | 62 |  | 704 | 16 | 16 | House Fan | 5632 | 9.9077 | 2 | 9.9077 | 2
211 | Classroom | 887 | 59 |  | 704 | 16 | 16 | House Fan | 5632 | 9.4496 | 2 | 9.4496 | 2
212 | Classroom | 751 | 50 |  | 704 | 16 | 16 | House Fan | 5632 | 8.0007 | 2 | 8.0007 | 2
213 | Classroom | 955 | 63 |  | 704 | 16 | 16 | House Fan | 5632 | 10.174 | 3 | 10.174 | 3
214 | Classroom | 950 | 63 |  | 704 | 16 | 16 | House Fan | 5632 | 10.1207 | 3 | 10.1207 | 3
316 | Classroom | 0 | 0 | Yes | 880 | 20 | 20 | House Fan | 7040 | 0 | 0 | 20 | 3
317 | Classroom | 361 | 24 |  | 484 | 11 | 11 | House Fan | 3872 | 5.594 | 2 | 5.594 | 2
318 | Classroom | 588 | 39 |  | 704 | 16 | 16 | House Fan | 5632 | 6.2642 | 2 | 6.2642 | 2
319 | Classroom | 341 | 22 |  | 704 | 16 | 16 | House Fan | 5632 | 3.6328 | 1 | 3.6328 | 1
320 | Classroom | 483 | 32 |  | 704 | 16 | 16 | House Fan | 5632 | 5.1456 | 2 | 5.1456 | 2
321 | Classroom | 743 | 49 |  | 704 | 16 | 16 | House Fan | 5632 | 7.9155 | 2 | 7.9155 | 2
322 | Classroom | 877 | 58 |  | 704 | 16 | 16 | House Fan | 5632 | 9.343 | 2 | 9.343 | 2
323 | Classroom | 642 | 42 |  | 748 | 17 | 17 | House Fan | 5984 | 6.4372 | 2 | 6.4372 | 2
324 | Classroom | 818 | 54 |  | 704 | 16 | 16 | House Fan | 5632 | 8.7145 | 2 | 8.7145 | 2
325 | Classroom | 809 | 53 |  | 704 | 16 | 16 | House Fan | 5632 | 8.6186 | 2 | 8.6186 | 2
326 | Classroom | 565 | 37 |  | 704 | 16 | 16 | House Fan | 5632 | 6.0192 | 2 | 6.0192 | 2
327 | Classroom | 698 | 46 |  | 704 | 16 | 16 | House Fan | 5632 | 7.4361 | 2 | 7.4361 | 2
328 | Classroom | 151 | 10 | Yes | 704 | 16 | 16 | House Fan | 5632 | 1.6087 | 1 | 21.6087 | 3
329 | Classroom | 0 | 0 | Yes | 264 | 6 | 6 | House Fan | 2112 | 0 | 0 | 20 | 3
2121 | Storage | 0 | 0 | Yes | 399 | 9 | 9 | House Fan | 3192 | 0 | 0 | 20 | 3
- | Auditorium | 2451 | 163 |  | 3520 | 80 | 80 | House Fan | 28160 | 5.2223 | 2 | 5.2223 | 2
- | Counselor Office | 0 | 0 | Yes | 220 | 5 | 5 | N/A | 1760 | 0 | 0 | 20 | 3
- | Gym | 0 | 0 | Yes | 3872 | 88 | 88 | N/A | 30976 | 0 | 0 | 20 | 3
- | Kitchen | 634 | 42 |  | 880 | 20 | 20 | House Fan | 7040 | 5.4034 | 2 | 5.4034 | 2
- | Library | 865 | 57 |  | 1675 | 38 | 38 | House Fan | 13400 | 3.8731 | 1 | 3.8731 | 1
- | Main Office | 0 | 0 | Yes | 308 | 7 | 7 | N/A | 2464 | 0 | 0 | 20 | 3
- | Principal Office | 0 | 0 | Yes | 160 | 3 | 3 | N/A | 1280 | 0 | 0 | 20 | 3
- | SEL Classroom | 970 | 64 |  | 704 | 16 | 16 | House Fan | 5632 | 10.3338 | 3 | 10.3338 | 3
- | Staff Lounge | 0 | 0 | Yes | 399 | 9 | 9 | N/A | 3192 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-17 | [8 empty] | unk | unk | unk | unk
School: | Bodine | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
401 | Classroom |  | 0 |  | 660 | 15 | 0 |  | 5280 | unk | unk | unk | unk
402 | classroom |  | 0 |  | 616 | 14 | 0 |  | 4928 | unk | unk | unk | unk
403 | Classroom |  | 0 |  | 598 | 13 | 0 |  | 4784 | unk | unk | unk | unk
404 | Classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | unk | unk | unk | unk
405 A | Dept Head |  | 0 |  | 98 | 2 | 0 |  | 784 | unk | unk | unk | unk
405 B | Counselor |  | 0 |  | 133 | 3 | 0 |  | 1064 | unk | unk | unk | unk
406 | Classroom |  | 0 |  | 672 | 15 | 0 |  | 5376 | unk | unk | unk | unk
407 | Classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | unk | unk | unk | unk
408 | Computer |  | 0 |  | 726 | 16 | 0 |  | 5808 | unk | unk | unk | unk
409 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
301 | Classroom |  | 0 |  | 667 | 15 | 0 |  | 5336 | unk | unk | unk | unk
302 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
303 | Classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | unk | unk | unk | unk
304 | Classroom |  | 0 |  | 621 | 14 | 0 |  | 4968 | unk | unk | unk | unk
305 | Faculty Area |  | 0 |  | 450 | 10 | 0 |  | 3600 | unk | unk | unk | unk
306 | Classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | unk | unk | unk | unk
307 | Classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | unk | unk | unk | unk
308 | Classrrom |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
309 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
201 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
202 | Classroom |  | 0 |  | 660 | 15 | 0 |  | 5280 | unk | unk | unk | unk
203 | Library |  | 0 |  | 1058 | 24 | 0 |  | 8464 | unk | unk | unk | unk
203 | Library office |  | 0 |  | 140 | 3 | 0 |  | 1120 | unk | unk | unk | unk
205 | Classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | unk | unk | unk | unk
206 | Classroom |  | 0 |  | 621 | 14 | 0 |  | 4968 | unk | unk | unk | unk
207 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
208 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
102 | Classroom |  | 0 |  | 880 | 20 | 0 |  | 7040 | unk | unk | unk | unk
103 | Counselor |  | 0 |  | 110 | 2 | 0 |  | 880 | unk | unk | unk | unk
104 | Teacher Lounge |  | 0 |  | 345 | 7 | 0 |  | 2760 | unk | unk | unk | unk
105 A | Office |  | 0 |  | 63 | 1 | 0 |  | 504 | unk | unk | unk | unk
105 B | Office |  | 0 |  | 108 | 2 | 0 |  | 864 | unk | unk | unk | unk
105 C | Office |  | 0 |  | 81 | 1 | 0 |  | 648 | unk | unk | unk | unk
108 | Room |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
109 | Room |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
2 | Art Room |  | 0 |  | 484 | 11 | 0 |  | 3872 | unk | unk | unk | unk
- | Main Office |  | 0 |  | 322 | 7 | 0 |  | 2576 | unk | unk | unk | unk
- | Principal Office |  | 0 |  | 96 | 2 | 0 |  | 768 | unk | unk | unk | unk
- | Conferance Room |  | 0 |  | 220 | 5 | 0 |  | 1760 | unk | unk | unk | unk
- | Gym / Lunchroom |  | 0 |  | 2760 | 62 | 0 |  | 22080 | unk | unk | unk | unk
- | Kitchen |  | 0 |  | 648 | 14 | 0 |  | 5184 | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-28 | [8 empty] | unk | unk | unk | unk
School: | Amedee F. Bregy Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Auditorium | 6957 | 463 |  | 4017 | 91 | 91 | House Fan | 32136 | 12.9892 | 3 | 12.9892 | 3
- | Cafeteria | 934 | 62 |  | 1584 | 36 | 36 | House Fan | 12672 | 4.4223 | 2 | 4.4223 | 2
- | Gym | 0 | 0 | Yes | 3872 | 88 | 88 | House Fan | 30976 | 0 | 0 | 20 | 3
- | Library | 991 | 66 |  | 1739 | 39 | 39 | House Fan | 13912 | 4.274 | 2 | 4.274 | 2
- | Basement Science Classroom | 557 | 37 |  | 1064 | 24 | 24 | House Fan | 8512 | 3.9262 | 1 | 3.9262 | 1
- | Basement Storage | 143 | 9 |  | 396 | 9 | 9 | House Fan | 3168 | 2.7083 | 1 | 2.7083 | 1
- | Basement Boy's Bathroom | 471 | 31 |  | 528 | 12 | 12 | House Fan | 4224 | 6.6903 | 2 | 6.6903 | 2
- | Basement Girl's Bathroom | 434 | 28 |  | 528 | 12 | 12 | House Fan | 4224 | 6.1648 | 2 | 6.1648 | 2
101 | Classroom | 271 | 18 |  | 660 | 15 | 15 | House Fan | 5280 | 3.0795 | 1 | 3.0795 | 1
102 | Classroom | 312 | 20 |  | 660 | 15 | 15 | House Fan | 5280 | 3.5455 | 1 | 3.5455 | 1
1K1 | Classroom | 823 | 54 |  | 660 | 15 | 15 | House Fan | 5280 | 9.3523 | 2 | 9.3523 | 2
103 | Classroom | 51 | 3 |  | 650 | 14 | 3 | House Fan | 5200 | 0.58846 | 0 | 0.58846 | 0
104 | Classroom | 564 | 37 |  | 650 | 14 | 14 | House Fan | 5200 | 6.5077 | 2 | 6.5077 | 2
105 | Classroom | 255 | 17 |  | 616 | 14 | 14 | House Fan | 4928 | 3.1047 | 1 | 3.1047 | 1
106 | Classroom | 723 | 48 |  | 616 | 14 | 14 | House Fan | 4928 | 8.8028 | 2 | 8.8028 | 2
107 | Classroom | 664 | 44 |  | 616 | 14 | 14 | House Fan | 4928 | 8.0844 | 2 | 8.0844 | 2
208 | Classroom | 866 | 57 |  | 660 | 15 | 15 | House Fan | 5280 | 9.8409 | 2 | 9.8409 | 2
209 | Classroom | 751 | 50 |  | 660 | 15 | 15 | House Fan | 5280 | 8.5341 | 2 | 8.5341 | 2
210 | Classroom | 128 | 8 | Yes | 652 | 14 | 14 | House Fan | 5216 | 1.4724 | 1 | 21.4724 | 3
211 | Classroom | 663 | 44 |  | 616 | 14 | 14 | House Fan | 4928 | 8.0722 | 2 | 8.0722 | 2
212 | Classroom | 669 | 44 |  | 660 | 15 | 15 | House Fan | 5280 | 7.6023 | 2 | 7.6023 | 2
213 | Classroom | 694 | 46 |  | 660 | 15 | 15 | House Fan | 5280 | 7.8864 | 2 | 7.8864 | 2
214 | Classroom | 629 | 41 |  | 660 | 15 | 15 | House Fan | 5280 | 7.1477 | 2 | 7.1477 | 2
215 | Classroom | 279 | 18 |  | 660 | 15 | 15 | House Fan | 5280 | 3.1705 | 1 | 3.1705 | 1
316 | Classroom | 404 | 26 |  | 660 | 15 | 15 | House Fan | 5280 | 4.5909 | 2 | 4.5909 | 2
317 | Classroom | 0 | 0 | Yes | 656 | 14 | 14 | House Fan | 5248 | 0 | 0 | 20 | 3
318 | Classroom | 577 | 38 |  | 660 | 15 | 15 | House Fan | 5280 | 6.5568 | 2 | 6.5568 | 2
319 | Classroom | 231 | 15 |  | 660 | 15 | 15 | House Fan | 5280 | 2.625 | 1 | 2.625 | 1
320 | Classroom | 726 | 48 |  | 704 | 16 | 16 | House Fan | 5632 | 7.7344 | 2 | 7.7344 | 2
321 | Classroom | 298 | 19 |  | 704 | 16 | 16 | House Fan | 5632 | 3.1747 | 1 | 3.1747 | 1
322 | Classroom | 511 | 34 |  | 704 | 16 | 16 | House Fan | 5632 | 5.4439 | 2 | 5.4439 | 2
323 | Classroom | 702 | 46 |  | 660 | 15 | 15 | House Fan | 5280 | 7.9773 | 2 | 7.9773 | 2
324 | Classroom | 375 | 25 |  | 660 | 15 | 15 | House Fan | 5280 | 4.2614 | 2 | 4.2614 | 2
325 | Classroom | 623 | 41 |  | 616 | 14 | 14 | House Fan | 4928 | 7.5852 | 2 | 7.5852 | 2
326 | Classroom | 557 | 37 |  | 654 | 14 | 14 | House Fan | 5232 | 6.3876 | 2 | 6.3876 | 2
327 | Classroom | 525 | 35 |  | 654 | 14 | 14 | House Fan | 5232 | 6.0206 | 2 | 6.0206 | 2
328 | Classroom | 664 | 44 |  | 660 | 15 | 15 | House Fan | 5280 | 7.5455 | 2 | 7.5455 | 2
- | Principal Office |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 220 | 5 | 5 | House Fan | 1760 | unk | unk | 20 | 3
Sheet Last Modified: | 2021-04-07 | [8 empty] | unk | unk | unk | unk
School: | Bridesburg Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | Goldner Part 2 | [7 empty] | unk | unk | unk | unk
| Devine Annex Retest | [8 empty] | unk | unk | unk | unk
School: | Bridesburg Elementary School Annex | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Main Building | [9 empty] | unk | unk | unk | unk
102 | Classroom | 422 | 28 |  | 846 | 19 | 19 | Unit Ventilator | 6768 | 3.7411 | 1 | 3.7411 | 1
103 | Classroom | 377 | 25 |  | 686 | 15 | 15 | Unit Ventilator | 5488 | 4.1217 | 2 | 4.1217 | 2
104 | Classroom | 476 | 31 |  | 993 | 22 | 22 | Unit Ventilator | 7944 | 3.5952 | 1 | 3.5952 | 1
105 | Classroom | 300 | 20 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 3.3482 | 1 | 3.3482 | 1
106 | Classroom | 536 | 35 |  | 972 | 22 | 22 | Unit Ventilator | 7776 | 4.1358 | 2 | 4.1358 | 2
107 | Classroom | 334 | 22 |  | 737 | 16 | 16 | Unit Ventilator | 5896 | 3.3989 | 1 | 3.3989 | 1
108 | Classroom | 322 | 21 |  | 1030 | 23 | 21 | Unit Ventilator | 8240 | 2.3447 | 1 | 2.3447 | 1
109 | Classroom | 294 | 19 |  | 684 | 15 | 15 | Unit Ventilator | 5472 | 3.2237 | 1 | 3.2237 | 1
110A | Counselor's Office | 198 | 13 |  | 130 | 2 | 2 | Unit Ventilator | 1040 | 11.4231 | 3 | 11.4231 | 3
111 | Classroom | 372 | 24 |  | 253 | 5 | 5 | Unit Ventilator | 2024 | 11.0277 | 3 | 11.0277 | 3
112 | Nurse's Office | 272 | 18 |  | 369 | 8 | 8 | Unit Ventilator | 2952 | 5.5285 | 2 | 5.5285 | 2
112A | Classroom | 0 | 0 |  | 218 | 4 | 0 | Unit Ventilator | 1744 | 0 | 0 | 0 | 0
112B | Classroom | 0 | 0 |  | 218 | 4 | 0 | Unit Ventilator | 1744 | 0 | 0 | 0 | 0
113 | Classroom | 137 | 9 |  | 117 | 2 | 2 | Unit Ventilator | 936 | 8.7821 | 2 | 8.7821 | 2
114 | Classroom | 327 | 21 |  | 930 | 21 | 21 | Unit Ventilator | 7440 | 2.6371 | 1 | 2.6371 | 1
115 | Classroom | 281 | 18 |  | 659 | 14 | 14 | Unit Ventilator | 5272 | 3.198 | 1 | 3.198 | 1
116 | Library | 1510 | 100 |  | 1700 | 38 | 38 | Unit Ventilator | 13600 | 6.6618 | 2 | 6.6618 | 2
200 | Classroom | 0 | 0 | Yes | 754 | 17 | 17 | Unit Ventilator | 6032 | 0 | 0 | 20 | 3
201 | Classroom | 136 | 9 |  | 609 | 13 | 9 | Unit Ventilator | 4872 | 1.6749 | 1 | 1.6749 | 1
202 | Classroom | 312 | 20 |  | 539 | 12 | 12 | Unit Ventilator | 4312 | 4.3414 | 2 | 4.3414 | 2
203 | Classroom | 377 | 25 |  | 714 | 16 | 16 | Unit Ventilator | 5712 | 3.9601 | 1 | 3.9601 | 1
204 | Classroom | 152 | 10 |  | 695 | 15 | 10 | Unit Ventilator | 5560 | 1.6403 | 1 | 1.6403 | 1
205 | Classroom | 1577 | 105 |  | 1129 | 25 | 25 | Unit Ventilator | 9032 | 10.4761 | 3 | 10.4761 | 3
206 | Classroom | 157 | 10 |  | 715 | 16 | 10 | Unit Ventilator | 5720 | 1.6469 | 1 | 1.6469 | 1
207 | Classroom | 247 | 16 |  | 725 | 16 | 16 | Unit Ventilator | 5800 | 2.5552 | 1 | 2.5552 | 1
208 | Classroom | 351 | 23 |  | 650 | 14 | 14 | Unit Ventilator | 5200 | 4.05 | 2 | 4.05 | 2
209 | Classroom | 0 | 0 | Yes | 709 | 16 | 16 | Unit Ventilator | 5672 | 0 | 0 | 20 | 3
210 | Classroom | 147 | 9 |  | 759 | 17 | 9 | Unit Ventilator | 6072 | 1.4526 | 1 | 1.4526 | 1
211 | Classroom | 147 | 9 |  | 735 | 16 | 9 | Unit Ventilator | 5880 | 1.5 | 1 | 1.5 | 1
212 | Classroom | 180 | 12 |  | 787 | 17 | 12 | Unit Ventilator | 6296 | 1.7154 | 1 | 1.7154 | 1
213 | Classroom | 283 | 18 |  | 665 | 15 | 15 | Unit Ventilator | 5320 | 3.1917 | 1 | 3.1917 | 1
214 | Classroom | 1248 | 83 |  | 845 | 19 | 19 | Unit Ventilator | 6760 | 11.0769 | 3 | 11.0769 | 3
215 | Classroom | 457 | 30 |  | 677 | 15 | 15 | Unit Ventilator | 5416 | 5.0628 | 2 | 5.0628 | 2
217 | Classroom | 282 | 18 |  | 735 | 16 | 16 | Unit Ventilator | 5880 | 2.8776 | 1 | 2.8776 | 1
218 | Classroom | 292 | 19 |  | 601 | 13 | 13 | Unit Ventilator | 4808 | 3.6439 | 1 | 3.6439 | 1
220 | Classroom | 287 | 19 |  | 706 | 16 | 16 | Unit Ventilator | 5648 | 3.0489 | 1 | 3.0489 | 1
- | Hallway |  | 0 |  |  | 0 | 0 | HRU |  | unk | unk | unk | unk
- | Hallway 2 |  | 0 |  |  | 0 | 0 | HRU |  | unk | unk | unk | unk
- | Hallway Right |  | 0 |  |  | 0 | 0 | HRU |  | unk | unk | unk | unk
- | Hallways 2 Center |  | 0 |  |  | 0 | 0 | HRU |  | unk | unk | unk | unk
- | Gym | 0 | 0 |  | 3925 | 89 | 0 | N/A | 31400 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 |  | 3080 | 70 | 0 | N/A | 24640 | 0 | 0 | 0 | 0
- | Kitchen | 0 | 0 |  | 697 | 15 | 0 | N/A | 5576 | 0 | 0 | 0 | 0
- | Main Office | 1167 | 77 |  | 752 | 17 | 17 | HRU | 6016 | 11.639 | 3 | 11.639 | 3
Bridesburg Elementary School Annex | [9 empty] | unk | unk | unk | unk
1 | Classroom |  | 0 | Yes | 710 | 16 | 16 | N/A | 5680 | unk | unk | 20 | 3
2 | Staff Lounge |  | 0 | Yes | 504 | 11 | 11 | N/A | 4032 | unk | unk | 20 | 3
3 | Classroom |  | 0 | Yes | 575 | 13 | 13 | N/A | 4600 | unk | unk | 20 | 3
4 | Vice Principal |  | 0 | Yes | 245 | 5 | 5 | N/A | 1960 | unk | unk | 20 | 3
5 | Classroom |  | 0 | Yes | 693 | 15 | 15 | N/A | 5544 | unk | unk | 20 | 3
6 | Classroom |  | 0 | Yes | 732 | 16 | 16 | N/A | 5856 | unk | unk | 20 | 3
7 | Classroom |  | 0 | Yes | 773 | 17 | 17 | N/A | 6184 | unk | unk | 20 | 3
8 | Classroom |  | 0 | Yes | 589 | 13 | 13 | N/A | 4712 | unk | unk | 20 | 3
9 | Classroom |  | 0 | Yes | 610 | 13 | 13 | N/A | 4880 | unk | unk | 20 | 3
10 | Classroom |  | 0 | Yes | 623 | 14 | 14 | N/A | 4984 | unk | unk | 20 | 3
11 | Classroom |  | 0 | Yes | 581 | 13 | 13 | N/A | 4648 | unk | unk | 20 | 3
12 | Classroom |  | 0 | Yes | 569 | 12 | 12 | N/A | 4552 | unk | unk | 20 | 3
13 | Classroom |  | 0 | Yes | 625 | 14 | 14 | N/A | 5000 | unk | unk | 20 | 3
14 | Classroom |  | 0 | Yes | 576 | 13 | 13 | N/A | 4608 | unk | unk | 20 | 3
15 | Classroom |  | 0 | Yes | 547 | 12 | 12 | N/A | 4376 | unk | unk | 20 | 3
- | Support Room |  | 0 | Yes | 140 | 3 | 3 | N/A | 1120 | unk | unk | 20 | 3
- | Speech Room |  | 0 | Yes | 152 | 3 | 3 | N/A | 1216 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 144 | 3 | 3 | N/A | 1152 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 334 | 7 | 7 | N/A | 2672 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Henry A. Brown Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Retest Report | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Admin | 418 | 27 |  | 1058 | 24 | 24 | FCU | 8464 | 2.9631 | 1 | 2.9631 | 1
- | Cafeteria | 2904 | 193 |  | 1994 | 45 | 45 | AHU | 15952 | 10.9228 | 3 | 10.9228 | 3
- | Gym | 1581 | 105 |  | 3360 | 76 | 76 | AHU | 26880 | 3.529 | 1 | 3.529 | 1
- | Library | 488 | 32 |  | 1486 | 33 | 32 | FCU | 11888 | 2.463 | 1 | 2.463 | 1
- | Nurses Room | 133 | 8 |  | 290 | 6 | 6 | FCU | 2320 | 3.4397 | 1 | 3.4397 | 1
- | Outside Library | 366 | 24 |  | 900 | 20 | 20 | FCU | 7200 | 3.05 | 1 | 3.05 | 1
100 | Classroom | 328 | 21 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 3.4894 | 1 | 3.4894 | 1
101 | Classroom | 395 | 26 |  | 730 | 16 | 16 | Unit Ventilator | 5840 | 4.0582 | 2 | 4.0582 | 2
113 | Classroom | 296 | 19 |  | 745 | 16 | 16 | Unit Ventilator | 5960 | 2.9799 | 1 | 2.9799 | 1
114 | Classroom | 309 | 20 |  | 700 | 15 | 15 | Unit Ventilator | 5600 | 3.3107 | 1 | 3.3107 | 1
151 | Classroom | 779 | 51 |  | 784 | 17 | 17 | FCU | 6272 | 7.4522 | 2 | 7.4522 | 2
153 | Classroom | 689 | 45 |  | 895 | 20 | 20 | FCU | 7160 | 5.7737 | 2 | 5.7737 | 2
154 | Classroom | 590 | 39 |  | 780 | 17 | 17 | FCU | 6240 | 5.6731 | 2 | 5.6731 | 2
156 | Classroom | 647 | 43 |  | 835 | 18 | 18 | FCU | 6680 | 5.8114 | 2 | 5.8114 | 2
200 | Classroom | 608 | 40 |  | 905 | 20 | 20 | Unit Ventilator | 7240 | 5.0387 | 2 | 5.0387 | 2
201 | Classroom | 633 | 42 |  | 900 | 20 | 20 | Unit Ventilator | 7200 | 5.275 | 2 | 5.275 | 2
202 | Classroom |  | 0 | Yes | 655 | 14 | 14 |  | 5240 | unk | unk | 20 | 3
206 | Classroom |  | 0 | Yes | 795 | 18 | 18 |  | 6360 | unk | unk | 20 | 3
209 | Classroom |  | 0 | Yes | 655 | 14 | 14 |  | 5240 | unk | unk | 20 | 3
211 | Classroom | 470 | 31 |  | 895 | 20 | 20 | Unit Ventilator | 7160 | 3.9385 | 1 | 3.9385 | 1
212 | Classroom | 307 | 20 |  | 905 | 20 | 20 | Unit Ventilator | 7240 | 2.5442 | 1 | 2.5442 | 1
213 | Classroom | 782 | 52 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 6.7029 | 2 | 6.7029 | 2
214 | Classroom | 616 | 41 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 5.28 | 2 | 5.28 | 2
217 | Classroom | 250 | 16 |  | 665 | 15 | 15 | Unit Ventilator | 5320 | 2.8195 | 1 | 2.8195 | 1
226 South | Classroom | 405 | 27 |  | 777 | 17 | 17 | Unit Ventilator | 6216 | 3.9093 | 1 | 3.9093 | 1
226 West | Classroom | 458 | 30 |  | 777 | 17 | 17 | Unit Ventilator | 6216 | 4.4208 | 2 | 4.4208 | 2
227 | Classroom | 487 | 32 |  | 740 | 16 | 16 | Unit Ventilator | 5920 | 4.9358 | 2 | 4.9358 | 2
228 | Classroom | 685 | 45 |  | 775 | 17 | 17 | Unit Ventilator | 6200 | 6.629 | 2 | 6.629 | 2
229 | Computer Lab | 103 | 6 | Yes | 990 | 22 | 22 | FCU | 7920 | 0.7803 | 0 | 20.7803 | 3
300 | Classroom | 582 | 38 |  | 905 | 20 | 20 | Unit Ventilator | 7240 | 4.8232 | 2 | 4.8232 | 2
301 | Classroom | 535 | 35 |  | 890 | 20 | 20 | Unit Ventilator | 7120 | 4.5084 | 2 | 4.5084 | 2
302 | Classroom | 151 | 10 |  | 695 | 15 | 10 | Unit Ventilator | 5560 | 1.6295 | 1 | 1.6295 | 1
304 | Classroom | 445 | 29 |  | 825 | 18 | 18 | Unit Ventilator | 6600 | 4.0455 | 2 | 4.0455 | 2
310 | Classroom | 657 | 43 |  | 715 | 16 | 16 | Unit Ventilator | 5720 | 6.8916 | 2 | 6.8916 | 2
311 | Classroom | 241 | 16 |  | 935 | 21 | 16 | Unit Ventilator | 7480 | 1.9332 | 1 | 1.9332 | 1
312 | Classroom | 426 | 28 |  | 935 | 21 | 21 | Unit Ventilator | 7480 | 3.4171 | 1 | 3.4171 | 1
313 | Classroom | 327 | 21 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 2.6658 | 1 | 2.6658 | 1
314 | Classroom | 512 | 34 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.1739 | 2 | 4.1739 | 2
317 | Classroom | 165 | 11 |  | 660 | 15 | 11 | Unit Ventilator | 5280 | 1.875 | 1 | 1.875 | 1
318 | Classroom | 473 | 31 |  | 1090 | 24 | 24 | FCU | 8720 | 3.2546 | 1 | 3.2546 | 1
319 | Classroom | 284 | 18 |  | 1125 | 25 | 18 | FCU | 9000 | 1.8933 | 1 | 1.8933 | 1
322 South | Classroom | 174 | 11 |  | 745 | 16 | 11 | Unit Ventilator | 5960 | 1.7517 | 1 | 1.7517 | 1
322 West | Classroom | 107 | 7 |  | 745 | 16 | 7 | Unit Ventilator | 5960 | 1.0772 | 1 | 1.0772 | 1
323 | Classroom | 472 | 31 |  | 730 | 16 | 16 | Unit Ventilator | 5840 | 4.8493 | 2 | 4.8493 | 2
324 | Classroom | 784 | 52 |  | 765 | 17 | 17 | Unit Ventilator | 6120 | 7.6863 | 2 | 7.6863 | 2
325 West | Classroom | 533 | 35 |  | 890 | 20 | 20 | Unit Ventilator | 7120 | 4.4916 | 2 | 4.4916 | 2
325 North | Classroom | 581 | 38 |  | 890 | 20 | 20 | Unit Ventilator | 7120 | 4.8961 | 2 | 4.8961 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | Joseph H. Brown Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Emcor Mechanical Retest | Emcor Exhaust Report | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | GYM | 921 | 61 |  | 3510 | 79 | 61 | Unit Ventilator | 28080 | 1.9679 | 1 | 1.9679 | 1
- | CAFE | 921 | 61 |  | 1440 | 32 | 32 | Unit Ventilator | 11520 | 4.7969 | 2 | 4.7969 | 2
101 | classroom | 519 | 34 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 5.8358 | 2 | 5.8358 | 2
102 | classroom | 562 | 37 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 6.3193 | 2 | 6.3193 | 2
103 | classroom | 358 | 23 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 3.7658 | 1 | 3.7658 | 1
104 | classroom | 932 | 62 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 8.2139 | 2 | 8.2139 | 2
105 | classroom | 844 | 56 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 6.8804 | 2 | 6.8804 | 2
106 | classroom | 786 | 52 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 6.4076 | 2 | 6.4076 | 2
107 | classroom | 985 | 65 |  | 1104 | 25 | 25 | Unit Ventilator | 8832 | 6.6916 | 2 | 6.6916 | 2
108 | classroom | 836 | 55 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 7.3678 | 2 | 7.3678 | 2
109 | Counselor Office |  | 0 | Yes | 112 | 2 | 2 |  | 896 | unk | unk | 20 | 3
110 | Nurse Room |  | 0 |  | 224 | 5 | 0 | N/A | 1792 | unk | unk | unk | unk
111 | Medical Waiting |  | 0 | Yes | 120 | 2 | 2 |  | 960 | unk | unk | 20 | 3
200 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
201 | classroom | 394 | 26 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.2826 | 2 | 4.2826 | 2
202 | classroom | 0 | 0 | Yes | 667 | 15 | 15 | Unit Ventilator | 5336 | 0 | 0 | 20 | 3
203 | classroom | 417 | 27 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 4.6889 | 2 | 4.6889 | 2
204 | classroom | 408 | 27 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.4348 | 2 | 4.4348 | 2
205 | classroom | 550 | 36 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.9783 | 2 | 5.9783 | 2
206 | classroom | 750 | 50 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 5.9211 | 2 | 5.9211 | 2
206A | Room |  | 0 | Yes | 288 | 6 | 6 |  | 2304 | unk | unk | 20 | 3
207 | classroom | 484 | 32 |  | 506 | 11 | 11 | Unit Ventilator | 4048 | 7.1739 | 2 | 7.1739 | 2
207A | Office |  | 0 | Yes | 168 | 3 | 3 |  | 1344 | unk | unk | 20 | 3
208 | classroom | 513 | 34 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 5.5761 | 2 | 5.5761 | 2
209 | classroom | 723 | 48 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 7.6052 | 2 | 7.6052 | 2
210 | classroom | 495 | 33 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 5.2069 | 2 | 5.2069 | 2
211 | classroom | 376 | 25 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 4.2279 | 2 | 4.2279 | 2
300 | classroom |  | 0 | Yes | 150 | 3 | 3 |  | 1200 | unk | unk | 20 | 3
301 | classroom | 605 | 40 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 6.8028 | 2 | 6.8028 | 2
302 | classroom | 457 | 30 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.9674 | 2 | 4.9674 | 2
303 | classroom | 389 | 25 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.2283 | 2 | 4.2283 | 2
304 | classroom | 469 | 31 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 4.9334 | 2 | 4.9334 | 2
305 | classroom | 0 | 0 | Yes | 713 | 16 | 16 | Unit Ventilator | 5704 | 0 | 0 | 20 | 3
306 | classroom | 0 | 0 | Yes | 874 | 19 | 19 | Unit Ventilator | 6992 | 0 | 0 | 20 | 3
307 | classroom | 419 | 27 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.5543 | 2 | 4.5543 | 2
308 | classroom |  | 0 | Yes | 713 | 16 | 16 |  | 5704 | unk | unk | 20 | 3
Principal | Office |  | 0 | Yes | 160 | 3 | 3 |  | 1280 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 368 | 8 | 8 | N/A | 2944 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | William C Bryant Elementary School | House fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Gym | 1521 | 101 |  | 2765 | 62 | 62 | House Fan | 22120 | 4.1257 | 2 | 4.1257 | 2
- | Shop Classroom | 795 | 53 |  | 740 | 16 | 16 | House Fan | 5920 | 8.0574 | 2 | 8.0574 | 2
- | Art Room | 0 | 0 |  | 740 | 16 | 0 | House Fan | 5920 | 0 | 0 | 0 | 0
- | Cafeteria/Auditorium | 1853 | 123 |  | 2479 | 56 | 56 | AHU | 19832 | 5.6061 | 2 | 5.6061 | 2
- | Principal's Office | 0 | 0 | Yes | 204 | 4 | 4 | House Fan | 1632 | 0 | 0 | 20 | 3
- | Office | 0 | 0 |  | 135 | 3 | 0 | House Fan | 1080 | 0 | 0 | 0 | 0
101 | Classroom | 1717 | 114 |  | 1013 | 23 | 23 | House Fan | 8104 | 12.7122 | 3 | 12.7122 | 3
102 | Classroom | 888 | 59 |  | 696 | 15 | 15 | House Fan | 5568 | 9.569 | 2 | 9.569 | 2
103 | Classroom | 853 | 56 |  | 690 | 15 | 15 | House Fan | 5520 | 9.2717 | 2 | 9.2717 | 2
104 | Classroom | 653 | 43 |  | 740 | 16 | 16 | House Fan | 5920 | 6.6182 | 2 | 6.6182 | 2
105 | Classroom | 0 | 0 | Yes | 700 | 15 | 15 | House Fan | 5600 | 0 | 0 | 20 | 3
106 | Classroom | 0 | 0 | Yes | 740 | 16 | 16 | House Fan | 5920 | 0 | 0 | 20 | 3
107 | Classroom | 0 | 0 | Yes | 718 | 16 | 16 | House Fan | 5744 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 795 | 18 | 18 | House Fan | 6360 | 0 | 0 | 20 | 3
110 | Nurse Office | 0 | 0 | Yes | 219 | 4 | 4 | House Fan | 1752 | 0 | 0 | 20 | 3
111 | - |  | 0 |  | 731 | 16 | 0 | House Fan | 5848 | unk | unk | unk | unk
112 | Main Office |  | 0 | Yes | 707 | 16 | 16 | House Fan | 5656 | unk | unk | 20 | 3
113 | Classroom | 0 | 0 | Yes | 674 | 15 | 15 | House Fan | 5392 | 0 | 0 | 20 | 3
114 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0 | 20 | 3
201 | Classroom | 1845 | 123 |  | 1013 | 23 | 23 | House Fan | 8104 | 13.6599 | 3 | 13.6599 | 3
202 | Classroom | 843 | 56 |  | 686 | 15 | 15 | House Fan | 5488 | 9.2165 | 2 | 9.2165 | 2
203 | Classroom | 108 | 7 | Yes | 690 | 15 | 15 | House Fan | 5520 | 1.1739 | 1 | 21.1739 | 3
204 | Classroom | 893 | 59 |  | 740 | 16 | 16 | House Fan | 5920 | 9.0507 | 2 | 9.0507 | 2
205 | Classroom | 0 | 0 | Yes | 700 | 15 | 15 | House Fan | 5600 | 0 | 0 | 20 | 3
206 | Classroom | 0 | 0 | Yes | 740 | 16 | 16 | House Fan | 5920 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 718 | 16 | 16 | House Fan | 5744 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 795 | 18 | 18 | House Fan | 6360 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 |  | 753 | 17 | 0 | House Fan | 6024 | 0 | 0 | 0 | 0
210 | Classroom | 0 | 0 | Yes | 715 | 16 | 16 | House Fan | 5720 | 0 | 0 | 20 | 3
211 | Classroom | 0 | 0 |  | 731 | 16 | 0 | House Fan | 5848 | 0 | 0 | 0 | 0
212 | Classroom | 0 | 0 | Yes | 707 | 16 | 16 | House Fan | 5656 | 0 | 0 | 20 | 3
213 | Classroom | 0 | 0 | Yes | 674 | 15 | 15 | House Fan | 5392 | 0 | 0 | 20 | 3
214 | Classroom | 0 | 0 |  | 713 | 16 | 0 | House Fan | 5704 | 0 | 0 | 0 | 0
- | IMC - Library | 0 | 0 |  | 2788 | 63 | 0 | Roof Top Unit | 22304 | 0 | 0 | 0 | 0
- | 2nd Flr Teacher's Lounge | 0 | 0 |  | 349 | 7 | 0 | House Fan | 2792 | 0 | 0 | 0 | 0
301 | Classroom | 387 | 25 |  | 1013 | 23 | 23 | House Fan | 8104 | 2.8653 | 1 | 2.8653 | 1
302 | Classroom | 748 | 49 |  | 686 | 15 | 15 | House Fan | 5488 | 8.1778 | 2 | 8.1778 | 2
303 | Classroom | 68 | 4 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0.73913 | 0 | 20.7391 | 3
304 | Classroom | 156 | 10 | Yes | 740 | 16 | 16 | House Fan | 5920 | 1.5811 | 1 | 21.5811 | 3
305 | Classroom | 0 | 0 | Yes | 700 | 15 | 15 | House Fan | 5600 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 740 | 16 | 16 | House Fan | 5920 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 |  | 718 | 16 | 0 | House Fan | 5744 | 0 | 0 | 0 | 0
308 | Classroom | 0 | 0 |  | 795 | 18 | 0 | House Fan | 6360 | 0 | 0 | 0 | 0
309 | Classroom | 0 | 0 |  | 753 | 17 | 0 | House Fan | 6024 | 0 | 0 | 0 | 0
310 | Classroom | 0 | 0 | Yes | 715 | 16 | 16 | House Fan | 5720 | 0 | 0 | 20 | 3
311 | Classroom | 0 | 0 | Yes | 731 | 16 | 16 | House Fan | 5848 | 0 | 0 | 20 | 3
312 | Classroom | 0 | 0 | Yes | 707 | 16 | 16 | House Fan | 5656 | 0 | 0 | 20 | 3
313 | Classroom | 0 | 0 | Yes | 674 | 15 | 15 | House Fan | 5392 | 0 | 0 | 20 | 3
314 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0 | 20 | 3
- | 3rd Flr Teacher's Lounge | 0 | 0 |  | 349 | 7 | 0 | House Fan | 2792 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-17 | [8 empty] | unk | unk | unk | unk
School: | Building 21 (Kinsey) | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
600 | Classroom |  | 0 |  | 810 | 18 | 0 |  | 6480 | unk | unk | unk | unk
2 | Classroom |  | 0 |  | 1104 | 25 | 0 |  | 8832 | unk | unk | unk | unk
4 | Classroom |  | 0 |  | 884 | 20 | 0 |  | 7072 | unk | unk | unk | unk
5 | Kitchen |  | 0 |  | 910 | 20 | 0 |  | 7280 | unk | unk | unk | unk
112 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
112A | Nurse |  | 0 |  | 99 | 2 | 0 |  | 792 | unk | unk | unk | unk
111 | Office |  | 0 |  | 319 | 7 | 0 |  | 2552 | unk | unk | unk | unk
111A | Office |  | 0 |  | 140 | 3 | 0 |  | 1120 | unk | unk | unk | unk
111B | Office |  | 0 |  | 168 | 3 | 0 |  | 1344 | unk | unk | unk | unk
113 | Office |  | 0 |  | 475 | 10 | 0 |  | 3800 | unk | unk | unk | unk
113A | Office |  | 0 |  | 81 | 1 | 0 |  | 648 | unk | unk | unk | unk
113B | Office |  | 0 |  | 81 | 1 | 0 |  | 648 | unk | unk | unk | unk
110 | Main Office |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
115 | Classroom |  | 0 |  | 140 | 3 | 0 |  | 1120 | unk | unk | unk | unk
114 | Classroom |  | 0 |  | 81 | 1 | 0 |  | 648 | unk | unk | unk | unk
109 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
108 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
107 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
106 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
105 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
104 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
103 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
102 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
101 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
116 | Aud |  | 0 |  | 5244 | 119 | 0 |  | 41952 | unk | unk | unk | unk
201 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
202 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
203 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
204 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
205 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
206 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
207 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
208 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
210 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
211 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
212 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
213 | Nurse |  | 0 |  | 295 | 6 | 0 |  | 2360 | unk | unk | unk | unk
214 | Office |  | 0 |  | 140 | 3 | 0 |  | 1120 | unk | unk | unk | unk
209 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
215 | Office |  | 0 |  | 140 | 3 | 0 |  | 1120 | unk | unk | unk | unk
301 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
302 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
303 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
304 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
305 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
306 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
307 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
308 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
309 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
310 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
311 | Classroom |  | 0 |  | 710 | 16 | 0 |  | 5680 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-21 | [8 empty] | unk | unk | unk | unk
School: | Camelot Academy @ Boone | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
300 | Office | 292 | 19 |  | 370 | 8 | 8 | Univent | 2960 | 5.9189 | 2 | 5.9189 | 2
301 | Classroom | 335 | 22 |  | 803 | 18 | 18 | Univent | 6424 | 3.1289 | 1 | 3.1289 | 1
302 | Classroom | 281 | 18 |  | 816 | 18 | 18 | Univent | 6528 | 2.5827 | 1 | 2.5827 | 1
304 | Classroom | 292 | 19 |  | 1808 | 41 | 19 | Univent | 14464 | 1.2113 | 1 | 1.2113 | 1
305 (309) | Classroom | 330 | 22 |  | 851 | 19 | 19 | Univent | 6808 | 2.9083 | 1 | 2.9083 | 1
306 | Classroom | 364 | 24 |  | 966 | 21 | 21 | Univent | 7728 | 2.8261 | 1 | 2.8261 | 1
307 | Classroom | 348 | 23 |  | 1647 | 37 | 23 | Univent | 13176 | 1.5847 | 1 | 1.5847 | 1
308 | Office | 266 | 17 |  | 494 | 11 | 11 | Univent | 3952 | 4.0385 | 2 | 4.0385 | 2
310 | Office | 135 | 9 |  | 399 | 9 | 9 | Univent | 3192 | 2.5376 | 1 | 2.5376 | 1
312 | Classroom | 293 | 19 |  | 663 | 15 | 15 | Univent | 5304 | 3.3145 | 1 | 3.3145 | 1
314 | Classroom | 218 | 14 |  | 458 | 10 | 10 | Univent | 3664 | 3.5699 | 1 | 3.5699 | 1
316 | Classroom | 367 | 24 |  | 877 | 19 | 19 | Univent | 7016 | 3.1385 | 1 | 3.1385 | 1
- | Principal Office | 424 | 28 |  | 312 | 7 | 7 | ERU | 2496 | 10.1923 | 3 | 10.1923 | 3
200 | Classroom | 332 | 22 |  | 807 | 18 | 18 | Univent | 6456 | 3.0855 | 1 | 3.0855 | 1
201 | Classroom | 305 | 20 |  | 593 | 13 | 13 | Univent | 4744 | 3.8575 | 1 | 3.8575 | 1
202 | Classroom | 287 | 19 |  | 589 | 13 | 13 | Univent | 4712 | 3.6545 | 1 | 3.6545 | 1
204 | Classroom | 300 | 20 |  | 1084 | 24 | 20 | Univent | 8672 | 2.0756 | 1 | 2.0756 | 1
206 | Classroom | 434 | 28 |  | 962 | 21 | 21 | Univent | 7696 | 3.3836 | 1 | 3.3836 | 1
207 | Classroom | 326 | 21 |  | 880 | 20 | 20 | Univent | 7040 | 2.7784 | 1 | 2.7784 | 1
208 | Office | 239 | 15 |  | 494 | 11 | 11 | Univent | 3952 | 3.6285 | 1 | 3.6285 | 1
209 | Classroom | 349 | 23 |  | 879 | 19 | 19 | Univent | 7032 | 2.9778 | 1 | 2.9778 | 1
- | Academic Office | 308 | 20 |  | 311 | 7 | 7 | Univent | 2488 | 7.4277 | 2 | 7.4277 | 2
- | Operations Office | 348 | 23 |  | 395 | 8 | 8 | ERU | 3160 | 6.6076 | 2 | 6.6076 | 2
212 | Classroom | 380 | 25 |  | 567 | 12 | 12 | Univent | 4536 | 5.0265 | 2 | 5.0265 | 2
214 | Classroom | 397 | 26 |  | 652 | 14 | 14 | Univent | 5216 | 4.5667 | 2 | 4.5667 | 2
216 | Classroom | 408 | 27 |  | 651 | 14 | 14 | Univent | 5208 | 4.7005 | 2 | 4.7005 | 2
104 | Conference Room | 424 | 28 |  | 497 | 11 | 11 | Univent | 3976 | 6.3984 | 2 | 6.3984 | 2
- | Main Office | 372 | 24 |  | 1055 | 23 | 23 | Univent | 8440 | 2.6445 | 1 | 2.6445 | 1
102 | Computer Lab | 304 | 20 | Yes | 1019 | 23 | 23 | Univent | 8152 | 2.2375 | 1 | 22.2375 | 3
B5 | Classroom | 310 | 20 |  | 1248 | 28 | 20 | Univent | 9984 | 1.863 | 1 | 1.863 | 1
B6 | Cosmo Room 1 | 290 | 19 |  | 535 | 12 | 12 | Univent | 4280 | 4.0654 | 2 | 4.0654 | 2
B7 | Hair Salon | 443 | 29 |  | 693 | 15 | 15 | Univent | 5544 | 4.7944 | 2 | 4.7944 | 2
B8 | Barbershop | 275 | 18 |  | 539 | 12 | 12 | Univent | 4312 | 3.8265 | 1 | 3.8265 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-14 | [8 empty] | unk | unk | unk | unk
School: | Philadelphia High School for the Creative & Performing Arts | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
109 | Room | 714 | 47 |  | 1215.8 | 27 | 27 |  | 9726.4 | 4.4045 | 2 | 4.4045 | 2
108 | Room | 0 | 0 |  | 872.49 | 19 | 0 |  | 6979.92 | 0 | 0 | 0 | 0
107 | Room | 468 | 31 |  | 1182.7 | 26 | 26 |  | 9461.6 | 2.9678 | 1 | 2.9678 | 1
105 | Room | 0 | 0 |  | 1171.6 | 26 | 0 |  | 9372.8 | 0 | 0 | 0 | 0
110 | Office | 45 | 3 |  | 171.71 | 3 | 3 |  | 1373.68 | 1.9655 | 1 | 1.9655 | 1
- | First Floor North Corridor | 290 | 19 |  | 3004.3 | 68 | 19 |  | 24034.4 | 0.72396 | 0 | 0.72396 | 0
- | First Floor South Corridor | 118 | 7 |  | 1139.3 | 25 | 7 |  | 9114.4 | 0.77679 | 0 | 0.77679 | 0
116 | Room | -100 | -6 |  | 216.61 | 4 | -6 |  | 1732.88 | 3.4624 | 1 | 3.4624 | 1
106 | Editing Suite | 15 | 1 |  | 112.47 | 2 | 1 |  | 899.76 | 1.0003 | 1 | 1.0003 | 1
106 | Room |  | 0 |  | 1119.1 | 25 | 0 |  | 8952.8 | unk | unk | unk | unk
114 | Room | -61 | -4 |  | 845.65 | 19 | -4 |  | 6765.2 | 0.541 | 0 | 0.541 | 0
116 | Control Room | 219 | 14 |  | 327.76 | 7 | 7 |  | 2622.08 | 5.0113 | 2 | 5.0113 | 2
- | Second Floor South Corridor Outside Stair 4 | 45 | 3 |  | 2223.7 | 50 | 3 |  | 17789.6 | 0.15177 | 0 | 0.15177 | 0
- | Second Floor South Corridor | 0 | 0 |  | 1642.3 | 37 | 0 |  | 13138.4 | 0 | 0 | 0 | 0
- | Second Floor North Corridor | 301 | 20 |  | 1642.3 | 37 | 20 |  | 13138.4 | 1.3746 | 1 | 1.3746 | 1
202 | Room | 78 | 5 |  | 275.81 | 6 | 5 |  | 2206.48 | 2.121 | 1 | 2.121 | 1
203 | Room | 142 | 9 |  | 1209.4 | 27 | 9 |  | 9675.2 | 0.8806 | 0 | 0.8806 | 0
204 | Room | 616 | 41 |  | 1059.9 | 24 | 24 |  | 8479.2 | 4.3589 | 2 | 4.3589 | 2
205 | Room | 607 | 40 |  | 874.01 | 19 | 19 |  | 6992.08 | 5.2088 | 2 | 5.2088 | 2
206 | Room | 0 | 0 |  | 1206.6 | 27 | 0 |  | 9652.8 | 0 | 0 | 0 | 0
207 | Room | 613 | 40 |  | 891.99 | 20 | 20 |  | 7135.92 | 5.1542 | 2 | 5.1542 | 2
208 | Room | 809 | 53 |  | 870.75 | 19 | 19 |  | 6966 | 6.9681 | 2 | 6.9681 | 2
209 | Room | 584 | 38 |  | 871.76 | 19 | 19 |  | 6974.08 | 5.0243 | 2 | 5.0243 | 2
210 | Room | 304 | 20 |  | 791.75 | 17 | 17 |  | 6334 | 2.8797 | 1 | 2.8797 | 1
211 | Room | 420 | 28 |  | 1119.8 | 25 | 25 |  | 8958.4 | 2.813 | 1 | 2.813 | 1
213 | Room | -85 | -5 |  | 815.15 | 18 | -5 |  | 6521.2 | 0.78206 | 0 | 0.78206 | 0
214 | Room | 567 | 37 |  | 1351.8 | 30 | 30 |  | 10814.4 | 3.1458 | 1 | 3.1458 | 1
304 | Room | 15 | 1 |  | 1059.9 | 24 | 1 |  | 8479.2 | 0.10614 | 0 | 0.10614 | 0
305 | Room | 70 | 4 |  | 192.7 | 4 | 4 |  | 1541.6 | 2.7244 | 1 | 2.7244 | 1
306 | Room | 122 | 8 |  | 888.58 | 20 | 8 |  | 7108.64 | 1.0297 | 1 | 1.0297 | 1
307 | Room | 0 | 0 |  | 251.97 | 5 | 0 |  | 2015.76 | 0 | 0 | 0 | 0
308 | Room | 533 | 35 |  | 1094.9 | 24 | 24 |  | 8759.2 | 3.651 | 1 | 3.651 | 1
310 | Room | 527 | 35 |  | 877.6 | 19 | 19 |  | 7020.8 | 4.5038 | 2 | 4.5038 | 2
311 | Room | 824 | 54 |  | 1209 | 27 | 27 |  | 9672 | 5.1117 | 2 | 5.1117 | 2
312 | Room | 101 | 6 |  | 892.16 | 20 | 6 |  | 7137.28 | 0.84906 | 0 | 0.84906 | 0
313 | Room | -121 | -8 |  | 870.18 | 19 | -8 |  | 6961.44 | 1.0429 | 1 | 1.0429 | 1
314 | Room | 342 | 22 |  | 771.96 | 17 | 17 |  | 6175.68 | 3.3227 | 1 | 3.3227 | 1
315 | Room | -455 | -30 |  | 888.8 | 20 | -30 |  | 7110.4 | 3.8394 | 1 | 3.8394 | 1
316 | Room | 1080 | 72 |  | 1532.3 | 34 | 34 |  | 12258.4 | 5.2862 | 2 | 5.2862 | 2
317 | Room | 754 | 50 |  | 850.53 | 19 | 19 |  | 6804.24 | 6.6488 | 2 | 6.6488 | 2
318 | Room | 849 | 56 |  | 1015 | 23 | 23 |  | 8120 | 6.2734 | 2 | 6.2734 | 2
320 | Room | -20 | -1 |  | 94.85 | 2 | -1 |  | 758.8 | 1.5814 | 1 | 1.5814 | 1
321 | Room | -15 | -1 |  | 77.87 | 1 | -1 |  | 622.96 | 1.4447 | 1 | 1.4447 | 1
322 | Room | -17 | -1 |  | 58.45 | 1 | -1 |  | 467.6 | 2.1814 | 1 | 2.1814 | 1
323 | Room | 35 | 2 |  | 1013.7 | 23 | 2 |  | 8109.6 | 0.25895 | 0 | 0.25895 | 0
324 | Room | 30 | 2 |  | 257.05 | 5 | 2 |  | 2056.4 | 0.87532 | 0 | 0.87532 | 0
326 | Room | -297 | -19 |  |  | 0 | -19 |  |  | unk | unk | unk | unk
- | Third Floor North Corridor | 303 | 20 |  | 1655.3 | 37 | 20 |  | 13242.4 | 1.3729 | 1 | 1.3729 | 1
- | Third Floor South Corridor | 0 | 0 |  | 1655.3 | 37 | 0 |  | 13242.4 | 0 | 0 | 0 | 0
400 | Room | 932 | 62 |  | 1893.6 | 43 | 43 |  | 15148.8 | 3.6914 | 1 | 3.6914 | 1
401 | Room | 302 | 20 |  | 1794.2 | 40 | 20 |  | 14353.6 | 1.2624 | 1 | 1.2624 | 1
402 | Room | 615 | 41 |  | 2176.1 | 49 | 41 |  | 17408.8 | 2.1196 | 1 | 2.1196 | 1
403 | Room | -67 | -4 |  | 216.87 | 4 | -4 |  | 1734.96 | 2.3171 | 1 | 2.3171 | 1
403 | Print Room | 130 | 8 |  | 275.87 | 6 | 6 |  | 2206.96 | 3.5343 | 1 | 3.5343 | 1
403 | Room | 52 | 3 |  | 2280.1 | 51 | 3 |  | 18240.8 | 0.17105 | 0 | 0.17105 | 0
404 | Room | 226 | 15 |  | 1882.5 | 42 | 15 |  | 15060 | 0.9004 | 0 | 0.9004 | 0
405 | Room | 390 | 26 |  | 1656.39 | 37 | 26 |  | 13251.12 | 1.7659 | 1 | 1.7659 | 1
405 | Prep Room | 45 | 3 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
406 | Room | 710 | 47 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
407 | Room | 113 | 7 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
408 | Room | 0 | 0 |  | 217.94 | 4 | 0 |  | 1743.52 | 0 | 0 | 0 | 0
- | 4th Floor Corridor South | 0 | 0 |  | 1677.4 | 38 | 0 |  | 13419.2 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Laura H. Carnell Elementary School | [8 empty] | unk | unk | unk | unk
| Laura H. Carnell Little School House | House Fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | LSH Retest | [7 empty] | unk | unk | unk | unk
| EMCOR | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Main Building | [9 empty] | unk | unk | unk | unk
- | Basement Corridor | 0 | 0 |  | 450 | 10 | 0 | Unit Ventilator | 3600 | 0 | 0 | 0 | 0
- | Gym Office | 0 | 0 |  | 144 | 3 | 0 | N/A | 1152 | 0 | 0 | 0 | 0
B-3 | Art | 0 | 0 |  | 920 | 20 | 0 | House Fan | 7360 | 0 | 0 | 0 | 0
B-4 | Music | 0 | 0 |  | 660 | 15 | 0 | House Fan | 5280 | 0 | 0 | 0 | 0
B1 | Counselors | 0 | 0 |  | 630 | 14 | 0 | House Fan | 5040 | 0 | 0 | 0 | 0
B2 | Family Resource | 0 | 0 |  | 1023 | 23 | 0 | House Fan | 8184 | 0 | 0 | 0 | 0
B5 | Classroom | 519 | 34 |  | 800 | 18 | 18 | Unit Ventilator | 6400 | 4.8656 | 2 | 4.8656 | 2
B6 | Classroom | 110 | 7 |  | 800 | 18 | 7 | Unit Ventilator | 6400 | 1.0312 | 1 | 1.0312 | 1
B7 | Classroom | 421 | 28 |  | 800 | 18 | 18 | Unit Ventilator | 6400 | 3.9469 | 1 | 3.9469 | 1
- | 1st flr Corridor |  | 0 |  | 828 | 18 | 0 | Unit Ventilator | 6624 | unk | unk | unk | unk
- | Main Office | 0 | 0 |  | 483 | 10 | 0 | N/A | 3864 | 0 | 0 | 0 | 0
- | Principal's Office | 0 | 0 |  | 304 | 6 | 0 | N/A | 2432 | 0 | 0 | 0 | 0
- | 1st Flr Security | 0 | 0 |  | 81 | 1 | 0 | N/A | 648 | 0 | 0 | 0 | 0
- | 1st Flr Counselors | 0 | 0 |  | 126 | 2 | 0 | N/A | 1008 | 0 | 0 | 0 | 0
- | 1st Flr Office |  | 0 |  | 216 | 4 | 0 | N/A | 1728 | unk | unk | unk | unk
101 | Classroom | 0 | 0 | Yes | 957 | 21 | 21 | House Fan | 7656 | 0 | 0 | 20 | 3
102 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan | 6960 | 0 | 0 | 0 | 0
103 | Classroom | 0 | 0 |  | 899 | 20 | 0 | House Fan | 7192 | 0 | 0 | 0 | 0
104 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | House Fan | 6960 | 0 | 0 | 20 | 3
105 | Classroom | 0 | 0 |  | 900 | 20 | 0 | House Fan | 7200 | 0 | 0 | 0 | 0
106 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan | 6960 | 0 | 0 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 | House Fan | 7200 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 930 | 21 | 21 | House Fan | 7440 | 0 | 0 | 20 | 3
109 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 | House Fan | 7200 | 0 | 0 | 20 | 3
110 | Classroom | 0 | 0 |  | 960 | 21 | 0 | House Fan | 7680 | 0 | 0 | 0 | 0
111 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0 | 0 | 0
112 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0 | 0 | 0
113 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0 | 0 | 0
- | 2nd flr Corridor |  | 0 |  | 828 | 18 | 0 | Unit Ventilator | 6624 | unk | unk | unk | unk
- | 2nd Flr Nurse's | 0 | 0 |  | 216 | 4 | 0 | N/A | 1728 | 0 | 0 | 0 | 0
- | 2nd Flr. Office | 0 | 0 |  | 126 | 2 | 0 | N/A | 1008 | 0 | 0 | 0 | 0
- | Asst. Principal | 0 | 0 |  | 312 | 7 | 0 | N/A | 2496 | 0 | 0 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 928 | 21 | 21 | House Fan | 7424 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan | 6960 | 0 | 0 | 0 | 0
203 | Classroom | 0 | 0 |  | 899 | 20 | 0 | House Fan | 7192 | 0 | 0 | 0 | 0
206 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan | 6960 | 0 | 0 | 0 | 0
207 | Classroom | 0 | 0 |  | 900 | 20 | 0 | House Fan | 7200 | 0 | 0 | 0 | 0
208 | Classroom | 0 | 0 | Yes | 930 | 21 | 21 | House Fan | 7440 | 0 | 0 | 20 | 3
209 | Computer Lab | 0 | 0 |  | 900 | 20 | 0 | House Fan | 7200 | 0 | 0 | 0 | 0
210 | Computer Lab | 0 | 0 |  | 960 | 21 | 0 | House Fan | 7680 | 0 | 0 | 0 | 0
211 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0 | 0 | 0
212 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0 | 0 | 0
213 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0 | 0 | 0
217 | Teachers Lounge | 0 | 0 |  | 552 | 12 | 0 | N/A | 4416 | 0 | 0 | 0 | 0
- | 3rd flr Corridor |  | 0 |  | 828 | 18 | 0 | Unit Ventilator | 6624 | unk | unk | unk | unk
- | 3rd Flr. Office | 0 | 0 |  | 126 | 2 | 0 | N/A | 1008 | 0 | 0 | 0 | 0
300 East | Classroom | 0 | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0 | 0 | 0
300 West | Office | 0 | 0 |  | 99 | 2 | 0 | N/A | 792 | 0 | 0 | 0 | 0
301 | Classroom | 0 | 0 | Yes | 928 | 21 | 21 | House Fan | 7424 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | House Fan | 6960 | 0 | 0 | 20 | 3
303 | Classroom | 0 | 0 |  | 899 | 20 | 0 | House Fan | 7192 | 0 | 0 | 0 | 0
304 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | House Fan | 6960 | 0 | 0 | 20 | 3
305 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 | House Fan | 7200 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 |  | 870 | 19 | 0 | House Fan | 6960 | 0 | 0 | 0 | 0
307 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 | House Fan | 7200 | 0 | 0 | 20 | 3
308 | Classroom | 0 | 0 | Yes | 930 | 21 | 21 | House Fan | 7440 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 |  | 900 | 20 | 0 | House Fan | 7200 | 0 | 0 | 0 | 0
310 | Classroom | 0 | 0 |  | 960 | 21 | 0 | House Fan | 7680 | 0 | 0 | 0 | 0
312 | Classroom | 544 | 36 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 5.3125 | 2 | 5.3125 | 2
313 | Classroom | 479 | 31 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 4.6777 | 2 | 4.6777 | 2
314 | Classroom | 65 | 4 |  | 768 | 17 | 4 | Unit Ventilator | 6144 | 0.63477 | 0 | 0.63477 | 0
317 | Speech | 0 | 0 |  | 117 | 2 | 0 | N/A | 936 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 |  | 3456 | 78 | 0 | House Fan | 27648 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 |  | 986 | 22 | 0 | N/A | 7888 | 0 | 0 | 0 | 0
- | Dean's Office | 0 | 0 |  | 108 | 2 | 0 | N/A | 864 | 0 | 0 | 0 | 0
- | Gym | 0 | 0 |  | 3306 | 75 | 0 | N/A | 26448 | 0 | 0 | 0 | 0
- | IMC Classroom | 0 | 0 |  | 1363 | 30 | 0 | House Fan | 10904 | 0 | 0 | 0 | 0
- | IMC Office | 0 | 0 |  | 95 | 2 | 0 | House Fan | 760 | 0 | 0 | 0 | 0
Little School House | [9 empty] | unk | unk | unk | unk
A-1 | Classroom | 293 | 19 |  | 1056 | 24 | 19 | AHU | 8448 | 2.081 | 1 | 2.081 | 1
A-3 | Classroom | 296 | 19 |  | 1056 | 24 | 19 | AHU | 8448 | 2.1023 | 1 | 2.1023 | 1
A-2 | Classroom | 331 | 22 |  | 1056 | 24 | 22 | AHU | 8448 | 2.3509 | 1 | 2.3509 | 1
A-4 | Classroom | 343 | 22 |  | 1056 | 24 | 22 | AHU | 8448 | 2.4361 | 1 | 2.4361 | 1
A-5 | Classroom |  | 0 |  | 1056 | 24 | 0 | BCU | 8448 | unk | unk | unk | unk
A-5 | Storage |  | 0 |  | 52 | 1 | 0 | BCU | 416 | unk | unk | unk | unk
A-7 | Classroom |  | 0 |  | 1056 | 24 | 0 | BCU | 8448 | unk | unk | unk | unk
A-6 | Classroom | 321 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.2798 | 1 | 2.2798 | 1
A-8 | Classroom | 355 | 23 |  | 1056 | 24 | 23 | AHU | 8448 | 2.5213 | 1 | 2.5213 | 1
A-9 | Classroom | 364 | 24 |  | 1056 | 24 | 24 | AHU | 8448 | 2.5852 | 1 | 2.5852 | 1
A-11 | Classroom | 396 | 26 |  | 1056 | 24 | 24 | AHU | 8448 | 2.8125 | 1 | 2.8125 | 1
A-10 | Classroom | 292 | 19 |  | 1056 | 24 | 19 | AHU | 8448 | 2.0739 | 1 | 2.0739 | 1
A-12 | Classroom | 285 | 19 |  | 1056 | 24 | 19 | AHU | 8448 | 2.0241 | 1 | 2.0241 | 1
- | Corridor | 0 | 0 |  | 1056 | 24 | 0 | AHU | 8448 | 0 | 0 | 0 | 0
- | Cafeteria | 2789 | 185 |  | 1850 | 42 | 42 | AHU | 14800 | 11.3068 | 3 | 11.3068 | 3
- | BE Office | 76 | 5 |  | 88 | 2 | 2 | AHU | 704 | 6.4773 | 2 | 6.4773 | 2
- | Main Office | 215 | 14 |  | 168 | 3 | 3 | AHU | 1344 | 9.5982 | 2 | 9.5982 | 2
- | Vice Principal | 93 | 6 |  | 100 | 2 | 2 | AHU | 800 | 6.975 | 2 | 6.975 | 2
- | Counselor | 105 | 7 |  | 100 | 2 | 2 | AHU | 800 | 7.875 | 2 | 7.875 | 2
- | Comm Closet | 54 | 3 |  | 50 | 1 | 1 | AHU | 400 | 8.1 | 2 | 8.1 | 2
- | Storage | 73 | 4 |  | 250 | 5 | 4 | AHU | 2000 | 2.19 | 1 | 2.19 | 1
- | Lobby | 66 | 4 |  | 216 | 4 | 4 | AHU | 1728 | 2.2917 | 1 | 2.2917 | 1
- | Store Room 1 Ceiling | 43 | 2 |  | 250 | 5 | 2 | BCU | 2000 | 1.29 | 1 | 1.29 | 1
- | Store Room 2 | 26 | 1 |  | 70 | 1 | 1 | BCU | 560 | 2.7857 | 1 | 2.7857 | 1
- | Store Room 3 | 27 | 1 |  | 70 | 1 | 1 | BCU | 560 | 2.8929 | 1 | 2.8929 | 1
- | Janitors Closet | 20 | 1 |  | 32 | 0 | 0 | BCU | 256 | 4.6875 | 2 | 4.6875 | 2
- | Storage next to B.E. | 22 | 1 |  | 99 | 2 | 1 | BCU | 792 | 1.6667 | 1 | 1.6667 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | George Washington Carver High School for Engineering and Science | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Retest | Devine 2nd Retest | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Carver Commons- in IMC Room 147 | 0 | 0 |  | 96 | 2 | 0 |  | 768 | 0 | 0 | 0 | 0
2 | Carver Commons- in IMC Room 147 | 0 | 0 |  | 147 | 3 | 0 |  | 1176 | 0 | 0 | 0 | 0
3 | Carver Commons- in IMC Room 147 | 0 | 0 |  | 143 | 3 | 0 |  | 1144 | 0 | 0 | 0 | 0
4 | Carver Commons- in IMC Room 147 | 0 | 0 |  | 99 | 2 | 0 |  | 792 | 0 | 0 | 0 | 0
104 | Room | 783 | 52 |  | 625 | 14 | 14 |  | 5000 | 9.396 | 2 | 9.396 | 2
107 | Room | 158 | 10 |  | 704 | 16 | 10 |  | 5632 | 1.6832 | 1 | 1.6832 | 1
114 | Room | 0 | 0 |  | 840 | 19 | 0 |  | 6720 | 0 | 0 | 0 | 0
115 | Room | 305 | 20 |  | 840 | 19 | 19 |  | 6720 | 2.7232 | 1 | 2.7232 | 1
123 | Room | 181 | 12 |  | 920 | 20 | 12 |  | 7360 | 1.4755 | 1 | 1.4755 | 1
124 | Room | 85 | 5 |  | 480 | 10 | 5 |  | 3840 | 1.3281 | 1 | 1.3281 | 1
125 | Room | 643 | 42 |  | 1753 | 39 | 39 |  | 14024 | 2.751 | 1 | 2.751 | 1
126 | Room | 399 | 26 |  | 750 | 17 | 17 |  | 6000 | 3.99 | 1 | 3.99 | 1
134 | Room | 221 | 14 |  | 566 | 12 | 12 |  | 4528 | 2.9284 | 1 | 2.9284 | 1
135 | Room | 0 | 0 |  | 400 | 9 | 0 |  | 3200 | 0 | 0 | 0 | 0
136 | Room | 86 | 5 |  | 200 | 4 | 4 |  | 1600 | 3.225 | 1 | 3.225 | 1
137 | Womens Room | 0 | 0 |  | 280 | 6 | 0 |  | 2240 | 0 | 0 | 0 | 0
138 | Weight Room | 417 | 27 |  | 1500 | 34 | 27 |  | 12000 | 2.085 | 1 | 2.085 | 1
139 | PE Office | 0 | 0 |  | 176 | 4 | 0 |  | 1408 | 0 | 0 | 0 | 0
139 | Training Room | 0 | 0 |  | 139 | 3 | 0 |  | 1112 | 0 | 0 | 0 | 0
139A | Lavatory | 0 | 0 |  | 96 | 2 | 0 |  | 768 | 0 | 0 | 0 | 0
144 | Room | 235 | 15 |  | 1311 | 29 | 15 |  | 10488 | 1.3444 | 1 | 1.3444 | 1
145 | Env. Science Lab | 373 | 24 |  | 2349 | 53 | 24 |  | 18792 | 1.1909 | 1 | 1.1909 | 1
147 | IMC | 1282 | 85 |  | 4087 | 92 | 85 |  | 32696 | 2.3526 | 1 | 2.3526 | 1
201 | Room | 0 | 0 |  | 1200 | 27 | 0 |  | 9600 | 0 | 0 | 0 | 0
202 | Room | 371 | 24 |  | 864 | 19 | 19 |  | 6912 | 3.2205 | 1 | 3.2205 | 1
203 | Room | 294 | 19 |  | 864 | 19 | 19 |  | 6912 | 2.5521 | 1 | 2.5521 | 1
209 | Room | 401 | 26 |  | 952 | 21 | 21 |  | 7616 | 3.1591 | 1 | 3.1591 | 1
211 | Room | 367 | 24 |  | 960 | 21 | 21 |  | 7680 | 2.8672 | 1 | 2.8672 | 1
212 | Room | 292 | 19 |  | 960 | 21 | 19 |  | 7680 | 2.2812 | 1 | 2.2812 | 1
213 | Room | 295 | 19 |  | 960 | 21 | 19 |  | 7680 | 2.3047 | 1 | 2.3047 | 1
214 | Room | 0 | 0 |  | 960 | 21 | 0 |  | 7680 | 0 | 0 | 0 | 0
217 | Room | 271 | 18 |  | 1250 | 28 | 18 |  | 10000 | 1.626 | 1 | 1.626 | 1
220 | Room | 0 | 0 |  | 1408 | 32 | 0 |  | 11264 | 0 | 0 | 0 | 0
221 | Room | 95 | 6 |  | 1680 | 38 | 6 |  | 13440 | 0.42411 | 0 | 0.42411 | 0
222 | Room | 201 | 13 |  | 1200 | 27 | 13 |  | 9600 | 1.2563 | 1 | 1.2563 | 1
224 | Room | 392 | 26 |  | 1680 | 38 | 26 |  | 13440 | 1.75 | 1 | 1.75 | 1
226 | Room | 309 | 20 |  | 1680 | 38 | 20 |  | 13440 | 1.3795 | 1 | 1.3795 | 1
229 | Room | 0 | 0 |  | 1600 | 36 | 0 |  | 12800 | 0 | 0 | 0 | 0
230 | Room | 162 | 10 |  | 1680 | 38 | 10 |  | 13440 | 0.72321 | 0 | 0.72321 | 0
301 | Room | 0 | 0 |  | 1157 | 26 | 0 |  | 9256 | 0 | 0 | 0 | 0
302 | Room | 834 | 55 |  | 864 | 19 | 19 |  | 6912 | 7.2396 | 2 | 7.2396 | 2
303 | Room | 281 | 18 |  | 864 | 19 | 18 |  | 6912 | 2.4392 | 1 | 2.4392 | 1
309 | Room | 462 | 30 |  | 864 | 19 | 19 |  | 6912 | 4.0104 | 2 | 4.0104 | 2
311 | Room | 533 | 35 |  | 1041 | 23 | 23 |  | 8328 | 3.8401 | 1 | 3.8401 | 1
312 | Room | 201 | 13 |  | 1118 | 25 | 13 |  | 8944 | 1.3484 | 1 | 1.3484 | 1
313 | Room | 243 | 16 |  | 816 | 18 | 16 |  | 6528 | 2.2335 | 1 | 2.2335 | 1
314 | Room | 389 | 25 |  | 816 | 18 | 18 |  | 6528 | 3.5754 | 1 | 3.5754 | 1
317 | Room | 0 | 0 |  | 816 | 18 | 0 |  | 6528 | 0 | 0 | 0 | 0
318 | Room | 170 | 11 |  | 768 | 17 | 11 |  | 6144 | 1.6602 | 1 | 1.6602 | 1
320 | Room | 142 | 9 |  | 1056 | 24 | 9 |  | 8448 | 1.0085 | 1 | 1.0085 | 1
321 | Room | 487 | 32 |  | 1200 | 27 | 27 |  | 9600 | 3.0438 | 1 | 3.0438 | 1
322 | Room | 460 | 30 |  | 1200 | 27 | 27 |  | 9600 | 2.875 | 1 | 2.875 | 1
324 | Room | 75 | 5 |  | 1200 | 27 | 5 |  | 9600 | 0.46875 | 0 | 0.46875 | 0
327 | Room | 226 | 15 |  | 1519 | 34 | 15 |  | 12152 | 1.1159 | 1 | 1.1159 | 1
329 | Room | 400 | 26 |  | 1440 | 32 | 26 |  | 11520 | 2.0833 | 1 | 2.0833 | 1
- | Art Room | 756 | 50 |  | 2500 | 56 | 50 |  | 20000 | 2.268 | 1 | 2.268 | 1
- | Auditorium | 4245 | 283 |  | 5612 | 127 | 127 |  | 44896 | 5.6731 | 2 | 5.6731 | 2
- | Cafeteria | 6739 | 449 |  | 3826 | 86 | 86 |  | 30608 | 13.2103 | 3 | 13.2103 | 3
- | Dance Area | 104 | 6 |  | 1920 | 43 | 6 |  | 15360 | 0.40625 | 0 | 0.40625 | 0
- | Dance Studio | 1644 | 109 |  | 336 | 7 | 7 |  | 2688 | 36.6964 | 4 | 36.6964 | 4
- | Gymnasium | 13040 | 869 |  | 8949 | 203 | 203 |  | 71592 | 10.9286 | 3 | 10.9286 | 3
- | Female Student Locker Room | 579 | 38 |  | 1200 | 27 | 27 |  | 9600 | 3.6187 | 1 | 3.6187 | 1
- | Male Student Locker Room | 176 | 11 |  | 1200 | 27 | 11 |  | 9600 | 1.1 | 1 | 1.1 | 1
- | Female Staff Locker Room | 52 | 3 |  | 117 | 2 | 2 |  | 936 | 3.3333 | 1 | 3.3333 | 1
- | Male Staff Locker Room | 446 | 29 |  | 112 | 2 | 2 |  | 896 | 29.8661 | 4 | 29.8661 | 4
- | Male Staff Locker Room | 446 | 29 |  | 112 | 2 | 2 |  | 896 | 29.8661 | 4 | 29.8661 | 4
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-06 | [8 empty] | unk | unk | unk | unk
School: | Lewis C. Cassidy Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Boy's Gang Bathroom | 560 | 37 |  | 575 | 13 | 13 | House Fan | 4600 | 7.3043 | 2 | 7.3043 | 2
- | Girl's Gang Bathroom | 326 | 21 |  | 396 | 9 | 9 | House Fan | 3168 | 6.1742 | 2 | 6.1742 | 2
B | Teachers Lounge | 384 | 25 |  | 308 | 7 | 7 | House Fan | 2464 | 9.3506 | 2 | 9.3506 | 2
B2 | Office | 0 | 0 | Yes | 748 | 17 | 17 |  | 5984 | 0 | 0 | 20 | 3
B3 | Classroom | 741 | 49 |  | 742 | 16 | 16 | House Fan | 5936 | 7.4899 | 2 | 7.4899 | 2
B7 | Gym | 0 | 0 | Yes | 3872 | 88 | 88 | N/A | 30976 | 0 | 0 | 20 | 3
B8 | Classroom | 527 | 35 |  | 968 | 22 | 22 | House Fan | 7744 | 4.0832 | 2 | 4.0832 | 2
101 | Classroom | 542 | 36 |  | 660 | 15 | 15 | House Fan | 5280 | 6.1591 | 2 | 6.1591 | 2
102 | Classroom | 478 | 31 |  | 660 | 15 | 15 | House Fan | 5280 | 5.4318 | 2 | 5.4318 | 2
103 | Classroom | 538 | 35 |  | 660 | 15 | 15 | House Fan | 5280 | 6.1136 | 2 | 6.1136 | 2
104 | Classroom | 473 | 31 |  | 616 | 14 | 14 | House Fan | 4928 | 5.7589 | 2 | 5.7589 | 2
105 | Office | 0 | 0 |  | 132 | 3 | 0 | N/A | 1056 | 0 | 0 | 0 | 0
106 | Classroom | 682 | 45 |  | 704 | 16 | 16 | House Fan | 5632 | 7.2656 | 2 | 7.2656 | 2
107 | Classroom | 741 | 49 |  | 616 | 14 | 14 | House Fan | 4928 | 9.0219 | 2 | 9.0219 | 2
108 | Classroom | 812 | 54 |  | 660 | 15 | 15 | House Fan | 5280 | 9.2273 | 2 | 9.2273 | 2
109 | Classroom | 734 | 48 |  | 660 | 15 | 15 | House Fan | 5280 | 8.3409 | 2 | 8.3409 | 2
201 | Nurses Office | 0 | 0 | Yes | 176 | 4 | 4 | N/A | 1408 | 0 | 0 | 20 | 3
202 | Classroom | 551 | 36 |  | 792 | 18 | 18 | House Fan | 6336 | 5.2178 | 2 | 5.2178 | 2
203 | Classroom | 389 | 25 |  | 660 | 15 | 15 | House Fan | 5280 | 4.4205 | 2 | 4.4205 | 2
204 | Classroom | 471 | 31 |  | 660 | 15 | 15 | House Fan | 5280 | 5.3523 | 2 | 5.3523 | 2
205 | Teachers Lounge | 0 | 0 | Yes | 308 | 7 | 7 | N/A | 2464 | 0 | 0 | 20 | 3
206 | Asst Principal | 0 | 0 | Yes | 207 | 4 | 4 | N/A | 1656 | 0 | 0 | 20 | 3
207 | Classroom | 525 | 35 |  | 660 | 15 | 15 | House Fan | 5280 | 5.9659 | 2 | 5.9659 | 2
208 | Small Classroom | 0 | 0 | Yes | 220 | 5 | 5 | House Fan | 1760 | 0 | 0 | 20 | 3
209 | Classroom | 675 | 45 |  | 660 | 15 | 15 | House Fan | 5280 | 7.6705 | 2 | 7.6705 | 2
210 | Classroom | 551 | 36 |  | 616 | 14 | 14 | House Fan | 4928 | 6.7086 | 2 | 6.7086 | 2
211 | Classroom | 565 | 37 |  | 660 | 15 | 15 | House Fan | 5280 | 6.4205 | 2 | 6.4205 | 2
212 | Classroom | 611 | 40 |  | 660 | 15 | 15 | House Fan | 5280 | 6.9432 | 2 | 6.9432 | 2
213 | Office | 0 | 0 | Yes | 264 | 6 | 6 | N/A | 2112 | 0 | 0 | 20 | 3
301 | Office | 0 | 0 | Yes | 264 | 6 | 6 | N/A | 2112 | 0 | 0 | 20 | 3
302 | Classroom | 562 | 37 |  | 704 | 16 | 16 | House Fan | 5632 | 5.9872 | 2 | 5.9872 | 2
303 | Classroom | 430 | 28 |  | 704 | 16 | 16 | House Fan | 5632 | 4.581 | 2 | 4.581 | 2
304 | Classroom | 392 | 26 |  | 616 | 14 | 14 | House Fan | 4928 | 4.7727 | 2 | 4.7727 | 2
305 | Classroom | 507 | 33 |  | 616 | 14 | 14 | House Fan | 4928 | 6.1729 | 2 | 6.1729 | 2
306 | Classroom | 112 | 7 | Yes | 704 | 16 | 16 | House Fan | 5632 | 1.1932 | 1 | 21.1932 | 3
307 | Classroom | 465 | 31 |  | 748 | 17 | 17 | House Fan | 5984 | 4.6624 | 2 | 4.6624 | 2
308 | Classroom | 378 | 25 |  | 899 | 20 | 20 | House Fan | 7192 | 3.1535 | 1 | 3.1535 | 1
309 | Classroom | 378 | 25 |  | 704 | 16 | 16 | House Fan | 5632 | 4.027 | 2 | 4.027 | 2
310 | Classroom | 154 | 10 |  | 660 | 15 | 10 | House Fan | 5280 | 1.75 | 1 | 1.75 | 1
311 | Classroom | 518 | 34 |  | 616 | 14 | 14 | House Fan | 4928 | 6.3068 | 2 | 6.3068 | 2
312 | Classroom | 718 | 47 |  | 616 | 14 | 14 | House Fan | 4928 | 8.7419 | 2 | 8.7419 | 2
313 | Classroom | 550 | 36 |  | 660 | 15 | 15 | House Fan | 5280 | 6.25 | 2 | 6.25 | 2
314 | Classroom | 561 | 37 |  | 660 | 15 | 15 | House Fan | 5280 | 6.375 | 2 | 6.375 | 2
315 | Storage | 0 | 0 |  | 264 | 6 | 0 | N/A | 2112 | 0 | 0 | 0 | 0
- | Attwood Lunch Rm | 940 | 62 |  | 836 | 19 | 19 | House Fan | 6688 | 8.433 | 2 | 8.433 | 2
- | Auditorium | 1895 | 126 |  | 3608 | 82 | 82 | House Fan | 28864 | 3.9392 | 1 | 3.9392 | 1
- | Backstage Office | 0 | 0 |  | 132 | 3 | 0 | N/A | 1056 | 0 | 0 | 0 | 0
- | Lunch Room | 660 | 44 |  | 880 | 20 | 20 | House Fan | 7040 | 5.625 | 2 | 5.625 | 2
- | Library | 732 | 48 |  | 704 | 16 | 16 | House Fan | 5632 | 7.7983 | 2 | 7.7983 | 2
- | Main Office | 0 | 0 | Yes | 308 | 7 | 7 | N/A | 2464 | 0 | 0 | 20 | 3
- | Principal's Office | 0 | 0 | Yes | 132 | 3 | 3 | N/A | 1056 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-19 | [8 empty] | unk | unk | unk | unk
School: | Joseph W. Catharine Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | Main Building Part 2 | [7 empty] | unk | unk | unk | unk
School: | Joseph W. Catharine Elementary School Annex | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Main Building | [9 empty] | unk | unk | unk | unk
- | Lunch | 503 | 33 |  | 1247 | 28 | 28 | Unit Ventilator | 9976 | 3.0253 | 1 | 3.0253 | 1
- | Gym | 976 | 65 |  | 4544 | 103 | 65 | Unit Ventilator | 36352 | 1.6109 | 1 | 1.6109 | 1
102 | Classroom | 270 | 18 |  | 681 | 15 | 15 | Unit Ventilator | 5448 | 2.9736 | 1 | 2.9736 | 1
103 | Classroom | 313 | 20 |  | 550 | 12 | 12 | Unit Ventilator | 4400 | 4.2682 | 2 | 4.2682 | 2
104 | Classroom | 670 | 44 |  | 953 | 21 | 21 | Unit Ventilator | 7624 | 5.2728 | 2 | 5.2728 | 2
105 | Classroom | 0 | 0 | Yes | 953 | 21 | 21 | Unit Ventilator | 7624 | 0 | 0 | 20 | 3
106 | Classroom | 0 | 0 | Yes | 842 | 19 | 19 | Unit Ventilator | 6736 | 0 | 0 | 20 | 3
107 | Classroom | 627 | 41 |  | 1062 | 24 | 24 | Unit Ventilator | 8496 | 4.428 | 2 | 4.428 | 2
108 | Classroom | 307 | 20 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.7542 | 1 | 2.7542 | 1
- | Office | 212 | 14 |  | 367 | 8 | 8 | Unit Ventilator | 2936 | 4.3324 | 2 | 4.3324 | 2
201 | Classroom | 407 | 27 |  | 676 | 15 | 15 | Unit Ventilator | 5408 | 4.5155 | 2 | 4.5155 | 2
202 | Classroom | 331 | 22 |  | 683 | 15 | 15 | Unit Ventilator | 5464 | 3.6347 | 1 | 3.6347 | 1
203 | Classroom | 306 | 20 |  | 673 | 15 | 15 | Unit Ventilator | 5384 | 3.4101 | 1 | 3.4101 | 1
204 | Classroom | 144 | 9 | Yes | 708 | 16 | 16 | Unit Ventilator | 5664 | 1.5254 | 1 | 21.5254 | 3
205 | Classroom | 300 | 20 |  | 678 | 15 | 15 | Unit Ventilator | 5424 | 3.3186 | 1 | 3.3186 | 1
206 | Classroom | 0 | 0 | Yes | 855 | 19 | 19 | Unit Ventilator | 6840 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 504 | 11 | 11 | Unit Ventilator | 4032 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 672 | 15 | 15 | Unit Ventilator | 5376 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 | Yes | 709 | 16 | 16 | Unit Ventilator | 5672 | 0 | 0 | 20 | 3
210 | Classroom | 0 | 0 | Yes | 705 | 16 | 16 | Unit Ventilator | 5640 | 0 | 0 | 20 | 3
211 | Classroom | 0 | 0 | Yes | 673 | 15 | 15 | Unit Ventilator | 5384 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 | Yes | 684 | 15 | 15 | Unit Ventilator | 5472 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 684 | 15 | 15 | Unit Ventilator | 5472 | 0 | 0 | 20 | 3
303 | Classroom | 0 | 0 | Yes | 679 | 15 | 15 | Unit Ventilator | 5432 | 0 | 0 | 20 | 3
304 | Classroom | 173 | 11 | Yes | 708 | 16 | 16 | Unit Ventilator | 5664 | 1.8326 | 1 | 21.8326 | 3
305 | Classroom | 209 | 13 | Yes | 698 | 15 | 15 | Unit Ventilator | 5584 | 2.2457 | 1 | 22.2457 | 3
306 | Classroom | 0 | 0 | Yes | 872 | 19 | 19 | Unit Ventilator | 6976 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 | Yes | 675 | 15 | 15 | Unit Ventilator | 5400 | 0 | 0 | 20 | 3
308 | Classroom | 198 | 13 | Yes | 674 | 15 | 15 | Unit Ventilator | 5392 | 2.2033 | 1 | 22.2033 | 3
309 | Classroom | 284 | 18 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 3.0213 | 1 | 3.0213 | 1
310 | Classroom | 297 | 19 |  | 707 | 16 | 16 | Unit Ventilator | 5656 | 3.1506 | 1 | 3.1506 | 1
311 | Classroom | 0 | 0 | Yes | 674 | 15 | 15 | Unit Ventilator | 5392 | 0 | 0 | 20 | 3
- | Principal's office | 0 | 0 | Yes | 359 | 8 | 8 |  | 2872 | 0 | 0 | 20 | 3
- | Nurse office | 0 | 0 | Yes | 324 | 7 | 7 |  | 2592 | 0 | 0 | 20 | 3
- | Counselor Office | 0 | 0 | Yes | 109 | 2 | 2 |  | 872 | 0 | 0 | 20 | 3
Joseph W. Catherine Elementary School Annex | [9 empty] | unk | unk | unk | unk
100 | Office |  | 0 | Yes | 273 | 6 | 6 | N/A | 2184 | unk | unk | 20 | 3
102 | K-1 Room |  | 0 | Yes | 680 | 15 | 15 | N/A | 5440 | unk | unk | 20 | 3
104 | K-2 Room |  | 0 | Yes | 714 | 16 | 16 | N/A | 5712 | unk | unk | 20 | 3
213 | K-3 |  | 0 | Yes | 1056 | 24 | 24 | N/A | 8448 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-28 | [8 empty] | unk | unk | unk | unk
School: | Cayuga Elementary School (former St. Henry’s) | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Devine Brothers Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | classroom | 355 | 23 |  | 830 | 18 | 18 | Unit Ventilator | 6640 | 3.2078 | 1 | 3.2078 | 1
102 | classroom | 375 | 25 |  | 740 | 16 | 16 | Unit Ventilator | 5920 | 3.8007 | 1 | 3.8007 | 1
103 | classroom | 315 | 21 |  | 795 | 18 | 18 | Unit Ventilator | 6360 | 2.9717 | 1 | 2.9717 | 1
104 | classroom | 280 | 18 |  | 796 | 18 | 18 | Unit Ventilator | 6368 | 2.6382 | 1 | 2.6382 | 1
105 | Nurse's Office |  | 0 | Yes | 330 | 7 | 7 | N/A | 2640 | unk | unk | 20 | 3
106 | classroom | 275 | 18 |  | 403 | 9 | 9 | Unit Ventilator | 3224 | 5.1179 | 2 | 5.1179 | 2
117 | classroom | 736 | 49 |  | 806 | 18 | 18 | Unit Ventilator | 6448 | 6.8486 | 2 | 6.8486 | 2
118 | classroom | 625 | 41 |  | 688 | 15 | 15 | Unit Ventilator | 5504 | 6.8132 | 2 | 6.8132 | 2
119 | classroom | 586 | 39 |  | 845 | 19 | 19 | Unit Ventilator | 6760 | 5.2012 | 2 | 5.2012 | 2
120 | classroom | 335 | 22 |  | 670 | 15 | 15 | Unit Ventilator | 5360 | 3.75 | 1 | 3.75 | 1
201 | classroom | 325 | 21 |  | 830 | 18 | 18 | Unit Ventilator | 6640 | 2.9367 | 1 | 2.9367 | 1
202 | classroom | 305 | 20 |  | 740 | 16 | 16 | Unit Ventilator | 5920 | 3.0912 | 1 | 3.0912 | 1
203 | classroom | 380 | 25 |  | 795 | 18 | 18 | Unit Ventilator | 6360 | 3.5849 | 1 | 3.5849 | 1
204 | classroom | 360 | 24 |  | 796 | 18 | 18 | Unit Ventilator | 6368 | 3.392 | 1 | 3.392 | 1
205 | classroom | 355 | 23 |  | 765 | 17 | 17 | Unit Ventilator | 6120 | 3.4804 | 1 | 3.4804 | 1
206 | classroom | 310 | 20 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.9808 | 1 | 2.9808 | 1
214 | classroom | 375 | 25 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 3.8633 | 1 | 3.8633 | 1
215 | classroom | 365 | 24 |  | 693 | 15 | 15 | Unit Ventilator | 5544 | 3.9502 | 1 | 3.9502 | 1
216 | classroom | 330 | 22 |  | 737 | 16 | 16 | Unit Ventilator | 5896 | 3.3582 | 1 | 3.3582 | 1
217 | classroom | 1606 | 107 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 14.6533 | 3 | 14.6533 | 3
301 | classroom | 345 | 23 |  | 830 | 18 | 18 | Unit Ventilator | 6640 | 3.1175 | 1 | 3.1175 | 1
302 | classroom | 275 | 18 |  | 740 | 16 | 16 | Unit Ventilator | 5920 | 2.7872 | 1 | 2.7872 | 1
303 | classroom | 380 | 25 |  | 795 | 18 | 18 | Unit Ventilator | 6360 | 3.5849 | 1 | 3.5849 | 1
304 | classroom | 380 | 25 |  | 796 | 18 | 18 | Unit Ventilator | 6368 | 3.5804 | 1 | 3.5804 | 1
305 | classroom | 553 | 36 |  | 765 | 17 | 17 | Unit Ventilator | 6120 | 5.4216 | 2 | 5.4216 | 2
306 | classroom | 315 | 21 |  | 790 | 17 | 17 | Unit Ventilator | 6320 | 2.9905 | 1 | 2.9905 | 1
- | Gym | 1213 | 80 |  | 2754 | 62 | 62 | AHU | 22032 | 3.3034 | 1 | 3.3034 | 1
- | Basement Corridor | 90 | 6 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | Main Entrance Corridor | 46 | 3 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | 1st Floor Corridor | 31 | 2 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | Cafeteria | 936 | 62 |  | 3432 | 78 | 62 | AHU | 27456 | 2.0455 | 1 | 2.0455 | 1
Sheet Last Modified: | 2091-04-29 | [8 empty] | unk | unk | unk | unk
School: | Central High School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Ceramic | 253 | 16 |  | 723 | 16 | 16 |  | 5784 | 2.6245 | 1 | 2.6245 | 1
2 | Kiln | 58 | 3 |  | 128 | 2 | 2 |  | 1024 | 3.3984 | 1 | 3.3984 | 1
3 | Drafting Studio | 403 | 26 |  | 1366 | 31 | 26 |  | 10928 | 2.2127 | 1 | 2.2127 | 1
4 | Fashion | 40 | 2 |  | 290 | 6 | 2 |  | 2320 | 1.0345 | 1 | 1.0345 | 1
5 | Office | 64 | 4 |  | 349 | 7 | 4 |  | 2792 | 1.3754 | 1 | 1.3754 | 1
6 | Photography | 32 | 2 |  | 171 | 3 | 2 |  | 1368 | 1.4035 | 1 | 1.4035 | 1
7 | Computer Lab | 31 | 2 |  | 148 | 3 | 2 |  | 1184 | 1.5709 | 1 | 1.5709 | 1
8 | Art Studio | 356 | 23 |  | 1452 | 33 | 23 |  | 11616 | 1.8388 | 1 | 1.8388 | 1
9 | Printing Studio | 70 | 4 |  | 390 | 8 | 4 |  | 3120 | 1.3462 | 1 | 1.3462 | 1
12 | Classroom | 333 | 22 |  | 840 | 19 | 19 |  | 6720 | 2.9732 | 1 | 2.9732 | 1
13 | Classroom | 388 | 25 |  | 709 | 16 | 16 |  | 5672 | 4.1044 | 2 | 4.1044 | 2
82 | Classroom | 301 | 20 |  | 1714 | 38 | 20 |  | 13712 | 1.3171 | 1 | 1.3171 | 1
84 | Classroom | 300 | 20 |  | 1531 | 34 | 20 |  | 12248 | 1.4696 | 1 | 1.4696 | 1
85 | Classroom | 300 | 20 |  | 1594 | 36 | 20 |  | 12752 | 1.4115 | 1 | 1.4115 | 1
89 | Classroom | 389 | 25 |  | 1327 | 30 | 25 |  | 10616 | 2.1986 | 1 | 2.1986 | 1
95 | Classroom | 604 | 40 |  | 1307 | 29 | 29 |  | 10456 | 3.466 | 1 | 3.466 | 1
97 | Classroom | 605 | 40 |  | 1216 | 27 | 27 |  | 9728 | 3.7315 | 1 | 3.7315 | 1
98 | Classroom | 428 | 28 |  | 1374 | 31 | 28 |  | 10992 | 2.3362 | 1 | 2.3362 | 1
99 | Classroom | 432 | 28 |  | 1258 | 28 | 28 |  | 10064 | 2.5755 | 1 | 2.5755 | 1
101 | Classroom | 376 | 25 |  | 876 | 19 | 19 |  | 7008 | 3.2192 | 1 | 3.2192 | 1
102 | Classroom | 370 | 24 |  | 852 | 19 | 19 |  | 6816 | 3.257 | 1 | 3.257 | 1
103 | Classroom | 387 | 25 |  | 876 | 19 | 19 |  | 7008 | 3.3134 | 1 | 3.3134 | 1
104 | Classroom | 316 | 21 |  | 700 | 15 | 15 |  | 5600 | 3.3857 | 1 | 3.3857 | 1
105 | Classroom | 305 | 20 |  | 675 | 15 | 15 |  | 5400 | 3.3889 | 1 | 3.3889 | 1
106 | Classroom | 283 | 18 |  | 687 | 15 | 15 |  | 5496 | 3.0895 | 1 | 3.0895 | 1
107 | Classroom | 288 | 19 |  | 706 | 16 | 16 |  | 5648 | 3.0595 | 1 | 3.0595 | 1
108 | Classroom | 329 | 21 |  | 700 | 15 | 15 |  | 5600 | 3.525 | 1 | 3.525 | 1
109 | Classroom | 0 | 0 |  | 675 | 15 | 0 |  | 5400 | 0 | 0 | 0 | 0
110 | Office | 248 | 16 |  | 339 | 7 | 7 |  | 2712 | 5.4867 | 2 | 5.4867 | 2
111 | Classroom | 0 | 0 |  | 654 | 14 | 0 |  | 5232 | 0 | 0 | 0 | 0
119 | Classroom | 0 | 0 |  | 470 | 10 | 0 |  | 3760 | 0 | 0 | 0 | 0
120 | Classroom | 332 | 22 |  | 857 | 19 | 19 |  | 6856 | 2.9055 | 1 | 2.9055 | 1
121 | Classroom | 366 | 24 |  | 694 | 15 | 15 |  | 5552 | 3.9553 | 1 | 3.9553 | 1
122 | Classroom | 346 | 23 |  | 724 | 16 | 16 |  | 5792 | 3.5843 | 1 | 3.5843 | 1
123 | Classroom | 297 | 19 |  | 694 | 15 | 15 |  | 5552 | 3.2097 | 1 | 3.2097 | 1
124 | Classroom | 280 | 18 |  | 680 | 15 | 15 |  | 5440 | 3.0882 | 1 | 3.0882 | 1
125 | Classroom | 427 | 28 |  | 683 | 15 | 15 |  | 5464 | 4.6889 | 2 | 4.6889 | 2
126 | Classroom | 415 | 27 |  | 720 | 16 | 16 |  | 5760 | 4.3229 | 2 | 4.3229 | 2
127 | Classroom | 290 | 19 |  | 722 | 16 | 16 |  | 5776 | 3.0125 | 1 | 3.0125 | 1
136 | Classroom | 281 | 18 |  | 297 | 6 | 6 |  | 2376 | 7.096 | 2 | 7.096 | 2
138 | Principal | 176 | 11 |  | 235 | 5 | 5 |  | 1880 | 5.617 | 2 | 5.617 | 2
141 | Classroom | 293 | 19 |  | 690 | 15 | 15 |  | 5520 | 3.1848 | 1 | 3.1848 | 1
142 | Office | 377 | 25 |  | 982 | 22 | 22 |  | 7856 | 2.8793 | 1 | 2.8793 | 1
143 | Classroom | 405 | 27 |  | 700 | 15 | 15 |  | 5600 | 4.3393 | 2 | 4.3393 | 2
144 | Roster Office | 179 | 11 |  | 652 | 14 | 11 |  | 5216 | 2.059 | 1 | 2.059 | 1
201 | Classroom | 0 | 0 |  | 530 | 12 | 0 |  | 4240 | 0 | 0 | 0 | 0
202 | Classroom | 288 | 19 |  | 834 | 18 | 18 |  | 6672 | 2.5899 | 1 | 2.5899 | 1
203 | Classroom | 293 | 19 |  | 681 | 15 | 15 |  | 5448 | 3.2269 | 1 | 3.2269 | 1
204 | Classroom | 288 | 19 |  | 692 | 15 | 15 |  | 5536 | 3.1214 | 1 | 3.1214 | 1
205 | Classroom | 283 | 18 |  | 676 | 15 | 15 |  | 5408 | 3.1398 | 1 | 3.1398 | 1
206 | Classroom | 344 | 22 |  | 681 | 15 | 15 |  | 5448 | 3.7885 | 1 | 3.7885 | 1
207 | Classroom | 344 | 22 |  | 705 | 16 | 16 |  | 5640 | 3.6596 | 1 | 3.6596 | 1
208 | Classroom | 286 | 19 |  | 682 | 15 | 15 |  | 5456 | 3.1452 | 1 | 3.1452 | 1
209 | Classroom | 306 | 20 |  | 694 | 15 | 15 |  | 5552 | 3.3069 | 1 | 3.3069 | 1
210 | Office | 226 | 15 |  | 336 | 7 | 7 |  | 2688 | 5.0446 | 2 | 5.0446 | 2
211 | Classroom | 0 | 0 |  | 650 | 14 | 0 |  | 5200 | 0 | 0 | 0 | 0
224 | Classroom | 646 | 43 |  | 831 | 18 | 18 |  | 6648 | 5.8303 | 2 | 5.8303 | 2
225 | Classroom | 289 | 19 |  | 800 | 18 | 18 |  | 6400 | 2.7094 | 1 | 2.7094 | 1
226 | Classroom | 286 | 19 |  | 700 | 15 | 15 |  | 5600 | 3.0643 | 1 | 3.0643 | 1
227 | Classroom | 0 | 0 |  | 693 | 15 | 0 |  | 5544 | 0 | 0 | 0 | 0
229 | Classroom | 377 | 25 |  | 676 | 15 | 15 |  | 5408 | 4.1827 | 2 | 4.1827 | 2
230 | Classroom | 358 | 23 |  | 680 | 15 | 15 |  | 5440 | 3.9485 | 1 | 3.9485 | 1
231 | Classroom | 0 | 0 |  | 680 | 15 | 0 |  | 5440 | 0 | 0 | 0 | 0
232 | Classroom | 315 | 21 |  | 638 | 14 | 14 |  | 5104 | 3.703 | 1 | 3.703 | 1
233 | Classroom | 246 | 16 |  | 597 | 13 | 13 |  | 4776 | 3.0905 | 1 | 3.0905 | 1
244 | Classroom | 357 | 23 |  | 840 | 19 | 19 |  | 6720 | 3.1875 | 1 | 3.1875 | 1
245 | Classroom | 316 | 21 |  | 840 | 19 | 19 |  | 6720 | 2.8214 | 1 | 2.8214 | 1
246 | Classroom | 315 | 21 |  | 683 | 15 | 15 |  | 5464 | 3.459 | 1 | 3.459 | 1
247 | Classroom | 368 | 24 |  | 686 | 15 | 15 |  | 5488 | 4.0233 | 2 | 4.0233 | 2
248 | Classroom | 401 | 26 |  | 705 | 16 | 16 |  | 5640 | 4.266 | 2 | 4.266 | 2
249 | Classroom | 379 | 25 |  | 694 | 15 | 15 |  | 5552 | 4.0958 | 2 | 4.0958 | 2
250 | Classroom | 314 | 20 |  | 687 | 15 | 15 |  | 5496 | 3.4279 | 1 | 3.4279 | 1
251 | Classroom | 458 | 30 |  | 705 | 16 | 16 |  | 5640 | 4.8723 | 2 | 4.8723 | 2
252 | Classroom | 364 | 24 |  | 670 | 15 | 15 |  | 5360 | 4.0746 | 2 | 4.0746 | 2
253 | Classroom | 314 | 20 |  | 330 | 7 | 7 |  | 2640 | 7.1364 | 2 | 7.1364 | 2
302 | classroom | 483 | 32 |  | 1260 | 28 | 28 |  | 10080 | 2.875 | 1 | 2.875 | 1
303 | Classroom | 331 | 22 |  | 1145 | 26 | 22 |  | 9160 | 2.1681 | 1 | 2.1681 | 1
304 | Classroom | 291 | 19 |  | 670 | 15 | 15 |  | 5360 | 3.2575 | 1 | 3.2575 | 1
305 | Theater | 250 | 16 |  | 480 | 10 | 10 |  | 3840 | 3.9062 | 1 | 3.9062 | 1
306 | Classroom | 430 | 28 |  | 661 | 15 | 15 |  | 5288 | 4.879 | 2 | 4.879 | 2
307 | Classroom | 478 | 31 |  | 657 | 14 | 14 |  | 5256 | 5.4566 | 2 | 5.4566 | 2
308 | Classroom | 209 | 13 |  | 624 | 14 | 13 |  | 4992 | 2.512 | 1 | 2.512 | 1
309 | Classroom | 200 | 13 |  | 700 | 15 | 13 |  | 5600 | 2.1429 | 1 | 2.1429 | 1
311 | Computer Lab | 64 | 4 |  | 827 | 18 | 4 |  | 6616 | 0.58041 | 0 | 0.58041 | 0
321C | Storage | 210 | 14 |  | 157 | 3 | 3 |  | 1256 | 10.0318 | 3 | 10.0318 | 3
323 | Classroom | 256 | 17 |  | 1082 | 24 | 17 |  | 8656 | 1.7745 | 1 | 1.7745 | 1
325 | Computer Lab | 314 | 20 |  | 654 | 14 | 14 |  | 5232 | 3.6009 | 1 | 3.6009 | 1
326 | Classroom | 294 | 19 |  | 654 | 14 | 14 |  | 5232 | 3.3716 | 1 | 3.3716 | 1
327 | Computer Lab | 356 | 23 |  | 654 | 14 | 14 |  | 5232 | 4.0826 | 2 | 4.0826 | 2
328 | Music Room | 289 | 19 |  | 647 | 14 | 14 |  | 5176 | 3.3501 | 1 | 3.3501 | 1
329 | Computer Lab | 205 | 13 |  | 296 | 6 | 6 |  | 2368 | 5.1943 | 2 | 5.1943 | 2
402 | Classroom | 625 | 41 |  | 941 | 21 | 21 |  | 7528 | 4.9814 | 2 | 4.9814 | 2
403 | Classroom | 391 | 26 |  | 779 | 17 | 17 |  | 6232 | 3.7644 | 1 | 3.7644 | 1
406 | Classroom | 531 | 35 |  | 1102 | 25 | 25 |  | 8816 | 3.6139 | 1 | 3.6139 | 1
407 | Classroom | 510 | 34 |  | 1102 | 25 | 25 |  | 8816 | 3.471 | 1 | 3.471 | 1
Gym | Gym |  | 0 | Yes | 16550 | 376 | 376 |  | 132400 | unk | unk | 20 | 3
- | Office Break Rm | 240 | 16 |  | 170 | 3 | 3 |  | 1360 | 10.5882 | 3 | 10.5882 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-05-03 | [8 empty] | unk | unk | unk | unk
School: | George W. Childs Elementary School @ Barratt | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Classroom |  | 0 | Yes | 1575 | 35 | 35 |  | 12600 | unk | unk | 20 | 3
2 | Classroom |  | 0 | Yes | 1075 | 24 | 24 |  | 8600 | unk | unk | 20 | 3
3 | Head Start Kitchen |  | 0 | Yes | 696 | 15 | 15 | House Fan | 5568 | unk | unk | 20 | 3
4 | - |  | 0 |  | 1224 | 27 | 0 | House Fan | 9792 | unk | unk | unk | unk
5 | - |  | 0 | Yes | 1035 | 23 | 23 | House Fan | 8280 | unk | unk | 20 | 3
8 | Classroom |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | unk | unk | unk | unk
100B | VP's Office |  | 0 |  | 143 | 3 | 0 | House Fan | 1144 | unk | unk | unk | unk
100C | Conference Room |  | 0 |  | 221 | 5 | 0 | House Fan | 1768 | unk | unk | unk | unk
102 | Classroom |  | 0 | Yes | 1012 | 23 | 23 | House Fan | 8096 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 1012 | 23 | 23 | House Fan | 8096 | unk | unk | 20 | 3
105 | Classroom |  | 0 | Yes | 851 | 19 | 19 | House Fan | 6808 | unk | unk | 20 | 3
105a | - |  | 0 | Yes | 575 | 13 | 13 | House Fan | 4600 | unk | unk | 20 | 3
106 | Classroom |  | 0 | Yes | 800 | 18 | 18 | House Fan | 6400 | unk | unk | 20 | 3
107 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
109A | Counsleor |  | 0 |  | 240 | 5 | 0 | House Fan | 1920 | unk | unk | unk | unk
109C | Dicipline Room |  | 0 |  | 240 | 5 | 0 |  | 1920 | unk | unk | unk | unk
118 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
119 | Nurse |  | 0 | Yes | 420 | 9 | 9 | House Fan | 3360 | unk | unk | 20 | 3
121 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 460 | 10 | 10 | House Fan | 3680 | unk | unk | 20 | 3
206 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
207 | Classroom |  | 0 | Yes | 504 | 11 | 11 | House Fan | 4032 | unk | unk | 20 | 3
208 | Classroom |  | 0 | Yes | 912 | 20 | 20 | House Fan | 7296 | unk | unk | 20 | 3
209 | Classroom |  | 0 | Yes | 828 | 18 | 18 | House Fan | 6624 | unk | unk | 20 | 3
210 | - |  | 0 | Yes | 912 | 20 | 20 | House Fan | 7296 | unk | unk | 20 | 3
212 | Classroom |  | 0 | Yes | 902 | 20 | 20 | House Fan | 7216 | unk | unk | 20 | 3
214 | Classroom |  | 0 | Yes | 966 | 21 | 21 | House Fan | 7728 | unk | unk | 20 | 3
215 | Classroom |  | 0 | Yes | 748 | 17 | 17 | House Fan | 5984 | unk | unk | 20 | 3
216 | Classroom |  | 0 | Yes | 1012 | 23 | 23 | House Fan | 8096 | unk | unk | 20 | 3
217 | - |  | 0 | Yes | 1450 | 32 | 32 | House Fan | 11600 | unk | unk | 20 | 3
219 | Classroom |  | 0 |  | 1450 | 32 | 0 | House Fan | 11600 | unk | unk | unk | unk
220 | Classroom |  | 0 | Yes | 1058 | 24 | 24 | House Fan | 8464 | unk | unk | 20 | 3
222 | - |  | 0 | Yes | 1058 | 24 | 24 | House Fan | 8464 | unk | unk | 20 | 3
224 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
224B | - |  | 0 | Yes | 689 | 15 | 15 | House Fan | 5512 | unk | unk | 20 | 3
226 | Classroom |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | unk | unk | unk | unk
2nd Floor | Special Needs Changing Room |  | 0 | Yes | 180 | 4 | 4 |  | 1440 | unk | unk | 20 | 3
301 | Classroom |  | 0 | Yes | 989 | 22 | 22 | House Fan | 7912 | unk | unk | 20 | 3
302 | Classroom |  | 0 | Yes | 989 | 22 | 22 | House Fan | 7912 | unk | unk | 20 | 3
304 | - |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | unk | unk | unk | unk
305 | - |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
306 | - |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
307 | Classroom |  | 0 | Yes | 552 | 12 | 12 | House Fan | 4416 | unk | unk | 20 | 3
308 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
309 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
310 | Classroom |  | 0 | Yes | 805 | 18 | 18 | House Fan | 6440 | unk | unk | 20 | 3
311 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
313 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
314 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
315 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
316 | Teacher's Lounge |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
401 | - |  | 0 |  | 989 | 22 | 0 | House Fan | 7912 | unk | unk | unk | unk
402 | - |  | 0 | Yes | 989 | 22 | 22 | House Fan | 7912 | unk | unk | 20 | 3
404 | Classroom |  | 0 | Yes | 989 | 22 | 22 | House Fan | 7912 | unk | unk | 20 | 3
405 | Classroom |  | 0 |  | 460 | 10 | 0 | House Fan | 3680 | unk | unk | unk | unk
406 | - |  | 0 | Yes | 989 | 22 | 22 | House Fan | 7912 | unk | unk | 20 | 3
407 | - |  | 0 | Yes | 828 | 18 | 18 | House Fan | 6624 | unk | unk | 20 | 3
408 | Classroom |  | 0 | Yes | 989 | 22 | 22 | House Fan | 7912 | unk | unk | 20 | 3
409 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
411 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
412 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
| Auditorium |  | 0 |  | 4128 | 93 | 0 |  | 33024 | unk | unk | unk | unk
- | Cafeteria |  | 0 | Yes | 5512 | 125 | 125 | House Fan | 44096 | unk | unk | 20 | 3
- | Special Needs Classroom |  | 0 | Yes | 345 | 7 | 7 | House Fan | 2760 | unk | unk | 20 | 3
- | IMC |  | 0 | Yes | 1725 | 39 | 39 | House Fan | 13800 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 726 | 16 | 16 | House Fan | 5808 | unk | unk | 20 | 3
- | Music Room |  | 0 |  | 726 | 16 | 0 | House Fan | 5808 | unk | unk | unk | unk
- | Principal |  | 0 | Yes | 312 | 7 | 7 | House Fan | 2496 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Roberto Clemente Middle School and The LINC High School | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Part 2 | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 126 | 8 |  | 664 | 15 | 8 | 1 Univent & 1 AHU | 5312 | 1.4232 | 1 | 1.4232 | 1
102 | Classroom | 54 | 3 |  | 664 | 15 | 3 | Univent | 5312 | 0.60994 | 0 | 0.60994 | 0
103 | Classroom | 95 | 6 |  | 664 | 15 | 6 | 1 Univent & 1 AHU | 5312 | 1.073 | 1 | 1.073 | 1
104 | Classroom | 54 | 3 |  | 664 | 15 | 3 | Univent | 5312 | 0.60994 | 0 | 0.60994 | 0
106 | Classroom | 24 | 1 |  | 312 | 7 | 1 |  | 2496 | 0.57692 | 0 | 0.57692 | 0
107 | Classroom | 179 | 11 |  | 682 | 15 | 11 | 1 Unitvent & 2 AHU | 5456 | 1.9685 | 1 | 1.9685 | 1
108 | Classroom | 108 | 7 |  | 682 | 15 | 7 | 1 Univent & 1 AHU | 5456 | 1.1877 | 1 | 1.1877 | 1
109 | Classroom | 83 | 5 |  | 672 | 15 | 5 | 1 Univent & 1 AHU | 5376 | 0.92634 | 0 | 0.92634 | 0
110 | Classroom | 54 | 3 |  | 530 | 12 | 3 | 1 Univent & 1 AHU | 4240 | 0.76415 | 0 | 0.76415 | 0
111 | Classroom | 86 | 5 |  | 984 | 22 | 5 | 1 Univent & 1 AHU | 7872 | 0.65549 | 0 | 0.65549 | 0
112 | Classroom | 113 | 7 |  | 984 | 22 | 7 | 1 Univent & 1 AHU | 7872 | 0.86128 | 0 | 0.86128 | 0
113 | Classroom | 116 | 7 |  | 987 | 22 | 7 | 1 Univent & 1 AHU | 7896 | 0.88146 | 0 | 0.88146 | 0
114 | Classroom | 87 | 5 |  | 987 | 22 | 5 | 1 Univent & 1 AHU | 7896 | 0.66109 | 0 | 0.66109 | 0
115 | Classroom | 87 | 5 |  | 987 | 22 | 5 | 1 Univent & 1 AHU | 7896 | 0.66109 | 0 | 0.66109 | 0
116 | Classroom | 82 | 5 |  | 987 | 22 | 5 | 1 Univent & 1 AHU | 7896 | 0.6231 | 0 | 0.6231 | 0
121 | - | 24 | 1 |  | 264 | 6 | 1 |  | 2112 | 0.68182 | 0 | 0.68182 | 0
125 | Classroom | 24 | 1 |  | 132 | 3 | 1 |  | 1056 | 1.3636 | 1 | 1.3636 | 1
126 | Classroom | 24 | 1 |  | 132 | 3 | 1 |  | 1056 | 1.3636 | 1 | 1.3636 | 1
128 | Classroom | 24 | 1 |  | 120 | 2 | 1 |  | 960 | 1.5 | 1 | 1.5 | 1
129 | Classroom | 24 | 1 |  | 120 | 2 | 1 |  | 960 | 1.5 | 1 | 1.5 | 1
131 | Classroom | 24 | 1 |  | 120 | 2 | 1 |  | 960 | 1.5 | 1 | 1.5 | 1
132 | Classroom | 24 | 1 |  | 120 | 2 | 1 |  | 960 | 1.5 | 1 | 1.5 | 1
144 | Classroom | 11 | 0 |  | 109 | 2 | 0 |  | 872 | 0.75688 | 0 | 0.75688 | 0
145 | Classroom | 11 | 0 |  | 70 | 1 | 0 |  | 560 | 1.1786 | 1 | 1.1786 | 1
146 | Classroom | 10 | 0 |  | 286 | 6 | 0 |  | 2288 | 0.26224 | 0 | 0.26224 | 0
147 | Classroom | 10 | 0 |  | 160 | 3 | 0 |  | 1280 | 0.46875 | 0 | 0.46875 | 0
148 | Classroom | 10 | 0 |  | 80 | 1 | 0 |  | 640 | 0.9375 | 0 | 0.9375 | 0
149 | Classroom | 10 | 0 |  | 90 | 2 | 0 |  | 720 | 0.83333 | 0 | 0.83333 | 0
150 | Classroom | 10 | 0 |  | 108 | 2 | 0 |  | 864 | 0.69444 | 0 | 0.69444 | 0
151 | Classroom | 10 | 0 |  | 70 | 1 | 0 |  | 560 | 1.0714 | 1 | 1.0714 | 1
152 | Classroom | 10 | 0 |  | 108 | 2 | 0 |  | 864 | 0.69444 | 0 | 0.69444 | 0
153 | Classroom | 10 | 0 |  | 108 | 2 | 0 |  | 864 | 0.69444 | 0 | 0.69444 | 0
201 | Classroom | 91 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 6528 | 0.8364 | 0 | 0.8364 | 0
202 | Classroom | 63 | 4 |  | 816 | 18 | 4 | 1 Univent & 1 AHU | 6528 | 0.57904 | 0 | 0.57904 | 0
203 | Classroom | 86 | 5 |  | 816 | 18 | 5 | 1 Univent & 1 AHU | 6528 | 0.79044 | 0 | 0.79044 | 0
204 | Classroom | 48 | 3 |  | 816 | 18 | 3 | 1 Univent & 1 AHU | 6528 | 0.44118 | 0 | 0.44118 | 0
205 | Classroom | 96 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 6528 | 0.88235 | 0 | 0.88235 | 0
206 | Classroom | 198 | 13 |  | 816 | 18 | 13 | 1 Univent & 1 AHU | 6528 | 1.8199 | 1 | 1.8199 | 1
207 | Classroom | 199 | 13 |  | 816 | 18 | 13 | 1 Univent & 1 AHU | 6528 | 1.829 | 1 | 1.829 | 1
208 | Classroom | 69 | 4 |  | 816 | 18 | 4 | 1 Univent & 1 AHU | 6528 | 0.63419 | 0 | 0.63419 | 0
209 | Classroom | 186 | 12 |  | 816 | 18 | 12 | 1 Univent & 1 AHU | 6528 | 1.7096 | 1 | 1.7096 | 1
210 | Classroom | 91 | 6 |  | 792 | 18 | 6 | 1 Univent & 1 AHU | 6336 | 0.86174 | 0 | 0.86174 | 0
211 | Classroom | 191 | 12 |  | 675 | 15 | 12 | 1 Univent & 1 AHU | 5400 | 2.1222 | 1 | 2.1222 | 1
212 | Classroom | 62 | 4 |  | 624 | 14 | 4 | 1 Univent & 1 AHU | 4992 | 0.74519 | 0 | 0.74519 | 0
213 | Classroom | 150 | 10 |  | 675 | 15 | 10 | 1 Univent & 1 AHU | 5400 | 1.6667 | 1 | 1.6667 | 1
214 | Classroom | 67 | 4 |  | 775 | 17 | 4 | 1 Univent & 1 AHU | 6200 | 0.64839 | 0 | 0.64839 | 0
215 | Classroom | 90 | 6 |  | 675 | 15 | 6 | 1 Univent & 1 AHU | 5400 | 1 | 0 | 1 | 0
216 | Classroom | 44 | 2 |  | 689 | 15 | 2 | 1 Univent & 1 AHU | 5512 | 0.47896 | 0 | 0.47896 | 0
217 | Classroom | 74 | 4 |  | 684 | 15 | 4 | 1 Univent & 1 AHU | 5472 | 0.8114 | 0 | 0.8114 | 0
218 | Classroom | 64 | 4 |  | 684 | 15 | 4 | 1 Univent & 1 AHU | 5472 | 0.70175 | 0 | 0.70175 | 0
219 | Classroom | 163 | 10 |  | 768 | 17 | 10 | 1 Univent & 1 AHU | 6144 | 1.5918 | 1 | 1.5918 | 1
220 | Classroom | 42 | 2 |  | 768 | 17 | 2 | 1 Univent & 1 AHU | 6144 | 0.41016 | 0 | 0.41016 | 0
221 | Classroom | 68 | 4 |  | 768 | 17 | 4 | 1 Univent & 1 AHU | 6144 | 0.66406 | 0 | 0.66406 | 0
222 | Classroom | 37 | 2 |  | 768 | 17 | 2 | Univent | 6144 | 0.36133 | 0 | 0.36133 | 0
223 | Classroom | 417 | 27 |  | 768 | 17 | 17 | 1 Univent & 1 AHU | 6144 | 4.0723 | 2 | 4.0723 | 2
224 | Classroom | 69 | 4 |  | 768 | 17 | 4 | 1 Univent & 1 AHU | 6144 | 0.67383 | 0 | 0.67383 | 0
225 | Classroom | 136 | 9 |  | 768 | 17 | 9 | 1 Univent & 1 AHU | 6144 | 1.3281 | 1 | 1.3281 | 1
226 | Classroom | 63 | 4 |  | 816 | 18 | 4 | 1 Univent & 1 AHU | 6528 | 0.57904 | 0 | 0.57904 | 0
227 | Classroom | 125 | 8 |  | 744 | 16 | 8 | 1 Univent & 1 AHU | 5952 | 1.2601 | 1 | 1.2601 | 1
228 | Classroom | 58 | 3 |  | 744 | 16 | 3 | 1 Univent & 1 AHU | 5952 | 0.58468 | 0 | 0.58468 | 0
301 | Classroom | 121 | 8 |  | 816 | 18 | 8 | 1 Univent & 1 AHU | 6528 | 1.1121 | 1 | 1.1121 | 1
302 | Classroom | 98 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 6528 | 0.90074 | 0 | 0.90074 | 0
303 | Classroom | 69 | 4 |  | 816 | 18 | 4 | Univent | 6528 | 0.63419 | 0 | 0.63419 | 0
304 | Classroom | 97 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 6528 | 0.89154 | 0 | 0.89154 | 0
305 | Classroom | 69 | 4 |  | 816 | 18 | 4 | Univent | 6528 | 0.63419 | 0 | 0.63419 | 0
306 | Classroom | 132 | 8 |  | 816 | 18 | 8 | 1 Univent & 1 AHU | 6528 | 1.2132 | 1 | 1.2132 | 1
307 | Classroom | 172 | 11 |  | 816 | 18 | 11 | 1 Univent & 1 AHU | 6528 | 1.5809 | 1 | 1.5809 | 1
308 | Classroom | 95 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 6528 | 0.87316 | 0 | 0.87316 | 0
309 | Classroom | 238 | 15 |  | 816 | 18 | 15 | 1 Univent & 1 AHU | 6528 | 2.1875 | 1 | 2.1875 | 1
310 | Classroom | 210 | 14 |  | 792 | 18 | 14 | 1 Univent & 1 AHU | 6336 | 1.9886 | 1 | 1.9886 | 1
311 | Classroom | 153 | 10 |  | 675 | 15 | 10 | 1 Univent & 1 AHU | 5400 | 1.7 | 1 | 1.7 | 1
312 | Classroom | 103 | 6 |  | 624 | 14 | 6 | 1 Univent & 1 AHU | 4992 | 1.238 | 1 | 1.238 | 1
313 | Classroom | 69 | 4 |  | 675 | 15 | 4 | Univent | 5400 | 0.76667 | 0 | 0.76667 | 0
314 | Classroom | 100 | 6 |  | 775 | 17 | 6 | 1 Univent & 1 AHU | 6200 | 0.96774 | 0 | 0.96774 | 0
315 | Classroom | 198 | 13 |  | 675 | 15 | 13 | 1 Univent & 1 AHU | 5400 | 2.2 | 1 | 2.2 | 1
316 | Classroom | 97 | 6 |  | 689 | 15 | 6 | 1 Univent & 1 AHU | 5512 | 1.0559 | 1 | 1.0559 | 1
317 | Classroom | 106 | 7 |  | 684 | 15 | 7 | 1 Univent & 1 AHU | 5472 | 1.1623 | 1 | 1.1623 | 1
318 | Classroom | 96 | 6 |  | 684 | 15 | 6 | 1 Univent & 1 AHU | 5472 | 1.0526 | 1 | 1.0526 | 1
319 | Classroom | 139 | 9 |  | 757 | 17 | 9 | 1 Univent & 1 AHU | 6056 | 1.3771 | 1 | 1.3771 | 1
320 | Classroom | 106 | 7 |  | 768 | 17 | 7 | 1 Univent & 1 AHU | 6144 | 1.0352 | 1 | 1.0352 | 1
321 | Classroom | 101 | 6 |  | 768 | 17 | 6 | 1 Univent & 1 AHU | 6144 | 0.98633 | 0 | 0.98633 | 0
322 | Classroom | 160 | 10 |  | 768 | 17 | 10 | 1 Univent & 1 AHU | 6144 | 1.5625 | 1 | 1.5625 | 1
323 | Classroom | 104 | 6 |  | 768 | 17 | 6 | 1 Univent & 1 AHU | 6144 | 1.0156 | 1 | 1.0156 | 1
324 | Classroom | 99 | 6 |  | 768 | 17 | 6 | 1 Univent & 1 AHU | 6144 | 0.9668 | 0 | 0.9668 | 0
325 | Classroom | 180 | 12 |  | 768 | 17 | 12 | 1 Univent & 1 AHU | 6144 | 1.7578 | 1 | 1.7578 | 1
326 | Classroom | 94 | 6 |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 6528 | 0.86397 | 0 | 0.86397 | 0
327 | Classroom | 120 | 8 |  | 744 | 16 | 8 | 1 Univent & 1 AHU | 5952 | 1.2097 | 1 | 1.2097 | 1
328 | Classroom | 252 | 16 |  | 744 | 16 | 16 | 1 Univent & 1 AHU | 5952 | 2.5403 | 1 | 2.5403 | 1
503 | Classroom | 180 | 12 |  | 714 | 16 | 12 | 1 Univent & 1 AHU | 5712 | 1.8908 | 1 | 1.8908 | 1
504 | Classroom | 252 | 16 |  | 849 | 19 | 16 | AHU | 6792 | 2.2261 | 1 | 2.2261 | 1
505 | Classroom | 149 | 9 |  | 1456 | 33 | 9 | 1 Univent & 1 AHU | 11648 | 0.76751 | 0 | 0.76751 | 0
507 | Classroom | 217 | 14 |  | 1458 | 33 | 14 | 1 Univent & 1 AHU | 11664 | 1.1163 | 1 | 1.1163 | 1
508 | Classroom | 149 | 9 |  | 765 | 17 | 9 | Univent | 6120 | 1.4608 | 1 | 1.4608 | 1
509 | Classroom | 204 | 13 |  | 738 | 16 | 13 | 1 Univent & 1 AHU | 5904 | 2.0732 | 1 | 2.0732 | 1
510 | Classroom | 205 | 13 |  | 848 | 19 | 13 | 1 Univent & 1 AHU | 6784 | 1.8131 | 1 | 1.8131 | 1
511 | Classroom | 226 | 15 |  | 740 | 16 | 15 | 1 Univent & 1 AHU | 5920 | 2.2905 | 1 | 2.2905 | 1
512 | Classroom | 196 | 13 |  | 833 | 18 | 13 | 1 Univent & 1 AHU | 6664 | 1.7647 | 1 | 1.7647 | 1
- | Auditorium | 1643 | 109 |  | 8015 | 182 | 109 |  | 64120 | 1.5374 | 1 | 1.5374 | 1
- | Basement / Cafe | 62 | 4 |  | 5900 | 134 | 4 |  | 47200 | 0.078814 | 0 | 0.078814 | 0
- | cubicle-1 | 48 | 3 |  | 437 | 9 | 3 |  | 3496 | 0.8238 | 0 | 0.8238 | 0
- | GYM | 2494 | 166 |  | 2633 | 59 | 59 |  | 21064 | 7.1041 | 2 | 7.1041 | 2
- | library | 288 | 19 |  | 2675 | 60 | 19 |  | 21400 | 0.80748 | 0 | 0.80748 | 0
- | mail room | 24 | 1 |  | 153 | 3 | 1 |  | 1224 | 1.1765 | 1 | 1.1765 | 1
- | Link Main Office | 201 | 13 |  | 809 | 18 | 13 |  | 6472 | 1.8634 | 1 | 1.8634 | 1
- | Clemente Main Office | 24 | 1 |  | 240 | 5 | 1 |  | 1920 | 0.75 | 0 | 0.75 | 0
Sheet Last Modified: | 2021-04-01 | [8 empty] | unk | unk | unk | unk
School: | Cleveland | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
109 | - |  | 0 | Yes | 850 | 19 | 19 |  | 6800 | unk | unk | 20 | 3
110 | - |  | 0 | Yes | 840 | 19 | 19 |  | 6720 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-19 | [8 empty] | unk | unk | unk | unk
School: | Benjamin B. Comegys Elementary School | House fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine | EMCOR | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
K-1 | Classroom | 418 | 27 |  | 2240 | 50 | 27 | Unit Ventilator | 17920 | 1.3996 | 1 | 1.3996 | 1
K-2 | Classroom | 462 | 30 |  | 2240 | 50 | 30 | Unit Ventilator | 17920 | 1.5469 | 1 | 1.5469 | 1
100 | Classroom | 366 | 24 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.1771 | 1 | 3.1771 | 1
101 | Classroom | 369 | 24 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 3.3263 | 1 | 3.3263 | 1
103 | Classroom | 273 | 18 |  | 864 | 19 | 18 | Unit Ventilator | 6912 | 2.3698 | 1 | 2.3698 | 1
104 | Classroom | 0 | 0 | Yes | 576 | 13 | 13 | Unit Ventilator | 4608 | 0 | 0 | 20 | 3
105 | Classroom | 231 | 15 |  | 864 | 19 | 15 | Unit Ventilator | 6912 | 2.0052 | 1 | 2.0052 | 1
106 | Classroom | 710 | 47 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 7.9241 | 2 | 7.9241 | 2
200 | Classroom | 251 | 16 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 2.8013 | 1 | 2.8013 | 1
201 | Classroom | 0 | 0 | Yes | 365 | 8 | 8 | Radiator | 2920 | 0 | 0 | 20 | 3
202 | Classroom | 371 | 24 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 4.1406 | 2 | 4.1406 | 2
203 | Classroom | 1226 | 81 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 13.683 | 3 | 13.683 | 3
204 | Classroom | 426 | 28 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 4.7545 | 2 | 4.7545 | 2
205 | Classroom | 366 | 24 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 4.0848 | 2 | 4.0848 | 2
206 | Classroom | 320 | 21 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 3.5714 | 1 | 3.5714 | 1
207 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | Unit Ventilator | 5824 | 0 | 0 | 20 | 3
208 | Classroom | 283 | 18 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 2.9155 | 1 | 2.9155 | 1
209 | Classroom | 288 | 19 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 2.967 | 1 | 2.967 | 1
210 | Classroom | 303 | 20 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 3.1216 | 1 | 3.1216 | 1
211 | Classroom | 272 | 18 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 2.8022 | 1 | 2.8022 | 1
212 | Classroom | 135 | 9 |  | 728 | 16 | 9 | Unit Ventilator | 5824 | 1.3908 | 1 | 1.3908 | 1
213 | Classroom | 913 | 60 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 9.4059 | 2 | 9.4059 | 2
214 | Classroom | 446 | 29 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 4.5948 | 2 | 4.5948 | 2
300 | Classroom | 226 | 15 |  | 728 | 16 | 15 | Unit Ventilator | 5824 | 2.3283 | 1 | 2.3283 | 1
301 | Classroom | 254 | 16 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 2.6168 | 1 | 2.6168 | 1
302 | Classroom | 322 | 21 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 3.3173 | 1 | 3.3173 | 1
303 | Classroom | 213 | 14 |  | 728 | 16 | 14 | Unit Ventilator | 5824 | 2.1944 | 1 | 2.1944 | 1
304 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | Unit Ventilator | 5824 | 0 | 0 | 20 | 3
305 | Classroom | 858 | 57 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 8.8393 | 2 | 8.8393 | 2
306 | Classroom | 883 | 58 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 9.0968 | 2 | 9.0968 | 2
307 | Classroom | 209 | 13 |  | 728 | 16 | 13 | Unit Ventilator | 5824 | 2.1532 | 1 | 2.1532 | 1
- | Art Classroom | 385 | 25 |  | 616 | 14 | 14 | Unit Ventilator | 4928 | 4.6875 | 2 | 4.6875 | 2
- | Main Office |  | 0 | Yes | 936 | 21 | 21 | Radiator | 7488 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 360 | 8 | 8 | Radiator | 2880 | unk | unk | 20 | 3
- | Counselor Office |  | 0 | Yes | 391 | 8 | 8 | Radiator | 3128 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 280 | 6 | 6 | Radiator | 2240 | unk | unk | 20 | 3
- | Auditorium | 271 | 18 |  | 4320 | 98 | 18 | AHU | 34560 | 0.47049 | 0 | 0.47049 | 0
- | Gym / Cafe | 477 | 31 |  | 3672 | 83 | 31 | AHU | 29376 | 0.97426 | 0 | 0.97426 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Watson Comly Elementary School | House fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Emcor Fluidics | 2nd Retest | 3rd Retest | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
102A | Classroom |  | 0 |  | 155 | 3 | 0 | House Fan | 1240 | unk | unk | unk | unk
103 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
103A | Classroom |  | 0 |  | 164 | 3 | 0 | House Fan | 1312 | unk | unk | unk | unk
104 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
105 | Classroom | 555 | 37 |  | 910 | 20 | 20 | Unit Ventilator | 7280 | 4.5742 | 2 | 4.5742 | 2
106 | Classroom | 581 | 38 |  | 910 | 20 | 20 | Unit Ventilator | 7280 | 4.7885 | 2 | 4.7885 | 2
107 | Classroom | 609 | 40 |  | 910 | 20 | 20 | Unit Ventilator | 7280 | 5.0192 | 2 | 5.0192 | 2
108 | Classroom |  | 0 | Yes | 910 | 20 | 20 | Unit Ventilator | 7280 | unk | unk | 20 | 3
110 (ESOL) | Classroom |  | 0 | Yes | 439 | 9 | 9 |  | 3512 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 435 | 9 | 9 |  | 3480 | unk | unk | 20 | 3
201A | Classroom |  | 0 | Yes | 306 | 6 | 6 | House Fan | 2448 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
204 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 690 | 15 | 15 | Unit Ventilator | 5520 | unk | unk | 20 | 3
206 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | unk | unk | 20 | 3
207 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | unk | unk | 20 | 3
208 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | unk | unk | 20 | 3
209 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | unk | unk | 20 | 3
210 | Classroom |  | 0 | Yes | 812 | 18 | 18 | Unit Ventilator | 6496 | unk | unk | 20 | 3
211 | Classroom | 147 | 9 |  | 812 | 18 | 9 | Unit Ventilator | 6496 | 1.3578 | 1 | 1.3578 | 1
212 | Classroom | 199 | 13 | Yes | 812 | 18 | 18 | Unit Ventilator | 6496 | 1.8381 | 1 | 21.8381 | 3
213 | Classroom | 197 | 13 |  | 812 | 18 | 13 | Unit Ventilator | 6496 | 1.8196 | 1 | 1.8196 | 1
214 | Classroom | 156 | 10 | Yes | 812 | 18 | 18 | Unit Ventilator | 6496 | 1.4409 | 1 | 21.4409 | 3
215 | Classroom | 510 | 34 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 4.7106 | 2 | 4.7106 | 2
216 | Classroom | 385 | 25 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.556 | 1 | 3.556 | 1
Art | 1st Fl Art Room | 342 | 22 |  | 1672 | 38 | 22 | Unit Ventilator | 13376 | 1.5341 | 1 | 1.5341 | 1
- | Art Teacher Office | 205 | 13 |  | 308 | 7 | 7 | MUA | 2464 | 4.9919 | 2 | 4.9919 | 2
- | Special Needs Room | 335 | 22 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.0942 | 1 | 3.0942 | 1
- | Music Room | 383 | 25 |  | 594 | 13 | 13 | Unit Ventilator | 4752 | 4.8359 | 2 | 4.8359 | 2
- | Office - Main | 183 | 12 |  | 169 | 3 | 3 | Unit Ventilator | 1352 | 8.1213 | 2 | 8.1213 | 2
- | Office-2 |  | 0 |  | 176 | 4 | 0 |  | 1408 | unk | unk | unk | unk
- | 2nd Floor Counselors Office |  | 0 | Yes | 182 | 4 | 4 |  | 1456 | unk | unk | 20 | 3
- | Counslor waiting rm |  | 0 |  | 104 | 2 | 0 |  | 832 | unk | unk | unk | unk
- | Conference room 1st floor |  | 0 |  | 338 | 7 | 0 |  | 2704 | unk | unk | unk | unk
- | Amy's Room |  | 0 |  | 156 | 3 | 0 |  | 1248 | unk | unk | unk | unk
- | Principals Office | 0 | 0 | Yes | 196 | 4 | 4 | N/A | 1568 | 0 | 0 | 20 | 3
- | Break Room | 0 | 0 |  | 390 | 8 | 0 | N/A | 3120 | 0 | 0 | 0 | 0
- | 2nd Floor Staff room |  | 0 |  | 170 | 3 | 0 |  | 1360 | unk | unk | unk | unk
- | Nurse 1st Floor | 90 | 6 |  | 150 | 3 | 3 | MUA | 1200 | 4.5 | 2 | 4.5 | 2
- | Nurse Office | 125 | 8 |  | 344 | 7 | 7 | MUA | 2752 | 2.7253 | 1 | 2.7253 | 1
- | Nurse waiting |  | 0 | Yes | 202 | 4 | 4 |  | 1616 | unk | unk | 20 | 3
- | Cafeteria |  | 0 | Yes | 3321 | 75 | 75 |  | 26568 | unk | unk | 20 | 3
- | Gym |  | 0 |  | 4838 | 109 | 0 |  | 38704 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-20 | [8 empty] | unk | unk | unk | unk
School: | Russell Conwell Middle School / Conwell Annex | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Conwell Main Building | [9 empty] | unk | unk | unk | unk
B1 | - |  | 0 |  | 1575 | 35 | 0 |  | 12600 | unk | unk | unk | unk
B2 | - |  | 0 |  | 782 | 17 | 0 |  | 6256 | unk | unk | unk | unk
Main Office | Office |  | 0 | Yes | 396 | 9 | 9 |  | 3168 | unk | unk | 20 | 3
Nurse | Office |  | 0 | Yes | 473 | 10 | 10 |  | 3784 | unk | unk | 20 | 3
102 | - |  | 0 |  | 575 | 13 | 0 |  | 4600 | unk | unk | unk | unk
107 | - |  | 0 |  | 120 | 2 | 0 |  | 960 | unk | unk | unk | unk
108 | - |  | 0 | Yes | 816 | 18 | 18 |  | 6528 | unk | unk | 20 | 3
109 | - |  | 0 | Yes | 850 | 19 | 19 |  | 6800 | unk | unk | 20 | 3
111 | - |  | 0 | Yes | 1200 | 27 | 27 |  | 9600 | unk | unk | 20 | 3
103/104/ IMC | - |  | 0 |  | 4300 | 97 | 0 |  | 34400 | unk | unk | unk | unk
201 | - |  | 0 |  | 850 | 19 | 0 |  | 6800 | unk | unk | unk | unk
202 | - |  | 0 |  | 840 | 19 | 0 |  | 6720 | unk | unk | unk | unk
204 | - |  | 0 |  | 625 | 14 | 0 |  | 5000 | unk | unk | unk | unk
205 | - |  | 0 |  | 550 | 12 | 0 |  | 4400 | unk | unk | unk | unk
206 | - |  | 0 |  | 875 | 19 | 0 |  | 7000 | unk | unk | unk | unk
207 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
208 | - |  | 0 |  | 805 | 18 | 0 |  | 6440 | unk | unk | unk | unk
209 | - |  | 0 | Yes | 850 | 19 | 19 |  | 6800 | unk | unk | 20 | 3
301 | - |  | 0 | Yes | 720 | 16 | 16 |  | 5760 | unk | unk | 20 | 3
302 | - |  | 0 |  | 805 | 18 | 0 |  | 6440 | unk | unk | unk | unk
303 | - |  | 0 |  | 550 | 12 | 0 |  | 4400 | unk | unk | unk | unk
304 | - |  | 0 |  | 625 | 14 | 0 |  | 5000 | unk | unk | unk | unk
305 | - |  | 0 |  | 506 | 11 | 0 |  | 4048 | unk | unk | unk | unk
306 | - |  | 0 |  | 875 | 19 | 0 |  | 7000 | unk | unk | unk | unk
307 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
308 | - |  | 0 |  | 805 | 18 | 0 |  | 6440 | unk | unk | unk | unk
309 | - |  | 0 | Yes | 575 | 13 | 13 |  | 4600 | unk | unk | 20 | 3
Conwell Annex | [9 empty] | unk | unk | unk | unk
1 | - |  | 0 |  | 1276 | 29 | 0 |  | 10208 | unk | unk | unk | unk
9 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | unk | unk | unk | unk
102 | - |  | 0 |  | 2318 | 52 | 0 |  | 18544 | unk | unk | unk | unk
104 | - |  | 0 |  | 870 | 19 | 0 |  | 6960 | unk | unk | unk | unk
203 | - |  | 0 |  | 4800 | 109 | 0 |  | 38400 | unk | unk | unk | unk
200 | - |  | 0 |  | 512 | 11 | 0 |  | 4096 | unk | unk | unk | unk
301 | - |  | 0 |  | 840 | 19 | 0 |  | 6720 | unk | unk | unk | unk
305 | - |  | 0 |  | 630 | 14 | 0 |  | 5040 | unk | unk | unk | unk
306 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Cook-Wissahickon Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Devine Retest | Capital | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Classroom | 310 | 20 |  | 695 | 15 | 15 | Unit Ventilator | 5560 | 3.3453 | 1 | 3.3453 | 1
2 | Classroom | 280 | 18 |  | 950 | 21 | 18 | Unit Ventilator | 7600 | 2.2105 | 1 | 2.2105 | 1
3 | Classroom | 443 | 29 |  | 513 | 11 | 11 | Unit Ventilator | 4104 | 6.4766 | 2 | 6.4766 | 2
15 | - | 131 | 8 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
016A | - | 131 | 8 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
101 | Classroom | 341 | 22 |  | 717 | 16 | 16 | Unit Ventilator | 5736 | 3.5669 | 1 | 3.5669 | 1
102 | Classroom | 694 | 46 |  | 700 | 15 | 15 | Unit Ventilator | 5600 | 7.4357 | 2 | 7.4357 | 2
103 | Classroom | 0 | 0 |  | 1495 | 33 | 0 | Unit Ventilator | 11960 | 0 | 0 | 0 | 0
105 | Classroom | 337 | 22 |  | 1005 | 22 | 22 | Unit Ventilator | 8040 | 2.5149 | 1 | 2.5149 | 1
106 | Classroom | 342 | 22 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.776 | 1 | 2.776 | 1
107 | Classroom | 327 | 21 |  | 630 | 14 | 14 | Unit Ventilator | 5040 | 3.8929 | 1 | 3.8929 | 1
108 | Classroom | 352 | 23 |  | 441 | 10 | 10 | Unit Ventilator | 3528 | 5.9864 | 2 | 5.9864 | 2
109 | Classroom | 585 | 39 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 5.1557 | 2 | 5.1557 | 2
110 | Classroom | 280 | 18 |  | 674 | 15 | 15 | Unit Ventilator | 5392 | 3.1157 | 1 | 3.1157 | 1
111 | Classroom | 285 | 19 |  | 386 | 8 | 8 | Unit Ventilator | 3088 | 5.5376 | 2 | 5.5376 | 2
200 | Classroom | 366 | 24 |  | 636 | 14 | 14 | Unit Ventilator | 5088 | 4.316 | 2 | 4.316 | 2
200A | Classroom | 324 | 21 |  | 485 | 11 | 11 | Unit Ventilator | 3880 | 5.0103 | 2 | 5.0103 | 2
201 | Classroom | 310 | 20 |  | 447 | 10 | 10 | Unit Ventilator | 3576 | 5.2013 | 2 | 5.2013 | 2
202 | Classroom | 418 | 27 |  | 730 | 16 | 16 | Unit Ventilator | 5840 | 4.2945 | 2 | 4.2945 | 2
203 | Classroom | 0 | 0 |  | 813 | 18 | 0 | Unit Ventilator | 6504 | 0 | 0 | 0 | 0
204 | Classroom | 326 | 21 |  | 867 | 19 | 19 | Unit Ventilator | 6936 | 2.8201 | 1 | 2.8201 | 1
205 | Classroom | 401 | 26 |  | 716 | 16 | 16 | Unit Ventilator | 5728 | 4.2004 | 2 | 4.2004 | 2
206 | Classroom | 0 | 0 |  | 810 | 18 | 0 | Unit Ventilator | 6480 | 0 | 0 | 0 | 0
207 | Classroom | 284 | 18 |  | 456 | 10 | 10 | Unit Ventilator | 3648 | 4.6711 | 2 | 4.6711 | 2
208 | Classroom | 336 | 22 |  | 422 | 9 | 9 | Unit Ventilator | 3376 | 5.9716 | 2 | 5.9716 | 2
209 | Classroom | 300 | 20 |  | 731 | 16 | 16 | Unit Ventilator | 5848 | 3.078 | 1 | 3.078 | 1
210 | Classroom | 315 | 21 |  | 731 | 16 | 16 | Unit Ventilator | 5848 | 3.2319 | 1 | 3.2319 | 1
211 | Classroom | 0 | 0 |  | 872 | 19 | 0 | Unit Ventilator | 6976 | 0 | 0 | 0 | 0
212 | Classroom | 440 | 29 |  | 365 | 8 | 8 | Unit Ventilator | 2920 | 9.0411 | 2 | 9.0411 | 2
213 | Room | 310 | 20 |  | 525 | 11 | 11 | Air Handling Unit | 4200 | 4.4286 | 2 | 4.4286 | 2
- | Cafeteria | 2213 | 147 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Copy Room | 340 | 22 |  | 199 | 4 | 4 | Air Handling Unit | 1592 | 12.8141 | 3 | 12.8141 | 3
- | Gymnasium | 1486 | 99 |  | 4325 | 98 | 98 | Air Handling Unit | 34600 | 2.5769 | 1 | 2.5769 | 1
- | Library | 1180 | 78 |  | 2998 | 68 | 68 | Air Handling Unit | 23984 | 2.952 | 1 | 2.952 | 1
- | Main Office | 789 | 52 |  | 396 | 9 | 9 | Air Handling Unit | 3168 | 14.9432 | 3 | 14.9432 | 3
- | Pricipal's office | 498 | 33 |  | 358 | 8 | 8 | Air Handling Unit | 2864 | 10.433 | 3 | 10.433 | 3
- | Speech Room | 330 | 22 |  | 358 | 8 | 8 | Air Handling Unit | 2864 | 6.9134 | 2 | 6.9134 | 2
- | Prep and lounge |  | 0 |  | 602 | 13 | 0 |  | 4816 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | Jay Cooke Elementary School | House Fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100C | Classroom | 293 | 19 |  | 506 | 11 | 11 | House Fan | 4048 | 4.3429 | 2 | 4.3429 | 2
101C | Classroom | 411 | 27 |  | 543 | 12 | 12 | House Fan | 4344 | 5.6768 | 2 | 5.6768 | 2
102C | Classroom | 284 | 18 |  | 833 | 18 | 18 | House Fan | 6664 | 2.557 | 1 | 2.557 | 1
103 | Classroom | 531 | 35 |  | 1082 | 24 | 24 | House Fan | 8656 | 3.6807 | 1 | 3.6807 | 1
104 | Classroom | 279 | 18 |  | 809 | 18 | 18 | House Fan | 6472 | 2.5865 | 1 | 2.5865 | 1
105 | Classroom | 369 | 24 |  | 695 | 15 | 15 | House Fan | 5560 | 3.982 | 1 | 3.982 | 1
108 | Classroom | 328 | 21 |  | 858 | 19 | 19 | House Fan | 6864 | 2.8671 | 1 | 2.8671 | 1
109 | Office | 313 | 20 |  | 548 | 12 | 12 | House Fan | 4384 | 4.2838 | 2 | 4.2838 | 2
110 | Classroom | 422 | 28 |  | 665 | 15 | 15 | House Fan | 5320 | 4.7594 | 2 | 4.7594 | 2
110A | Office | 335 | 22 |  | 333 | 7 | 7 | House Fan | 2664 | 7.545 | 2 | 7.545 | 2
201 | Classroom | 335 | 22 |  | 711 | 16 | 16 | House Fan | 5688 | 3.5338 | 1 | 3.5338 | 1
202 | Classroom | 515 | 34 |  | 674 | 15 | 15 | House Fan | 5392 | 5.7307 | 2 | 5.7307 | 2
202A | Classroom | 347 | 23 |  | 1015 | 23 | 23 | House Fan | 8120 | 2.564 | 1 | 2.564 | 1
203 | Classroom | 388 | 25 |  | 717 | 16 | 16 | House Fan | 5736 | 4.0586 | 2 | 4.0586 | 2
205 | Office | 0 | 0 |  | 304 | 6 | 0 | House Fan(partial Duct) | 2432 | 0 | 0 | 0 | 0
206 | Office | 0 | 0 | Yes | 240 | 5 | 5 | House Fan(partial Duct) | 1920 | 0 | 0 | 20 | 3
207 | Classroom | 435 | 29 |  | 726 | 16 | 16 | House Fan | 5808 | 4.4938 | 2 | 4.4938 | 2
207A | Classroom | 330 | 22 |  | 334 | 7 | 7 | House Fan | 2672 | 7.4102 | 2 | 7.4102 | 2
208 | Classroom | 433 | 28 |  | 673 | 15 | 15 | House Fan | 5384 | 4.8254 | 2 | 4.8254 | 2
208A | Storage | 279 | 18 |  | 720 | 16 | 16 |  | 5760 | 2.9062 | 1 | 2.9062 | 1
209 | Classroom | 363 | 24 |  | 693 | 15 | 15 | House Fan | 5544 | 3.9286 | 1 | 3.9286 | 1
210 | Classroom | 378 | 25 |  | 650 | 14 | 14 | House Fan | 5200 | 4.3615 | 2 | 4.3615 | 2
211 | Classroom | 748 | 49 |  | 211 | 4 | 4 | House Fan | 1688 | 26.5877 | 4 | 26.5877 | 4
212 | Classroom | 736 | 49 |  | 774 | 17 | 17 | House Fan | 6192 | 7.1318 | 2 | 7.1318 | 2
213 | Classroom | 807 | 53 |  | 720 | 16 | 16 | House Fan | 5760 | 8.4062 | 2 | 8.4062 | 2
214 | Classroom | 846 | 56 |  | 727 | 16 | 16 | House Fan | 5816 | 8.7276 | 2 | 8.7276 | 2
215 | Classroom | 797 | 53 |  | 748 | 17 | 17 | House Fan | 5984 | 7.9913 | 2 | 7.9913 | 2
216 | Classroom | 811 | 54 |  | 762 | 17 | 17 | House Fan | 6096 | 7.9823 | 2 | 7.9823 | 2
217 | Classroom | 496 | 33 |  | 670 | 15 | 15 | House Fan | 5360 | 5.5522 | 2 | 5.5522 | 2
301 | Classroom | 278 | 18 |  | 711 | 16 | 16 | House Fan | 5688 | 2.9325 | 1 | 2.9325 | 1
302 | Classroom | 522 | 34 |  | 690 | 15 | 15 | House Fan | 5520 | 5.6739 | 2 | 5.6739 | 2
302A | Classroom | 273 | 18 |  | 405 | 9 | 9 | House Fan | 3240 | 5.0556 | 2 | 5.0556 | 2
303 | Classroom | 581 | 38 |  | 714 | 16 | 16 | House Fan | 5712 | 6.1029 | 2 | 6.1029 | 2
303A | Classroom | 284 | 18 | Yes | 405 | 9 | 9 | House Fan | 3240 | 5.2593 | 2 | 25.2593 | 4
303B | Classroom | 0 | 0 | Yes | 216 | 4 | 4 |  | 1728 | 0 | 0 | 20 | 3
304 | Classroom | 633 | 42 |  | 882 | 20 | 20 | House Fan | 7056 | 5.3827 | 2 | 5.3827 | 2
305 | Classroom | 437 | 29 |  | 907 | 20 | 20 | House Fan | 7256 | 3.6136 | 1 | 3.6136 | 1
306 | Classroom | 456 | 30 |  | 815 | 18 | 18 | House Fan | 6520 | 4.1963 | 2 | 4.1963 | 2
307 | Classroom | 541 | 36 |  | 798 | 18 | 18 | House Fan | 6384 | 5.0846 | 2 | 5.0846 | 2
308 | Classroom | 469 | 31 |  | 1031 | 23 | 23 | House Fan | 8248 | 3.4117 | 1 | 3.4117 | 1
309 | Classroom | 456 | 30 |  | 896 | 20 | 20 | House Fan | 7168 | 3.817 | 1 | 3.817 | 1
310 | Classroom | 441 | 29 |  | 769 | 17 | 17 | House Fan | 6152 | 4.301 | 2 | 4.301 | 2
311 | Classroom | 617 | 41 |  | 985 | 22 | 22 | House Fan | 7880 | 4.698 | 2 | 4.698 | 2
312 | Classroom | 333 | 22 |  | 713 | 16 | 16 | House Fan | 5704 | 3.5028 | 1 | 3.5028 | 1
312A | Classroom | 325 | 21 |  | 332 | 7 | 7 | House Fan | 2656 | 7.3419 | 2 | 7.3419 | 2
313 | Classroom | 393 | 26 |  | 666 | 15 | 15 | House Fan | 5328 | 4.4257 | 2 | 4.4257 | 2
313A | Classroom | 307 | 20 |  | 703 | 15 | 15 | House Fan | 5624 | 3.2752 | 1 | 3.2752 | 1
314 | Classroom | 365 | 24 |  | 709 | 16 | 16 | House Fan | 5672 | 3.8611 | 1 | 3.8611 | 1
315 | Classroom | 271 | 18 |  | 650 | 14 | 14 | House Fan | 5200 | 3.1269 | 1 | 3.1269 | 1
316 | Classroom | 673 | 44 |  | 765 | 17 | 17 | House Fan | 6120 | 6.598 | 2 | 6.598 | 2
317 | Classroom | 278 | 18 |  | 729 | 16 | 16 | House Fan | 5832 | 2.8601 | 1 | 2.8601 | 1
318 | Classroom | 744 | 49 |  | 730 | 16 | 16 | House Fan | 5840 | 7.6438 | 2 | 7.6438 | 2
319 | Classroom | 656 | 43 |  | 719 | 16 | 16 | House Fan | 5752 | 6.8428 | 2 | 6.8428 | 2
320 | Classroom | 764 | 50 |  | 700 | 15 | 15 | House Fan | 5600 | 8.1857 | 2 | 8.1857 | 2
321 | Classroom | 480 | 32 |  | 787 | 17 | 17 | House Fan | 6296 | 4.5743 | 2 | 4.5743 | 2
322 | Classroom | 353 | 23 |  | 653 | 14 | 14 | House Fan | 5224 | 4.0544 | 2 | 4.0544 | 2
- | Asst. Principal Waiting Room | 125 | 8 |  | 118 | 2 | 2 | House Fan | 944 | 7.9449 | 2 | 7.9449 | 2
- | Asst. Principal Office |  | 0 | Yes | 110 | 2 | 2 |  | 880 | unk | unk | 20 | 3
- | Auditorium | 3875 | 258 |  | 3793 | 86 | 86 | House Fan | 30344 | 7.6621 | 2 | 7.6621 | 2
- | Boy's Cafeteria | 1403 | 93 |  | 2254 | 51 | 51 | House Fan | 18032 | 4.6684 | 2 | 4.6684 | 2
- | Boy's Gym | 1455 | 97 |  | 2806 | 63 | 63 | House Fan | 22448 | 3.889 | 1 | 3.889 | 1
- | Counselor Waiting Room | 134 | 8 |  | 123 | 2 | 2 | House Fan | 984 | 8.1707 | 2 | 8.1707 | 2
- | Counselor Office 1 | 0 | 0 | Yes | 92 | 2 | 2 | House Fan | 736 | 0 | 0 | 20 | 3
- | Counselor Office 2 | 0 | 0 |  | 101 | 2 | 0 | House Fan | 808 | 0 | 0 | 0 | 0
- | Counselor Office 3 | 0 | 0 |  | 156 | 3 | 0 |  | 1248 | 0 | 0 | 0 | 0
- | Girl's Cafeteria | 1178 | 78 |  | 1944 | 44 | 44 | House Fan | 15552 | 4.5448 | 2 | 4.5448 | 2
- | Girl's Gym | 1461 | 97 |  | 2806 | 63 | 63 | House Fan | 22448 | 3.905 | 1 | 3.905 | 1
- | Kitchen | 321 | 21 |  | 409 | 9 | 9 | House Fan | 3272 | 5.8863 | 2 | 5.8863 | 2
- | Library | 1042 | 69 |  | 2053 | 46 | 46 | House Fan | 16424 | 3.8066 | 1 | 3.8066 | 1
- | Nurse Office | 53 | 3 | Yes | 186 | 4 | 4 | House Fan | 1488 | 2.1371 | 1 | 22.1371 | 3
- | Principal Office | 141 | 9 |  | 336 | 7 | 7 | House Fan | 2688 | 3.1473 | 1 | 3.1473 | 1
- | Weight Room | 842 | 56 |  | 1027 | 23 | 23 | House Fan | 8216 | 6.149 | 2 | 6.149 | 2
- | CASST Office | 0 | 0 | Yes | 264 | 6 | 6 |  | 2112 | 0 | 0 | 20 | 3
- | SPECM Speech Therapy Office | 0 | 0 |  | 112 | 2 | 0 |  | 896 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | William Cramp Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
102 | Office | 27 | 1 |  | 133 | 3 | 1 |  | 1064 | 1.5226 | 1 | 1.5226 | 1
102A | Office | 20 | 1 |  | 133 | 3 | 1 |  | 1064 | 1.1278 | 1 | 1.1278 | 1
103 | Small Classroom | 103 | 6 |  | 533 | 12 | 6 |  | 4264 | 1.4493 | 1 | 1.4493 | 1
106 | Classroom | 387 | 25 |  | 1033 | 23 | 23 | Unit Ventilator | 8264 | 2.8098 | 1 | 2.8098 | 1
107 | Counselor | 137 | 9 |  | 385 | 8 | 8 |  | 3080 | 2.6688 | 1 | 2.6688 | 1
108 | Classroom | 148 | 9 | Yes | 1220 | 27 | 27 | Unit Ventilator | 9760 | 0.90984 | 0 | 20.9098 | 3
109 | Classroom | 405 | 27 |  | 1120 | 25 | 25 | Unit Ventilator | 8960 | 2.7121 | 1 | 2.7121 | 1
110 | Classroom | 277 | 18 |  | 1543 | 35 | 18 | Unit Ventilator | 12344 | 1.3464 | 1 | 1.3464 | 1
111 | Classroom | 318 | 21 |  | 1228 | 27 | 21 | Unit Ventilator | 9824 | 1.9422 | 1 | 1.9422 | 1
112 | Classroom | 498 | 33 |  | 1170 | 26 | 26 |  | 9360 | 3.1923 | 1 | 3.1923 | 1
112E | Office | 29 | 1 |  | 200 | 4 | 1 |  | 1600 | 1.0875 | 1 | 1.0875 | 1
113 | Classroom | 338 | 22 |  | 1311 | 29 | 22 | Unit Ventilator | 10488 | 1.9336 | 1 | 1.9336 | 1
13A | Classroom | 307 | 20 |  | 1073 | 24 | 20 |  | 8584 | 2.1459 | 1 | 2.1459 | 1
13B | Classroom | 500 | 33 |  | 1294 | 29 | 29 | Unit Ventilator | 10352 | 2.898 | 1 | 2.898 | 1
114 | Art | 385 | 25 |  | 876 | 19 | 19 | AHU | 7008 | 3.2962 | 1 | 3.2962 | 1
115 | Classroom | 283 | 18 |  | 1559 | 35 | 18 |  | 12472 | 1.3614 | 1 | 1.3614 | 1
119 | Office | 0 | 0 |  | 459 | 10 | 0 |  | 3672 | 0 | 0 | 0 | 0
200 | Classroom | 763 | 50 |  | 967 | 21 | 21 | Unit Ventilator | 7736 | 5.9178 | 2 | 5.9178 | 2
201 | Classroom | 605 | 40 |  | 825 | 18 | 18 | Unit Ventilator | 6600 | 5.5 | 2 | 5.5 | 2
202 | Counselor | 26 | 1 |  | 151 | 3 | 1 |  | 1208 | 1.2914 | 1 | 1.2914 | 1
203/212 | Speech | 27 | 1 |  | 151 | 3 | 1 |  | 1208 | 1.3411 | 1 | 1.3411 | 1
204 | Classroom | 527 | 35 |  | 1050 | 23 | 23 | Unit Ventilator | 8400 | 3.7643 | 1 | 3.7643 | 1
205 | Classroom | 128 | 8 |  | 902 | 20 | 8 | Unit Ventilator | 7216 | 1.0643 | 1 | 1.0643 | 1
206 | Classroom | 437 | 29 |  | 1030 | 23 | 23 | Unit Ventilator | 8240 | 3.182 | 1 | 3.182 | 1
207 | Classroom | 440 | 29 |  | 971 | 22 | 22 | Unit Ventilator | 7768 | 3.3986 | 1 | 3.3986 | 1
208 | Classroom | 544 | 36 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 4.2947 | 2 | 4.2947 | 2
209 | Classroom | 438 | 29 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 3.6622 | 1 | 3.6622 | 1
210 | Classroom | 462 | 30 |  | 967 | 21 | 21 | Unit Ventilator | 7736 | 3.5832 | 1 | 3.5832 | 1
211 | Classroom | 118 | 7 |  | 976 | 22 | 7 | Unit Ventilator | 7808 | 0.90676 | 0 | 0.90676 | 0
300 | Classroom | 782 | 52 |  | 866 | 19 | 19 | Unit Ventilator | 6928 | 6.7725 | 2 | 6.7725 | 2
301 | Classroom | 675 | 45 |  | 982 | 22 | 22 | Unit Ventilator | 7856 | 5.1553 | 2 | 5.1553 | 2
302 | Counselor | 42 | 2 |  | 151 | 3 | 2 |  | 1208 | 2.0861 | 1 | 2.0861 | 1
303/312 | Office | 48 | 3 |  | 151 | 3 | 3 |  | 1208 | 2.3841 | 1 | 2.3841 | 1
304 | Classroom | 133 | 8 |  | 1050 | 23 | 8 | Unit Ventilator | 8400 | 0.95 | 0 | 0.95 | 0
304 | Classroom | 330 | 22 |  | 1050 | 23 | 22 |  | 8400 | 2.3571 | 1 | 2.3571 | 1
305 | Classroom | 393 | 26 |  | 968 | 22 | 22 | Unit Ventilator | 7744 | 3.0449 | 1 | 3.0449 | 1
306 | Classroom | 122 | 8 |  | 855 | 19 | 8 | Unit Ventilator | 6840 | 1.0702 | 1 | 1.0702 | 1
306 | Classroom | 501 | 33 |  | 855 | 19 | 19 |  | 6840 | 4.3947 | 2 | 4.3947 | 2
307 | Classroom | 713 | 47 |  | 965 | 21 | 21 | Unit Ventilator | 7720 | 5.5415 | 2 | 5.5415 | 2
308 | Classroom | 320 | 21 |  | 772 | 17 | 17 | Unit Ventilator | 6176 | 3.1088 | 1 | 3.1088 | 1
309 | Classroom | 471 | 31 |  | 941 | 21 | 21 | Unit Ventilator | 7528 | 3.754 | 1 | 3.754 | 1
310 | Classroom | 327 | 21 |  | 972 | 22 | 21 | Unit Ventilator | 7776 | 2.5231 | 1 | 2.5231 | 1
311 | Classroom | 421 | 28 |  | 896 | 20 | 20 | Unit Ventilator | 7168 | 3.524 | 1 | 3.524 | 1
313 | Classroom | 329 | 21 |  | 368 | 8 | 8 | Unit Ventilator | 2944 | 6.7052 | 2 | 6.7052 | 2
- | Gym | 42 | 2 |  | 4800 | 109 | 2 | AHU | 38400 | 0.065625 | 0 | 0.065625 | 0
- | LGI | 736 | 49 |  | 697 | 15 | 15 | AHU | 5576 | 7.9197 | 2 | 7.9197 | 2
- | Admin Office | 827 | 55 |  | 251 | 5 | 5 | AHU | 2008 | 24.7112 | 4 | 24.7112 | 4
- | Cafeteria | 630 | 42 |  | 7287 | 165 | 42 | AHU | 58296 | 0.64841 | 0 | 0.64841 | 0
- | Computer Lab | 498 | 33 |  | 2840 | 64 | 33 | Unit Ventilator | 22720 | 1.3151 | 1 | 1.3151 | 1
- | Computer Room | 1015 | 67 |  | 2437 | 55 | 55 | AHU | 19496 | 3.1237 | 1 | 3.1237 | 1
- | Conference/Storage | 110 | 7 |  | 199 | 4 | 4 |  | 1592 | 4.1457 | 2 | 4.1457 | 2
- | IMC Office | 40 | 2 |  | 141 | 3 | 2 |  | 1128 | 2.1277 | 1 | 2.1277 | 1
- | IMC Library | 36 | 2 |  | 2456 | 55 | 2 |  | 19648 | 0.10993 | 0 | 0.10993 | 0
- | Kitchen | 1510 | 100 |  | 972 | 22 | 22 |  | 7776 | 11.6512 | 3 | 11.6512 | 3
- | Library North Classroom | 537 | 35 |  | 2635 | 59 | 35 | Unit Ventilator | 21080 | 1.5285 | 1 | 1.5285 | 1
- | Library South Classroom | 443 | 29 |  | 362 | 8 | 8 | Unit Ventilator | 2896 | 9.1782 | 2 | 9.1782 | 2
- | Mail Room | 47 | 3 |  | 133 | 3 | 3 |  | 1064 | 2.6504 | 1 | 2.6504 | 1
- | Main Office | 113 | 7 |  | 571 | 12 | 7 |  | 4568 | 1.4842 | 1 | 1.4842 | 1
- | Nurse Office | 109 | 7 |  | 374 | 8 | 7 |  | 2992 | 2.1858 | 1 | 2.1858 | 1
- | Nurse Exam Room | 44 | 2 |  | 128 | 2 | 2 |  | 1024 | 2.5781 | 1 | 2.5781 | 1
- | Principals Office | 60 | 4 |  | 258 | 5 | 4 |  | 2064 | 1.7442 | 1 | 1.7442 | 1
- | Teachers Lounge | 354 | 23 |  | 775 | 17 | 17 |  | 6200 | 3.4258 | 1 | 3.4258 | 1
- | Vice Principal's Office | 64 | 4 |  | 213 | 4 | 4 |  | 1704 | 2.2535 | 1 | 2.2535 | 1
Sheet Last Modified: | 2021-04-05 | [8 empty] | unk | unk | unk | unk
School: | Kenneth C. Crossan Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Kindergarten Classroom | 580 | 38 |  | 1088 | 24 | 24 | House Fan | 8704 | 3.9982 | 1 | 3.9982 | 1
2 | Classroom | 555 | 37 |  | 900 | 20 | 20 | House Fan | 7200 | 4.625 | 2 | 4.625 | 2
3 | Classroom | 522 | 34 |  | 930 | 21 | 21 | House Fan | 7440 | 4.2097 | 2 | 4.2097 | 2
4 | Classroom | 299 | 19 |  | 840 | 19 | 19 | House Fan | 6720 | 2.6696 | 1 | 2.6696 | 1
5 | Kindergarten Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | unk | unk | 20 | 3
5 | Classroom | 505 | 33 |  | 600 | 13 | 13 | House Fan | 4800 | 6.3125 | 2 | 6.3125 | 2
6 | Classroom | 820 | 54 |  | 805 | 18 | 18 | House Fan | 6440 | 7.6398 | 2 | 7.6398 | 2
7 | Computer Classrm. | 437 | 29 |  | 900 | 20 | 20 | House Fan | 7200 | 3.6417 | 1 | 3.6417 | 1
8 | Classroom | 580 | 38 |  | 1094 | 24 | 24 | House Fan | 8752 | 3.9762 | 1 | 3.9762 | 1
9 | Classrom | 444 | 29 |  | 840 | 19 | 19 | House Fan | 6720 | 3.9643 | 1 | 3.9643 | 1
9A | Teachers Rm. | 0 | 0 | Yes | 450 | 10 | 10 | N/A | 3600 | 0 | 0 | 20 | 3
10 | Classroom | 822 | 54 |  | 600 | 13 | 13 |  | 4800 | 10.275 | 3 | 10.275 | 3
11 | Classroom | 466 | 31 |  | 720 | 16 | 16 | House Fan | 5760 | 4.8542 | 2 | 4.8542 | 2
12 | Classroom | 606 | 40 |  | 720 | 16 | 16 | House Fan | 5760 | 6.3125 | 2 | 6.3125 | 2
13 | Classroom | 626 | 41 |  | 720 | 16 | 16 | House Fan | 5760 | 6.5208 | 2 | 6.5208 | 2
- | Auditorium | 1107 | 73 |  | 2760 | 62 | 62 | House Fan | 22080 | 3.0082 | 1 | 3.0082 | 1
- | Cafeteria/Gym | 0 | 0 |  | 2300 | 52 | 0 | N/A | 18400 | 0 | 0 | 0 | 0
- | Counselors Rm. | 0 | 0 | Yes | 450 | 10 | 10 | N/A | 3600 | 0 | 0 | 20 | 3
- | Grnd. Fl. Boys Bathrm. | 568 | 37 |  | 736 | 16 | 16 | House Fan | 5888 | 5.788 | 2 | 5.788 | 2
- | Grnd. Fl. Girls Bathrm. | 620 | 41 |  | 775 | 17 | 17 | House Fan | 6200 | 6 | 2 | 6 | 2
- | Ind. Arts Classroom | 0 | 0 |  | 600 | 13 | 0 | N/A | 4800 | 0 | 0 | 0 | 0
- | Library | 525 | 35 |  | 1152 | 26 | 26 | House Fan | 9216 | 3.418 | 1 | 3.418 | 1
- | Main Office | 0 | 0 | Yes | 460 | 10 | 10 | N/A | 3680 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 450 | 10 | 10 |  | 3600 | unk | unk | 20 | 3
- | Art Room |  | 0 | Yes | 600 | 13 | 13 |  | 4800 | unk | unk | 20 | 3
- | Principal's Ofice | 0 | 0 |  | 450 | 10 | 0 | N/A | 3600 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Anne Blakiston Day Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR / Chadwick | [8 empty] | unk | unk | unk | unk
School: | Anne Blakiston Day Elementary School- Little School House | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Part 2 and Exhaust | Exhaust | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Anna Blakiston Day Elementary School- Main Building | [9 empty] | unk | unk | unk | unk
101 | classroom | 186 | 12 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 1.5852 | 1 | 21.5852 | 3
102 | classroom | 194 | 12 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 1.6534 | 1 | 21.6534 | 3
103 | classroom | 45 | 3 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0.38352 | 0 | 20.3835 | 3
104 | classroom | 75 | 5 | Yes | 1440 | 32 | 32 | Unit Ventilator | 11520 | 0.39062 | 0 | 20.3906 | 3
105 | classroom | 126 | 8 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 1.0739 | 1 | 21.0739 | 3
106 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0 | 0 | 20 | 3
107 | classroom | 210 | 14 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 1.7898 | 1 | 21.7898 | 3
108 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0 | 0 | 20 | 3
109 | classroom |  | 0 | Yes | 880 | 20 | 20 |  | 7040 | unk | unk | 20 | 3
111 | Classroom |  | 0 | Yes | 880 | 20 | 20 |  | 7040 | unk | unk | 20 | 3
112 | Classroom |  | 0 | Yes | 260 | 5 | 5 |  | 2080 | unk | unk | 20 | 3
201 | classroom | 255 | 17 | Yes | 875 | 19 | 19 | Unit Ventilator | 7000 | 2.1857 | 1 | 22.1857 | 3
202 | classroom | 257 | 17 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.1903 | 1 | 22.1903 | 3
203 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0 | 0 | 20 | 3
204 | classroom | 365 | 24 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 3.1108 | 1 | 23.1108 | 3
205 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0 | 0 | 20 | 3
206 | classroom | 84 | 5 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0.71591 | 0 | 20.7159 | 3
207 | classroom | 0 | 0 | Yes | 575 | 13 | 13 | Unit Ventilator | 4600 | 0 | 0 | 20 | 3
208 | classroom | 47 | 3 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0.40057 | 0 | 20.4006 | 3
209 | classroom | 235 | 15 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.0028 | 1 | 22.0028 | 3
210 | classroom | 0 | 0 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 0 | 0 | 20 | 3
211 | classroom | 244 | 16 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.0795 | 1 | 22.0795 | 3
214 | Classroom |  | 0 | Yes | 228 | 5 | 5 |  | 1824 | unk | unk | 20 | 3
- | Auditorium | 0 | 0 |  | 3300 | 75 | 0 | AHU | 26400 | 0 | 0 | 0 | 0
- | GYM | 573 | 38 |  | 5000 | 113 | 38 | AHU | 40000 | 0.8595 | 0 | 0.8595 | 0
- | Library | 0 | 0 |  | 2700 | 61 | 0 | RTU | 21600 | 0 | 0 | 0 | 0
Anna Blakiston Day Elementary School- Little School House | [9 empty] | unk | unk | unk | unk
1 | classroom | 322 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.2869 | 1 | 2.2869 | 1
2 | classroom | 274 | 18 |  | 1056 | 24 | 18 | AHU | 8448 | 1.946 | 1 | 1.946 | 1
3 | classroom | 322 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.2869 | 1 | 2.2869 | 1
4 | classroom | 510 | 34 |  | 1056 | 24 | 24 | AHU | 8448 | 3.6222 | 1 | 3.6222 | 1
5 | classroom | 302 | 20 |  | 1056 | 24 | 20 | AHU | 8448 | 2.1449 | 1 | 2.1449 | 1
6 | classroom | 325 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.3082 | 1 | 2.3082 | 1
7 | classroom | 302 | 20 |  | 1056 | 24 | 20 | AHU | 8448 | 2.1449 | 1 | 2.1449 | 1
8 | classroom | 325 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.3082 | 1 | 2.3082 | 1
9 | classroom | 302 | 20 |  | 1056 | 24 | 20 | AHU | 8448 | 2.1449 | 1 | 2.1449 | 1
10 | classroom | 325 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.3082 | 1 | 2.3082 | 1
11 | classroom | 302 | 20 |  | 1056 | 24 | 20 | AHU | 8448 | 2.1449 | 1 | 2.1449 | 1
12 | classroom | 325 | 21 |  | 1056 | 24 | 21 | AHU | 8448 | 2.3082 | 1 | 2.3082 | 1
- | Lunchroom | 1136 | 75 |  | 1750 | 39 | 39 | AHU | 14000 | 4.8686 | 2 | 4.8686 | 2
- | Staff Bathroom Staff Toilet | 159 | 10 |  | 120 | 2 | 2 | N/A | 960 | 9.9375 | 2 | 9.9375 | 2
- | Staff Bathroom Staff Toilet | 277 | 18 |  | 120 | 2 | 2 | N/A | 960 | 17.3125 | 3 | 17.3125 | 3
- | Various Office | 392 | 26 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | Corridor | 224 | 14 |  |  | 0 | 0 | FCU |  | unk | unk | unk | unk
- | Various Storage | 374 | 24 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-21 | [8 empty] | unk | unk | unk | unk
School: | Julia deBurgos Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
108 | storage |  | 0 |  | 100 | 2 | 0 | AHU-1 | 800 | unk | unk | unk | unk
111 | work rm |  | 0 |  | 100 | 2 | 0 | AHU-1 | 800 | unk | unk | unk | unk
115 | office | 100 | 6 |  | 150 | 3 | 3 | AHU-1 | 1200 | 5 | 2 | 5 | 2
116 | classroom | 281 | 18 |  | 658 | 14 | 14 | Univent | 5264 | 3.2029 | 1 | 3.2029 | 1
118 | classroom |  | 0 |  | 400 | 9 | 0 | AHU-1 | 3200 | unk | unk | unk | unk
120 | classroom | 380 | 25 |  | 759 | 17 | 17 | Univent | 6072 | 3.7549 | 1 | 3.7549 | 1
121 | classroom | 288 | 19 |  | 759 | 17 | 17 | Univent | 6072 | 2.8458 | 1 | 2.8458 | 1
123 | classroom | 486 | 32 |  | 759 | 17 | 17 | Univent | 6072 | 4.8024 | 2 | 4.8024 | 2
125 | classroom | 307 | 20 |  | 759 | 17 | 17 | Univent | 6072 | 3.0336 | 1 | 3.0336 | 1
129 | classroom | 335 | 22 |  | 640 | 14 | 14 | Univent | 5120 | 3.9258 | 1 | 3.9258 | 1
130 | classroom | 295 | 19 |  | 672 | 15 | 15 | Univent | 5376 | 3.2924 | 1 | 3.2924 | 1
132 | classroom | 470 | 31 |  | 704 | 16 | 16 | Univent | 5632 | 5.0071 | 2 | 5.0071 | 2
133 | classroom | 345 | 23 |  | 880 | 20 | 20 | Univent | 7040 | 2.9403 | 1 | 2.9403 | 1
134 | classroom | 301 | 20 |  | 667 | 15 | 15 | AHU-5 | 5336 | 3.3846 | 1 | 3.3846 | 1
135 | classroom | 552 | 36 |  | 750 | 17 | 17 | Univent | 6000 | 5.52 | 2 | 5.52 | 2
136 | classroom | 291 | 19 |  | 750 | 17 | 17 | Univent | 6000 | 2.91 | 1 | 2.91 | 1
138 | classroom | 734 | 48 |  | 748 | 17 | 17 | AHU-5 | 5984 | 7.3596 | 2 | 7.3596 | 2
139 | classroom | 0 | 0 | Yes | 704 | 16 | 16 | AHU-5 | 5632 | 0 | 0 | 20 | 3
139B | PRACTICE RM | 0 | 0 |  | 100 | 2 | 0 | AHU-5 | 800 | 0 | 0 | 0 | 0
139C | PRACTICE RM | 0 | 0 |  | 100 | 2 | 0 | AHU-5 | 800 | 0 | 0 | 0 | 0
148 | office | 244 | 16 |  | 350 | 7 | 7 | AHU-5 | 2800 | 5.2286 | 2 | 5.2286 | 2
148A | office | 130 | 8 |  | 100 | 2 | 2 | AHU-5 | 800 | 9.75 | 2 | 9.75 | 2
148B | office | 54 | 3 |  | 110 | 2 | 2 | AHU-5 | 880 | 3.6818 | 1 | 3.6818 | 1
148C | office | 37 | 2 |  | 100 | 2 | 2 | AHU-5 | 800 | 2.775 | 1 | 2.775 | 1
148D | office | 51 | 3 |  | 100 | 2 | 2 | AHU-5 | 800 | 3.825 | 1 | 3.825 | 1
148E | office | 67 | 4 |  | 100 | 2 | 2 | AHU-5 | 800 | 5.025 | 2 | 5.025 | 2
148F | office | 89 | 5 |  | 100 | 2 | 2 | AHU-5 | 800 | 6.675 | 2 | 6.675 | 2
148G | office | 44 | 2 |  | 100 | 2 | 2 | AHU-5 | 800 | 3.3 | 1 | 3.3 | 1
148H | office | 26 | 1 |  | 100 | 2 | 1 | AHU-5 | 800 | 1.95 | 1 | 1.95 | 1
148I | office | 64 | 4 |  | 100 | 2 | 2 | AHU-5 | 800 | 4.8 | 2 | 4.8 | 2
148L | office | 126 | 8 |  | 242 | 5 | 5 | AHU-5 | 1936 | 3.905 | 1 | 3.905 | 1
149 | office | 59 | 3 |  | 100 | 2 | 2 | AHU-5 | 800 | 4.425 | 2 | 4.425 | 2
- | Nurse Office |  | 0 | Yes | 180 | 4 | 4 | AHU-5 | 1440 | unk | unk | 20 | 3
151 | WAITING RM | 22 | 1 | Yes | 180 | 4 | 4 | AHU-5 | 1440 | 0.91667 | 0 | 20.9167 | 3
151A | OFFICE | 0 | 0 |  | 110 | 2 | 0 | AHU-5 | 880 | 0 | 0 | 0 | 0
151B | OFFICE | 17 | 1 |  | 150 | 3 | 1 | AHU-5 | 1200 | 0.85 | 0 | 0.85 | 0
151C | OFFICE | 17 | 1 |  | 80 | 1 | 1 | AHU-5 | 640 | 1.5938 | 1 | 1.5938 | 1
151E | OFFICE | 0 | 0 |  | 100 | 2 | 0 | AHU-5 | 800 | 0 | 0 | 0 | 0
152f | office | 39 | 2 |  | 99 | 2 | 2 | AHU-5 | 792 | 2.9545 | 1 | 2.9545 | 1
152g | office | 47 | 3 |  | 99 | 2 | 2 | AHU-5 | 792 | 3.5606 | 1 | 3.5606 | 1
152h | office | 0 | 0 |  | 208 | 4 | 0 | AHU-5 | 1664 | 0 | 0 | 0 | 0
152j | office | 178 | 11 |  | 288 | 6 | 6 | AHU-5 | 2304 | 4.6354 | 2 | 4.6354 | 2
152k | office | 160 | 10 |  | 368 | 8 | 8 | AHU-5 | 2944 | 3.2609 | 1 | 3.2609 | 1
202 | classroom | 608 | 40 |  | 759 | 17 | 17 | Univent | 6072 | 6.0079 | 2 | 6.0079 | 2
203 | classroom | 481 | 32 |  | 759 | 17 | 17 | Univent | 6072 | 4.753 | 2 | 4.753 | 2
207 | classroom | 310 | 20 |  | 1081 | 24 | 20 | Univent | 8648 | 2.1508 | 1 | 2.1508 | 1
208 | classroom | 331 | 22 |  | 621 | 14 | 14 | Univent | 4968 | 3.9976 | 1 | 3.9976 | 1
211 | classroom | 300 | 20 |  | 759 | 17 | 17 | Univent | 6072 | 2.9644 | 1 | 2.9644 | 1
212 | classroom | 405 | 27 |  | 759 | 17 | 17 | Univent | 6072 | 4.002 | 2 | 4.002 | 2
213 | classroom | 345 | 23 |  | 759 | 17 | 17 | Univent | 6072 | 3.4091 | 1 | 3.4091 | 1
215 | office | 385 | 25 |  | 675 | 15 | 15 | AHU-1 | 5400 | 4.2778 | 2 | 4.2778 | 2
218 | classroom | 720 | 48 |  | 759 | 17 | 17 | Univent | 6072 | 7.1146 | 2 | 7.1146 | 2
220 | classroom | 360 | 24 |  | 759 | 17 | 17 | Univent | 6072 | 3.5573 | 1 | 3.5573 | 1
221 | classroom | 310 | 20 |  | 759 | 17 | 17 | Univent | 6072 | 3.0632 | 1 | 3.0632 | 1
225 | classroom | 413 | 27 |  | 759 | 17 | 17 | Univent | 6072 | 4.081 | 2 | 4.081 | 2
226 | classroom | 328 | 21 |  | 759 | 17 | 17 | Univent | 6072 | 3.2411 | 1 | 3.2411 | 1
228 | classroom | 345 | 23 |  | 759 | 17 | 17 | Univent | 6072 | 3.4091 | 1 | 3.4091 | 1
229 | classroom | 300 | 20 |  | 759 | 17 | 17 | Univent | 6072 | 2.9644 | 1 | 2.9644 | 1
230 | classroom | 345 | 23 |  | 1196 | 27 | 23 | Univent | 9568 | 2.1635 | 1 | 2.1635 | 1
236 | classroom | 83 | 5 |  | 494 | 11 | 5 | AHU-5 | 3952 | 1.2601 | 1 | 1.2601 | 1
236A | STORAGE | 150 | 10 |  | 171 | 3 | 3 | AHU-5 | 1368 | 6.5789 | 2 | 6.5789 | 2
236B | OFFICE | 0 | 0 |  | 171 | 3 | 0 | AHU-5 | 1368 | 0 | 0 | 0 | 0
237B | STORAGE | 37 | 2 |  | 165 | 3 | 2 | AHU-5 | 1320 | 1.6818 | 1 | 1.6818 | 1
237C | OFFICE | 63 | 4 |  | 165 | 3 | 3 | AHU-5 | 1320 | 2.8636 | 1 | 2.8636 | 1
238 | classroom | 442 | 29 |  | 759 | 17 | 17 | Univent | 6072 | 4.3676 | 2 | 4.3676 | 2
239 | classroom | 284 | 18 |  | 759 | 17 | 17 | Univent | 6072 | 2.8063 | 1 | 2.8063 | 1
302 | classroom | 430 | 28 |  | 1081 | 24 | 24 | Univent | 8648 | 2.9833 | 1 | 2.9833 | 1
306 | classroom | 289 | 19 |  | 526 | 11 | 11 | Univent | 4208 | 4.1207 | 2 | 4.1207 | 2
307 | classroom | 299 | 19 |  | 621 | 14 | 14 | Univent | 4968 | 3.6111 | 1 | 3.6111 | 1
308 | classroom | 285 | 19 |  | 504 | 11 | 11 | Univent | 4032 | 4.2411 | 2 | 4.2411 | 2
310 | classroom | 320 | 21 |  | 759 | 17 | 17 | Univent | 6072 | 3.1621 | 1 | 3.1621 | 1
311 | classroom | 365 | 24 |  | 759 | 17 | 17 | Univent | 6072 | 3.6067 | 1 | 3.6067 | 1
312 | classroom | 325 | 21 |  | 759 | 17 | 17 | Univent | 6072 | 3.2115 | 1 | 3.2115 | 1
313 | office | 453 | 30 |  | 675 | 15 | 15 | AHU-1 | 5400 | 5.0333 | 2 | 5.0333 | 2
316 | classroom | 345 | 23 |  | 759 | 17 | 17 | Univent | 6072 | 3.4091 | 1 | 3.4091 | 1
317 | classroom | 380 | 25 |  | 759 | 17 | 17 | Univent | 6072 | 3.7549 | 1 | 3.7549 | 1
319 | classroom | 307 | 20 |  | 989 | 22 | 20 | Unit Ventilator | 7912 | 2.3281 | 1 | 2.3281 | 1
319A | storage | 233 | 15 |  | 367 | 8 | 8 | Unit Ventilator | 2936 | 4.7616 | 2 | 4.7616 | 2
323 | classroom | 336 | 22 |  | 759 | 17 | 17 | Univent | 6072 | 3.3202 | 1 | 3.3202 | 1
324 | classroom | 384 | 25 |  | 759 | 17 | 17 | Univent | 6072 | 3.7945 | 1 | 3.7945 | 1
326 | classroom | 423 | 28 |  | 759 | 17 | 17 | Univent | 6072 | 4.1798 | 2 | 4.1798 | 2
327 | classroom | 453 | 30 |  | 759 | 17 | 17 | Univent | 6072 | 4.4763 | 2 | 4.4763 | 2
328 | classroom | 425 | 28 |  | 759 | 17 | 17 | Univent | 6072 | 4.1996 | 2 | 4.1996 | 2
335 | STUDIO | 389 | 25 |  | 798 | 18 | 18 | AHU-8 | 6384 | 3.656 | 1 | 3.656 | 1
336 | classroom | 366 | 24 |  | 759 | 17 | 17 | Univent | 6072 | 3.6166 | 1 | 3.6166 | 1
337 | classroom | 375 | 25 |  | 759 | 17 | 17 | Univent | 6072 | 3.7055 | 1 | 3.7055 | 1
- | BOYS LOCKER ROOM | 80 | 5 |  | 143 | 3 | 3 | AHU-5 | 1144 | 4.1958 | 2 | 4.1958 | 2
- | FRONT IMC LIBRARY | 118 | 7 |  | 171 | 3 | 3 | AHU-5 | 1368 | 5.1754 | 2 | 5.1754 | 2
- | GIRLS LOCKER ROOM | 84 | 5 |  | 143 | 3 | 3 | AHU-5 | 1144 | 4.4056 | 2 | 4.4056 | 2
- | GYM OFFICE | 41 | 2 |  | 225 | 5 | 2 | AHU-5 | 1800 | 1.3667 | 1 | 1.3667 | 1
- | LIBRARY | 892 | 59 |  | 3276 | 74 | 59 | AHU-8 | 26208 | 2.0421 | 1 | 2.0421 | 1
- | Mail Room | 159 | 10 |  | 200 | 4 | 4 | AHU-5 | 1600 | 5.9625 | 2 | 5.9625 | 2
- | Main Office | 618 | 41 |  | 924 | 21 | 21 | AHU-5 | 7392 | 5.0162 | 2 | 5.0162 | 2
- | Principal Office | 208 | 13 |  | 324 | 7 | 7 | AHU-5 | 2592 | 4.8148 | 2 | 4.8148 | 2
- | Staff Locker Room |  | 0 |  | 70 | 1 | 0 | AHU-1 | 560 | unk | unk | unk | unk
- | Storage Office | 38 | 2 |  | 100 | 2 | 2 | AHU-5 | 800 | 2.85 | 1 | 2.85 | 1
- | Cafeteria | 4650 | 310 |  | 6020 | 136 | 136 | AHU-2 | 48160 | 5.7932 | 2 | 5.7932 | 2
- | Gym | 3322 | 221 |  | 5904 | 134 | 134 | ahu-6 | 47232 | 4.22 | 2 | 4.22 | 2
- | Auditorium | 3405 | 227 |  | 2983 | 67 | 67 | AHU-7 | 23864 | 8.561 | 2 | 8.561 | 2
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | Stephen Decatur Elementary School | [8 empty] | unk | unk | unk | unk
| Stephen Decatur Elementary School Annex | [8 empty] | unk | unk | unk | unk
| Stephen Decatur Elementary School White Building | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | Devine Brothers | Devine Retest | Emcor Retest 2-15 | [5 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Decatur Main Building | [9 empty] | unk | unk | unk | unk
K-1 | classroom | 283 | 18 |  | 1450 | 32 | 18 | Unit Ventilator | 11600 | 1.4638 | 1 | 1.4638 | 1
K-2 | classroom | 375 | 25 |  | 1450 | 32 | 25 | Unit Ventilator | 11600 | 1.9397 | 1 | 1.9397 | 1
100 | classroom | 329 | 21 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 2.7508 | 1 | 2.7508 | 1
101 | classroom | 271 | 18 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 2.5248 | 1 | 2.5248 | 1
102 | classroom | 228 | 15 |  | 897 | 20 | 15 | Unit Ventilator | 7176 | 1.9064 | 1 | 1.9064 | 1
103 | classroom | 253 | 16 |  | 805 | 18 | 16 | Unit Ventilator | 6440 | 2.3571 | 1 | 2.3571 | 1
104 | classroom | 240 | 16 |  | 897 | 20 | 16 | Unit Ventilator | 7176 | 2.0067 | 1 | 2.0067 | 1
105 | classroom | 321 | 21 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 2.9907 | 1 | 2.9907 | 1
106 | Nurse's Office |  | 0 | Yes | 357 | 8 | 8 | N/A | 2856 | unk | unk | 20 | 3
107 | classroom | 326 | 21 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 3.0373 | 1 | 3.0373 | 1
108 | classroom | 322 | 21 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 2.6923 | 1 | 2.6923 | 1
109 | classroom | 326 | 21 |  | 851 | 19 | 19 | Unit Ventilator | 6808 | 2.8731 | 1 | 2.8731 | 1
110 | classroom | 301 | 20 |  | 702 | 15 | 15 | Unit Ventilator | 5616 | 3.2158 | 1 | 3.2158 | 1
200 | Classroom | 352 | 23 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 3.2795 | 1 | 3.2795 | 1
201 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | unk | unk | 20 | 3
203 | Classroom | 234 | 15 |  | 854 | 19 | 15 | Unit Ventilator | 6832 | 2.055 | 1 | 2.055 | 1
204 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | unk | unk | 20 | 3
206 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | unk | unk | 20 | 3
208 | Classroom | 301 | 20 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 2.8043 | 1 | 2.8043 | 1
210 | Classroom | 242 | 16 |  | 805 | 18 | 16 | Unit Ventilator | 6440 | 2.2547 | 1 | 2.2547 | 1
212 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | unk | unk | 20 | 3
214 | Classroom | 247 | 16 |  | 391 | 8 | 8 | Unit Ventilator | 3128 | 4.7379 | 2 | 4.7379 | 2
216/218 | Classroom | 599 | 39 |  | 1702 | 38 | 38 | Unit Ventilator | 13616 | 2.6395 | 1 | 2.6395 | 1
217 | Classroom | 283 | 18 |  | 1352 | 30 | 18 | Unit Ventilator | 10816 | 1.5699 | 1 | 1.5699 | 1
219 | Classroom | 274 | 18 |  | 798 | 18 | 18 | Unit Ventilator | 6384 | 2.5752 | 1 | 2.5752 | 1
220 | Classroom | 184 | 12 | Yes | 865 | 19 | 19 | Unit Ventilator | 6920 | 1.5954 | 1 | 21.5954 | 3
300 | Classroom |  | 0 | Yes | 910 | 20 | 20 |  | 7280 | unk | unk | 20 | 3
301 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | unk | unk | 20 | 3
302 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | unk | unk | 20 | 3
303 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | unk | unk | 20 | 3
304 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | unk | unk | 20 | 3
305 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | unk | unk | 20 | 3
306 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | unk | unk | 20 | 3
308 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | unk | unk | 20 | 3
310 | Classroom |  | 0 | Yes | 910 | 20 | 20 |  | 7280 | unk | unk | 20 | 3
312 | Classroom | 277 | 18 |  | 391 | 8 | 8 | Unit Ventilator | 3128 | 5.3133 | 2 | 5.3133 | 2
314 | Classroom | 241 | 16 |  | 397 | 9 | 9 | Unit Ventilator | 3176 | 4.5529 | 2 | 4.5529 | 2
316 | Classroom | 238 | 15 |  | 851 | 19 | 15 | Unit Ventilator | 6808 | 2.0975 | 1 | 2.0975 | 1
317 | Classroom |  | 0 | Yes | 910 | 20 | 20 |  | 7280 | unk | unk | 20 | 3
318 | Classroom |  | 0 | Yes | 850 | 19 | 19 |  | 6800 | unk | unk | 20 | 3
319 | Classroom |  | 0 | Yes | 910 | 20 | 20 |  | 7280 | unk | unk | 20 | 3
320 | Classroom |  | 0 | Yes | 910 | 20 | 20 |  | 7280 | unk | unk | 20 | 3
- | AP | N/A | 0 |  | 126 | 2 | 0 | N/A | 1008 | unk | unk | unk | unk
- | Auditorium | 675 | 45 |  | 2800 | 63 | 45 | AHU | 22400 | 1.808 | 1 | 1.808 | 1
- | Basement | 0 | 0 |  | 456 | 10 | 0 | N/A | 3648 | 0 | 0 | 0 | 0
B-1 | - |  | 0 | Yes | 731 | 16 | 16 | Unit Ventilator | 5848 | unk | unk | 20 | 3
B-2 | Counselors | 356 | 23 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 3.0514 | 1 | 3.0514 | 1
- | Dean | N/A | 0 |  | 126 | 2 | 0 | N/A | 1008 | unk | unk | unk | unk
- | ESOL | 275 | 18 |  | 750 | 17 | 17 | Unit Ventilator | 6000 | 2.75 | 1 | 2.75 | 1
- | GYM | 1543 | 102 |  | 4108 | 93 | 93 | AHU | 32864 | 2.8171 | 1 | 2.8171 | 1
- | IMC | 301 | 20 |  | 1404 | 31 | 20 | RTU | 11232 | 1.6079 | 1 | 1.6079 | 1
- | Main Office | 360 | 24 |  | 999 | 22 | 22 | Unit Ventilator | 7992 | 2.7027 | 1 | 2.7027 | 1
- | Cafeteria | 0 | 0 | Yes | 6161 | 140 | 140 | Unit Ventilator | 49288 | 0 | 0 | 20 | 3
Decatur Annex | [9 empty] | unk | unk | unk | unk
A-1 | classroom | 335 | 22 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 2.8714 | 1 | 2.8714 | 1
A-2 | classroom | 294 | 19 |  | 899 | 20 | 19 | Unit Ventilator | 7192 | 2.4527 | 1 | 2.4527 | 1
A-3 | classroom | 329 | 21 |  | 874 | 19 | 19 | Unit Ventilator | 6992 | 2.8232 | 1 | 2.8232 | 1
A-4 | classroom | 285 | 19 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 2.5088 | 1 | 2.5088 | 1
A-5 | classroom | 326 | 21 |  | 861 | 19 | 19 | Unit Ventilator | 6888 | 2.8397 | 1 | 2.8397 | 1
A-6 | classroom | 322 | 21 |  | 789 | 17 | 17 | Unit Ventilator | 6312 | 3.0608 | 1 | 3.0608 | 1
A-7 | classroom | 317 | 21 |  | 899 | 20 | 20 | Unit Ventilator | 7192 | 2.6446 | 1 | 2.6446 | 1
A-8 | classroom | 332 | 22 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.9928 | 1 | 2.9928 | 1
A-9 | classroom | 288 | 19 |  | 879 | 19 | 19 | Unit Ventilator | 7032 | 2.4573 | 1 | 2.4573 | 1
A-10 | classroom | 281 | 18 |  | 888 | 20 | 18 | Unit Ventilator | 7104 | 2.3733 | 1 | 2.3733 | 1
Decatur White Building | [9 empty] | unk | unk | unk | unk
1 | classroom | 315 | 21 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 2.7 | 1 | 2.7 | 1
2 | classroom | 241 | 16 |  | 888 | 20 | 16 | Unit Ventilator | 7104 | 2.0355 | 1 | 2.0355 | 1
3 | classroom | 340 | 22 |  | 878 | 19 | 19 | Unit Ventilator | 7024 | 2.9043 | 1 | 2.9043 | 1
4 | classroom | 284 | 18 |  | 845 | 19 | 18 | Unit Ventilator | 6760 | 2.5207 | 1 | 2.5207 | 1
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | William Dick Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | Exhaust Report | Retest Report | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 355 | 23 |  | 963 | 21 | 21 | Unit Ventilator | 7704 | 2.7648 | 1 | 2.7648 | 1
102 | Classroom | 319 | 21 |  | 963 | 21 | 21 | Unit Ventilator | 7704 | 2.4844 | 1 | 2.4844 | 1
103 | Nurses Office |  | 0 | Yes | 825 | 18 | 18 |  | 6600 | unk | unk | 20 | 3
104 | Classroom | 481 | 32 |  | 1036 | 23 | 23 | Unit Ventilator | 8288 | 3.4821 | 1 | 3.4821 | 1
105 | Office | 0 | 0 | Yes | 4046 | 91 | 91 | Unit Ventilator | 32368 | 0 | 0 | 20 | 3
105-A | Principal's Office |  | 0 | Yes | 280 | 6 | 6 |  | 2240 | unk | unk | 20 | 3
106 | Small room |  | 0 | Yes | 303 | 6 | 6 |  | 2424 | unk | unk | 20 | 3
107 | Classroom | 328 | 21 |  | 1050 | 23 | 21 | Unit Ventilator | 8400 | 2.3429 | 1 | 2.3429 | 1
108 | Classroom | 167 | 11 |  | 1055 | 23 | 11 | Unit Ventilator | 8440 | 1.1872 | 1 | 1.1872 | 1
109 | Classroom | 237 | 15 | Yes | 1048 | 23 | 23 | Unit Ventilator | 8384 | 1.6961 | 1 | 21.6961 | 3
111 | Classroom | 176 | 11 | Yes | 1272 | 28 | 28 | Unit Ventilator | 10176 | 1.0377 | 1 | 21.0377 | 3
112 | Classroom | 345 | 23 |  | 1275 | 28 | 23 | Unit Ventilator | 10200 | 2.0294 | 1 | 2.0294 | 1
200 | Room |  | 0 | Yes | 133 | 3 | 3 |  | 1064 | unk | unk | 20 | 3
201 | Classroom | 356 | 23 |  | 747 | 16 | 16 | Unit Ventilator | 5976 | 3.5743 | 1 | 3.5743 | 1
202 | Classroom | 286 | 19 |  | 1051 | 23 | 19 | Unit Ventilator | 8408 | 2.0409 | 1 | 2.0409 | 1
203 | Classroom | 158 | 10 | Yes | 1052 | 23 | 23 | Unit Ventilator | 8416 | 1.1264 | 1 | 21.1264 | 3
204 | Classroom | 142 | 9 | Yes | 1035 | 23 | 23 | Unit Ventilator | 8280 | 1.029 | 1 | 21.029 | 3
205 | Classroom | 191 | 12 | Yes | 1057 | 24 | 24 | Unit Ventilator | 8456 | 1.3553 | 1 | 21.3553 | 3
207 | Classroom | 199 | 13 | Yes | 1009 | 22 | 22 | Unit Ventilator | 8072 | 1.4792 | 1 | 21.4792 | 3
208 | Classroom | 207 | 13 | Yes | 1049 | 23 | 23 | Unit Ventilator | 8392 | 1.48 | 1 | 21.48 | 3
209 | Classroom | 317 | 21 |  | 1055 | 23 | 21 | Unit Ventilator | 8440 | 2.2536 | 1 | 2.2536 | 1
211 | Classroom | 286 | 19 |  | 1049 | 23 | 19 | Unit Ventilator | 8392 | 2.0448 | 1 | 2.0448 | 1
212 | Classroom | 344 | 22 |  | 1048 | 23 | 22 | Unit Ventilator | 8384 | 2.4618 | 1 | 2.4618 | 1
213 | Classroom | 235 | 15 | Yes | 1049 | 23 | 23 | Unit Ventilator | 8392 | 1.6802 | 1 | 21.6802 | 3
214 | Classroom | 119 | 7 | Yes | 1029 | 23 | 23 | Unit Ventilator | 8232 | 0.86735 | 0 | 20.8673 | 3
300 | Counselor's Office |  | 0 | Yes | 164 | 3 | 3 |  | 1312 | unk | unk | 20 | 3
301 | Classroom | 136 | 9 | Yes | 741 | 16 | 16 | Unit Ventilator | 5928 | 1.3765 | 1 | 21.3765 | 3
302 | Classroom | 398 | 26 |  | 1053 | 23 | 23 | Unit Ventilator | 8424 | 2.8348 | 1 | 2.8348 | 1
303 | Library | 241 | 16 | Yes | 1032 | 23 | 23 | Unit Ventilator | 8256 | 1.7515 | 1 | 21.7515 | 3
304 | Classroom | 169 | 11 | Yes | 1049 | 23 | 23 | Unit Ventilator | 8392 | 1.2083 | 1 | 21.2083 | 3
305 | Classroom | 330 | 22 |  | 1213 | 27 | 22 | Unit Ventilator | 9704 | 2.0404 | 1 | 2.0404 | 1
307 | Classroom | 101 | 6 | Yes | 1057 | 24 | 24 | Unit Ventilator | 8456 | 0.71665 | 0 | 20.7167 | 3
308 | Classroom | 133 | 8 | Yes | 1028 | 23 | 23 | Unit Ventilator | 8224 | 0.97033 | 0 | 20.9703 | 3
309 | Classroom | 369 | 24 |  | 1048 | 23 | 23 | Unit Ventilator | 8384 | 2.6407 | 1 | 2.6407 | 1
311 | Classroom | 406 | 27 |  | 1050 | 23 | 23 | Unit Ventilator | 8400 | 2.9 | 1 | 2.9 | 1
312 | Classroom | 281 | 18 |  | 1046 | 23 | 18 | Unit Ventilator | 8368 | 2.0148 | 1 | 2.0148 | 1
313 | Classroom | 53 | 3 | Yes | 1046 | 23 | 23 | Unit Ventilator | 8368 | 0.38002 | 0 | 20.38 | 3
314 | Classroom | 0 | 0 | Yes | 1047 | 23 | 23 | Unit Ventilator | 8376 | 0 | 0 | 20 | 3
- | Gymnasium | 248 | 16 |  | 739 | 16 | 16 | Unit Ventilator | 5912 | 2.5169 | 1 | 2.5169 | 1
- | Auditorium |  | 0 |  | 4436 | 100 | 0 | AHU | 35488 | unk | unk | unk | unk
- | Building Engineer's Office |  | 0 | Yes | 482 | 10 | 10 |  | 3856 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-03 | [8 empty] | unk | unk | unk | unk
School: | Hamilton Disston Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Mechanical Rm. |  | 0 |  | 570 | 12 | 0 | House Fan | 4560 | unk | unk | unk | unk
B1 | Cafeteria | 1021 | 68 |  | 1680 | 38 | 38 | House Fan | 13440 | 4.558 | 2 | 4.558 | 2
B2 | Food Service | 1059 | 70 |  | 816 | 18 | 18 | House Fan | 6528 | 9.7335 | 2 | 9.7335 | 2
B3 | Gym | 0 | 0 | Yes | 3840 | 87 | 87 | House Fan | 30720 | 0 | 0 | 20 | 3
- | Gym Office | 0 | 0 |  | 288 | 6 | 0 | House Fan | 2304 | 0 | 0 | 0 | 0
B4 | Classroom | 0 | 0 | Yes | 1008 | 22 | 22 | House Fan | 8064 | 0 | 0 | 20 | 3
B5 | Classroom | 1005 | 67 |  | 864 | 19 | 19 | House Fan | 6912 | 8.724 | 2 | 8.724 | 2
B6 | Classroom | 768 | 51 |  | 984 | 22 | 22 | House Fan | 7872 | 5.8537 | 2 | 5.8537 | 2
017B | Basement Girls Bathroom | 464 | 30 |  | 504 | 11 | 11 | House Fan | 4032 | 6.9048 | 2 | 6.9048 | 2
011B | Basement Boys Bathroom | 271 | 18 |  | 528 | 12 | 12 | House Fan | 4224 | 3.8494 | 1 | 3.8494 | 1
101 | Classroom | 545 | 36 |  | 816 | 18 | 18 | House Fan | 6528 | 5.0092 | 2 | 5.0092 | 2
102 | Classroom | 764 | 50 |  | 720 | 16 | 16 | House Fan | 5760 | 7.9583 | 2 | 7.9583 | 2
103 | Classroom | 821 | 54 |  | 864 | 19 | 19 | House Fan | 6912 | 7.1267 | 2 | 7.1267 | 2
104 | Classroom | 593 | 39 |  | 766 | 17 | 17 | House Fan | 6128 | 5.8061 | 2 | 5.8061 | 2
104A | Office | 0 | 0 | Yes | 168 | 3 | 3 | House Fan | 1344 | 0 | 0 | 20 | 3
- | Auditorium | 3956 | 263 |  | 2784 | 63 | 63 | House Fan | 22272 | 10.6573 | 3 | 10.6573 | 3
105 | Classroom | 635 | 42 |  | 766 | 17 | 17 | House Fan | 6128 | 6.2174 | 2 | 6.2174 | 2
106 | Classroom | 403 | 26 |  | 864 | 19 | 19 | House Fan | 6912 | 3.4983 | 1 | 3.4983 | 1
107 | Classroom | 574 | 38 |  | 720 | 16 | 16 | House Fan | 5760 | 5.9792 | 2 | 5.9792 | 2
108 | Classroom | 593 | 39 |  | 816 | 18 | 18 | House Fan | 6528 | 5.4504 | 2 | 5.4504 | 2
- | Nurses Office | 0 | 0 | Yes | 200 | 4 | 4 | House Fan | 1600 | 0 | 0 | 20 | 3
201 | Classroom | 447 | 29 |  | 816 | 18 | 18 | House Fan | 6528 | 4.1085 | 2 | 4.1085 | 2
202 | Classroom | 668 | 44 |  | 720 | 16 | 16 | House Fan | 5760 | 6.9583 | 2 | 6.9583 | 2
203 | Classroom | 601 | 40 |  | 864 | 19 | 19 | House Fan | 6912 | 5.217 | 2 | 5.217 | 2
203A | Climate Office | 0 | 0 | Yes | 280 | 6 | 6 | House Fan | 2240 | 0 | 0 | 20 | 3
204 | Classroom | 548 | 36 |  | 816 | 18 | 18 | House Fan | 6528 | 5.0368 | 2 | 5.0368 | 2
204A | AP Office | 0 | 0 |  | 180 | 4 | 0 | House Fan | 1440 | 0 | 0 | 0 | 0
205 | Classroom | 301 | 20 |  | 816 | 18 | 18 | House Fan | 6528 | 2.7665 | 1 | 2.7665 | 1
- | Counselor's Office | 0 | 0 | Yes | 260 | 5 | 5 | House Fan | 2080 | 0 | 0 | 20 | 3
206 | Classroom | 570 | 38 |  | 864 | 19 | 19 | House Fan | 6912 | 4.9479 | 2 | 4.9479 | 2
207 | Classroom | 421 | 28 |  | 720 | 16 | 16 | House Fan | 5760 | 4.3854 | 2 | 4.3854 | 2
208 | Classroom | 281 | 18 |  | 816 | 18 | 18 | House Fan | 6528 | 2.5827 | 1 | 2.5827 | 1
- | Helping Hands Office | 0 | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | 0 | 0 | 20 | 3
301A | Office | 0 | 0 |  | 280 | 6 | 0 | House Fan | 2240 | 0 | 0 | 0 | 0
301 | Classroom | 365 | 24 |  | 816 | 18 | 18 | House Fan | 6528 | 3.3548 | 1 | 3.3548 | 1
302 | Classroom | 563 | 37 |  | 720 | 16 | 16 | House Fan | 5760 | 5.8646 | 2 | 5.8646 | 2
303 | Classroom | 442 | 29 |  | 864 | 19 | 19 | House Fan | 6912 | 3.8368 | 1 | 3.8368 | 1
304 | Classroom | 657 | 43 |  | 816 | 18 | 18 | House Fan | 6528 | 6.0386 | 2 | 6.0386 | 2
305 | Classroom | 53 | 3 | Yes | 870 | 19 | 19 | House Fan | 6960 | 0.4569 | 0 | 20.4569 | 3
306 | Classroom | 186 | 12 |  | 864 | 19 | 12 | House Fan | 6912 | 1.6146 | 1 | 1.6146 | 1
307 | Classroom | 56 | 3 | Yes | 957 | 21 | 21 | House Fan | 7656 | 0.43887 | 0 | 20.4389 | 3
308 | Classroom | 489 | 32 |  | 864 | 19 | 19 | House Fan | 6912 | 4.2448 | 2 | 4.2448 | 2
309 | Classroom | 127 | 8 | Yes | 900 | 20 | 20 | House Fan | 7200 | 1.0583 | 1 | 21.0583 | 3
310 | Classroom | 96 | 6 | Yes | 816 | 18 | 18 | House Fan | 6528 | 0.88235 | 0 | 20.8824 | 3
311 | Classroom | 611 | 40 |  | 864 | 19 | 19 | House Fan | 6912 | 5.3038 | 2 | 5.3038 | 2
312 | Classroom | 424 | 28 |  | 720 | 16 | 16 | House Fan | 5760 | 4.4167 | 2 | 4.4167 | 2
313 | Classroom | 411 | 27 |  | 816 | 18 | 18 | House Fan | 6528 | 3.7776 | 1 | 3.7776 | 1
313A | Office | 0 | 0 |  | 816 | 18 | 0 | House Fan | 6528 | 0 | 0 | 0 | 0
- | Library | 747 | 49 |  | 2156 | 49 | 49 | RTU-1 | 17248 | 2.5986 | 1 | 2.5986 | 1
- | Office | 155 | 10 |  | 312 | 7 | 7 | RTU-1 | 2496 | 3.726 | 1 | 3.726 | 1
- | Office | 55 | 3 |  | 312 | 7 | 3 | RTU-1 | 2496 | 1.3221 | 1 | 1.3221 | 1
- | Main Office | 0 | 0 | Yes | 308 | 7 | 7 | RTU-2 | 2464 | 0 | 0 | 20 | 3
- | Principal Office | 0 | 0 |  | 160 | 3 | 0 | RTU-2 | 1280 | 0 | 0 | 0 | 0
- | Faculty Lounge | 0 | 0 |  | 312 | 7 | 0 | RTU-2 | 2496 | 0 | 0 | 0 | 0
- | Modular Classroom | 0 | 0 |  | 720 | 16 | 0 | AHU | 5760 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-19 | [8 empty] | unk | unk | unk | unk
School: | Murrell Dobbins Vocational High School | [8 empty] | unk | unk | unk | unk
Vendor: | Capital | Devine Brothers | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
016 B-5 | Classroom | 1130 | 75 |  | 2511 | 57 | 57 |  | 20088 | 3.3751 | 1 | 3.3751 | 1
016 B-6 | Classroom | 536 | 35 |  | 2511 | 57 | 35 |  | 20088 | 1.601 | 1 | 1.601 | 1
016 B-7 | Classroom | 718 | 47 |  | 2424 | 55 | 47 |  | 19392 | 2.2215 | 1 | 2.2215 | 1
016 B-8 | Classroom | 494 | 32 |  | 2543 | 57 | 32 |  | 20344 | 1.4569 | 1 | 1.4569 | 1
120 | Classroom | 249 | 16 |  | 597 | 13 | 13 |  | 4776 | 3.1281 | 1 | 3.1281 | 1
122-A | Classroom | 325 | 21 |  | 1226 | 27 | 21 |  | 9808 | 1.9882 | 1 | 1.9882 | 1
122-B | Classroom | 391 | 26 |  | 1226 | 27 | 26 |  | 9808 | 2.3919 | 1 | 2.3919 | 1
123-A | Classroom | 287 | 19 |  | 1445 | 32 | 19 |  | 11560 | 1.4896 | 1 | 1.4896 | 1
123-B | Classroom | 0 | 0 |  | 1445 | 32 | 0 |  | 11560 | 0 | 0 | 0 | 0
123C | Classroom | 0 | 0 |  | 136 | 3 | 0 |  | 1088 | 0 | 0 | 0 | 0
123J | Classroom | 428 | 28 |  | 322 | 7 | 7 |  | 2576 | 9.9689 | 2 | 9.9689 | 2
130 | Classroom | 284 | 18 |  | 1017 | 23 | 18 |  | 8136 | 2.0944 | 1 | 2.0944 | 1
131-A | Classroom | 0 | 0 |  | 2226 | 50 | 0 |  | 17808 | 0 | 0 | 0 | 0
131-B | Classroom | 458 | 30 |  | 2226 | 50 | 30 |  | 17808 | 1.5431 | 1 | 1.5431 | 1
131-C | Classroom | 0 | 0 |  | 2226 | 50 | 0 |  | 17808 | 0 | 0 | 0 | 0
131-D | Classroom | 232 | 15 |  | 2226 | 50 | 15 |  | 17808 | 0.78167 | 0 | 0.78167 | 0
134 | Classroom | 0 | 0 |  | 596 | 13 | 0 |  | 4768 | 0 | 0 | 0 | 0
201 | Library/IMC | 397 | 26 |  | 3115 | 70 | 26 |  | 24920 | 0.95586 | 0 | 0.95586 | 0
220-A | Classroom | 760 | 50 |  | 435 | 9 | 9 |  | 3480 | 13.1034 | 3 | 13.1034 | 3
220-B | Classroom | 452 | 30 |  | 210 | 4 | 4 |  | 1680 | 16.1429 | 3 | 16.1429 | 3
220-C | Classroom | 398 | 26 |  | 210 | 4 | 4 |  | 1680 | 14.2143 | 3 | 14.2143 | 3
220-D | Classroom | 411 | 27 |  | 308 | 7 | 7 |  | 2464 | 10.0081 | 3 | 10.0081 | 3
222 | Classroom | 299 | 19 |  | 1228 | 27 | 19 |  | 9824 | 1.8261 | 1 | 1.8261 | 1
223 | Classroom | 393 | 26 |  | 720 | 16 | 16 |  | 5760 | 4.0938 | 2 | 4.0938 | 2
225 | Classroom | 394 | 26 |  | 735 | 16 | 16 |  | 5880 | 4.0204 | 2 | 4.0204 | 2
227-A | Classroom | 505 | 33 |  | 871 | 19 | 19 |  | 6968 | 4.3485 | 2 | 4.3485 | 2
227-B | Classroom | 335 | 22 |  | 871 | 19 | 19 |  | 6968 | 2.8846 | 1 | 2.8846 | 1
231-A | Classroom | 0 | 0 |  | 1125 | 25 | 0 |  | 9000 | 0 | 0 | 0 | 0
231-B | Classroom | 141 | 9 |  | 1125 | 25 | 9 |  | 9000 | 0.94 | 0 | 0.94 | 0
233-A | Classroom | 371 | 24 |  | 2122 | 48 | 24 |  | 16976 | 1.3113 | 1 | 1.3113 | 1
233-B | Classroom | 347 | 23 |  | 2122 | 48 | 23 |  | 16976 | 1.2264 | 1 | 1.2264 | 1
233-C | Classroom | 319 | 21 |  | 2122 | 48 | 21 |  | 16976 | 1.1275 | 1 | 1.1275 | 1
234 | Classroom | 0 | 0 |  | 771 | 17 | 0 |  | 6168 | 0 | 0 | 0 | 0
236 | Classroom | 381 | 25 |  | 1030 | 23 | 23 |  | 8240 | 2.7743 | 1 | 2.7743 | 1
236,234,233, | Classrooms | 6741 | 449 |  | 792 | 18 | 18 |  | 6336 | 63.8352 | 5 | 63.8352 | 5
232, & 231 | [9 empty] | unk | unk | unk | unk
- | 2nd E/Center Corr | 375 | 25 |  | 2310 | 52 | 25 |  | 18480 | 1.2175 | 1 | 1.2175 | 1
- | 2nd East Corr | 312 | 20 |  | 2310 | 52 | 20 |  | 18480 | 1.013 | 1 | 1.013 | 1
- | 2nd W/Center Corr | 292 | 19 |  | 2310 | 52 | 19 |  | 18480 | 0.94805 | 0 | 0.94805 | 0
- | 2nd West Corr | 0 | 0 |  | 2310 | 52 | 0 |  | 18480 | 0 | 0 | 0 | 0
300 | Classroom | 451 | 30 |  | 975 | 22 | 22 |  | 7800 | 3.4692 | 1 | 3.4692 | 1
305,330,331, | Classrooms | 7434 | 495 |  | 792 | 18 | 18 |  | 6336 | 70.3977 | 5 | 70.3977 | 5
332, & 332A | [9 empty] | unk | unk | unk | unk
315-A | Classroom | 300 | 20 |  | 1008 | 22 | 20 |  | 8064 | 2.2321 | 1 | 2.2321 | 1
315-B | Classroom | 390 | 26 |  | 1008 | 22 | 22 |  | 8064 | 2.9018 | 1 | 2.9018 | 1
317 | Classroom | 346 | 23 |  | 832 | 18 | 18 |  | 6656 | 3.119 | 1 | 3.119 | 1
321,323,322, | Classrooms | 5053 | 336 |  | 792 | 18 | 18 |  | 6336 | 47.8504 | 4 | 47.8504 | 4
322A, &322B | [9 empty] | unk | unk | unk | unk
322-A | Classroom | 0 | 0 |  | 3737 | 84 | 0 |  | 29896 | 0 | 0 | 0 | 0
322-B | Classroom | 171 | 11 |  | 3737 | 84 | 11 |  | 29896 | 0.34319 | 0 | 0.34319 | 0
322-C | Classroom | 0 | 0 |  | 3737 | 84 | 0 |  | 29896 | 0 | 0 | 0 | 0
322-D | Classroom | 680 | 45 |  | 3737 | 84 | 45 |  | 29896 | 1.3647 | 1 | 1.3647 | 1
322-E | Classroom | 756 | 50 |  | 3737 | 84 | 50 |  | 29896 | 1.5173 | 1 | 1.5173 | 1
322B | Classroom | 89 | 5 |  | 187 | 4 | 4 |  | 1496 | 3.5695 | 1 | 3.5695 | 1
323-A | Classroom | 682 | 45 |  | 1035 | 23 | 23 |  | 8280 | 4.942 | 2 | 4.942 | 2
331-A | Classroom | 538 | 35 |  | 1852 | 42 | 35 |  | 14816 | 2.1787 | 1 | 2.1787 | 1
331-B | Classroom | 221 | 14 |  | 1852 | 42 | 14 |  | 14816 | 0.89498 | 0 | 0.89498 | 0
332-A | Classroom | 352 | 23 |  | 963 | 21 | 21 |  | 7704 | 2.7414 | 1 | 2.7414 | 1
332-B | Classroom | 371 | 24 |  | 963 | 21 | 21 |  | 7704 | 2.8894 | 1 | 2.8894 | 1
333-A | Classroom | 478 | 31 |  | 1862 | 42 | 31 |  | 14896 | 1.9253 | 1 | 1.9253 | 1
333-B | Classroom | 0 | 0 |  | 1862 | 42 | 0 |  | 14896 | 0 | 0 | 0 | 0
333-C | Classroom | 543 | 36 |  | 1862 | 42 | 36 |  | 14896 | 2.1872 | 1 | 2.1872 | 1
335 | Classroom | 393 | 26 |  | 250 | 5 | 5 |  | 2000 | 11.79 | 3 | 11.79 | 3
- | 3rd E/Center Corr | 296 | 19 |  | 2310 | 52 | 19 |  | 18480 | 0.96104 | 0 | 0.96104 | 0
- | 3rd East Corr | 310 | 20 |  | 2310 | 52 | 20 |  | 18480 | 1.0065 | 1 | 1.0065 | 1
- | 3rd W/Center Corr | 437 | 29 |  | 2310 | 52 | 29 |  | 18480 | 1.4188 | 1 | 1.4188 | 1
- | 3rd West Corr | 0 | 0 |  | 2310 | 52 | 0 |  | 18480 | 0 | 0 | 0 | 0
400-A | Classroom | 356 | 23 |  | 2045 | 46 | 23 |  | 16360 | 1.3056 | 1 | 1.3056 | 1
400-B | Classroom | 333 | 22 |  | 2045 | 46 | 22 |  | 16360 | 1.2213 | 1 | 1.2213 | 1
400, 402, 403, & 403A | Classroom | 21 | 1 |  | 2310 | 52 | 1 |  | 18480 | 0.068182 | 0 | 0.068182 | 0
401-A | Classroom | 0 | 0 |  | 1080 | 24 | 0 |  | 8640 | 0 | 0 | 0 | 0
401-B | Classroom | 168 | 11 |  | 1080 | 24 | 11 |  | 8640 | 1.1667 | 1 | 1.1667 | 1
401A | Storage | 264 | 17 |  | 222 | 5 | 5 |  | 1776 | 8.9189 | 2 | 8.9189 | 2
402-A | Classroom | 0 | 0 |  | 951 | 21 | 0 |  | 7608 | 0 | 0 | 0 | 0
402-B | Classroom | 194 | 12 |  | 951 | 21 | 12 |  | 7608 | 1.53 | 1 | 1.53 | 1
403-A | Classroom | 257 | 17 |  | 2279 | 51 | 17 |  | 18232 | 0.84577 | 0 | 0.84577 | 0
403-B | Classroom | 81 | 5 |  | 2279 | 51 | 5 |  | 18232 | 0.26656 | 0 | 0.26656 | 0
403-C | Classroom | 190 | 12 |  | 2279 | 51 | 12 |  | 18232 | 0.62527 | 0 | 0.62527 | 0
403-D | Classroom | 226 | 15 |  | 2279 | 51 | 15 |  | 18232 | 0.74375 | 0 | 0.74375 | 0
410-A | Classroom | 273 | 18 |  | 1058 | 24 | 18 |  | 8464 | 1.9353 | 1 | 1.9353 | 1
410-B | Classroom | 273 | 18 |  | 1058 | 24 | 18 |  | 8464 | 1.9353 | 1 | 1.9353 | 1
411-A | Classroom | 0 | 0 |  | 1067 | 24 | 0 |  | 8536 | 0 | 0 | 0 | 0
411-B | Classroom | 0 | 0 |  | 1067 | 24 | 0 |  | 8536 | 0 | 0 | 0 | 0
412 | Classroom | 422 | 28 |  | 1066 | 24 | 24 |  | 8528 | 2.969 | 1 | 2.969 | 1
413 | Classroom | 0 | 0 |  | 952 | 21 | 0 |  | 7616 | 0 | 0 | 0 | 0
414 | Classroom | 364 | 24 |  | 921 | 20 | 20 |  | 7368 | 2.9642 | 1 | 2.9642 | 1
420-A | Classroom | 766 | 51 |  | 745 | 16 | 16 |  | 5960 | 7.7114 | 2 | 7.7114 | 2
420-B | Classroom | 326 | 21 |  | 745 | 16 | 16 |  | 5960 | 3.2819 | 1 | 3.2819 | 1
422-A | Classroom | 514 | 34 |  | 2438 | 55 | 34 |  | 19504 | 1.5812 | 1 | 1.5812 | 1
422-B | Classroom | 417 | 27 |  | 2438 | 55 | 27 |  | 19504 | 1.2828 | 1 | 1.2828 | 1
422-C | Classroom | 407 | 27 |  | 2438 | 55 | 27 |  | 19504 | 1.2521 | 1 | 1.2521 | 1
423 & 420 | Classrooms | 0 | 0 |  | 576 | 13 | 0 |  | 4608 | 0 | 0 | 0 | 0
423-A | Classroom | 0 | 0 |  | 1372 | 31 | 0 |  | 10976 | 0 | 0 | 0 | 0
423-B | Classroom | 0 | 0 |  | 1372 | 31 | 0 |  | 10976 | 0 | 0 | 0 | 0
430-A | Classroom | 300 | 20 |  | 1431 | 32 | 20 |  | 11448 | 1.5723 | 1 | 1.5723 | 1
430-B | Classroom | 319 | 21 |  | 1431 | 32 | 21 |  | 11448 | 1.6719 | 1 | 1.6719 | 1
430,431, & 432 | Classrooms | 8038 | 535 |  | 792 | 18 | 18 |  | 6336 | 76.1174 | 5 | 76.1174 | 5
431-A | Classroom | 673 | 44 |  | 2491 | 56 | 44 |  | 19928 | 2.0263 | 1 | 2.0263 | 1
431-B | Classroom | 221 | 14 |  | 2491 | 56 | 14 |  | 19928 | 0.6654 | 0 | 0.6654 | 0
431-C | Classroom | 533 | 35 |  | 2491 | 56 | 35 |  | 19928 | 1.6048 | 1 | 1.6048 | 1
431-D | Classroom | 347 | 23 |  | 2491 | 56 | 23 |  | 19928 | 1.0448 | 1 | 1.0448 | 1
431-E | Classroom | 325 | 21 |  | 2491 | 56 | 21 |  | 19928 | 0.97852 | 0 | 0.97852 | 0
- | 4th E/Center Corr | 0 | 0 |  | 2310 | 52 | 0 |  | 18480 | 0 | 0 | 0 | 0
- | 4th East Corr | 0 | 0 |  | 2310 | 52 | 0 |  | 18480 | 0 | 0 | 0 | 0
- | 4th W/ Center Corr | 199 | 13 |  | 2310 | 52 | 13 |  | 18480 | 0.6461 | 0 | 0.6461 | 0
- | 4th West Corr | 267 | 17 |  | 2310 | 52 | 17 |  | 18480 | 0.86688 | 0 | 0.86688 | 0
500 | Classroom | 299 | 19 |  | 1160 | 26 | 19 |  | 9280 | 1.9332 | 1 | 1.9332 | 1
500-A | Classroom | 301 | 20 |  | 270 | 6 | 6 |  | 2160 | 8.3611 | 2 | 8.3611 | 2
501 | Classroom | 388 | 25 |  | 956 | 21 | 21 |  | 7648 | 3.0439 | 1 | 3.0439 | 1
502-A | Classroom | 206 | 13 |  | 956 | 21 | 13 |  | 7648 | 1.6161 | 1 | 1.6161 | 1
502-B | Classroom | 258 | 17 |  | 956 | 21 | 17 |  | 7648 | 2.0241 | 1 | 2.0241 | 1
503-A | Classroom | 208 | 13 |  | 956 | 21 | 13 |  | 7648 | 1.6318 | 1 | 1.6318 | 1
503-B | Classroom | 144 | 9 |  | 956 | 21 | 9 |  | 7648 | 1.1297 | 1 | 1.1297 | 1
504-A | Classroom | 224 | 14 |  | 957 | 21 | 14 |  | 7656 | 1.7555 | 1 | 1.7555 | 1
504-B | Classroom | 108 | 7 |  | 957 | 21 | 7 |  | 7656 | 0.84639 | 0 | 0.84639 | 0
505 | Classroom | 0 | 0 |  | 863 | 19 | 0 |  | 6904 | 0 | 0 | 0 | 0
506-A | Classroom | 0 | 0 |  | 833 | 18 | 0 |  | 6664 | 0 | 0 | 0 | 0
506-B | Classroom | 280 | 18 |  | 833 | 18 | 18 |  | 6664 | 2.521 | 1 | 2.521 | 1
507-A | Classroom | 221 | 14 |  | 1032 | 23 | 14 |  | 8256 | 1.6061 | 1 | 1.6061 | 1
507-B | Classroom | 467 | 31 |  | 1032 | 23 | 23 |  | 8256 | 3.3939 | 1 | 3.3939 | 1
510-A | Classroom | 313 | 20 |  | 1085 | 24 | 20 |  | 8680 | 2.1636 | 1 | 2.1636 | 1
510-B | Classroom | 323 | 21 |  | 1085 | 24 | 21 |  | 8680 | 2.2327 | 1 | 2.2327 | 1
511 | Classroom | 293 | 19 |  | 954 | 21 | 19 |  | 7632 | 2.3035 | 1 | 2.3035 | 1
512 | Classroom | 344 | 22 |  | 712 | 16 | 16 |  | 5696 | 3.6236 | 1 | 3.6236 | 1
513 | Classroom | 294 | 19 |  | 712 | 16 | 16 |  | 5696 | 3.0969 | 1 | 3.0969 | 1
514 | Classroom | 311 | 20 |  | 665 | 15 | 15 |  | 5320 | 3.5075 | 1 | 3.5075 | 1
515 | Classroom | 358 | 23 |  | 818 | 18 | 18 |  | 6544 | 3.2824 | 1 | 3.2824 | 1
516 | Classroom | 394 | 26 |  | 819 | 18 | 18 |  | 6552 | 3.6081 | 1 | 3.6081 | 1
520-B | Classroom | 0 | 0 |  | 221 | 5 | 0 |  | 1768 | 0 | 0 | 0 | 0
522 | Classroom | 0 | 0 |  | 316 | 7 | 0 |  | 2528 | 0 | 0 | 0 | 0
523 | Classroom | 0 | 0 |  | 795 | 18 | 0 |  | 6360 | 0 | 0 | 0 | 0
524 | Classroom | 0 | 0 |  | 800 | 18 | 0 |  | 6400 | 0 | 0 | 0 | 0
525 | Classroom | 378 | 25 |  | 851 | 19 | 19 |  | 6808 | 3.3314 | 1 | 3.3314 | 1
526-A | Classroom | 57 | 3 |  | 961 | 21 | 3 |  | 7688 | 0.44485 | 0 | 0.44485 | 0
526-B | Classroom | 377 | 25 |  | 961 | 21 | 21 |  | 7688 | 2.9422 | 1 | 2.9422 | 1
530 | Classroom | 293 | 19 |  | 821 | 18 | 18 |  | 6568 | 2.6766 | 1 | 2.6766 | 1
531-A | Classroom | 576 | 38 |  | 724 | 16 | 16 |  | 5792 | 5.9669 | 2 | 5.9669 | 2
531-B | Classroom | 81 | 5 |  | 724 | 16 | 5 |  | 5792 | 0.83909 | 0 | 0.83909 | 0
532 | Classroom | 292 | 19 |  | 879 | 19 | 19 |  | 7032 | 2.4915 | 1 | 2.4915 | 1
533-A | Classroom | 225 | 15 |  | 800 | 18 | 15 |  | 6400 | 2.1094 | 1 | 2.1094 | 1
533-B | Classroom | 0 | 0 |  | 800 | 18 | 0 |  | 6400 | 0 | 0 | 0 | 0
534-A | Classroom | 438 | 29 |  | 1036 | 23 | 23 |  | 8288 | 3.1708 | 1 | 3.1708 | 1
534-B | Classroom | 0 | 0 |  | 1036 | 23 | 0 |  | 8288 | 0 | 0 | 0 | 0
535 | Classroom | 0 | 0 |  | 1006 | 22 | 0 |  | 8048 | 0 | 0 | 0 | 0
- | 5th E.Cent Corr | 201 | 13 |  | 2310 | 52 | 13 |  | 18480 | 0.6526 | 0 | 0.6526 | 0
- | 5th East Corr. | 0 | 0 |  | 2310 | 52 | 0 |  | 18480 | 0 | 0 | 0 | 0
- | 5th W.Cent Corr | 276 | 18 |  | 2310 | 52 | 18 |  | 18480 | 0.8961 | 0 | 0.8961 | 0
601-A | Classroom | 138 | 9 |  | 1553 | 35 | 9 |  | 12424 | 0.66645 | 0 | 0.66645 | 0
601-B | Classroom | 0 | 0 |  | 1553 | 35 | 0 |  | 12424 | 0 | 0 | 0 | 0
601-C | Classroom | 0 | 0 |  | 1553 | 35 | 0 |  | 12424 | 0 | 0 | 0 | 0
603-A | Classroom | 0 | 0 |  | 962 | 21 | 0 |  | 7696 | 0 | 0 | 0 | 0
603-B | Classroom | 229 | 15 |  | 962 | 21 | 15 |  | 7696 | 1.7853 | 1 | 1.7853 | 1
604 | Classroom | 0 | 0 |  | 400 | 9 | 0 |  | 3200 | 0 | 0 | 0 | 0
610 | Classroom | 331 | 22 |  | 738 | 16 | 16 |  | 5904 | 3.3638 | 1 | 3.3638 | 1
611 | Classroom | 460 | 30 |  | 712 | 16 | 16 |  | 5696 | 4.8455 | 2 | 4.8455 | 2
612 | Classroom | 298 | 19 |  | 704 | 16 | 16 |  | 5632 | 3.1747 | 1 | 3.1747 | 1
613 | Classroom | 257 | 17 |  | 711 | 16 | 16 |  | 5688 | 2.711 | 1 | 2.711 | 1
614 | Classroom | 270 | 18 |  | 800 | 18 | 18 |  | 6400 | 2.5312 | 1 | 2.5312 | 1
615 | Classroom | 382 | 25 |  | 814 | 18 | 18 |  | 6512 | 3.5197 | 1 | 3.5197 | 1
622-A | Classroom | 0 | 0 |  | 801 | 18 | 0 |  | 6408 | 0 | 0 | 0 | 0
622-B | Classroom | 242 | 16 |  | 801 | 18 | 16 |  | 6408 | 2.2659 | 1 | 2.2659 | 1
623 | Classroom | 682 | 45 |  | 679 | 15 | 15 |  | 5432 | 7.5331 | 2 | 7.5331 | 2
624 | Classroom | 267 | 17 |  | 820 | 18 | 17 |  | 6560 | 2.4421 | 1 | 2.4421 | 1
625 | Classroom | 174 | 11 |  | 680 | 15 | 11 |  | 5440 | 1.9191 | 1 | 1.9191 | 1
627 | Classroom | 815 | 54 |  | 794 | 18 | 18 |  | 6352 | 7.6984 | 2 | 7.6984 | 2
- | 6th Center Corr. | 0 | 0 |  | 792 | 18 | 0 |  | 6336 | 0 | 0 | 0 | 0
- | 6th East Corr. | 466 | 31 |  | 792 | 18 | 18 |  | 6336 | 4.4129 | 2 | 4.4129 | 2
- | Admin | 4788 | 319 |  | 786 | 17 | 17 |  | 6288 | 45.687 | 4 | 45.687 | 4
- | Auditorium | 0 | 0 | Yes | 10676 | 242 | 242 |  | 85408 | 0 | 0 | 20 | 3
- | Boy's Gym | 0 | 0 |  | 5940 | 135 | 0 |  | 47520 | 0 | 0 | 0 | 0
- | Girl's Gym | 0 | 0 |  | 5696 | 129 | 0 |  | 45568 | 0 | 0 | 0 | 0
- | Lunch Rm | 0 | 0 |  | 4563 | 103 | 0 |  | 36504 | 0 | 0 | 0 | 0
- | Lunch Rm | 0 | 0 |  | 4563 | 103 | 0 |  | 36504 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | James Dobson Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | unk | unk | 20 | 3
101 | Classroom |  | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
104 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
106 | Office |  | 0 | Yes | 638 | 14 | 14 | House Fan | 5104 | unk | unk | 20 | 3
107 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
108 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
109 | Classroom |  | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
204 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
205 | Office |  | 0 | Yes | 342 | 7 | 7 | House Fan | 2736 | unk | unk | 20 | 3
206 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
207 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
208 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
209 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
210 | Office |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
303/304 | Classroom |  | 0 | Yes | 1320 | 30 | 30 | House Fan | 10560 | unk | unk | 20 | 3
306/307 | Classroom |  | 0 | Yes | 1320 | 30 | 30 | House Fan | 10560 | unk | unk | 20 | 3
308 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
309 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
313 | Classroom |  | 0 | Yes | 858 | 19 | 19 | House Fan | 6864 | unk | unk | 20 | 3
- | Councelors office |  | 0 | Yes | 243 | 5 | 5 |  | 1944 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 510 | 11 | 11 | House Fan | 4080 | unk | unk | 20 | 3
- | Principals office |  | 0 | Yes | 236 | 5 | 5 | House Fan | 1888 | unk | unk | 20 | 3
- | Gym |  | 0 | Yes | 3080 | 70 | 70 |  | 24640 | unk | unk | 20 | 3
- | Cafeteria large |  | 0 |  | 944 | 21 | 0 |  | 7552 | unk | unk | unk | unk
- | Auditorium |  | 0 |  | 3124 | 71 | 0 |  | 24992 | unk | unk | unk | unk
- | Library |  | 0 | Yes | 1320 | 30 | 30 |  | 10560 | unk | unk | 20 | 3
- | Nurses office |  | 0 | Yes | 264 | 6 | 6 |  | 2112 | unk | unk | 20 | 3
| Cafeteria small |  | 0 |  | 919 | 20 |  |  | 7352 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-21 | [8 empty] | unk | unk | unk | unk
School: | Tanner Duckrey Elementary School | [8 empty] | unk | unk | unk | unk
| Exhaust Report | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B19 | Art Room | 358 | 23 |  | 1032 | 23 | 23 | AHU | 8256 | 2.6017 | 1 | 2.6017 | 1
B21 | Classroom | 0 | 0 | Yes | 1029 | 23 | 23 | Unit Ventilator | 8232 | 0 | 0 | 20 | 3
111 | Classroom | 718 | 47 |  | 1115 | 25 | 25 | Unit Ventilator | 8920 | 4.8296 | 2 | 4.8296 | 2
114 | Classroom | 284 | 18 |  | 941 | 21 | 18 | Unit Ventilator | 7528 | 2.2635 | 1 | 2.2635 | 1
117 | Classroom | 608 | 40 |  | 940 | 21 | 21 | Unit Ventilator | 7520 | 4.8511 | 2 | 4.8511 | 2
118 | Classroom | 271 | 18 |  | 691 | 15 | 15 | Unit Ventilator | 5528 | 2.9414 | 1 | 2.9414 | 1
119 | - | 276 | 18 | Yes | 1237 | 28 | 28 | Unit Ventilator | 9896 | 1.6734 | 1 | 21.6734 | 3
120 | Classroom | 638 | 42 |  | 1024 | 23 | 23 | Unit Ventilator | 8192 | 4.6729 | 2 | 4.6729 | 2
121A | Classroom | 367 | 24 |  | 715 | 16 | 16 | Unit Ventilator | 5720 | 3.8497 | 1 | 3.8497 | 1
121B | Classroom | 315 | 21 |  | 795 | 18 | 18 | Unit Ventilator | 6360 | 2.9717 | 1 | 2.9717 | 1
122 | Classroom | 413 | 27 |  | 1027 | 23 | 23 | Unit Ventilator | 8216 | 3.0161 | 1 | 3.0161 | 1
124 | Classroom | 686 | 45 |  | 921 | 20 | 20 | Unit Ventilator | 7368 | 5.5863 | 2 | 5.5863 | 2
126 | Classroom | 310 | 20 |  | 927 | 21 | 20 | Unit Ventilator | 7416 | 2.5081 | 1 | 2.5081 | 1
128 | Classroom | 409 | 27 |  | 1012 | 23 | 23 | Unit Ventilator | 8096 | 3.0311 | 1 | 3.0311 | 1
130 | Classroom | 429 | 28 |  | 1101 | 25 | 25 | Unit Ventilator | 8808 | 2.9223 | 1 | 2.9223 | 1
200 | - | 639 | 42 |  | 1036 | 23 | 23 | Unit Ventilator | 8288 | 4.626 | 2 | 4.626 | 2
201 | - | 803 | 53 |  | 1050 | 23 | 23 | Unit Ventilator | 8400 | 5.7357 | 2 | 5.7357 | 2
204 | - | 564 | 37 |  | 952 | 21 | 21 | Unit Ventilator | 7616 | 4.4433 | 2 | 4.4433 | 2
207 | - | 0 | 0 | Yes | 951 | 21 | 21 | Unit Ventilator | 7608 | 0 | 0 | 20 | 3
208 | - | 786 | 52 |  | 917 | 20 | 20 | Unit Ventilator | 7336 | 6.4286 | 2 | 6.4286 | 2
209 | - | 648 | 43 |  | 951 | 21 | 21 | Unit Ventilator | 7608 | 5.1104 | 2 | 5.1104 | 2
210 | - | 638 | 42 |  | 953 | 21 | 21 | Unit Ventilator | 7624 | 5.021 | 2 | 5.021 | 2
211 | - | 617 | 41 |  | 919 | 20 | 20 | Unit Ventilator | 7352 | 5.0354 | 2 | 5.0354 | 2
212 | - |  | 0 | Yes | 1023 | 23 | 23 |  | 8184 | unk | unk | 20 | 3
213 | - | 830 | 55 |  | 1088 | 24 | 24 | Unit Ventilator | 8704 | 5.7215 | 2 | 5.7215 | 2
214 | - | 819 | 54 |  | 1037 | 23 | 23 | Unit Ventilator | 8296 | 5.9233 | 2 | 5.9233 | 2
215 | - | 475 | 31 |  | 1035 | 23 | 23 | Unit Ventilator | 8280 | 3.442 | 1 | 3.442 | 1
216 | - | 838 | 55 |  | 1039 | 23 | 23 | Unit Ventilator | 8312 | 6.0491 | 2 | 6.0491 | 2
216A | - | 384 | 25 |  | 926 | 21 | 21 | Unit Ventilator | 7408 | 3.1102 | 1 | 3.1102 | 1
217 | - | 546 | 36 |  | 922 | 20 | 20 | Unit Ventilator | 7376 | 4.4414 | 2 | 4.4414 | 2
218 | - | 307 | 20 |  | 922 | 20 | 20 | Unit Ventilator | 7376 | 2.4973 | 1 | 2.4973 | 1
219 | - | 348 | 23 |  | 925 | 21 | 21 | Unit Ventilator | 7400 | 2.8216 | 1 | 2.8216 | 1
220 | - | 459 | 30 |  | 411 | 9 | 9 | Unit Ventilator | 3288 | 8.3759 | 2 | 8.3759 | 2
220A | - | 290 | 19 |  | 330 | 7 | 7 | Unit Ventilator | 2640 | 6.5909 | 2 | 6.5909 | 2
221 | - | 556 | 37 |  | 873 | 19 | 19 | Unit Ventilator | 6984 | 4.7766 | 2 | 4.7766 | 2
221A | - | 432 | 28 |  | 194 | 4 | 4 | Unit Ventilator | 1552 | 16.701 | 3 | 16.701 | 3
222 | - | 334 | 22 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 2.8629 | 1 | 2.8629 | 1
223 | - | 538 | 35 |  | 872 | 19 | 19 | Unit Ventilator | 6976 | 4.6273 | 2 | 4.6273 | 2
- | Auditorium/Cafe | 264 | 17 | Yes | 5376 | 122 | 122 | AHU | 43008 | 0.3683 | 0 | 20.3683 | 3
- | Faculty Lounge | 1156 | 77 |  | 513 | 11 | 11 | Unit Ventilator | 4104 | 16.9006 | 3 | 16.9006 | 3
- | Kitchen | 203 | 13 |  | 2070 | 47 | 13 | AHU | 16560 | 0.73551 | 0 | 0.73551 | 0
- | Library | 336 | 22 |  | 1914 | 43 | 22 | AHU | 15312 | 1.3166 | 1 | 1.3166 | 1
- | Main Office | 1063 | 70 |  | 903 | 20 | 20 | Unit Ventilator | 7224 | 8.8289 | 2 | 8.8289 | 2
- | Nurse | 334 | 22 |  | 387 | 8 | 8 | Unit Ventilator | 3096 | 6.4729 | 2 | 6.4729 | 2
- | Science Room | 1464 | 97 |  | 799 | 18 | 18 | Unit Ventilator | 6392 | 13.7422 | 3 | 13.7422 | 3
- | Gym | 215 | 14 |  | 4808 | 109 | 14 | AHU | 38464 | 0.33538 | 0 | 0.33538 | 0
Sheet Last Modified: | 2021-04-06 | [8 empty] | unk | unk | unk | unk
School: | Paul L. Dunbar High School | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
102 | Clasroom | 0 | 0 | Yes | 730 | 16 | 16 | House Fan | 5840 | 0 | 0 | 20 | 3
103 | office | 0 | 0 | Yes | 682 | 15 | 15 | House Fan | 5456 | 0 | 0 | 20 | 3
103 | bathroom | 0 | 0 |  | 49 | 1 | 0 | House Fan | 392 | 0 | 0 | 0 | 0
104 | Lunchroom | 0 | 0 | Yes | 1413 | 32 | 32 | House Fan | 11304 | 0 | 0 | 20 | 3
105 | Classroom | 0 | 0 | Yes | 730 | 16 | 16 | House Fan | 5840 | 0 | 0 | 20 | 3
105 | Bathroom | 0 | 0 |  | 54 | 1 | 0 | House Fan | 432 | 0 | 0 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 914 | 20 | 20 | House Fan | 7312 | 0 | 0 | 20 | 3
107 | Bathroom | 0 | 0 |  | 41 | 0 | 0 | House Fan | 328 | 0 | 0 | 0 | 0
108 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | House Fan | 5456 | 0 | 0 | 20 | 3
108 | Bathroom | 0 | 0 |  | 45 | 1 | 0 | House Fan | 360 | 0 | 0 | 0 | 0
109 | Climate rm | 0 | 0 | Yes | 251 | 5 | 5 | House Fan | 2008 | 0 | 0 | 20 | 3
109 | Bathroom | 0 | 0 |  | 58 | 1 | 0 | House Fan | 464 | 0 | 0 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | House Fan | 5456 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 | Yes | 698 | 15 | 15 | House Fan | 5584 | 0 | 0 | 20 | 3
203 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | House Fan | 5456 | 0 | 0 | 20 | 3
204 | Classroom | 0 | 0 | Yes | 666 | 15 | 15 | House Fan | 5328 | 0 | 0 | 20 | 3
205 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | House Fan | 5456 | 0 | 0 | 20 | 3
206 | Classroom | 0 | 0 | Yes | 716 | 16 | 16 | House Fan | 5728 | 0 | 0 | 20 | 3
207 | Art room | 0 | 0 | Yes | 838 | 19 | 19 | House Fan | 6704 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 679 | 15 | 15 | House Fan | 5432 | 0 | 0 | 20 | 3
209 | scc room | 0 | 0 | Yes | 457 | 10 | 10 | House Fan | 3656 | 0 | 0 | 20 | 3
300 | computer lab | 0 | 0 | Yes | 688 | 15 | 15 | House Fan | 5504 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 | Yes | 688 | 15 | 15 | House Fan | 5504 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 704 | 15 | 15 | House Fan | 5632 | 0 | 0 | 20 | 3
303 | Classroom | 0 | 0 | Yes | 670 | 15 | 15 | House Fan | 5360 | 0 | 0 | 20 | 3
304 | Classroom | 0 | 0 | Yes | 643 | 14 | 14 | House Fan | 5144 | 0 | 0 | 20 | 3
305 | Classroom | 0 | 0 | Yes | 691 | 15 | 15 | House Fan | 5528 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 725 | 16 | 16 | House Fan | 5800 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 | Yes | 966 | 21 | 21 | House Fan | 7728 | 0 | 0 | 20 | 3
308 |  | 0 |  |  | 688 |  | 0 | House Fan | 5504 | 0 | 0 | 0 | 0
309 |  | 0 |  |  | 360 |  | 0 | House Fan | 2880 | 0 | 0 | 0 | 0
310 |  | 0 |  |  | 172 |  | 0 | House Fan | 1376 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 |  | 3202 | 72 | 0 | House Fan | 25616 | 0 | 0 | 0 | 0
- | Boys bathroom near rm 307 | 0 | 0 |  | 297 | 6 | 0 | N/A | 2376 | 0 | 0 | 0 | 0
- | Boys bathroom near Nurse's Office | 0 | 0 |  | 144 | 3 | 0 | N/A | 1152 | 0 | 0 | 0 | 0
- | Basement Boys Bathroom | 0 | 0 |  | 599 | 13 | 0 | N/A | 4792 | 0 | 0 | 0 | 0
- | Basement Boys Bathroom | 0 | 0 |  | 317 | 7 | 0 | N/A | 2536 | 0 | 0 | 0 | 0
- | Girls bathroom near rm 301 | 0 | 0 |  | 415 | 9 | 0 | N/A | 3320 | 0 | 0 | 0 | 0
- | Basement Girls Bathroom | 0 | 0 |  | 387 | 8 | 0 | N/A | 3096 | 0 | 0 | 0 | 0
- | Girls bathroom near rm 201 | 0 | 0 |  | 441 | 10 | 0 | N/A | 3528 | 0 | 0 | 0 | 0
- | Gym | 0 | 0 |  | 2723 | 61 | 0 | House Fan | 21784 | 0 | 0 | 0 | 0
- | IMC | 0 | 0 | Yes | 1168 | 26 | 26 | House Fan | 9344 | 0 | 0 | 20 | 3
- | Main Office | 0 | 0 | Yes | 360 | 8 | 8 | House Fan | 2880 | 0 | 0 | 20 | 3
- | Nurse Office | 0 | 0 | Yes | 175 | 3 | 3 | House Fan | 1400 | 0 | 0 | 20 | 3
- | Principal Office | 0 | 0 | Yes | 231 | 5 | 5 | House Fan | 1848 | 0 | 0 | 20 | 3
- | Asst Principal Office |  | 0 | Yes | 879 | 19 | 19 | House Fan | 7032 | unk | unk | 20 | 3
- | Counselor Office |  | 0 | Yes | 458 | 10 | 10 | House Fan | 3664 | unk | unk | 20 | 3
- | Teachers Lounge | 0 | 0 |  | 605 | 13 | 0 | House Fan | 4840 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-20 | [8 empty] | unk | unk | unk | unk
School: | Thomas Edison High School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Retest | [7 empty] | unk | unk | unk | unk
| Devine 2nd Retest | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Office | 85 | 5 |  | 568 | 12 | 5 | AHU | 4544 | 1.1224 | 1 | 1.1224 | 1
102 | Nurse | 212 | 14 |  | 498 | 11 | 11 | AHU | 3984 | 3.1928 | 1 | 3.1928 | 1
103A | Mail room | 261 | 17 |  | 414 | 9 | 9 | AHU | 3312 | 4.7283 | 2 | 4.7283 | 2
104 | Office | 66 | 4 |  | 140 | 3 | 3 | AHU | 1120 | 3.5357 | 1 | 3.5357 | 1
105 | Office | 171 | 11 |  | 284 | 6 | 6 | AHU | 2272 | 4.5158 | 2 | 4.5158 | 2
105C | Conference | 79 | 5 |  | 242 | 5 | 5 | AHU | 1936 | 2.4483 | 1 | 2.4483 | 1
106 | Office | 94 | 6 |  | 119 | 2 | 2 | AHU | 952 | 5.9244 | 2 | 5.9244 | 2
107 | Office | 68 | 4 |  | 112 | 2 | 2 | AHU | 896 | 4.5536 | 2 | 4.5536 | 2
108 | Office | 61 | 4 |  | 86 | 1 | 1 | AHU | 688 | 5.3198 | 2 | 5.3198 | 2
109 | Office | 56 | 3 |  | 74 | 1 | 1 | AHU | 592 | 5.6757 | 2 | 5.6757 | 2
110 | Office | 71 | 4 |  | 86 | 1 | 1 | AHU | 688 | 6.1919 | 2 | 6.1919 | 2
111 | Office | 68 | 4 |  | 86 | 1 | 1 | AHU | 688 | 5.9302 | 2 | 5.9302 | 2
112 | Office | 80 | 5 |  | 86 | 1 | 1 | AHU | 688 | 6.9767 | 2 | 6.9767 | 2
113 | Office | 63 | 4 |  | 86 | 1 | 1 | AHU | 688 | 5.4942 | 2 | 5.4942 | 2
114 | Office | 115 | 7 |  | 86 | 1 | 1 | AHU | 688 | 10.0291 | 3 | 10.0291 | 3
115 | Office | 124 | 8 |  | 86 | 1 | 1 | AHU | 688 | 10.814 | 3 | 10.814 | 3
116 | Office | 160 | 10 |  | 242 | 5 | 5 | AHU | 1936 | 4.9587 | 2 | 4.9587 | 2
117 | Office | 92 | 6 |  | 20 | 0 | 0 | AHU | 160 | 34.5 | 4 | 34.5 | 4
118 | Office | 55 | 3 |  | 83 | 1 | 1 | AHU | 664 | 4.9699 | 2 | 4.9699 | 2
120 | Office | 70 | 4 |  | 90 | 2 | 2 | AHU | 720 | 5.8333 | 2 | 5.8333 | 2
121 | Office | 56 | 3 |  | 90 | 2 | 2 | AHU | 720 | 4.6667 | 2 | 4.6667 | 2
122 | Office | 69 | 4 |  | 90 | 2 | 2 | AHU | 720 | 5.75 | 2 | 5.75 | 2
123 | Office | 59 | 3 |  | 90 | 2 | 2 | AHU | 720 | 4.9167 | 2 | 4.9167 | 2
124 | Office | 57 | 3 |  | 90 | 2 | 2 | AHU | 720 | 4.75 | 2 | 4.75 | 2
125 | Office | 68 | 4 |  | 90 | 2 | 2 | AHU | 720 | 5.6667 | 2 | 5.6667 | 2
127B | Office | 136 | 9 |  | 174 | 3 | 3 | AHU | 1392 | 5.8621 | 2 | 5.8621 | 2
128 | Conference | 658 | 43 |  | 676 | 15 | 15 | AHU | 5408 | 7.3003 | 2 | 7.3003 | 2
129 | Office | 150 | 10 |  | 281 | 6 | 6 | AHU | 2248 | 4.0036 | 2 | 4.0036 | 2
130 | Office | 262 | 17 |  | 345 | 7 | 7 | AHU | 2760 | 5.6957 | 2 | 5.6957 | 2
131 | Break Room | 84 | 5 |  | 131 | 2 | 2 | AHU | 1048 | 4.8092 | 2 | 4.8092 | 2
132 | Classroom | 292 | 19 |  | 713 | 16 | 16 | AHU | 5704 | 3.0715 | 1 | 3.0715 | 1
133 | Classroom | 273 | 18 |  | 566 | 12 | 12 | AHU | 4528 | 3.6175 | 1 | 3.6175 | 1
134 | Classroom | 575 | 38 |  | 2286 | 51 | 38 | AHU | 18288 | 1.8865 | 1 | 1.8865 | 1
135 | Classroom | 460 | 30 |  | 1604 | 36 | 30 | AHU | 12832 | 2.1509 | 1 | 2.1509 | 1
135A | Kitchen | 61 | 4 |  | 37 | 0 | 0 | AHU | 296 | 12.3649 | 3 | 12.3649 | 3
135B | Office | 78 | 5 |  | 137 | 3 | 3 | AHU | 1096 | 4.2701 | 2 | 4.2701 | 2
136 | Classroom | 310 | 20 |  | 1144 | 26 | 20 | AHU | 9152 | 2.0323 | 1 | 2.0323 | 1
136B | Classroom | 483 | 32 |  | 1142 | 25 | 25 | AHU | 9136 | 3.1721 | 1 | 3.1721 | 1
137 | Classroom | 297 | 19 |  | 2086 | 47 | 19 | AHU | 16688 | 1.0678 | 1 | 1.0678 | 1
137A | Office | 77 | 5 |  | 228 | 5 | 5 | AHU | 1824 | 2.5329 | 1 | 2.5329 | 1
138 | Womens Locker Room | 1166 | 77 |  | 4342 | 98 | 77 | AHU | 34736 | 2.014 | 1 | 2.014 | 1
138A | Office | 50 | 3 |  | 78 | 1 | 1 | AHU | 624 | 4.8077 | 2 | 4.8077 | 2
138B | Office | 124 | 8 |  | 314 | 7 | 7 | AHU | 2512 | 2.9618 | 1 | 2.9618 | 1
139 | Mens Locker Room | 1278 | 85 |  | 3031 | 68 | 68 | AHU | 24248 | 3.1623 | 1 | 3.1623 | 1
139A | Office | 122 | 8 |  | 77 | 1 | 1 | AHU | 616 | 11.8831 | 3 | 11.8831 | 3
139B | Storage | 66 | 4 |  | 178 | 4 | 4 | AHU | 1424 | 2.7809 | 1 | 2.7809 | 1
141 | Physical Fitness | 603 | 40 |  | 1325 | 30 | 30 | AHU | 10600 | 3.4132 | 1 | 3.4132 | 1
144A | Bathroom | 52 | 3 |  | 333 | 7 | 3 | AHU | 2664 | 1.1712 | 1 | 1.1712 | 1
144B | Bathroom | 36 | 2 |  | 211 | 4 | 2 | AHU | 1688 | 1.2796 | 1 | 1.2796 | 1
145 | Plumbing Shop | 6184 | 412 |  | 1635 | 37 | 37 | AHU | 13080 | 28.367 | 4 | 28.367 | 4
145 | Classroom | 358 | 23 |  | 2286 | 51 | 23 | AHU | 18288 | 1.1745 | 1 | 1.1745 | 1
145B | Classroom | 161 | 10 |  | 498 | 11 | 10 | AHU | 3984 | 2.4247 | 1 | 2.4247 | 1
146 | Office | 297 | 19 |  | 1280 | 29 | 19 | AHU | 10240 | 1.7402 | 1 | 1.7402 | 1
146 | Office | 332 | 22 |  | 276 | 6 | 6 | AHU | 2208 | 9.0217 | 2 | 9.0217 | 2
147 | Storage | 87 | 5 |  | 476 | 10 | 5 | AHU | 3808 | 1.3708 | 1 | 1.3708 | 1
147 | Classroom | 553 | 36 |  | 1497 | 34 | 34 | AHU | 11976 | 2.7705 | 1 | 2.7705 | 1
148 | Classroom |  | 0 | Yes | 3146 | 71 | 71 |  | 25168 | unk | unk | 20 | 3
149 | Camera Room | 88 | 5 |  | 208 | 4 | 4 | AHU | 1664 | 3.1731 | 1 | 3.1731 | 1
150 | Classroom | 375 | 25 |  | 814 | 18 | 18 | AHU | 6512 | 3.4552 | 1 | 3.4552 | 1
150A | Office | 0 | 0 |  | 165 | 3 | 0 | AHU | 1320 | 0 | 0 | 0 | 0
150B | Studio | 114 | 7 |  | 1182 | 26 | 7 | AHU | 9456 | 0.72335 | 0 | 0.72335 | 0
151A | Classroom | 534 | 35 |  | 1233 | 28 | 28 | AHU | 9864 | 3.2482 | 1 | 3.2482 | 1
151B | Classroom | 912 | 60 |  | 1441 | 32 | 32 | AHU | 11528 | 4.7467 | 2 | 4.7467 | 2
152 | Classroom | 655 | 43 |  | 794 | 18 | 18 | AHU | 6352 | 6.187 | 2 | 6.187 | 2
152A | Classroom | 994 | 66 |  | 244 | 5 | 5 | AHU | 1952 | 30.5533 | 4 | 30.5533 | 4
152B | Classroom | 901 | 60 |  | 1073 | 24 | 24 | AHU | 8584 | 6.2978 | 2 | 6.2978 | 2
153A | Classroom | 321 | 21 |  | 533 | 12 | 12 | AHU | 4264 | 4.5169 | 2 | 4.5169 | 2
153B | Classroom | 302 | 20 |  | 107 | 2 | 2 | AHU | 856 | 21.1682 | 3 | 21.1682 | 3
154A | Office | 278 | 18 |  | 175 | 3 | 3 | AHU | 1400 | 11.9143 | 3 | 11.9143 | 3
154E | Classroom | 0 | 0 |  | 516 | 11 | 0 | AHU | 4128 | 0 | 0 | 0 | 0
154H | Classroom | 304 | 20 |  | 407 | 9 | 9 | AHU | 3256 | 5.602 | 2 | 5.602 | 2
154D 154A | Theory | 240 | 16 |  | 514 | 11 | 11 | AHU | 4112 | 3.5019 | 1 | 3.5019 | 1
156 | Classroom | 293 | 19 |  | 514 | 11 | 11 | AHU | 4112 | 4.2753 | 2 | 4.2753 | 2
157 | Classroom | 961 | 64 |  | 1255 | 28 | 28 | AHU | 10040 | 5.743 | 2 | 5.743 | 2
158 | Classroom | 592 | 39 |  | 1234 | 28 | 28 | AHU | 9872 | 3.5981 | 1 | 3.5981 | 1
160 | Classroom | 727 | 48 |  | 1267 | 28 | 28 | AHU | 10136 | 4.3035 | 2 | 4.3035 | 2
160A | Office | 78 | 5 |  | 119 | 2 | 2 | AHU | 952 | 4.916 | 2 | 4.916 | 2
161 | Classroom | 551 | 36 |  | 1440 | 32 | 32 | AHU | 11520 | 2.8698 | 1 | 2.8698 | 1
161A | Office | 88 | 5 |  | 120 | 2 | 2 | AHU | 960 | 5.5 | 2 | 5.5 | 2
161H | Classroom | 52 | 3 |  | 36 | 0 | 0 | AHU | 288 | 10.8333 | 3 | 10.8333 | 3
161I | Practice room | 9 | 0 |  | 36 | 0 | 0 | AHU | 288 | 1.875 | 1 | 1.875 | 1
161J | Classroom | 73 | 4 |  | 90 | 2 | 2 | AHU | 720 | 6.0833 | 2 | 6.0833 | 2
164 | Classroom | 1398 | 93 |  | 825 | 18 | 18 | AHU | 6600 | 12.7091 | 3 | 12.7091 | 3
164B | Classroom | 402 | 26 |  | 159 | 3 | 3 | AHU | 1272 | 18.9623 | 3 | 18.9623 | 3
171 | Classroom | 0 | 0 |  | 1392 | 31 | 0 | AHU | 11136 | 0 | 0 | 0 | 0
201 | Classroom | 333 | 22 |  | 679 | 15 | 15 | AHU | 5432 | 3.6782 | 1 | 3.6782 | 1
202 | Classroom | 334 | 22 |  | 677 | 15 | 15 | AHU | 5416 | 3.7001 | 1 | 3.7001 | 1
203 | Classroom | 325 | 21 |  | 680 | 15 | 15 | AHU | 5440 | 3.5846 | 1 | 3.5846 | 1
204 | Classroom | 436 | 29 |  | 770 | 17 | 17 | AHU | 6160 | 4.2468 | 2 | 4.2468 | 2
205 | Classroom | 601 | 40 |  | 1444 | 32 | 32 | AHU | 11552 | 3.1215 | 1 | 3.1215 | 1
205B | Storage | 153 | 10 |  | 375 | 8 | 8 | AHU | 3000 | 3.06 | 1 | 3.06 | 1
207 | Classroom | 845 | 56 |  | 2973 | 67 | 56 | AHU | 23784 | 2.1317 | 1 | 2.1317 | 1
209 | Classroom | 472 | 31 |  | 1646 | 37 | 31 | AHU | 13168 | 2.1507 | 1 | 2.1507 | 1
209B | Storage | 112 | 7 |  | 279 | 6 | 6 | AHU | 2232 | 3.0108 | 1 | 3.0108 | 1
210 | Classroom | 466 | 31 |  | 1552 | 35 | 31 | AHU | 12416 | 2.2519 | 1 | 2.2519 | 1
210B | Storage | 190 | 12 |  | 331 | 7 | 7 | AHU | 2648 | 4.3051 | 2 | 4.3051 | 2
212 | Office | 134 | 8 |  | 174 | 3 | 3 | AHU | 1392 | 5.7759 | 2 | 5.7759 | 2
213A | Classroom | 384 | 25 |  | 721 | 16 | 16 | AHU | 5768 | 3.9945 | 1 | 3.9945 | 1
213B | Classroom | 312 | 20 |  | 872 | 19 | 19 | AHU | 6976 | 2.6835 | 1 | 2.6835 | 1
214 | Classroom | 282 | 18 |  | 703 | 15 | 15 | AHU | 5624 | 3.0085 | 1 | 3.0085 | 1
215 | Classroom | 286 | 19 |  | 828 | 18 | 18 | AHU | 6624 | 2.5906 | 1 | 2.5906 | 1
216 | Office | 164 | 10 |  | 397 | 9 | 9 | AHU | 3176 | 3.0982 | 1 | 3.0982 | 1
217 | Classroom | 356 | 23 |  | 601 | 13 | 13 | AHU | 4808 | 4.4426 | 2 | 4.4426 | 2
218 | Classroom | 352 | 23 |  | 639 | 14 | 14 | AHU | 5112 | 4.1315 | 2 | 4.1315 | 2
219 | Office | 129 | 8 |  | 265 | 6 | 6 | AHU | 2120 | 3.6509 | 1 | 3.6509 | 1
220 | Classroom | 444 | 29 |  | 715 | 16 | 16 | AHU | 5720 | 4.6573 | 2 | 4.6573 | 2
220 | Classroom | 456 | 30 |  | 715 | 16 | 16 | AHU | 5720 | 4.7832 | 2 | 4.7832 | 2
221 | Classroom | 321 | 21 |  | 720 | 16 | 16 | AHU | 5760 | 3.3438 | 1 | 3.3438 | 1
222 | Classroom | 328 | 21 |  | 680 | 15 | 15 | AHU | 5440 | 3.6176 | 1 | 3.6176 | 1
223 | Classroom | 299 | 19 |  | 781 | 17 | 17 | AHU | 6248 | 2.8713 | 1 | 2.8713 | 1
224 | Classroom | 292 | 19 |  | 790 | 17 | 17 | AHU | 6320 | 2.7722 | 1 | 2.7722 | 1
225 | Classroom | 284 | 18 |  | 749 | 17 | 17 | AHU | 5992 | 2.8438 | 1 | 2.8438 | 1
226 | Classroom | 293 | 19 |  | 721 | 16 | 16 | AHU | 5768 | 3.0479 | 1 | 3.0479 | 1
229 | Library | 1039 | 69 |  | 6194 | 140 | 69 | AHU | 49552 | 1.2581 | 1 | 1.2581 | 1
229A | Office | 79 | 5 |  | 117 | 2 | 2 | AHU | 936 | 5.0641 | 2 | 5.0641 | 2
229B | Office | 148 | 9 |  | 229 | 5 | 5 | AHU | 1832 | 4.8472 | 2 | 4.8472 | 2
229C | Computer Lab | 100 | 6 |  | 270 | 6 | 6 | AHU | 2160 | 2.7778 | 1 | 2.7778 | 1
230 | Office | 79 | 5 |  | 218 | 4 | 4 | AHU | 1744 | 2.7179 | 1 | 2.7179 | 1
231 | Classroom | 308 | 20 |  | 613 | 13 | 13 | AHU | 4904 | 3.7684 | 1 | 3.7684 | 1
232 | Office | 144 | 9 |  | 931 | 21 | 9 | AHU | 7448 | 1.16 | 1 | 1.16 | 1
233 | Classroom | 325 | 21 |  | 613 | 13 | 13 | AHU | 4904 | 3.9763 | 1 | 3.9763 | 1
234 | Classroom | 334 | 22 |  | 700 | 15 | 15 | AHU | 5600 | 3.5786 | 1 | 3.5786 | 1
235 | Classroom | 457 | 30 |  | 592 | 13 | 13 | AHU | 4736 | 5.7897 | 2 | 5.7897 | 2
236 | Classroom | 431 | 28 |  | 720 | 16 | 16 | AHU | 5760 | 4.4896 | 2 | 4.4896 | 2
237 | Classroom | 220 | 14 |  | 931 | 21 | 14 | AHU | 7448 | 1.7723 | 1 | 1.7723 | 1
238 | Classroom | 112 | 7 |  | 606 | 13 | 7 | AHU | 4848 | 1.3861 | 1 | 1.3861 | 1
239 | Classroom | 494 | 32 |  | 627 | 14 | 14 | AHU | 5016 | 5.9091 | 2 | 5.9091 | 2
240 | Classroom | 957 | 63 |  | 1407 | 31 | 31 | AHU | 11256 | 5.1013 | 2 | 5.1013 | 2
241 | Classroom | 318 | 21 |  | 714 | 16 | 16 | AHU | 5712 | 3.3403 | 1 | 3.3403 | 1
241A | Classroom | 156 | 10 |  | 700 | 15 | 10 | AHU | 5600 | 1.6714 | 1 | 1.6714 | 1
242 | Classroom | 1072 | 71 |  | 1512 | 34 | 34 | AHU | 12096 | 5.3175 | 2 | 5.3175 | 2
243 | Classroom | 605 | 40 |  | 2253 | 51 | 40 | AHU | 18024 | 2.014 | 1 | 2.014 | 1
245 | Classroom | 403 | 26 |  | 1908 | 43 | 26 | AHU | 15264 | 1.5841 | 1 | 1.5841 | 1
245A | Office | 107 | 7 |  | 258 | 5 | 5 | AHU | 2064 | 3.1105 | 1 | 3.1105 | 1
246 | Classroom | 380 | 25 |  | 2009 | 45 | 25 | AHU | 16072 | 1.4186 | 1 | 1.4186 | 1
246B | Classroom | 308 | 20 |  | 510 | 11 | 11 | AHU | 4080 | 4.5294 | 2 | 4.5294 | 2
247 | Classroom | 676 | 45 |  | 1992 | 45 | 45 | AHU | 15936 | 2.5452 | 1 | 2.5452 | 1
247A | Classroom | 383 | 25 |  | 495 | 11 | 11 | AHU | 3960 | 5.803 | 2 | 5.803 | 2
249 | Classroom | 307 | 20 |  | 888 | 20 | 20 | AHU | 7104 | 2.5929 | 1 | 2.5929 | 1
250 | Classroom | 121 | 8 |  | 142 | 3 | 3 | AHU | 1136 | 6.3908 | 2 | 6.3908 | 2
251 | Classroom | 223 | 14 |  | 504 | 11 | 11 | AHU | 4032 | 3.3185 | 1 | 3.3185 | 1
253 | Classroom | 0 | 0 |  | 939 | 21 | 0 | AHU | 7512 | 0 | 0 | 0 | 0
301 | Science Lab | 428 | 28 |  | 940 | 21 | 21 | AHU | 7520 | 3.4149 | 1 | 3.4149 | 1
302 | science prep | 0 | 0 |  | 197 | 4 | 0 | AHU | 1576 | 0 | 0 | 0 | 0
304 | Classroom | 448 | 29 |  | 1086 | 24 | 24 | AHU | 8688 | 3.0939 | 1 | 3.0939 | 1
305 | Classroom | 428 | 28 |  | 469 | 10 | 10 | AHU | 3752 | 6.8443 | 2 | 6.8443 | 2
307 | Lab | 150 | 10 |  | 370 | 8 | 8 | AHU | 2960 | 3.0405 | 1 | 3.0405 | 1
307B | Office | 205 | 13 |  | 161 | 3 | 3 | AHU | 1288 | 9.5497 | 2 | 9.5497 | 2
307C | Office | 152 | 10 |  | 92 | 2 | 2 | AHU | 736 | 12.3913 | 3 | 12.3913 | 3
308 | Science Lab | 360 | 24 |  | 1015 | 23 | 23 | AHU | 8120 | 2.6601 | 1 | 2.6601 | 1
309 | Science Prep | 316 | 21 |  | 260 | 5 | 5 | AHU | 2080 | 9.1154 | 2 | 9.1154 | 2
310 | Classroom | 331 | 22 |  | 990 | 22 | 22 | AHU | 7920 | 2.5076 | 1 | 2.5076 | 1
311 | Classroom | 417 | 27 |  | 997 | 22 | 22 | AHU | 7976 | 3.1369 | 1 | 3.1369 | 1
313 | Classroom | 389 | 25 |  | 716 | 16 | 16 | AHU | 5728 | 4.0747 | 2 | 4.0747 | 2
314 | Classroom | 296 | 19 |  | 793 | 18 | 18 | AHU | 6344 | 2.7995 | 1 | 2.7995 | 1
315 | Classroom | 410 | 27 |  | 804 | 18 | 18 | AHU | 6432 | 3.8246 | 1 | 3.8246 | 1
316 | Classroom | 326 | 21 |  | 750 | 17 | 17 | AHU | 6000 | 3.26 | 1 | 3.26 | 1
317A | Office | 58 | 3 |  | 213 | 4 | 3 | AHU | 1704 | 2.0423 | 1 | 2.0423 | 1
317B | Office | 42 | 2 |  | 220 | 5 | 2 | AHU | 1760 | 1.4318 | 1 | 1.4318 | 1
318 | Classroom | 378 | 25 |  | 678 | 15 | 15 | AHU | 5424 | 4.1814 | 2 | 4.1814 | 2
319 | Classroom | 329 | 21 |  | 678 | 15 | 15 | AHU | 5424 | 3.6394 | 1 | 3.6394 | 1
320 | Classroom | 325 | 21 |  | 678 | 15 | 15 | AHU | 5424 | 3.5951 | 1 | 3.5951 | 1
321 | Classroom | 367 | 24 |  | 678 | 15 | 15 | AHU | 5424 | 4.0597 | 2 | 4.0597 | 2
322 | Faculty Lounge | 34 | 2 |  | 196 | 4 | 2 | AHU | 1568 | 1.301 | 1 | 1.301 | 1
324 | Classroom | 282 | 18 |  | 611 | 13 | 13 | AHU | 4888 | 3.4615 | 1 | 3.4615 | 1
325 | Classroom | 326 | 21 |  | 703 | 15 | 15 | AHU | 5624 | 3.478 | 1 | 3.478 | 1
326 | Classroom | 280 | 18 |  | 681 | 15 | 15 | AHU | 5448 | 3.0837 | 1 | 3.0837 | 1
327 | Classroom | 310 | 20 |  | 702 | 15 | 15 | AHU | 5616 | 3.312 | 1 | 3.312 | 1
328 | Office | 135 | 9 |  | 334 | 7 | 7 | AHU | 2672 | 3.0314 | 1 | 3.0314 | 1
328A and B | Office | 229 | 15 |  | 391 | 8 | 8 | AHU | 3128 | 4.3926 | 2 | 4.3926 | 2
329 | Classroom | 310 | 20 |  | 573 | 13 | 13 | AHU | 4584 | 4.0576 | 2 | 4.0576 | 2
330 | Classroom | 330 | 22 |  | 573 | 13 | 13 | AHU | 4584 | 4.3194 | 2 | 4.3194 | 2
331 | Classroom | 425 | 28 |  | 708 | 16 | 16 | AHU | 5664 | 4.5021 | 2 | 4.5021 | 2
333 | Classroom | 304 | 20 |  | 697 | 15 | 15 | AHU | 5576 | 3.2712 | 1 | 3.2712 | 1
334 | Classroom | 296 | 19 |  | 631 | 14 | 14 | AHU | 5048 | 3.5182 | 1 | 3.5182 | 1
335 | Classroom | 280 | 18 |  | 614 | 13 | 13 | AHU | 4912 | 3.4202 | 1 | 3.4202 | 1
336 | Classroom | 282 | 18 |  | 632 | 14 | 14 | AHU | 5056 | 3.3465 | 1 | 3.3465 | 1
338 | Classroom | 283 | 18 |  | 678 | 15 | 15 | AHU | 5424 | 3.1305 | 1 | 3.1305 | 1
339 | Office | 47 | 3 |  | 322 | 7 | 3 | AHU | 2576 | 1.0947 | 1 | 1.0947 | 1
340 | Classroom | 281 | 18 |  | 931 | 21 | 18 | AHU | 7448 | 2.2637 | 1 | 2.2637 | 1
341A | Classroom | 300 | 20 |  | 834 | 18 | 18 | AHU | 6672 | 2.6978 | 1 | 2.6978 | 1
341B | Classroom | 122 | 8 |  | 262 | 5 | 5 | AHU | 2096 | 3.4924 | 1 | 3.4924 | 1
342 | Classroom | 332 | 22 |  | 587 | 13 | 13 | AHU | 4696 | 4.2419 | 2 | 4.2419 | 2
344 | Classroom | 311 | 20 |  | 820 | 18 | 18 | AHU | 6560 | 2.8445 | 1 | 2.8445 | 1
345 | Classroom | 290 | 19 |  | 1154 | 26 | 19 | AHU | 9232 | 1.8847 | 1 | 1.8847 | 1
- | Main office Rear reception desk | 79 | 5 |  | 429 | 9 | 5 | AHU | 3432 | 1.3811 | 1 | 1.3811 | 1
- | Main office | 221 | 14 |  | 1109 | 25 | 14 | AHU | 8872 | 1.4946 | 1 | 1.4946 | 1
- | Student Store | 236 | 15 |  | 339 | 7 | 7 | AHU | 2712 | 5.2212 | 2 | 5.2212 | 2
- | Teaching Kitchen | 2167 | 144 |  | 2843 | 64 | 64 | AHU | 22744 | 5.7167 | 2 | 5.7167 | 2
- | Cafeteria | 0 | 0 |  | 8970 | 203 | 0 | AHU | 71760 | 0 | 0 | 0 | 0
- | Teaching Kitchen | 2480 | 165 |  | 1316 | 29 | 29 | AHU | 10528 | 14.1337 | 3 | 14.1337 | 3
- | Kitchen | 1030 | 68 |  | 1361 | 30 | 30 | AHU | 10888 | 5.676 | 2 | 5.676 | 2
- | Kitchen Hood | 3846 | 256 |  | N/A | 0 | 0 | AHU |  | unk | unk | unk | unk
- | Auditorium | 6454 | 430 |  | 5600 | 127 | 127 | AHU | 44800 | 8.6438 | 2 | 8.6438 | 2
- | 1st Floor NE | 176 | 11 |  | 20126 | 457 | 11 | AHU | 161008 | 0.065587 | 0 | 0.065587 | 0
- | Heavy Equipment | 2723 | 181 |  | 3189 | 72 | 72 | AHU | 25512 | 6.404 | 2 | 6.404 | 2
- | Autobody | 4337 | 289 |  | 444 | 10 | 10 | AHU | 3552 | 73.2601 | 5 | 73.2601 | 5
- | Welding | 1296 | 86 |  | 520 | 11 | 11 | AHU | 4160 | 18.6923 | 3 | 18.6923 | 3
- | Sheet Metal | 3436 | 229 |  | 514 | 11 | 11 | AHU | 4112 | 50.1362 | 5 | 50.1362 | 5
- | Warehouse Classroom | 8094 | 539 |  | 533 | 12 | 12 | AHU | 4264 | 113.8931 | 5 | 113.8931 | 5
- | Gym | 7088 | 472 |  | 15450 | 351 | 351 | AHU | 123600 | 3.4408 | 1 | 3.4408 | 1
- | Factory Lab | 3833 | 255 |  | 417 | 9 | 9 | AHU | 3336 | 68.9388 | 5 | 68.9388 | 5
- | 1st Floor | 210 | 14 |  | 2760 | 62 | 14 | AHU | 22080 | 0.57065 | 0 | 0.57065 | 0
- | Vending Machine Repair | 317 | 21 |  | 3167 | 71 | 21 | AHU | 25336 | 0.75071 | 0 | 0.75071 | 0
- | Boiler Room | 3303 | 220 |  | 4914 | 111 | 111 | AHU | 39312 | 5.0412 | 2 | 5.0412 | 2
- | Maint. Break room | 153 | 10 |  | 461 | 10 | 10 | AHU | 3688 | 2.4892 | 1 | 2.4892 | 1
- | Eng. Office | 128 | 8 |  | 187 | 4 | 4 | AHU | 1496 | 5.1337 | 2 | 5.1337 | 2
- | Weight Room | 990 | 66 |  | 939 | 21 | 21 | AHU | 7512 | 7.9073 | 2 | 7.9073 | 2
- | Offices | 3928 | 261 |  | 90 | 2 | 2 | AHU | 720 | 327.3333 | 6 | 327.3333 | 6
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-21 | [8 empty] | unk | unk | unk | unk
School: | Franklin S. Edmonds Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B1 | Classroom | 0 | 0 | Yes | 400 | 9 | 9 | Unit Ventilator | 3200 | 0 | 0 | 20 | 3
B2 | Kitchen | 75 | 5 |  | 572 | 13 | 5 | Unit Ventilator | 4576 | 0.98339 | 0 | 0.98339 | 0
B3 | Kitchen | 165 | 11 |  | 480 | 10 | 10 | Unit Ventilator | 3840 | 2.5781 | 1 | 2.5781 | 1
H2 | Office |  | 0 | Yes | 178 | 4 | 4 |  | 1424 | unk | unk | 20 | 3
101 | Classroom | 165 | 11 | Yes | 1128 | 25 | 25 | Unit Ventilator | 9024 | 1.0971 | 1 | 21.0971 | 3
102 | Classroom | 441 | 29 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.1321 | 1 | 3.1321 | 1
103 | Classroom | 397 | 26 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.4462 | 1 | 3.4462 | 1
104 | Classroom | 455 | 30 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.2315 | 1 | 3.2315 | 1
105 | Classroom | 412 | 27 |  | 1128 | 25 | 25 | Unit Ventilator | 9024 | 2.7394 | 1 | 2.7394 | 1
106 | Classroom | 460 | 30 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.267 | 1 | 3.267 | 1
107 | Classroom | 256 | 17 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 2.6667 | 1 | 2.6667 | 1
108 | Classroom | 567 | 37 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 4.027 | 2 | 4.027 | 2
109 | Classroom | 527 | 35 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.7429 | 1 | 3.7429 | 1
110 | Classroom | 431 | 28 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.0611 | 1 | 3.0611 | 1
111 | Classroom | 634 | 42 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 4.7173 | 2 | 4.7173 | 2
112A | Office |  | 0 | Yes | 364 | 8 | 8 | Not supplied | 2912 | unk | unk | 20 | 3
112B | Office |  | 0 | Yes | 210 | 4 | 4 |  | 1680 | unk | unk | 20 | 3
113 | Classroom | 662 | 44 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 4.9256 | 2 | 4.9256 | 2
114 | Office |  | 0 | Yes | 364 | 8 | 8 | Unit Ventilator | 2912 | unk | unk | 20 | 3
115 | Classroom | 551 | 36 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 4.0997 | 2 | 4.0997 | 2
115A | Office |  | 0 | Yes | 252 | 5 | 5 |  | 2016 | unk | unk | 20 | 3
116 | Classroom | 169 | 11 | Yes | 736 | 16 | 16 | Unit Ventilator | 5888 | 1.7221 | 1 | 21.7221 | 3
117 | Classroom | 299 | 19 |  | 912 | 20 | 19 | Unit Ventilator | 7296 | 2.4589 | 1 | 2.4589 | 1
118 | Classroom | 281 | 18 |  | 912 | 20 | 18 | Unit Ventilator | 7296 | 2.3109 | 1 | 2.3109 | 1
118A | Office |  | 0 |  | 175 | 3 | 0 |  | 1400 | unk | unk | unk | unk
119 | Classroom | 282 | 18 |  | 912 | 20 | 18 | Unit Ventilator | 7296 | 2.3191 | 1 | 2.3191 | 1
120 | Classroom | 0 | 0 | Yes | 912 | 20 | 20 | Unit Ventilator | 7296 | 0 | 0 | 20 | 3
121 | Classroom | 0 | 0 | Yes | 912 | 20 | 20 | Unit Ventilator | 7296 | 0 | 0 | 20 | 3
122 | Classroom | 340 | 22 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 2.7961 | 1 | 2.7961 | 1
201 | Classroom | 503 | 33 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.5724 | 1 | 3.5724 | 1
202 | Classroom | 418 | 27 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.9688 | 1 | 2.9688 | 1
203 | Classroom | 415 | 27 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.9474 | 1 | 2.9474 | 1
204 | Classroom | 395 | 26 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.8054 | 1 | 2.8054 | 1
205 | Classroom | 491 | 32 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.4872 | 1 | 3.4872 | 1
206 | Classroom | 414 | 27 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.9403 | 1 | 2.9403 | 1
207 | Classroom | 485 | 32 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.4446 | 1 | 3.4446 | 1
208 | Classroom | 348 | 23 |  | 1056 | 24 | 23 | Unit Ventilator | 8448 | 2.4716 | 1 | 2.4716 | 1
209 | Classroom | 431 | 28 |  | 1056 | 24 | 24 | Unit Ventilator | 8448 | 3.0611 | 1 | 3.0611 | 1
210 | Classroom | 304 | 20 |  | 1056 | 24 | 20 | Unit Ventilator | 8448 | 2.1591 | 1 | 2.1591 | 1
211 | Classroom | 322 | 21 |  | 1056 | 24 | 21 | Unit Ventilator | 8448 | 2.2869 | 1 | 2.2869 | 1
212 | Classroom | 31 | 2 | Yes | 1056 | 24 | 24 | Unit Ventilator | 8448 | 0.22017 | 0 | 20.2202 | 3
213 | Classroom | 186 | 12 |  | 1008 | 22 | 12 | Unit Ventilator | 8064 | 1.3839 | 1 | 1.3839 | 1
215 | Classroom | 509 | 33 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 3.7872 | 1 | 3.7872 | 1
216 | Library | 969 | 64 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 7.2098 | 2 | 7.2098 | 2
217 | Classroom | 503 | 33 |  | 1008 | 22 | 22 | Unit Ventilator | 8064 | 3.7426 | 1 | 3.7426 | 1
217-A | VP office |  | 0 | Yes | 252 | 5 | 5 | Convector | 2016 | unk | unk | 20 | 3
218 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0 | 20 | 3
219 | Classroom | 44 | 2 |  | 1008 | 22 | 2 | Unit Ventilator | 8064 | 0.32738 | 0 | 0.32738 | 0
- | Auditorium | 1860 | 124 |  | 1849 | 42 | 42 | AHU | 14792 | 7.5446 | 2 | 7.5446 | 2
- | Gym | 1195 | 79 |  | 2795 | 63 | 63 | AHU | 22360 | 3.2066 | 1 | 3.2066 | 1
- | Lunch | 0 | 0 |  | 780 | 17 | 0 | Unit Ventilator | 6240 | 0 | 0 | 0 | 0
- | Cafeteria | 411 | 27 | Yes | 1560 | 35 | 35 | Unit Ventilator | 12480 | 1.976 | 1 | 21.976 | 3
- | Kitchen | 0 | 0 | Yes | 400 | 9 | 9 | Unit Ventilator | 3200 | 0 | 0 | 20 | 3
| Women Helper |  | 0 | Yes | 262 | 5 | 5 |  | 2096 | unk | unk | 20 | 3
- | Nurse | 0 | 0 | Yes | 280 | 6 | 6 | N/A | 2240 | 0 | 0 | 20 | 3
- | Prin. Office | 0 | 0 | Yes | 322 | 7 | 7 | Convector | 2576 | 0 | 0 | 20 | 3
- | Main Office | 0 | 0 | Yes | 650 | 14 | 14 | Convector | 5200 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | Lewis Elkin Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Part 1 | Devine Part 2 | Devine Part 3 | [6 empty] | unk | unk | unk | unk
School: | Elkin Little School House | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Main Building | [9 empty] | unk | unk | unk | unk
101 | Classroom | 391 | 26 |  | 420 | 9 | 9 | Unit Ventilator | 3360 | 6.9821 | 2 | 6.9821 | 2
102 | Classroom | 0 | 0 | Yes | 1136 | 25 | 25 | Unit Ventilator | 9088 | 0 | 0 | 20 | 3
103 | Classroom | 299 | 19 | Yes | 1303 | 29 | 29 | Unit Ventilator | 10424 | 1.721 | 1 | 21.721 | 3
104 | Classroom | 293 | 19 |  | 1201 | 27 | 19 | Unit Ventilator | 9608 | 1.8297 | 1 | 1.8297 | 1
105 | Classroom | 301 | 20 | Yes | 1269 | 28 | 28 | Unit Ventilator | 10152 | 1.779 | 1 | 21.779 | 3
106 | Classroom | 300 | 20 |  | 418 | 9 | 9 | Unit Ventilator | 3344 | 5.3828 | 2 | 5.3828 | 2
107 | Classroom | 411 | 27 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 3.4365 | 1 | 3.4365 | 1
108 | Classroom | 386 | 25 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 3.2274 | 1 | 3.2274 | 1
109 | Classroom | 389 | 25 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 3.2525 | 1 | 3.2525 | 1
110 | Classroom | 376 | 25 |  | 821 | 18 | 18 | Unit Ventilator | 6568 | 3.4348 | 1 | 3.4348 | 1
111 | Classroom | 313 | 20 |  | 938 | 21 | 20 | Unit Ventilator | 7504 | 2.5027 | 1 | 2.5027 | 1
112 | Classroom | 363 | 24 |  | 898 | 20 | 20 | Unit Ventilator | 7184 | 3.0317 | 1 | 3.0317 | 1
113 | Classroom | 318 | 21 |  | 898 | 20 | 20 | Unit Ventilator | 7184 | 2.6559 | 1 | 2.6559 | 1
114 | Classroom | 349 | 23 |  | 898 | 20 | 20 | Unit Ventilator | 7184 | 2.9148 | 1 | 2.9148 | 1
115 | Classroom | 345 | 23 |  | 1024 | 23 | 23 | Unit Ventilator | 8192 | 2.5269 | 1 | 2.5269 | 1
116 | Lounge | 133 | 8 |  | 309 | 7 | 7 | Unit Ventilator | 2472 | 3.2282 | 1 | 3.2282 | 1
117 | Classroom | 129 | 8 |  | 215 | 4 | 4 | Unit Ventilator | 1720 | 4.5 | 2 | 4.5 | 2
117 | Office | 96 | 6 |  | 317 | 7 | 6 | Unit Ventilator | 2536 | 2.2713 | 1 | 2.2713 | 1
117A | Classroom Vestibule | 171 | 11 |  | 102 | 2 | 2 | Unit Ventilator | 816 | 12.5735 | 3 | 12.5735 | 3
118 | Office | 109 | 7 |  | 122 | 2 | 2 | Unit Ventilator | 976 | 6.7008 | 2 | 6.7008 | 2
119 | Office | 105 | 7 |  | 117 | 2 | 2 | Unit Ventilator | 936 | 6.7308 | 2 | 6.7308 | 2
120 | Security Office | 214 | 14 |  | 259 | 5 | 5 | Unit Ventilator | 2072 | 6.1969 | 2 | 6.1969 | 2
121 | Office |  | 0 | Yes | 400 | 9 | 9 |  | 3200 | unk | unk | 20 | 3
201 | Classroom | 496 | 33 |  | 772 | 17 | 17 | Unit Ventilator | 6176 | 4.8187 | 2 | 4.8187 | 2
202 | Classroom | 325 | 21 |  | 933 | 21 | 21 | Unit Ventilator | 7464 | 2.6125 | 1 | 2.6125 | 1
203 | Classroom | 385 | 25 |  | 838 | 19 | 19 | Unit Ventilator | 6704 | 3.4457 | 1 | 3.4457 | 1
204 | Classroom | 360 | 24 |  | 756 | 17 | 17 | Unit Ventilator | 6048 | 3.5714 | 1 | 3.5714 | 1
204A | Office | 178 | 11 |  | 201 | 4 | 4 | Unit Ventilator | 1608 | 6.6418 | 2 | 6.6418 | 2
205 | Classroom | 334 | 22 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 3.0736 | 1 | 3.0736 | 1
206 | Classroom | 402 | 26 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 3.6994 | 1 | 3.6994 | 1
207 | Classroom | 357 | 23 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 3.2853 | 1 | 3.2853 | 1
207A | Office | 74 | 4 |  | 201 | 4 | 4 | Unit Ventilator | 1608 | 2.7612 | 1 | 2.7612 | 1
208 | Classroom | 388 | 25 |  | 762 | 17 | 17 | Unit Ventilator | 6096 | 3.8189 | 1 | 3.8189 | 1
209 | Classroom | 365 | 24 |  | 811 | 18 | 18 | Unit Ventilator | 6488 | 3.3755 | 1 | 3.3755 | 1
210 | Classroom | 285 | 19 |  | 814 | 18 | 18 | Unit Ventilator | 6512 | 2.6259 | 1 | 2.6259 | 1
211 | Classroom | 430 | 28 |  | 746 | 16 | 16 | Unit Ventilator | 5968 | 4.3231 | 2 | 4.3231 | 2
211A | Office | 161 | 10 |  | 201 | 4 | 4 | Unit Ventilator | 1608 | 6.0075 | 2 | 6.0075 | 2
212 | Classroom | 312 | 20 |  | 810 | 18 | 18 | Unit Ventilator | 6480 | 2.8889 | 1 | 2.8889 | 1
213 | Classroom | 358 | 23 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 3.2945 | 1 | 3.2945 | 1
214 | Classroom | 376 | 25 |  | 786 | 17 | 17 | Unit Ventilator | 6288 | 3.5878 | 1 | 3.5878 | 1
215 | Classroom | 0 | 0 | Yes | 863 | 19 | 19 | Unit Ventilator | 6904 | 0 | 0 | 20 | 3
215A | Classroom | 131 | 8 |  | 201 | 4 | 4 | Unit Ventilator | 1608 | 4.8881 | 2 | 4.8881 | 2
216 | Classroom | 395 | 26 |  | 855 | 19 | 19 | Unit Ventilator | 6840 | 3.4649 | 1 | 3.4649 | 1
217 | Classroom | 493 | 32 |  | 1259 | 28 | 28 | Unit Ventilator | 10072 | 2.9369 | 1 | 2.9369 | 1
218 | Classroom | 437 | 29 |  | 788 | 17 | 17 | Unit Ventilator | 6304 | 4.1593 | 2 | 4.1593 | 2
219 | Classroom | 76 | 5 |  | 117 | 2 | 2 | Unit Ventilator | 936 | 4.8718 | 2 | 4.8718 | 2
220 | Library | 1770 | 118 |  | 2982 | 67 | 67 | Unit Ventilator | 23856 | 4.4517 | 2 | 4.4517 | 2
220A | Office | 214 | 14 |  | 373 | 8 | 8 | Unit Ventilator | 2984 | 4.3029 | 2 | 4.3029 | 2
220B | Office | 0 | 0 |  | 421 | 9 | 0 | N/A | 3368 | 0 | 0 | 0 | 0
220C | Office | 0 | 0 |  | 398 | 9 | 0 | N/A | 3184 | 0 | 0 | 0 | 0
221 | Room | 0 | 0 |  | 141 | 3 | 0 | Unit Ventilator | 1128 | 0 | 0 | 0 | 0
B01 | Classroom | 360 | 24 |  | 1859 | 42 | 24 | Unit Ventilator | 14872 | 1.4524 | 1 | 1.4524 | 1
B02 | Classroom | 364 | 24 |  | 928 | 21 | 21 | Unit Ventilator | 7424 | 2.9418 | 1 | 2.9418 | 1
B03 | Classroom | 183 | 12 |  | 525 | 11 | 11 | Unit Ventilator | 4200 | 2.6143 | 1 | 2.6143 | 1
B04 | Classroom | 300 | 20 |  | 613 | 13 | 13 | Unit Ventilator | 4904 | 3.6705 | 1 | 3.6705 | 1
- | Assistant Principal's Office | 40 | 2 |  | 98 | 2 | 2 | Unit Ventilator | 784 | 3.0612 | 1 | 3.0612 | 1
- | Auditorium | 0 | 0 |  | 7138 | 162 | 0 | Unit Ventilator | 57104 | 0 | 0 | 0 | 0
- | Main Office Conference Room | 0 | 0 |  | 181 | 4 | 0 | Unit Ventilator | 1448 | 0 | 0 | 0 | 0
- | Copy room | 34 | 2 |  | 179 | 4 | 2 | Unit Ventilator | 1432 | 1.4246 | 1 | 1.4246 | 1
- | Parent Resources Office | 0 | 0 |  | 84 | 1 | 0 | Unit Ventilator | 672 | 0 | 0 | 0 | 0
- | Education Office | 57 | 3 |  | 207 | 4 | 3 | Unit Ventilator | 1656 | 2.0652 | 1 | 2.0652 | 1
- | Gymnasium | 3457 | 230 |  | 4778 | 108 | 108 | Unit Ventilator | 38224 | 5.4264 | 2 | 5.4264 | 2
- | Ms. Potts' Office | 46 | 3 |  | 133 | 3 | 3 | Unit Ventilator | 1064 | 2.594 | 1 | 2.594 | 1
- | Health Office/Nurses Area/Nurse's Suite | 480 | 32 |  | 637 | 14 | 14 | Unit Ventilator | 5096 | 5.6515 | 2 | 5.6515 | 2
- | Cafeteria/Lunchroom | 1731 | 115 |  | 2558 | 58 | 58 | Unit Ventilator | 20464 | 5.0753 | 2 | 5.0753 | 2
- | Principal's Office | 34 | 2 |  | 167 | 3 | 2 | Unit Ventilator | 1336 | 1.5269 | 1 | 1.5269 | 1
- | Main Office | 235 | 15 | Yes | 674 | 15 | 15 | Unit Ventilator | 5392 | 2.615 | 1 | 22.615 | 3
- | Teacher's Lounge | 0 | 0 |  | 623 | 14 | 0 | Unit Ventilator | 4984 | 0 | 0 | 0 | 0
- | Library (Wall mount unit, south area) | 33 | 2 |  | 2775 | 63 | 2 | Unit Ventilator | 22200 | 0.089189 | 0 | 0.089189 | 0
LSH Building | [9 empty] | unk | unk | unk | unk
1 | Classroom | 829 | 55 |  | 1018 | 23 | 23 | AHU | 8144 | 6.1076 | 2 | 6.1076 | 2
2 | Classroom | 619 | 41 |  | 1018 | 23 | 23 | AHU | 8144 | 4.5604 | 2 | 4.5604 | 2
3 | Classroom | 651 | 43 |  | 1018 | 23 | 23 | AHU | 8144 | 4.7962 | 2 | 4.7962 | 2
4 | Classroom | 486 | 32 |  | 1018 | 23 | 23 | AHU | 8144 | 3.5806 | 1 | 3.5806 | 1
5 | Classroom | 410 | 27 |  | 1018 | 23 | 23 | AHU | 8144 | 3.0206 | 1 | 3.0206 | 1
6 | Classroom | 586 | 39 |  | 1018 | 23 | 23 | AHU | 8144 | 4.3173 | 2 | 4.3173 | 2
7 | Classroom | 379 | 25 |  | 1018 | 23 | 23 | AHU | 8144 | 2.7922 | 1 | 2.7922 | 1
8 | Classroom | 519 | 34 |  | 1018 | 23 | 23 | AHU | 8144 | 3.8237 | 1 | 3.8237 | 1
- | Main Office | 0 | 0 |  | 295 | 6 | 0 | AHU | 2360 | 0 | 0 | 0 | 0
- | Multi Purpose Room | 1105 | 73 |  | 1995 | 45 | 45 | AHU | 15960 | 4.1541 | 2 | 4.1541 | 2
- | Teacher's Lounge | 0 | 0 |  | 220 | 5 | 0 | AHU | 1760 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-12 | [8 empty] | unk | unk | unk | unk
School: | Ellwood Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | Exhaust | Retest | [6 empty] | unk | unk | unk | unk
| Devine 2nd Retest | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | 100 | 13 | 0 | Yes | 1465 | 33 | 33 | Unit Ventilator | 11720 | 0.066553 | 0 | 20.0666 | 3
100 A | Counselor Office |  | 0 | Yes | 297 | 6 | 6 |  | 2376 | unk | unk | 20 | 3
100 B-C | Nurse |  | 0 | Yes | 342 | 7 | 7 |  | 2736 | unk | unk | 20 | 3
100 E | Main Office |  | 0 | Yes | 416 | 9 | 9 |  | 3328 | unk | unk | 20 | 3
102 | 102 | 414 | 27 |  | 574 | 13 | 13 | Unit Ventilator | 4592 | 5.4094 | 2 | 5.4094 | 2
102 C | Principal |  | 0 | Yes | 400 | 9 | 9 |  | 3200 | unk | unk | 20 | 3
103 | 103 | 328 | 21 |  | 582 | 13 | 13 | Unit Ventilator | 4656 | 4.2268 | 2 | 4.2268 | 2
104 | 104 | 392 | 26 |  | 701 | 15 | 15 | Unit Ventilator | 5608 | 4.194 | 2 | 4.194 | 2
105 | 105 | 457 | 30 |  | 1158 | 26 | 26 | Unit Ventilator | 9264 | 2.9598 | 1 | 2.9598 | 1
107 | 107 | 420 | 28 |  | 905 | 20 | 20 | Unit Ventilator | 7240 | 3.4807 | 1 | 3.4807 | 1
108 | 108 | 443 | 29 |  | 906 | 20 | 20 | Unit Ventilator | 7248 | 3.6672 | 1 | 3.6672 | 1
109 | 109 | 468 | 31 |  | 904 | 20 | 20 | Unit Ventilator | 7232 | 3.8827 | 1 | 3.8827 | 1
110 | 110 | 372 | 24 |  | 916 | 20 | 20 | Unit Ventilator | 7328 | 3.0459 | 1 | 3.0459 | 1
111 | 111 | 260 | 17 |  | 448 | 10 | 10 | Unit Ventilator | 3584 | 4.3527 | 2 | 4.3527 | 2
201 | 201 | 520 | 34 |  | 940 | 21 | 21 | Unit Ventilator | 7520 | 4.1489 | 2 | 4.1489 | 2
202 | 202 | 195 | 13 |  | 912 | 20 | 13 | Unit Ventilator | 7296 | 1.6036 | 1 | 1.6036 | 1
203 | 203 | 640 | 42 |  | 903 | 20 | 20 | Unit Ventilator | 7224 | 5.3156 | 2 | 5.3156 | 2
204 | 204 | 430 | 28 |  | 914 | 20 | 20 | Unit Ventilator | 7312 | 3.5284 | 1 | 3.5284 | 1
206 | 206 | 409 | 27 |  | 860 | 19 | 19 | Unit Ventilator | 6880 | 3.5669 | 1 | 3.5669 | 1
207 | 207 | 423 | 28 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 3.4786 | 1 | 3.4786 | 1
208 | 208 | 417 | 27 |  | 904 | 20 | 20 | Unit Ventilator | 7232 | 3.4596 | 1 | 3.4596 | 1
210 | 210 | 154 | 10 |  | 903 | 20 | 10 | Unit Ventilator | 7224 | 1.2791 | 1 | 1.2791 | 1
211 | 211 | 511 | 34 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 4.2023 | 2 | 4.2023 | 2
212 | 212 | 534 | 35 |  | 975 | 22 | 22 | Unit Ventilator | 7800 | 4.1077 | 2 | 4.1077 | 2
- | Auditorium | 0 | 0 |  | 2900 | 65 | 0 | AHU | 23200 | 0 | 0 | 0 | 0
- | Gym | 2115 | 141 |  | 3922 | 89 | 89 | AHU | 31376 | 4.0445 | 2 | 4.0445 | 2
- | Library | 0 | 0 | Yes | 2809 | 63 | 63 | AHU | 22472 | 0 | 0 | 20 | 3
- | Floor 1 East Corridor | 0 | 0 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
- | Floor 1 East Corridor | 0 | 0 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-17 | [8 empty] | unk | unk | unk | unk
School: | Philadelphia Military Academy At Elverson | [8 empty] | unk | unk | unk | unk
Vendor: | Meehan | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
103 | Conference room | 788 | 52 |  | 690 | 15 | 15 |  | 5520 | 8.5652 | 2 | 8.5652 | 2
104 | IMC | 973 | 64 |  | 690 | 15 | 15 |  | 5520 | 10.5761 | 3 | 10.5761 | 3
105 | Conference room | 354 | 23 |  | 690 | 15 | 15 |  | 5520 | 3.8478 | 1 | 3.8478 | 1
106 | Weight room | 871 | 58 |  | 943 | 21 | 21 |  | 7544 | 6.9274 | 2 | 6.9274 | 2
107 | Classroom | 1423 | 94 |  | 690 | 15 | 15 |  | 5520 | 15.4674 | 3 | 15.4674 | 3
108 | Classroom | 787 | 52 |  | 690 | 15 | 15 |  | 5520 | 8.5543 | 2 | 8.5543 | 2
111 | Classroom | 625 | 41 |  | 736 | 16 | 16 |  | 5888 | 6.3689 | 2 | 6.3689 | 2
112 | Classroom | 112 | 7 |  | 736 | 16 | 7 |  | 5888 | 1.1413 | 1 | 1.1413 | 1
113 | Classroom | 728 | 48 |  | 736 | 16 | 16 |  | 5888 | 7.4185 | 2 | 7.4185 | 2
114 | Classroom | 525 | 35 |  | 1180 | 26 | 26 |  | 9440 | 3.3369 | 1 | 3.3369 | 1
201 | Classroom | 1325 | 88 |  | 690 | 15 | 15 |  | 5520 | 14.4022 | 3 | 14.4022 | 3
202 | Classroom | 180 | 12 |  | 690 | 15 | 12 |  | 5520 | 1.9565 | 1 | 1.9565 | 1
203 | Classroom | 428 | 28 |  | 690 | 15 | 15 |  | 5520 | 4.6522 | 2 | 4.6522 | 2
204 | Classroom | 487 | 32 |  | 690 | 15 | 15 |  | 5520 | 5.2935 | 2 | 5.2935 | 2
205 | Classroom | 73 | 4 |  | 805 | 18 | 4 |  | 6440 | 0.68012 | 0 | 0.68012 | 0
206 | Classroom | 796 | 53 |  | 943 | 21 | 21 |  | 7544 | 6.3309 | 2 | 6.3309 | 2
207 | Classroom | 63 | 4 |  | 690 | 15 | 4 |  | 5520 | 0.68478 | 0 | 0.68478 | 0
208 | Classroom | 445 | 29 |  | 690 | 15 | 15 |  | 5520 | 4.837 | 2 | 4.837 | 2
211 | Classroom | 0 | 0 |  | 736 | 16 | 0 |  | 5888 | 0 | 0 | 0 | 0
212 | Classroom | 0 | 0 |  | 736 | 16 | 0 |  | 5888 | 0 | 0 | 0 | 0
213 | Classroom | 670 | 44 |  | 736 | 16 | 16 |  | 5888 | 6.8274 | 2 | 6.8274 | 2
214 | Classroom | 0 | 0 |  | 736 | 16 | 0 |  | 5888 | 0 | 0 | 0 | 0
215 | Classroom | 745 | 49 |  | 736 | 16 | 16 |  | 5888 | 7.5917 | 2 | 7.5917 | 2
301 | Classroom | 142 | 9 |  | 690 | 15 | 9 |  | 5520 | 1.5435 | 1 | 1.5435 | 1
302 | Classroom | 447 | 29 |  | 690 | 15 | 15 |  | 5520 | 4.8587 | 2 | 4.8587 | 2
303 | Classroom | 117 | 7 |  | 690 | 15 | 7 |  | 5520 | 1.2717 | 1 | 1.2717 | 1
304 | Classroom | 147 | 9 |  | 690 | 15 | 9 |  | 5520 | 1.5978 | 1 | 1.5978 | 1
305 | Classroom | 120 | 8 |  | 805 | 18 | 8 |  | 6440 | 1.118 | 1 | 1.118 | 1
306 | Classroom | 796 | 53 |  | 1048 | 23 | 23 |  | 8384 | 5.6966 | 2 | 5.6966 | 2
307 | Classroom | 370 | 24 |  | 690 | 15 | 15 |  | 5520 | 4.0217 | 2 | 4.0217 | 2
308 | Classroom | 477 | 31 |  | 690 | 15 | 15 |  | 5520 | 5.1848 | 2 | 5.1848 | 2
309 | Classroom | 115 | 7 |  | 690 | 15 | 7 |  | 5520 | 1.25 | 1 | 1.25 | 1
311 | Classroom | 572 | 38 |  | 736 | 16 | 16 |  | 5888 | 5.8288 | 2 | 5.8288 | 2
312 | Classroom | 0 | 0 |  | 736 | 16 | 0 |  | 5888 | 0 | 0 | 0 | 0
313 | Classroom | 697 | 46 |  | 736 | 16 | 16 |  | 5888 | 7.1026 | 2 | 7.1026 | 2
314 | Classroom | 0 | 0 |  | 736 | 16 | 0 |  | 5888 | 0 | 0 | 0 | 0
315 | Classroom | 0 | 0 |  | 736 | 16 | 0 |  | 5888 | 0 | 0 | 0 | 0
- | Cafeteria / Kitchen | 970 | 64 |  | 2595 | 58 | 58 |  | 20760 | 2.8035 | 1 | 2.8035 | 1
- | Hallway | 462 | 30 |  | 1400 | 31 | 30 |  | 11200 | 2.475 | 1 | 2.475 | 1
- | Hallway | 0 | 0 |  | 1400 | 31 | 0 |  | 11200 | 0 | 0 | 0 | 0
- | Hallway | 432 | 28 |  | 1400 | 31 | 28 |  | 11200 | 2.3143 | 1 | 2.3143 | 1
- | main office | 1050 | 70 |  | 744 | 16 | 16 |  | 5952 | 10.5847 | 3 | 10.5847 | 3
- | Office / storage | 735 | 49 |  | 720 | 16 | 16 |  | 5760 | 7.6562 | 2 | 7.6562 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-21 | [8 empty] | unk | unk | unk | unk
School: | Eleanor Emlen Elementary School | House fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Part 2 | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B001 | Classroom | 736 | 49 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 7.5 | 2 | 7.5 | 2
B002 | Classroom | 0 | 0 | Yes | 1848 | 42 | 42 | Unit Ventilator | 14784 | 0 | 0 | 20 | 3
B003 | Classroom | 994 | 66 |  | 1032 | 23 | 23 | Unit Ventilator | 8256 | 7.2238 | 2 | 7.2238 | 2
B004A | Classroom | 701 | 46 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 6.8457 | 2 | 6.8457 | 2
B004B | Classroom | 360 | 24 |  | 816 | 18 | 18 | Unit Ventilator | 6528 | 3.3088 | 1 | 3.3088 | 1
B005 | Classroom | 419 | 27 |  | 546 | 12 | 12 | Unit Ventilator | 4368 | 5.7555 | 2 | 5.7555 | 2
101 | Classroom | 857 | 57 |  | 768 | 17 | 17 | House Fan | 6144 | 8.3691 | 2 | 8.3691 | 2
102 | Classroom | 267 | 17 |  | 690 | 15 | 15 | House Fan | 5520 | 2.9022 | 1 | 2.9022 | 1
103 | Classroom | 517 | 34 |  | 690 | 15 | 15 | House Fan | 5520 | 5.6196 | 2 | 5.6196 | 2
104 | Office | 193 | 12 |  | 88 | 2 | 2 | House Fan | 704 | 16.4489 | 3 | 16.4489 | 3
104D | Waiting Room | 255 | 17 |  | 90 | 2 | 2 | House Fan | 720 | 21.25 | 3 | 21.25 | 3
104D | Office | 199 | 13 |  | 396 | 9 | 9 | House Fan | 3168 | 3.7689 | 1 | 3.7689 | 1
104D | Storage | 136 | 9 |  | 207 | 4 | 4 | House Fan | 1656 | 4.9275 | 2 | 4.9275 | 2
104D | Nurse | 173 | 11 |  | 144 | 3 | 3 | House Fan | 1152 | 9.0104 | 2 | 9.0104 | 2
105 | Waiting Room | 174 | 11 |  | 248 | 5 | 5 | House Fan | 1984 | 5.2621 | 2 | 5.2621 | 2
105A | Office | 93 | 6 |  | 182 | 4 | 4 | House Fan | 1456 | 3.8324 | 1 | 3.8324 | 1
105B | Office | 85 | 5 |  | 126 | 2 | 2 | House Fan | 1008 | 5.0595 | 2 | 5.0595 | 2
105C | Office | 103 | 6 |  | 126 | 2 | 2 | House Fan | 1008 | 6.131 | 2 | 6.131 | 2
106 | Classroom | 378 | 25 |  | 690 | 15 | 15 | House Fan | 5520 | 4.1087 | 2 | 4.1087 | 2
107 | Classroom | 289 | 19 |  | 792 | 18 | 18 | House Fan | 6336 | 2.7367 | 1 | 2.7367 | 1
108 | Classroom | 643 | 42 |  | 690 | 15 | 15 | House Fan | 5520 | 6.9891 | 2 | 6.9891 | 2
109 | Classroom | 782 | 52 |  | 1050 | 23 | 23 | House Fan | 8400 | 5.5857 | 2 | 5.5857 | 2
110 | Classroom | 485 | 32 |  | 621 | 14 | 14 | House Fan | 4968 | 5.8575 | 2 | 5.8575 | 2
200 | Classroom | 0 | 0 | Yes | 528 | 12 | 12 | House Fan | 4224 | 0 | 0 | 20 | 3
201 | Classroom | 531 | 35 |  | 800 | 18 | 18 | House Fan | 6400 | 4.9781 | 2 | 4.9781 | 2
202 | Classroom | 312 | 20 |  | 690 | 15 | 15 | House Fan | 5520 | 3.3913 | 1 | 3.3913 | 1
203 | Classroom | 273 | 18 |  | 690 | 15 | 15 | House Fan | 5520 | 2.9674 | 1 | 2.9674 | 1
204 | Classroom | 97 | 6 | Yes | 690 | 15 | 15 | House Fan | 5520 | 1.0543 | 1 | 21.0543 | 3
205 | Classroom | 443 | 29 |  | 690 | 15 | 15 | House Fan | 5520 | 4.8152 | 2 | 4.8152 | 2
206 | Classroom | 267 | 17 |  | 900 | 20 | 17 | House Fan | 7200 | 2.225 | 1 | 2.225 | 1
207 | Classroom | 372 | 24 |  | 690 | 15 | 15 | House Fan | 5520 | 4.0435 | 2 | 4.0435 | 2
208 | Classroom | 437 | 29 |  | 805 | 18 | 18 | House Fan | 6440 | 4.0714 | 2 | 4.0714 | 2
209 | Classroom | 504 | 33 |  | 690 | 15 | 15 | House Fan | 5520 | 5.4783 | 2 | 5.4783 | 2
210 | Classroom | 361 | 24 |  | 690 | 15 | 15 | House Fan | 5520 | 3.9239 | 1 | 3.9239 | 1
211 | Classroom | 416 | 27 |  | 690 | 15 | 15 | House Fan | 5520 | 4.5217 | 2 | 4.5217 | 2
213 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0 | 20 | 3
214 | Classroom | 0 | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0 | 20 | 3
215 | Classroom | 0 | 0 | Yes | 744 | 16 | 16 | House Fan | 5952 | 0 | 0 | 20 | 3
216 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0 | 20 | 3
217 | Classroom | 0 | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | 0 | 0 | 20 | 3
218 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 | Yes | 1190 | 27 |  |  | 9520 | unk | unk | 20 | 3
302 | Classroom | 695 | 46 |  | 660 | 15 | 15 | House Fan | 5280 | 7.8977 | 2 | 7.8977 | 2
303 | Classroom | 99 | 6 | Yes | 660 | 15 | 15 | House Fan | 5280 | 1.125 | 1 | 21.125 | 3
304 | Classroom | 719 | 47 |  | 660 | 15 | 15 | House Fan | 5280 | 8.1705 | 2 | 8.1705 | 2
305 | Classroom | 427 | 28 |  | 616 | 14 | 14 | House Fan | 4928 | 5.1989 | 2 | 5.1989 | 2
306 | Classroom | 259 | 17 |  | 638 | 14 | 14 | House Fan | 5104 | 3.0447 | 1 | 3.0447 | 1
307 | Classroom | 336 | 22 |  | 690 | 15 | 15 | House Fan | 5520 | 3.6522 | 1 | 3.6522 | 1
308 | Classroom | 372 | 24 |  | 660 | 15 | 15 | House Fan | 5280 | 4.2273 | 2 | 4.2273 | 2
308A | Classroom |  | 0 | Yes | 220 | 5 |  |  | 1760 | unk | unk | 20 | 3
309 | Classroom | 105 | 7 | Yes | 690 | 15 | 15 | House Fan | 5520 | 1.1413 | 1 | 21.1413 | 3
310 | Classroom | 346 | 23 |  | 540 | 12 | 12 | House Fan | 4320 | 4.8056 | 2 | 4.8056 | 2
311 | Classroom | 178 | 11 |  | 690 | 15 | 11 | House Fan | 5520 | 1.9348 | 1 | 1.9348 | 1
Portable Building | Cafeteria 1 |  | 0 |  | 1840 | 41 |  |  | 14720 | unk | unk | unk | unk
Portable Building | Cafeteria 2 |  | 0 |  | 989 | 22 |  |  | 7912 | unk | unk | unk | unk
- | Auditorium | 0 | 0 | Yes | 5336 | 121 | 121 | House Fan | 42688 | 0 | 0 | 20 | 3
- | Basement Office/Classroom | 617 | 41 |  | 1088 | 24 | 24 | House Fan | 8704 | 4.2532 | 2 | 4.2532 | 2
- | Gym | 3331 | 222 |  | 5005 | 113 | 113 | AHU | 40040 | 4.9915 | 2 | 4.9915 | 2
- | Prinicipal Office |  | 0 |  | 108 | 2 | 0 |  | 864 | unk | unk | unk | unk
- | Main Office |  | 0 |  | 234 | 5 | 0 |  | 1872 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | Louis H. Farrell Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | Retest | [7 empty] | unk | unk | unk | unk
| Devine 2nd Retest | Devine 3rd Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
A-2 | LS | 269 | 17 |  | 891 | 20 | 17 | Unit Ventilator | 7128 | 2.2643 | 1 | 2.2643 | 1
A-3 | LS | 319 | 21 |  | 891 | 20 | 20 | Unit Ventilator | 7128 | 2.6852 | 1 | 2.6852 | 1
A-4 | LS | 259 | 17 |  | 540 | 12 | 12 | Unit Ventilator | 4320 | 3.5972 | 1 | 3.5972 | 1
A-6 | LS | 274 | 18 |  | 891 | 20 | 18 | Unit Ventilator | 7128 | 2.3064 | 1 | 2.3064 | 1
A-10 | A-10 | 290 | 19 |  | 1130 | 25 | 19 | RTU | 9040 | 1.9248 | 1 | 1.9248 | 1
A-11 | A-11 | 276 | 18 |  | 800 | 18 | 18 | RTU | 6400 | 2.5875 | 1 | 2.5875 | 1
A-12 | A-12 | 296 | 19 |  | 800 | 18 | 18 | RTU | 6400 | 2.775 | 1 | 2.775 | 1
A-13 | A-13 | 306 | 20 |  | 800 | 18 | 18 | RTU | 6400 | 2.8687 | 1 | 2.8687 | 1
A-14 | A-14 | 293 | 19 |  | 800 | 18 | 18 | RTU | 6400 | 2.7469 | 1 | 2.7469 | 1
A-15 | A-15 | 331 | 22 |  | 800 | 18 | 18 | RTU | 6400 | 3.1031 | 1 | 3.1031 | 1
A-16 | A-16 | 303 | 20 |  | 800 | 18 | 18 | RTU | 6400 | 2.8406 | 1 | 2.8406 | 1
A-21 | A-21 | 314 | 20 |  | 800 | 18 | 18 | RTU | 6400 | 2.9438 | 1 | 2.9438 | 1
A-22 | A-22 | 285 | 19 |  | 800 | 18 | 18 | RTU | 6400 | 2.6719 | 1 | 2.6719 | 1
A-23 | A-23 | 293 | 19 |  | 800 | 18 | 18 | RTU | 6400 | 2.7469 | 1 | 2.7469 | 1
A-24 | A-24 | 293 | 19 |  | 800 | 18 | 18 | RTU | 6400 | 2.7469 | 1 | 2.7469 | 1
A-25 | A-25 | 333 | 22 |  | 800 | 18 | 18 | RTU | 6400 | 3.1219 | 1 | 3.1219 | 1
A-26 | A-26 | 316 | 21 |  | 800 | 18 | 18 | RTU | 6400 | 2.9625 | 1 | 2.9625 | 1
100 | LS | 328 | 21 |  | 1813 | 41 | 21 | Unit Ventilator | 14504 | 1.3569 | 1 | 1.3569 | 1
101 | LS | 326 | 21 |  | 1813 | 41 | 21 | Unit Ventilator | 14504 | 1.3486 | 1 | 1.3486 | 1
103 | LS | 406 | 27 |  | 925 | 21 | 21 | Unit Ventilator | 7400 | 3.2919 | 1 | 3.2919 | 1
105 | AS | 318 | 21 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 3.5491 | 1 | 3.5491 | 1
108 |  |  |  | Yes | 350 |  |  | N/A | 2800 | unk | unk | 20 | 3
111 | AS | 241 | 16 |  | 950 | 21 | 16 | Unit Ventilator | 7600 | 1.9026 | 1 | 1.9026 | 1
112 | ? | 282 | 18 |  | 950 | 21 | 18 | Unit Ventilator | 7600 | 2.2263 | 1 | 2.2263 | 1
113 | ? | 222 | 14 |  | 950 | 21 | 14 | Unit Ventilator | 7600 | 1.7526 | 1 | 1.7526 | 1
200 | LIT/SS | 318 | 21 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 2.5105 | 1 | 2.5105 | 1
201 | M/SC | 278 | 18 |  | 950 | 21 | 18 | Unit Ventilator | 7600 | 2.1947 | 1 | 2.1947 | 1
202 | LS | 297 | 19 |  | 950 | 21 | 19 | Unit Ventilator | 7600 | 2.3447 | 1 | 2.3447 | 1
203 | RELA/LS/EL PI | 297 | 19 |  | 950 | 21 | 19 | Unit Ventilator | 7600 | 2.3447 | 1 | 2.3447 | 1
204 | Classroom |  | 0 | Yes | 288 | 6 | 6 | Unit Ventilator | 2304 | unk | unk | 20 | 3
205 | M/SC/SS | 345 | 23 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 2.7237 | 1 | 2.7237 | 1
206 | RELA | 327 | 21 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 2.5816 | 1 | 2.5816 | 1
207 | ESOL | 372 | 24 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 2.9368 | 1 | 2.9368 | 1
208 | MATH | 308 | 20 |  | 950 | 21 | 20 | Unit Ventilator | 7600 | 2.4316 | 1 | 2.4316 | 1
209 | M/SC/SS | 294 | 19 |  | 950 | 21 | 19 | Unit Ventilator | 7600 | 2.3211 | 1 | 2.3211 | 1
209A |  |  |  | Yes | 310 |  |  | N/A | 2480 | unk | unk | 20 | 3
210 | RELA/SS | 203 | 13 |  | 950 | 21 | 13 | Unit Ventilator | 7600 | 1.6026 | 1 | 1.6026 | 1
211 | MATH/SC | 245 | 16 |  | 950 | 21 | 16 | Unit Ventilator | 7600 | 1.9342 | 1 | 1.9342 | 1
212 | RELA | 293 | 19 |  | 950 | 21 | 19 | Unit Ventilator | 7600 | 2.3132 | 1 | 2.3132 | 1
213 | SC/SS | 283 | 18 |  | 950 | 21 | 18 | Unit Ventilator | 7600 | 2.2342 | 1 | 2.2342 | 1
300 | RELA / SS | 265 | 17 |  | 950 | 21 | 17 | Unit Ventilator | 7600 | 2.0921 | 1 | 2.0921 | 1
301 | CSC | 277 | 18 |  | 950 | 21 | 18 | Unit Ventilator | 7600 | 2.1868 | 1 | 2.1868 | 1
302 | MATH | 254 | 16 |  | 950 | 21 | 16 | Unit Ventilator | 7600 | 2.0053 | 1 | 2.0053 | 1
303 | SC/SS | 224 | 14 |  | 950 | 21 | 14 | Unit Ventilator | 7600 | 1.7684 | 1 | 1.7684 | 1
304 | Room |  | 0 | Yes | 192 | 4 | 4 |  | 1536 | unk | unk | 20 | 3
305 | SC/MATH | 287 | 19 |  | 950 | 21 | 19 | Unit Ventilator | 7600 | 2.2658 | 1 | 2.2658 | 1
306 | MATH | 300 | 20 |  | 950 | 21 | 20 | Unit Ventilator | 7600 | 2.3684 | 1 | 2.3684 | 1
307 | SS/RELA | 226 | 15 |  | 950 | 21 | 15 | Unit Ventilator | 7600 | 1.7842 | 1 | 1.7842 | 1
308 | RELA/EL B | 277 | 18 |  | 950 | 21 | 18 | Unit Ventilator | 7600 | 2.1868 | 1 | 2.1868 | 1
309 | SC/SS | 277 | 18 |  | 1175 | 26 | 18 | Unit Ventilator | 9400 | 1.7681 | 1 | 1.7681 | 1
310 | MATH | 346 | 23 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 2.7316 | 1 | 2.7316 | 1
311 | RELA EL PI | 232 | 15 |  | 950 | 21 | 15 | Unit Ventilator | 7600 | 1.8316 | 1 | 1.8316 | 1
312 | SS/RELA ALG | 203 | 13 |  | 950 | 21 | 13 | Unit Ventilator | 7600 | 1.6026 | 1 | 1.6026 | 1
313 | SC/MATH | 223 | 14 |  | 950 | 21 | 14 | Unit Ventilator | 7600 | 1.7605 | 1 | 1.7605 | 1
- | Lunchroom | 815 | 54 |  | 2604 | 59 | 54 | Unit Ventilator | 20832 | 2.3474 | 1 | 2.3474 | 1
Gymnasium | Gymnasium |  | 0 | Yes | 3940 | 89 | 89 |  | 31520 | unk | unk | 20 | 3
Gymnasium | Office |  | 0 | Yes | 247 | 5 | 5 |  | 1976 | unk | unk | 20 | 3
- | Auditorium | 72 | 4 |  | 3808 | 86 | 4 | Unit Ventilator | 30464 | 0.14181 | 0 | 0.14181 | 0
- | Main Office |  | 0 | Yes | 279 | 6 | 6 | N/A | 2232 | unk | unk | 20 | 3
- | Principal Office |  | 0 |  | 288 | 6 | 0 | N/A | 2304 | unk | unk | unk | unk
Vice Principal | Office |  | 0 | Yes | 96 | 2 | 2 |  | 768 | unk | unk | 20 | 3
- | Counselor Office |  | 0 | Yes | 288 | 6 | 6 | N/A | 2304 | unk | unk | 20 | 3
Building Engineer | Office |  | 0 | Yes | 275 | 6 | 6 |  | 2200 | unk | unk | 20 | 3
- | IMC |  | 0 | Yes | 1485 | 33 | 33 | N/A | 11880 | unk | unk | 20 | 3
- | Nurse |  | 0 | Yes | 234 | 5 | 5 | N/A | 1872 | unk | unk | 20 | 3
Sheet Last Modified: | 2021-03-23 | [8 empty] | unk | unk | unk | unk
School: | D. Newlin Fell Elementary-Middle School | House fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
2 | Music Room | 519 | 34 |  | 418 | 9 | 9 | House Fan | 3344 | 9.3122 | 2 | 9.3122 | 2
100 | Classroom | 677 | 45 |  | 704 | 16 | 16 | House Fan | 5632 | 7.2124 | 2 | 7.2124 | 2
101 | Classroom | 791 | 52 |  | 308 | 7 | 7 | House Fan | 2464 | 19.2614 | 3 | 19.2614 | 3
102 | Classroom | 653 | 43 |  | 704 | 16 | 16 | House Fan | 5632 | 6.9567 | 2 | 6.9567 | 2
103 | Classroom | 588 | 39 |  | 660 | 15 | 15 | House Fan | 5280 | 6.6818 | 2 | 6.6818 | 2
104 | Classroom | 604 | 40 |  | 660 | 15 | 15 | House Fan | 5280 | 6.8636 | 2 | 6.8636 | 2
105 | Classroom | 960 | 64 |  | 660 | 15 | 15 | House Fan | 5280 | 10.9091 | 3 | 10.9091 | 3
106 | Classroom | 560 | 37 |  | 660 | 15 | 15 | House Fan | 5280 | 6.3636 | 2 | 6.3636 | 2
107 | Classroom | 760 | 50 |  | 682 | 15 | 15 | House Fan | 5456 | 8.3578 | 2 | 8.3578 | 2
108 | Classroom | 550 | 36 |  | 638 | 14 | 14 | House Fan | 5104 | 6.4655 | 2 | 6.4655 | 2
109 | Classroom | 491 | 32 |  | 687 | 15 | 15 | House Fan | 5496 | 5.3603 | 2 | 5.3603 | 2
200 | Classroom | 362 | 24 |  | 682 | 15 | 15 | House Fan | 5456 | 3.9809 | 1 | 3.9809 | 1
201 | Classroom | 750 | 50 |  | 638 | 14 | 14 | House Fan | 5104 | 8.8166 | 2 | 8.8166 | 2
202 | Classroom | 840 | 56 |  | 682 | 15 | 15 | House Fan | 5456 | 9.2375 | 2 | 9.2375 | 2
203 | Classroom | 411 | 27 |  | 660 | 15 | 15 | House Fan | 5280 | 4.6705 | 2 | 4.6705 | 2
204 | Classroom | 952 | 63 |  | 660 | 15 | 15 | House Fan | 5280 | 10.8182 | 3 | 10.8182 | 3
205 | Library | 670 | 44 |  | 638 | 14 | 14 | House Fan | 5104 | 7.8762 | 2 | 7.8762 | 2
206 | Library | 668 | 44 |  | 638 | 14 | 14 | House Fan | 5104 | 7.8527 | 2 | 7.8527 | 2
207 | Classroom | 512 | 34 |  | 682 | 15 | 15 | House Fan | 5456 | 5.6305 | 2 | 5.6305 | 2
208 | Classroom | 765 | 51 |  | 638 | 14 | 14 | House Fan | 5104 | 8.9929 | 2 | 8.9929 | 2
209 | Classroom | 478 | 31 |  | 682 | 15 | 15 | House Fan | 5456 | 5.2566 | 2 | 5.2566 | 2
300 | Classroom | 500 | 33 |  | 704 | 16 | 16 | House Fan | 5632 | 5.3267 | 2 | 5.3267 | 2
301 | Classroom | 406 | 27 |  | 638 | 14 | 14 | House Fan | 5104 | 4.7727 | 2 | 4.7727 | 2
302 | Classroom | 110 | 7 |  | 682 | 15 | 7 | House Fan | 5456 | 1.2097 | 1 | 1.2097 | 1
303 | Classroom | 426 | 28 |  | 660 | 15 | 15 | House Fan | 5280 | 4.8409 | 2 | 4.8409 | 2
304 | Classroom | 630 | 42 |  | 660 | 15 | 15 | House Fan | 5280 | 7.1591 | 2 | 7.1591 | 2
305 | Classroom | 888 | 59 |  | 660 | 15 | 15 | House Fan | 5280 | 10.0909 | 3 | 10.0909 | 3
306 | Classroom | 791 | 52 |  | 660 | 15 | 15 | House Fan | 5280 | 8.9886 | 2 | 8.9886 | 2
307 | Classroom | 407 | 27 |  | 682 | 15 | 15 | House Fan | 5456 | 4.4758 | 2 | 4.4758 | 2
308 | Classroom | 641 | 42 |  | 638 | 14 | 14 | House Fan | 5104 | 7.5353 | 2 | 7.5353 | 2
309 | Classroom | 645 | 43 |  | 704 | 16 | 16 | House Fan | 5632 | 6.8714 | 2 | 6.8714 | 2
309A | Classroom |  | 0 | Yes | 275 | 6 | 6 | N/A | 2200 | unk | unk | 20 | 3
310 | Classroom | 310 | 20 |  | 275 | 6 | 6 | House Fan | 2200 | 8.4545 | 2 | 8.4545 | 2
- | Auditrium | 3031 | 202 |  | 3055 | 69 | 69 | House Fan | 24440 | 7.4411 | 2 | 7.4411 | 2
- | Boys Bathroom | 300 | 20 |  | 114 | 2 | 2 | N/A | 912 | 19.7368 | 3 | 19.7368 | 3
- | Cafeteria | 375 | 25 |  | 990 | 22 | 22 | House Fan | 7920 | 2.8409 | 1 | 2.8409 | 1
- | Girls Bathroom | 421 | 28 |  | 96 | 2 | 2 | N/A | 768 | 32.8906 | 4 | 32.8906 | 4
- | Gym | 0 | 0 | Yes | 3219 | 73 | 73 | N/A | 25752 | 0 | 0 | 20 | 3
- | Main Office | 0 | 0 | Yes | 330 | 7 | 7 | House Fan | 2640 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 288 | 6 | 6 | N/A | 2304 | unk | unk | 20 | 3
- | Nurse Office | 0 | 0 | Yes | 220 | 5 | 5 | House Fan | 1760 | 0 | 0 | 20 | 3
- | PTA Room | 900 | 60 |  | 1540 | 35 | 35 | House Fan | 12320 | 4.3831 | 2 | 4.3831 | 2
- | Speech Room | 438 | 29 |  | 506 | 11 | 11 | House Fan | 4048 | 6.4921 | 2 | 6.4921 | 2
- | Teachers Lounge | 0 | 0 |  | 330 | 7 | 0 | House Fan | 2640 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | Samuel Fels High School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
A100 | Classroom | 69 | 4 |  | 290 | 6 | 4 |  | 2320 | 1.7845 | 1 | 1.7845 | 1
A103 | Classroom | 125 | 8 |  | 870 | 19 | 8 |  | 6960 | 1.0776 | 1 | 1.0776 | 1
A105 | Classroom | 148 | 9 |  | 870 | 19 | 9 |  | 6960 | 1.2759 | 1 | 1.2759 | 1
A106 | Classroom | 147 | 9 |  | 870 | 19 | 9 |  | 6960 | 1.2672 | 1 | 1.2672 | 1
A107 | Classroom | 135 | 9 |  | 870 | 19 | 9 |  | 6960 | 1.1638 | 1 | 1.1638 | 1
A108 | Classroom | 39 | 2 |  | 870 | 19 | 2 |  | 6960 | 0.33621 | 0 | 0.33621 | 0
A109 | Classroom | 162 | 10 |  | 870 | 19 | 10 |  | 6960 | 1.3966 | 1 | 1.3966 | 1
A110 | Classroom | 162 | 10 |  | 870 | 19 | 10 |  | 6960 | 1.3966 | 1 | 1.3966 | 1
A111 | Classroom | 167 | 11 |  | 870 | 19 | 11 |  | 6960 | 1.4397 | 1 | 1.4397 | 1
A113 | Classroom | 161 | 10 |  | 870 | 19 | 10 |  | 6960 | 1.3879 | 1 | 1.3879 | 1
A114 | Classroom | 0 | 0 |  | 930 | 21 | 0 |  | 7440 | 0 | 0 | 0 | 0
A120 | Office | 125 | 8 |  | 144 | 3 | 3 |  | 1152 | 6.5104 | 2 | 6.5104 | 2
A123 | Classroom | 298 | 19 |  | 900 | 20 | 19 |  | 7200 | 2.4833 | 1 | 2.4833 | 1
A124 | Classroom | 345 | 23 |  | 900 | 20 | 20 |  | 7200 | 2.875 | 1 | 2.875 | 1
A125 | Classroom | 376 | 25 |  | 900 | 20 | 20 |  | 7200 | 3.1333 | 1 | 3.1333 | 1
A126 | Classroom | 266 | 17 |  | 900 | 20 | 17 |  | 7200 | 2.2167 | 1 | 2.2167 | 1
A130 | Classroom | 697 | 46 |  | 900 | 20 | 20 |  | 7200 | 5.8083 | 2 | 5.8083 | 2
A131 | Classroom | 155 | 10 |  | 900 | 20 | 10 |  | 7200 | 1.2917 | 1 | 1.2917 | 1
A132 | Classroom | 291 | 19 |  | 960 | 21 | 19 |  | 7680 | 2.2734 | 1 | 2.2734 | 1
A135 | Classroom | 645 | 43 |  | 960 | 21 | 21 |  | 7680 | 5.0391 | 2 | 5.0391 | 2
A136 | Classroom | 162 | 10 |  | 960 | 21 | 10 |  | 7680 | 1.2656 | 1 | 1.2656 | 1
A137 | Classroom | 229 | 15 |  | 1320 | 30 | 15 |  | 10560 | 1.3011 | 1 | 1.3011 | 1
A138 | Classroom | 963 | 64 |  | 1376 | 31 | 31 |  | 11008 | 5.2489 | 2 | 5.2489 | 2
A139 | Classroom | 161 | 10 |  | 1376 | 31 | 10 |  | 11008 | 0.87754 | 0 | 0.87754 | 0
A140 | Classroom | 1027 | 68 |  | 1376 | 31 | 31 |  | 11008 | 5.5977 | 2 | 5.5977 | 2
A142 | Classroom | 1338 | 89 |  | 1271 | 28 | 28 |  | 10168 | 7.8954 | 2 | 7.8954 | 2
A143 | Classroom | 964 | 64 |  | 1505 | 34 | 34 |  | 12040 | 4.804 | 2 | 4.804 | 2
A144 | Classroom | 937 | 62 |  | 1394 | 31 | 31 |  | 11152 | 5.0412 | 2 | 5.0412 | 2
A148 | Hallway | 193 | 12 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
A150 | Hallway | 255 | 17 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
A152 | Hallway | 180 | 12 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
A200 | Classroom | 451 | 30 |  | 290 | 6 | 6 |  | 2320 | 11.6638 | 3 | 11.6638 | 3
A203 | Classroom | 252 | 16 |  | 870 | 19 | 16 |  | 6960 | 2.1724 | 1 | 2.1724 | 1
A205 | Classroom | 332 | 22 |  | 870 | 19 | 19 |  | 6960 | 2.8621 | 1 | 2.8621 | 1
A206 | Classroom | 911 | 60 |  | 870 | 19 | 19 |  | 6960 | 7.8534 | 2 | 7.8534 | 2
A207 | Classroom | 536 | 35 |  | 870 | 19 | 19 |  | 6960 | 4.6207 | 2 | 4.6207 | 2
A208 | Classroom | 1475 | 98 |  | 870 | 19 | 19 |  | 6960 | 12.7155 | 3 | 12.7155 | 3
A209 | Classroom | 620 | 41 |  | 870 | 19 | 19 |  | 6960 | 5.3448 | 2 | 5.3448 | 2
A210 | Classroom | 1060 | 70 |  | 870 | 19 | 19 |  | 6960 | 9.1379 | 2 | 9.1379 | 2
A211 | Classroom | 1246 | 83 |  | 870 | 19 | 19 |  | 6960 | 10.7414 | 3 | 10.7414 | 3
A212 | Classroom | 1262 | 84 |  | 1271 | 28 | 28 |  | 10168 | 7.4469 | 2 | 7.4469 | 2
A213 | Classroom | 879 | 58 |  | 961 | 21 | 21 |  | 7688 | 6.86 | 2 | 6.86 | 2
A214 | Classroom | 667 | 44 |  | 961 | 21 | 21 |  | 7688 | 5.2055 | 2 | 5.2055 | 2
A220 | Office | 7 | 0 |  | 144 | 3 | 0 |  | 1152 | 0.36458 | 0 | 0.36458 | 0
A223 | Classroom | 486 | 32 |  | 1860 | 42 | 32 |  | 14880 | 1.9597 | 1 | 1.9597 | 1
A225 | Classroom | 90 | 6 |  | 160 | 3 | 3 |  | 1280 | 4.2188 | 2 | 4.2188 | 2
A226 | Classroom | 323 | 21 |  | 900 | 20 | 20 |  | 7200 | 2.6917 | 1 | 2.6917 | 1
A227 | Classroom | 830 | 55 |  | 960 | 21 | 21 |  | 7680 | 6.4844 | 2 | 6.4844 | 2
A231 | Classroom | 260 | 17 |  | 1320 | 30 | 17 |  | 10560 | 1.4773 | 1 | 1.4773 | 1
A236 | Classroom | 8 | 0 |  | 120 | 2 | 0 |  | 960 | 0.5 | 0 | 0.5 | 0
A237 | Classroom | 9 | 0 |  | 104 | 2 | 0 |  | 832 | 0.64904 | 0 | 0.64904 | 0
A238 | Classroom | 207 | 13 |  | 1680 | 38 | 13 |  | 13440 | 0.92411 | 0 | 0.92411 | 0
A239 | Classroom | 1272 | 84 |  | 1376 | 31 | 31 |  | 11008 | 6.9331 | 2 | 6.9331 | 2
A240 | Classroom | 249 | 16 |  | 224 | 5 | 5 |  | 1792 | 8.3371 | 2 | 8.3371 | 2
A241 | Classroom | 1797 | 119 |  | 1364 | 31 | 31 |  | 10912 | 9.8809 | 2 | 9.8809 | 2
A242 | Classroom | 1960 | 130 |  | 1320 | 30 | 30 |  | 10560 | 11.1364 | 3 | 11.1364 | 3
A243 | Classroom | 960 | 64 |  | 1320 | 30 | 30 |  | 10560 | 5.4545 | 2 | 5.4545 | 2
A244 | Classroom | 1222 | 81 |  | 1505 | 34 | 34 |  | 12040 | 6.0897 | 2 | 6.0897 | 2
A245 | Classroom | 695 | 46 |  | 1394 | 31 | 31 |  | 11152 | 3.7392 | 1 | 3.7392 | 1
A248 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
A250 | Hallway | 297 | 19 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
A252 | Hallway | 566 | 37 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
A255 | Classroom | 0 | 0 |  | 120 | 2 | 0 |  | 960 | 0 | 0 | 0 | 0
B100 | Classroom | 0 | 0 |  | 930 | 21 | 0 |  | 7440 | 0 | 0 | 0 | 0
B102 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0 | 0 | 0
B103 | Classroom | 0 | 0 |  | 1023 | 23 | 0 |  | 8184 | 0 | 0 | 0 | 0
B105 | Classroom | 0 | 0 |  | 1311 | 29 | 0 |  | 10488 | 0 | 0 | 0 | 0
B106 | Classroom | 0 | 0 |  | 280 | 6 | 0 |  | 2240 | 0 | 0 | 0 | 0
B107 | Classroom | 0 | 0 |  | 1265 | 28 | 0 |  | 10120 | 0 | 0 | 0 | 0
B108 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0 | 0 | 0
B109 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0 | 0 | 0
B117 | Classroom | 0 | 0 |  | 576 | 13 | 0 |  | 4608 | 0 | 0 | 0 | 0
B118 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0 | 0 | 0
B120 | Classroom | 0 | 0 |  | 208 | 4 | 0 |  | 1664 | 0 | 0 | 0 | 0
B123 | Classroom | 0 | 0 |  | 990 | 22 | 0 |  | 7920 | 0 | 0 | 0 | 0
B124 | Classroom | 0 | 0 |  | 990 | 22 | 0 |  | 7920 | 0 | 0 | 0 | 0
B125 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
B126 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
B127 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
B128 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
B200 | Classroom | 0 | 0 |  | 930 | 21 | 0 |  | 7440 | 0 | 0 | 0 | 0
B201 | Classroom | 0 | 0 |  | 1316 | 29 | 0 |  | 10528 | 0 | 0 | 0 | 0
B201B | Classroom | 0 | 0 |  | 224 | 5 | 0 |  | 1792 | 0 | 0 | 0 | 0
B202 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0 | 0 | 0
B203 | Classroom | 0 | 0 |  | 1023 | 23 | 0 |  | 8184 | 0 | 0 | 0 | 0
B204 | Classroom | 0 | 0 |  | 1311 | 29 | 0 |  | 10488 | 0 | 0 | 0 | 0
B205 | Classroom | 0 | 0 |  | 1265 | 28 | 0 |  | 10120 | 0 | 0 | 0 | 0
B208 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0 | 0 | 0
B209 | Classroom | 0 | 0 |  | 961 | 21 | 0 |  | 7688 | 0 | 0 | 0 | 0
B210 | Classroom | 0 | 0 |  | 144 | 3 | 0 |  | 1152 | 0 | 0 | 0 | 0
B218 | Classroom | 0 | 0 |  | 990 | 22 | 0 |  | 7920 | 0 | 0 | 0 | 0
B219 | Classroom | 0 | 0 |  | 990 | 22 | 0 |  | 7920 | 0 | 0 | 0 | 0
B222 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
B223 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
B224 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
B225 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
C101 | Front of house | 160 | 10 |  | 384 | 8 | 8 |  | 3072 | 3.125 | 1 | 3.125 | 1
C103 | Auditorium | 12689 | 845 |  | 9310 | 211 | 211 |  | 74480 | 10.2221 | 3 | 10.2221 | 3
C105 | Stage | 770 | 51 |  | 3400 | 77 | 51 |  | 27200 | 1.6985 | 1 | 1.6985 | 1
C106 | Classroom | 0 | 0 |  | 1302 | 29 | 0 |  | 10416 | 0 | 0 | 0 | 0
C107 | Backstage | 59 | 3 |  | 870 | 19 | 3 |  | 6960 | 0.50862 | 0 | 0.50862 | 0
C108 | Classroom | 39 | 2 |  | 870 | 19 | 2 |  | 6960 | 0.33621 | 0 | 0.33621 | 0
C109 | Classroom | 77 | 5 |  | 870 | 19 | 5 |  | 6960 | 0.66379 | 0 | 0.66379 | 0
C110 | Classroom | 89 | 5 |  | 870 | 19 | 5 |  | 6960 | 0.76724 | 0 | 0.76724 | 0
C111 | Classroom | 576 | 38 |  | 870 | 19 | 19 |  | 6960 | 4.9655 | 2 | 4.9655 | 2
C112 | Classroom | 112 | 7 |  | 870 | 19 | 7 |  | 6960 | 0.96552 | 0 | 0.96552 | 0
C113 | Classroom | 1414 | 94 |  | 2016 | 45 | 45 |  | 16128 | 5.2604 | 2 | 5.2604 | 2
C114 | Classroom | 20 | 1 |  | 870 | 19 | 1 |  | 6960 | 0.17241 | 0 | 0.17241 | 0
C115 | Classroom | 18 | 1 |  | 840 | 19 | 1 |  | 6720 | 0.16071 | 0 | 0.16071 | 0
C116 | Classroom | 20 | 1 |  | 840 | 19 | 1 |  | 6720 | 0.17857 | 0 | 0.17857 | 0
C117 | Classroom | 18 | 1 |  | 840 | 19 | 1 |  | 6720 | 0.16071 | 0 | 0.16071 | 0
C118 | Classroom | 210 | 14 |  | 840 | 19 | 14 |  | 6720 | 1.875 | 1 | 1.875 | 1
C119 | Classroom | 168 | 11 |  | 840 | 19 | 11 |  | 6720 | 1.5 | 1 | 1.5 | 1
C121 | Classroom | 0 | 0 |  | 840 | 19 | 0 |  | 6720 | 0 | 0 | 0 | 0
D104 | Locker room | 4 | 0 |  | 1680 | 38 | 0 |  | 13440 | 0.017857 | 0 | 0.017857 | 0
D105 | Locker room | 5 | 0 |  | 1680 | 38 | 0 |  | 13440 | 0.022321 | 0 | 0.022321 | 0
D106 | Office | 25 | 1 |  | 120 | 2 | 1 |  | 960 | 1.5625 | 1 | 1.5625 | 1
D109 | Locker room | 12 | 0 |  | 522 | 11 | 0 |  | 4176 | 0.17241 | 0 | 0.17241 | 0
D111 | Locker room | 8 | 0 |  | 522 | 11 | 0 |  | 4176 | 0.11494 | 0 | 0.11494 | 0
D112 | Office | 22 | 1 |  | 240 | 5 | 1 |  | 1920 | 0.6875 | 0 | 0.6875 | 0
D113 | Office | 26 | 1 |  | 240 | 5 | 1 |  | 1920 | 0.8125 | 0 | 0.8125 | 0
D114 | Locker room | 39 | 2 |  | 720 | 16 | 2 |  | 5760 | 0.40625 | 0 | 0.40625 | 0
D115 | Office | 0 | 0 |  | 260 | 5 | 0 |  | 2080 | 0 | 0 | 0 | 0
D116 | Weight room | 181 | 12 |  | 1392 | 31 | 12 |  | 11136 | 0.97522 | 0 | 0.97522 | 0
D119 | Classroom | 91 | 6 |  | 1240 | 28 | 6 |  | 9920 | 0.5504 | 0 | 0.5504 | 0
D126 | Vestibule | 42 | 2 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
D128 | Hallway | 249 | 16 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E100A | Library | 274 | 18 |  | 9200 | 209 | 18 |  | 73600 | 0.22337 | 0 | 0.22337 | 0
E100B | Office | 28 | 1 |  | 225 | 5 | 1 |  | 1800 | 0.93333 | 0 | 0.93333 | 0
E101 | Classroom | 17 | 1 |  | 992 | 22 | 1 |  | 7936 | 0.12853 | 0 | 0.12853 | 0
E102 | Office | 12 | 0 |  | 225 | 5 | 0 |  | 1800 | 0.4 | 0 | 0.4 | 0
E103 | Office | 14 | 0 |  | 225 | 5 | 0 |  | 1800 | 0.46667 | 0 | 0.46667 | 0
E104 | Office | 0 | 0 |  | 150 | 3 | 0 |  | 1200 | 0 | 0 | 0 | 0
E105A | Storage | 6 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E105B | Storage | 8 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E107 | Office | 52 | 3 |  | 286 | 6 | 3 |  | 2288 | 1.3636 | 1 | 1.3636 | 1
E111 | Office | 0 | 0 |  | 368 | 8 | 0 |  | 2944 | 0 | 0 | 0 | 0
E112 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E113 | Office | 0 | 0 |  | 132 | 3 | 0 |  | 1056 | 0 | 0 | 0 | 0
E114 | Office | 0 | 0 |  | 84 | 1 | 0 |  | 672 | 0 | 0 | 0 | 0
E115 | Office | 0 | 0 |  | 180 | 4 | 0 |  | 1440 | 0 | 0 | 0 | 0
E116 | Office | 0 | 0 |  | 72 | 1 | 0 |  | 576 | 0 | 0 | 0 | 0
E117 | Office | 0 | 0 |  | 120 | 2 | 0 |  | 960 | 0 | 0 | 0 | 0
E118 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E119 | Office | 0 | 0 |  | 400 | 9 | 0 |  | 3200 | 0 | 0 | 0 | 0
E120 | Office | 0 | 0 |  | 180 | 4 | 0 |  | 1440 | 0 | 0 | 0 | 0
E121 | Office | 0 | 0 |  | 180 | 4 | 0 |  | 1440 | 0 | 0 | 0 | 0
E123 | Office | 0 | 0 |  | 220 | 5 | 0 |  | 1760 | 0 | 0 | 0 | 0
E124 | Office | 0 | 0 |  | 220 | 5 | 0 |  | 1760 | 0 | 0 | 0 | 0
E125 | Office | 0 | 0 |  | 150 | 3 | 0 |  | 1200 | 0 | 0 | 0 | 0
E126 | Office | 0 | 0 |  | 216 | 4 | 0 |  | 1728 | 0 | 0 | 0 | 0
E127 | Office | 0 | 0 |  | 90 | 2 | 0 |  | 720 | 0 | 0 | 0 | 0
E128 | Office | 0 | 0 |  | 150 | 3 | 0 |  | 1200 | 0 | 0 | 0 | 0
E129 | Office | 0 | 0 |  | 216 | 4 | 0 |  | 1728 | 0 | 0 | 0 | 0
E130 | Office | 0 | 0 |  | 285 | 6 | 0 |  | 2280 | 0 | 0 | 0 | 0
E131 | Office | 0 | 0 |  | 195 | 4 | 0 |  | 1560 | 0 | 0 | 0 | 0
E132 | Office | 0 | 0 |  | 195 | 4 | 0 |  | 1560 | 0 | 0 | 0 | 0
E133 | Office | 0 | 0 |  | 315 | 7 | 0 |  | 2520 | 0 | 0 | 0 | 0
E134 | Office | 0 | 0 |  | 315 | 7 | 0 |  | 2520 | 0 | 0 | 0 | 0
E137 | Office | 0 | 0 |  | 420 | 9 | 0 |  | 3360 | 0 | 0 | 0 | 0
E139 | Office | 0 | 0 |  | 264 | 6 | 0 |  | 2112 | 0 | 0 | 0 | 0
E144 | Server room | 0 | 0 |  | 368 | 8 | 0 |  | 2944 | 0 | 0 | 0 | 0
E146 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E147 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E148 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E149 | Vestibule | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E150 | Vestibule | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E151 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E152 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E157 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
E201 | Office | 0 | 0 |  | 126 | 2 | 0 |  | 1008 | 0 | 0 | 0 | 0
E202 | Office | 0 | 0 |  | 126 | 2 | 0 |  | 1008 | 0 | 0 | 0 | 0
E203B | Office | 0 | 0 |  | 266 | 6 | 0 |  | 2128 | 0 | 0 | 0 | 0
E204 | Office | 0 | 0 |  | 126 | 2 | 0 |  | 1008 | 0 | 0 | 0 | 0
E205 | Office | 0 | 0 |  | 126 | 2 | 0 |  | 1008 | 0 | 0 | 0 | 0
E209 | Office | 0 | 0 |  | 1040 | 23 | 0 |  | 8320 | 0 | 0 | 0 | 0
E210 | Hallway | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
F100 | Cafeteria | 8136 | 542 |  | 8448 | 192 | 192 |  | 67584 | 7.223 | 2 | 7.223 | 2
F101 | Kitchen | 1521 | 101 |  | 1636 | 37 | 37 |  | 13088 | 6.9728 | 2 | 6.9728 | 2
F104 | Kitchen | 81 | 5 |  | 230 | 5 | 5 |  | 1840 | 2.6413 | 1 | 2.6413 | 1
F106 | Kitchen | 99 | 6 |  | 306 | 6 | 6 |  | 2448 | 2.4265 | 1 | 2.4265 | 1
F107 | Kitchen | 0 | 0 |  | 401 | 9 | 0 |  | 3208 | 0 | 0 | 0 | 0
F108 | Kitchen | 199 | 13 |  | 836 | 19 | 13 |  | 6688 | 1.7853 | 1 | 1.7853 | 1
F109 | Maintenance | 59 | 3 |  | 686 | 15 | 3 |  | 5488 | 0.64504 | 0 | 0.64504 | 0
F110 | Maintenance | 40 | 2 |  | 256 | 5 | 2 |  | 2048 | 1.1719 | 1 | 1.1719 | 1
F111 | Maintenance | 69 | 4 |  | 162 | 3 | 3 |  | 1296 | 3.1944 | 1 | 3.1944 | 1
F112 | Maintenance | 89 | 5 |  | 340 | 7 | 5 |  | 2720 | 1.9632 | 1 | 1.9632 | 1
F116 | Kitchen | 0 | 0 |  | 1636 | 37 | 0 |  | 13088 | 0 | 0 | 0 | 0
F119 | Engineer's office | 135 | 9 |  | 176 | 4 | 4 |  | 1408 | 5.7528 | 2 | 5.7528 | 2
F120 | Hallway | 149 | 9 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
F121 | Hallway | 1306 | 87 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
- | Gym | 2098 | 139 |  | 13184 | 299 | 139 |  | 105472 | 1.1935 | 1 | 1.1935 | 1
- | Office | 0 | 0 |  | 120 | 2 | 0 |  | 960 | 0 | 0 | 0 | 0
- | Storage | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
- | Pool | 5277 | 351 |  | 6426 | 146 | 146 |  | 51408 | 6.159 | 2 | 6.159 | 2
- | Principal Office | 0 | 0 |  | 288 | 6 | 0 |  | 2304 | 0 | 0 | 0 | 0
- | Stage | 3751 | 250 |  | 3400 | 77 | 77 |  | 27200 | 8.2743 | 2 | 8.2743 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-06 | [8 empty] | unk | unk | unk | unk
School: | Feltonville Arts & Sciences Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
104 | Classroom | 256 | 17 |  | 775 | 17 | 17 |  | 6200 | 2.4774 | 1 | 2.4774 | 1
105 | Classroom | 614 | 40 |  | 810 | 18 | 18 |  | 6480 | 5.6852 | 2 | 5.6852 | 2
106 | Classroom | 599 | 39 |  | 802 | 18 | 18 |  | 6416 | 5.6016 | 2 | 5.6016 | 2
107 | Classroom | 428 | 28 |  | 804 | 18 | 18 |  | 6432 | 3.9925 | 1 | 3.9925 | 1
108 | Classroom | 352 | 23 |  | 802 | 18 | 18 |  | 6416 | 3.2918 | 1 | 3.2918 | 1
109 | Classroom | 699 | 46 |  | 791 | 17 | 17 |  | 6328 | 6.6277 | 2 | 6.6277 | 2
110 | Classroom | 311 | 20 |  | 838 | 19 | 19 |  | 6704 | 2.7834 | 1 | 2.7834 | 1
111 | Classroom | 232 | 15 |  | 953 | 21 | 15 |  | 7624 | 1.8258 | 1 | 1.8258 | 1
112 | Classroom | 311 | 20 |  | 633 | 14 | 14 |  | 5064 | 3.6848 | 1 | 3.6848 | 1
205 | Classroom | 455 | 30 |  | 774 | 17 | 17 |  | 6192 | 4.4089 | 2 | 4.4089 | 2
206 | Classroom | 398 | 26 |  | 759 | 17 | 17 |  | 6072 | 3.9328 | 1 | 3.9328 | 1
207 | Classroom | 352 | 23 |  | 749 | 17 | 17 |  | 5992 | 3.5247 | 1 | 3.5247 | 1
208 | Classroom | 313 | 20 |  | 812 | 18 | 18 |  | 6496 | 2.891 | 1 | 2.891 | 1
210 | Classroom | 0 | 0 | Yes | 808 | 18 | 18 |  | 6464 | 0 | 0 | 20 | 3
211 | Classroom | 650 | 43 |  | 765 | 17 | 17 |  | 6120 | 6.3725 | 2 | 6.3725 | 2
212 | Classroom | 283 | 18 |  | 802 | 18 | 18 |  | 6416 | 2.6465 | 1 | 2.6465 | 1
214 | Classroom | 605 | 40 |  | 632 | 14 | 14 |  | 5056 | 7.1796 | 2 | 7.1796 | 2
301 | Classroom | 288 | 19 |  | 776 | 17 | 17 |  | 6208 | 2.7835 | 1 | 2.7835 | 1
302 | Classroom | 297 | 19 |  | 760 | 17 | 17 |  | 6080 | 2.9309 | 1 | 2.9309 | 1
303 | Classroom | 305 | 20 |  | 817 | 18 | 18 |  | 6536 | 2.7999 | 1 | 2.7999 | 1
304 | Classroom | 700 | 46 |  | 811 | 18 | 18 |  | 6488 | 6.4735 | 2 | 6.4735 | 2
305 | Classroom | 357 | 23 |  | 808 | 18 | 18 |  | 6464 | 3.3137 | 1 | 3.3137 | 1
306 | Classroom | 490 | 32 |  | 783 | 17 | 17 |  | 6264 | 4.6935 | 2 | 4.6935 | 2
307 | Classroom | 309 | 20 |  | 803 | 18 | 18 |  | 6424 | 2.8861 | 1 | 2.8861 | 1
308 | Classroom | 211 | 14 | Yes | 809 | 18 | 18 |  | 6472 | 1.9561 | 1 | 21.9561 | 3
309 | Classroom | 1419 | 94 |  | 2223 | 50 | 50 |  | 17784 | 4.7874 | 2 | 4.7874 | 2
- | Basement | 4061 | 270 |  | 4615 | 104 | 104 |  | 36920 | 6.5997 | 2 | 6.5997 | 2
- | Cafeteria, Kitchen, Faculty Room | 761 | 50 |  | 5110 | 116 | 50 |  | 40880 | 1.1169 | 1 | 1.1169 | 1
- | Classroom above 214 | 403 | 26 |  | 631 | 14 | 14 |  | 5048 | 4.79 | 2 | 4.79 | 2
- | Classroom Art Lab Computer Lab | 315 | 21 | Yes | 1017 | 23 | 23 |  | 8136 | 2.323 | 1 | 22.323 | 3
- | Classroom Science Lab 1 | 345 | 23 |  | 993 | 22 | 22 |  | 7944 | 2.6057 | 1 | 2.6057 | 1
- | Classroom Science Lab 2 3rd Floor | 344 | 22 |  | 989 | 22 | 22 |  | 7912 | 2.6087 | 1 | 2.6087 | 1
- | Classroom Science Lab 2 Right | 455 | 30 |  | 989 | 22 | 22 |  | 7912 | 3.4505 | 1 | 3.4505 | 1
- | Classroom Science Lab STEM Lab Left | 740 | 49 |  | 1631 | 37 | 37 |  | 13048 | 3.4028 | 1 | 3.4028 | 1
- | Dean's Office 1st Floor | 31 | 2 | Yes | 170 | 3 | 3 |  | 1360 | 1.3676 | 1 | 21.3676 | 3
- | Dean's Office 2nd Floor | 18 | 1 | Yes | 170 | 3 | 3 |  | 1360 | 0.79412 | 0 | 20.7941 | 3
- | Dean's Office 3rd Floor | 38 | 2 | Yes | 168 | 3 | 3 |  | 1344 | 1.6964 | 1 | 21.6964 | 3
- | Drama Room | 747 | 49 |  | 3095 | 70 | 49 |  | 24760 | 1.8102 | 1 | 1.8102 | 1
- | First Floor | 5315 | 354 |  | 6974 | 158 | 158 |  | 55792 | 5.7159 | 2 | 5.7159 | 2
- | First Floor Multi-Purpose Room | 572 | 38 |  | 3095 | 70 | 38 |  | 24760 | 1.3861 | 1 | 1.3861 | 1
- | Gym | 1186 | 79 |  | 5237 | 119 | 79 |  | 41896 | 1.6985 | 1 | 1.6985 | 1
- | Health Room | 0 | 0 | Yes | 594 | 13 | 13 |  | 4752 | 0 | 0 | 20 | 3
- | Second Floor | 1094 | 72 |  | 4743 | 107 | 72 |  | 37944 | 1.7299 | 1 | 1.7299 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Feltonville Intermediate Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | Exhaust Report | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | - |  | 0 | Yes | 462 | 10 | 10 |  | 3696 | unk | unk | 20 | 3
101 | - |  | 0 |  | 948 | 21 | 0 |  | 7584 | unk | unk | unk | unk
101A | - |  | 0 |  | 127 | 2 | 0 |  | 1016 | unk | unk | unk | unk
102 | - |  | 0 | Yes | 243 | 5 | 5 |  | 1944 | unk | unk | 20 | 3
103 | - |  | 0 |  | 101 | 2 | 0 |  | 808 | unk | unk | unk | unk
103A | - |  | 0 |  | 125 | 2 | 0 |  | 1000 | unk | unk | unk | unk
104 | - |  | 0 | Yes | 967 | 21 | 21 |  | 7736 | unk | unk | 20 | 3
106 | - |  | 0 | Yes | 1120 | 25 | 25 |  | 8960 | unk | unk | 20 | 3
107 | - |  | 0 |  | 213 | 4 | 0 |  | 1704 | unk | unk | unk | unk
108 | Room |  | 0 | Yes | 1436 | 32 | 32 |  | 11488 | unk | unk | 20 | 3
109 | Room | 0 | 0 | Yes | 893 | 20 | 20 |  | 7144 | 0 | 0 | 20 | 3
110 | Room | 647 | 43 |  | 1479 | 33 | 33 |  | 11832 | 3.2809 | 1 | 3.2809 | 1
112 | Room |  | 0 | Yes | 1415 | 32 | 32 |  | 11320 | unk | unk | 20 | 3
112A | - |  | 0 |  | 129 | 2 | 0 |  | 1032 | unk | unk | unk | unk
113 | Room |  | 0 |  | 1200 | 27 | 0 |  | 9600 | unk | unk | unk | unk
114 | - |  | 0 | Yes | 976 | 22 | 22 |  | 7808 | unk | unk | 20 | 3
116 | - |  | 0 |  | 1064 | 24 | 0 |  | 8512 | unk | unk | unk | unk
118 | Gym Office | 0 | 0 |  | 1027 | 23 | 0 |  | 8216 | 0 | 0 | 0 | 0
153A | Small Office Inside M/O |  | 0 |  | 108 | 2 | 0 |  | 864 | unk | unk | unk | unk
156B | Counselor #2 |  | 0 |  | 182 | 4 | 0 |  | 1456 | unk | unk | unk | unk
157 | - |  | 0 |  | 108 | 2 | 0 |  | 864 | unk | unk | unk | unk
200 | - |  | 0 |  | 478 | 10 | 0 |  | 3824 | unk | unk | unk | unk
201 | - |  | 0 | Yes | 1071 | 24 | 24 |  | 8568 | unk | unk | 20 | 3
202 | - |  | 0 |  | 578 | 13 | 0 |  | 4624 | unk | unk | unk | unk
202A | - |  | 0 |  | 179 | 4 | 0 |  | 1432 | unk | unk | unk | unk
203 | - |  | 0 | Yes | 677 | 15 | 15 |  | 5416 | unk | unk | 20 | 3
203A | - |  | 0 |  | 436 | 9 | 0 |  | 3488 | unk | unk | unk | unk
204 | - |  | 0 | Yes | 574 | 13 | 13 |  | 4592 | unk | unk | 20 | 3
205 | - |  | 0 |  | 829 | 18 | 0 |  | 6632 | unk | unk | unk | unk
206 | - |  | 0 | Yes | 629 | 14 | 14 |  | 5032 | unk | unk | 20 | 3
206A | - |  | 0 |  | 220 | 5 | 0 |  | 1760 | unk | unk | unk | unk
207 | - |  | 0 | Yes | 818 | 18 | 18 |  | 6544 | unk | unk | 20 | 3
207A | - |  | 0 |  | 126 | 2 | 0 |  | 1008 | unk | unk | unk | unk
208 | - |  | 0 | Yes | 752 | 17 | 17 |  | 6016 | unk | unk | 20 | 3
208A | - |  | 0 |  | 113 | 2 | 0 |  | 904 | unk | unk | unk | unk
209 | - |  | 0 | Yes | 788 | 17 | 17 |  | 6304 | unk | unk | 20 | 3
210 | - | 225 | 15 | Yes | 740 | 16 | 16 |  | 5920 | 2.2804 | 1 | 22.2804 | 3
300 | - |  | 0 | Yes | 858 | 19 | 19 |  | 6864 | unk | unk | 20 | 3
301 | - |  | 0 | Yes | 491 | 11 | 11 |  | 3928 | unk | unk | 20 | 3
302 | - |  | 0 | Yes | 765 | 17 | 17 |  | 6120 | unk | unk | 20 | 3
303 | - |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
304 | - |  | 0 |  | 505 | 11 | 0 |  | 4040 | unk | unk | unk | unk
305 | - |  | 0 | Yes | 626 | 14 | 14 |  | 5008 | unk | unk | 20 | 3
306 | - |  | 0 | Yes | 769 | 17 | 17 |  | 6152 | unk | unk | 20 | 3
307 | - |  | 0 | Yes | 1108 | 25 | 25 |  | 8864 | unk | unk | 20 | 3
307A | - |  | 0 |  | 73 | 1 | 0 |  | 584 | unk | unk | unk | unk
307B | - |  | 0 |  | 127 | 2 | 0 |  | 1016 | unk | unk | unk | unk
309 | - |  | 0 |  | 488 | 11 | 0 |  | 3904 | unk | unk | unk | unk
309A | - |  | 0 |  | 135 | 3 | 0 |  | 1080 | unk | unk | unk | unk
311 | - |  | 0 | Yes | 842 | 19 | 19 |  | 6736 | unk | unk | 20 | 3
313 | - |  | 0 | Yes | 662 | 15 | 15 |  | 5296 | unk | unk | 20 | 3
315 | - |  | 0 | Yes | 735 | 16 | 16 |  | 5880 | unk | unk | 20 | 3
- | Bradham Office |  | 0 |  | 141 | 3 | 0 |  | 1128 | unk | unk | unk | unk
- | Cafeteria (2nd Floor) |  | 0 |  | 5423 | 123 | 0 |  | 43384 | unk | unk | unk | unk
- | Confrence Room |  | 0 |  | 216 | 4 | 0 |  | 1728 | unk | unk | unk | unk
- | Counselor |  | 0 |  | 132 | 3 | 0 |  | 1056 | unk | unk | unk | unk
- | Custodial Staff Room |  | 0 |  | 118 | 2 | 0 |  | 944 | unk | unk | unk | unk
- | Food Service Locker Room |  | 0 |  | 83 | 1 | 0 |  | 664 | unk | unk | unk | unk
- | Food Service Manager's Office |  | 0 |  | 56 | 1 | 0 |  | 448 | unk | unk | unk | unk
- | Gymnasium |  | 0 |  | 4006 | 91 | 0 |  | 32048 | unk | unk | unk | unk
- | Kitchen |  | 0 |  | 954 | 21 | 0 |  | 7632 | unk | unk | unk | unk
- | Main Office |  | 0 |  | 505 | 11 | 0 |  | 4040 | unk | unk | unk | unk
- | MPR / Auditorium |  | 0 | Yes | 2669 | 60 | 60 |  | 21352 | unk | unk | 20 | 3
- | Nurse |  | 0 |  | 191 | 4 | 0 |  | 1528 | unk | unk | unk | unk
- | Nurse Waiting Area |  | 0 |  | 159 | 3 | 0 |  | 1272 | unk | unk | unk | unk
- | Principal's Office |  | 0 |  | 351 | 7 | 0 |  | 2808 | unk | unk | unk | unk
- | Psychologist's Office |  | 0 |  | 66 | 1 | 0 |  | 528 | unk | unk | unk | unk
- | Storage |  | 0 |  | 107 | 2 | 0 |  | 856 | unk | unk | unk | unk
- | Storage Room #2 |  | 0 |  | 99 | 2 | 0 |  | 792 | unk | unk | unk | unk
- | Supply Closet |  | 0 |  | 126 | 2 | 0 |  | 1008 | unk | unk | unk | unk
- | Teacher's Lounge |  | 0 |  | 226 | 5 | 0 |  | 1808 | unk | unk | unk | unk
- | 1st Floor Lunchroom | 0 | 0 |  | 2677 | 60 | 0 |  | 21416 | 0 | 0 | 0 | 0
- | Closet | 34 | 2 |  | 40 | 0 | 0 |  | 320 | 6.375 | 2 | 6.375 | 2
- | 3rd Floor Lunchroom |  | 0 |  | 4452 | 101 | 0 |  | 35616 | unk | unk | unk | unk
- | Cafeteria Manager's Office | 75 | 5 |  | 55 | 1 | 1 |  | 440 | 10.2273 | 3 | 10.2273 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-02-23 | [8 empty] | unk | unk | unk | unk
School: | Feltonville Headstart | House Fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | N/A | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-24 | [8 empty] | unk | unk | unk | unk
School: | Thomas Finletter Academics Plus Elementary School | House fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine |  | Devine Brothers Retest | [6 empty] | unk | unk | unk | unk
School: | Finletter LSH | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Finletter Main Building | [9 empty] | unk | unk | unk | unk
101 | Classroom | 535 | 35 |  | 1056 | 24 | 24 | House Fan | 8448 | 3.7997 | 1 | 3.7997 | 1
102 | Classroom | 458 | 30 |  | 1056 | 24 | 24 | House Fan | 8448 | 3.2528 | 1 | 3.2528 | 1
103 | Classroom | 621 | 41 |  | 1056 | 24 | 24 | House Fan | 8448 | 4.4105 | 2 | 4.4105 | 2
104 | Classroom | 595 | 39 |  | 870 | 19 | 19 | House Fan | 6960 | 5.1293 | 2 | 5.1293 | 2
105 | Classroom | 554 | 36 |  | 870 | 19 | 19 | House Fan | 6960 | 4.7759 | 2 | 4.7759 | 2
106 | Classroom | 1227 | 81 |  | 870 | 19 | 19 | House Fan | 6960 | 10.5776 | 3 | 10.5776 | 3
107 | Classroom | 980 | 65 |  | 870 | 19 | 19 | House Fan | 6960 | 8.4483 | 2 | 8.4483 | 2
108 | Classroom | 817 | 54 |  | 899 | 20 | 20 | House Fan | 7192 | 6.8159 | 2 | 6.8159 | 2
109 | Classroom | 876 | 58 |  | 899 | 20 | 20 | House Fan | 7192 | 7.3081 | 2 | 7.3081 | 2
110 | Classroom | 535 | 35 |  | 928 | 21 | 21 | House Fan | 7424 | 4.3238 | 2 | 4.3238 | 2
201 | Classroom | 477 | 31 |  | 1056 | 24 | 24 | House Fan | 8448 | 3.3878 | 1 | 3.3878 | 1
202 | Classroom | 334 | 22 |  | 1056 | 24 | 22 | House Fan | 8448 | 2.3722 | 1 | 2.3722 | 1
203 | Classroom | 411 | 27 |  | 1056 | 24 | 24 | House Fan | 8448 | 2.919 | 1 | 2.919 | 1
204 | Classroom | 916 | 61 |  | 870 | 19 | 19 | House Fan | 6960 | 7.8966 | 2 | 7.8966 | 2
205 | Classroom | 1018 | 67 |  | 870 | 19 | 19 | House Fan | 6960 | 8.7759 | 2 | 8.7759 | 2
206 | Classroom | 1222 | 81 |  | 870 | 19 | 19 | House Fan | 6960 | 10.5345 | 3 | 10.5345 | 3
207 | Classroom | 1203 | 80 |  | 870 | 19 | 19 | House Fan | 6960 | 10.3707 | 3 | 10.3707 | 3
208 | Classroom | 450 | 30 |  | 899 | 20 | 20 | House Fan | 7192 | 3.7542 | 1 | 3.7542 | 1
209 | Classroom | 363 | 24 |  | 899 | 20 | 20 | House Fan | 7192 | 3.0284 | 1 | 3.0284 | 1
210 | Classroom | 434 | 28 |  | 928 | 21 | 21 | House Fan | 7424 | 3.5075 | 1 | 3.5075 | 1
211 | Classroom | 0 | 0 |  | 195 | 4 | 0 | N/A | 1560 | 0 | 0 | 0 | 0
212 | Classroom | 0 | 0 |  | 384 | 8 | 0 | N/A | 3072 | 0 | 0 | 0 | 0
301 | Classroom | 278 | 18 |  | 1056 | 24 | 18 | House Fan | 8448 | 1.9744 | 1 | 1.9744 | 1
302 | Classroom | 458 | 30 |  | 1056 | 24 | 24 | House Fan | 8448 | 3.2528 | 1 | 3.2528 | 1
303 | Classroom | 125 | 8 |  | 1056 | 24 | 8 | House Fan | 8448 | 0.88778 | 0 | 0.88778 | 0
304 | Classroom | 288 | 19 |  | 870 | 19 | 19 | House Fan | 6960 | 2.4828 | 1 | 2.4828 | 1
305 | Classroom | 645 | 43 |  | 870 | 19 | 19 | House Fan | 6960 | 5.5603 | 2 | 5.5603 | 2
306 | Classroom | 289 | 19 |  | 870 | 19 | 19 | House Fan | 6960 | 2.4914 | 1 | 2.4914 | 1
307 | Classroom | 654 | 43 |  | 870 | 19 | 19 | House Fan | 6960 | 5.6379 | 2 | 5.6379 | 2
308 | Classroom | 345 | 23 |  | 899 | 20 | 20 | House Fan | 7192 | 2.8782 | 1 | 2.8782 | 1
309 | Classroom | 319 | 21 |  | 899 | 20 | 20 | House Fan | 7192 | 2.6613 | 1 | 2.6613 | 1
310 | Classroom | 675 | 45 |  | 928 | 21 | 21 | House Fan | 7424 | 5.4553 | 2 | 5.4553 | 2
311 | Classroom | 705 | 47 |  | 667 | 15 | 15 | House Fan | 5336 | 7.9273 | 2 | 7.9273 | 2
312 | Classroom | 0 | 0 |  | 275 | 6 | 0 | N/A | 2200 | 0 | 0 | 0 | 0
402 | Health | 335 | 22 |  | 588 | 13 | 13 | House Fan | 4704 | 4.273 | 2 | 4.273 | 2
403 | Music Room | 491 | 32 |  | 990 | 22 | 22 | House Fan | 7920 | 3.7197 | 1 | 3.7197 | 1
- | Annex Classroom | 65 | 4 |  | 960 | 21 | 4 | House Fan | 7680 | 0.50781 | 0 | 0.50781 | 0
- | Art | 882 | 58 |  | 1421 | 32 | 32 | House Fan | 11368 | 4.6552 | 2 | 4.6552 | 2
- | Auditorium | 3675 | 245 |  | 3431 | 77 | 77 | House Fan | 27448 | 8.0334 | 2 | 8.0334 | 2
- | Health Classroom | 0 | 0 |  | 250 | 5 | 0 | House Fan | 2000 | 0 | 0 | 0 | 0
- | Gym/Cafe |  | 0 | Yes | 3432 | 78 | 78 |  | 27456 | unk | unk | 20 | 3
- | Main office | 0 | 0 | Yes | 322 | 7 | 7 | N/A | 2576 | 0 | 0 | 20 | 3
Finletter LSH | [9 empty] | unk | unk | unk | unk
105 | Womens Staff Bathroom |  | 0 |  | 96 | 2 | 0 | AHU | 768 | unk | unk | unk | unk
105 | Mens Staff Bathroom |  | 0 |  | 77 | 1 | 0 | AHU | 616 | unk | unk | unk | unk
106 | Custodial | 57 | 3 |  | 36 | 0 | 0 | AHU | 288 | 11.875 | 3 | 11.875 | 3
111 | Lobby |  | 0 |  | 187 | 4 | 0 | AHU | 1496 | unk | unk | unk | unk
112 | Office | 118 | 7 |  | 110 | 2 | 2 | AHU | 880 | 8.0455 | 2 | 8.0455 | 2
113 | Office | 118 | 7 |  | 110 | 2 | 2 | AHU | 880 | 8.0455 | 2 | 8.0455 | 2
114 | General Storage | 216 | 14 |  | 54 | 1 | 1 | AHU | 432 | 30 | 4 | 30 | 4
115 | Multipurpose Room | 2476 | 165 |  | 2166 | 49 | 49 | AHU | 17328 | 8.5734 | 2 | 8.5734 | 2
116 | Corridor #2 |  | 0 |  | 120 | 2 | 0 | AHU | 960 | unk | unk | unk | unk
123 | Custodial Storage | 76 | 5 |  | 54 | 1 | 1 | AHU | 432 | 10.5556 | 3 | 10.5556 | 3
125 | Academic Storage | 66 | 4 |  | 18 | 0 | 0 | AHU | 144 | 27.5 | 4 | 27.5 | 4
A | Classroom | 341 | 22 |  | 986 | 22 | 22 | AHU | 7888 | 2.5938 | 1 | 2.5938 | 1
B | Classroom | 332 | 22 |  | 986 | 22 | 22 | AHU | 7888 | 2.5254 | 1 | 2.5254 | 1
C | Classroom | 341 | 22 |  | 986 | 22 | 22 | AHU | 7888 | 2.5938 | 1 | 2.5938 | 1
D | Classroom | 332 | 22 |  | 986 | 22 | 22 | AHU | 7888 | 2.5254 | 1 | 2.5254 | 1
E | Classroom | 327 | 21 |  | 986 | 22 | 21 | AHU | 7888 | 2.4873 | 1 | 2.4873 | 1
F | Classroom | 327 | 21 |  | 986 | 22 | 21 | AHU | 7888 | 2.4873 | 1 | 2.4873 | 1
G | Classroom | 327 | 21 |  | 986 | 22 | 21 | AHU | 7888 | 2.4873 | 1 | 2.4873 | 1
H | Classroom | 327 | 21 |  | 986 | 22 | 21 | AHU | 7888 | 2.4873 | 1 | 2.4873 | 1
I | Classroom | 293 | 19 |  | 986 | 22 | 19 | AHU | 7888 | 2.2287 | 1 | 2.2287 | 1
J | Classroom | 359 | 23 |  | 986 | 22 | 22 | AHU | 7888 | 2.7307 | 1 | 2.7307 | 1
K | Classroom | 293 | 19 |  | 986 | 22 | 19 | AHU | 7888 | 2.2287 | 1 | 2.2287 | 1
L | Classroom | 359 | 23 |  | 986 | 22 | 22 | AHU | 7888 | 2.7307 | 1 | 2.7307 | 1
- | Custodial Office |  | 0 | Yes |  | 0 | 0 | AHU |  | unk | unk | 20 | 3
- | Teachers Lounge |  | 0 | No | 288 | 6 | 0 | AHU | 2304 | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-22 | [8 empty] | unk | unk | unk | unk
School: | Fitler Academic Plus Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Meehan | Devine Retest | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
105 | Classroom | 707 | 47 |  | 1024 | 23 | 23 | House Fan | 8192 | 5.1782 | 2 | 5.1782 | 2
106 | Classroom | 796 | 53 |  | 720 | 16 | 16 | House Fan | 5760 | 8.2917 | 2 | 8.2917 | 2
107 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0 | 0 | 20 | 3
201 | Classroom | 834 | 55 |  | 1024 | 23 | 23 | House Fan | 8192 | 6.1084 | 2 | 6.1084 | 2
202 | Classroom | 879 | 58 |  | 1024 | 23 | 23 | House Fan | 8192 | 6.438 | 2 | 6.438 | 2
203 | Classroom | 510 | 34 |  | 1024 | 23 | 23 | House Fan | 8192 | 3.7354 | 1 | 3.7354 | 1
204 | Classroom | 951 | 63 |  | 1024 | 23 | 23 | House Fan | 8192 | 6.9653 | 2 | 6.9653 | 2
205 | Classroom | 716 | 47 |  | 1024 | 23 | 23 | House Fan | 8192 | 5.2441 | 2 | 5.2441 | 2
206 | Classroom | 668 | 44 |  | 720 | 16 | 16 | House Fan | 5760 | 6.9583 | 2 | 6.9583 | 2
207 | Classroom | 78 | 5 | Yes | 720 | 16 | 16 | House Fan | 5760 | 0.8125 | 0 | 20.8125 | 3
301 | Classroom | 860 | 57 |  | 720 | 16 | 16 | House Fan | 5760 | 8.9583 | 2 | 8.9583 | 2
302 | Classroom | 550 | 36 |  | 1024 | 23 | 23 | House Fan | 8192 | 4.0283 | 2 | 4.0283 | 2
303 | Classroom | 538 | 35 |  | 1024 | 23 | 23 | House Fan | 8192 | 3.9404 | 1 | 3.9404 | 1
304 | Classroom | 957 | 63 |  | 1024 | 23 | 23 | House Fan | 8192 | 7.0093 | 2 | 7.0093 | 2
305 | Classroom | 746 | 49 |  | 1024 | 23 | 23 | House Fan | 8192 | 5.4639 | 2 | 5.4639 | 2
306 | Classroom | 637 | 42 |  | 720 | 16 | 16 | House Fan | 5760 | 6.6354 | 2 | 6.6354 | 2
307 | Classroom | 364 | 24 | Yes | 720 | 16 | 16 | House Fan | 5760 | 3.7917 | 1 | 23.7917 | 3
- | Combo room | 883 | 58 |  | 1024 | 23 | 23 | House Fan | 8192 | 6.4673 | 2 | 6.4673 | 2
- | Gym | 1325 | 88 |  | 1344 | 30 | 30 | House Fan | 10752 | 7.394 | 2 | 7.394 | 2
- | Library | 1641 | 109 |  | 2400 | 54 | 54 | House Fan | 19200 | 5.1281 | 2 | 5.1281 | 2
- | Main office | 850 | 56 |  | 1156 | 26 | 26 | House Fan | 9248 | 5.5147 | 2 | 5.5147 | 2
- | Restroom | 781 | 52 |  | 660 | 15 | 15 | House Fan | 5280 | 8.875 | 2 | 8.875 | 2
- | Counselors Office | 1062 | 70 |  | 175 | 3 | 3 | ERU | 1400 | 45.5143 | 4 | 45.5143 | 4
- | Cafeteria | 0 | 0 |  | 1944 | 44 | 0 | NA | 15552 | 0 | 0 | 0 | 0
- | Nurses Office |  | 0 | Yes | 75 | 1 | 1 |  | 600 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-12 | [8 empty] | unk | unk | unk | unk
School: | Aloysius L. Fitzpatrick Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Part 2 | Part 3 | [6 empty] | unk | unk | unk | unk
School: | Aloysius L. Fitzpatrick Elementary School Annex | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Part 2 | Part 3 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Main Building | [9 empty] | unk | unk | unk | unk
B-10 | Classroom | 313 | 20 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 3.3345 | 1 | 3.3345 | 1
100 | Classroom | 298 | 19 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.3864 | 1 | 3.3864 | 1
101 | Classroom | 281 | 18 |  | 744 | 16 | 16 | Unit Ventilator | 5952 | 2.8327 | 1 | 2.8327 | 1
102 | Classroom | 315 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.8125 | 1 | 2.8125 | 1
103 | Classroom | 289 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.5804 | 1 | 2.5804 | 1
104 | Classroom | 337 | 22 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 3.1398 | 1 | 3.1398 | 1
105 | Classroom | 306 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7321 | 1 | 2.7321 | 1
106 | Classroom | 293 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6161 | 1 | 2.6161 | 1
107 | Classroom | 287 | 19 |  | 576 | 13 | 13 | Unit Ventilator | 4608 | 3.737 | 1 | 3.737 | 1
108 | Classroom | 409 | 27 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.7047 | 1 | 3.7047 | 1
109 | Classroom | 26 | 1 | Yes | 600 | 13 | 13 | Unit Ventilator | 4800 | 0.325 | 0 | 20.325 | 3
110 | Classroom | 340 | 22 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.0357 | 1 | 3.0357 | 1
112 | Classroom | 341 | 22 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.0888 | 1 | 3.0888 | 1
200 | Classroom | 319 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.8482 | 1 | 2.8482 | 1
201 | Classroom | 275 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4554 | 1 | 2.4554 | 1
202 | Classroom | 300 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6786 | 1 | 2.6786 | 1
203 | Classroom | 309 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7589 | 1 | 2.7589 | 1
204 | Classroom | 290 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.5893 | 1 | 2.5893 | 1
205 | Classroom | 314 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.8036 | 1 | 2.8036 | 1
206 | Library | 656 | 43 |  | 1680 | 38 | 38 | Unit Ventilator | 13440 | 2.9286 | 1 | 2.9286 | 1
207 | Classroom | 326 | 21 |  | 425 | 9 | 9 | Unit Ventilator | 3400 | 5.7529 | 2 | 5.7529 | 2
210 | Classroom | 293 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6161 | 1 | 2.6161 | 1
212 | Classroom | 334 | 22 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9821 | 1 | 2.9821 | 1
214 | Classroom | 304 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7143 | 1 | 2.7143 | 1
216 | Classroom | 325 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9018 | 1 | 2.9018 | 1
218 | Classroom | 307 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7411 | 1 | 2.7411 | 1
300 | Classroom | 289 | 19 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.5087 | 1 | 2.5087 | 1
301 | Classroom | 305 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7232 | 1 | 2.7232 | 1
302 | Classroom | 281 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.5089 | 1 | 2.5089 | 1
303 | Classroom | 299 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6696 | 1 | 2.6696 | 1
304 | Classroom | 329 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9375 | 1 | 2.9375 | 1
305 | Classroom | 294 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.625 | 1 | 2.625 | 1
306 | Classroom | 607 | 40 |  | 1704 | 38 | 38 | Unit Ventilator | 13632 | 2.6717 | 1 | 2.6717 | 1
307 | Classroom | 340 | 22 |  | 425 | 9 | 9 | Unit Ventilator | 3400 | 6 | 2 | 6 | 2
310 | Classroom | 299 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6696 | 1 | 2.6696 | 1
312 | Classroom | 326 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9107 | 1 | 2.9107 | 1
314 | Classroom | 304 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7143 | 1 | 2.7143 | 1
316 | Classroom | 329 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9375 | 1 | 2.9375 | 1
318 | Classroom | 337 | 22 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.0089 | 1 | 3.0089 | 1
- | Auditorium | 92 | 6 |  | 1825 | 41 | 6 | AHU | 14600 | 0.37808 | 0 | 0.37808 | 0
B-1 | Classroom | 466 | 31 |  | 966 | 21 | 21 | Unit Ventilator | 7728 | 3.618 | 1 | 3.618 | 1
B-2 | Classroom | 287 | 19 |  | 966 | 21 | 19 | Unit Ventilator | 7728 | 2.2283 | 1 | 2.2283 | 1
B-4 | Classroom | 236 | 15 |  | 704 | 16 | 15 | Unit Ventilator | 5632 | 2.5142 | 1 | 2.5142 | 1
B-8 | Classroom | 269 | 17 |  | 792 | 18 | 17 | Unit Ventilator | 6336 | 2.5473 | 1 | 2.5473 | 1
- | Cafeteria | 72 | 4 |  | 2835 | 64 | 4 | Unit Ventilator | 22680 | 0.19048 | 0 | 0.19048 | 0
- | Gymnasium | 72 | 4 | Yes | 3922 | 89 | 89 | AHU | 31376 | 0.13768 | 0 | 20.1377 | 3
- | Main Office | 284 | 18 |  | 1000 | 22 | 18 | Unit Ventilator | 8000 | 2.13 | 1 | 2.13 | 1
- | Music | 29 | 1 |  | 768 | 17 | 1 | Unit Ventilator | 6144 | 0.2832 | 0 | 0.2832 | 0
Annex Building | [9 empty] | unk | unk | unk | unk
9 | Classroom | 165 | 11 | Yes | 1040 | 23 | 23 | Unit Ventilator | 8320 | 1.1899 | 1 | 21.1899 | 3
10 | Classroom | 310 | 20 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.691 | 1 | 2.691 | 1
11 | Classroom | 311 | 20 |  | 962 | 21 | 20 | Unit Ventilator | 7696 | 2.4246 | 1 | 2.4246 | 1
12 | Classroom | 291 | 19 |  | 1040 | 23 | 19 | Unit Ventilator | 8320 | 2.0986 | 1 | 2.0986 | 1
Sheet Last Modified: | 2021-04-14 | [8 empty] | unk | unk | unk | unk
School: | Edwin Forrest Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
School: | Edwin Forrest Elementary School- Little School House | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Brothers Part 2 | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Edwin Forrest Elementary School Main Building | [9 empty] | unk | unk | unk | unk
- | Auditorium | 955 | 63 |  | 3552 | 80 | 63 | Unit Ventilator | 28416 | 2.0165 | 1 | 2.0165 | 1
- | PreK | 281 | 18 |  | 1084 | 24 | 18 | Unit Ventilator | 8672 | 1.9442 | 1 | 1.9442 | 1
101 | admin |  | 0 | Yes | 920 | 20 | 20 | House Fan | 7360 | unk | unk | 20 | 3
102 | 2nd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
103 | admin |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
104 | Specialist K-6 |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
105 | 2nd grade |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
106 | 2nd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
107 | 4th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
108 | 2nd |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
109 | 2nd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 336 | 7 | 7 | House Fan | 2688 | unk | unk | 20 | 3
110 | 2nd |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 210 | 4 | 4 | House Fan | 1680 | unk | unk | 20 | 3
- | Nurses Office |  | 0 | Yes | 264 | 6 | 6 | House Fan | 2112 | unk | unk | 20 | 3
201 | 4th |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
202 | 4th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
203 | 4th |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
204 | 4th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
205 | 3rd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
206 | 3rd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
207 | 3rd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
208 | 3rd |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
209 | 3rd |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
210 | 3rd |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
211 | small group instruction |  | 0 | Yes | 192 | 4 | 4 | House Fan | 1536 | unk | unk | 20 | 3
212 | counselor office |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | unk | unk | 20 | 3
- | Teachers Lounge |  | 0 | Yes | 253 | 5 | 5 | House Fan | 2024 | unk | unk | 20 | 3
301 | 6th |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
302 | 6th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
303 | 6th |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
304 | 5th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
305 | 5th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
306 | 6th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
307 | 6th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
308 | 5th |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
309 | 5th |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
310 | 5th |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
311 | 3rd fl computer room |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
312 | Small group instruction |  | 0 | Yes | 192 | 4 | 4 | House Fan | 1536 | unk | unk | 20 | 3
314 |  |  |  | Yes | 180 |  |  | House Fan | 1440 | unk | unk | 20 | 3
- | Speech Room |  | 0 | Yes | 180 | 4 | 4 | House Fan | 1440 | unk | unk | 20 | 3
b1 | music room |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
b2a | Small group instruction |  | 0 | Yes | 352 | 8 | 8 | House Fan | 2816 | unk | unk | 20 | 3
b2 | Small group instruction |  | 0 | Yes | 352 | 8 | 8 | House Fan | 2816 | unk | unk | 20 | 3
b3 | Small group instruction |  | 0 | Yes | 506 | 11 | 11 | House Fan | 4048 | unk | unk | 20 | 3
B4 | Computer Lab |  | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | unk | unk | 20 | 3
- | Gym/caf |  | 0 | Yes | 3432 | 78 | 78 | N/A | 27456 | unk | unk | 20 | 3
- | Kitchen |  | 0 | Yes | 609 | 13 | 13 | House Fan | 4872 | unk | unk | 20 | 3
- | 2nd Flr Counselor Office |  | 0 | Yes | 195 | 4 | 4 | House Fan | 1560 | unk | unk | 20 | 3
- | 3rd Flr Counselor Office |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | unk | unk | 20 | 3
Edwin Forrest Elementary School- Little School House | [9 empty] | unk | unk | unk | unk
P1 | - | 348 | 23 |  | 986 | 22 | 22 | Unit Ventilator | 7888 | 2.6471 | 1 | 2.6471 | 1
P2 | - | 303 | 20 |  | 986 | 22 | 20 | Unit Ventilator | 7888 | 2.3048 | 1 | 2.3048 | 1
P3 | - | 362 | 24 |  | 986 | 22 | 22 | Unit Ventilator | 7888 | 2.7535 | 1 | 2.7535 | 1
P4 | - | 327 | 21 |  | 986 | 22 | 21 | Unit Ventilator | 7888 | 2.4873 | 1 | 2.4873 | 1
P5 | - | 304 | 20 |  | 986 | 22 | 20 | Unit Ventilator | 7888 | 2.3124 | 1 | 2.3124 | 1
P6 | - | 390 | 26 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.6022 | 1 | 3.6022 | 1
P7 | - | 308 | 20 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 2.8448 | 1 | 2.8448 | 1
P8 | - | 308 | 20 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 2.8448 | 1 | 2.8448 | 1
P9 | - | 382 | 25 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.5283 | 1 | 3.5283 | 1
P10 | - | 312 | 20 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 2.8818 | 1 | 2.8818 | 1
P11 | - | 311 | 20 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 2.8725 | 1 | 2.8725 | 1
P12 | - | 316 | 21 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 2.9187 | 1 | 2.9187 | 1
P13 | - | 327 | 21 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.0203 | 1 | 3.0203 | 1
- | Administration and Corridors | 727 | 48 |  | 576 | 13 | 13 | AHU | 4608 | 9.4661 | 2 | 9.4661 | 2
- | Cafeteria | 78 | 5 | Yes | 2014 | 45 | 45 | AHU | 16112 | 0.29047 | 0 | 20.2905 | 3
- | Faculty Break Room | 312 | 20 |  | 210 | 4 | 4 | Unit Ventilator | 1680 | 11.1429 | 3 | 11.1429 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-08 | [8 empty] | unk | unk | unk | unk
School: | Fox Chase Elementary School | [8 empty] | unk | unk | unk | unk
| Fox Chase Farm | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Fox Chase Main Building | [9 empty] | unk | unk | unk | unk
101 | Classroom | 338 | 22 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.0179 | 1 | 3.0179 | 1
102 | Classroom | 316 | 21 |  | 1104 | 25 | 21 | Unit Ventilator | 8832 | 2.1467 | 1 | 2.1467 | 1
103 | Classroom | 291 | 19 |  | 989 | 22 | 19 | Unit Ventilator | 7912 | 2.2068 | 1 | 2.2068 | 1
104 | Classroom | 302 | 20 |  | 960 | 21 | 20 | Unit Ventilator | 7680 | 2.3594 | 1 | 2.3594 | 1
105 | Classroom | 312 | 20 |  | 984 | 22 | 20 | Unit Ventilator | 7872 | 2.378 | 1 | 2.378 | 1
105A | Office | 0 | 0 | Yes | 216 | 4 | 4 | Unit Ventilator | 1728 | 0 | 0 | 20 | 3
107 | Examing Room |  | 0 | Yes | 234 | 5 | 5 | N/A | 1872 | unk | unk | 20 | 3
107A | Office | 0 | 0 | Yes | 225 | 5 | 5 | N/A | 1800 | 0 | 0 | 20 | 3
108 | Classroom |  | 0 | Yes | 216 | 4 | 4 |  | 1728 | unk | unk | 20 | 3
109 | Classroom | 315 | 21 |  | 1035 | 23 | 21 | Unit Ventilator | 8280 | 2.2826 | 1 | 2.2826 | 1
110 | Classroom | 300 | 20 |  | 1032 | 23 | 20 | Unit Ventilator | 8256 | 2.1802 | 1 | 2.1802 | 1
111 | Classroom | 155 | 10 | Yes | 1012 | 23 | 23 | Unit Ventilator | 8096 | 1.1487 | 1 | 21.1487 | 3
112 | Classroom | 161 | 10 | Yes | 1081 | 24 | 24 | Unit Ventilator | 8648 | 1.117 | 1 | 21.117 | 3
201 | Classroom | 341 | 22 |  | 943 | 21 | 21 | Unit Ventilator | 7544 | 2.7121 | 1 | 2.7121 | 1
202 | Classroom | 382 | 25 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 3.194 | 1 | 3.194 | 1
203 | Classroom | 382 | 25 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 3.194 | 1 | 3.194 | 1
204 | Classroom | 237 | 15 |  | 462 | 10 | 10 | Unit Ventilator | 3696 | 3.8474 | 1 | 3.8474 | 1
205 | Classroom | 192 | 12 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | 1.5385 | 1 | 21.5385 | 3
206 | Classroom | 391 | 26 |  | 912 | 20 | 20 | Unit Ventilator | 7296 | 3.2155 | 1 | 3.2155 | 1
207 | Classroom | 0 | 0 | Yes | 943 | 21 | 21 | Unit Ventilator | 7544 | 0 | 0 | 20 | 3
208 | Classroom | 71 | 4 | Yes | 960 | 21 | 21 | Unit Ventilator | 7680 | 0.55469 | 0 | 20.5547 | 3
3340 | Ag Room |  | 0 | Yes | 1283 | 29 | 29 | Unit Ventilator | 10264 | unk | unk | 20 | 3
- | 1st Floor Teacher's Lounge | 0 | 0 |  | 336 | 7 | 0 | N/A | 2688 | 0 | 0 | 0 | 0
A-1 | Classroom | 281 | 18 |  | 836 | 19 | 18 | Unit Ventilator | 6688 | 2.5209 | 1 | 2.5209 | 1
A-2 | Classroom | 283 | 18 |  | 836 | 19 | 18 | Unit Ventilator | 6688 | 2.5389 | 1 | 2.5389 | 1
A-3 | Classroom | 319 | 21 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.8618 | 1 | 2.8618 | 1
A-4 | Classroom | 252 | 16 |  | 836 | 19 | 16 | Unit Ventilator | 6688 | 2.2608 | 1 | 2.2608 | 1
A-5 | Classroom | 241 | 16 |  | 836 | 19 | 16 | Unit Ventilator | 6688 | 2.1621 | 1 | 2.1621 | 1
A-6 | Classroom | 295 | 19 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.6465 | 1 | 2.6465 | 1
C-1 | Classroom |  | 0 | Yes | 1560 | 35 | 35 | N/A | 12480 | unk | unk | 20 | 3
C-4 | Classroom |  | 0 | Yes | 380 | 8 | 8 | N/A | 3040 | unk | unk | 20 | 3
- | Annex | 0 | 0 |  | 1283 | 29 | 0 | Unit Ventilator | 10264 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 |  | 4420 | 100 | 0 | AHU | 35360 | 0 | 0 | 0 | 0
Instrument Room | Stage Area |  | 0 | Yes | 228 | 5 | 5 |  | 1824 | unk | unk | 20 | 3
- | Cafeteria | 704 | 46 |  | 2340 | 53 | 46 | Unit Ventilator | 18720 | 2.2564 | 1 | 2.2564 | 1
- | Counselor | 0 | 0 |  | 230 | 5 | 0 | N/A | 1840 | 0 | 0 | 0 | 0
- | Dental Office | 0 | 0 | Yes | 208 | 4 | 4 | N/A | 1664 | 0 | 0 | 20 | 3
- | Examining Room | 0 | 0 |  | 234 | 5 | 0 | N/A | 1872 | 0 | 0 | 0 | 0
- | Gym | 0 | 0 |  | 5429 | 123 | 0 | AHU | 43432 | 0 | 0 | 0 | 0
- | Kitchen Storage | 296 | 19 |  | 260 | 5 | 5 | Unit Ventilator | 2080 | 8.5385 | 2 | 8.5385 | 2
- | Main Office | 0 | 0 | Yes | 226 | 5 | 5 | N/A | 1808 | 0 | 0 | 20 | 3
- | Music Room | 581 | 38 |  | 1400 | 31 | 31 | Unit Ventilator | 11200 | 3.1125 | 1 | 3.1125 | 1
- | Nurse | 0 | 0 | Yes | 234 | 5 | 5 | N/A | 1872 | 0 | 0 | 20 | 3
- | Principal | 0 | 0 | Yes | 234 | 5 | 5 | N/A | 1872 | 0 | 0 | 20 | 3
Fox Chase Farm | [9 empty] | unk | unk | unk | unk
- | Data Closet | 14 | 0 |  | 30 | 0 | 0 | AC | 240 | 3.5 | 1 | 3.5 | 1
- | Kitchen | 190 | 12 |  | 156 | 3 | 3 | AC | 1248 | 9.1346 | 2 | 9.1346 | 2
- | Men's Bathroom | 56 | 3 |  | 225 | 5 | 3 | AC | 1800 | 1.8667 | 1 | 1.8667 | 1
- | Teaching Area Classroom | 658 | 43 |  | 1692 | 38 | 38 | AC | 13536 | 2.9167 | 1 | 2.9167 | 1
- | Women's Bathroom | 55 | 3 |  | 225 | 5 | 3 | AC | 1800 | 1.8333 | 1 | 1.8333 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Anne Frank Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Retest | [7 empty] | unk | unk | unk | unk
School: | Anne Frank Elementary School- Little School House | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Frank Main Building | [9 empty] | unk | unk | unk | unk
100 | Classroom | 283 | 18 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.4566 | 1 | 22.4566 | 3
101 | Classroom | 284 | 18 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.4653 | 1 | 22.4653 | 3
102 | Classroom | 236 | 15 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.0486 | 1 | 22.0486 | 3
103 | Classroom | 260 | 17 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.2569 | 1 | 22.2569 | 3
104 | Classroom | 56 | 3 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0.48611 | 0 | 20.4861 | 3
106 | Classroom | 0 | 0 |  | 240 | 5 | 0 | Unit Ventilator | 1920 | 0 | 0 | 0 | 0
108 | Classroom | 191 | 12 | Yes | 456 | 10 | 10 | Unit Ventilator | 3648 | 3.1414 | 1 | 23.1414 | 3
109 | Classroom | 0 | 0 | Yes | 456 | 10 | 10 | Unit Ventilator | 3648 | 0 | 0 | 20 | 3
110 | Classroom | 305 | 20 | Yes | 1032 | 23 | 23 | Unit Ventilator | 8256 | 2.2166 | 1 | 22.2166 | 3
125 | Classroom | 348 | 23 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 3.8839 | 1 | 3.8839 | 1
- | Admin Office | 0 | 0 |  | 135 | 3 | 0 | Unit Ventilator | 1080 | 0 | 0 | 0 | 0
200 | Classroom | 283 | 18 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.4566 | 1 | 22.4566 | 3
201 | Library | 60 | 4 | Yes | 875 | 19 | 19 | Unit Ventilator | 7000 | 0.51429 | 0 | 20.5143 | 3
202 | Classroom | 293 | 19 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.5434 | 1 | 2.5434 | 1
203 | Classroom | 304 | 20 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.6389 | 1 | 2.6389 | 1
204 | Classroom | 322 | 21 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.7951 | 1 | 2.7951 | 1
205 | Classroom | 215 | 14 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.8663 | 1 | 21.8663 | 3
206 | Classroom | 205 | 13 |  | 240 | 5 | 5 | Unit Ventilator | 1920 | 6.4062 | 2 | 6.4062 | 2
207 | Classroom | 257 | 17 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.2309 | 1 | 22.2309 | 3
208 | Classroom | 299 | 19 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.5955 | 1 | 2.5955 | 1
209 | Classroom | 203 | 13 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.7622 | 1 | 21.7622 | 3
210 | Classroom | 225 | 15 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.9531 | 1 | 21.9531 | 3
211 | Classroom | 333 | 22 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.8906 | 1 | 2.8906 | 1
212 | Classroom | 153 | 10 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.3281 | 1 | 21.3281 | 3
213 | Classroom | 226 | 15 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.9618 | 1 | 21.9618 | 3
214 | Classroom |  | 0 | Yes | 864 | 19 | 19 |  | 6912 | unk | unk | 20 | 3
215 | Classroom | 284 | 18 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.4653 | 1 | 22.4653 | 3
- | Library | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0 | 20 | 3
300 | Classroom | 241 | 16 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.092 | 1 | 22.092 | 3
301 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0 | 20 | 3
303 | Classroom | 185 | 12 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.6059 | 1 | 21.6059 | 3
304 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0 | 20 | 3
305 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 240 | 5 | 5 | Unit Ventilator | 1920 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0 | 20 | 3
308 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0 | 20 | 3
310 | Classroom | 127 | 8 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 1.1024 | 1 | 21.1024 | 3
311 | Classroom | 42 | 2 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0.36458 | 0 | 20.3646 | 3
312 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0 | 20 | 3
313 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0 | 20 | 3
315 | Classroom | 0 | 0 | Yes | 864 | 19 | 19 | Unit Ventilator | 6912 | 0 | 0 | 20 | 3
| Auditorium | 0 | 0 |  | 3180 | 72 | 0 |  | 25440 | 0 | 0 | 0 | 0
| Cafeteria | 0 | 0 | Yes | 2720 | 61 | 61 |  | 21760 | 0 | 0 | 20 | 3
| Gymnasium | 0 | 0 | Yes | 3657 | 83 | 83 |  | 29256 | 0 | 0 | 20 | 3
| Gymnasium Office |  | 0 |  | 165 | 3 | 0 |  | 1320 | unk | unk | unk | unk
- | Counselor Office | 0 | 0 | Yes | 132 | 3 | 3 | NA | 1056 | 0 | 0 | 20 | 3
- | Main Office | 60 | 4 | Yes | 951 | 21 | 21 | Unit Ventilator | 7608 | 0.47319 | 0 | 20.4732 | 3
- | Nurses Office | 0 | 0 | Yes | 304 | 6 | 6 | NA | 2432 | 0 | 0 | 20 | 3
- | Principals Office | 0 | 0 | Yes | 210 | 4 | 4 | NA | 1680 | 0 | 0 | 20 | 3
- | Vice Principals Office | 0 | 0 | Yes | 72 | 1 | 1 | NA | 576 | 0 | 0 | 20 | 3
Frank LSH | [9 empty] | unk | unk | unk | unk
1 | Classroom | 931 | 62 |  | 928 | 21 | 21 | BCU | 7424 | 7.5242 | 2 | 7.5242 | 2
2 | Classroom | 595 | 39 |  | 928 | 21 | 21 | BCU | 7424 | 4.8087 | 2 | 4.8087 | 2
3 | Classroom | 945 | 63 |  | 928 | 21 | 21 | BCU | 7424 | 7.6374 | 2 | 7.6374 | 2
4 | Classroom | 610 | 40 |  | 928 | 21 | 21 | BCU | 7424 | 4.93 | 2 | 4.93 | 2
5 | Classroom | 322 | 21 |  | 928 | 21 | 21 | BCU | 7424 | 2.6024 | 1 | 2.6024 | 1
6 | Classroom | 307 | 20 | Yes | 928 | 21 | 21 | BCU | 7424 | 2.4811 | 1 | 22.4811 | 3
7 | Classroom | 310 | 20 | Yes | 928 | 21 | 21 | BCU | 7424 | 2.5054 | 1 | 22.5054 | 3
8 | Classroom | 305 | 20 | Yes | 928 | 21 | 21 | BCU | 7424 | 2.465 | 1 | 22.465 | 3
9 | Classroom | 370 | 24 |  | 928 | 21 | 21 | BCU | 7424 | 2.9903 | 1 | 2.9903 | 1
10 | Classroom | 329 | 21 |  | 928 | 21 | 21 | BCU | 7424 | 2.6589 | 1 | 2.6589 | 1
11 | Classroom | 396 | 26 |  | 928 | 21 | 21 | BCU | 7424 | 3.2004 | 1 | 3.2004 | 1
12 | Classroom | 319 | 21 |  | 928 | 21 | 21 | BCU | 7424 | 2.5781 | 1 | 2.5781 | 1
- | Bathrooms, Corridor and Main Entrance | 284 | 18 |  | 225 | 5 | 5 | FCU | 1800 | 9.4667 | 2 | 9.4667 | 2
- | Corner Facilities/Guidance Office | 0 | 0 |  | 196 | 4 | 0 | FCU | 1568 | 0 | 0 | 0 | 0
- | Counselor Office | 0 | 0 | Yes | 100 | 2 | 2 | FCU | 800 | 0 | 0 | 20 | 3
- | Janitor Close and Storage Rooms | 262 | 17 |  | 24 | 0 | 0 | FCU | 192 | 81.875 | 5 | 81.875 | 5
- | Main Office | 587 | 39 |  | 315 | 7 | 7 | FCU | 2520 | 13.9762 | 3 | 13.9762 | 3
- | Cafeteria | 922 | 61 |  | 1696 | 38 | 38 | BCU | 13568 | 4.0772 | 2 | 4.0772 | 2
- | Art Teacher Office | 102 | 6 |  | 100 | 2 | 2 | BCU | 800 | 7.65 | 2 | 7.65 | 2
- | ESL Teacher Office | 110 | 7 |  | 100 | 2 | 2 | BCU | 800 | 8.25 | 2 | 8.25 | 2
- | ESL Room | 241 | 16 |  | 80 | 1 | 1 | BCU | 640 | 22.5938 | 3 | 22.5938 | 3
Frank Annex | [9 empty] | unk | unk | unk | unk
7 | Classroom | 36 | 2 | Yes | 1080 | 24 | 24 | Unit Ventilator | 8640 | 0.25 | 0 | 20.25 | 3
8 | Classroom | 235 | 15 | Yes | 1080 | 24 | 24 | Unit Ventilator | 8640 | 1.6319 | 1 | 21.6319 | 3
- | gang girlsnboys |  | 0 |  | 480 | 10 | 0 | N/A | 3840 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-17 | [8 empty] | unk | unk | unk | unk
School: | Frankford High School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
9 | Classroom | 122 | 8 |  | 1836 | 41 | 8 | Unit Ventilator | 14688 | 0.49837 | 0 | 0.49837 | 0
11 | Classroom | 0 | 0 |  | 2011 | 45 | 0 | Unit Ventilator | 16088 | 0 | 0 | 0 | 0
12 | Classroom | 0 | 0 |  | 2011 | 45 | 0 | Unit Ventilator | 16088 | 0 | 0 | 0 | 0
14 | Classroom | 167 | 11 |  | 812 | 18 | 11 | Unit Ventilator | 6496 | 1.5425 | 1 | 1.5425 | 1
15-14 | Classroom | 0 | 0 |  | N/A | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
15A | Classroom | 107 | 7 |  | 812 | 18 | 7 | Unit Ventilator | 6496 | 0.9883 | 0 | 0.9883 | 0
16 | Classroom | 0 | 0 |  | 476 | 10 | 0 | Unit Ventilator | 3808 | 0 | 0 | 0 | 0
17 | Classroom | 0 | 0 |  | 952 | 21 | 0 | Unit Ventilator | 7616 | 0 | 0 | 0 | 0
18 | Classroom | 76 | 5 |  | 884 | 20 | 5 | Unit Ventilator | 7072 | 0.6448 | 0 | 0.6448 | 0
19 | Classroom | 55 | 3 |  | 576 | 13 | 3 | Unit Ventilator | 4608 | 0.71615 | 0 | 0.71615 | 0
20 | Classroom | 0 | 0 |  | 1023 | 23 | 0 | Unit Ventilator | 8184 | 0 | 0 | 0 | 0
124 | Classroom | 210 | 14 |  | 1702 | 38 | 14 | Unit Ventilator | 13616 | 0.92538 | 0 | 0.92538 | 0
222 | Classroom | 80 | 5 |  | 889 | 20 | 5 | Unit Ventilator | 7112 | 0.67492 | 0 | 0.67492 | 0
223 | Classroom | 163 | 10 |  | 991 | 22 | 10 | Unit Ventilator | 7928 | 1.2336 | 1 | 1.2336 | 1
224 | Classroom | 80 | 5 |  | 991 | 22 | 5 | Unit Ventilator | 7928 | 0.60545 | 0 | 0.60545 | 0
225 | Classroom | 50 | 3 |  | 1005 | 22 | 3 | Unit Ventilator | 8040 | 0.37313 | 0 | 0.37313 | 0
226 | Classroom | 149 | 9 |  | 991 | 22 | 9 | Unit Ventilator | 7928 | 1.1276 | 1 | 1.1276 | 1
227 | Classroom | 128 | 8 |  | 864 | 19 | 8 | Unit Ventilator | 6912 | 1.1111 | 1 | 1.1111 | 1
228 | Classroom | 255 | 17 |  | 899 | 20 | 17 | Unit Ventilator | 7192 | 2.1274 | 1 | 2.1274 | 1
229 | Classroom | 0 | 0 |  | 462 | 10 | 0 | Unit Ventilator | 3696 | 0 | 0 | 0 | 0
230 | Classroom | 181 | 12 |  | 1001 | 22 | 12 | Unit Ventilator | 8008 | 1.3561 | 1 | 1.3561 | 1
231A | Classroom | 286 | 19 |  | 986 | 22 | 19 | Unit Ventilator | 7888 | 2.1755 | 1 | 2.1755 | 1
232A | Classroom | 80 | 5 |  | 1048 | 23 | 5 | Unit Ventilator | 8384 | 0.57252 | 0 | 0.57252 | 0
233 | Classroom | 40 | 2 |  | 1120 | 25 | 2 | Unit Ventilator | 8960 | 0.26786 | 0 | 0.26786 | 0
326 | Classroom | 91 | 6 |  | 775 | 17 | 6 | Unit Ventilator | 6200 | 0.88065 | 0 | 0.88065 | 0
327 | Classroom | 48 | 3 |  | 775 | 17 | 3 | Unit Ventilator | 6200 | 0.46452 | 0 | 0.46452 | 0
330-331 | Classroom | 166 | 11 |  | 969 | 22 | 11 | Unit Ventilator | 7752 | 1.2848 | 1 | 1.2848 | 1
332 | Classroom | 84 | 5 |  | 1505 | 34 | 5 | Unit Ventilator | 12040 | 0.4186 | 0 | 0.4186 | 0
333 | Classroom | 0 | 0 |  | 1505 | 34 | 0 | Unit Ventilator | 12040 | 0 | 0 | 0 | 0
335 | Classroom | 0 | 0 |  | 1120 | 25 | 0 | Unit Ventilator | 8960 | 0 | 0 | 0 | 0
- | IMC | 264 | 17 |  | 5398 | 122 | 17 | Unit Ventilator | 43184 | 0.3668 | 0 | 0.3668 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-21 | [8 empty] | unk | unk | unk | unk
School: | Benjamin Franklin Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Devine 2nd Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Basement Boy's Restroom | 0 | 0 |  | 234 | 5 | 0 | AHU | 1872 | 0 | 0 | 0 | 0
- | Basement Girl's Restroom | 0 | 0 |  | 234 | 5 | 0 | AHU | 1872 | 0 | 0 | 0 | 0
- | 1st Floor Boy's Restroom | 27 | 1 |  | 234 | 5 | 1 | AHU | 1872 | 0.86538 | 0 | 0.86538 | 0
- | 1st Floor Girl's Restroom | 40 | 2 |  | 234 | 5 | 2 | AHU | 1872 | 1.2821 | 1 | 1.2821 | 1
- | 2nd Floor Girl's Restroom | 28 | 1 |  | 234 | 5 | 1 | AHU | 1872 | 0.89744 | 0 | 0.89744 | 0
- | 2nd Floor Boy's Restroom | 40 | 2 |  | 234 | 5 | 2 | AHU | 1872 | 1.2821 | 1 | 1.2821 | 1
1 | Classroom |  | 0 | Yes | 304 | 6 | 6 | Unit Ventilator | 2432 | unk | unk | 20 | 3
1B | Classroom |  | 0 | Yes | 667 | 15 |  |  | 5336 | unk | unk | 20 | 3
6 | Classroom | 350 | 23 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.3654 | 1 | 3.3654 | 1
7 | Cafeteria | 1972 | 131 |  | 2800 | 63 | 63 | AHU | 22400 | 5.2821 | 2 | 5.2821 | 2
8 | Classroom | 299 | 19 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.875 | 1 | 2.875 | 1
- | Kitchen | 1585 | 105 |  | 1023 | 23 | 23 | AHU | 8184 | 11.6202 | 3 | 11.6202 | 3
- | Kitchen Office | 225 | 15 |  | 80 | 1 | 1 | AHU | 640 | 21.0938 | 3 | 21.0938 | 3
101 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
104 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | unk | unk | 20 | 3
105 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | unk | unk | 20 | 3
106 | Classroom |  | 0 | Yes | 650 | 14 | 14 |  | 5200 | unk | unk | 20 | 3
107 | Classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | unk | unk | unk | unk
110 | Classroom | 352 | 23 |  | 780 | 17 | 17 | House Fan | 6240 | 3.3846 | 1 | 3.3846 | 1
111 | Classroom | 321 | 21 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.0865 | 1 | 3.0865 | 1
112 | Classroom | 300 | 20 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.8846 | 1 | 2.8846 | 1
113 | Classroom | 312 | 20 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3 | 1 | 3 | 1
114 | Classroom | 410 | 27 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.9423 | 1 | 3.9423 | 1
115 | Classroom | 346 | 23 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.3269 | 1 | 3.3269 | 1
116 | Asst Principals Office | 352 | 23 |  | 207 | 4 | 4 | Unit Ventilator | 1656 | 12.7536 | 3 | 12.7536 | 3
117 | Classroom | 332 | 22 |  | 609 | 13 | 13 | Unit Ventilator | 4872 | 4.0887 | 2 | 4.0887 | 2
201 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
204 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | unk | unk | 20 | 3
206 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | unk | unk | 20 | 3
207 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | unk | unk | 20 | 3
208 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
209 | Library | 568 | 37 | Yes | 1600 | 36 | 36 | Unit Ventilator | 12800 | 2.6625 | 1 | 22.6625 | 3
210 | Trs Lounge | 330 | 22 |  | 380 | 8 | 8 | Unit Ventilator | 3040 | 6.5132 | 2 | 6.5132 | 2
212 | TECH LAB | 487 | 32 |  | 1600 | 36 | 32 | Unit Ventilator | 12800 | 2.2828 | 1 | 2.2828 | 1
214 | Classroom | 305 | 20 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.9327 | 1 | 2.9327 | 1
215 | Classroom | 325 | 21 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.125 | 1 | 3.125 | 1
216 | Classroom | 325 | 21 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.125 | 1 | 3.125 | 1
217 | Classroom | 287 | 19 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.7596 | 1 | 2.7596 | 1
218 | Classroom | 323 | 21 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.1058 | 1 | 3.1058 | 1
219 | Classroom | 291 | 19 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.7981 | 1 | 2.7981 | 1
220 | Counselor's Office | 287 | 19 |  | 207 | 4 | 4 | Unit Ventilator | 1656 | 10.3986 | 3 | 10.3986 | 3
221 | Classroom | 314 | 20 |  | 605 | 13 | 13 | Unit Ventilator | 4840 | 3.8926 | 1 | 3.8926 | 1
- | Faculty Lounge | 0 | 0 |  | 160 | 3 | 0 | Unit Ventilator | 1280 | 0 | 0 | 0 | 0
- | Nurses Office |  | 0 | Yes | 132 | 3 | 3 |  | 1056 | unk | unk | 20 | 3
- | Psychology Office | 33 | 2 |  | 90 | 2 | 2 | Unit Ventilator | 720 | 2.75 | 1 | 2.75 | 1
- | Main Office |  | 0 | Yes | 220 | 5 | 5 |  | 1760 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-19 | [8 empty] | unk | unk | unk | unk
School: | Benjamin Franklin High School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Weight room | 63 | 4 |  | 713 | 16 | 4 | HV+ AHU | 5704 | 0.66269 | 0 | 0.66269 | 0
2 | Weight room | 0 | 0 |  | 775 | 17 | 0 | HV | 6200 | 0 | 0 | 0 | 0
3 | Weight room | 0 | 0 |  | 1632 | 37 | 0 | HV | 13056 | 0 | 0 | 0 | 0
4 | Welding | 9254 | 616 |  | 2176 | 49 | 49 | MUA | 17408 | 31.8957 | 4 | 31.8957 | 4
4A | Classroom | 280 | 18 |  | 640 | 14 | 14 | AC | 5120 | 3.2812 | 1 | 3.2812 | 1
6 | Classroom | 0 | 0 | Yes | 2655 | 60 | 60 | AHU | 21240 | 0 | 0 | 20 | 3
7 | Classroom | 0 | 0 |  | 216 | 4 | 0 | AHU | 1728 | 0 | 0 | 0 | 0
8 | Classroom | 0 | 0 |  | 588 | 13 | 0 | AHU | 4704 | 0 | 0 | 0 | 0
9 | Classroom | 0 | 0 |  | 621 | 14 | 0 | AHU | 4968 | 0 | 0 | 0 | 0
10 | Machine Shop | 810 | 54 |  | 2961 | 67 | 54 | HV | 23688 | 2.0517 | 1 | 2.0517 | 1
11 | Classroom | 176 | 11 |  | 1740 | 39 | 11 | AC | 13920 | 0.75862 | 0 | 0.75862 | 0
12 | Classroom | 842 | 56 |  | 1581 | 35 | 35 | HV | 12648 | 3.9943 | 1 | 3.9943 | 1
13 | Classroom | 175 | 11 |  | 1239 | 28 | 11 | AC | 9912 | 1.0593 | 1 | 1.0593 | 1
13A | Classroom | 93 | 6 |  | 552 | 12 | 6 | AC | 4416 | 1.2636 | 1 | 1.2636 | 1
14 | Classroom | 136 | 9 |  | 756 | 17 | 9 | AC | 6048 | 1.3492 | 1 | 1.3492 | 1
15 | Classroom | 155 | 10 |  | 912 | 20 | 10 | AC | 7296 | 1.2747 | 1 | 1.2747 | 1
15A | Practice Room | 77 | 5 |  | 77 | 1 | 1 | HV | 616 | 7.5 | 2 | 7.5 | 2
15B | Practice Room | 188 | 12 |  | 77 | 1 | 1 | HV | 616 | 18.3117 | 3 | 18.3117 | 3
15C | Practice Room | 143 | 9 |  | 77 | 1 | 1 | HV | 616 | 13.9286 | 3 | 13.9286 | 3
15D | Music Office | 142 | 9 |  | 180 | 4 | 4 | HV | 1440 | 5.9167 | 2 | 5.9167 | 2
16 | Lecture Hall | 2049 | 136 |  | 2068 | 47 | 47 | HV | 16544 | 7.4311 | 2 | 7.4311 | 2
17 | Lecture Hall | 387 | 25 |  | 2280 | 51 | 25 | HV | 18240 | 1.273 | 1 | 1.273 | 1
18 | Classroom | 803 | 53 |  | 1080 | 24 | 24 | AC | 8640 | 5.5764 | 2 | 5.5764 | 2
19 | Classroom | 781 | 52 |  | 1344 | 30 | 30 | AC | 10752 | 4.3583 | 2 | 4.3583 | 2
20 | Classroom | 635 | 42 |  | 828 | 18 | 18 | AC | 6624 | 5.7518 | 2 | 5.7518 | 2
100 | Classroom | 280 | 18 |  | 775 | 17 | 17 | UV | 6200 | 2.7097 | 1 | 2.7097 | 1
102 | Classroom | 382 | 25 |  | 961 | 21 | 21 | UV | 7688 | 2.9813 | 1 | 2.9813 | 1
110 | Room | 0 | 0 |  | 195 | 4 | 0 | FC | 1560 | 0 | 0 | 0 | 0
111A | Room | 0 | 0 |  | 104 | 2 | 0 | FC | 832 | 0 | 0 | 0 | 0
113 | Room | 0 | 0 |  | 315 | 7 | 0 | FC | 2520 | 0 | 0 | 0 | 0
115 | Room | 0 | 0 |  | 352 | 8 | 0 | FC | 2816 | 0 | 0 | 0 | 0
116 | Room | 0 | 0 |  | 196 | 4 | 0 | FC | 1568 | 0 | 0 | 0 | 0
150 | Kitchen | 0 | 0 |  | 1955 | 44 | 0 | RTU | 15640 | 0 | 0 | 0 | 0
152 | Cafeteria | 0 | 0 |  | 3363 | 76 | 0 | RTU | 26904 | 0 | 0 | 0 | 0
200 | Living Room | 140 | 9 |  | 819 | 18 | 9 | UV | 6552 | 1.2821 | 1 | 1.2821 | 1
201 | Classroom | 217 | 14 |  | 792 | 18 | 14 | UV | 6336 | 2.0549 | 1 | 2.0549 | 1
202 | Office-A | 201 | 13 |  | 600 | 13 | 13 | UV | 4800 | 2.5125 | 1 | 2.5125 | 1
202 | Office-B | 171 | 11 |  | 396 | 9 | 9 | UV | 3168 | 3.2386 | 1 | 3.2386 | 1
204 | Principal Office | 41 | 2 |  | 180 | 4 | 2 | OAS-1A & OAS-1B | 1440 | 1.7083 | 1 | 1.7083 | 1
206 | Co-Principal | 40 | 2 |  | 120 | 2 | 2 | OAS-1A & OAS-1B | 960 | 2.5 | 1 | 2.5 | 1
207 | Classroom | 257 | 17 |  | 792 | 18 | 17 | UV | 6336 | 2.4337 | 1 | 2.4337 | 1
209 | Storage | 189 | 12 |  | 165 | 3 | 3 | UV | 1320 | 8.5909 | 2 | 8.5909 | 2
209B | Office | 287 | 19 |  | 180 | 4 | 4 | UV | 1440 | 11.9583 | 3 | 11.9583 | 3
211 | Classroom | 358 | 23 |  | 713 | 16 | 16 | UV | 5704 | 3.7658 | 1 | 3.7658 | 1
212 | Work Room | 49 | 3 |  | 297 | 6 | 3 | OAS-1A & OAS-1B | 2376 | 1.2374 | 1 | 1.2374 | 1
214 | Office | 57 | 3 |  | 121 | 2 | 2 | OAS-1A & OAS-1B | 968 | 3.5331 | 1 | 3.5331 | 1
215 | Classroom | 295 | 19 |  | 806 | 18 | 18 | UV | 6448 | 2.745 | 1 | 2.745 | 1
216 | Conference | 44 | 2 |  | 72 | 1 | 1 | OAS-1A & OAS-1B | 576 | 4.5833 | 2 | 4.5833 | 2
217 | Learning Lounge | 263 | 17 |  | 572 | 13 | 13 | UV | 4576 | 3.4484 | 1 | 3.4484 | 1
218 | College Office | 50 | 3 |  | 132 | 3 | 3 | OAS-1A & OAS-1B | 1056 | 2.8409 | 1 | 2.8409 | 1
220 | College | 49 | 3 |  | 120 | 2 | 2 | OAS-1A & OAS-1B | 960 | 3.0625 | 1 | 3.0625 | 1
222 | Health Suite | 45 | 3 |  | 256 | 5 | 3 | OAS-1A & OAS-1B | 2048 | 1.3184 | 1 | 1.3184 | 1
222A | Nurse Office | 50 | 3 |  | 108 | 2 | 2 | OAS-1A & OAS-1B | 864 | 3.4722 | 1 | 3.4722 | 1
222B | Exam | 48 | 3 |  | 99 | 2 | 2 | OAS-1A & OAS-1B | 792 | 3.6364 | 1 | 3.6364 | 1
223A | Dining | 856 | 57 |  | 1760 | 40 | 40 | UV | 14080 | 3.6477 | 1 | 3.6477 | 1
229 | Classroom |  | 0 | Yes | 589 | 13 | 13 |  | 4712 | unk | unk | 20 | 3
231 | Office | 150 | 10 |  | 210 | 4 | 4 | UV | 1680 | 5.3571 | 2 | 5.3571 | 2
232 | Health Suite | 221 | 14 |  | 464 | 10 | 10 | OAS-1A & OAS-1B | 3712 | 3.5722 | 1 | 3.5722 | 1
232B | Storage | 0 | 0 |  | 45 | 1 | 0 | OAS-1A & OAS-1B | 360 | 0 | 0 | 0 | 0
232C | Nurse Health | 0 | 0 |  | 99 | 2 | 0 | AC | 792 | 0 | 0 | 0 | 0
232D | Nurse Health | 0 | 0 |  | 106 | 2 | 0 | AC | 848 | 0 | 0 | 0 | 0
238 | Conference | 119 | 7 |  | 228 | 5 | 5 | OAS-1A & OAS-1B | 1824 | 3.9145 | 1 | 3.9145 | 1
240 | Office | 131 | 8 |  | 143 | 3 | 3 | OAS-1A & OAS-1B | 1144 | 6.8706 | 2 | 6.8706 | 2
242 | Storage | 146 | 9 |  | 71 | 1 | 1 | OAS-1A & OAS-1B | 568 | 15.4225 | 3 | 15.4225 | 3
244 | Office | 124 | 8 |  | 143 | 3 | 3 | OAS-1A & OAS-1B | 1144 | 6.5035 | 2 | 6.5035 | 2
246 | Open Work Area | 119 | 7 |  | 252 | 5 | 5 | OAS-1A & OAS-1B | 2016 | 3.5417 | 1 | 3.5417 | 1
248 | Office | 135 | 9 |  | 143 | 3 | 3 | OAS-1A & OAS-1B | 1144 | 7.0804 | 2 | 7.0804 | 2
250 | Main Office | 408 | 27 |  | 675 | 15 | 15 | UV | 5400 | 4.5333 | 2 | 4.5333 | 2
300 | Collaboration | 25 | 1 |  | 264 | 6 | 1 | OAS-1A & OAS-1B | 2112 | 0.71023 | 0 | 0.71023 | 0
301 | Classroom | 192 | 12 |  | 792 | 18 | 12 | UV | 6336 | 1.8182 | 1 | 1.8182 | 1
302 | Classroom | 233 | 15 |  | 900 | 20 | 15 | UV | 7200 | 1.9417 | 1 | 1.9417 | 1
304 | Classroom | 255 | 17 |  | 851 | 19 | 17 | UV | 6808 | 2.2474 | 1 | 2.2474 | 1
306 | Classroom | 218 | 14 |  | 897 | 20 | 14 | UV | 7176 | 1.8227 | 1 | 1.8227 | 1
308 | Classroom | 206 | 13 |  | 759 | 17 | 13 | UV | 6072 | 2.0356 | 1 | 2.0356 | 1
309 | Classroom | 308 | 20 |  | 736 | 16 | 16 | UV | 5888 | 3.1386 | 1 | 3.1386 | 1
311 | Classroom | 301 | 20 |  | 576 | 13 | 13 | UV | 4608 | 3.9193 | 1 | 3.9193 | 1
315 | Classroom | 138 | 9 |  | 759 | 17 | 9 | UV | 6072 | 1.3636 | 1 | 1.3636 | 1
316 | Classroom | 482 | 32 |  | 759 | 17 | 17 | UV | 6072 | 4.7628 | 2 | 4.7628 | 2
317 | Classroom | 182 | 12 | Yes | 1173 | 26 | 26 | UV | 9384 | 1.1637 | 1 | 21.1637 | 3
318 | Classroom | 146 | 9 | Yes | 713 | 16 | 16 | UV | 5704 | 1.5358 | 1 | 21.5358 | 3
319 | Classroom | 209 | 13 |  | 736 | 16 | 13 | UV | 5888 | 2.1298 | 1 | 2.1298 | 1
320 | Classroom | 165 | 11 |  | 736 | 16 | 11 | UV | 5888 | 1.6814 | 1 | 1.6814 | 1
321A | Office | 96 | 6 |  | 154 | 3 | 3 | UV | 1232 | 4.6753 | 2 | 4.6753 | 2
321B | Storage | 289 | 19 |  | 154 | 3 | 3 | UV | 1232 | 14.0747 | 3 | 14.0747 | 3
322 | Classroom | 154 | 10 | Yes | 736 | 16 | 16 | UV | 5888 | 1.5693 | 1 | 21.5693 | 3
324 | Classroom | 0 | 0 |  | 558 | 12 | 0 | UV | 4464 | 0 | 0 | 0 | 0
326 | Classroom | 225 | 15 |  | 900 | 20 | 15 | UV | 7200 | 1.875 | 1 | 1.875 | 1
327 | Office | 236 | 15 |  | 240 | 5 | 5 | UV | 1920 | 7.375 | 2 | 7.375 | 2
328 | LSS Community Rm | 43 | 2 |  | 288 | 6 | 2 | OAS-1A & OAS-1B | 2304 | 1.1198 | 1 | 1.1198 | 1
329 | Classroom | 224 | 14 |  | 936 | 21 | 14 | UV | 7488 | 1.7949 | 1 | 1.7949 | 1
400 | Collaboration | 0 | 0 |  | 264 | 6 | 0 | OAS-1A & OAS-1B | 2112 | 0 | 0 | 0 | 0
401 | Classroom | 0 | 0 |  | 759 | 17 | 0 | UV | 6072 | 0 | 0 | 0 | 0
402 | Classroom | 264 | 17 |  | 1311 | 29 | 17 | UV | 10488 | 1.5103 | 1 | 1.5103 | 1
404 | Classroom | 250 | 16 |  | 345 | 7 | 7 | UV | 2760 | 5.4348 | 2 | 5.4348 | 2
406 | Classroom | 330 | 22 |  | 1311 | 29 | 22 | UV | 10488 | 1.8879 | 1 | 1.8879 | 1
407 | Classroom | 258 | 17 |  | 736 | 16 | 16 | UV | 5888 | 2.6291 | 1 | 2.6291 | 1
409 | Classroom | 97 | 6 |  | 736 | 16 | 6 | UV | 5888 | 0.98845 | 0 | 0.98845 | 0
411 | Classroom | 648 | 43 |  | 552 | 12 | 12 | UV | 4416 | 8.8043 | 2 | 8.8043 | 2
415 | Classroom | 178 | 11 |  | 759 | 17 | 11 | UV | 6072 | 1.7589 | 1 | 1.7589 | 1
416 | Classroom | 155 | 10 |  | 851 | 19 | 10 | UV | 6808 | 1.366 | 1 | 1.366 | 1
417 | Classroom | 3 | 0 |  | 713 | 16 | 0 | UV | 5704 | 0.031557 | 0 | 0.031557 | 0
418 | Classroom | 182 | 12 |  | 851 | 19 | 12 | UV | 6808 | 1.604 | 1 | 1.604 | 1
419 | Classroom | 219 | 14 |  | 736 | 16 | 14 | UV | 5888 | 2.2317 | 1 | 2.2317 | 1
420 | Classroom | 162 | 10 |  | 828 | 18 | 10 | UV | 6624 | 1.4674 | 1 | 1.4674 | 1
421 | Office | 86 | 5 |  | 529 | 12 | 5 | UV | 4232 | 1.2193 | 1 | 1.2193 | 1
422 | Classroom | 132 | 8 |  | 828 | 18 | 8 | UV | 6624 | 1.1957 | 1 | 1.1957 | 1
424 | Office | 158 | 10 |  | 99 | 2 | 2 | UV | 792 | 11.9697 | 3 | 11.9697 | 3
426 | Classroom | 73 | 4 |  | 900 | 20 | 4 | UV | 7200 | 0.60833 | 0 | 0.60833 | 0
427 | Classroom | 339 | 22 |  | 1200 | 27 | 22 | UV | 9600 | 2.1187 | 1 | 2.1187 | 1
428 | Collaboration | 62 | 4 |  | 444 | 10 | 4 | OAS-1A & OAS-1B | 3552 | 1.0473 | 1 | 1.0473 | 1
500 | Collaboration | 22 | 1 |  | 322 | 7 | 1 | OAS-1A & OAS-1B | 2576 | 0.51242 | 0 | 0.51242 | 0
501 | Classroom | 201 | 13 |  | 825 | 18 | 13 | UV | 6600 | 1.8273 | 1 | 1.8273 | 1
502 | Classroom | 681 | 45 |  | 1380 | 31 | 31 | UV | 11040 | 3.7011 | 1 | 3.7011 | 1
504 | Storage | 216 | 14 |  | 352 | 8 | 8 | UV | 2816 | 4.6023 | 2 | 4.6023 | 2
506 | Classroom | 477 | 31 |  | 1357 | 30 | 30 | UV | 10856 | 2.6363 | 1 | 2.6363 | 1
507 | Classroom | 155 | 10 |  | 851 | 19 | 10 | UV | 6808 | 1.366 | 1 | 1.366 | 1
509 | Classroom | 194 | 12 |  | 805 | 18 | 12 | UV | 6440 | 1.8075 | 1 | 1.8075 | 1
515 | Classroom | 269 | 17 |  | 920 | 20 | 17 | UV | 7360 | 2.1929 | 1 | 2.1929 | 1
516 | Classroom | 162 | 10 |  | 1012 | 23 | 10 | UV | 8096 | 1.2006 | 1 | 1.2006 | 1
517 | Classroom | 647 | 43 |  | 943 | 21 | 21 | UV | 7544 | 5.1458 | 2 | 5.1458 | 2
518 | Classroom | 73 | 4 |  | 851 | 19 | 4 | UV | 6808 | 0.64336 | 0 | 0.64336 | 0
519 | Classroom | 201 | 13 |  | 693 | 15 | 13 | UV | 5544 | 2.1753 | 1 | 2.1753 | 1
520 | Classroom | 515 | 34 |  | 858 | 19 | 19 | UV | 6864 | 4.5017 | 2 | 4.5017 | 2
522A | Office | 21 | 1 |  | 100 | 2 | 1 | OAS-1A & OAS-1B | 800 | 1.575 | 1 | 1.575 | 1
523 | Classroom | 950 | 63 |  | 1344 | 30 | 30 | UV | 10752 | 5.3013 | 2 | 5.3013 | 2
524 | Staff Lounge | 527 | 35 |  | 375 | 8 | 8 | UV | 3000 | 10.54 | 3 | 10.54 | 3
526 | Classroom | 1235 | 82 |  | 1175 | 26 | 26 | UV | 9400 | 7.883 | 2 | 7.883 | 2
601 | Classroom | 231 | 15 |  | 936 | 21 | 15 | UV | 7488 | 1.851 | 1 | 1.851 | 1
602 | Classroom | 325 | 21 |  | 920 | 20 | 20 | UV | 7360 | 2.6495 | 1 | 2.6495 | 1
603 | Production Studio | 25 | 1 |  | 160 | 3 | 1 | OAS-1A & OAS-1B | 1280 | 1.1719 | 1 | 1.1719 | 1
603A | Control Rm | 25 | 1 |  | 96 | 2 | 1 | OAS-1A & OAS-1B | 768 | 1.9531 | 1 | 1.9531 | 1
604 | Classroom | 568 | 37 |  | 460 | 10 | 10 | UV | 3680 | 9.2609 | 2 | 9.2609 | 2
605 | Classroom | 609 | 40 |  | 1152 | 26 | 26 | UV | 9216 | 3.9648 | 1 | 3.9648 | 1
606 | Classroom | 140 | 9 |  | 621 | 14 | 9 | UV | 4968 | 1.6908 | 1 | 1.6908 | 1
609 | Classroom | 614 | 40 |  | 900 | 20 | 20 | UV | 7200 | 5.1167 | 2 | 5.1167 | 2
611 | Classroom | 256 | 17 |  | 900 | 20 | 17 | UV | 7200 | 2.1333 | 1 | 2.1333 | 1
612 | Classroom | 208 | 13 |  | 714 | 16 | 13 | UV | 5712 | 2.1849 | 1 | 2.1849 | 1
613 | Classroom | 564 | 37 |  | 792 | 18 | 18 | UV | 6336 | 5.3409 | 2 | 5.3409 | 2
614 | Classroom | 290 | 19 |  | 756 | 17 | 17 | UV | 6048 | 2.877 | 1 | 2.877 | 1
615 | Storage | 261 | 17 |  | 336 | 7 | 7 | UV | 2688 | 5.8259 | 2 | 5.8259 | 2
616 | Classroom | 265 | 17 |  | 900 | 20 | 17 | UV | 7200 | 2.2083 | 1 | 2.2083 | 1
617 | Office | 92 | 6 |  | 300 | 6 | 6 | UV | 2400 | 2.3 | 1 | 2.3 | 1
620 | Classroom | 750 | 50 |  | 900 | 20 | 20 | UV | 7200 | 6.25 | 2 | 6.25 | 2
620 | Classroom | 567 | 37 |  | 2304 | 52 | 37 | UV | 18432 | 1.8457 | 1 | 1.8457 | 1
- | Auditorium | 1102 | 73 |  | 8648 | 196 | 73 | AHU | 69184 | 0.95571 | 0 | 0.95571 | 0
- | Faculty/Office | 0 | 0 |  | 330 | 7 | 0 | AC | 2640 | 0 | 0 | 0 | 0
- | Practice Room 1 | 0 | 0 |  | 77 | 1 | 0 | HV | 616 | 0 | 0 | 0 | 0
- | Practice Room 2 | 0 | 0 |  | 77 | 1 | 0 | HV | 616 | 0 | 0 | 0 | 0
- | Practice Room 3 | 0 | 0 |  | 77 | 1 | 0 | HV | 616 | 0 | 0 | 0 | 0
- | Kitchen Office | 15 | 1 |  | 99 | 2 | 1 | RTU | 792 | 1.1364 | 1 | 1.1364 | 1
- | Weight Room | 163 | 10 |  | 1632 | 37 | 10 | AHU | 13056 | 0.74908 | 0 | 0.74908 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | Franklin Learning Center | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 318 | 21 |  | 840 | 19 | 19 |  | 6720 | 2.8393 | 1 | 2.8393 | 1
101/102 | Classroom | 144 | 9 |  | 1426 | 32 | 9 |  | 11408 | 0.75736 | 0 | 0.75736 | 0
103 / 104 | Conference | 811 | 54 |  | 1612 | 36 | 36 |  | 12896 | 3.7733 | 1 | 3.7733 | 1
105 | Classroom | 186 | 12 |  | 690 | 15 | 12 |  | 5520 | 2.0217 | 1 | 2.0217 | 1
108 | ESOL |  | 0 |  | 242 | 5 | 0 |  | 1936 | unk | unk | unk | unk
111 | Classroom | 44 | 2 |  | 221 | 5 | 2 |  | 1768 | 1.4932 | 1 | 1.4932 | 1
120 | Classroom | 528 | 35 |  | 625 | 14 | 14 |  | 5000 | 6.336 | 2 | 6.336 | 2
121 | Classroom | 486 | 32 |  | 806 | 18 | 18 |  | 6448 | 4.5223 | 2 | 4.5223 | 2
122 | Classroom | 640 | 42 |  | 744 | 16 | 16 |  | 5952 | 6.4516 | 2 | 6.4516 | 2
123 | Classroom | 705 | 47 |  | 660 | 15 | 15 |  | 5280 | 8.0114 | 2 | 8.0114 | 2
124 | Classroom | 504 | 33 |  | 266 | 6 | 6 |  | 2128 | 14.2105 | 3 | 14.2105 | 3
125 | Classroom | 615 | 41 |  | 575 | 13 | 13 |  | 4600 | 8.0217 | 2 | 8.0217 | 2
126 | Classroom | 615 | 41 |  | 275 | 6 | 6 |  | 2200 | 16.7727 | 3 | 16.7727 | 3
129 | Classroom | 238 | 15 |  | 675 | 15 | 15 |  | 5400 | 2.6444 | 1 | 2.6444 | 1
132 | Classroom | 264 | 17 |  | 414 | 9 | 9 |  | 3312 | 4.7826 | 2 | 4.7826 | 2
132a | Classroom | 391 | 26 |  | 690 | 15 | 15 |  | 5520 | 4.25 | 2 | 4.25 | 2
133 | Classroom | 730 | 48 |  | 759 | 17 | 17 |  | 6072 | 7.2134 | 2 | 7.2134 | 2
200 | Classroom | 447 | 29 |  | 950 | 21 | 21 |  | 7600 | 3.5289 | 1 | 3.5289 | 1
201 | Classroom | 372 | 24 |  | 713 | 16 | 16 |  | 5704 | 3.913 | 1 | 3.913 | 1
202 | Classroom | 349 | 23 |  | 690 | 15 | 15 |  | 5520 | 3.7935 | 1 | 3.7935 | 1
203 / 204 | Classroom | 655 | 43 |  | 1426 | 32 | 32 |  | 11408 | 3.445 | 1 | 3.445 | 1
205 | Classroom | 294 | 19 |  | 713 | 16 | 16 |  | 5704 | 3.0926 | 1 | 3.0926 | 1
206 | Classroom | 0 | 0 |  | 198 | 4 | 0 |  | 1584 | 0 | 0 | 0 | 0
207 | Classroom | 37 | 2 |  | 925 | 21 | 2 |  | 7400 | 0.3 | 0 | 0.3 | 0
208 | Classroom | 314 | 20 |  | 782 | 17 | 17 |  | 6256 | 3.0115 | 1 | 3.0115 | 1
209 | Classroom | 638 | 42 |  | 875 | 19 | 19 |  | 7000 | 5.4686 | 2 | 5.4686 | 2
210 | Classroom | 661 | 44 |  | 782 | 17 | 17 |  | 6256 | 6.3395 | 2 | 6.3395 | 2
212 | Classroom | 621 | 41 |  | 851 | 19 | 19 |  | 6808 | 5.473 | 2 | 5.473 | 2
213 | Classroom | 0 | 0 |  | 165 | 3 | 0 |  | 1320 | 0 | 0 | 0 | 0
214 | Classroom | 580 | 38 |  | 625 | 14 | 14 |  | 5000 | 6.96 | 2 | 6.96 | 2
215 | Classroom | 446 | 29 |  | 720 | 16 | 16 |  | 5760 | 4.6458 | 2 | 4.6458 | 2
216 | Classroom | 486 | 32 |  | 960 | 21 | 21 |  | 7680 | 3.7969 | 1 | 3.7969 | 1
217 | Classroom | 410 | 27 |  | 960 | 21 | 21 |  | 7680 | 3.2031 | 1 | 3.2031 | 1
218 | Classroom | 377 | 25 |  | 600 | 13 | 13 |  | 4800 | 4.7125 | 2 | 4.7125 | 2
220 | Classroom | 174 | 11 |  | 980 | 22 | 11 |  | 7840 | 1.3316 | 1 | 1.3316 | 1
221 | IMC/ Library | 433 | 28 |  | 1536 | 34 | 28 |  | 12288 | 2.1143 | 1 | 2.1143 | 1
221 | Office | 210 | 14 |  | 154 | 3 | 3 |  | 1232 | 10.2273 | 3 | 10.2273 | 3
300 | Classroom | 88 | 5 |  | 900 | 20 | 5 |  | 7200 | 0.73333 | 0 | 0.73333 | 0
301 | Classroom | 215 | 14 |  | 506 | 11 | 11 |  | 4048 | 3.1868 | 1 | 3.1868 | 1
302 | Classroom | 403 | 26 |  | 975 | 22 | 22 |  | 7800 | 3.1 | 1 | 3.1 | 1
303 | Classroom | 368 | 24 |  | 936 | 21 | 21 |  | 7488 | 2.9487 | 1 | 2.9487 | 1
304 | Classroom | 287 | 19 |  | 575 | 13 | 13 |  | 4600 | 3.7435 | 1 | 3.7435 | 1
305 | Classroom | 392 | 26 |  | 713 | 16 | 16 |  | 5704 | 4.1234 | 2 | 4.1234 | 2
306 | Classroom | 168 | 11 |  | 297 | 6 | 6 |  | 2376 | 4.2424 | 2 | 4.2424 | 2
307 | Classroom | 729 | 48 |  | 700 | 15 | 15 |  | 5600 | 7.8107 | 2 | 7.8107 | 2
309 | Classroom | 443 | 29 |  | 480 | 10 | 10 |  | 3840 | 6.9219 | 2 | 6.9219 | 2
310 | Medical Classroom | 1312 | 87 |  | 1403 | 31 | 31 |  | 11224 | 7.0135 | 2 | 7.0135 | 2
310 | Doctor's Office | 3 | 0 |  | 77 | 1 | 0 |  | 616 | 0.29221 | 0 | 0.29221 | 0
310 | Bathroom | 12 | 0 |  | 120 | 2 | 0 |  | 960 | 0.75 | 0 | 0.75 | 0
310 | Storage | 11 | 0 |  | 140 | 3 | 0 |  | 1120 | 0.58929 | 0 | 0.58929 | 0
312 | Classroom | 538 | 35 |  | 575 | 13 | 13 |  | 4600 | 7.0174 | 2 | 7.0174 | 2
312 | Councelor | 0 | 0 |  | 950 | 21 | 0 |  | 7600 | 0 | 0 | 0 | 0
315 | Classroom | 255 | 17 |  | 675 | 15 | 15 |  | 5400 | 2.8333 | 1 | 2.8333 | 1
316 | Classroom | 353 | 23 |  | 644 | 14 | 14 |  | 5152 | 4.111 | 2 | 4.111 | 2
317 | Classroom | 465 | 31 |  | 950 | 21 | 21 |  | 7600 | 3.6711 | 1 | 3.6711 | 1
318 | Classroom | 465 | 31 |  | 897 | 20 | 20 |  | 7176 | 3.888 | 1 | 3.888 | 1
318 | Prep Room / Chemistry |  | 0 |  | 156 | 3 | 0 |  | 1248 | unk | unk | unk | unk
318 | Secure Closet |  | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
319 | Classroom | 263 | 17 |  | 575 | 13 | 13 |  | 4600 | 3.4304 | 1 | 3.4304 | 1
321 | Classroom | 506 | 33 |  | 588 | 13 | 13 |  | 4704 | 6.4541 | 2 | 6.4541 | 2
322 | Computer | 0 | 0 |  | 299 | 6 | 0 |  | 2392 | 0 | 0 | 0 | 0
323 | Classroom | 374 | 24 |  | 598 | 13 | 13 |  | 4784 | 4.6906 | 2 | 4.6906 | 2
324 | Classroom | 104 | 6 |  | 552 | 12 | 6 |  | 4416 | 1.413 | 1 | 1.413 | 1
325 | Classroom | 118 | 7 |  | 594 | 13 | 7 |  | 4752 | 1.4899 | 1 | 1.4899 | 1
- | Cafeteria | 1320 | 88 |  | 2808 | 63 | 63 |  | 22464 | 3.5256 | 1 | 3.5256 | 1
- | Gym |  | 0 |  | 3649 | 82 | 0 |  | 29192 | unk | unk | unk | unk
- | Office | 58 | 3 |  | 230 | 5 | 3 |  | 1840 | 1.8913 | 1 | 1.8913 | 1
- | Office | 223 | 14 |  | 567 | 12 | 12 |  | 4536 | 2.9497 | 1 | 2.9497 | 1
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Horace H. Furness High School | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Classroom |  | 0 |  | 1224 | 27 | 0 |  | 9792 | unk | unk | unk | unk
3 | Classroom |  | 0 |  | 672 | 15 | 0 |  | 5376 | unk | unk | unk | unk
4 | Classroom |  | 0 |  | 840 | 19 | 0 |  | 6720 | unk | unk | unk | unk
5 | Classroom |  | 0 |  | 840 | 19 | 0 |  | 6720 | unk | unk | unk | unk
101 | Classroom | 306 | 20 |  | 667 | 15 | 15 |  | 5336 | 3.4408 | 1 | 3.4408 | 1
102 | Classroom |  | 0 |  | 768 | 17 | 0 |  | 6144 | unk | unk | unk | unk
103 | classroom | 297 | 19 |  | 667 | 15 | 15 |  | 5336 | 3.3396 | 1 | 3.3396 | 1
104 | Classroom |  | 0 |  | 896 | 20 | 0 |  | 7168 | unk | unk | unk | unk
105 | classroom |  | 0 |  | 667 | 15 | 0 |  | 5336 | unk | unk | unk | unk
106 | classroom | 326 | 21 |  | 667 | 15 | 15 |  | 5336 | 3.6657 | 1 | 3.6657 | 1
107 | Library | 1463 | 97 |  | 2448 | 55 | 55 |  | 19584 | 4.4822 | 2 | 4.4822 | 2
112 | Classroom |  | 0 |  | 448 | 10 | 0 |  | 3584 | unk | unk | unk | unk
201 | classroom | 272 | 18 |  | 735 | 16 | 16 |  | 5880 | 2.7755 | 1 | 2.7755 | 1
201A | Room |  | 0 |  | 448 | 10 | 0 |  | 3584 | unk | unk | unk | unk
202 | Classroom |  | 0 |  | 1536 | 34 | 0 |  | 12288 | unk | unk | unk | unk
203 | classroom | 540 | 36 |  | 874 | 19 | 19 |  | 6992 | 4.6339 | 2 | 4.6339 | 2
204 | classroom | 443 | 29 |  | 814 | 18 | 18 |  | 6512 | 4.0817 | 2 | 4.0817 | 2
205 | classroom | 392 | 26 |  | 667 | 15 | 15 |  | 5336 | 4.4078 | 2 | 4.4078 | 2
206 | classroom |  | 0 |  | 667 | 15 | 0 |  | 5336 | unk | unk | unk | unk
207 | classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | unk | unk | unk | unk
208 | classroom | 328 | 21 |  | 660 | 15 | 15 |  | 5280 | 3.7273 | 1 | 3.7273 | 1
209 | classroom |  | 0 |  | 725 | 16 | 0 |  | 5800 | unk | unk | unk | unk
210 | classroom |  | 0 |  | 696 | 15 | 0 |  | 5568 | unk | unk | unk | unk
211 | classroom | 319 | 21 |  | 696 | 15 | 15 |  | 5568 | 3.4375 | 1 | 3.4375 | 1
212 | classroom | 359 | 23 |  | 696 | 15 | 15 |  | 5568 | 3.8685 | 1 | 3.8685 | 1
213 | classroom | 316 | 21 |  | 696 | 15 | 15 |  | 5568 | 3.4052 | 1 | 3.4052 | 1
214 | classroom |  | 0 |  | 696 | 15 | 0 |  | 5568 | unk | unk | unk | unk
215 | Classroom |  | 0 |  | 576 | 13 | 0 |  | 4608 | unk | unk | unk | unk
218 | classroom | 367 | 24 |  | 720 | 16 | 16 |  | 5760 | 3.8229 | 1 | 3.8229 | 1
219A | classroom |  | 0 |  | 783 | 17 | 0 |  | 6264 | unk | unk | unk | unk
219B | classroom | 275 | 18 |  | 1100 | 25 | 18 |  | 8800 | 1.875 | 1 | 1.875 | 1
220 | classroom | 292 | 19 |  | 690 | 15 | 15 |  | 5520 | 3.1739 | 1 | 3.1739 | 1
221 | classroom | 490 | 32 |  | 770 | 17 | 17 |  | 6160 | 4.7727 | 2 | 4.7727 | 2
221A | classroom | 380 | 25 |  | 770 | 17 | 17 |  | 6160 | 3.7013 | 1 | 3.7013 | 1
222 | classroom |  | 0 |  | 161 | 3 | 0 |  | 1288 | unk | unk | unk | unk
222A | Room |  | 0 |  | 560 | 12 | 0 |  | 4480 | unk | unk | unk | unk
301A | classroom 301 | 360 | 24 |  | 690 | 15 | 15 |  | 5520 | 3.913 | 1 | 3.913 | 1
301B | classroom 301 | 345 | 23 |  | 672 | 15 | 15 |  | 5376 | 3.8504 | 1 | 3.8504 | 1
302A | classroom 302 | 272 | 18 |  | 1056 | 24 | 18 |  | 8448 | 1.9318 | 1 | 1.9318 | 1
302B | classroom 302 | 356 | 23 |  | 624 | 14 | 14 |  | 4992 | 4.2788 | 2 | 4.2788 | 2
303 | classroom | 438 | 29 |  | 770 | 17 | 17 |  | 6160 | 4.2662 | 2 | 4.2662 | 2
304 | classroom |  | 0 |  | 690 | 15 | 0 |  | 5520 | unk | unk | unk | unk
305 | classroom |  | 0 |  | 672 | 15 | 0 |  | 5376 | unk | unk | unk | unk
306 | classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | unk | unk | unk | unk
307 | classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | unk | unk | unk | unk
308 | classroom | 246 | 16 |  | 720 | 16 | 16 |  | 5760 | 2.5625 | 1 | 2.5625 | 1
309 | classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | unk | unk | unk | unk
310A | classroom |  | 0 |  | 1008 | 22 | 0 |  | 8064 | unk | unk | unk | unk
310b | classroom |  | 0 |  | 1344 | 30 | 0 |  | 10752 | unk | unk | unk | unk
311A | classroom | 201 | 13 |  | 1008 | 22 | 13 |  | 8064 | 1.4955 | 1 | 1.4955 | 1
311B | classroom |  | 0 |  | 1148 | 26 | 0 |  | 9184 | unk | unk | unk | unk
312A | classroom |  | 0 |  | 960 | 21 | 0 |  | 7680 | unk | unk | unk | unk
312B | classroom |  | 0 |  | 400 | 9 | 0 |  | 3200 | unk | unk | unk | unk
313A | classroom | 175 | 11 |  | 1008 | 22 | 11 |  | 8064 | 1.3021 | 1 | 1.3021 | 1
313B | classroom |  | 0 |  | 480 | 10 | 0 |  | 3840 | unk | unk | unk | unk
314 | Classroom |  | 0 |  | 448 | 10 | 0 |  | 3584 | unk | unk | unk | unk
315 | Classroom |  | 0 |  | 392 | 8 | 0 |  | 3136 | unk | unk | unk | unk
316 | classroom | 73 | 4 |  | 696 | 15 | 4 |  | 5568 | 0.78664 | 0 | 0.78664 | 0
317A | classroom |  | 0 |  | 1137 | 25 | 0 |  | 9096 | unk | unk | unk | unk
317B | classroom | 117 | 7 |  | 1008 | 22 | 7 |  | 8064 | 0.87054 | 0 | 0.87054 | 0
318A | classroom |  | 0 |  | 1152 | 26 | 0 |  | 9216 | unk | unk | unk | unk
318B | classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | unk | unk | unk | unk
319A | classroom | 392 | 26 |  | 1056 | 24 | 24 |  | 8448 | 2.7841 | 1 | 2.7841 | 1
319B | classroom | 215 | 14 |  | 320 | 7 | 7 |  | 2560 | 5.0391 | 2 | 5.0391 | 2
320A | classroom |  | 0 |  | 920 | 20 | 0 |  | 7360 | unk | unk | unk | unk
320B | classroom |  | 0 |  | 1056 | 24 | 0 |  | 8448 | unk | unk | unk | unk
321A | classroom |  | 0 |  | 1056 | 24 | 0 |  | 8448 | unk | unk | unk | unk
321B | classroom | 302 | 20 |  | 1056 | 24 | 20 |  | 8448 | 2.1449 | 1 | 2.1449 | 1
- | Cafeteria | 153 | 10 |  | 3665 | 83 | 10 |  | 29320 | 0.3131 | 0 | 0.3131 | 0
Main Office | Office |  | 0 |  | 1248 | 28 | 0 |  | 9984 | unk | unk | unk | unk
Assistant Principal | Office |  | 0 |  | 360 | 8 | 0 |  | 2880 | unk | unk | unk | unk
Burke | Office |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
SSO | Office |  | 0 |  | 240 | 5 | 0 |  | 1920 | unk | unk | unk | unk
Nurse | Suite |  | 0 |  | 960 | 21 | 0 |  | 7680 | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Girard Academic Music Program (GAMP) High School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | CAFE | 9130 | 608 |  | 977 | 22 | 22 |  | 7816 | 70.087 | 5 | 70.087 | 5
- | GYM |  | 0 |  | 6667 | 151 | 0 |  | 53336 | unk | unk | unk | unk
- | GYM OFFICE |  | 0 |  | 99 | 2 | 0 |  | 792 | unk | unk | unk | unk
- | LOWER HALF OF AUDITORIUM | 13845 | 923 |  | 6498 | 147 | 147 |  | 51984 | 15.9799 | 3 | 15.9799 | 3
- | UPPER HALF OF AUDITORIUM | 14721 | 981 |  | 3247 | 73 | 73 |  | 25976 | 34.0029 | 4 | 34.0029 | 4
Principal | Office | 0 | 0 | Yes | 363 | 8 | 8 |  | 2904 | 0 | 0 | 20 | 3
Assistant Principal | Office | 0 | 0 |  | 169 | 3 | 0 |  | 1352 | 0 | 0 | 0 | 0
Main Office | Office | 0 | 0 | Yes | 266 | 6 | 6 |  | 2128 | 0 | 0 | 20 | 3
Counselor 1 | Office | 0 | 0 | Yes | 134 | 3 | 3 |  | 1072 | 0 | 0 | 20 | 3
Counselor 2 | Office | 0 | 0 | Yes | 246 | 5 | 5 |  | 1968 | 0 | 0 | 20 | 3
Nurse | Office | 0 | 0 | Yes | 88 | 2 | 2 |  | 704 | 0 | 0 | 20 | 3
Lunch Room | Lunch Room | 0 | 0 |  | 2580 | 58 | 0 |  | 20640 | 0 | 0 | 0 | 0
Orchestra Room | Orchestra Room | 0 | 0 | Yes | 1082 | 24 | 24 |  | 8656 | 0 | 0 | 20 | 3
Orchestra Room | Office |  | 0 |  | 330 | 7 |  |  | 2640 | unk | unk | unk | unk
Band Room | Band Room | 0 | 0 | Yes | 1221 | 27 | 27 |  | 9768 | 0 | 0 | 20 | 3
102 | Classroom | 0 | 0 | Yes | 685 | 15 | 15 |  | 5480 | 0 | 0 | 20 | 3
103 | Classroom | 0 | 0 | Yes | 722 | 16 | 16 |  | 5776 | 0 | 0 | 20 | 3
104/105 | Classroom | 0 | 0 | Yes | 1063 | 24 | 24 |  | 8504 | 0 | 0 | 20 | 3
107 | Classroom | 0 | 0 | Yes | 735 | 16 | 16 |  | 5880 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 695 | 15 | 15 |  | 5560 | 0 | 0 | 20 | 3
109 | Classroom | 0 | 0 | Yes | 685 | 15 | 15 |  | 5480 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 679 | 15 | 15 |  | 5432 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 | Yes | 679 | 15 | 15 |  | 5432 | 0 | 0 | 20 | 3
203 | Classroom | 0 | 0 | Yes | 715 | 16 | 16 |  | 5720 | 0 | 0 | 20 | 3
204 | Classroom | 0 | 0 | Yes | 683 | 15 | 15 |  | 5464 | 0 | 0 | 20 | 3
205 | Classroom | 0 | 0 | Yes | 680 | 15 | 15 |  | 5440 | 0 | 0 | 20 | 3
206 | Classroom | 0 | 0 | Yes | 711 | 16 | 16 |  | 5688 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 734 | 16 | 16 |  | 5872 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 634 | 14 | 14 |  | 5072 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 | Yes | 686 | 15 | 15 |  | 5488 | 0 | 0 | 20 | 3
211 | Classroom | 0 | 0 |  | 394 | 8 | 0 |  | 3152 | 0 | 0 | 0 | 0
301 | Classroom | 0 | 0 | Yes | 689 | 15 | 15 |  | 5512 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 645 | 14 | 14 |  | 5160 | 0 | 0 | 20 | 3
303 | Classroom | 0 | 0 | Yes | 669 | 15 | 15 |  | 5352 | 0 | 0 | 20 | 3
304 | Classroom | 0 | 0 | Yes | 725 | 16 | 16 |  | 5800 | 0 | 0 | 20 | 3
305 | Classroom | 0 | 0 | Yes | 729 | 16 | 16 |  | 5832 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 950 | 21 | 21 |  | 7600 | 0 | 0 | 20 | 3
307A | Classroom | 0 | 0 | Yes | 292 | 6 | 6 |  | 2336 | 0 | 0 | 20 | 3
308 | Classroom | 0 | 0 | Yes | 900 | 20 | 20 |  | 7200 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 | Yes | 687 | 15 | 15 |  | 5496 | 0 | 0 | 20 | 3
311 | Classroom | 0 | 0 | Yes | 348 | 7 | 7 |  | 2784 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-12 | [8 empty] | unk | unk | unk | unk
School: | Edward Gideon Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Emcor Retest | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 309 | 20 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 2.8436 | 1 | 2.8436 | 1
102 | Classroom | 380 | 25 |  | 745 | 16 | 16 | Unit Ventilator | 5960 | 3.8255 | 1 | 3.8255 | 1
Hallway @ 102 | Hallway | 0 | 0 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
- | Girls Bathroom next to Room 102 |  | 0 |  | 262 | 5 | 0 | N/A | 2096 | unk | unk | unk | unk
- | Boys Bathroom next to Room 102 |  | 0 |  | 294 | 6 | 0 | N/A | 2352 | unk | unk | unk | unk
103 | Classroom | 247 | 16 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
103 A | - |  | 0 |  | 207 | 4 | 0 | Unit Ventilator | 1656 | unk | unk | unk | unk
103 B | - |  | 0 |  | 175 | 3 | 0 | Unit Ventilator | 1400 | unk | unk | unk | unk
104 | Classroom | 226 | 15 |  | 450 | 10 | 10 | Unit Ventilator | 3600 | 3.7667 | 1 | 3.7667 | 1
104 A | - |  | 0 |  | 97 | 2 | 0 | Unit Ventilator | 776 | unk | unk | unk | unk
104 B | - |  | 0 |  | 151 | 3 | 0 | Unit Ventilator | 1208 | unk | unk | unk | unk
104 C | - |  | 0 |  | 134 | 3 | 0 | Unit Ventilator | 1072 | unk | unk | unk | unk
104 | Counselor |  | 0 |  | 451 | 10 | 0 | Unit Ventilator | 3608 | unk | unk | unk | unk
105 | Classroom | 323 | 21 |  | 872 | 19 | 19 | Unit Ventilator | 6976 | 2.7781 | 1 | 2.7781 | 1
Hallway @ 105 | Hallway | 325 | 21 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
106A | Main Office |  | 0 | Yes | 394 | 8 | 8 | Unit Ventilator | 3152 | unk | unk | 20 | 3
106E | Principal Office |  | 0 | Yes | 166 | 3 | 3 | Unit Ventilator | 1328 | unk | unk | 20 | 3
109 | Classroom | 351 | 23 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 3.0682 | 1 | 3.0682 | 1
110 | Classroom | 374 | 24 |  | 811 | 18 | 18 | Unit Ventilator | 6488 | 3.4587 | 1 | 3.4587 | 1
111 | Classroom | 253 | 16 |  | 866 | 19 | 16 | Unit Ventilator | 6928 | 2.1911 | 1 | 2.1911 | 1
113 A | School police |  | 0 |  | 317 | 7 | 0 | Unit Ventilator | 2536 | unk | unk | unk | unk
113 b | inner office |  | 0 |  | 153 | 3 | 0 | Unit Ventilator | 1224 | unk | unk | unk | unk
113 c | inner office |  | 0 | Yes | 164 | 3 | 3 | Unit Ventilator | 1312 | unk | unk | 20 | 3
201 | Classroom | 154 | 10 |  | 1019 | 23 | 10 | Unit Ventilator | 8152 | 1.1335 | 1 | 1.1335 | 1
Hallway @ 201 | Hallway | 225 | 15 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
202 | Classroom | 537 | 35 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 4.3588 | 2 | 4.3588 | 2
203 | Classroom | 0 | 0 | Yes | 938 | 21 | 21 | Unit Ventilator | 7504 | 0 | 0 | 20 | 3
204 | Classroom | 319 | 21 |  | 788 | 17 | 17 | Unit Ventilator | 6304 | 3.0362 | 1 | 3.0362 | 1
205 | Classroom | 296 | 19 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 2.7007 | 1 | 2.7007 | 1
206 | Classroom | 310 | 20 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 2.8285 | 1 | 2.8285 | 1
Hallway @ 206 | Hallway | 0 | 0 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
207 | Classroom | 350 | 23 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 3.1934 | 1 | 3.1934 | 1
- | Boys Bathroom outside Room 207 |  | 0 |  | 164 | 3 | 0 | N/A | 1312 | unk | unk | unk | unk
208 | Classroom | 328 | 21 |  | 825 | 18 | 18 | Unit Ventilator | 6600 | 2.9818 | 1 | 2.9818 | 1
- | Female Staff Bathroom outside Room 208 |  | 0 |  | 61 | 1 | 0 | N/A | 488 | unk | unk | unk | unk
- | Girls Bathroom outside Room 208 |  | 0 |  | 127 | 2 | 0 | N/A | 1016 | unk | unk | unk | unk
209 | Classroom | 310 | 20 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 2.8285 | 1 | 2.8285 | 1
210 | Classroom | 253 | 16 |  | 811 | 18 | 16 | Unit Ventilator | 6488 | 2.3397 | 1 | 2.3397 | 1
211 | Classroom | 262 | 17 |  | 829 | 18 | 17 | Unit Ventilator | 6632 | 2.3703 | 1 | 2.3703 | 1
212 | Classroom | 365 | 24 |  | 825 | 18 | 18 | Unit Ventilator | 6600 | 3.3182 | 1 | 3.3182 | 1
Hallway @ 212 | Hallway | 215 | 14 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
213 | Classroom | 357 | 23 |  | 426 | 9 | 9 | Unit Ventilator | 3408 | 6.2852 | 2 | 6.2852 | 2
301 | Classroom | 189 | 12 | Yes | 829 | 18 | 18 | Unit Ventilator | 6632 | 1.7099 | 1 | 21.7099 | 3
302 | Classroom | 298 | 19 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 2.719 | 1 | 2.719 | 1
302 A | Bathroom |  | 0 |  | 232 | 5 | 0 | N/A | 1856 | unk | unk | unk | unk
302 B | Bathroom |  | 0 |  | 147 | 3 | 0 | N/A | 1176 | unk | unk | unk | unk
303 | Classroom | 0 | 0 | Yes | 894 | 20 | 20 | Unit Ventilator | 7152 | 0 | 0 | 20 | 3
304 | Classroom | 316 | 21 |  | 788 | 17 | 17 | Unit Ventilator | 6304 | 3.0076 | 1 | 3.0076 | 1
305 | Classroom | 422 | 28 |  | 820 | 18 | 18 | Unit Ventilator | 6560 | 3.8598 | 1 | 3.8598 | 1
306 | Classroom | 288 | 19 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 2.6277 | 1 | 2.6277 | 1
Hallway @ 306 | Hallway | 0 | 0 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
307 | Classroom | 351 | 23 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 3.2026 | 1 | 3.2026 | 1
308 | Classroom | 476 | 31 |  | 826 | 18 | 18 | Unit Ventilator | 6608 | 4.322 | 2 | 4.322 | 2
Hallway @ 308 | Hallway | 250 | 16 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
309 | Classroom | 349 | 23 |  | 826 | 18 | 18 | Unit Ventilator | 6608 | 3.1689 | 1 | 3.1689 | 1
310 | Classroom | 321 | 21 |  | 811 | 18 | 18 | Unit Ventilator | 6488 | 2.9686 | 1 | 2.9686 | 1
311 | Classroom | 331 | 22 |  | 829 | 18 | 18 | Unit Ventilator | 6632 | 2.9946 | 1 | 2.9946 | 1
312 | Classroom | 367 | 24 |  | 822 | 18 | 18 | Unit Ventilator | 6576 | 3.3485 | 1 | 3.3485 | 1
Hallway @ 312 | Hallway | 215 | 14 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
- | Auditorium | 630 | 42 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
GYM | GYM | 572 | 38 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
Hallway @ Elevator | Hallway | 0 | 0 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
Hallway @ Stair D | Hallway | 231 | 15 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
- | Nurse | 0 | 0 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
- | Teachers Lounge | 0 | 0 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
- | Auditorium |  | 0 |  | 2998 | 68 | 0 | AHU | 23984 | unk | unk | unk | unk
- | Auditorium Rear classroom |  | 0 |  | 251 | 5 | 0 | AHU | 2008 | unk | unk | unk | unk
- | Boys bathroom outside main offce |  | 0 |  | 303 | 6 | 0 | N/A | 2424 | unk | unk | unk | unk
- | 3rd floor Boys bathroom |  | 0 |  | 220 | 4 | 0 | N/A | 1760 | unk | unk | unk | unk
- | Building Engineer Office |  | 0 |  | 99 | 2 | 0 | N/A | 792 | unk | unk | unk | unk
- | 3rd floor Girls bathroom |  | 0 |  | 192 | 4 | 0 | N/A | 1536 | unk | unk | unk | unk
- | Girls bathroom outside main offce |  | 0 |  | 300 | 6 | 0 | N/A | 2400 | unk | unk | unk | unk
- | 3rd floor Gym Teacher office |  | 0 |  | 284 | 6 | 0 | N/A | 2272 | unk | unk | unk | unk
- | 3rd floor Gym/Lunchroom |  | 0 |  | 3603 | 81 | 0 | Unit Ventilator | 28824 | unk | unk | unk | unk
- | Kitchen |  | 0 |  | 509 | 11 | 0 | N/A | 4072 | unk | unk | unk | unk
- | Parent & teacher conf rm |  | 0 |  | 123 | 2 | 0 | Unit Ventilator | 984 | unk | unk | unk | unk
- | Principal Conf rm |  | 0 |  | 159 | 3 | 0 | Unit Ventilator | 1272 | unk | unk | unk | unk
- | Teacher Lounge |  | 0 |  | 436 | 9 | 0 | Unit Ventilator | 3488 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Stephen Girard Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Meehan | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | 100 | 51 | 3 | Yes | 672 | 15 | 15 | Unit Ventilator | 5376 | 0.5692 | 0 | 20.5692 | 3
101 | 101 | 114 | 7 | Yes | 1200 | 27 | 27 | Unit Ventilator | 9600 | 0.7125 | 0 | 20.7125 | 3
103 | 103 | 27 | 1 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0.24107 | 0 | 20.2411 | 3
105 | 105 | 62 | 4 |  | 840 | 19 | 4 | Unit Ventilator | 6720 | 0.55357 | 0 | 0.55357 | 0
118 | Speech Classroom |  | 0 | Yes | 275 | 6 | 6 | N/A | 2200 | unk | unk | 20 | 3
200 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
204 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
206 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
207 | Classroom |  | 0 | Yes | 375 | 8 | 8 | Unit Ventilator | 3000 | unk | unk | 20 | 3
208 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
209 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
210 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
216 | Classroom |  | 0 |  | 200 | 4 | 0 |  | 1600 | unk | unk | unk | unk
300 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
301 | Classroom |  | 0 |  | 840 | 19 | 0 | Unit Ventilator | 6720 | unk | unk | unk | unk
302 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
303 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
304 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
305 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
306 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
307 / 309 | Classroom |  | 0 | Yes | 1375 | 31 | 31 | Unit Ventilator | 11000 | unk | unk | 20 | 3
308 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
308A | Classroom |  | 0 |  | 364 | 8 | 0 |  | 2912 | unk | unk | unk | unk
310 | Classroom |  | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | unk | unk | 20 | 3
- | Auditorium | 11536 | 769 |  | 2600 | 59 | 59 | AHU | 20800 | 33.2769 | 4 | 33.2769 | 4
- | Gymnasium | 1656 | 110 |  | 3550 | 80 | 80 | AHU | 28400 | 3.4986 | 1 | 3.4986 | 1
- | IMC | 227 | 15 |  | 1846 | 41 | 15 | Unit Ventilator | 14768 | 0.92226 | 0 | 0.92226 | 0
- | Nurse |  | 0 | Yes | 170 | 3 | 3 | N/A | 1360 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 294 | 6 | 6 |  | 2352 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 396 | 9 | 9 | Unit Ventilator | 3168 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | Philadelphia High School for Girls | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B-12 | Showers | 2144 | 142 |  | 2163 | 49 | 49 | AHU | 17304 | 7.4341 | 2 | 7.4341 | 2
B-13 | Visitors' Lockers | 0 | 0 |  | 256 | 5 | 0 | Unit Ventilator | 2048 | 0 | 0 | 0 | 0
B-14 | Home Lockers | 0 | 0 |  | 316 | 7 | 0 | Unit Ventilator | 2528 | 0 | 0 | 0 | 0
B-16 | Girls' Locker Room | 1254 | 83 |  | 4702 | 106 | 83 | Unit Ventilator | 37616 | 2.0002 | 1 | 2.0002 | 1
G-1 | Classroom | 292 | 19 |  | 1032 | 23 | 19 | Unit Ventilator | 8256 | 2.1221 | 1 | 2.1221 | 1
G-3 | Classroom | 459 | 30 |  | 1216 | 27 | 27 | Unit Ventilator | 9728 | 2.831 | 1 | 2.831 | 1
G-6 | - | 0 | 0 |  | 734 | 16 | 0 | Unit Ventilator | 5872 | 0 | 0 | 0 | 0
G-8 | Dance | 277 | 18 |  | 1275 | 28 | 18 | Unit Ventilator | 10200 | 1.6294 | 1 | 1.6294 | 1
G-10 | Classroom | 281 | 18 |  | 741 | 16 | 16 | Unit Ventilator | 5928 | 2.8441 | 1 | 2.8441 | 1
G-11 | Classroom | 274 | 18 |  | 745 | 16 | 16 | Unit Ventilator | 5960 | 2.7584 | 1 | 2.7584 | 1
G-12 | Classroom | 222 | 14 |  | 714 | 16 | 14 | Unit Ventilator | 5712 | 2.3319 | 1 | 2.3319 | 1
G-17 | Classroom | 93 | 6 |  | 748 | 17 | 6 | Unit Ventilator | 5984 | 0.93249 | 0 | 0.93249 | 0
G-19 | Classroom | 277 | 18 |  | 718 | 16 | 16 | Unit Ventilator | 5744 | 2.8935 | 1 | 2.8935 | 1
1 | Fitness Room | 227 | 15 |  | 1169 | 26 | 15 | Unit Ventilator | 9352 | 1.4564 | 1 | 1.4564 | 1
2 | Fitness Room | 506 | 33 |  | 2048 | 46 | 33 | Unit Ventilator | 16384 | 1.853 | 1 | 1.853 | 1
100 | Classroom | 306 | 20 |  | 756 | 17 | 17 | Unit Ventilator | 6048 | 3.0357 | 1 | 3.0357 | 1
101 | Classroom | 275 | 18 |  | 756 | 17 | 17 | Unit Ventilator | 6048 | 2.7282 | 1 | 2.7282 | 1
102 | Archives | 145 | 9 |  | 689 | 15 | 9 | Unit Ventilator | 5512 | 1.5784 | 1 | 1.5784 | 1
104 | Classroom | 221 | 14 |  | 756 | 17 | 14 | Unit Ventilator | 6048 | 2.1925 | 1 | 2.1925 | 1
105 | Instruments | 612 | 40 |  | 2376 | 54 | 40 | Unit Ventilator | 19008 | 1.9318 | 1 | 1.9318 | 1
106 | Roster Office | 208 | 13 |  | 778 | 17 | 13 | Unit Ventilator | 6224 | 2.0051 | 1 | 2.0051 | 1
107 | Office | 290 | 19 |  | 799 | 18 | 18 | Unit Ventilator | 6392 | 2.7222 | 1 | 2.7222 | 1
108 | Office | 0 | 0 |  | 769 | 17 | 0 | Unit Ventilator | 6152 | 0 | 0 | 0 | 0
109 | Office | 291 | 19 |  | 790 | 17 | 17 | Unit Ventilator | 6320 | 2.7627 | 1 | 2.7627 | 1
110 | Office | 203 | 13 |  | 768 | 17 | 13 | Unit Ventilator | 6144 | 1.9824 | 1 | 1.9824 | 1
111 | Poetry | 188 | 12 |  | 1182 | 26 | 12 | Unit Ventilator | 9456 | 1.1929 | 1 | 1.1929 | 1
111-A | Health Office | 0 | 0 |  | 462 | 10 | 0 | Unit Ventilator | 3696 | 0 | 0 | 0 | 0
112 | Classroom | 0 | 0 |  | 767 | 17 | 0 | Unit Ventilator | 6136 | 0 | 0 | 0 | 0
113 | Classroom | 0 | 0 |  | 1655 | 37 | 0 | Unit Ventilator | 13240 | 0 | 0 | 0 | 0
114 | Classroom | 0 | 0 |  | 769 | 17 | 0 | Unit Ventilator | 6152 | 0 | 0 | 0 | 0
115 | Classroom | 0 | 0 |  | 1749 | 39 | 0 | Unit Ventilator | 13992 | 0 | 0 | 0 | 0
116 | Classroom | 0 | 0 |  | 749 | 17 | 0 | Unit Ventilator | 5992 | 0 | 0 | 0 | 0
118 | Classroom | 0 | 0 |  | 752 | 17 | 0 | Unit Ventilator | 6016 | 0 | 0 | 0 | 0
200 | Classroom | 0 | 0 |  | 775 | 17 | 0 | Unit Ventilator | 6200 | 0 | 0 | 0 | 0
201 | Classroom | 221 | 14 |  | 763 | 17 | 14 | Unit Ventilator | 6104 | 2.1723 | 1 | 2.1723 | 1
202 | Classroom | 213 | 14 |  | 771 | 17 | 14 | Unit Ventilator | 6168 | 2.072 | 1 | 2.072 | 1
204 | Classroom | 0 | 0 |  | 771 | 17 | 0 | Unit Ventilator | 6168 | 0 | 0 | 0 | 0
205 | Music Office | 472 | 31 |  | 2334 | 53 | 31 | Unit Ventilator | 18672 | 1.5167 | 1 | 1.5167 | 1
206 | Classroom | 0 | 0 |  | 780 | 17 | 0 | Unit Ventilator | 6240 | 0 | 0 | 0 | 0
207 | Classroom | 289 | 19 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 2.8223 | 1 | 2.8223 | 1
208 | Classroom | 213 | 14 |  | 776 | 17 | 14 | Unit Ventilator | 6208 | 2.0586 | 1 | 2.0586 | 1
209 | Classroom | 251 | 16 |  | 786 | 17 | 16 | Unit Ventilator | 6288 | 2.395 | 1 | 2.395 | 1
210 | Classroom | 255 | 17 |  | 781 | 17 | 17 | Unit Ventilator | 6248 | 2.4488 | 1 | 2.4488 | 1
211 | Classroom | 268 | 17 |  | 744 | 16 | 16 | Unit Ventilator | 5952 | 2.7016 | 1 | 2.7016 | 1
212 | Classroom | 388 | 25 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.7308 | 1 | 3.7308 | 1
214 | Classroom | 251 | 16 |  | 776 | 17 | 16 | Unit Ventilator | 6208 | 2.4259 | 1 | 2.4259 | 1
215 | Classroom | 402 | 26 |  | 781 | 17 | 17 | Unit Ventilator | 6248 | 3.8604 | 1 | 3.8604 | 1
216 | Classroom | 244 | 16 |  | 772 | 17 | 16 | Unit Ventilator | 6176 | 2.3705 | 1 | 2.3705 | 1
217 | Classroom | 178 | 11 |  | 787 | 17 | 11 | Unit Ventilator | 6296 | 1.6963 | 1 | 1.6963 | 1
218 | Classroom | 0 | 0 |  | 789 | 17 | 0 | Unit Ventilator | 6312 | 0 | 0 | 0 | 0
219 | Classroom | 54 | 3 |  | 783 | 17 | 3 | Unit Ventilator | 6264 | 0.51724 | 0 | 0.51724 | 0
221 | Classroom | 290 | 19 |  | 841 | 19 | 19 | Unit Ventilator | 6728 | 2.5862 | 1 | 2.5862 | 1
223 | Classroom | 0 | 0 |  | 891 | 20 | 0 | Unit Ventilator | 7128 | 0 | 0 | 0 | 0
300 | Classroom | 270 | 18 |  | 786 | 17 | 17 | Unit Ventilator | 6288 | 2.5763 | 1 | 2.5763 | 1
302 | Classroom | 416 | 27 |  | 996 | 22 | 22 | Unit Ventilator | 7968 | 3.1325 | 1 | 3.1325 | 1
303 | Classroom | 555 | 37 |  | 1052 | 23 | 23 | Unit Ventilator | 8416 | 3.9567 | 1 | 3.9567 | 1
304 | Classroom | 525 | 35 |  | 1007 | 22 | 22 | Unit Ventilator | 8056 | 3.9101 | 1 | 3.9101 | 1
305 | Classroom | 279 | 18 |  | 791 | 17 | 17 | Unit Ventilator | 6328 | 2.6454 | 1 | 2.6454 | 1
306 | Classroom | 378 | 25 |  | 1034 | 23 | 23 | Unit Ventilator | 8272 | 2.7418 | 1 | 2.7418 | 1
307 | Classroom | 0 | 0 |  | 781 | 17 | 0 | Unit Ventilator | 6248 | 0 | 0 | 0 | 0
308 | Classroom | 158 | 10 |  | 1048 | 23 | 10 | Unit Ventilator | 8384 | 1.1307 | 1 | 1.1307 | 1
309 | Classroom | 188 | 12 |  | 787 | 17 | 12 | Unit Ventilator | 6296 | 1.7916 | 1 | 1.7916 | 1
310 | Classroom | 403 | 26 |  | 1115 | 25 | 25 | Unit Ventilator | 8920 | 2.7108 | 1 | 2.7108 | 1
311 | Classroom | 186 | 12 |  | 792 | 18 | 12 | Unit Ventilator | 6336 | 1.7614 | 1 | 1.7614 | 1
312 | Classroom | 240 | 16 |  | 1015 | 23 | 16 | Unit Ventilator | 8120 | 1.7734 | 1 | 1.7734 | 1
313 | Classroom | 202 | 13 |  | 779 | 17 | 13 | Unit Ventilator | 6232 | 1.9448 | 1 | 1.9448 | 1
314 | Classroom | 329 | 21 |  | 1008 | 22 | 21 | Unit Ventilator | 8064 | 2.4479 | 1 | 2.4479 | 1
315 | Classroom | 289 | 19 |  | 790 | 17 | 17 | Unit Ventilator | 6320 | 2.7437 | 1 | 2.7437 | 1
316 | Classroom | 326 | 21 |  | 788 | 17 | 17 | Unit Ventilator | 6304 | 3.1028 | 1 | 3.1028 | 1
317 | Classroom | 169 | 11 |  | 780 | 17 | 11 | Unit Ventilator | 6240 | 1.625 | 1 | 1.625 | 1
319 | Classroom | 351 | 23 |  | 706 | 16 | 16 | Unit Ventilator | 5648 | 3.7288 | 1 | 3.7288 | 1
321 | Classroom | 293 | 19 |  | 716 | 16 | 16 | Unit Ventilator | 5728 | 3.0691 | 1 | 3.0691 | 1
- | Auditorium | 946 | 63 |  | 10546 | 239 | 63 | AHU | 84368 | 0.67277 | 0 | 0.67277 | 0
- | Gymnasium | 287 | 19 |  | 10449 | 237 | 19 | AHU | 83592 | 0.206 | 0 | 0.206 | 0
- | Main Cafeteria | 2523 | 168 |  | 12220 | 277 | 168 | Unit Ventilator | 97760 | 1.5485 | 1 | 1.5485 | 1
- | Faculty Cafeteria | 549 | 36 |  | 1172 | 26 | 26 | Unit Ventilator | 9376 | 3.5132 | 1 | 3.5132 | 1
- | Main Office | 192 | 12 |  | 1054 | 23 | 12 | Unit Ventilator | 8432 | 1.3662 | 1 | 1.3662 | 1
- | Library | 538 | 35 |  | 5853 | 133 | 35 | Unit Ventilator | 46824 | 0.68939 | 0 | 0.68939 | 0
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Samuel Gompers Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Capital | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Kindergarten | 334 | 22 |  | 2002 | 45 | 22 | Unit Ventilator | 16016 | 1.2512 | 1 | 1.2512 | 1
102 | Classroom | 429 | 28 |  | 1106 | 25 | 25 | Unit Ventilator | 8848 | 2.9091 | 1 | 2.9091 | 1
104 | Classroom | 450 | 30 |  | 1099 | 24 | 24 | Unit Ventilator | 8792 | 3.071 | 1 | 3.071 | 1
105 | Classroom | 444 | 29 |  | 1094 | 24 | 24 | Unit Ventilator | 8752 | 3.0439 | 1 | 3.0439 | 1
106 | Classroom | 436 | 29 |  | 1095 | 24 | 24 | Unit Ventilator | 8760 | 2.9863 | 1 | 2.9863 | 1
107 | Classroom | 432 | 28 |  | 1102 | 25 | 25 | Unit Ventilator | 8816 | 2.9401 | 1 | 2.9401 | 1
B-107 | Library | 492 | 32 |  | 1241 | 28 | 28 | Unit Ventilator | 9928 | 2.9734 | 1 | 2.9734 | 1
B-107A | Workroom | 28 | 1 |  | 204 | 4 | 1 | Unit Ventilator | 1632 | 1.0294 | 1 | 1.0294 | 1
A-108 | Teacher Room | 138 | 9 |  | 387 | 8 | 8 | Unit Ventilator | 3096 | 2.6744 | 1 | 2.6744 | 1
A-112 | Infirmary | 21 | 1 |  | 198 | 4 | 1 | Unit Ventilator | 1584 | 0.79545 | 0 | 0.79545 | 0
A-113 | Waiting | 80 | 5 |  | 155 | 3 | 3 | FCU | 1240 | 3.871 | 1 | 3.871 | 1
A-114 | Nurse’s Office | 339 | 22 |  | 186 | 4 | 4 | FCU | 1488 | 13.6694 | 3 | 13.6694 | 3
A-121 | Examination | 226 | 15 |  | 310 | 7 | 7 | FCU | 2480 | 5.4677 | 2 | 5.4677 | 2
A-122 | Office | 22 | 1 |  | 133 | 3 | 1 | Unit Ventilator | 1064 | 1.2406 | 1 | 1.2406 | 1
A-124 | Counselor Office | 34 | 2 |  | 178 | 4 | 2 | Unit Ventilator | 1424 | 1.4326 | 1 | 1.4326 | 1
A-131 | General Office | 51 | 3 |  | 488 | 11 | 3 | Unit Ventilator | 3904 | 0.78381 | 0 | 0.78381 | 0
A-133 | Principal Office | 32 | 2 |  | 232 | 5 | 2 | Unit Ventilator | 1856 | 1.0345 | 1 | 1.0345 | 1
A-137 | Conference | 96 | 6 |  | 333 | 7 | 6 | Unit Ventilator | 2664 | 2.1622 | 1 | 2.1622 | 1
A-150 | Office | 117 | 7 |  | 324 | 7 | 7 | FCU | 2592 | 2.7083 | 1 | 2.7083 | 1
A-153 | Office | 122 | 8 |  | 322 | 7 | 7 | FCU | 2576 | 2.8416 | 1 | 2.8416 | 1
201 | Classroom | 429 | 28 |  | 1083 | 24 | 24 | Unit Ventilator | 8664 | 2.9709 | 1 | 2.9709 | 1
202 | Classroom | 431 | 28 |  | 1074 | 24 | 24 | Unit Ventilator | 8592 | 3.0098 | 1 | 3.0098 | 1
203 | Classroom | 432 | 28 |  | 1075 | 24 | 24 | Unit Ventilator | 8600 | 3.014 | 1 | 3.014 | 1
204 | Classroom | 265 | 17 |  | 544 | 12 | 12 | Unit Ventilator | 4352 | 3.6535 | 1 | 3.6535 | 1
205 | Classroom | 418 | 27 |  | 1109 | 25 | 25 | Unit Ventilator | 8872 | 2.8269 | 1 | 2.8269 | 1
A-205 | Teachers Room | 156 | 10 |  | 353 | 8 | 8 | Unit Ventilator | 2824 | 3.3144 | 1 | 3.3144 | 1
206 | Classroom | 433 | 28 |  | 1110 | 25 | 25 | Unit Ventilator | 8880 | 2.9257 | 1 | 2.9257 | 1
207 | Classroom | 435 | 29 |  | 1112 | 25 | 25 | Unit Ventilator | 8896 | 2.9339 | 1 | 2.9339 | 1
208 | Classroom | 438 | 29 |  | 1095 | 24 | 24 | Unit Ventilator | 8760 | 3 | 1 | 3 | 1
A-208 | After School Programs | 65 | 4 |  | 441 | 10 | 4 | Unit Ventilator | 3528 | 1.1054 | 1 | 1.1054 | 1
B-209 | Classroom | 262 | 17 |  | 537 | 12 | 12 | Unit Ventilator | 4296 | 3.6592 | 1 | 3.6592 | 1
B-210 | Classroom | 437 | 29 |  | 1093 | 24 | 24 | Unit Ventilator | 8744 | 2.9986 | 1 | 2.9986 | 1
B-211 | Classroom | 435 | 29 |  | 1095 | 24 | 24 | Unit Ventilator | 8760 | 2.9795 | 1 | 2.9795 | 1
212 | Classroom | 419 | 27 |  | 1084 | 24 | 24 | Unit Ventilator | 8672 | 2.899 | 1 | 2.899 | 1
213 | Classroom | 454 | 30 |  | 1087 | 24 | 24 | Unit Ventilator | 8696 | 3.1325 | 1 | 3.1325 | 1
A-217 | Cafeteria | 466 | 31 |  | 1943 | 44 | 31 | AHU | 15544 | 1.7988 | 1 | 1.7988 | 1
A-218 | Gymnasium | 1290 | 86 |  | 3950 | 89 | 86 | AHU | 31600 | 2.4494 | 1 | 2.4494 | 1
Portable | R1 |  | 0 | Yes | 843 | 19 | 19 |  | 6744 | unk | unk | 20 | 3
Portable | R2 |  | 0 | Yes | 842 | 19 | 19 |  | 6736 | unk | unk | 20 | 3
Portable | R3 |  | 0 | Yes | 852 | 19 | 19 |  | 6816 | unk | unk | 20 | 3
Portable | R4 |  | 0 | Yes | 1033 | 23 | 23 |  | 8264 | unk | unk | 20 | 3
Portable | R5 |  | 0 | Yes | 1022 | 23 | 23 |  | 8176 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-22 | [8 empty] | unk | unk | unk | unk
School: | Joseph Greenberg Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Borthers | Devine Brothers Retest | [7 empty] | unk | unk | unk | unk
|  | Devine Brothers 2nd Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 325 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9438 | 1 | 2.9438 | 1
101 | Classroom | 335 | 22 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.0344 | 1 | 3.0344 | 1
102 | Classroom | 380 | 25 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.442 | 1 | 3.442 | 1
103 | Classroom | 288 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6087 | 1 | 2.6087 | 1
104 | Classroom | 284 | 18 |  | 384 | 8 | 8 | Unit Ventilator | 3072 | 5.5469 | 2 | 5.5469 | 2
105 | Nurse | 300 | 20 |  | 432 | 9 | 9 | Unit Ventilator | 3456 | 5.2083 | 2 | 5.2083 | 2
106 | Classroom | 530 | 35 |  | 1012 | 23 | 23 | Unit Ventilator | 8096 | 3.9279 | 1 | 3.9279 | 1
107 | Classroom | 671 | 44 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 5.8247 | 2 | 5.8247 | 2
107A | Meeting room |  | 0 | Yes | 432 | 9 | 9 | Unit Ventilator | 3456 | unk | unk | 20 | 3
108 | Classroom | 441 | 29 |  | 1012 | 23 | 23 | Unit Ventilator | 8096 | 3.2683 | 1 | 3.2683 | 1
109 | Classroom | 298 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6993 | 1 | 2.6993 | 1
111 | Classroom | 291 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6359 | 1 | 2.6359 | 1
200 | Classroom | 308 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.7899 | 1 | 2.7899 | 1
201 | Classroom | 281 | 18 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.5453 | 1 | 2.5453 | 1
202 | Classroom | 295 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6721 | 1 | 2.6721 | 1
203 | Classroom | 351 | 23 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.1793 | 1 | 3.1793 | 1
204 | Classroom | 317 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.8714 | 1 | 2.8714 | 1
205 | Classroom | 326 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9529 | 1 | 2.9529 | 1
207 | Classroom | 320 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.8986 | 1 | 2.8986 | 1
209 | Classroom | 345 | 23 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.125 | 1 | 3.125 | 1
210 | Classroom | 316 | 21 |  | 384 | 8 | 8 | Unit Ventilator | 3072 | 6.1719 | 2 | 6.1719 | 2
211 | Classroom | 281 | 18 |  | 368 | 8 | 8 | Unit Ventilator | 2944 | 5.7269 | 2 | 5.7269 | 2
211a | Classroom | 375 | 25 |  | 621 | 14 | 14 | Unit Ventilator | 4968 | 4.529 | 2 | 4.529 | 2
211b | Classroom | 307 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.7808 | 1 | 2.7808 | 1
212 | Classroom | 351 | 23 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.1793 | 1 | 3.1793 | 1
213 | Classroom | 344 | 22 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.1159 | 1 | 3.1159 | 1
214 | Classroom | 345 | 23 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.125 | 1 | 3.125 | 1
215 | Classroom | 375 | 25 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.3967 | 1 | 3.3967 | 1
216 | Classroom | 312 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.8261 | 1 | 2.8261 | 1
217 | Classroom | 326 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9529 | 1 | 2.9529 | 1
300 | Classroom | 325 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9438 | 1 | 2.9438 | 1
301 | Classroom | 291 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6359 | 1 | 2.6359 | 1
302 | Classroom | 285 | 19 |  | 552 | 12 | 12 | Unit Ventilator | 4416 | 3.8723 | 1 | 3.8723 | 1
303 | Classroom | 330 | 22 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9891 | 1 | 2.9891 | 1
304 | Classroom | 325 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9438 | 1 | 2.9438 | 1
305 | Classroom | 321 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9076 | 1 | 2.9076 | 1
306 | Classroom | 289 | 19 |  | 384 | 8 | 8 | Unit Ventilator | 3072 | 5.6445 | 2 | 5.6445 | 2
307 | Classroom | 345 | 23 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.125 | 1 | 3.125 | 1
309 | Classroom | 350 | 23 |  | 1242 | 28 | 23 | Unit Ventilator | 9936 | 2.1135 | 1 | 2.1135 | 1
313 | Classroom | 302 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.7355 | 1 | 2.7355 | 1
314 | Classroom | 289 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6178 | 1 | 2.6178 | 1
315 | Classroom | 321 | 21 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9076 | 1 | 2.9076 | 1
316 | Classroom | 311 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.817 | 1 | 2.817 | 1
317 | Classroom | 331 | 22 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.9982 | 1 | 2.9982 | 1
318 | Classroom | 314 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.8442 | 1 | 2.8442 | 1
319 | Classroom | 311 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.817 | 1 | 2.817 | 1
321 | Classroom | 288 | 19 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.6087 | 1 | 2.6087 | 1
400 | Classroom | 375 | 25 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.2552 | 1 | 3.2552 | 1
401 | IMC Classroom | 310 | 20 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 2.808 | 1 | 2.808 | 1
- | Auditorium | 12200 | 813 |  | 3213 | 73 | 73 | AHU | 25704 | 28.4781 | 4 | 28.4781 | 4
- | Cafeteria | 7911 | 527 |  | 5250 | 119 | 119 | AHU | 42000 | 11.3014 | 3 | 11.3014 | 3
- | Gym | 8800 | 586 |  | 3978 | 90 | 90 | AHU | 31824 | 16.5913 | 3 | 16.5913 | 3
- | IMC Classroom | 220 | 14 |  | 828 | 18 | 14 | Unit Ventilator | 6624 | 1.9928 | 1 | 1.9928 | 1
- | Teacher Lounge | 448 | 29 |  | 168 | 3 | 3 | Unit Ventilator | 1344 | 20 | 3 | 20 | 3
- | Main Office | 280 | 18 |  | 1134 | 25 | 18 | Unit Ventilator | 9072 | 1.8519 | 1 | 1.8519 | 1
- | Dean's office |  | 0 | Yes | 135 | 3 | 3 | Unit Ventilator | 1080 | unk | unk | 20 | 3
- | Assistant principal office |  | 0 | Yes | 135 | 3 | 3 | Unit Ventilator | 1080 | unk | unk | 20 | 3
- | Principal's Office |  | 0 | Yes | 432 | 9 | 9 | Unit Ventilator | 3456 | unk | unk | 20 | 3
- | Kitchen |  | 0 | Yes | 864 | 19 | 19 | N/A | 6912 | unk | unk | 20 | 3
- | BE office | 275 | 18 |  | 441 | 10 | 10 | N/A | 3528 | 4.6769 | 2 | 4.6769 | 2
- | Custodial office | 95 | 6 |  | 195 | 4 | 4 | N/A | 1560 | 3.6538 | 1 | 3.6538 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | Albert M. Greenfield Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Meehan | Devine | Capital Part I | [6 empty] | unk | unk | unk | unk
Vendor: | Capital Part II | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B06 | Music rm. | 329 | 21 |  | 416 | 9 | 9 | AHU | 3328 | 5.9315 | 2 | 5.9315 | 2
B17 | Storage | 229 | 15 |  | 320 | 7 | 7 | N/A | 2560 | 5.3672 | 2 | 5.3672 | 2
B36 | Music main | 452 | 30 |  | 962 | 21 | 21 | AHU | 7696 | 3.5239 | 1 | 3.5239 | 1
B37 | Music Office | 151 | 10 |  | 168 | 3 | 3 | AHU | 1344 | 6.7411 | 2 | 6.7411 | 2
B38 | Practice rm | 44 | 2 |  | 64 | 1 | 1 | AHU | 512 | 5.1562 | 2 | 5.1562 | 2
B40 | Music Ensamble | 163 | 10 |  | 312 | 7 | 7 | AHU | 2496 | 3.9183 | 1 | 3.9183 | 1
101 | Reception | 121 | 8 |  | 360 | 8 | 8 | AHU | 2880 | 2.5208 | 1 | 2.5208 | 1
102 |  | 0 |  | Yes | 120 |  |  | N/A | 960 | 0 | 0 | 20 | 3
103 | Offices | 0 | 0 | Yes | 120 | 2 | 2 | AHU | 960 | 0 | 0 | 20 | 3
104 | Offices | 0 | 0 | Yes | 120 | 2 | 2 | AHU | 960 | 0 | 0 | 20 | 3
105 | Sensory Room | 46 | 3 |  | 120 | 2 | 2 | AHU | 960 | 2.875 | 1 | 2.875 | 1
106 | Office | 76 | 5 |  | 231 | 5 | 5 | AHU | 1848 | 2.4675 | 1 | 2.4675 | 1
107 | Nurse Reception | 0 | 0 | Yes | 81 | 1 | 1 | AHU | 648 | 0 | 0 | 20 | 3
107A | Nurse Office | 48 | 3 | Yes | 189 | 4 | 4 | AHU | 1512 | 1.9048 | 1 | 21.9048 | 3
107B | Offices | 0 | 0 | Yes | 99 | 2 | 2 | AHU | 792 | 0 | 0 | 20 | 3
107C | Storage | 0 | 0 |  | 110 | 2 | 0 | N/A | 880 | 0 | 0 | 0 | 0
108 | Conference | 65 | 4 |  | 238 | 5 | 4 | AHU | 1904 | 2.0483 | 1 | 2.0483 | 1
109 | Admin | 0 | 0 | Yes | 130 | 2 | 2 | AHU | 1040 | 0 | 0 | 20 | 3
110 | Classroom | 340 | 22 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 2.7244 | 1 | 2.7244 | 1
111 | Classroom | 491 | 32 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 3.9343 | 1 | 3.9343 | 1
112 | Classroom | 366 | 24 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 2.9327 | 1 | 2.9327 | 1
113A | Classroom | 1038 | 69 |  | 676 | 15 | 15 | Unit Ventilator | 5408 | 11.5163 | 3 | 11.5163 | 3
126 | Lobby | 55 | 3 |  | 676 | 15 | 3 | Unit Ventilator | 5408 | 0.61021 | 0 | 0.61021 | 0
128 | Corridor | 60 | 4 |  | 456 | 10 | 4 | Unit Ventilator | 3648 | 0.98684 | 0 | 0.98684 | 0
129 | Principal Office | 94 | 6 |  | 220 | 5 | 5 | Unit Ventilator | 1760 | 3.2045 | 1 | 3.2045 | 1
201 | Classroom | 150 | 10 |  | 260 | 5 | 5 | Unit Ventilator | 2080 | 4.3269 | 2 | 4.3269 | 2
202 | Classroom | 390 | 26 |  | 884 | 20 | 20 | Unit Ventilator | 7072 | 3.3088 | 1 | 3.3088 | 1
203 | Classroom | 302 | 20 |  | 884 | 20 | 20 | Unit Ventilator | 7072 | 2.5622 | 1 | 2.5622 | 1
204 | Classroom | 493 | 32 |  | 725 | 16 | 16 | Unit Ventilator | 5800 | 5.1 | 2 | 5.1 | 2
205 | Classroom | 475 | 31 |  | 850 | 19 | 19 | Unit Ventilator | 6800 | 4.1912 | 2 | 4.1912 | 2
206 | Classroom | 488 | 32 |  | 918 | 20 | 20 | Unit Ventilator | 7344 | 3.9869 | 1 | 3.9869 | 1
207 | Classroom | 570 | 38 |  | 990 | 22 | 22 | Unit Ventilator | 7920 | 4.3182 | 2 | 4.3182 | 2
208 | Classroom | 407 | 27 |  | 362 | 8 | 8 | Unit Ventilator | 2896 | 8.4323 | 2 | 8.4323 | 2
208A | Classroom | 74 | 4 |  | 195 | 4 | 4 | Unit Ventilator | 1560 | 2.8462 | 1 | 2.8462 | 1
209 | Classroom | 461 | 30 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 5.1451 | 2 | 5.1451 | 2
210 | Classroom | 357 | 23 |  | 957 | 21 | 21 | Unit Ventilator | 7656 | 2.7978 | 1 | 2.7978 | 1
211 | Classroom | 545 | 36 |  | 990 | 22 | 22 | Unit Ventilator | 7920 | 4.1288 | 2 | 4.1288 | 2
212 | Classroom | 416 | 27 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.8424 | 1 | 3.8424 | 1
213 | Classroom | 444 | 29 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 3.6039 | 1 | 3.6039 | 1
214 | Classroom | 430 | 28 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.7326 | 1 | 3.7326 | 1
215 | Classroom | 429 | 28 |  | 952 | 21 | 21 | Unit Ventilator | 7616 | 3.3797 | 1 | 3.3797 | 1
216 | Classroom | 180 | 12 |  | 325 | 7 | 7 | Unit Ventilator | 2600 | 4.1538 | 2 | 4.1538 | 2
217 | Classroom | 206 | 13 |  | 420 | 9 | 9 | Unit Ventilator | 3360 | 3.6786 | 1 | 3.6786 | 1
218 | Classroom | 0 | 0 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
225 | Library | 1255 | 83 |  | 3628 | 82 | 82 | Unit Ventilator | 29024 | 2.5944 | 1 | 2.5944 | 1
301 | Classroom | 570 | 38 |  | 957 | 21 | 21 | Unit Ventilator | 7656 | 4.4671 | 2 | 4.4671 | 2
302 | Classroom | 289 | 19 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.5087 | 1 | 2.5087 | 1
303 | Classroom | 328 | 21 |  | 957 | 21 | 21 | Unit Ventilator | 7656 | 2.5705 | 1 | 2.5705 | 1
304 | Classroom | 501 | 33 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 4.9834 | 2 | 4.9834 | 2
305 | Classroom | 336 | 22 |  | 1020 | 23 | 22 | Unit Ventilator | 8160 | 2.4706 | 1 | 2.4706 | 1
306 | Classroom | 545 | 36 |  | 1020 | 23 | 23 | Unit Ventilator | 8160 | 4.0074 | 2 | 4.0074 | 2
307 | Classroom | 374 | 24 |  | 506 | 11 | 11 | Unit Ventilator | 4048 | 5.5435 | 2 | 5.5435 | 2
308 | Classroom | 418 | 27 |  | 460 | 10 | 10 | Unit Ventilator | 3680 | 6.8152 | 2 | 6.8152 | 2
309 | Classroom | 550 | 36 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 4.4643 | 2 | 4.4643 | 2
310 | Classroom | 441 | 29 |  | 1020 | 23 | 23 | Unit Ventilator | 8160 | 3.2426 | 1 | 3.2426 | 1
311 | Classroom | 439 | 29 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 3.5633 | 1 | 3.5633 | 1
312 | Classroom | 401 | 26 |  | 696 | 15 | 15 | Unit Ventilator | 5568 | 4.3211 | 2 | 4.3211 | 2
313 | Classroom | 530 | 35 |  | 957 | 21 | 21 | Unit Ventilator | 7656 | 4.1536 | 2 | 4.1536 | 2
314 | Classroom | 325 | 21 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 2.8409 | 1 | 2.8409 | 1
315 | Classroom | 568 | 37 |  | 1650 | 37 | 37 | Unit Ventilator | 13200 | 2.5818 | 1 | 2.5818 | 1
316 | Classroom | 318 | 21 |  | 1650 | 37 | 21 | Unit Ventilator | 13200 | 1.4455 | 1 | 1.4455 | 1
317 | Classroom | 300 | 20 |  | 1664 | 37 | 20 | Unit Ventilator | 13312 | 1.3522 | 1 | 1.3522 | 1
318 | Classroom | 62 | 4 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
- | B.E. Office | 139 | 9 |  | 88 | 2 | 2 | AHU | 704 | 11.8466 | 3 | 11.8466 | 3
- | GYM | 1357 | 90 |  | 6110 | 138 | 90 | AHU | 48880 | 1.6657 | 1 | 1.6657 | 1
- | Stage/Auditorium/Cafeteria | 0 | 0 |  | 4588 | 104 | 0 | AHU | 36704 | 0 | 0 | 0 | 0
- | Kitchen | 47 | 3 |  | 403 | 9 | 3 | AHU | 3224 | 0.87469 | 0 | 0.87469 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-07 | [8 empty] | unk | unk | unk | unk
School: | Horatio Hackett Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Part 2 | Part 3 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
104 | Library | 501 | 33 | Yes | 1920 | 43 | 43 | Unit Ventilator | 15360 | 1.957 | 1 | 21.957 | 3
106 | Gym Mechanical | 497 | 33 |  | 624 | 14 | 14 | AHU | 4992 | 5.9736 | 2 | 5.9736 | 2
107 | Gym Mechanical | 959 | 63 |  | 1400 | 31 | 31 | AHU | 11200 | 5.1375 | 2 | 5.1375 | 2
108 | Lounge | 299 | 19 |  | 560 | 12 | 12 | Unit Ventilator | 4480 | 4.0045 | 2 | 4.0045 | 2
109 | Classroom | 394 | 26 |  | 1136 | 25 | 25 | Unit Ventilator | 9088 | 2.6012 | 1 | 2.6012 | 1
110 | Classroom | 323 | 21 |  | 1024 | 23 | 21 | Unit Ventilator | 8192 | 2.3657 | 1 | 2.3657 | 1
111 | Classroom | 284 | 18 |  | 776 | 17 | 17 | Unit Ventilator | 6208 | 2.7448 | 1 | 2.7448 | 1
112 | Classroom | 280 | 18 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 2.9167 | 1 | 2.9167 | 1
201 | Classroom | 279 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4911 | 1 | 2.4911 | 1
202 | Classroom | 658 | 43 |  | 784 | 17 | 17 | Unit Ventilator | 6272 | 6.2946 | 2 | 6.2946 | 2
203 | Classroom | 335 | 22 |  | 784 | 17 | 17 | Unit Ventilator | 6272 | 3.2047 | 1 | 3.2047 | 1
204 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | Unit Ventilator | 6720 | 0 | 0 | 20 | 3
205 | Classroom | 475 | 31 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 4.2411 | 2 | 4.2411 | 2
205A | Sm office / Speech Room | 223 | 14 |  | 304 | 6 | 6 | Unit Ventilator | 2432 | 5.5016 | 2 | 5.5016 | 2
206 | Classroom | 0 | 0 | Yes | 696 | 15 | 15 | Unit Ventilator | 5568 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 488 | 11 | 11 | Unit Ventilator | 3904 | 0 | 0 | 20 | 3
207A | Small Office | 120 | 8 |  | 248 | 5 | 5 | Unit Ventilator | 1984 | 3.629 | 1 | 3.629 | 1
208 | Classroom | 278 | 18 |  | 784 | 17 | 17 | Unit Ventilator | 6272 | 2.6594 | 1 | 2.6594 | 1
209 | Classroom | 362 | 24 |  | 672 | 15 | 15 | Unit Ventilator | 5376 | 4.0402 | 2 | 4.0402 | 2
210 | Classroom | 0 | 0 | Yes | 784 | 17 | 17 | Unit Ventilator | 6272 | 0 | 0 | 20 | 3
211 | Classroom | 334 | 22 |  | 784 | 17 | 17 | Unit Ventilator | 6272 | 3.1952 | 1 | 3.1952 | 1
212 | Classroom | 355 | 23 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.1696 | 1 | 3.1696 | 1
212A | Office/Councelors |  | 0 |  | 336 | 7 | 0 | N/A | 2688 | unk | unk | unk | unk
214 | Classroom | 455 | 30 |  | 864 | 19 | 19 | AHU | 6912 | 3.9497 | 1 | 3.9497 | 1
215 | Classroom | 405 | 27 |  | 920 | 20 | 20 | AHU | 7360 | 3.3016 | 1 | 3.3016 | 1
216 | Classroom | 505 | 33 |  | 832 | 18 | 18 | AHU | 6656 | 4.5523 | 2 | 4.5523 | 2
217 | Classroom | 390 | 26 |  | 768 | 17 | 17 | Unit Ventilator | 6144 | 3.8086 | 1 | 3.8086 | 1
218 | Classroom | 311 | 20 | Yes | 976 | 22 | 22 | AHU | 7808 | 2.3899 | 1 | 22.3899 | 3
219 | Classroom | 405 | 27 |  | 880 | 20 | 20 | AHU | 7040 | 3.4517 | 1 | 3.4517 | 1
219c | Classroom | 123 | 8 |  | 288 | 6 | 6 | Unit Ventilator | 2304 | 3.2031 | 1 | 3.2031 | 1
305 | Classroom | 400 | 26 |  | 1000 | 22 | 22 | Unit Ventilator | 8000 | 3 | 1 | 3 | 1
306 | Classroom | 0 | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | 0 | 0 | 20 | 3
307 | Classroom | 315 | 21 |  | 824 | 18 | 18 | Unit Ventilator | 6592 | 2.8671 | 1 | 2.8671 | 1
308 | Classroom | 329 | 21 |  | 824 | 18 | 18 | Unit Ventilator | 6592 | 2.9945 | 1 | 2.9945 | 1
308D | Councelors | 38 | 2 | Yes | 384 | 8 | 8 | Unit Ventilator | 3072 | 0.74219 | 0 | 20.7422 | 3
309 | Classroom | 395 | 26 |  | 944 | 21 | 21 | Unit Ventilator | 7552 | 3.1382 | 1 | 3.1382 | 1
- | Caf/Auditorium | 1435 | 95 |  | 6914 | 157 | 95 | AHU | 55312 | 1.5566 | 1 | 1.5566 | 1
- | GYM | 964 | 64 |  | 4770 | 108 | 64 | AHU | 38160 | 1.5157 | 1 | 1.5157 | 1
- | Kitchen | 413 | 27 |  | 954 | 21 | 21 | AHU | 7632 | 3.2469 | 1 | 3.2469 | 1
- | Main Office | 304 | 20 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.7404 | 1 | 2.7404 | 1
- | Nurses Office | 50 | 3 | Yes | 564 | 12 | 12 | Unit Ventilator | 4512 | 0.66489 | 0 | 20.6649 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-08 | [8 empty] | unk | unk | unk | unk
School: | Andrew Hamilton Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Capital | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
104 | Classroom | 398 | 26 |  | 598 | 13 | 13 | Unit Ventilator | 4784 | 4.9916 | 2 | 4.9916 | 2
106 | Classroom | 407 | 27 |  | 755 | 17 | 17 | Unit Ventilator | 6040 | 4.043 | 2 | 4.043 | 2
107 | Classroom | 376 | 25 |  | 599 | 13 | 13 | Unit Ventilator | 4792 | 4.7078 | 2 | 4.7078 | 2
111 | Cafeteria | 1724 | 114 |  | 2444 | 55 | 55 | AHU | 19552 | 5.2905 | 2 | 5.2905 | 2
112 | Auditorium | 813 | 54 |  | 3875 | 88 | 54 | AHU | 31000 | 1.5735 | 1 | 1.5735 | 1
119 | Music | 391 | 26 |  | 827 | 18 | 18 | AHU | 6616 | 3.5459 | 1 | 3.5459 | 1
121 | Gym | 1663 | 110 |  | 4628 | 105 | 105 | AHU | 37024 | 2.695 | 1 | 2.695 | 1
127 | Classroom | 595 | 39 |  | 1186 | 26 | 26 | Unit Ventilator | 9488 | 3.7626 | 1 | 3.7626 | 1
128 | Classroom | 628 | 41 |  | 1370 | 31 | 31 | Unit Ventilator | 10960 | 3.438 | 1 | 3.438 | 1
129 | Classroom | 565 | 37 |  | 1112 | 25 | 25 | Unit Ventilator | 8896 | 3.8107 | 1 | 3.8107 | 1
130 | Classroom | 608 | 40 |  | 1378 | 31 | 31 | Unit Ventilator | 11024 | 3.3091 | 1 | 3.3091 | 1
131 | Classroom | 575 | 38 |  | 1169 | 26 | 26 | Unit Ventilator | 9352 | 3.6891 | 1 | 3.6891 | 1
200 | Classroom | 415 | 27 |  | 763 | 17 | 17 | Unit Ventilator | 6104 | 4.0793 | 2 | 4.0793 | 2
201 | Classroom | 527 | 35 |  | 776 | 17 | 17 | Unit Ventilator | 6208 | 5.0934 | 2 | 5.0934 | 2
202 | Teachers Lounge | 300 | 20 |  | 469 | 10 | 10 | Unit Ventilator | 3752 | 4.7974 | 2 | 4.7974 | 2
205 | Team Planning | 353 | 23 |  | 431 | 9 | 9 | Unit Ventilator | 3448 | 6.1427 | 2 | 6.1427 | 2
206 | Classroom | 454 | 30 |  | 595 | 13 | 13 | Unit Ventilator | 4760 | 5.7227 | 2 | 5.7227 | 2
207 | Classroom | 454 | 30 |  | 847 | 19 | 19 | Unit Ventilator | 6776 | 4.0201 | 2 | 4.0201 | 2
209 | General Office | 750 | 50 |  | 866 | 19 | 19 | Unit Ventilator | 6928 | 6.4954 | 2 | 6.4954 | 2
223 | Classroom | 432 | 28 |  | 847 | 19 | 19 | Unit Ventilator | 6776 | 3.8253 | 1 | 3.8253 | 1
224 | Classroom | 426 | 28 |  | 837 | 19 | 19 | Unit Ventilator | 6696 | 3.8172 | 1 | 3.8172 | 1
225 | Classroom | 394 | 26 |  | 837 | 19 | 19 | Unit Ventilator | 6696 | 3.5305 | 1 | 3.5305 | 1
226 | Classroom | 393 | 26 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.5089 | 1 | 3.5089 | 1
227 | Classroom | 395 | 26 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 3.5607 | 1 | 3.5607 | 1
228 | Classroom | 477 | 31 |  | 847 | 19 | 19 | Unit Ventilator | 6776 | 4.2237 | 2 | 4.2237 | 2
300 | Classroom | 400 | 26 |  | 793 | 18 | 18 | Unit Ventilator | 6344 | 3.7831 | 1 | 3.7831 | 1
301 | Classroom | 421 | 28 |  | 791 | 17 | 17 | Unit Ventilator | 6328 | 3.9918 | 1 | 3.9918 | 1
302 | Classroom | 393 | 26 |  | 786 | 17 | 17 | Unit Ventilator | 6288 | 3.75 | 1 | 3.75 | 1
303 | Classroom | 365 | 24 |  | 640 | 14 | 14 | Unit Ventilator | 5120 | 4.2773 | 2 | 4.2773 | 2
306 | Classroom | 413 | 27 |  | 793 | 18 | 18 | Unit Ventilator | 6344 | 3.9061 | 1 | 3.9061 | 1
307 | Classroom | 464 | 30 |  | 793 | 18 | 18 | Unit Ventilator | 6344 | 4.3884 | 2 | 4.3884 | 2
309 | Classroom | 306 | 20 |  | 597 | 13 | 13 | Unit Ventilator | 4776 | 3.8442 | 1 | 3.8442 | 1
310 | Classroom | 0 | 0 | Yes | 708 | 16 | 16 |  | 5664 | 0 | 0 | 20 | 3
311J | Janitors | 173 | 11 |  | 59 | 1 | 1 | Unit Ventilator | 472 | 21.9915 | 3 | 21.9915 | 3
314 | Office | 551 | 36 |  | 214 | 4 | 4 | Unit Ventilator | 1712 | 19.3107 | 3 | 19.3107 | 3
315 | Office | 724 | 48 |  | 214 | 4 | 4 | Unit Ventilator | 1712 | 25.3738 | 4 | 25.3738 | 4
318 | Classroom | 382 | 25 |  | 911 | 20 | 20 | Unit Ventilator | 7288 | 3.1449 | 1 | 3.1449 | 1
319 | Classroom | 0 | 0 | Yes | 616 | 14 | 14 | Unit Ventilator | 4928 | 0 | 0 | 20 | 3
320 | Team Planning | 0 | 0 | Yes | 235 | 5 | 5 | Unit Ventilator | 1880 | 0 | 0 | 20 | 3
321 | Team Planning | 300 | 20 |  | 243 | 5 | 5 | Unit Ventilator | 1944 | 9.2593 | 2 | 9.2593 | 2
322 | Classroom | 450 | 30 |  | 820 | 18 | 18 | Unit Ventilator | 6560 | 4.1159 | 2 | 4.1159 | 2
323 | Classroom | 0 | 0 | Yes | 620 | 14 | 14 | Unit Ventilator | 4960 | 0 | 0 | 20 | 3
327 | Office | 432 | 28 |  | 201 | 4 | 4 | Unit Ventilator | 1608 | 16.1194 | 3 | 16.1194 | 3
328 | Office | 735 | 49 |  | 233 | 5 | 5 | Unit Ventilator | 1864 | 23.6588 | 3 | 23.6588 | 3
331 | Classroom | 0 | 0 | Yes | 667 | 15 | 15 | Unit Ventilator | 5336 | 0 | 0 | 20 | 3
332 | Classroom | 339 | 22 |  | 625 | 14 | 14 | Unit Ventilator | 5000 | 4.068 | 2 | 4.068 | 2
333 | Classroom | 423 | 28 |  | 894 | 20 | 20 | Unit Ventilator | 7152 | 3.5487 | 1 | 3.5487 | 1
334 | Classroom | 393 | 26 |  | 800 | 18 | 18 | Unit Ventilator | 6400 | 3.6844 | 1 | 3.6844 | 1
335 | Classroom | 838 | 55 |  | 1684 | 38 | 38 | Unit Ventilator | 13472 | 3.7322 | 1 | 3.7322 | 1
336 | Classroom | 375 | 25 |  | 908 | 20 | 20 | Unit Ventilator | 7264 | 3.0975 | 1 | 3.0975 | 1
337 | Classroom | 0 | 0 | Yes | 932 | 21 | 21 | Unit Ventilator | 7456 | 0 | 0 | 20 | 3
- | Library | 2442 | 162 |  | 3672 | 83 | 83 | Unit Ventilator | 29376 | 4.9877 | 2 | 4.9877 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-21 | [8 empty] | unk | unk | unk | unk
School: | John Hancock Demonstrative Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 127 | 8 |  | 528 | 12 | 8 | Unit Ventilator | 4224 | 1.804 | 1 | 1.804 | 1
102 | Classroom | 416 | 27 |  | 750 | 17 | 17 | Unit Ventilator | 6000 | 4.16 | 2 | 4.16 | 2
103 | Classroom | 123 | 8 |  | 567 | 12 | 8 | Unit Ventilator | 4536 | 1.627 | 1 | 1.627 | 1
104 | Classroom | 283 | 18 |  | 483 | 10 | 10 | Unit Ventilator | 3864 | 4.3944 | 2 | 4.3944 | 2
105 | Classroom | 0 | 0 | Yes | 567 | 12 | 12 | Unit Ventilator | 4536 | 0 | 0 | 20 | 3
106 | Classroom | 171 | 11 |  | 756 | 17 | 11 | Unit Ventilator | 6048 | 1.6964 | 1 | 1.6964 | 1
107 | Classroom | 237 | 15 |  | 806 | 18 | 15 | Unit Ventilator | 6448 | 2.2053 | 1 | 2.2053 | 1
108 | Classroom | 0 | 0 | Yes | 648 | 14 | 14 | Unit Ventilator | 5184 | 0 | 0 | 20 | 3
109 | Classroom | 173 | 11 |  | 638 | 14 | 11 | Unit Ventilator | 5104 | 2.0337 | 1 | 2.0337 | 1
110 | Classroom | 233 | 15 |  | 812 | 18 | 15 | Unit Ventilator | 6496 | 2.1521 | 1 | 2.1521 | 1
111 | Classroom | 168 | 11 |  | 588 | 13 | 11 | Unit Ventilator | 4704 | 2.1429 | 1 | 2.1429 | 1
200 | Classroom | 323 | 21 | Yes | 510 | 11 | 11 | Unit Ventilator | 4080 | 4.75 | 2 | 24.75 | 4
200A | Office |  | 0 | Yes |  | 0 | 0 |  |  | unk | unk | 20 | 3
202 | Classroom | 432 | 28 |  | 1271 | 28 | 28 | Unit Ventilator | 10168 | 2.5492 | 1 | 2.5492 | 1
203 | Classroom | 299 | 19 |  | 588 | 13 | 13 | Unit Ventilator | 4704 | 3.8138 | 1 | 3.8138 | 1
204 | Classroom | 324 | 21 |  | 575 | 13 | 13 | Unit Ventilator | 4600 | 4.2261 | 2 | 4.2261 | 2
205 | Classroom | 255 | 17 |  | 616 | 14 | 14 | Unit Ventilator | 4928 | 3.1047 | 1 | 3.1047 | 1
206 | Classroom | 324 | 21 |  | 1116 | 25 | 21 | Unit Ventilator | 8928 | 2.1774 | 1 | 2.1774 | 1
207 | Classroom | 310 | 20 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.691 | 1 | 2.691 | 1
208 | Classroom | 308 | 20 |  | 837 | 19 | 19 | Unit Ventilator | 6696 | 2.7599 | 1 | 2.7599 | 1
209 | Classroom | 312 | 20 |  | 868 | 19 | 19 | Unit Ventilator | 6944 | 2.6959 | 1 | 2.6959 | 1
210 | Classroom | 303 | 20 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 3.1216 | 1 | 3.1216 | 1
211 | Classroom | 298 | 19 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 2.9642 | 1 | 2.9642 | 1
212 | Classroom |  | 0 | Yes | 744 | 16 | 16 | Unit Ventilator | 5952 | unk | unk | 20 | 3
213 | Classroom | 174 | 11 | Yes | 806 | 18 | 18 | Unit Ventilator | 6448 | 1.6191 | 1 | 21.6191 | 3
214 | Computer Lab | 312 | 20 |  | 462 | 10 | 10 | Unit Ventilator | 3696 | 5.0649 | 2 | 5.0649 | 2
215 | Classroom | 0 | 0 | Yes | 364 | 8 | 8 | Unit Ventilator | 2912 | 0 | 0 | 20 | 3
216 | Classroom | 0 | 0 |  | 364 | 8 | 0 | Unit Ventilator | 2912 | 0 | 0 | 0 | 0
217 | Classroom | 334 | 22 |  | 875 | 19 | 19 | Unit Ventilator | 7000 | 2.8629 | 1 | 2.8629 | 1
219 | Classroom | 294 | 19 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.7841 | 1 | 2.7841 | 1
218 | Nurse Office |  | 0 | Yes | 252 | 5 | 5 |  | 2016 | unk | unk | 20 | 3
220 | Office | 0 | 0 | Yes | 126 | 2 | 2 | Unit Ventilator | 1008 | 0 | 0 | 20 | 3
B213 | Classroom |  | 0 | Yes | 363 | 8 | 8 |  | 2904 | unk | unk | 20 | 3
B3 | Faculty Lounge | 184 | 12 | Yes | 540 | 12 | 12 | Unit Ventilator | 4320 | 2.5556 | 1 | 22.5556 | 3
B13 | Classroom |  | 0 | Yes |  | 0 | 0 |  |  | unk | unk | 20 | 3
HS215 | Classroom |  | 0 | Yes | 608 | 13 | 13 |  | 4864 | unk | unk | 20 | 3
HS216 | Classroom |  | 0 | Yes | 608 | 13 | 13 |  | 4864 | unk | unk | 20 | 3
- | Classroom Behind kitchen | 37 | 2 |  | 224 | 5 | 2 | Unit Ventilator | 1792 | 1.2388 | 1 | 1.2388 | 1
- | Gym Office | 0 | 0 | Yes | 100 | 2 | 2 | Unit Ventilator | 800 | 0 | 0 | 20 | 3
- | Gym |  | 0 |  | 288 | 6 | 0 | AHU | 2304 | unk | unk | unk | unk
- | Cafeteria | 0 | 0 |  | 4600 | 104 | 0 | AHU | 36800 | 0 | 0 | 0 | 0
- | Kitchen | 0 | 0 | Yes | 448 | 10 | 10 | Unit Ventilator | 3584 | 0 | 0 | 20 | 3
- | Main Lobby | 0 | 0 |  | 720 | 16 | 0 | Unit Ventilator | 5760 | 0 | 0 | 0 | 0
- | Main Office | 201 | 13 |  | 340 | 7 | 7 | Unit Ventilator | 2720 | 4.4338 | 2 | 4.4338 | 2
- | Main Office Side Office | 0 | 0 |  | 104 | 2 | 0 | Unit Ventilator | 832 | 0 | 0 | 0 | 0
- | Principals Office | 196 | 13 |  | 238 | 5 | 5 | Unit Ventilator | 1904 | 6.1765 | 2 | 6.1765 | 2
Assistant Principal | Office |  | 0 | Yes |  | 0 | 0 |  |  | unk | unk | 20 | 3
Dean | Office |  | 0 | Yes |  | 0 | 0 |  |  | unk | unk | 20 | 3
- | Library | 692 | 46 |  | 1520 | 34 | 34 | Unit Ventilator | 12160 | 3.4145 | 1 | 3.4145 | 1
- | Office Across from 210 | 0 | 0 |  | 120 | 2 | 0 | N/A | 960 | 0 | 0 | 0 | 0
- | Office across from gym | 0 | 0 |  | 204 | 4 | 0 | Unit Ventilator | 1632 | 0 | 0 | 0 | 0
- | Office across from Room 107 | 76 | 5 |  | 140 | 3 | 3 | Unit Ventilator | 1120 | 4.0714 | 2 | 4.0714 | 2
- | Office across from room 110 | 115 | 7 |  | 140 | 3 | 3 | Unit Ventilator | 1120 | 6.1607 | 2 | 6.1607 | 2
- | Office Next to gym | 0 | 0 |  | 80 | 1 | 0 | Unit Ventilator | 640 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-05-03 | [8 empty] | unk | unk | unk | unk
School: | Warren G. Harding Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | - |  | 0 |  | 288 | 6 | 0 |  | 2304 | unk | unk | unk | unk
101a | - |  | 0 |  | 288 | 6 | 0 |  | 2304 | unk | unk | unk | unk
102 | - |  | 0 | Yes | 1128 | 25 | 25 |  | 9024 | unk | unk | 20 | 3
102a | - |  | 0 |  | 100 | 2 | 0 |  | 800 | unk | unk | unk | unk
103 | - |  | 0 |  | 720 | 16 | 0 |  | 5760 | unk | unk | unk | unk
104 | - |  | 0 | Yes | 888 | 20 | 20 |  | 7104 | unk | unk | 20 | 3
104a | - |  | 0 |  | 110 | 2 | 0 |  | 880 | unk | unk | unk | unk
105 | - |  | 0 |  | 648 | 14 | 0 |  | 5184 | unk | unk | unk | unk
105b | - |  | 0 |  | 770 | 17 | 0 |  | 6160 | unk | unk | unk | unk
106c | - |  | 0 |  | 248 | 5 | 0 |  | 1984 | unk | unk | unk | unk
107 | - |  | 0 |  | 936 | 21 | 0 |  | 7488 | unk | unk | unk | unk
107a | - |  | 0 |  | 248 | 5 | 0 |  | 1984 | unk | unk | unk | unk
107b | - |  | 0 |  | 50 | 1 | 0 |  | 400 | unk | unk | unk | unk
107c | - |  | 0 |  | 25 | 0 | 0 |  | 200 | unk | unk | unk | unk
108 | - |  | 0 | Yes | 886 | 20 | 20 |  | 7088 | unk | unk | 20 | 3
108a | - |  | 0 |  | 130 | 2 | 0 |  | 1040 | unk | unk | unk | unk
108b | - |  | 0 |  | 25 | 0 | 0 |  | 200 | unk | unk | unk | unk
108c | - |  | 0 |  | 50 | 1 | 0 |  | 400 | unk | unk | unk | unk
109 | - |  | 0 |  | 576 | 13 | 0 |  | 4608 | unk | unk | unk | unk
109a | - |  | 0 |  | 135 | 3 | 0 |  | 1080 | unk | unk | unk | unk
110 | - |  | 0 |  | 912 | 20 | 0 |  | 7296 | unk | unk | unk | unk
110a | - |  | 0 |  | 40 | 0 | 0 |  | 320 | unk | unk | unk | unk
111 | - |  | 0 |  | 624 | 14 | 0 |  | 4992 | unk | unk | unk | unk
112 | - |  | 0 |  | 576 | 13 | 0 |  | 4608 | unk | unk | unk | unk
112a | - |  | 0 |  | 308 | 7 | 0 |  | 2464 | unk | unk | unk | unk
113 | - |  | 0 |  | 360 | 8 | 0 |  | 2880 | unk | unk | unk | unk
113a | - |  | 0 |  | 242 | 5 | 0 |  | 1936 | unk | unk | unk | unk
113b | - |  | 0 |  | 352 | 8 | 0 |  | 2816 | unk | unk | unk | unk
114 | - |  | 0 | Yes | 204 | 4 | 4 |  | 1632 | unk | unk | 20 | 3
116 | - |  | 0 |  | 2120 | 48 | 0 |  | 16960 | unk | unk | unk | unk
116a | - |  | 0 |  | 416 | 9 | 0 |  | 3328 | unk | unk | unk | unk
117 | - |  | 0 |  | 2700 | 61 | 0 |  | 21600 | unk | unk | unk | unk
201 | - |  | 0 | Yes | 360 | 8 | 8 |  | 2880 | unk | unk | 20 | 3
201a | - |  | 0 |  | 432 | 9 | 0 |  | 3456 | unk | unk | unk | unk
202 | - |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | unk | unk | 20 | 3
203 | - |  | 0 |  | 288 | 6 | 0 |  | 2304 | unk | unk | unk | unk
203B | - |  | 0 | Yes | 200 | 4 | 4 |  | 1600 | unk | unk | 20 | 3
204 | - |  | 0 | Yes | 720 | 16 | 16 |  | 5760 | unk | unk | 20 | 3
205 | - |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | unk | unk | 20 | 3
206 | - |  | 0 |  | 319 | 7 | 0 |  | 2552 | unk | unk | unk | unk
206a | - |  | 0 |  | 224 | 5 | 0 |  | 1792 | unk | unk | unk | unk
206b | - |  | 0 |  | 112 | 2 | 0 |  | 896 | unk | unk | unk | unk
208 | - |  | 0 | Yes | 792 | 18 | 18 |  | 6336 | unk | unk | 20 | 3
209 | IMC |  | 0 | Yes | 2160 | 49 | 49 |  | 17280 | unk | unk | 20 | 3
211 | - |  | 0 |  | 936 | 21 | 0 |  | 7488 | unk | unk | unk | unk
212 | - |  | 0 |  | 888 | 20 | 0 |  | 7104 | unk | unk | unk | unk
213 | - |  | 0 |  | 336 | 7 | 0 |  | 2688 | unk | unk | unk | unk
214 | - |  | 0 |  | 696 | 15 | 0 |  | 5568 | unk | unk | unk | unk
215 | - |  | 0 | Yes | 648 | 14 | 14 |  | 5184 | unk | unk | 20 | 3
216 | - |  | 0 |  | 744 | 16 | 0 |  | 5952 | unk | unk | unk | unk
217 | - |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
218 | - |  | 0 |  | 792 | 18 | 0 |  | 6336 | unk | unk | unk | unk
219 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | unk | unk | unk | unk
220 | - |  | 0 |  | 744 | 16 | 0 |  | 5952 | unk | unk | unk | unk
221 | - |  | 0 |  | 744 | 16 | 0 |  | 5952 | unk | unk | unk | unk
222 | - |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | unk | unk | 20 | 3
223 | - |  | 0 | Yes | 816 | 18 | 18 |  | 6528 | unk | unk | 20 | 3
224 | - |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | unk | unk | 20 | 3
225 | - |  | 0 |  | 144 | 3 | 0 |  | 1152 | unk | unk | unk | unk
301 | - |  | 0 |  | 648 | 14 | 0 |  | 5184 | unk | unk | unk | unk
302 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | unk | unk | unk | unk
303 | - |  | 0 | Yes | 390 | 8 | 8 |  | 3120 | unk | unk | 20 | 3
304 | - |  | 0 |  | 720 | 16 | 0 |  | 5760 | unk | unk | unk | unk
305 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | unk | unk | unk | unk
306 | - |  | 0 |  | 966 | 21 | 0 |  | 7728 | unk | unk | unk | unk
307a | - |  | 0 |  | 360 | 8 | 0 |  | 2880 | unk | unk | unk | unk
307b | - |  | 0 |  | 600 | 13 | 0 |  | 4800 | unk | unk | unk | unk
308a | - |  | 0 |  | 480 | 10 | 0 |  | 3840 | unk | unk | unk | unk
308b | - |  | 0 |  | 336 | 7 | 0 |  | 2688 | unk | unk | unk | unk
309 | - |  | 0 |  | 816 | 18 | 0 |  | 6528 | unk | unk | unk | unk
310 | - |  | 0 |  | 1056 | 24 | 0 |  | 8448 | unk | unk | unk | unk
311 | - |  | 0 |  | 960 | 21 | 0 |  | 7680 | unk | unk | unk | unk
311a | - |  | 0 |  | 143 | 3 | 0 |  | 1144 | unk | unk | unk | unk
312 | - |  | 0 | Yes | 936 | 21 | 21 |  | 7488 | unk | unk | 20 | 3
313 | - |  | 0 |  | 984 | 22 | 0 |  | 7872 | unk | unk | unk | unk
314 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | unk | unk | unk | unk
315 | - |  | 0 |  | 360 | 8 | 0 |  | 2880 | unk | unk | unk | unk
316 | - |  | 0 |  | 720 | 16 | 0 |  | 5760 | unk | unk | unk | unk
317 | - |  | 0 | Yes | 720 | 16 | 16 |  | 5760 | unk | unk | 20 | 3
318 | - |  | 0 |  | 744 | 16 | 0 |  | 5952 | unk | unk | unk | unk
320 | - |  | 0 |  | 816 | 18 | 0 |  | 6528 | unk | unk | unk | unk
321 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | unk | unk | unk | unk
322 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | unk | unk | unk | unk
323 | - |  | 0 |  | 768 | 17 | 0 |  | 6144 | unk | unk | unk | unk
324 | - |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | unk | unk | 20 | 3
325 | - |  | 0 |  | 816 | 18 | 0 |  | 6528 | unk | unk | unk | unk
326 | - |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
- | Main Office |  | 0 | Yes | 468 | 10 | 10 |  | 3744 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 144 | 3 | 3 |  | 1152 | unk | unk | 20 | 3
- | Auditorium |  | 0 |  | 1944 | 44 | 0 |  | 15552 | unk | unk | unk | unk
- | Girls Lunchroom |  | 0 |  | 2173 | 49 | 0 |  | 17384 | unk | unk | unk | unk
- | Girls Gym |  | 0 |  | 1419 | 32 | 0 |  | 11352 | unk | unk | unk | unk
- | Boy's Lunchroom |  | 0 |  | 2173 | 49 | 0 |  | 17384 | unk | unk | unk | unk
- | Boy's Gym |  | 0 |  | 1419 | 32 | 0 |  | 11352 | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-21 | [8 empty] | unk | unk | unk | unk
School: | Avery D. Harrington Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | Devine Retest | [7 empty] | unk | unk | unk | unk
| EMCOR Retest | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B1 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | House Fan | 6440 | 0 | 0 | 20 | 3
B2 | Classroom | 0 | 0 | Yes | 594 | 13 | 13 | House Fan | 4752 | 0 | 0 | 20 | 3
B3 | Classroom | 530 | 35 |  | 1122 | 25 | 25 | Unit Ventilator | 8976 | 3.5428 | 1 | 3.5428 | 1
B4 | B4 | 295 | 19 |  | 1064 | 24 | 19 | Unit Ventilator | 8512 | 2.0794 | 1 | 2.0794 | 1
B5 | Classroom | 299 | 19 |  | 910 | 20 | 19 | Unit Ventilator | 7280 | 2.4643 | 1 | 2.4643 | 1
B6 | - | 363 | 24 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 3.3528 | 1 | 3.3528 | 1
B8 | Classroom | 0 | 0 | Yes | 651 | 14 | 0 | House Fan | 5208 | 0 | 0 | 20 | 3
B9 | - |  | 0 | Yes | 600 | 13 | 13 |  | 4800 | unk | unk | 20 | 3
10A | Classroom |  | 0 | Yes | 253 | 5 |  |  | 2024 | unk | unk | 20 | 3
101 | Classroom | 0 | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | 0 | 0 | 20 | 3
102 | Teachers Lounge |  | 0 |  | 216 | 4 | 0 | House Fan | 1728 | unk | unk | unk | unk
103 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
104 | Classroom |  | 0 | Yes | 840 | 19 | 19 | House Fan | 6720 | unk | unk | 20 | 3
106 | Classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | unk | unk | unk | unk
107 | Classroom | 0 | 0 | Yes | 725 | 16 | 16 | House Fan | 5800 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 750 | 17 | 17 | House Fan | 6000 | 0 | 0 | 20 | 3
109 | Classroom | 651 | 43 |  | 1120 | 25 | 25 | Unit Ventilator | 8960 | 4.3594 | 2 | 4.3594 | 2
109A | Classroom |  | 0 | Yes | 168 | 3 |  |  | 1344 | unk | unk | 20 | 3
109B | Classroom |  | 0 | Yes | 170 | 3 |  |  | 1360 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 775 | 17 | 17 | House Fan | 6200 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 750 | 17 | 17 | House Fan | 6000 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | unk | unk | 20 | 3
203a | Asst Princ Office |  | 0 | Yes | 403 | 9 | 9 | House Fan | 3224 | unk | unk | 20 | 3
204 | Classroom |  | 0 | Yes | 900 | 20 | 20 | House Fan | 7200 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan | 6912 | unk | unk | 20 | 3
206 | Classroom |  | 0 | Yes | 840 | 19 | 19 | House Fan | 6720 | unk | unk | 20 | 3
207 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
208 | Classroom |  | 0 | Yes | 696 | 15 | 15 | House Fan | 5568 | unk | unk | 20 | 3
301 | Classroom |  | 0 | Yes | 900 | 20 | 20 | House Fan | 7200 | unk | unk | 20 | 3
302 | Classroom |  | 0 | Yes | 780 | 17 | 17 | House Fan | 6240 | unk | unk | 20 | 3
303 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | unk | unk | 20 | 3
303a | Counselor Office |  | 0 | Yes | 403 | 9 | 9 | House Fan | 3224 | unk | unk | 20 | 3
304 | Classroom |  | 0 | Yes | 930 | 21 | 21 | House Fan | 7440 | unk | unk | 20 | 3
305 | Classroom |  | 0 | Yes | 810 | 18 | 18 | House Fan | 6480 | unk | unk | 20 | 3
306 | Classroom |  | 0 | Yes | 870 | 19 | 19 | House Fan | 6960 | unk | unk | 20 | 3
307 | Classroom |  | 0 | Yes | 725 | 16 | 16 | House Fan | 5800 | unk | unk | 20 | 3
308 | Classroom |  | 0 | Yes | 754 | 17 | 17 | House Fan | 6032 | unk | unk | 20 | 3
- | Library | 1190 | 79 |  | 3822 | 86 | 79 | Unit Ventilator | 30576 | 2.3352 | 1 | 2.3352 | 1
- | Auditorium | 130 | 8 |  | 90 | 2 | 2 | AHU | 720 | 10.8333 | 3 | 10.8333 | 3
- | Gym |  | 0 |  | 2760 | 62 | 0 |  | 22080 | unk | unk | unk | unk
- | Gym / Storeroom | 0 | 0 |  | 513 | 11 | 0 | AHU | 4104 | 0 | 0 | 0 | 0
| Kitchen |  | 0 | Yes | 120 | 2 |  |  | 960 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 190 | 4 | 4 | House Fan | 1520 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 420 | 9 | 9 | House Fan | 3360 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 377 | 8 | 8 | House Fan | 3016 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-06 | [8 empty] | unk | unk | unk | unk
School: | John F. Hartranft Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 560 | 37 |  | 1519 | 34 | 34 | Unit Ventilator | 12152 | 2.765 | 1 | 2.765 | 1
100A | Office | 0 | 0 |  | 108 | 2 | 0 | AHU | 864 | 0 | 0 | 0 | 0
100C | Office |  | 0 | Yes | 144 | 3 | 3 |  | 1152 | unk | unk | 20 | 3
100E | Office | 0 | 0 |  | 304 | 6 | 0 | AHU | 2432 | 0 | 0 | 0 | 0
100G | Office |  | 0 | Yes | 304 | 6 | 6 | AHU | 2432 | unk | unk | 20 | 3
100J | Office | 0 | 0 | Yes | 77 | 1 | 1 | AHU | 616 | 0 | 0 | 20 | 3
101 | Classroom | 310 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7679 | 1 | 2.7679 | 1
102 | Classroom | 309 | 20 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 1.78 | 1 | 21.78 | 3
103 | Classroom | 344 | 22 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 1.9816 | 1 | 21.9816 | 3
104 | Classroom | 440 | 29 |  | 1178 | 26 | 26 | Unit Ventilator | 9424 | 2.8014 | 1 | 2.8014 | 1
105 | Classroom | 348 | 23 |  | 1178 | 26 | 23 | Unit Ventilator | 9424 | 2.2156 | 1 | 2.2156 | 1
106 | Classroom | 258 | 17 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 1.4862 | 1 | 21.4862 | 3
107 | Classroom | 488 | 32 |  | 1302 | 29 | 29 | Unit Ventilator | 10416 | 2.8111 | 1 | 2.8111 | 1
108 | Classroom | 346 | 23 |  | 1178 | 26 | 23 | Unit Ventilator | 9424 | 2.2029 | 1 | 2.2029 | 1
109 | Classroom | 226 | 15 | Yes | 1178 | 26 | 26 | Unit Ventilator | 9424 | 1.4389 | 1 | 21.4389 | 3
110 | Classroom | 277 | 18 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 1.5956 | 1 | 21.5956 | 3
111 | Classroom | 519 | 34 |  | 966 | 21 | 21 | Unit Ventilator | 7728 | 4.0295 | 2 | 4.0295 | 2
112 | Classroom | 500 | 33 |  | 1302 | 29 | 29 | Unit Ventilator | 10416 | 2.8802 | 1 | 2.8802 | 1
113 | Classroom | 485 | 32 |  | 874 | 19 | 19 | Unit Ventilator | 6992 | 4.1619 | 2 | 4.1619 | 2
114 | Classroom | 407 | 27 |  | 950 | 21 | 21 | Unit Ventilator | 7600 | 3.2132 | 1 | 3.2132 | 1
115 | Classroom | 316 | 21 | Yes | 1305 | 29 | 29 | Unit Ventilator | 10440 | 1.8161 | 1 | 21.8161 | 3
116 | Classroom | 261 | 17 | Yes | 1305 | 29 | 29 | Unit Ventilator | 10440 | 1.5 | 1 | 21.5 | 3
117 | Classroom | 313 | 20 | Yes | 1305 | 29 | 29 | Unit Ventilator | 10440 | 1.7989 | 1 | 21.7989 | 3
118 | Classroom | 473 | 31 |  | 1305 | 29 | 29 | Unit Ventilator | 10440 | 2.7184 | 1 | 2.7184 | 1
118A | Classroom | 12 | 0 | Yes | 680 | 15 | 15 | AHU | 5440 | 0.13235 | 0 | 20.1324 | 3
121 | Classroom | 55 | 3 | Yes | 792 | 18 | 18 | AHU | 6336 | 0.52083 | 0 | 20.5208 | 3
121 | Backroom | 59 | 3 |  | 310 | 7 | 3 | AHU | 2480 | 1.4274 | 1 | 1.4274 | 1
200 | Classroom | 368 | 24 | Yes | 1462 | 33 | 33 | Unit Ventilator | 11696 | 1.8878 | 1 | 21.8878 | 3
201 | Classroom | 647 | 43 |  | 1178 | 26 | 26 | Unit Ventilator | 9424 | 4.1193 | 2 | 4.1193 | 2
202 | Classroom | 454 | 30 |  | 1302 | 29 | 29 | Unit Ventilator | 10416 | 2.6152 | 1 | 2.6152 | 1
203 | Classroom | 355 | 23 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 2.0449 | 1 | 22.0449 | 3
204 | Classroom | 258 | 17 | Yes | 1178 | 26 | 26 | Unit Ventilator | 9424 | 1.6426 | 1 | 21.6426 | 3
205 | Classroom | 491 | 32 |  | 1178 | 26 | 26 | Unit Ventilator | 9424 | 3.1261 | 1 | 3.1261 | 1
206 | Classroom | 282 | 18 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 1.6244 | 1 | 21.6244 | 3
207 | Classroom | 225 | 15 | Yes | 1302 | 29 | 29 | Unit Ventilator | 10416 | 1.2961 | 1 | 21.2961 | 3
208 | Classroom | 247 | 16 | Yes | 1179 | 26 | 26 | Unit Ventilator | 9432 | 1.5712 | 1 | 21.5712 | 3
209 | Classroom | 274 | 18 | Yes | 1179 | 26 | 26 | Unit Ventilator | 9432 | 1.743 | 1 | 21.743 | 3
210 | Classroom | 485 | 32 |  | 1302 | 29 | 29 | Unit Ventilator | 10416 | 2.7938 | 1 | 2.7938 | 1
211 | Classroom | 519 | 34 |  | 1302 | 29 | 29 | Unit Ventilator | 10416 | 2.9896 | 1 | 2.9896 | 1
212 | Classroom | 309 | 20 | Yes | 1178 | 26 | 26 | Unit Ventilator | 9424 | 1.9673 | 1 | 21.9673 | 3
214 | Classroom | 325 | 21 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 3.117 | 1 | 3.117 | 1
- | Cafeteria | 2300 | 153 |  | 1593 | 36 | 36 | AHU | 12744 | 10.8286 | 3 | 10.8286 | 3
- | Cafeteria Entrance Hallway | 0 | 0 |  | 730 | 16 | 0 | AHU | 5840 | 0 | 0 | 0 | 0
- | Conference/Office | 0 | 0 |  | 304 | 6 | 0 | AHU | 2432 | 0 | 0 | 0 | 0
- | Engineer Office | 0 | 0 |  | 112 | 2 | 0 | AHU | 896 | 0 | 0 | 0 | 0
- | Engineer Breakroom | 0 | 0 |  | 99 | 2 | 0 | AHU | 792 | 0 | 0 | 0 | 0
- | Gym | 3499 | 233 |  | 6160 | 140 | 140 | AHU | 49280 | 4.2601 | 2 | 4.2601 | 2
- | Kitchen | 0 | 0 |  | 864 | 19 | 0 | AHU | 6912 | 0 | 0 | 0 | 0
- | Main Office | 0 | 0 | Yes | 1056 | 24 | 24 | AHU | 8448 | 0 | 0 | 20 | 3
- | Nurse Office | 0 | 0 | Yes | 425 | 9 | 9 | AHU | 3400 | 0 | 0 | 20 | 3
- | Principal Office | 0 | 0 | Yes | 228 | 5 | 5 | AHU | 1824 | 0 | 0 | 20 | 3
- | Rear Entrance Hallway | 0 | 0 |  | 736 | 16 | 0 | AHU | 5888 | 0 | 0 | 0 | 0
- | Teacher Office | 0 | 0 |  | 77 | 1 | 0 | AHU | 616 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Haverford Child Development Center | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Brothers Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
2 | Classroom | 291 | 19 | Yes | 1058 | 24 | 24 | RTU | 8464 | 2.0629 | 1 | 22.0629 | 3
3 | Classroom | 323 | 21 | Yes | 1058 | 24 | 24 | RTU | 8464 | 2.2897 | 1 | 22.2897 | 3
4 | Classroom | 277 | 18 | Yes | 1058 | 24 | 24 | RTU | 8464 | 1.9636 | 1 | 21.9636 | 3
5 | Classroom | 374 | 24 |  | 1058 | 24 | 24 | RTU | 8464 | 2.6512 | 1 | 2.6512 | 1
5A | Office | 15 | 1 |  | 170 | 3 | 1 | RTU | 1360 | 0.66176 | 0 | 0.66176 | 0
6 | Conference | 418 | 27 |  | 621 | 14 | 14 | RTU | 4968 | 5.0483 | 2 | 5.0483 | 2
7 | Conference | 415 | 27 |  | 621 | 14 | 14 | RTU | 4968 | 5.0121 | 2 | 5.0121 | 2
8 | Classroom | 287 | 19 |  | 560 | 12 | 12 | RTU | 4480 | 3.8438 | 1 | 3.8438 | 1
8A | Office | 336 | 22 |  | 210 | 4 | 4 | RTU | 1680 | 12 | 3 | 12 | 3
9 | Classroom | 723 | 48 |  | 962 | 21 | 21 | RTU | 7696 | 5.6367 | 2 | 5.6367 | 2
10A | Lounge | 34 | 2 |  | 216 | 4 | 2 | RTU | 1728 | 1.1806 | 1 | 1.1806 | 1
10B | Book Storage | 11 | 0 |  | 288 | 6 | 0 | RTU | 2304 | 0.28646 | 0 | 0.28646 | 0
- | Gym | 1065 | 71 |  | 2204 | 50 | 50 | RTU | 17632 | 3.6241 | 1 | 3.6241 | 1
- | Lobby | 18 | 1 |  | 608 | 13 | 1 | RTU | 4864 | 0.22204 | 0 | 0.22204 | 0
- | Storage | 89 | 5 |  | 572 | 13 | 5 | RTU | 4576 | 1.167 | 1 | 1.167 | 1
- | BE Office | 18 | 1 |  | 128 | 2 | 1 | RTU | 1024 | 1.0547 | 1 | 1.0547 | 1
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-05 | [8 empty] | unk | unk | unk | unk
School: | Charles W. Henry Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Devine Part 2 | Devine Part 3 | Devine Part 4 | [5 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 0 | 0 | Yes | 650 | 14 | 14 | Unit Ventilator | 5200 | 0 | 0 | 20 | 3
102 | Classroom | 443 | 29 |  | 837 | 19 | 19 | Unit Ventilator | 6696 | 3.9695 | 1 | 3.9695 | 1
103 | Classroom | 371 | 24 |  | 817 | 18 | 18 | Unit Ventilator | 6536 | 3.4058 | 1 | 3.4058 | 1
104 | Classroom | 374 | 24 |  | 818 | 18 | 18 | Unit Ventilator | 6544 | 3.4291 | 1 | 3.4291 | 1
104A | Office | 0 | 0 | Yes | 57 | 1 | 1 |  | 456 | 0 | 0 | 20 | 3
105 | Classroom | 397 | 26 |  | 951 | 21 | 21 | Unit Ventilator | 7608 | 3.1309 | 1 | 3.1309 | 1
106 | Classroom | 308 | 20 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 2.8344 | 1 | 2.8344 | 1
108 | Classroom | 481 | 32 |  | 650 | 14 | 14 | Unit Ventilator | 5200 | 5.55 | 2 | 5.55 | 2
109 | Classroom | 763 | 50 |  | 712 | 16 | 16 | Unit Ventilator | 5696 | 8.0372 | 2 | 8.0372 | 2
110 | Classroom | 756 | 50 |  | 650 | 14 | 14 | Unit Ventilator | 5200 | 8.7231 | 2 | 8.7231 | 2
110A | Office | 0 | 0 | Yes | 98 | 2 | 2 |  | 784 | 0 | 0 | 20 | 3
114 | Classroom | 773 | 51 |  | 749 | 17 | 17 |  | 5992 | 7.7403 | 2 | 7.7403 | 2
201 | Classroom | 289 | 19 |  | 775 | 17 | 17 | Unit Ventilator | 6200 | 2.7968 | 1 | 2.7968 | 1
202 | Classroom | 314 | 20 |  | 765 | 17 | 17 | Unit Ventilator | 6120 | 3.0784 | 1 | 3.0784 | 1
203 | Classroom | 282 | 18 |  | 781 | 17 | 17 | Unit Ventilator | 6248 | 2.7081 | 1 | 2.7081 | 1
203A | Office | 0 | 0 | Yes | 115 | 2 | 2 |  | 920 | 0 | 0 | 20 | 3
204 | Classroom | 262 | 17 | Yes | 847 | 19 | 19 | Unit Ventilator | 6776 | 2.32 | 1 | 22.32 | 3
206 | Classroom | 285 | 19 |  | 546 | 12 | 12 | Unit Ventilator | 4368 | 3.9148 | 1 | 3.9148 | 1
207 | Classroom | 273 | 18 |  | 815 | 18 | 18 | Unit Ventilator | 6520 | 2.5123 | 1 | 2.5123 | 1
208 | Classroom | 265 | 17 |  | 787 | 17 | 17 | Unit Ventilator | 6296 | 2.5254 | 1 | 2.5254 | 1
208A | Office | 0 | 0 | Yes | 170 | 3 | 3 |  | 1360 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 | Yes | 800 | 18 | 18 | Unit Ventilator | 6400 | 0 | 0 | 20 | 3
210 | Classroom | 398 | 26 |  | 946 | 21 | 21 | Unit Ventilator | 7568 | 3.1554 | 1 | 3.1554 | 1
214 | Classroom | 282 | 18 | Yes | 1736 | 39 | 39 | Unit Ventilator | 13888 | 1.2183 | 1 | 21.2183 | 3
215 | Classroom | 387 | 25 |  | 1128 | 25 | 25 | Unit Ventilator | 9024 | 2.5731 | 1 | 2.5731 | 1
216 | Classroom | 284 | 18 |  | 546 | 12 | 12 | Unit Ventilator | 4368 | 3.9011 | 1 | 3.9011 | 1
217 | Classroom | 393 | 26 |  | 544 | 12 | 12 | Unit Ventilator | 4352 | 5.4182 | 2 | 5.4182 | 2
218 | Classroom | 307 | 20 | Yes | 1023 | 23 | 23 | Unit Ventilator | 8184 | 2.2507 | 1 | 22.2507 | 3
- | Art Classroom | 249 | 16 |  | 778 | 17 | 16 | Unit Ventilator | 6224 | 2.4004 | 1 | 2.4004 | 1
- | Auditorium | 1908 | 127 |  | 2417 | 54 | 54 | Unit Ventilator | 19336 | 5.9206 | 2 | 5.9206 | 2
- | Cafe | 0 | 0 | Yes | 2104 | 47 | 47 | Unit Ventilator | 16832 | 0 | 0 | 20 | 3
- | Gym | 1076 | 71 | Yes | 3199 | 72 | 72 | Unit Ventilator | 25592 | 2.5227 | 1 | 22.5227 | 3
- | Janitor Office | 0 | 0 |  |  | 0 | 0 | N/A |  | unk | unk | unk | unk
- | Music Classroom | 292 | 19 |  | 833 | 18 | 18 | Unit Ventilator | 6664 | 2.6291 | 1 | 2.6291 | 1
- | Sensory Classroom | 0 | 0 | Yes | 377 | 8 | 8 | Unit Ventilator | 3016 | 0 | 0 | 20 | 3
- | Counselor's Office | 0 | 0 |  | 299 | 6 | 0 |  | 2392 | 0 | 0 | 0 | 0
- | Nurse's Office | 0 | 0 | Yes | 263 | 5 | 5 |  | 2104 | 0 | 0 | 20 | 3
- | Medical Waiting Room | 0 | 0 | Yes | 177 | 4 | 4 |  | 1416 | 0 | 0 | 20 | 3
- | Principal's Office | 0 | 0 | Yes | 307 | 6 | 6 |  | 2456 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-16 | [8 empty] | unk | unk | unk | unk
School: | Edward Heston Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Brothers 2nd Retest | [7 empty] | unk | unk | unk | unk
| Devine Brothers 3rd Retest | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 148 | 9 |  | 440 | 10 | 9 | AHU | 3520 | 2.5227 | 1 | 2.5227 | 1
102 | Office | 44 | 2 |  | 180 | 4 | 2 | AHU | 1440 | 1.8333 | 1 | 1.8333 | 1
103 | Classroom | 70 | 4 |  | 308 | 7 | 4 | AHU | 2464 | 1.7045 | 1 | 1.7045 | 1
103B | Office | 53 | 3 |  | 418 | 9 | 3 | AHU | 3344 | 0.95096 | 0 | 0.95096 | 0
104 | Vestible | 25 | 1 |  | 220 | 5 | 1 | Unit Ventilator | 1760 | 0.85227 | 0 | 0.85227 | 0
104A | Office | 36 | 2 |  | 102 | 2 | 2 | AHU | 816 | 2.6471 | 1 | 2.6471 | 1
104B | Security Office | 56 | 3 |  | 123 | 2 | 2 | AHU | 984 | 3.4146 | 1 | 3.4146 | 1
104C | Office | 27 | 1 |  | 99 | 2 | 1 | AHU | 792 | 2.0455 | 1 | 2.0455 | 1
106 | Classroom | 328 | 21 | Yes | 1540 | 35 | 35 | Unit Ventilator | 12320 | 1.5974 | 1 | 21.5974 | 3
107 | Classroom | 35 | 2 | Yes | 440 | 10 | 10 | AHU | 3520 | 0.59659 | 0 | 20.5966 | 3
107A | Office | 74 | 4 |  | 840 | 19 | 4 | AHU | 6720 | 0.66071 | 0 | 0.66071 | 0
107B | Storage | 17 | 1 |  | 196 | 4 | 1 | AHU | 1568 | 0.65051 | 0 | 0.65051 | 0
108 | Classroom | 296 | 19 | Yes | 1540 | 35 | 35 | Unit Ventilator | 12320 | 1.4416 | 1 | 21.4416 | 3
109 | Classroom | 275 | 18 |  | 440 | 10 | 10 | AHU | 3520 | 4.6875 | 2 | 4.6875 | 2
110 | Classroom | 322 | 21 | Yes | 1056 | 24 | 24 | Unit Ventilator | 8448 | 2.2869 | 1 | 22.2869 | 3
112 | Classroom | 312 | 20 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.799 | 1 | 2.799 | 1
114 | Classroom | 276 | 18 |  | 1012 | 23 | 18 | Unit Ventilator | 8096 | 2.0455 | 1 | 2.0455 | 1
116 | Classroom | 279 | 18 | Yes | 968 | 22 | 22 | Unit Ventilator | 7744 | 2.1617 | 1 | 22.1617 | 3
127 | Kitchen | 169 | 11 |  | 972 | 22 | 11 | AHU | 7776 | 1.304 | 1 | 1.304 | 1
200 | Classroom | 296 | 19 |  | 264 | 6 | 6 | Unit Ventilator | 2112 | 8.4091 | 2 | 8.4091 | 2
202 | Classroom | 276 | 18 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 2.9403 | 1 | 2.9403 | 1
204 | Classroom | 316 | 21 |  | 396 | 9 | 9 | Unit Ventilator | 3168 | 5.9848 | 2 | 5.9848 | 2
206 | Classroom | 317 | 21 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 3.3771 | 1 | 3.3771 | 1
208 | Classroom | 281 | 18 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 2.8175 | 1 | 2.8175 | 1
210 | Classroom | 318 | 21 |  | 528 | 12 | 12 | Unit Ventilator | 4224 | 4.517 | 2 | 4.517 | 2
212 | Classroom | 329 | 21 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 3.2988 | 1 | 3.2988 | 1
214 | Classroom | 318 | 21 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 3.1885 | 1 | 3.1885 | 1
216 | Classroom | 270 | 18 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 2.7072 | 1 | 2.7072 | 1
218 | Classroom | 291 | 19 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 2.9178 | 1 | 2.9178 | 1
220 | Classroom | 424 | 28 |  | 748 | 17 | 17 | AHU | 5984 | 4.2513 | 2 | 4.2513 | 2
222 | Classroom | 289 | 19 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 2.8977 | 1 | 2.8977 | 1
224 | Classroom | 284 | 18 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.6894 | 1 | 2.6894 | 1
228 | Room | 55 | 3 | Yes | 264 | 6 | 6 | Unit Ventilator | 2112 | 1.5625 | 1 | 21.5625 | 3
232 | Classroom | 285 | 19 |  | 264 | 6 | 6 | Unit Ventilator | 2112 | 8.0966 | 2 | 8.0966 | 2
300 | Lounge | 347 | 23 |  | 264 | 6 | 6 | Unit Ventilator | 2112 | 9.858 | 2 | 9.858 | 2
301 | Classroom | 175 | 11 | Yes | 1568 | 35 | 35 | AHU | 12544 | 0.83705 | 0 | 20.8371 | 3
302 | Classroom | 291 | 19 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 3.1001 | 1 | 3.1001 | 1
304 | Classroom | 284 | 18 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 2.8476 | 1 | 2.8476 | 1
306 | Classroom | 327 | 21 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 3.2787 | 1 | 3.2787 | 1
308 | Classroom | 321 | 21 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 3.4197 | 1 | 3.4197 | 1
310 | Room | 0 | 0 | Yes | 748 | 17 | 17 | Unit Ventilator | 5984 | 0 | 0 | 20 | 3
312 | Classroom | 289 | 19 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 2.8977 | 1 | 2.8977 | 1
314 | Room | 53 | 3 | Yes | 792 | 18 | 18 | Unit Ventilator | 6336 | 0.50189 | 0 | 20.5019 | 3
316 | Classroom | 290 | 19 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.7462 | 1 | 2.7462 | 1
318 | Room | 0 | 0 | Yes | 748 | 17 | 17 | Unit Ventilator | 5984 | 0 | 0 | 20 | 3
320 | Classroom | 303 | 20 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 3.0381 | 1 | 3.0381 | 1
322 | Room | 249 | 16 |  | 748 | 17 | 16 | Unit Ventilator | 5984 | 2.4967 | 1 | 2.4967 | 1
324 | Classroom | 302 | 20 |  | 748 | 17 | 17 | Unit Ventilator | 5984 | 3.0281 | 1 | 3.0281 | 1
328 | Classroom | 298 | 19 |  | 264 | 6 | 6 | Unit Ventilator | 2112 | 8.4659 | 2 | 8.4659 | 2
- | Copy Room | 38 | 2 |  | 44 | 1 | 1 | Unit Ventilator | 352 | 6.4773 | 2 | 6.4773 | 2
- | Main office | 78 | 5 | Yes | 484 | 11 | 11 | Unit Ventilator | 3872 | 1.2087 | 1 | 21.2087 | 3
- | Nurse | 30 | 2 |  | 176 | 4 | 2 | Unit Ventilator | 1408 | 1.2784 | 1 | 1.2784 | 1
- | Nurse Examination | 76 | 5 |  | 88 | 2 | 2 | Unit Ventilator | 704 | 6.4773 | 2 | 6.4773 | 2
- | Principal | 43 | 2 |  | 176 | 4 | 2 | Unit Ventilator | 1408 | 1.8324 | 1 | 1.8324 | 1
- | Cafeteria/Aud | 4461 | 297 |  | 4268 | 97 | 97 | AHU | 34144 | 7.8392 | 2 | 7.8392 | 2
- | Gym | 2645 | 176 |  | 4620 | 105 | 105 | AHU | 36960 | 4.2938 | 2 | 4.2938 | 2
- | IMC | 1002 | 66 |  | 2948 | 67 | 66 | AHU | 23584 | 2.5492 | 1 | 2.5492 | 1
- | IMC/Classrooms | 58 | 3 |  | 176 | 4 | 3 | AHU | 1408 | 2.4716 | 1 | 2.4716 | 1
- | Teachers Lounge | 52 | 3 | Yes | 296 | 6 | 6 | AHU | 2368 | 1.3176 | 1 | 21.3176 | 3
- | Dean's Office | 31 | 2 |  | 117 | 2 | 2 | AHU | 936 | 1.9872 | 1 | 1.9872 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Hill-Freedman World Academy at Leeds Campus | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Room |  | 0 |  | 775 | 17 | 0 |  | 6200 | unk | unk | unk | unk
2 | Room |  | 0 |  | 1008 | 22 | 0 |  | 8064 | unk | unk | unk | unk
3 | Room | 0 | 0 |  | 832 | 18 | 0 |  | 6656 | 0 | 0 | 0 | 0
4 | Room |  | 0 |  | 784 | 17 | 0 |  | 6272 | unk | unk | unk | unk
5 | Office |  | 0 |  | 240 | 5 | 0 |  | 1920 | unk | unk | unk | unk
5 | Room |  | 0 |  | 1300 | 29 | 0 |  | 10400 | unk | unk | unk | unk
6 | Office |  | 0 |  | 64 | 1 | 0 |  | 512 | unk | unk | unk | unk
6 | Room | 0 | 0 |  | 300 | 6 | 0 |  | 2400 | 0 | 0 | 0 | 0
7 | Room | 0 | 0 |  | 672 | 15 | 0 |  | 5376 | 0 | 0 | 0 | 0
8 | Room |  | 0 |  | 500 | 11 | 0 |  | 4000 | unk | unk | unk | unk
9 | Room |  | 0 |  | 1300 | 29 | 0 |  | 10400 | unk | unk | unk | unk
10 | Room |  | 0 |  | 840 | 19 | 0 |  | 6720 | unk | unk | unk | unk
119 | Classroom |  | 0 | Yes | 504 | 11 | 11 |  | 4032 | unk | unk | 20 | 3
121 | Classroom |  | 0 | Yes | 525 | 11 | 11 |  | 4200 | unk | unk | 20 | 3
124 | Classroom |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | unk | unk | 20 | 3
131 | Classroom |  | 0 | Yes | 735 | 16 | 16 |  | 5880 | unk | unk | 20 | 3
134 | Classroom |  | 0 | Yes | 1224 | 27 | 27 |  | 9792 | unk | unk | 20 | 3
- | Auditorium |  | 0 |  | 8760 | 199 | 0 |  | 70080 | unk | unk | unk | unk
Main Office | Office |  | 0 |  | 588 | 13 | 0 |  | 4704 | unk | unk | unk | unk
Principal | Office |  | 0 |  | 154 | 3 | 0 |  | 1232 | unk | unk | unk | unk
Nurse | Office Suite |  | 0 | Yes | 892 | 20 | 20 |  | 7136 | unk | unk | 20 | 3
- | Boys Gym | 1074 | 71 |  | 5760 | 130 | 71 |  | 46080 | 1.3984 | 1 | 1.3984 | 1
- | Boys Locker Room |  | 0 |  | 3420 | 77 | 0 |  | 27360 | unk | unk | unk | unk
- | Cafeteria |  | 0 |  | 11360 | 258 | 0 |  | 90880 | unk | unk | unk | unk
- | Conference Room |  | 0 |  | 390 | 8 | 0 |  | 3120 | unk | unk | unk | unk
- | Girls Gym |  | 0 |  | 5760 | 130 | 0 |  | 46080 | unk | unk | unk | unk
- | Girls Locker Room |  | 0 |  | 3420 | 77 | 0 |  | 27360 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-28 | [8 empty] | unk | unk | unk | unk
School: | Thomas Holme Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Part 2 | Part 3 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Classroom | 619 | 41 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 4.6941 | 2 | 4.6941 | 2
2 | Classroom | 524 | 34 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 3.9737 | 1 | 3.9737 | 1
3 | Classroom | 285 | 19 |  | 920 | 20 | 19 | Unit Ventilator | 7360 | 2.3234 | 1 | 2.3234 | 1
4 | Classroom | 576 | 38 |  | 1058 | 24 | 24 | Unit Ventilator | 8464 | 4.0832 | 2 | 4.0832 | 2
5 | Classroom | 550 | 36 |  | 1058 | 24 | 24 | Unit Ventilator | 8464 | 3.8989 | 1 | 3.8989 | 1
61 | Classroom | 214 | 14 | Yes | 1040 | 23 | 23 | Unit Ventilator | 8320 | 1.5433 | 1 | 21.5433 | 3
62 | Truancy Court | 207 | 13 | Yes | 520 | 11 | 11 | Unit Ventilator | 4160 | 2.9856 | 1 | 22.9856 | 3
63 | Classroom | 312 | 20 | Yes | 1040 | 23 | 23 | Unit Ventilator | 8320 | 2.25 | 1 | 22.25 | 3
64 | Classroom | 527 | 35 |  | 1040 | 23 | 23 | Unit Ventilator | 8320 | 3.8005 | 1 | 3.8005 | 1
65 | Classroom | 300 | 20 | Yes | 1040 | 23 | 23 | Unit Ventilator | 8320 | 2.1635 | 1 | 22.1635 | 3
66 | Classroom | 423 | 28 |  | 1040 | 23 | 23 | Unit Ventilator | 8320 | 3.0505 | 1 | 3.0505 | 1
101 | Classroom | 679 | 45 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.5353 | 2 | 5.5353 | 2
102 | Classroom | 626 | 41 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.1033 | 2 | 5.1033 | 2
103 | Classroom | 500 | 33 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.0761 | 2 | 4.0761 | 2
104 | Classroom | 615 | 41 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.0136 | 2 | 5.0136 | 2
105 | Classroom | 628 | 41 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.1196 | 2 | 5.1196 | 2
106 | Classroom | 697 | 46 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 7.5761 | 2 | 7.5761 | 2
107 | Classroom | 321 | 21 |  | 960 | 21 | 21 | Unit Ventilator | 7680 | 2.5078 | 1 | 2.5078 | 1
108 | Classroom |  | 0 | Yes | 108 | 2 | 2 |  | 864 | unk | unk | 20 | 3
109 | Classroom | 503 | 33 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.1005 | 2 | 4.1005 | 2
110 | Classroom | 483 | 32 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 3.9375 | 1 | 3.9375 | 1
111 | Classroom | 553 | 36 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.5082 | 2 | 4.5082 | 2
112 | Classroom | 568 | 37 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.6304 | 2 | 4.6304 | 2
113 | Classroom | 622 | 41 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.0707 | 2 | 5.0707 | 2
201 | Classroom | 649 | 43 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.2908 | 2 | 5.2908 | 2
202 | Classroom | 320 | 21 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 2.6087 | 1 | 2.6087 | 1
203 | Classroom | 261 | 17 |  | 920 | 20 | 17 | Unit Ventilator | 7360 | 2.1277 | 1 | 2.1277 | 1
204 | Classroom | 469 | 31 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 3.8234 | 1 | 3.8234 | 1
205 | Classroom | 658 | 43 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.3641 | 2 | 5.3641 | 2
206 | Classroom | 624 | 41 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.087 | 2 | 5.087 | 2
207 | Classroom | 607 | 40 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.9484 | 2 | 4.9484 | 2
208 | Classroom | 626 | 41 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.1033 | 2 | 5.1033 | 2
209 | Classroom | 764 | 50 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 6.2283 | 2 | 6.2283 | 2
210 | Classroom | 589 | 39 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.8016 | 2 | 4.8016 | 2
211 | Classroom | 279 | 18 |  | 920 | 20 | 18 | Unit Ventilator | 7360 | 2.2745 | 1 | 2.2745 | 1
212 | Classroom | 597 | 39 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 4.8668 | 2 | 4.8668 | 2
213 | Classroom | 664 | 44 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.413 | 2 | 5.413 | 2
214 | Classroom | 681 | 45 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 5.5516 | 2 | 5.5516 | 2
215 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | unk | unk | 20 | 3
216 | Classroom |  | 0 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | unk | unk | 20 | 3
- | Auditorium | 0 | 0 |  | 2880 | 65 | 0 | AHU | 23040 | 0 | 0 | 0 | 0
- | Cafeteria | 127 | 8 |  | 2250 | 51 | 8 | Unit Ventilator | 18000 | 0.42333 | 0 | 0.42333 | 0
- | Kitchen |  | 0 | Yes | 475 | 10 | 10 |  | 3800 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 231 | 5 | 5 | Purifier | 1848 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 150 | 3 | 3 |  | 1200 | unk | unk | 20 | 3
- | Vice Principal Office |  | 0 | Yes | 84 | 1 | 1 |  | 672 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 204 | 4 | 4 |  | 1632 | unk | unk | 20 | 3
- | Counselor Office |  | 0 | Yes | 135 | 3 | 3 |  | 1080 | unk | unk | 20 | 3
- | Admin Office |  | 0 | Yes | 156 | 3 | 3 |  | 1248 | unk | unk | 20 | 3
- | Dean Office |  | 0 | Yes | 140 | 3 | 3 |  | 1120 | unk | unk | 20 | 3
- | School Police Office |  | 0 | Yes | 99 | 2 | 2 |  | 792 | unk | unk | 20 | 3
- | Gym | 189 | 12 | Yes | 3950 | 89 | 89 | Unit Ventilator | 31600 | 0.35886 | 0 | 20.3589 | 3
- | Music | 0 | 0 |  | 2340 | 53 | 0 | AHU | 18720 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Francis Hopkinson Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Main Building Retest | [7 empty] | unk | unk | unk | unk
School: | Francis Hopkinson Elementary School- Little School House | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Main Building | [9 empty] | unk | unk | unk | unk
101 | Classrooms | 1030 | 68 |  | 687 | 15 | 15 | House Fan | 5496 | 11.2445 | 3 | 11.2445 | 3
102 | Classrooms | 873 | 58 |  | 627 | 14 | 14 | House Fan | 5016 | 10.4426 | 3 | 10.4426 | 3
103 | Classrooms | 276 | 18 |  | 696 | 15 | 15 | House Fan | 5568 | 2.9741 | 1 | 2.9741 | 1
104 | Classrooms | 1044 | 69 |  | 643 | 14 | 14 | House Fan | 5144 | 12.1773 | 3 | 12.1773 | 3
105 | Classrooms | 562 | 37 |  | 638 | 14 | 14 | House Fan | 5104 | 6.6066 | 2 | 6.6066 | 2
106 | Classroom | 953 | 63 |  | 648 | 14 | 14 | House Fan | 5184 | 11.0301 | 3 | 11.0301 | 3
107 | Classroom | 1035 | 69 |  | 638 | 14 | 14 | House Fan | 5104 | 12.1669 | 3 | 12.1669 | 3
108 | Classrooms | 432 | 28 |  | 675 | 15 | 15 | House Fan | 5400 | 4.8 | 2 | 4.8 | 2
109 | Classrooms | 635 | 42 |  | 631 | 14 | 14 | House Fan | 5048 | 7.5475 | 2 | 7.5475 | 2
110 | Classroom | 322 | 21 |  | 695 | 15 | 15 | House Fan | 5560 | 3.4748 | 1 | 3.4748 | 1
201 | Classrooms | 707 | 47 |  | 696 | 15 | 15 | House Fan | 5568 | 7.6185 | 2 | 7.6185 | 2
202 | Classroom | 767 | 51 |  | 656 | 14 | 14 | House Fan | 5248 | 8.7691 | 2 | 8.7691 | 2
203 | Classrooms | 734 | 48 |  | 693 | 15 | 15 | House Fan | 5544 | 7.9437 | 2 | 7.9437 | 2
204 | Classrooms | 787 | 52 |  | 647 | 14 | 14 | House Fan | 5176 | 9.1229 | 2 | 9.1229 | 2
205 | Classroom | 737 | 49 |  | 674 | 15 | 15 | House Fan | 5392 | 8.201 | 2 | 8.201 | 2
206 | Classroom | 792 | 52 |  | 657 | 14 | 14 | House Fan | 5256 | 9.0411 | 2 | 9.0411 | 2
207 | Classrooms | 618 | 41 |  | 679 | 15 | 15 | House Fan | 5432 | 6.8262 | 2 | 6.8262 | 2
208 | Classroom | 702 | 46 |  | 686 | 15 | 15 | House Fan | 5488 | 7.6749 | 2 | 7.6749 | 2
209 | Classroom | 892 | 59 |  | 667 | 15 | 15 | House Fan | 5336 | 10.03 | 3 | 10.03 | 3
210 | Classroom | 386 | 25 |  | 687 | 15 | 15 | House Fan | 5496 | 4.214 | 2 | 4.214 | 2
300 | Office |  | 0 | Yes | 275 | 6 | 6 | House Fan | 2200 | unk | unk | 20 | 3
301 | Classrooms | 425 | 28 |  | 677 | 15 | 15 | House Fan | 5416 | 4.7083 | 2 | 4.7083 | 2
302 | Classroom | 0 | 0 | Yes | 668 | 15 | 15 | House Fan | 5344 | 0 | 0 | 20 | 3
303 | Classrooms | 263 | 17 |  | 694 | 15 | 15 | House Fan | 5552 | 2.8422 | 1 | 2.8422 | 1
304 | Classrooms | 612 | 40 |  | 614 | 13 | 13 | House Fan | 4912 | 7.4756 | 2 | 7.4756 | 2
305 | Classroom | 437 | 29 |  | 672 | 15 | 15 | House Fan | 5376 | 4.8772 | 2 | 4.8772 | 2
306 | Classroom | 497 | 33 |  | 696 | 15 | 15 | House Fan | 5568 | 5.3556 | 2 | 5.3556 | 2
307 | Classrooms | 1017 | 67 |  | 661 | 15 | 15 | House Fan | 5288 | 11.5393 | 3 | 11.5393 | 3
308 | Classroom | 604 | 40 |  | 664 | 15 | 15 | House Fan | 5312 | 6.8223 | 2 | 6.8223 | 2
309 | Classroom | 702 | 46 |  | 673 | 15 | 15 | House Fan | 5384 | 7.8232 | 2 | 7.8232 | 2
310 | Classroom | 321 | 21 |  | 668 | 15 | 15 | House Fan | 5344 | 3.604 | 1 | 3.604 | 1
311 | Classrooms | 393 | 26 |  | 638 | 14 | 14 | House Fan | 5104 | 4.6199 | 2 | 4.6199 | 2
- | Auditorium | 1307 | 87 |  | 3184 | 72 | 72 | House Fan | 25472 | 3.0787 | 1 | 3.0787 | 1
- | B Art Room | 242 | 16 |  | 570 | 12 | 12 | House Fan | 4560 | 3.1842 | 1 | 3.1842 | 1
- | B Café / Gym | 0 | 0 | Yes | 3572 | 81 | 81 | N/A | 28576 | 0 | 0 | 20 | 3
- | B ESOL Room | 269 | 17 |  | 683 | 15 | 15 | House Fan | 5464 | 2.9539 | 1 | 2.9539 | 1
- | B Music Room | 603 | 40 |  | 688 | 15 | 15 | House Fan | 5504 | 6.5734 | 2 | 6.5734 | 2
- | B Science Room | 864 | 57 |  | 704 | 16 | 16 | House Fan | 5632 | 9.2045 | 2 | 9.2045 | 2
- | Main Office |  | 0 | Yes | 345 | 7 | 7 |  | 2760 | unk | unk | 20 | 3
- | Vice Principal's Office |  | 0 | Yes | 126 | 2 | 2 |  | 1008 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 275 | 6 | 6 |  | 2200 | unk | unk | 20 | 3
P1 | Classroom | 198 | 13 | Yes | 1184 | 26 | 26 | Unit Ventilator | 9472 | 1.2542 | 1 | 21.2542 | 3
P2 | Classroom | 348 | 23 |  | 747 | 16 | 16 | Unit Ventilator | 5976 | 3.494 | 1 | 3.494 | 1
Hopkinson LSH | [9 empty] | unk | unk | unk | unk
1 | Room | 308 | 20 |  | 877 | 19 | 19 | AHU | 7016 | 2.634 | 1 | 2.634 | 1
2 | Room | 323 | 21 |  | 900 | 20 | 20 | AHU | 7200 | 2.6917 | 1 | 2.6917 | 1
3 | Room | 318 | 21 |  | 885 | 20 | 20 | AHU | 7080 | 2.6949 | 1 | 2.6949 | 1
4 | Room | 349 | 23 |  | 908 | 20 | 20 | AHU | 7264 | 2.8827 | 1 | 2.8827 | 1
5 | Room | 308 | 20 |  | 863 | 19 | 19 | AHU | 6904 | 2.6767 | 1 | 2.6767 | 1
6 | Room | 256 | 17 | Yes | 876 | 19 | 19 | AHU | 7008 | 2.1918 | 1 | 22.1918 | 3
- | Corridor and Bathrooms | 46 | 3 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | Multi-Purpose Room | 626 | 41 |  | 2003 | 45 | 41 | AHU | 16024 | 2.344 | 1 | 2.344 | 1
- | Office Area | 204 | 13 |  | 352 | 8 | 8 | AHU | 2816 | 4.3466 | 2 | 4.3466 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-01 | [8 empty] | unk | unk | unk | unk
School: | Henry H. Houston Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom |  | 0 | Yes | 784 | 17 | 17 | House Fan | 6272 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 651 | 14 | 14 | House Fan | 5208 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 664 | 15 | 15 | House Fan | 5312 | unk | unk | 20 | 3
103A | Classroom |  | 0 |  | 157 | 3 | 0 | House Fan | 1256 | unk | unk | unk | unk
104 | Classroom |  | 0 | Yes | 675 | 15 | 15 | House Fan | 5400 | unk | unk | 20 | 3
105 | Office/Principal |  | 0 |  | 354 | 8 | 0 | House Fan | 2832 | unk | unk | unk | unk
106 | Classroom |  | 0 | Yes | 651 | 14 | 14 | House Fan | 5208 | unk | unk | 20 | 3
107 | Classroom |  | 0 | Yes | 459 | 10 | 10 | House Fan | 3672 | unk | unk | 20 | 3
108 | Classroom |  | 0 | Yes | 681 | 15 | 15 | House Fan | 5448 | unk | unk | 20 | 3
109 | Classroom |  | 0 | Yes | 950 | 21 | 21 | House Fan | 7600 | unk | unk | 20 | 3
111 | Classroom | 276 | 18 |  | 375 | 8 | 8 | House Fan and Univent | 3000 | 5.52 | 2 | 5.52 | 2
112 | Classroom | 350 | 23 |  | 312 | 7 | 7 | House Fan and Univent | 2496 | 8.4135 | 2 | 8.4135 | 2
201 | Classroom |  | 0 |  | 561 | 12 | 0 | House Fan | 4488 | unk | unk | unk | unk
202 | Classroom |  | 0 |  | 701 | 15 | 0 | House Fan | 5608 | unk | unk | unk | unk
203 | Classroom |  | 0 |  | 207 | 4 | 0 | House Fan | 1656 | unk | unk | unk | unk
204 | Classroom |  | 0 |  | 710 | 16 | 0 | House Fan | 5680 | unk | unk | unk | unk
205 | Classroom |  | 0 |  | 653 | 14 | 0 | House Fan | 5224 | unk | unk | unk | unk
206 | Classroom |  | 0 |  | 660 | 15 | 0 | House Fan | 5280 | unk | unk | unk | unk
207 | Classroom |  | 0 |  | 769 | 17 | 0 | House Fan | 6152 | unk | unk | unk | unk
208 | Classroom |  | 0 |  | 750 | 17 | 0 | House Fan | 6000 | unk | unk | unk | unk
209 | Classroom |  | 0 |  | 693 | 15 | 0 | House Fan | 5544 | unk | unk | unk | unk
210 | Classroom |  | 0 |  | 437 | 9 | 0 | N/A | 3496 | unk | unk | unk | unk
211 | Classroom | 329 | 21 |  | 795 | 18 | 18 | Unit Ventilator | 6360 | 3.1038 | 1 | 3.1038 | 1
212 | Classroom | 309 | 20 |  | 396 | 9 | 9 | Unit Ventilator | 3168 | 5.8523 | 2 | 5.8523 | 2
213 | Classroom | 274 | 18 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
301 | Classroom |  | 0 |  | 667 | 15 | 0 | House Fan | 5336 | unk | unk | unk | unk
302 | Classroom |  | 0 | Yes | 661 | 15 | 15 | House Fan | 5288 | unk | unk | 20 | 3
303 | Classroom |  | 0 |  | 664 | 15 | 0 | House Fan | 5312 | unk | unk | unk | unk
304 | Classroom |  | 0 |  | 729 | 16 | 0 | House Fan | 5832 | unk | unk | unk | unk
305 | Classroom |  | 0 |  | 674 | 15 | 0 | House Fan | 5392 | unk | unk | unk | unk
306 | Classroom |  | 0 |  | 670 | 15 | 0 | House Fan | 5360 | unk | unk | unk | unk
307 | Classroom |  | 0 |  | 758 | 17 | 0 | House Fan | 6064 | unk | unk | unk | unk
308 | Classroom |  | 0 |  | 716 | 16 | 0 | House Fan | 5728 | unk | unk | unk | unk
309 | Classroom |  | 0 |  | 613 | 13 | 0 | House Fan | 4904 | unk | unk | unk | unk
309A | Small Office |  | 0 |  | 201 | 4 | 0 | House Fan | 1608 | unk | unk | unk | unk
- | Kitchen | 0 | 0 |  | 638 | 14 | 0 | N/A | 5104 | 0 | 0 | 0 | 0
- | Auditorium | 1853 | 123 |  | 1500 | 34 | 34 | AHU 1 and 2 | 12000 | 9.265 | 2 | 9.265 | 2
- | Library | 0 | 0 |  | 1404 | 31 | 0 | RTU | 11232 | 0 | 0 | 0 | 0
- | Gym |  | 0 | Yes | 2232 | 50 | 50 | N/A | 17856 | unk | unk | 20 | 3
- | Old Art Room |  | 0 |  | 631 | 14 | 0 | N/A | 5048 | unk | unk | unk | unk
- | Cafeteria | 0 | 0 |  | 4500 | 102 | 0 | Nesbitt Unit Ventilator | 36000 | 0 | 0 | 0 | 0
- | Old School Store A | 230 | 15 |  | 863 | 19 | 15 | Nesbitt Unit Ventilator | 6904 | 1.9988 | 1 | 1.9988 | 1
- | Old School Store B | 345 | 23 |  | 311 | 7 | 7 | Nesbitt Unit Ventilator | 2488 | 8.3199 | 2 | 8.3199 | 2
- | New School Store | 347 | 23 |  | 291 | 6 | 6 | Nesbitt Unit Ventilator | 2328 | 8.9433 | 2 | 8.9433 | 2
- | Medical Suite Large |  | 0 |  | 242 | 5 |  |  | 1936 | unk | unk | unk | unk
- | Medical Suite Small |  | 0 |  | 126 | 2 |  |  | 1008 | unk | unk | unk | unk
- | Medical Suite Medium |  | 0 |  | 238 | 5 | 0 | House Fan | 1904 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-21 | [8 empty] | unk | unk | unk | unk
School: | Julia Ward Howe Academics Plus Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B-1 | Art | 751 | 50 |  | 754 | 17 | 17 | House Fan | 6032 | 7.4702 | 2 | 7.4702 | 2
1 | Classroom | 1269 | 84 |  | 690 | 15 | 15 | House Fan | 5520 | 13.7935 | 3 | 13.7935 | 3
2 | Classroom | 1240 | 82 |  | 690 | 15 | 15 | House Fan | 5520 | 13.4783 | 3 | 13.4783 | 3
3 | Classroom | 344 | 22 |  | 690 | 15 | 15 | House Fan | 5520 | 3.7391 | 1 | 3.7391 | 1
4 | Classroom | 455 | 30 |  | 690 | 15 | 15 | House Fan | 5520 | 4.9457 | 2 | 4.9457 | 2
5 | Classroom | 1500 | 100 |  | 196 | 4 | 4 | House Fan | 1568 | 57.398 | 5 | 57.398 | 5
6 | Classroom | 479 | 31 |  | 713 | 16 | 16 | House Fan | 5704 | 5.0386 | 2 | 5.0386 | 2
7 | Classroom | 1470 | 98 |  | 690 | 15 | 15 | House Fan | 5520 | 15.9783 | 3 | 15.9783 | 3
8 | Classroom | 1454 | 96 |  | 690 | 15 | 15 | House Fan | 5520 | 15.8043 | 3 | 15.8043 | 3
9 | Classroom | 564 | 37 |  | 720 | 16 | 16 | House Fan | 5760 | 5.875 | 2 | 5.875 | 2
10 | Classroom | 1739 | 115 |  | 690 | 15 | 15 | House Fan | 5520 | 18.9022 | 3 | 18.9022 | 3
11 | Classroom | 628 | 41 |  | 690 | 15 | 15 | House Fan | 5520 | 6.8261 | 2 | 6.8261 | 2
12 | Classroom | 829 | 55 |  | 720 | 16 | 16 | House Fan | 5760 | 8.6354 | 2 | 8.6354 | 2
13 | Library | 0 | 0 |  | 720 | 16 | 0 | House Fan | 5760 | 0 | 0 | 0 | 0
14 | Classroom | 1302 | 86 |  | 690 | 15 | 15 | House Fan | 5520 | 14.1522 | 3 | 14.1522 | 3
15 | Classroom | 1044 | 69 |  | 690 | 15 | 15 | House Fan | 5520 | 11.3478 | 3 | 11.3478 | 3
16 | Computer Lab | 0 | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0 | 0 | 0
17 | Classroom | 548 | 36 |  | 690 | 15 | 15 | House Fan | 5520 | 5.9565 | 2 | 5.9565 | 2
18 | Classroom | 824 | 54 |  | 690 | 15 | 15 | House Fan | 5520 | 8.9565 | 2 | 8.9565 | 2
19 | Classroom | 869 | 57 |  | 690 | 15 | 15 | House Fan | 5520 | 9.4457 | 2 | 9.4457 | 2
20 | Classroom | 0 | 0 |  | 690 | 15 | 0 | House Fan | 5520 | 0 | 0 | 0 | 0
21 | Classroom | 149 | 9 | Yes | 690 | 15 | 15 | House Fan | 5520 | 1.6196 | 1 | 21.6196 | 3
22 | Classroom | 898 | 59 |  | 690 | 15 | 15 | House Fan | 5520 | 9.7609 | 2 | 9.7609 | 2
23 | Classroom | 210 | 14 |  | 690 | 15 | 14 | House Fan | 5520 | 2.2826 | 1 | 2.2826 | 1
23A | - |  | 0 | Yes | 91 | 2 | 2 | House Fan | 728 | unk | unk | 20 | 3
24 | Classroom | 0 | 0 |  | 350 | 7 | 0 | House Fan | 2800 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 | Yes | 1566 | 35 | 35 | House Fan | 12528 | 0 | 0 | 20 | 3
- | Gym |  | 0 | Yes | 1060 | 24 | 24 | House Fan | 8480 | unk | unk | 20 | 3
- | Jugg Room |  | 0 |  | 195 | 4 | 0 | House Fan | 1560 | unk | unk | unk | unk
- | Main Office |  | 0 |  | 238 | 5 | 0 | House Fan | 1904 | unk | unk | unk | unk
- | Principals Office |  | 0 | Yes | 180 | 4 | 4 | House Fan | 1440 | unk | unk | 20 | 3
- | Counselors Office |  | 0 |  | 162 | 3 | 0 | House Fan | 1296 | unk | unk | unk | unk
- | Psychologists Office |  | 0 | Yes | 99 | 2 | 2 | House Fan | 792 | unk | unk | 20 | 3
- | Lounge |  | 0 |  | 266 | 6 | 0 | House Fan | 2128 | unk | unk | unk | unk
- | Security |  | 0 | Yes | 91 | 2 | 2 | House Fan | 728 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-06 | [8 empty] | unk | unk | unk | unk
School: | New William H. Hunter Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Retest | [7 empty] | unk | unk | unk | unk
| Devine 2nd Retest | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Office | 40 | 2 |  | 149 | 3 | 2 | AHU-3 | 1192 | 2.0134 | 1 | 2.0134 | 1
2 | Office | 33 | 2 |  | 143 | 3 | 2 | AHU-3 | 1144 | 1.7308 | 1 | 1.7308 | 1
3 | Office | 24 | 1 |  | 72 | 1 | 1 | AHU-3 | 576 | 2.5 | 1 | 2.5 | 1
4 | Office | 48 | 3 |  | 92 | 2 | 2 | AHU-3 | 736 | 3.913 | 1 | 3.913 | 1
101A | Classroom | 363 | 24 |  | 695 | 15 | 15 | AHU-1 | 5560 | 3.9173 | 1 | 3.9173 | 1
101B | Classroom | 378 | 25 |  | 695 | 15 | 15 | AHU-1 + UV | 5560 | 4.0791 | 2 | 4.0791 | 2
101C | Classroom | 358 | 23 |  | 650 | 14 | 14 | AHU-1 | 5200 | 4.1308 | 2 | 4.1308 | 2
101D | Classroom | 551 | 36 |  | 650 | 14 | 14 | AHU-1 + UV | 5200 | 6.3577 | 2 | 6.3577 | 2
101E | Classroom | 351 | 23 |  | 610 | 13 | 13 | AHU-1 | 4880 | 4.3156 | 2 | 4.3156 | 2
101F | Classroom | 393 | 26 |  | 650 | 14 | 14 | AHU-1 + UV | 5200 | 4.5346 | 2 | 4.5346 | 2
102 | Classroom | 375 | 25 |  | 410 | 9 | 9 | AHU-1 and UV | 3280 | 6.8598 | 2 | 6.8598 | 2
107 | Main Office Entry | 103 | 6 |  | 350 | 7 | 6 | AHU-3 | 2800 | 2.2071 | 1 | 2.2071 | 1
107 | Main Office | 195 | 13 | Yes | 1125 | 25 | 25 | AHU-3 | 9000 | 1.3 | 1 | 21.3 | 3
108 | Classroom | 666 | 44 |  | 715 | 16 | 16 | AHU-5 + UV | 5720 | 6.986 | 2 | 6.986 | 2
109 | Classroom | 497 | 33 |  | 695 | 15 | 15 | AHU-5 + UV | 5560 | 5.3633 | 2 | 5.3633 | 2
110 | Classroom | 477 | 31 |  | 695 | 15 | 15 | AHU-5 + UV | 5560 | 5.1475 | 2 | 5.1475 | 2
111 | Classroom | 632 | 42 |  | 695 | 15 | 15 | AHU-5 + UV | 5560 | 6.8201 | 2 | 6.8201 | 2
112 | Classroom | 496 | 33 |  | 695 | 15 | 15 | AHU-5 + UV | 5560 | 5.3525 | 2 | 5.3525 | 2
113 | Music Room | 456 | 30 |  | 1430 | 32 | 30 | AHU-7 | 11440 | 2.3916 | 1 | 2.3916 | 1
113 | Practice Rm 1 | 23 | 1 |  | 72 | 1 | 1 | AHU-7 | 576 | 2.3958 | 1 | 2.3958 | 1
113 | Practice Rm 2 | 27 | 1 |  | 78 | 1 | 1 | AHU-7 | 624 | 2.5962 | 1 | 2.5962 | 1
201 | IMC | 1373 | 91 |  | 2995 | 68 | 68 | AHU-10 + UV | 23960 | 3.4382 | 1 | 3.4382 | 1
202 | Classroom | 467 | 31 |  | 1125 | 25 | 25 | Unit Ventilator and AHU | 9000 | 3.1133 | 1 | 3.1133 | 1
202 | Media | 0 | 0 | Yes | 385 | 8 | 8 | Unit Ventilator and AHU | 3080 | 0 | 0 | 20 | 3
BAS 205 | IMC - Reading Small Classroom | 303 | 20 |  | 102 | 2 | 2 | Tightened damper Actuator to the shaft | 816 | 22.2794 | 3 | 22.2794 | 3
BAS 206 | IMC - Reading Small Classroom | 317 | 21 |  | 859 | 19 | 19 | Tightened damper Actuator to the shaft | 6872 | 2.7678 | 1 | 2.7678 | 1
206 | Classroom | 464 | 30 |  | 842 | 19 | 19 | AHU-1 + UV | 6736 | 4.133 | 2 | 4.133 | 2
207 | Classroom | 610 | 40 |  | 1325 | 30 | 30 | Unit Ventilator and AHU | 10600 | 3.4528 | 1 | 3.4528 | 1
208 | Classroom | 318 | 21 | Yes | 1395 | 31 | 31 | Unit Ventilator and AHU | 11160 | 1.7097 | 1 | 21.7097 | 3
208 | Computer Lab | 81 | 5 |  | 1210 | 27 | 5 |  | 9680 | 0.50207 | 0 | 0.50207 | 0
209 | Classroom | 293 | 19 |  | 750 | 17 | 17 | AHU-1 + UV | 6000 | 2.93 | 1 | 2.93 | 1
210 | Classroom | 526 | 35 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 5.2321 | 2 | 5.2321 | 2
211 | Classroom | 551 | 36 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 5.4808 | 2 | 5.4808 | 2
212 | Classroom | 426 | 28 |  | 753 | 17 | 17 | Unit Ventilator and AHU | 6024 | 4.243 | 2 | 4.243 | 2
213 | Classroom | 497 | 33 |  | 753 | 17 | 17 | Unit Ventilator and AHU | 6024 | 4.9502 | 2 | 4.9502 | 2
214 | Classroom | 478 | 31 |  | 724 | 16 | 16 | Unit Ventilator and AHU | 5792 | 4.9517 | 2 | 4.9517 | 2
215 | Art Room | 367 | 24 | Yes | 1324 | 30 | 30 | AHU-12 | 10592 | 2.0789 | 1 | 22.0789 | 3
304 | Classroom | 367 | 24 |  | 725 | 16 | 16 | Unit Ventilator and AHU | 5800 | 3.7966 | 1 | 3.7966 | 1
305 | Classroom | 431 | 28 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 4.2871 | 2 | 4.2871 | 2
306 | Classroom | 395 | 26 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 3.929 | 1 | 3.929 | 1
307 | Classroom | 315 | 21 |  | 753 | 17 | 17 | Unit Ventilator and AHU | 6024 | 3.1375 | 1 | 3.1375 | 1
308 | Classroom | 350 | 23 |  | 753 | 17 | 17 | Unit Ventilator and AHU | 6024 | 3.4861 | 1 | 3.4861 | 1
309 | Classroom | 340 | 22 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 3.382 | 1 | 3.382 | 1
310 | Classroom | 361 | 24 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 3.5908 | 1 | 3.5908 | 1
311 | Classroom | 317 | 21 |  | 753 | 17 | 17 | Unit Ventilator and AHU | 6024 | 3.1574 | 1 | 3.1574 | 1
312 | Classroom | 427 | 28 |  | 753 | 17 | 17 | Unit Ventilator and AHU | 6024 | 4.253 | 2 | 4.253 | 2
313 | Classroom | 387 | 25 |  | 754 | 17 | 17 | Unit Ventilator and AHU | 6032 | 3.8495 | 1 | 3.8495 | 1
314 | Classroom | 411 | 27 |  | 715 | 16 | 16 | Unit Ventilator and AHU | 5720 | 4.3112 | 2 | 4.3112 | 2
315 | Classroom | 363 | 24 |  | 810 | 18 | 18 | Unit Ventilator and AHU | 6480 | 3.3611 | 1 | 3.3611 | 1
- | Auditorium | 2966 | 197 |  | 2910 | 66 | 66 | AHU-6 | 23280 | 7.6443 | 2 | 7.6443 | 2
- | Cafeteria | 2006 | 133 |  | 3590 | 81 | 81 | AHU | 28720 | 4.1908 | 2 | 4.1908 | 2
- | Kitchen | 35 | 2 | Yes | 1116 | 25 | 25 | AHU-3 | 8928 | 0.23522 | 0 | 20.2352 | 3
- | Nurses Office | 98 | 6 |  | 105 | 2 | 2 | FC 5-1 | 840 | 7 | 2 | 7 | 2
- | Nurse Exam Room | 110 | 7 |  | 94 | 2 | 2 | FC 5-1 | 752 | 8.7766 | 2 | 8.7766 | 2
- | Nurses Waiting Room | 108 | 7 |  | 130 | 2 | 2 | FC 5-1 | 1040 | 6.2308 | 2 | 6.2308 | 2
- | Principal Office | 74 | 4 | Yes | 322 | 7 | 7 | AHU-3 | 2576 | 1.7236 | 1 | 21.7236 | 3
- | Conference Room | 147 | 9 |  | 429 | 9 | 9 | AHU-3 | 3432 | 2.5699 | 1 | 2.5699 | 1
- | Gym | 1430 | 95 |  | 4969 | 112 | 95 | AHU-8 + AHU-9 | 39752 | 2.1584 | 1 | 2.1584 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-13 | [8 empty] | unk | unk | unk | unk
School: | Andrew Jackson Elementary School | House fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B1 | Music Room | 324 | 21 |  | 1036 | 23 | 21 | AHU | 8288 | 2.3456 | 1 | 2.3456 | 1
101 | Classroom | 536 | 35 |  | 1190 | 27 | 27 | AHU | 9520 | 3.3782 | 1 | 3.3782 | 1
102 | Classroom | 436 | 29 |  | 638 | 14 | 14 | AHU | 5104 | 5.1254 | 2 | 5.1254 | 2
103 | Classroom | 567 | 37 |  | 805 | 18 | 18 | AHU | 6440 | 5.2826 | 2 | 5.2826 | 2
104 | Classroom | 363 | 24 |  | 840 | 19 | 19 | AHU | 6720 | 3.2411 | 1 | 3.2411 | 1
105 | Classroom | 398 | 26 |  | 828 | 18 | 18 | AHU | 6624 | 3.6051 | 1 | 3.6051 | 1
106 | Classroom | 740 | 49 |  | 748 | 17 | 17 | AHU | 5984 | 7.4198 | 2 | 7.4198 | 2
107 | Classroom | 567 | 37 |  | 736 | 16 | 16 | AHU | 5888 | 5.7779 | 2 | 5.7779 | 2
107B | - |  | 0 | Yes | 132 | 3 | 3 | N/A | 1056 | unk | unk | 20 | 3
107C | - |  | 0 | Yes | 220 | 5 | 5 | N/A | 1760 | unk | unk | 20 | 3
108 | Classroom | 396 | 26 |  | 841 | 19 | 19 | AHU | 6728 | 3.5315 | 1 | 3.5315 | 1
109 | Classroom | 669 | 44 |  | 1218 | 27 | 27 | AHU | 9744 | 4.1195 | 2 | 4.1195 | 2
110 | Classroom | 482 | 32 |  | 848 | 19 | 19 | AHU | 6784 | 4.263 | 2 | 4.263 | 2
201 | Classroom | 581 | 38 |  | 1225 | 27 | 27 | AHU | 9800 | 3.5571 | 1 | 3.5571 | 1
202 | Classroom | 346 | 23 |  | 726 | 16 | 16 | AHU | 5808 | 3.5744 | 1 | 3.5744 | 1
203 | Classroom | 384 | 25 |  | 864 | 19 | 19 | AHU | 6912 | 3.3333 | 1 | 3.3333 | 1
204 | Classroom | 453 | 30 |  | 850 | 19 | 19 | AHU | 6800 | 3.9971 | 1 | 3.9971 | 1
204A | Office | 0 | 0 | Yes | 468 | 10 | 10 |  | 3744 | 0 | 0 | 20 | 3
205 | Classroom | 304 | 20 |  | 840 | 19 | 19 | AHU | 6720 | 2.7143 | 1 | 2.7143 | 1
206 | Classroom | 531 | 35 |  | 864 | 19 | 19 | AHU | 6912 | 4.6094 | 2 | 4.6094 | 2
207 | Classroom | 614 | 40 |  | 805 | 18 | 18 | AHU | 6440 | 5.7205 | 2 | 5.7205 | 2
208 | Classroom | 367 | 24 |  | 850 | 19 | 19 | AHU | 6800 | 3.2382 | 1 | 3.2382 | 1
209/210 | Classroom | 1387 | 92 |  | 1680 | 38 | 38 | AHU | 13440 | 6.192 | 2 | 6.192 | 2
211 | Classroom | 490 | 32 |  | 840 | 19 | 19 | AHU | 6720 | 4.375 | 2 | 4.375 | 2
301 | Classroom | 530 | 35 |  | 980 | 22 | 22 | AHU | 7840 | 4.0561 | 2 | 4.0561 | 2
302 | Classroom | 303 | 20 |  | 816 | 18 | 18 | AHU | 6528 | 2.7849 | 1 | 2.7849 | 1
303 | Classroom | 88 | 5 | Yes | 828 | 18 | 18 |  | 6624 | 0.7971 | 0 | 20.7971 | 3
304 | Classroom | 427 | 28 |  | 805 | 18 | 18 | AHU | 6440 | 3.9783 | 1 | 3.9783 | 1
304A | Office | 0 | 0 | Yes | 442 | 10 | 10 |  | 3536 | 0 | 0 | 20 | 3
305 | Classroom | 619 | 41 |  | 840 | 19 | 19 | AHU | 6720 | 5.5268 | 2 | 5.5268 | 2
306 | Classroom | 528 | 35 |  | 840 | 19 | 19 | AHU | 6720 | 4.7143 | 2 | 4.7143 | 2
307 | Classroom | 375 | 25 |  | 782 | 17 | 17 | AHU | 6256 | 3.5965 | 1 | 3.5965 | 1
308 | Classroom | 417 | 27 |  | 816 | 18 | 18 | AHU | 6528 | 3.8327 | 1 | 3.8327 | 1
- | Gym/Cafeteria | 2408 | 160 |  | 3005 | 68 | 68 | AHU | 24040 | 6.01 | 2 | 6.01 | 2
- | Library | 740 | 49 |  | 2320 | 52 | 49 | AHU | 18560 | 2.3922 | 1 | 2.3922 | 1
- | I.M.C. Office | 160 | 10 |  | 400 | 9 | 9 | AHU | 3200 | 3 | 1 | 3 | 1
- | Main Office | 0 | 0 | Yes | 484 | 11 | 11 |  | 3872 | 0 | 0 | 20 | 3
- | Princpal's Office |  | 0 | Yes | 308 | 7 | 7 | N/A | 2464 | unk | unk | 20 | 3
- | Nurse's Office |  | 0 | Yes | 264 | 6 | 6 | N/A | 2112 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | James Martin- Alternative Middle Years (Middle School) | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 0 | 0 | Yes | 696 | 15 | 15 |  | 5568 | 0 | 0 | 20 | 3
106 | Classroom | 280 | 18 |  | 720 | 16 | 16 |  | 5760 | 2.9167 | 1 | 2.9167 | 1
107 | Classroom | 313 | 20 |  | 720 | 16 | 16 |  | 5760 | 3.2604 | 1 | 3.2604 | 1
108 | Classroom | 0 | 0 | Yes | 696 | 15 | 15 |  | 5568 | 0 | 0 | 20 | 3
109 | Classroom | 0 | 0 | Yes | 672 | 15 | 15 |  | 5376 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 |  | 5760 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 | Yes | 750 | 17 | 17 |  | 6000 | 0 | 0 | 20 | 3
203 | Classroom | 306 | 20 |  | 750 | 17 | 17 |  | 6000 | 3.06 | 1 | 3.06 | 1
204 | Lounge | 371 | 24 |  | 480 | 10 | 10 |  | 3840 | 5.7969 | 2 | 5.7969 | 2
205 | Classroom | 345 | 23 |  | 912 | 20 | 20 |  | 7296 | 2.8372 | 1 | 2.8372 | 1
206 | School Store | 291 | 19 |  | 384 | 8 | 8 |  | 3072 | 5.6836 | 2 | 5.6836 | 2
207 | Classroom | 309 | 20 |  | 750 | 17 | 17 |  | 6000 | 3.09 | 1 | 3.09 | 1
208 | Classroom | 331 | 22 |  | 720 | 16 | 16 |  | 5760 | 3.4479 | 1 | 3.4479 | 1
209 | Classroom | 303 | 20 |  | 667 | 15 | 15 |  | 5336 | 3.407 | 1 | 3.407 | 1
210 | Classroom | 292 | 19 |  | 667 | 15 | 15 |  | 5336 | 3.2834 | 1 | 3.2834 | 1
211 | Classroom | 0 | 0 | Yes | 672 | 15 | 15 |  | 5376 | 0 | 0 | 20 | 3
214 | Security Office | 0 | 0 | Yes | 256 | 5 | 5 |  | 2048 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 | Yes | 696 | 15 | 15 |  | 5568 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 696 | 15 | 15 |  | 5568 | 0 | 0 | 20 | 3
303 | Classroom | 301 | 20 |  | 720 | 16 | 16 |  | 5760 | 3.1354 | 1 | 3.1354 | 1
304 | Classroom | 275 | 18 |  | 720 | 16 | 16 |  | 5760 | 2.8646 | 1 | 2.8646 | 1
305 | Classroom | 297 | 19 |  | 696 | 15 | 15 |  | 5568 | 3.2004 | 1 | 3.2004 | 1
306 | Classroom | 284 | 18 |  | 720 | 16 | 16 |  | 5760 | 2.9583 | 1 | 2.9583 | 1
307 | Classroom | 297 | 19 |  | 768 | 17 | 17 |  | 6144 | 2.9004 | 1 | 2.9004 | 1
308 | Classroom | 317 | 21 |  | 696 | 15 | 15 |  | 5568 | 3.4159 | 1 | 3.4159 | 1
309 | Classroom | 272 | 18 |  | 696 | 15 | 15 |  | 5568 | 2.931 | 1 | 2.931 | 1
310 | Classroom | 293 | 19 |  | 720 | 16 | 16 |  | 5760 | 3.0521 | 1 | 3.0521 | 1
311 | Art Room | 0 | 0 | Yes | 928 | 21 | 21 |  | 7424 | 0 | 0 | 20 | 3
314 | Office | 0 | 0 | Yes | 256 | 5 | 5 |  | 2048 | 0 | 0 | 20 | 3
- | Boys Cafeteria | 0 | 0 | Yes | 851 | 19 | 19 |  | 6808 | 0 | 0 | 20 | 3
- | Counselors Office | 0 | 0 | Yes | 160 | 3 | 3 |  | 1280 | 0 | 0 | 20 | 3
- | Girls Cafeteria | 0 | 0 | Yes | 1728 | 39 | 39 |  | 13824 | 0 | 0 | 20 | 3
- | Gym | 0 | 0 |  | 1760 | 40 | 0 |  | 14080 | 0 | 0 | 0 | 0
- | IMC-A | 270 | 18 |  | 720 | 16 | 16 |  | 5760 | 2.8125 | 1 | 2.8125 | 1
- | IMC-B | 292 | 19 |  | 720 | 16 | 16 |  | 5760 | 3.0417 | 1 | 3.0417 | 1
- | IMC-C | 283 | 18 |  | 720 | 16 | 16 |  | 5760 | 2.9479 | 1 | 2.9479 | 1
- | Main Office | 0 | 0 | Yes | 360 | 8 | 8 |  | 2880 | 0 | 0 | 20 | 3
- | Nurses Office | 0 | 0 | Yes | 256 | 5 | 5 |  | 2048 | 0 | 0 | 20 | 3
- | Teachers Lounge | 0 | 0 |  | 480 | 10 | 0 |  | 3840 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | Abraham S. Jenks Elementary School | House fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
14 | Classroom | 422 | 28 |  | 638 | 14 | 14 | House Fan | 5104 | 4.9608 | 2 | 4.9608 | 2
15 | Cafeteria | 221 | 14 |  | 638 | 14 | 14 | House Fan | 5104 | 2.598 | 1 | 2.598 | 1
101 | Classroom | 459 | 30 |  | 660 | 15 | 15 | House Fan | 5280 | 5.2159 | 2 | 5.2159 | 2
102 | Classroom | 1235 | 82 |  | 660 | 15 | 15 | House Fan | 5280 | 14.0341 | 3 | 14.0341 | 3
103 | Classroom | 1253 | 83 |  | 660 | 15 | 15 | House Fan | 5280 | 14.2386 | 3 | 14.2386 | 3
104 | Classroom | 919 | 61 |  | 660 | 15 | 15 | House Fan | 5280 | 10.4432 | 3 | 10.4432 | 3
105 | Classroom | 632 | 42 |  | 660 | 15 | 15 | House Fan | 5280 | 7.1818 | 2 | 7.1818 | 2
106 | Classroom | 748 | 49 |  | 660 | 15 | 15 | House Fan | 5280 | 8.5 | 2 | 8.5 | 2
201 | Classroom | 1277 | 85 |  | 690 | 15 | 15 | House Fan | 5520 | 13.8804 | 3 | 13.8804 | 3
202 | Classroom | 522 | 34 |  | 690 | 15 | 15 | House Fan | 5520 | 5.6739 | 2 | 5.6739 | 2
203 | Classroom | 1094 | 72 |  | 690 | 15 | 15 | House Fan | 5520 | 11.8913 | 3 | 11.8913 | 3
204 | Classroom | 803 | 53 |  | 690 | 15 | 15 | House Fan | 5520 | 8.7283 | 2 | 8.7283 | 2
205 | Classroom | 749 | 49 |  | 690 | 15 | 15 | House Fan | 5520 | 8.1413 | 2 | 8.1413 | 2
206 | Classroom | 1198 | 79 |  | 690 | 15 | 15 | House Fan | 5520 | 13.0217 | 3 | 13.0217 | 3
207 | Classroom | 1279 | 85 |  | 744 | 16 | 16 | House Fan | 5952 | 12.8931 | 3 | 12.8931 | 3
- | Principals Office |  | 0 | Yes | 165 | 3 | 3 |  | 1320 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 195 | 4 | 4 |  | 1560 | unk | unk | 20 | 3
- | Teacher Lounge |  | 0 |  | 165 | 3 | 0 |  | 1320 | unk | unk | unk | unk
- | Nurses Office |  | 0 | Yes | 190 | 4 | 4 |  | 1520 | unk | unk | 20 | 3
- | Library | 176 | 11 |  | 638 | 14 | 11 | House Fan | 5104 | 2.069 | 1 | 2.069 | 1
- | Auditorium | 217 | 14 |  | 1540 | 35 | 14 | UV | 12320 | 1.0568 | 1 | 1.0568 | 1
- | Cafeteria | 362 | 24 |  | 638 | 14 | 14 | House Fan | 5104 | 4.2555 | 2 | 4.2555 | 2
- | North Trailer Classroom | 227 | 15 |  | N/A | 0 | 0 | N/A used for storage |  | unk | unk | unk | unk
- | South Trailer Classroom | 261 | 17 |  | 638 | 14 | 14 | AHU | 5104 | 3.0682 | 1 | 3.0682 | 1
- | Gym |  | 0 | Yes | 1700 | 38 | 38 | N/A | 13600 | unk | unk | 20 | 3
Sheet Last Modified: | 2021-04-28 | [8 empty] | unk | unk | unk | unk
School: | John S. Jenks Elementary-Middle School | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
322 | Classroom |  | 0 | Yes | 658 | 14 | 14 | House Fan | 5264 | unk | unk | 20 | 3
321 | Classroom |  | 0 | Yes | 692 | 15 | 15 | House Fan | 5536 | unk | unk | 20 | 3
320 | Classroom |  | 0 | Yes | 685 | 15 | 15 | House Fan | 5480 | unk | unk | 20 | 3
319B | - |  | 0 | Yes | 658 | 14 | 14 | House Fan | 5264 | unk | unk | 20 | 3
319A | - |  | 0 | Yes | 305 | 6 | 6 | House Fan | 2440 | unk | unk | 20 | 3
318 | Classroom |  | 0 | Yes | 654 | 14 | 14 | House Fan | 5232 | unk | unk | 20 | 3
317 | Classroom |  | 0 | Yes | 674 | 15 | 15 | House Fan | 5392 | unk | unk | 20 | 3
316 | Classroom |  | 0 | Yes | 693 | 15 | 15 | House Fan | 5544 | unk | unk | 20 | 3
315 | Classroom |  | 0 | Yes | 654 | 14 | 14 | House Fan | 5232 | unk | unk | 20 | 3
214 | Classroom |  | 0 | Yes | 671 | 15 | 15 | House Fan | 5368 | unk | unk | 20 | 3
213 | Classroom |  | 0 | Yes | 689 | 15 | 15 | House Fan | 5512 | unk | unk | 20 | 3
212 | Classroom |  | 0 | Yes | 683 | 15 | 15 | House Fan | 5464 | unk | unk | 20 | 3
211 | Classroom |  | 0 | Yes | 673 | 15 | 15 | House Fan | 5384 | unk | unk | 20 | 3
210 | Classroom |  | 0 | Yes | 671 | 15 | 15 | House Fan | 5368 | unk | unk | 20 | 3
209 | Classroom |  | 0 | Yes | 680 | 15 | 15 | House Fan | 5440 | unk | unk | 20 | 3
208 | Classroom |  | 0 | Yes | 695 | 15 | 15 | House Fan | 5560 | unk | unk | 20 | 3
207 | Classroom |  | 0 | Yes | 636 | 14 | 14 | House Fan | 5088 | unk | unk | 20 | 3
110 | - |  | 0 | Yes | 336 | 7 | 7 | House Fan | 2688 | unk | unk | 20 | 3
109 | - |  | 0 | Yes | 156 | 3 | 3 | house Fan | 1248 | unk | unk | 20 | 3
106 | IMC |  | 0 | Yes | 671 | 15 | 15 | House Fan | 5368 | unk | unk | 20 | 3
105 | Classroom |  | 0 | Yes | 640 | 14 | 14 | House Fan | 5120 | unk | unk | 20 | 3
104 | Classroom |  | 0 | Yes | 627 | 14 | 14 | House Fan | 5016 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 666 | 15 | 15 | House Fan | 5328 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 668 | 15 | 15 | House Fan | 5344 | unk | unk | 20 | 3
101 | Classroom |  | 0 | Yes | 602 | 13 | 13 | House Fan | 4816 | unk | unk | 20 | 3
100 | Classroom |  | 0 | Yes | 1053 | 23 | 23 | House Fan | 8424 | unk | unk | 20 | 3
- | Kindergarten Classroom |  | 0 | Yes | 1512 | 34 | 34 | House Fan | 12096 | unk | unk | 20 | 3
- | Gym |  | 0 | Yes | 4500 | 102 | 102 |  | 36000 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 385 | 8 | 8 |  | 3080 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 112 | 2 | 2 |  | 896 | unk | unk | 20 | 3
- | Library |  | 0 | Yes | 616 | 13 | 13 |  | 4928 | unk | unk | 20 | 3
- | Teachers Lounge |  | 0 | Yes | 402 | 9 | 9 |  | 3216 | unk | unk | 20 | 3
- | Spo |  | 0 | Yes | 180 | 4 | 4 |  | 1440 | unk | unk | 20 | 3
- | Counselor Office |  | 0 | Yes | 165 | 3 | 3 |  | 1320 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 263 | 5 | 5 |  | 2104 | unk | unk | 20 | 3
- | Speech Room |  | 0 | Yes | 103 | 2 | 2 |  | 824 | unk | unk | 20 | 3
- | Auditorium |  | 0 |  | 3463 | 78 | 0 |  | 27704 | unk | unk | unk | unk
- | Copy Room |  | 0 |  | 166 | 3 | 0 |  | 1328 | unk | unk | unk | unk
- | Art Room |  | 0 | Yes | 1085 | 24 | 24 |  | 8680 | unk | unk | 20 | 3
- | Lego Room |  | 0 | Yes | 165 | 3 | 3 |  | 1320 | unk | unk | 20 | 3
- | Kitchen |  | 0 | Yes | 578 | 13 | 13 |  | 4624 | unk | unk | 20 | 3
- | Gym Office |  | 0 |  | 588 | 13 | 0 |  | 4704 | unk | unk | unk | unk
- | Home & school |  | 0 |  | 364 | 8 | 0 |  | 2912 | unk | unk | unk | unk
- | Boys Room |  | 0 |  | 144 | 3 | 0 |  | 1152 | unk | unk | unk | unk
- | Girls Room |  | 0 |  | 144 | 3 | 0 |  | 1152 | unk | unk | unk | unk
- | Boys room by gym |  | 0 |  | 614 | 13 | 0 |  | 4912 | unk | unk | unk | unk
- | Girls room by gym |  | 0 |  | 614 | 13 | 0 |  | 4912 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-06 | [8 empty] | unk | unk | unk | unk
School: | Juniata Park Academy Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Classroom | 1020 | 68 |  | 1100 | 25 | 25 | RTU/UV | 8800 | 6.9545 | 2 | 6.9545 | 2
2 | Classroom | 897 | 59 |  | 1108 | 25 | 25 | RTU/UV | 8864 | 6.0718 | 2 | 6.0718 | 2
3 | Classroom | 1328 | 88 |  | 1108 | 25 | 25 | RTU/UV | 8864 | 8.9892 | 2 | 8.9892 | 2
4 | Classroom | 1321 | 88 |  | 1093 | 24 | 24 | RTU/UV | 8744 | 9.0645 | 2 | 9.0645 | 2
5 | Classroom | 975 | 65 |  | 1123 | 25 | 25 | RTU/UV | 8984 | 6.5116 | 2 | 6.5116 | 2
6 | Classroom | 874 | 58 |  | 1125 | 25 | 25 | RTU/UV | 9000 | 5.8267 | 2 | 5.8267 | 2
100 | Classroom | 750 | 50 |  | 660 | 15 | 15 | RTU/UV | 5280 | 8.5227 | 2 | 8.5227 | 2
101 | Classroom | 969 | 64 |  | 660 | 15 | 15 | RTU/UV | 5280 | 11.0114 | 3 | 11.0114 | 3
102 | Classroom | 836 | 55 |  | 952 | 21 | 21 | RTU/UV | 7616 | 6.5861 | 2 | 6.5861 | 2
103 | Classroom | 1212 | 80 |  | 792 | 18 | 18 | RTU/UV | 6336 | 11.4773 | 3 | 11.4773 | 3
104 | Classroom | 1119 | 74 |  | 792 | 18 | 18 | RTU/UV | 6336 | 10.5966 | 3 | 10.5966 | 3
105 | Classroom | 2327 | 155 |  | 794 | 18 | 18 | RTU/UV | 6352 | 21.9805 | 3 | 21.9805 | 3
106 | Classroom | 1053 | 70 |  | 794 | 18 | 18 | RTU/UV | 6352 | 9.9465 | 2 | 9.9465 | 2
107 | Classroom | 789 | 52 |  | 794 | 18 | 18 | RTU/UV | 6352 | 7.4528 | 2 | 7.4528 | 2
108 | Classroom | 952 | 63 |  | 794 | 18 | 18 | RTU/UV | 6352 | 8.9924 | 2 | 8.9924 | 2
109 | Classroom | 910 | 60 |  | 794 | 18 | 18 | RTU/UV | 6352 | 8.5957 | 2 | 8.5957 | 2
110 | Classroom | 817 | 54 |  | 794 | 18 | 18 | RTU/UV | 6352 | 7.7173 | 2 | 7.7173 | 2
111 | Classroom | 1240 | 82 |  | 794 | 18 | 18 | RTU/UV | 6352 | 11.7128 | 3 | 11.7128 | 3
112 | Classroom | 1129 | 75 |  | 794 | 18 | 18 | RTU/UV | 6352 | 10.6644 | 3 | 10.6644 | 3
113 | Classroom | 967 | 64 |  | 794 | 18 | 18 | RTU/UV | 6352 | 9.1341 | 2 | 9.1341 | 2
114 | Classroom | 906 | 60 |  | 794 | 18 | 18 | RTU/UV | 6352 | 8.5579 | 2 | 8.5579 | 2
115 | Classroom | 1064 | 70 |  | 792 | 18 | 18 | RTU/UV | 6336 | 10.0758 | 3 | 10.0758 | 3
117 | Girls' Toilet Room | 115 | 7 |  | 140 | 3 | 3 | RTU/UV | 1120 | 6.1607 | 2 | 6.1607 | 2
116 | Classroom | 853 | 56 |  | 792 | 18 | 18 | RTU/UV | 6336 | 8.0777 | 2 | 8.0777 | 2
117 | Classroom | 636 | 42 |  | 672 | 15 | 15 | RTU/UV | 5376 | 7.0982 | 2 | 7.0982 | 2
120 | Boys' Toilet Room | 120 | 8 |  | 200 | 4 | 4 | RTU/UV | 1600 | 4.5 | 2 | 4.5 | 2
200 | Classroom | 661 | 44 |  | 609 | 13 | 13 | RTU/UV | 4872 | 8.1404 | 2 | 8.1404 | 2
201 | Classroom | 638 | 42 |  | 772 | 17 | 17 | RTU/UV | 6176 | 6.1982 | 2 | 6.1982 | 2
202 | Classroom | 449 | 29 |  | 721 | 16 | 16 | RTU/UV | 5768 | 4.6706 | 2 | 4.6706 | 2
203 | Classroom | 691 | 46 |  | 673 | 15 | 15 | RTU/UV | 5384 | 7.7006 | 2 | 7.7006 | 2
204 | Classroom | 534 | 35 |  | 794 | 18 | 18 | RTU/UV | 6352 | 5.0441 | 2 | 5.0441 | 2
205 | Classroom | 627 | 41 |  | 794 | 18 | 18 | RTU/UV | 6352 | 5.9225 | 2 | 5.9225 | 2
205 | Girls' Toilet Room | 22 | 1 |  | 182 | 4 | 1 | RTU/UV | 1456 | 0.90659 | 0 | 0.90659 | 0
206 | Classroom | 530 | 35 |  | 794 | 18 | 18 | RTU/UV | 6352 | 5.0063 | 2 | 5.0063 | 2
207 | Classroom | 539 | 35 |  | 794 | 18 | 18 | RTU/UV | 6352 | 5.0913 | 2 | 5.0913 | 2
208 | Classroom | 665 | 44 |  | 794 | 18 | 18 | RTU/UV | 6352 | 6.2815 | 2 | 6.2815 | 2
208 | Boys' Toilet Room | 24 | 1 |  | 195 | 4 | 1 | RTU/UV | 1560 | 0.92308 | 0 | 0.92308 | 0
209 | Classroom | 509 | 33 |  | 794 | 18 | 18 | RTU/UV | 6352 | 4.8079 | 2 | 4.8079 | 2
210 | Classroom | 310 | 20 |  | 794 | 18 | 18 | RTU/UV | 6352 | 2.9282 | 1 | 2.9282 | 1
211 | Classroom | 418 | 27 |  | 794 | 18 | 18 | RTU/UV | 6352 | 3.9484 | 1 | 3.9484 | 1
212 | Classroom | 487 | 32 |  | 794 | 18 | 18 | RTU/UV | 6352 | 4.6001 | 2 | 4.6001 | 2
213 | Classroom | 539 | 35 |  | 794 | 18 | 18 | RTU/UV | 6352 | 5.0913 | 2 | 5.0913 | 2
215 | Classroom | 538 | 35 |  | 794 | 18 | 18 | RTU/UV | 6352 | 5.0819 | 2 | 5.0819 | 2
217 | Classroom | 683 | 45 |  | 793 | 18 | 18 | RTU/UV | 6344 | 6.4596 | 2 | 6.4596 | 2
229 | Girls' Toilet Room | 330 | 22 |  | 195 | 4 | 4 | RTU/UV | 1560 | 12.6923 | 3 | 12.6923 | 3
235 | Boys' Toilet Room | 140 | 9 |  | 200 | 4 | 4 | RTU/UV | 1600 | 5.25 | 2 | 5.25 | 2
- | Main Office | 740 | 49 |  | 500 | 11 | 11 | RTU/UV | 4000 | 11.1 | 3 | 11.1 | 3
- | Confrence Room | 475 | 31 |  | 203 | 4 | 4 | RTU/UV | 1624 | 17.5493 | 3 | 17.5493 | 3
- | Main Office 4 | 255 | 17 |  | 153 | 3 | 3 | RTU/UV | 1224 | 12.5 | 3 | 12.5 | 3
- | Main Office 3 | 255 | 17 |  | 120 | 2 | 2 | RTU/UV | 960 | 15.9375 | 3 | 15.9375 | 3
- | Main Office 2 | 260 | 17 |  | 120 | 2 | 2 | RTU/UV | 960 | 16.25 | 3 | 16.25 | 3
- | Main Office 1 | 310 | 20 |  | 162 | 3 | 3 | RTU/UV | 1296 | 14.3519 | 3 | 14.3519 | 3
- | Main Office Work Room | 245 | 16 |  | 165 | 3 | 3 | RTU/UV | 1320 | 11.1364 | 3 | 11.1364 | 3
- | Principals Office | 365 | 24 |  | 201 | 4 | 4 | RTU/UV | 1608 | 13.6194 | 3 | 13.6194 | 3
- | Principal Bathroom | 52 | 3 |  | 77 | 1 | 1 | RTU/UV | 616 | 5.0649 | 2 | 5.0649 | 2
- | IMC Workroom | 79 | 5 |  | 347 | 7 | 5 | RTU/UV | 2776 | 1.7075 | 1 | 1.7075 | 1
- | IMC Conference Rm | 128 | 8 |  | 360 | 8 | 8 | RTU/UV | 2880 | 2.6667 | 1 | 2.6667 | 1
- | IMC Reference | 62 | 4 |  | 260 | 5 | 4 | RTU/UV | 2080 | 1.7885 | 1 | 1.7885 | 1
- | IMC Main Area North | 320 | 21 |  | 1432 | 32 | 21 | RTU/UV | 11456 | 1.676 | 1 | 1.676 | 1
- | IMC Main Area South | 217 | 14 |  | 1432 | 32 | 14 | RTU/UV | 11456 | 1.1365 | 1 | 1.1365 | 1
- | Library | 710 | 47 |  | 2864 | 65 | 47 | RTU/UV | 22912 | 1.8593 | 1 | 1.8593 | 1
- | Art Room | 701 | 46 |  | 1202 | 27 | 27 | RTU/UV | 9616 | 4.374 | 2 | 4.374 | 2
- | Music Classroom | 738 | 49 |  | 1248 | 28 | 28 | RTU/UV | 9984 | 4.4351 | 2 | 4.4351 | 2
- | Cafeteria | 9535 | 635 |  | 4250 | 96 | 96 | RTU/UV | 34000 | 16.8265 | 3 | 16.8265 | 3
- | Food Service | 135 | 9 | Yes | 1600 | 36 | 36 | RTU/UV | 12800 | 0.63281 | 0 | 20.6328 | 3
- | Computer Lab | 1062 | 70 |  | 1000 | 22 | 22 | RTU/UV | 8000 | 7.965 | 2 | 7.965 | 2
- | Science Lab | 1041 | 69 |  | 1436 | 32 | 32 | RTU/UV | 11488 | 5.437 | 2 | 5.437 | 2
- | Tech Ed | 1222 | 81 |  | 1415 | 32 | 32 | RTU/UV | 11320 | 6.477 | 2 | 6.477 | 2
- | Health Suite | 575 | 38 |  | 250 | 5 | 5 | RTU/UV | 2000 | 17.25 | 3 | 17.25 | 3
- | Conference Rm | 37 | 2 |  | 99 | 2 | 2 | RTU/UV | 792 | 2.803 | 1 | 2.803 | 1
- | Corridor | 405 | 27 |  |  | 0 | 0 | RTU/UV |  | unk | unk | unk | unk
- | Lounge | 220 | 14 |  | 418 | 9 | 9 | RTU/UV | 3344 | 3.9474 | 1 | 3.9474 | 1
- | Refrence Rm | 165 | 11 |  | 120 | 2 | 2 | RTU/UV | 960 | 10.3125 | 3 | 10.3125 | 3
- | Boys' Toilet Room | 327 | 21 |  | 200 | 4 | 4 | RTU/UV | 1600 | 12.2625 | 3 | 12.2625 | 3
- | Girls' Toilet Room | 227 | 15 |  | 140 | 3 | 3 | RTU/UV | 1120 | 12.1607 | 3 | 12.1607 | 3
- | Storage | 190 | 12 |  | 156 | 3 | 3 | RTU/UV | 1248 | 9.1346 | 2 | 9.1346 | 2
- | Trash Rm | 160 | 10 |  | 213 | 4 | 4 | RTU/UV | 1704 | 5.6338 | 2 | 5.6338 | 2
- | Work Room | 160 | 10 |  | 152 | 3 | 3 | RTU/UV | 1216 | 7.8947 | 2 | 7.8947 | 2
- | Workshop | 210 | 14 |  | 153 | 3 | 3 | RTU/UV | 1224 | 10.2941 | 3 | 10.2941 | 3
- | Bldg Engineer | 160 | 10 |  | 150 | 3 | 3 | RTU/UV | 1200 | 8 | 2 | 8 | 2
- | Gym |  | 0 |  | 6809 | 154 | 0 | AHU | 54472 | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-13 | [8 empty] | unk | unk | unk | unk
School: | General Philip Kearny Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Exhaust Report | Retest | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Classroom | 0 | 0 |  | 780 | 17 | 0 | UV | 6240 | 0 | 0 | 0 | 0
2 | classroom | 900 | 60 |  | 780 | 17 | 17 | UV | 6240 | 8.6538 | 2 | 8.6538 | 2
3 | classroom | 1129 | 75 |  | 780 | 17 | 17 | UV | 6240 | 10.8558 | 3 | 10.8558 | 3
4 | classroom | 1177 | 78 |  | 780 | 17 | 17 | UV | 6240 | 11.3173 | 3 | 11.3173 | 3
100 | classroom | 1118 | 74 |  | 750 | 17 | 17 | House Fan | 6000 | 11.18 | 3 | 11.18 | 3
101 | classroom | 1353 | 90 |  | 700 | 15 | 15 | House Fan | 5600 | 14.4964 | 3 | 14.4964 | 3
103 | classroom | 1342 | 89 |  | 945 | 21 | 21 | House Fan | 7560 | 10.6508 | 3 | 10.6508 | 3
105 | classroom | 1642 | 109 |  | 696 | 15 | 15 | House Fan | 5568 | 17.694 | 3 | 17.694 | 3
107 | classroom | 314 | 20 |  | 744 | 16 | 16 | House Fan | 5952 | 3.1653 | 1 | 3.1653 | 1
200 | classroom | 1129 | 75 |  | 696 | 15 | 15 | House Fan | 5568 | 12.1659 | 3 | 12.1659 | 3
201 | classroom | 1048 | 69 |  | 696 | 15 | 15 | House Fan | 5568 | 11.2931 | 3 | 11.2931 | 3
202 | classroom | 1034 | 68 |  | 783 | 17 | 17 | House Fan | 6264 | 9.9042 | 2 | 9.9042 | 2
203 | classroom | 1345 | 89 |  | 810 | 18 | 18 | House Fan | 6480 | 12.4537 | 3 | 12.4537 | 3
204 | classroom | 1224 | 81 |  | 324 | 7 | 7 | House Fan | 2592 | 28.3333 | 4 | 28.3333 | 4
207 | classroom | 1653 | 110 |  | 768 | 17 | 17 | House Fan | 6144 | 16.1426 | 3 | 16.1426 | 3
300 | classroom | 1129 | 75 |  | 672 | 15 | 15 | House Fan | 5376 | 12.6004 | 3 | 12.6004 | 3
301 | classroom | 990 | 66 |  | 725 | 16 | 16 | House Fan | 5800 | 10.2414 | 3 | 10.2414 | 3
302 | classroom | 623 | 41 |  | 783 | 17 | 17 | House Fan | 6264 | 5.9674 | 2 | 5.9674 | 2
303 | classroom | 986 | 65 |  | 810 | 18 | 18 | House Fan | 6480 | 9.1296 | 2 | 9.1296 | 2
305 | classroom | 1268 | 84 |  | 720 | 16 | 16 | House Fan | 5760 | 13.2083 | 3 | 13.2083 | 3
306 | classroom | 1338 | 89 |  | 414 | 9 | 9 | House Fan | 3312 | 24.2391 | 4 | 24.2391 | 4
307 | classroom | 1067 | 71 |  | 768 | 17 | 17 | House Fan | 6144 | 10.4199 | 3 | 10.4199 | 3
308 | classroom | 931 | 62 |  | 675 | 15 | 15 | House Fan | 5400 | 10.3444 | 3 | 10.3444 | 3
309 | classroom | 1059 | 70 |  | 675 | 15 | 15 | House Fan | 5400 | 11.7667 | 3 | 11.7667 | 3
310 | classroom | 1114 | 74 |  | 675 | 15 | 15 | House Fan | 5400 | 12.3778 | 3 | 12.3778 | 3
311 | classroom | 1191 | 79 |  | 675 | 15 | 15 | House Fan | 5400 | 13.2333 | 3 | 13.2333 | 3
312 | classroom | 924 | 61 |  | 414 | 9 | 9 | House Fan | 3312 | 16.7391 | 3 | 16.7391 | 3
312 | classroom | 1529 | 101 |  | 414 | 9 | 9 | House Fan | 3312 | 27.6993 | 4 | 27.6993 | 4
315 | classroom | 1386 | 92 |  | 702 | 15 | 15 | House Fan | 5616 | 14.8077 | 3 | 14.8077 | 3
- | Gym | 9069 | 604 |  | 6100 | 138 | 138 | RTU | 48800 | 11.1504 | 3 | 11.1504 | 3
- | Main office |  | 0 | Yes | 340 | 7 | 7 | House Fan | 2720 | unk | unk | 20 | 3
- | Principal office |  | 0 | Yes | 320 | 7 | 7 | House Fan | 2560 | unk | unk | 20 | 3
| Cafeteria |  | 0 | Yes | 3240 | 73 | 73 |  | 25920 | unk | unk | 20 | 3
- | Auditorium |  | 0 |  | 3240 | 73 | 0 | House Fan | 25920 | unk | unk | unk | unk
- | Faculty |  | 0 |  | 336 | 7 | 0 |  | 2688 | unk | unk | unk | unk
- | Kitchen |  | 0 |  | 700 | 15 | 0 | House Fan | 5600 | unk | unk | unk | unk
- | Nurse |  | 0 | Yes | 171 | 3 | 3 | House Fan | 1368 | unk | unk | 20 | 3
- | Lunchroom |  | 0 | Yes | 3078 | 69 | 69 | House Fan | 24624 | unk | unk | 20 | 3
Sheet Last Modified: | 2021-04-22 | [8 empty] | unk | unk | unk | unk
School: | William D. Kelley Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Part 2 | [7 empty] | unk | unk | unk | unk
| Devine Part 3 | Devine Part 4 | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 315 | 21 |  | 1053 | 23 | 21 | UV | 8424 | 2.2436 | 1 | 2.2436 | 1
102 | Classroom | 322 | 21 |  | 880 | 20 | 20 | UV | 7040 | 2.7443 | 1 | 2.7443 | 1
103 | Classroom | 319 | 21 |  | 735 | 16 | 16 | UV | 5880 | 3.2551 | 1 | 3.2551 | 1
104 | Classroom | 318 | 21 |  | 805 | 18 | 18 | UV | 6440 | 2.9627 | 1 | 2.9627 | 1
104B | Classroom | 301 | 20 |  | 870 | 19 | 19 | UV | 6960 | 2.5948 | 1 | 2.5948 | 1
105 | Classroom | 357 | 23 |  | 735 | 16 | 16 | UV | 5880 | 3.6429 | 1 | 3.6429 | 1
106 | Classroom | 395 | 26 |  | 735 | 16 | 16 | UV | 5880 | 4.0306 | 2 | 4.0306 | 2
108 | Classroom | 376 | 25 |  | 735 | 16 | 16 | UV | 5880 | 3.8367 | 1 | 3.8367 | 1
109 | Classroom | 302 | 20 |  | 735 | 16 | 16 | UV | 5880 | 3.0816 | 1 | 3.0816 | 1
110 | Classroom | 321 | 21 |  | 442 | 10 | 10 | UV | 3536 | 5.4468 | 2 | 5.4468 | 2
111 | Classroom | 339 | 22 |  | 735 | 16 | 16 | UV | 5880 | 3.4592 | 1 | 3.4592 | 1
200 | Classroom | 357 | 23 |  | 700 | 15 | 15 | UV | 5600 | 3.825 | 1 | 3.825 | 1
201 | Classroom | 302 | 20 |  | 720 | 16 | 16 | UV | 5760 | 3.1458 | 1 | 3.1458 | 1
202 | Classroom | 330 | 22 |  | 770 | 17 | 17 | UV | 6160 | 3.2143 | 1 | 3.2143 | 1
203 | Classroom | 314 | 20 |  | 735 | 16 | 16 | UV | 5880 | 3.2041 | 1 | 3.2041 | 1
204 | Classroom | 355 | 23 |  | 735 | 16 | 16 | UV | 5880 | 3.6224 | 1 | 3.6224 | 1
205 | Classroom | 344 | 22 |  | 735 | 16 | 16 | UV | 5880 | 3.5102 | 1 | 3.5102 | 1
206 | Classroom | 284 | 18 |  | 406 | 9 | 9 | UV | 3248 | 5.2463 | 2 | 5.2463 | 2
207 | Classroom | 332 | 22 |  | 735 | 16 | 16 | UV | 5880 | 3.3878 | 1 | 3.3878 | 1
208 | IMC | 302 | 20 |  | 1540 | 35 | 20 | UV | 12320 | 1.4708 | 1 | 1.4708 | 1
209 | Classroom | 341 | 22 |  | 770 | 17 | 17 | UV | 6160 | 3.3214 | 1 | 3.3214 | 1
210 | IMC | 323 | 21 |  | 1540 | 35 | 21 | UV | 12320 | 1.5731 | 1 | 1.5731 | 1
211 | Classroom | 307 | 20 |  | 735 | 16 | 16 | UV | 5880 | 3.1327 | 1 | 3.1327 | 1
212 | Classroom | 305 | 20 |  | 510 | 11 | 11 | UV | 4080 | 4.4853 | 2 | 4.4853 | 2
214 | Classroom | 339 | 22 |  | 735 | 16 | 16 | UV | 5880 | 3.4592 | 1 | 3.4592 | 1
216 | Classroom | 330 | 22 |  | 735 | 16 | 16 | UV | 5880 | 3.3673 | 1 | 3.3673 | 1
218 | Classroom | 180 | 12 |  | 143 | 3 | 3 | UV | 1144 | 9.4406 | 2 | 9.4406 | 2
300 | Classroom | 311 | 20 |  | 700 | 15 | 15 | UV | 5600 | 3.3321 | 1 | 3.3321 | 1
301 | Classroom | 320 | 21 |  | 720 | 16 | 16 | UV | 5760 | 3.3333 | 1 | 3.3333 | 1
302 | Classroom | 416 | 27 |  | 770 | 17 | 17 | UV | 6160 | 4.0519 | 2 | 4.0519 | 2
303 | Classroom | 380 | 25 |  | 735 | 16 | 16 | UV | 5880 | 3.8776 | 1 | 3.8776 | 1
304 | Classroom | 305 | 20 |  | 735 | 16 | 16 | UV | 5880 | 3.1122 | 1 | 3.1122 | 1
306 | Classroom | 281 | 18 |  | 406 | 9 | 9 | UV | 3248 | 5.1909 | 2 | 5.1909 | 2
307 | Classroom | 292 | 19 |  | 735 | 16 | 16 | UV | 5880 | 2.9796 | 1 | 2.9796 | 1
308 | Classroom | 385 | 25 |  | 735 | 16 | 16 | UV | 5880 | 3.9286 | 1 | 3.9286 | 1
309 | Classroom | 318 | 21 |  | 735 | 16 | 16 | UV | 5880 | 3.2449 | 1 | 3.2449 | 1
310 | Classroom | 163 | 10 | Yes | 735 | 16 | 16 | UV | 5880 | 1.6633 | 1 | 21.6633 | 3
311 | Classroom | 334 | 22 |  | 735 | 16 | 16 | UV | 5880 | 3.4082 | 1 | 3.4082 | 1
312 | Classroom | 275 | 18 |  | 510 | 11 | 11 | UV | 4080 | 4.0441 | 2 | 4.0441 | 2
314 | Classroom | 325 | 21 |  | 735 | 16 | 16 | UV | 5880 | 3.3163 | 1 | 3.3163 | 1
316 | Classroom | 302 | 20 |  | 735 | 16 | 16 | UV | 5880 | 3.0816 | 1 | 3.0816 | 1
318 | Classroom | 181 | 12 |  | 143 | 3 | 3 | UV | 1144 | 9.493 | 2 | 9.493 | 2
- | Auditorium | 1841 | 122 |  | 4278 | 97 | 97 | AHU | 34224 | 3.2276 | 1 | 3.2276 | 1
- | Gymnasium | 899 | 59 |  | 3588 | 81 | 59 | AHU | 28704 | 1.8792 | 1 | 1.8792 | 1
- | Library | 625 | 41 |  | 1540 | 35 | 35 | UV | 12320 | 3.0438 | 1 | 3.0438 | 1
- | Main Office | 101 | 6 | Yes | 483 | 10 | 10 | AHU | 3864 | 1.5683 | 1 | 21.5683 | 3
- | Nurse Office | 84 | 5 | Yes | 368 | 8 | 8 |  | 2944 | 1.712 | 1 | 21.712 | 3
- | Admin Asst. Office | 38 | 2 |  | 99 | 2 | 2 |  | 792 | 2.8788 | 1 | 2.8788 | 1
- | Principal's Office | 41 | 2 |  | 315 | 7 | 2 |  | 2520 | 0.97619 | 0 | 0.97619 | 0
- | Conference/Office | 90 | 6 |  | 384 | 8 | 6 |  | 3072 | 1.7578 | 1 | 1.7578 | 1
- | Counselor's Office | 0 | 0 |  | 442 | 10 | 0 |  | 3536 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | John B. Kelly Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Capital | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Retest | 2nd Retest | [6 empty] | unk | unk | unk | unk
| Devine 3rd Retest | Devine 4th Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Teachers Dining | 340 | 22 |  | 868 | 19 | 19 | UV | 6944 | 2.9378 | 1 | 2.9378 | 1
102 | Classroom | 497 | 33 |  | 850 | 19 | 19 | UV | 6800 | 4.3853 | 2 | 4.3853 | 2
102A | Classroom | 155 | 10 |  | 550 | 12 | 10 | UV | 4400 | 2.1136 | 1 | 2.1136 | 1
103 | Classroom | 673 | 44 |  | 850 | 19 | 19 | UV | 6800 | 5.9382 | 2 | 5.9382 | 2
103A | Classroom | 216 | 14 |  | 550 | 12 | 12 | UV | 4400 | 2.9455 | 1 | 2.9455 | 1
104 | Classroom | 607 | 40 |  | 850 | 19 | 19 | UV | 6800 | 5.3559 | 2 | 5.3559 | 2
105 | Classroom | 592 | 39 |  | 850 | 19 | 19 | UV | 6800 | 5.2235 | 2 | 5.2235 | 2
106 | Classroom | 576 | 38 |  | 850 | 19 | 19 | UV | 6800 | 5.0824 | 2 | 5.0824 | 2
107 | Classroom | 572 | 38 |  | 850 | 19 | 19 | UV | 6800 | 5.0471 | 2 | 5.0471 | 2
108 | Classroom | 576 | 38 |  | 850 | 19 | 19 | UV | 6800 | 5.0824 | 2 | 5.0824 | 2
109 | Classroom | 539 | 35 |  | 850 | 19 | 19 | UV | 6800 | 4.7559 | 2 | 4.7559 | 2
110 | Classroom | 434 | 28 |  | 850 | 19 | 19 | UV | 6800 | 3.8294 | 1 | 3.8294 | 1
111 | Classroom | 336 | 22 |  | 850 | 19 | 19 | UV | 6800 | 2.9647 | 1 | 2.9647 | 1
112 | Classroom | 627 | 41 |  | 850 | 19 | 19 | UV | 6800 | 5.5324 | 2 | 5.5324 | 2
113 | Classroom | 320 | 21 |  | 850 | 19 | 19 | UV | 6800 | 2.8235 | 1 | 2.8235 | 1
114 | Classroom | 534 | 35 |  | 850 | 19 | 19 | UV | 6800 | 4.7118 | 2 | 4.7118 | 2
160 | Classroom | 305 | 20 |  | 942 | 21 | 20 | UV | 7536 | 2.4283 | 1 | 2.4283 | 1
160 | Main Office | 182 | 12 |  | 232 | 5 | 5 | UV | 1856 | 5.8836 | 2 | 5.8836 | 2
201 | Classroom | 370 | 24 |  | 850 | 19 | 19 | UV | 6800 | 3.2647 | 1 | 3.2647 | 1
202 | Classroom | 494 | 32 |  | 850 | 19 | 19 | UV | 6800 | 4.3588 | 2 | 4.3588 | 2
202A | Office | 33 | 2 |  | 140 | 3 | 2 | UV | 1120 | 1.7679 | 1 | 1.7679 | 1
203 | Classroom | 744 | 49 |  | 1088 | 24 | 24 | UV | 8704 | 5.1287 | 2 | 5.1287 | 2
204 | Classroom | 609 | 40 |  | 850 | 19 | 19 | UV | 6800 | 5.3735 | 2 | 5.3735 | 2
204A | Classroom | 282 | 18 |  | 550 | 12 | 12 | UV | 4400 | 3.8455 | 1 | 3.8455 | 1
205 | Classroom | 327 | 21 |  | 850 | 19 | 19 | UV | 6800 | 2.8853 | 1 | 2.8853 | 1
205A | Classroom | 293 | 19 |  | 550 | 12 | 12 | UV | 4400 | 3.9955 | 1 | 3.9955 | 1
206 | Classroom | 284 | 18 |  | 1088 | 24 | 18 | UV | 8704 | 1.9577 | 1 | 1.9577 | 1
207 | Classroom | 468 | 31 |  | 850 | 19 | 19 | UV | 6800 | 4.1294 | 2 | 4.1294 | 2
208 | Classroom | 586 | 39 |  | 850 | 19 | 19 | UV | 6800 | 5.1706 | 2 | 5.1706 | 2
209 | Classroom | 381 | 25 |  | 850 | 19 | 19 | UV | 6800 | 3.3618 | 1 | 3.3618 | 1
210 | Classroom | 341 | 22 |  | 1088 | 24 | 22 | UV | 8704 | 2.3506 | 1 | 2.3506 | 1
210A | Office | 188 | 12 |  | 136 | 3 | 3 | UV | 1088 | 10.3676 | 3 | 10.3676 | 3
211 | Classroom | 530 | 35 |  | 850 | 19 | 19 | UV | 6800 | 4.6765 | 2 | 4.6765 | 2
212 | Classroom | 729 | 48 |  | 850 | 19 | 19 | UV | 6800 | 6.4324 | 2 | 6.4324 | 2
212A | Classroom | 289 | 19 |  | 550 | 12 | 12 | UV | 4400 | 3.9409 | 1 | 3.9409 | 1
213 | Classroom | 661 | 44 |  | 850 | 19 | 19 | UV | 6800 | 5.8324 | 2 | 5.8324 | 2
213A | Classroom | 233 | 15 |  | 550 | 12 | 12 | UV | 4400 | 3.1773 | 1 | 3.1773 | 1
214 | Classroom | 588 | 39 |  | 1088 | 24 | 24 | UV | 8704 | 4.0533 | 2 | 4.0533 | 2
215 | Classroom | 341 | 22 |  | 676 | 15 | 15 | UV | 5408 | 3.7833 | 1 | 3.7833 | 1
216 | Classroom | 425 | 28 |  | 850 | 19 | 19 | UV | 6800 | 3.75 | 1 | 3.75 | 1
217 East | Classroom | 294 | 19 |  | 1006 | 22 | 19 | UV | 8048 | 2.1918 | 1 | 2.1918 | 1
217 North | Classroom | 227 | 15 |  | 1093 | 24 | 15 | UV | 8744 | 1.5576 | 1 | 1.5576 | 1
217 South Center | Classroom | 382 | 25 |  | 1069 | 24 | 24 | UV | 8552 | 2.6801 | 1 | 2.6801 | 1
217 West Center | Classroom | 285 | 19 |  | 1093 | 24 | 19 | UV | 8744 | 1.9556 | 1 | 1.9556 | 1
- | Admin/Asst. Office | 66 | 4 |  | 179 | 4 | 4 | UV | 1432 | 2.7654 | 1 | 2.7654 | 1
- | Administration Offices | 1305 | 87 |  | 535 | 12 | 12 | UV | 4280 | 18.2944 | 3 | 18.2944 | 3
ART | Art Classroom | 731 | 48 |  | 1350 | 30 | 30 | UV | 10800 | 4.0611 | 2 | 4.0611 | 2
ART -A | Art Classroom | 401 | 26 |  |  | 0 | 0 | UV |  | unk | unk | unk | unk
ART -B | Art Classroom | 557 | 37 |  |  | 0 | 0 | UV |  | unk | unk | unk | unk
ART -C | Art Classroom | 111 | 7 |  |  | 0 | 0 | UV |  | unk | unk | unk | unk
ART -D | Art Classroom | 318 | 21 |  |  | 0 | 0 | UV |  | unk | unk | unk | unk
- | Auditorium | 1721 | 114 |  | 6080 | 138 | 114 | UV | 48640 | 2.1229 | 1 | 2.1229 | 1
- | 1st Flr A-Wing Left Boys Bathroom | 53 | 3 |  | 88 | 2 | 2 | AHU | 704 | 4.517 | 2 | 4.517 | 2
- | 2nd Flr A-Wing Left Boys Bathroom | 101 | 6 |  | 96 | 2 | 2 | AHU | 768 | 7.8906 | 2 | 7.8906 | 2
- | 2nd Flr A-Wing Right Boys Bathroom | 43 | 2 |  | 103 | 2 | 2 | AHU | 824 | 3.1311 | 1 | 3.1311 | 1
- | Conference Room | 139 | 9 |  | 211 | 4 | 4 | AHU | 1688 | 4.9408 | 2 | 4.9408 | 2
- | Copy/Storage Room | 110 | 7 |  | 165 | 3 | 3 | AHU | 1320 | 5 | 2 | 5 | 2
- | Corridor | 41 | 2 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | Counselor Office | 58 | 3 |  | 123 | 2 | 2 | AHU | 984 | 3.5366 | 1 | 3.5366 | 1
- | Dressing - A Backstage | 307 | 20 |  | 232 | 5 | 5 | UV | 1856 | 9.9246 | 2 | 9.9246 | 2
- | Dressing - B Backstage | 461 | 30 |  | 196 | 4 | 4 | UV | 1568 | 17.6403 | 3 | 17.6403 | 3
- | Dressing - C Backstage | 493 | 32 |  | 190 | 4 | 4 | UV | 1520 | 19.4605 | 3 | 19.4605 | 3
- | Dressing - D Backstage | 275 | 18 |  | 199 | 4 | 4 | UV | 1592 | 10.3643 | 3 | 10.3643 | 3
- | 1st Flr A-Wing Left Girls Bathroom | 41 | 2 |  | 109 | 2 | 2 | AHU | 872 | 2.8211 | 1 | 2.8211 | 1
- | 2nd Flr A-Wing Left Girls Bathroom | 78 | 5 |  | 106 | 2 | 2 | AHU | 848 | 5.5189 | 2 | 5.5189 | 2
- | 2nd Flr A-Wing Right Girls Bathroom | 54 | 3 |  | 103 | 2 | 2 | AHU | 824 | 3.932 | 1 | 3.932 | 1
- | IMC | 0 | 0 |  | 8471 | 192 | 0 | AHU | 67768 | 0 | 0 | 0 | 0
- | IMC North Side | 947 | 63 |  | 480 | 10 | 10 | AHU | 3840 | 14.7969 | 3 | 14.7969 | 3
- | IMC South Side | 822 | 54 |  | 480 | 10 | 10 | AHU | 3840 | 12.8438 | 3 | 12.8438 | 3
- | IMC Entry from Office | 0 | 0 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | IMC Entry to Hall | 0 | 0 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | IMC-1 Office | 80 | 5 |  | 293 | 6 | 5 | AHU | 2344 | 2.0478 | 1 | 2.0478 | 1
- | IMC-2 Storage | 151 | 10 |  | 330 | 7 | 7 | AHU | 2640 | 3.4318 | 1 | 3.4318 | 1
- | IMC-4 Storage | 175 | 11 |  | 372 | 8 | 8 | AHU | 2976 | 3.5282 | 1 | 3.5282 | 1
- | IMC-5 Data/Storage | 68 | 4 |  | 277 | 6 | 4 | AHU | 2216 | 1.8412 | 1 | 1.8412 | 1
- | Cafeteria | 0 | 0 |  | 1195 | 27 | 0 | AHU | 9560 | 0 | 0 | 0 | 0
- | Cafeteria | 1928 | 128 |  | 4807 | 109 | 109 | AHU | 38456 | 3.0081 | 1 | 3.0081 | 1
- | Gym | 2934 | 195 |  | 387 | 8 | 8 | AHU | 3096 | 56.8605 | 5 | 56.8605 | 5
- | Music Classroom A | 326 | 21 |  |  | 0 | 0 | UV |  | unk | unk | unk | unk
- | Music Classroom B | 555 | 37 |  |  | 0 | 0 | UV |  | unk | unk | unk | unk
- | Music Classroom C | 152 | 10 |  |  | 0 | 0 | UV |  | unk | unk | unk | unk
- | Music Classroom D | 106 | 7 |  |  | 0 | 0 | UV |  | unk | unk | unk | unk
- | Main Music Classroom | 463 | 30 |  | 380 | 8 | 8 | UV | 3040 | 9.1382 | 2 | 9.1382 | 2
- | Music Office | 136 | 9 |  | 355 | 8 | 8 | AHU | 2840 | 2.8732 | 1 | 2.8732 | 1
- | Nurse Exam Room | 0 | 0 |  | 209 | 4 | 0 | AHU | 1672 | 0 | 0 | 0 | 0
- | Nurse Exam Room | 43 | 2 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | Nurses Office | 0 | 0 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | Nurses Rest | 68 | 4 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | Nurses Suite | 411 | 27 |  |  | 0 | 0 | UV |  | unk | unk | unk | unk
- | Aud & Dental | 31 | 2 |  | 270 | 6 | 2 | AHU | 2160 | 0.86111 | 0 | 0.86111 | 0
- | Principals Office | 98 | 6 |  | 270 | 6 | 6 | AHU | 2160 | 2.7222 | 1 | 2.7222 | 1
- | Speech/Com | 388 | 25 |  | 736 | 16 | 16 | UV | 5888 | 3.9538 | 1 | 3.9538 | 1
- | Server Room | 55 | 3 |  | 121 | 2 | 2 | Split System | 968 | 3.4091 | 1 | 3.4091 | 1
- | Storage | 247 | 16 |  | 809 | 18 | 16 | AHU | 6472 | 2.2899 | 1 | 2.2899 | 1
- | Office / Waiting Room | 277 | 18 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
K - 1 | Kindergarten | 452 | 30 |  | 1488 | 33 | 30 | UV | 11904 | 2.2782 | 1 | 2.2782 | 1
K - 2 | Kindergarten | 490 | 32 |  | 1488 | 33 | 32 | UV | 11904 | 2.4698 | 1 | 2.4698 | 1
K - 3 | Kindergarten | 498 | 33 |  | 1488 | 33 | 33 | UV | 11904 | 2.5101 | 1 | 2.5101 | 1
K - 4 | Kindergarten | 635 | 42 |  | 1488 | 33 | 33 | UV | 11904 | 3.2006 | 1 | 3.2006 | 1
K - 5 | Kindergarten | 280 | 18 |  | 1488 | 33 | 18 | UV | 11904 | 1.4113 | 1 | 1.4113 | 1
K - 6 | Kindergarten | 300 | 20 |  | 1488 | 33 | 20 | UV | 11904 | 1.5121 | 1 | 1.5121 | 1
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Kenderton Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Part 2 | Part 3 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 229 | 15 |  | 1012 | 23 | 15 | UV | 8096 | 1.6971 | 1 | 1.6971 | 1
101 | Classroom | 451 | 30 |  | 1680 | 38 | 30 | UV | 13440 | 2.0134 | 1 | 2.0134 | 1
102 | Classroom | 458 | 30 |  | 1652 | 37 | 30 | UV | 13216 | 2.0793 | 1 | 2.0793 | 1
103 | Classroom | 331 | 22 | Yes | 1344 | 30 | 30 | UV | 10752 | 1.8471 | 1 | 21.8471 | 3
104 | Nurse |  | 0 | Yes | 275 | 6 | 6 |  | 2200 | unk | unk | 20 | 3
200A | Classroom | 198 | 13 |  | 442 | 10 | 10 | UV | 3536 | 3.3597 | 1 | 3.3597 | 1
200 | Classroom | 0 | 0 |  | 891 | 20 | 0 | UV | 7128 | 0 | 0 | 0 | 0
201 | Classroom | 278 | 18 | Yes | 891 | 20 | 20 | UV | 7128 | 2.3401 | 1 | 22.3401 | 3
202 | Classroom | 331 | 22 |  | 918 | 20 | 20 | UV | 7344 | 2.7042 | 1 | 2.7042 | 1
203 | Classroom | 297 | 19 |  | 980 | 22 | 19 | UV | 7840 | 2.273 | 1 | 2.273 | 1
204 | Classroom | 302 | 20 |  | 918 | 20 | 20 | UV | 7344 | 2.4673 | 1 | 2.4673 | 1
205 | Classroom | 198 | 13 |  | 918 | 20 | 13 | UV | 7344 | 1.6176 | 1 | 1.6176 | 1
206 | Classroom | 273 | 18 |  | 616 | 14 | 14 | UV | 4928 | 3.3239 | 1 | 3.3239 | 1
207 | Classroom | 273 | 18 |  | 918 | 20 | 18 | UV | 7344 | 2.2304 | 1 | 2.2304 | 1
208 | Classroom | 191 | 12 | Yes | 120 | 2 | 2 | UV | 960 | 11.9375 | 3 | 31.9375 | 4
209 | Classroom | 283 | 18 |  | 918 | 20 | 18 | UV | 7344 | 2.3121 | 1 | 2.3121 | 1
211 | Classroom | 276 | 18 |  | 286 | 6 | 6 | UV | 2288 | 7.2378 | 2 | 7.2378 | 2
213 | Classroom | 271 | 18 |  | 918 | 20 | 18 | UV | 7344 | 2.2141 | 1 | 2.2141 | 1
300 | Classroom | 278 | 18 | Yes | 918 | 20 | 20 | UV | 7344 | 2.2712 | 1 | 22.2712 | 3
301 | Classroom | 271 | 18 |  | 918 | 20 | 18 | UV | 7344 | 2.2141 | 1 | 2.2141 | 1
302 | Classroom | 272 | 18 | Yes | 918 | 20 | 20 | UV | 7344 | 2.2222 | 1 | 22.2222 | 3
303 | Classroom | 296 | 19 |  | 980 | 22 | 19 | UV | 7840 | 2.2653 | 1 | 2.2653 | 1
304 | Classroom | 276 | 18 |  | 864 | 19 | 18 | UV | 6912 | 2.3958 | 1 | 2.3958 | 1
306 | Classroom | 316 | 21 |  | 918 | 20 | 20 | UV | 7344 | 2.5817 | 1 | 2.5817 | 1
307 | Classroom | 281 | 18 | Yes | 924 | 21 | 21 | UV | 7392 | 2.2808 | 1 | 22.2808 | 3
308 | Classroom | 0 | 0 | Yes | 924 | 21 | 21 | UV | 7392 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 |  | 980 | 22 | 0 | UV | 7840 | 0 | 0 | 0 | 0
310 | Classroom | 0 | 0 | Yes | 616 | 14 | 14 | UV | 4928 | 0 | 0 | 20 | 3
311 | Classroom | 0 | 0 | Yes | 918 | 20 | 20 | UV | 7344 | 0 | 0 | 20 | 3
312 | Computer Room |  | 0 | Yes | 860 | 19 | 19 |  | 6880 | unk | unk | 20 | 3
313 | Classroom | 0 | 0 | Yes | 918 | 20 | 20 | UV | 7344 | 0 | 0 | 20 | 3
314 | Classroom | 0 | 0 |  | 280 | 6 | 0 | UV | 2240 | 0 | 0 | 0 | 0
315 | Classroom | 0 | 0 | Yes | 918 | 20 | 20 | UV | 7344 | 0 | 0 | 20 | 3
316 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | UV | 6720 | 0 | 0 | 20 | 3
319 | Classroom | 0 | 0 |  | 918 | 20 | 0 | UV | 7344 | 0 | 0 | 0 | 0
400 | Classroom | 286 | 19 |  | 2660 | 60 | 19 | UV | 21280 | 0.80639 | 0 | 0.80639 | 0
401 | Classroom | 279 | 18 |  | 918 | 20 | 18 | UV | 7344 | 2.2794 | 1 | 2.2794 | 1
402 | Classroom | 313 | 20 |  | 918 | 20 | 20 | UV | 7344 | 2.5572 | 1 | 2.5572 | 1
403 | Classroom | 340 | 22 |  | 918 | 20 | 20 | UV | 7344 | 2.7778 | 1 | 2.7778 | 1
404 | Classroom | 0 | 0 |  | 868 | 19 | 0 | UV | 6944 | 0 | 0 | 0 | 0
406 | Classroom | 291 | 19 |  | 918 | 20 | 19 | UV | 7344 | 2.3775 | 1 | 2.3775 | 1
407 | Classroom | 0 | 0 | Yes | 924 | 21 | 21 | UV | 7392 | 0 | 0 | 20 | 3
408 | Classroom | 0 | 0 | Yes | 918 | 20 | 20 | UV | 7344 | 0 | 0 | 20 | 3
409 | Classroom | 0 | 0 | Yes | 980 | 22 | 22 | UV | 7840 | 0 | 0 | 20 | 3
410 | Classroom | 335 | 22 | Yes | 644 | 14 | 14 | UV | 5152 | 3.9014 | 1 | 23.9014 | 3
411 | Classroom | 0 | 0 |  | 918 | 20 | 0 | UV | 7344 | 0 | 0 | 0 | 0
412 | Classroom | 276 | 18 |  | 308 | 7 | 7 | UV | 2464 | 6.7208 | 2 | 6.7208 | 2
413 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | UV | 6720 | 0 | 0 | 20 | 3
414 | Classroom | 0 | 0 | Yes | 270 | 6 | 6 | UV | 2160 | 0 | 0 | 20 | 3
415 | Classroom | 0 | 0 |  | 918 | 20 | 0 | UV | 7344 | 0 | 0 | 0 | 0
- | Parent Resource | 0 | 0 |  | 2 | 0 | 0 | UV | 16 | 0 | 0 | 0 | 0
- | Main Office | 42 | 2 |  | 406 | 9 | 2 | UV | 3248 | 0.77586 | 0 | 0.77586 | 0
- | Principal's Office |  | 0 |  | 320 | 7 | 0 |  | 2560 | unk | unk | unk | unk
- | Asist Prince | 172 | 11 |  | 11 | 0 | 0 | UV | 88 | 117.2727 | 5 | 117.2727 | 5
Sheet Last Modified: | 2021-04-19 | [8 empty] | unk | unk | unk | unk
School: | Kensington High School | House fan Abated | [7 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | - |  | 0 |  | 675 | 15 | 0 |  | 5400 | unk | unk | unk | unk
2 | - |  | 0 |  | 1014 | 23 | 0 |  | 8112 | unk | unk | unk | unk
3 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
4 | - |  | 0 |  | 364 | 8 | 0 |  | 2912 | unk | unk | unk | unk
5 | - |  | 0 |  | 850 | 19 | 0 |  | 6800 | unk | unk | unk | unk
100 | Main Office |  | 0 |  | 1014 | 23 | 0 |  | 8112 | unk | unk | unk | unk
102 | - |  | 0 | Yes | 800 | 18 | 18 |  | 6400 | unk | unk | 20 | 3
103 | IMC |  | 0 |  | 1690 | 38 | 0 |  | 13520 | unk | unk | unk | unk
104 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
105 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
107 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
108 | - |  | 0 |  | 962 | 21 | 0 |  | 7696 | unk | unk | unk | unk
109 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
111 | - |  | 0 |  | 910 | 20 | 0 |  | 7280 | unk | unk | unk | unk
114 | - |  | 0 | Yes | 728 | 16 | 16 |  | 5824 | unk | unk | 20 | 3
115 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
116 | - |  | 0 |  | 702 | 15 | 0 |  | 5616 | unk | unk | unk | unk
117 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
118 | - |  | 0 | Yes | 728 | 16 | 16 |  | 5824 | unk | unk | 20 | 3
120 | - |  | 0 |  | 845 | 19 | 0 |  | 6760 | unk | unk | unk | unk
125 | - |  | 0 |  | 1020 | 23 | 0 |  | 8160 | unk | unk | unk | unk
200 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
201 | - |  | 0 |  | 962 | 21 | 0 |  | 7696 | unk | unk | unk | unk
202 | - |  | 0 |  | 910 | 20 | 0 |  | 7280 | unk | unk | unk | unk
203 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
204 | - |  | 0 |  | 702 | 15 | 0 |  | 5616 | unk | unk | unk | unk
205 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
207 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
208 | - |  | 0 |  | 884 | 20 | 0 |  | 7072 | unk | unk | unk | unk
209 | - |  | 0 |  | 546 | 12 | 0 |  | 4368 | unk | unk | unk | unk
210 | - |  | 0 |  | 546 | 12 | 0 |  | 4368 | unk | unk | unk | unk
211 | - |  | 0 |  | 884 | 20 | 0 |  | 7072 | unk | unk | unk | unk
214 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
215 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
217 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
218 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
221 | - |  | 0 |  | 1037 | 23 | 0 |  | 8296 | unk | unk | unk | unk
300 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
301 | - |  | 0 |  | 910 | 20 | 0 |  | 7280 | unk | unk | unk | unk
302 | - |  | 0 |  | 910 | 20 | 0 |  | 7280 | unk | unk | unk | unk
303 | - |  | 0 |  | 702 | 15 | 0 |  | 5616 | unk | unk | unk | unk
304 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
305 | - |  | 0 |  | 702 | 15 | 0 |  | 5616 | unk | unk | unk | unk
307 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
308 | - |  | 0 |  | 910 | 20 | 0 |  | 7280 | unk | unk | unk | unk
309 | - |  | 0 |  | 546 | 12 | 0 |  | 4368 | unk | unk | unk | unk
310 | - |  | 0 |  | 546 | 12 | 0 |  | 4368 | unk | unk | unk | unk
311 | - |  | 0 |  | 884 | 20 | 0 |  | 7072 | unk | unk | unk | unk
314 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
315 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
316 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
317 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
318 | - |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
322 | Gym |  | 0 |  | 6360 | 144 | 0 |  | 50880 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-22 | [8 empty] | unk | unk | unk | unk
School: | Kensington Creative and Performing Arts (CAPA) High School | [8 empty] | unk | unk | unk | unk
Vendor: | Meehan | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Auditorium |  | 0 |  | 5100 | 115 | 0 |  | 40800 | unk | unk | unk | unk
- | Gymnasium |  | 0 |  | 8400 | 190 | 0 |  | 67200 | unk | unk | unk | unk
101b | - |  | 0 |  | 450 | 10 | 0 |  | 3600 | unk | unk | unk | unk
101 | - |  | 0 |  | 400 | 9 | 0 |  | 3200 | unk | unk | unk | unk
103 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | unk | unk | unk | unk
106 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | unk | unk | unk | unk
118 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
119 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
121 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
122 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
123 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
131 | - |  | 0 |  | 1150 | 26 | 0 |  | 9200 | unk | unk | unk | unk
134 | - |  | 0 | Yes | 700 | 15 | 15 |  | 5600 | unk | unk | 20 | 3
135 | - |  | 0 |  | 750 | 17 | 0 |  | 6000 | unk | unk | unk | unk
201 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | unk | unk | unk | unk
209 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
210 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
212 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
213 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
214 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
216 | - |  | 0 | Yes | 1400 | 31 | 31 |  | 11200 | unk | unk | 20 | 3
217 | - |  | 0 |  | 1400 | 31 | 0 |  | 11200 | unk | unk | unk | unk
218 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | unk | unk | unk | unk
220 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | unk | unk | unk | unk
221 | - |  | 0 |  | 1200 | 27 | 0 |  | 9600 | unk | unk | unk | unk
224 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
225 | - |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
- | Cafe |  | 0 |  | 2400 | 54 | 0 |  | 19200 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Kensington Health Sciences Academy High School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Room | 247 | 16 |  | 857 | 19 | 16 |  | 6856 | 2.1616 | 1 | 2.1616 | 1
102 | Room | 338 | 22 |  | 792 | 18 | 18 |  | 6336 | 3.2008 | 1 | 3.2008 | 1
103 | Room | 206 | 13 |  | 854 | 19 | 13 |  | 6832 | 1.8091 | 1 | 1.8091 | 1
104 | Room | 248 | 16 |  | 834 | 18 | 16 |  | 6672 | 2.2302 | 1 | 2.2302 | 1
105 | Room | 212 | 14 |  | 854 | 19 | 14 |  | 6832 | 1.8618 | 1 | 1.8618 | 1
106 | Room | 548 | 36 |  | 834 | 18 | 18 |  | 6672 | 4.9281 | 2 | 4.9281 | 2
107 & 107A | Room | 613 | 40 |  | 783 | 17 | 17 |  | 6264 | 5.8716 | 2 | 5.8716 | 2
110 | Room | 184 | 12 |  | 793 | 18 | 12 |  | 6344 | 1.7402 | 1 | 1.7402 | 1
114 | Nurse |  | 0 |  | 114 | 2 | 0 |  | 912 | unk | unk | unk | unk
115 | Room | 191 | 12 |  | 337 | 7 | 7 |  | 2696 | 4.2507 | 2 | 4.2507 | 2
116 | Room | 171 | 11 |  | 848 | 19 | 11 |  | 6784 | 1.5124 | 1 | 1.5124 | 1
201 | Room | 506 | 33 |  | 919 | 20 | 20 |  | 7352 | 4.1295 | 2 | 4.1295 | 2
203 | Room | 0 | 0 |  | 795 | 18 | 0 |  | 6360 | 0 | 0 | 0 | 0
208 | 2nd Floor Bed and Dental Area | 1803 | 120 |  | 943 | 21 | 21 |  | 7544 | 14.3399 | 3 | 14.3399 | 3
211 | Room | 273 | 18 |  | 860 | 19 | 18 |  | 6880 | 2.3808 | 1 | 2.3808 | 1
212 | Room | 77 | 5 |  | 456 | 10 | 5 |  | 3648 | 1.2664 | 1 | 1.2664 | 1
213 | Room | 250 | 16 |  | 681 | 15 | 15 |  | 5448 | 2.7533 | 1 | 2.7533 | 1
214 | Dental Classroom | 171 | 11 |  | 794 | 18 | 11 |  | 6352 | 1.6152 | 1 | 1.6152 | 1
215 | Room | 204 | 13 |  | 689 | 15 | 13 |  | 5512 | 2.2206 | 1 | 2.2206 | 1
216 | Room | 191 | 12 |  | 756 | 17 | 12 |  | 6048 | 1.8948 | 1 | 1.8948 | 1
217 | Room | 222 | 14 |  | 681 | 15 | 14 |  | 5448 | 2.4449 | 1 | 2.4449 | 1
218 | Room | 276 | 18 |  | 599 | 13 | 13 |  | 4792 | 3.4558 | 1 | 3.4558 | 1
- | Cafeteria | 586 | 39 |  | 1697 | 38 | 38 |  | 13576 | 2.5899 | 1 | 2.5899 | 1
Sheet Last Modified: | 2021-03-30 | [8 empty] | unk | unk | unk | unk
School: | Francis Scott Key Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | [9 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Gym |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | unk | unk | 20 | 3
104 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
105 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
106 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
107 | Classroom |  | 0 |  | 437 | 9 | 0 | House Fan | 3496 | unk | unk | unk | unk
108 | Classroom |  | 0 |  | 667 | 15 | 0 | House Fan | 5336 | unk | unk | unk | unk
109 | Classroom |  | 0 |  | 667 | 15 | 0 | House Fan | 5336 | unk | unk | unk | unk
110 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
111 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
212 | Classroom |  | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | unk | unk | 20 | 3
213 | Classroom |  | 0 | Yes | 837 | 19 | 19 | House Fan | 6696 | unk | unk | 20 | 3
215 | IMC |  | 0 | Yes | 1536 | 34 | 34 | House Fan | 12288 | unk | unk | 20 | 3
216 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
217 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
218 | Classroom |  | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | unk | unk | 20 | 3
219 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
220 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
221 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
222 | Computer Lab |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | unk | unk | unk | unk
323 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan | 5704 | unk | unk | unk | unk
324 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan | 5704 | unk | unk | unk | unk
325 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan | 5704 | unk | unk | unk | unk
326 | Classroom |  | 0 |  | 736 | 16 | 0 | House Fan | 5888 | unk | unk | unk | unk
327 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan | 5704 | unk | unk | unk | unk
328 | Classroom |  | 0 |  | 768 | 17 | 0 | House Fan | 6144 | unk | unk | unk | unk
329 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
330 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
331 | Classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | unk | unk | unk | unk
332 | Classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | unk | unk | unk | unk
333 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
- | Boy's Gang Bathrrom |  | 0 |  | 620 | 14 | 0 | N/A | 4960 | unk | unk | unk | unk
- | Caferteria |  | 0 | Yes | 2240 | 50 | 50 | House Fan | 17920 | unk | unk | 20 | 3
- | Counselor's Office |  | 0 |  | 180 | 4 | 0 | House Fan | 1440 | unk | unk | unk | unk
- | Girls Gang Bathrrom |  | 0 |  | 620 | 14 | 0 | N/A | 4960 | unk | unk | unk | unk
- | Main Office |  | 0 | Yes | 361 | 8 | 8 | House Fan | 2888 | unk | unk | 20 | 3
- | Nurse |  | 0 | Yes | 391 | 8 | 8 | House Fan | 3128 | unk | unk | 20 | 3
- | Principle's Office |  | 0 |  | 276 | 6 | 0 | House Fan | 2208 | unk | unk | unk | unk
- | Teachers' Lounge |  | 0 |  | 391 | 8 | 0 | House Fan | 3128 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-24 | [8 empty] | unk | unk | unk | unk
School: | Eliza B. Kirkbride Elementary-Middle | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | - |  | 0 | Yes | 805 | 18 | 18 | House Fan | 6440 | unk | unk | 20 | 3
102 | - |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
103 | - |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
104 | - |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
106 | - |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
107 | - |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
108 | - |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
109 | - |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
110 | - |  | 0 | Yes | 841 | 19 | 19 | House Fan | 6728 | unk | unk | 20 | 3
201 | - |  | 0 | Yes | 814 | 18 | 18 | House Fan | 6512 | unk | unk | 20 | 3
202 | - |  | 0 |  | 660 | 15 | 0 | House Fan | 5280 | unk | unk | unk | unk
203 | - |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
204 | - |  | 0 |  | 660 | 15 | 0 | House Fan | 5280 | unk | unk | unk | unk
205 | - |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
208 | - |  | 0 | Yes | 638 | 14 | 14 | House Fan | 5104 | unk | unk | 20 | 3
209 | - |  | 0 |  | 638 | 14 | 0 | House Fan | 5104 | unk | unk | unk | unk
210 | - |  | 0 | Yes | 841 | 19 | 19 | House Fan | 6728 | unk | unk | 20 | 3
211 | - |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
212 | - |  | 0 |  | 638 | 14 | 0 | House Fan | 5104 | unk | unk | unk | unk
301 | - |  | 0 |  | 851 | 19 | 0 | House Fan | 6808 | unk | unk | unk | unk
302 | - |  | 0 |  | 660 | 15 | 0 | House Fan | 5280 | unk | unk | unk | unk
303 | - |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | unk | unk | unk | unk
304 | - |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
305/306 | - |  | 0 |  | 1357 | 30 | 0 | House Fan | 10856 | unk | unk | unk | unk
307 | - |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
308 | - |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
309 | - |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
310 | - |  | 0 |  | 841 | 19 | 0 | House Fan | 6728 | unk | unk | unk | unk
311 | - |  | 0 |  | 660 | 15 | 0 | House Fan | 5280 | unk | unk | unk | unk
312 | - |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
- | Art |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
- | Counselor Suite |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
- | Gym |  | 0 | Yes | 3680 | 83 | 83 | House Fan | 29440 | unk | unk | 20 | 3
- | Library |  | 0 | Yes | 1380 | 31 | 31 | House Fan | 11040 | unk | unk | 20 | 3
- | Lunchroom1 |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
- | Lunchroom2 |  | 0 | Yes | 1100 | 25 | 25 | House Fan | 8800 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 322 | 7 | 7 | House Fan | 2576 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 96 | 2 | 2 | House Fan | 768 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 240 | 5 | 5 | House Fan | 1920 | unk | unk | 20 | 3
- | Teacher Lounge/BE office |  | 0 | Yes | 960 | 21 | 21 | House Fan | 7680 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-20 | [8 empty] | unk | unk | unk | unk
School: | John Hancock Demonstration Middle School @ General J Harry LaBrum Campus | [8 empty] | unk | unk | unk | unk
| LaBrum Building | LaBrum Retest | [7 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
102 | Classroom | 391 | 26 |  | 875 | 19 | 19 | UV | 7000 | 3.3514 | 1 | 3.3514 | 1
102A | Classroom | 230 | 15 |  | 578 | 13 | 13 | UV | 4624 | 2.9844 | 1 | 2.9844 | 1
103 | Classroom | 0 | 0 | Yes | 910 | 20 | 20 | UV | 7280 | 0 | 0 | 20 | 3
104 | Classroom | 622 | 41 |  | 612 | 13 | 13 | UV | 4896 | 7.6225 | 2 | 7.6225 | 2
105 | Classroom | 150 | 10 | Yes | 1152 | 26 | 26 | UV | 9216 | 0.97656 | 0 | 20.9766 | 3
106 | Classroom | 320 | 21 |  | 342 | 7 | 7 | UV | 2736 | 7.0175 | 2 | 7.0175 | 2
107 | Classroom | 221 | 14 | Yes | 1044 | 23 | 23 | UV | 8352 | 1.5876 | 1 | 21.5876 | 3
201 | Classroom | 362 | 24 |  | 864 | 19 | 19 | UV | 6912 | 3.1424 | 1 | 3.1424 | 1
202 | Classroom | 267 | 17 |  | 782 | 17 | 17 | UV | 6256 | 2.5607 | 1 | 2.5607 | 1
203 | Classroom | 245 | 16 | Yes | 884 | 20 | 20 | UV | 7072 | 2.0786 | 1 | 22.0786 | 3
204 | Classroom | 240 | 16 | Yes | 1116 | 25 | 25 | UV | 8928 | 1.6129 | 1 | 21.6129 | 3
205 | Classroom | 311 | 20 |  | 900 | 20 | 20 | UV | 7200 | 2.5917 | 1 | 2.5917 | 1
206 | Classroom | 583 | 38 |  | 858 | 19 | 19 | UV | 6864 | 5.0962 | 2 | 5.0962 | 2
207 | Classroom | 340 | 22 |  | 840 | 19 | 19 | UV | 6720 | 3.0357 | 1 | 3.0357 | 1
208 | Classroom | 462 | 30 |  | 816 | 18 | 18 | UV | 6528 | 4.2463 | 2 | 4.2463 | 2
209 | Classroom | 410 | 27 |  | 720 | 16 | 16 | UV | 5760 | 4.2708 | 2 | 4.2708 | 2
210 | Classroom | 327 | 21 |  | 888 | 20 | 20 | UV | 7104 | 2.7618 | 1 | 2.7618 | 1
212 | Classroom | 390 | 26 |  | 875 | 19 | 19 | UV | 7000 | 3.3429 | 1 | 3.3429 | 1
213 | Classroom | 336 | 22 |  | 864 | 19 | 19 | UV | 6912 | 2.9167 | 1 | 2.9167 | 1
214 | Classroom | 366 | 24 |  | 828 | 18 | 18 | UV | 6624 | 3.3152 | 1 | 3.3152 | 1
- | Admin | 0 | 0 | Yes | 286 | 6 | 6 | UV | 2288 | 0 | 0 | 20 | 3
- | Cafeteria | 450 | 30 |  | 2765 | 62 | 30 | UV | 22120 | 1.2206 | 1 | 1.2206 | 1
- | Gym | 0 | 0 |  | 5248 | 119 | 0 |  | 41984 | 0 | 0 | 0 | 0
- | Library | 538 | 35 |  | 2016 | 45 | 35 | UV | 16128 | 2.0015 | 1 | 2.0015 | 1
- | Nurse's Room | 0 | 0 | Yes | 550 | 12 | 12 | UV | 4400 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | Robert E. Lamberton Elementary School | [8 empty] | unk | unk | unk | unk
School: | Robert E. Lamberton Elementary- Little School House | [8 empty] | unk | unk | unk | unk
School: | Robert E. Lamberton Elementary- Little School House- Part 2 | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Main Building | [9 empty] | unk | unk | unk | unk
1A | Music Room | 261 | 17 |  | 506 | 11 | 11 | UV | 4048 | 3.8686 | 1 | 3.8686 | 1
1B | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | UV | 5760 | 0 | 0 | 20 | 3
2A | Classroom | 264 | 17 |  | 504 | 11 | 11 | UV | 4032 | 3.9286 | 1 | 3.9286 | 1
4 | Classroom | 159 | 10 | Yes | 2024 | 46 | 46 | UV | 16192 | 0.58918 | 0 | 20.5892 | 3
5A | Classroom | 0 | 0 | Yes | 600 | 13 | 13 | UV | 4800 | 0 | 0 | 20 | 3
6 | Classroom | 0 | 0 | Yes | 625 | 14 | 14 | UV | 5000 | 0 | 0 | 20 | 3
7 | Classroom |  | 0 | Yes | 1206 | 27 | 27 | UV | 9648 | unk | unk | 20 | 3
101 | Classroom | 457 | 30 |  | 506 | 11 | 11 | UV | 4048 | 6.7737 | 2 | 6.7737 | 2
102 | Classroom | 348 | 23 |  | 1012 | 23 | 23 | UV | 8096 | 2.5791 | 1 | 2.5791 | 1
103 | Classroom | 466 | 31 |  | 989 | 22 | 22 | UV | 7912 | 3.5339 | 1 | 3.5339 | 1
104 | Classroom | 335 | 22 | Yes | 1012 | 23 | 23 | UV | 8096 | 2.4827 | 1 | 22.4827 | 3
105 | Classroom | 277 | 18 | Yes | 989 | 22 | 22 | UV | 7912 | 2.1006 | 1 | 22.1006 | 3
106 | Classroom | 198 | 13 | Yes | 1012 | 23 | 23 | UV | 8096 | 1.4674 | 1 | 21.4674 | 3
107 | Classroom | 406 | 27 |  | 1012 | 23 | 23 | UV | 8096 | 3.0089 | 1 | 3.0089 | 1
108 | Classroom | 271 | 18 |  | 667 | 15 | 15 | UV | 5336 | 3.0472 | 1 | 3.0472 | 1
109 | Classroom | 351 | 23 |  | 1012 | 23 | 23 | UV | 8096 | 2.6013 | 1 | 2.6013 | 1
110 | Classroom | 420 | 28 |  | 989 | 22 | 22 | UV | 7912 | 3.185 | 1 | 3.185 | 1
111 | Classroom | 338 | 22 |  | 989 | 22 | 22 | UV | 7912 | 2.5632 | 1 | 2.5632 | 1
112 | Classroom | 0 | 0 | Yes | 989 | 22 | 22 | UV | 7912 | 0 | 0 | 20 | 3
113 | Classroom | 280 | 18 |  | 575 | 13 | 13 | UV | 4600 | 3.6522 | 1 | 3.6522 | 1
114 | Classroom | 271 | 18 | Yes | 874 | 19 | 19 | UV | 6992 | 2.3255 | 1 | 22.3255 | 3
115 | Classroom | 278 | 18 | Yes | 874 | 19 | 19 | UV | 6992 | 2.3856 | 1 | 22.3856 | 3
116 | Classroom | 387 | 25 |  | 874 | 19 | 19 | UV | 6992 | 3.3209 | 1 | 3.3209 | 1
117 | Classroom | 176 | 11 | Yes | 874 | 19 | 19 | UV | 6992 | 1.5103 | 1 | 21.5103 | 3
118 | Classroom | 243 | 16 | Yes | 1012 | 23 | 23 | UV | 8096 | 1.8009 | 1 | 21.8009 | 3
119 | Assitant Principal |  | 0 | Yes | 361 | 8 | 8 |  | 2888 | unk | unk | 20 | 3
120A | Tescher's Lounge |  | 0 | Yes | 377 | 8 | 8 |  | 3016 | unk | unk | 20 | 3
120 | Nurse |  | 0 |  | 501 | 11 | 0 |  | 4008 | unk | unk | unk | unk
121 | Special Education |  | 0 | Yes | 531 | 12 | 12 |  | 4248 | unk | unk | 20 | 3
201 | Classroom | 320 | 21 | Yes | 989 | 22 | 22 | UV | 7912 | 2.4267 | 1 | 22.4267 | 3
202 | Classroom | 0 | 0 | Yes | 667 | 15 | 15 | UV | 5336 | 0 | 0 | 20 | 3
203 | Classroom | 418 | 27 |  | 989 | 22 | 22 | UV | 7912 | 3.1699 | 1 | 3.1699 | 1
204 | Classroom | 511 | 34 |  | 1012 | 23 | 23 | UV | 8096 | 3.7871 | 1 | 3.7871 | 1
205 | Classroom | 560 | 37 |  | 1012 | 23 | 23 | UV | 8096 | 4.1502 | 2 | 4.1502 | 2
206 | Classroom | 770 | 51 |  | 1012 | 23 | 23 | UV | 8096 | 5.7065 | 2 | 5.7065 | 2
207 | Classroom | 0 | 0 | Yes | 1012 | 23 | 23 | UV | 8096 | 0 | 0 | 20 | 3
208 | Classroom | 246 | 16 | Yes | 989 | 22 | 22 | UV | 7912 | 1.8655 | 1 | 21.8655 | 3
209 | Classroom | 446 | 29 |  | 1012 | 23 | 23 | UV | 8096 | 3.3053 | 1 | 3.3053 | 1
210A | Classroom | 233 | 15 |  | 504 | 11 | 11 | UV | 4032 | 3.4673 | 1 | 3.4673 | 1
210B | Classroom | 0 | 0 | Yes | 504 | 11 | 11 | UV | 4032 | 0 | 0 | 20 | 3
215 | Classroom | 0 | 0 | Yes | 874 | 19 | 19 | UV | 6992 | 0 | 0 | 20 | 3
216 | Classroom | 0 | 0 | Yes | 874 | 19 | 19 | UV | 6992 | 0 | 0 | 20 | 3
217 | Classroom | 220 | 14 | Yes | 874 | 19 | 19 | UV | 6992 | 1.8879 | 1 | 21.8879 | 3
218 | Classroom | 359 | 23 |  | 874 | 19 | 19 | UV | 6992 | 3.0807 | 1 | 3.0807 | 1
220 | Classroom | 232 | 15 | Yes | 1012 | 23 | 23 | UV | 8096 | 1.7194 | 1 | 21.7194 | 3
221 | Classroom | 441 | 29 |  | 1058 | 24 | 24 | UV | 8464 | 3.1262 | 1 | 3.1262 | 1
- | Principal |  | 0 | Yes | 387 | 8 | 8 |  | 3096 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 784 | 17 | 17 |  | 6272 | unk | unk | 20 | 3
- | Auditorium | 4864 | 324 |  | 5832 | 132 | 132 | AHU | 46656 | 6.2551 | 2 | 6.2551 | 2
Lamberton LSH | [9 empty] | unk | unk | unk | unk
15 | Classroom | 313 | 20 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.5296 | 1 | 22.5296 | 3
16 | Classroom | 299 | 19 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.4165 | 1 | 22.4165 | 3
17 | Classroom | 317 | 21 |  | 928 | 21 | 21 | AHU | 7424 | 2.562 | 1 | 2.562 | 1
18 | Classroom | 329 | 21 |  | 928 | 21 | 21 | AHU | 7424 | 2.6589 | 1 | 2.6589 | 1
19 | Classroom | 291 | 19 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.3518 | 1 | 22.3518 | 3
20 | Classroom | 295 | 19 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.3842 | 1 | 22.3842 | 3
21 | Classroom | 316 | 21 |  | 928 | 21 | 21 | AHU | 7424 | 2.5539 | 1 | 2.5539 | 1
22 | Classroom | 324 | 21 |  | 928 | 21 | 21 | AHU | 7424 | 2.6185 | 1 | 2.6185 | 1
23 | Classroom | 314 | 20 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.5377 | 1 | 22.5377 | 3
24 | Classroom | 327 | 21 |  | 928 | 21 | 21 | AHU | 7424 | 2.6428 | 1 | 2.6428 | 1
25 | Classroom | 287 | 19 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.3195 | 1 | 22.3195 | 3
26 | Classroom | 303 | 20 | Yes | 928 | 21 | 21 | AHU | 7424 | 2.4488 | 1 | 22.4488 | 3
- | Main Office | 4 | 0 | Yes | 300 | 6 | 6 | AHU | 2400 | 0.1 | 0 | 20.1 | 3
- | Multi Purpose | 1539 | 102 |  | 1749 | 39 | 39 | AHU | 13992 | 6.5995 | 2 | 6.5995 | 2
- | Janitor | 0 | 0 |  | 80 | 1 | 0 | AHU | 640 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-16 | [8 empty] | unk | unk | unk | unk
School: | Lankenau Environmental Science High School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
201 | Classroom | 407 | 27 |  | 585 | 13 | 13 |  | 4680 | 5.2179 | 2 | 5.2179 | 2
205 | Classroom | 242 | 16 |  | 534 | 12 | 12 |  | 4272 | 3.3989 | 1 | 3.3989 | 1
206 | Classroom | 183 | 12 |  | 529 | 12 | 12 |  | 4232 | 2.5945 | 1 | 2.5945 | 1
207 | Classroom | 182 | 12 |  | 529 | 12 | 12 |  | 4232 | 2.5803 | 1 | 2.5803 | 1
208 | Classroom | 178 | 11 |  | 522 | 11 | 11 |  | 4176 | 2.5575 | 1 | 2.5575 | 1
210 | Classroom | 117 | 7 |  | 493 | 11 | 7 |  | 3944 | 1.7799 | 1 | 1.7799 | 1
211 | Classroom | 120 | 8 |  | 475 | 10 | 8 |  | 3800 | 1.8947 | 1 | 1.8947 | 1
212 | Classroom | 63 | 4 |  | 507 | 11 | 4 |  | 4056 | 0.93195 | 0 | 0.93195 | 0
213 | Classroom | 63 | 4 |  | 531 | 12 | 4 |  | 4248 | 0.88983 | 0 | 0.88983 | 0
214 | Classroom | 67 | 4 |  | 603 | 13 | 4 |  | 4824 | 0.83333 | 0 | 0.83333 | 0
302 | Classroom | 84 | 5 |  | 586 | 13 | 5 |  | 4688 | 1.0751 | 1 | 1.0751 | 1
303 | Classroom | 87 | 5 |  | 589 | 13 | 5 |  | 4712 | 1.1078 | 1 | 1.1078 | 1
304 | Classroom | 85 | 5 |  | 573 | 13 | 5 |  | 4584 | 1.1126 | 1 | 1.1126 | 1
305 | Classroom | 73 | 4 |  | 613 | 13 | 4 |  | 4904 | 0.89315 | 0 | 0.89315 | 0
307 | Classroom | 517 | 34 |  | 1146 | 26 | 26 |  | 9168 | 3.3835 | 1 | 3.3835 | 1
308 | 308 | 412 | 27 |  | 879 | 19 | 19 |  | 7032 | 3.5154 | 1 | 3.5154 | 1
308B | 308B | 38 | 2 |  | 350 | 7 | 2 |  | 2800 | 0.81429 | 0 | 0.81429 | 0
309 | Classroom | 611 | 40 |  | 1120 | 25 | 25 |  | 8960 | 4.0915 | 2 | 4.0915 | 2
- | Auditorium storage 1 | 23 | 1 |  | 67 | 1 | 1 |  | 536 | 2.5746 | 1 | 2.5746 | 1
- | Auditorium storage 2 | 22 | 1 |  | 109 | 2 | 1 |  | 872 | 1.5138 | 1 | 1.5138 | 1
- | Botany / Storage area | 198 | 13 |  | 3264 | 74 | 13 |  | 26112 | 0.45496 | 0 | 0.45496 | 0
- | Cafeteria | 706 | 47 |  | 1326 | 30 | 30 |  | 10608 | 3.9932 | 1 | 3.9932 | 1
- | Cafeteria 2 (Small) | 158 | 10 |  | 518 | 11 | 10 |  | 4144 | 2.2876 | 1 | 2.2876 | 1
- | Cafeteria 3 (Main) | 662 | 44 |  | 1536 | 34 | 34 |  | 12288 | 3.2324 | 1 | 3.2324 | 1
- | Conference Room | 55 | 3 |  | 254 | 5 | 3 |  | 2032 | 1.624 | 1 | 1.624 | 1
- | Counselors Office | 241 | 16 |  | 700 | 15 | 15 |  | 5600 | 2.5821 | 1 | 2.5821 | 1
- | Dean's Office | 54 | 3 |  | 280 | 6 | 3 |  | 2240 | 1.4464 | 1 | 1.4464 | 1
- | Gym | 606 | 40 |  | 2089 | 47 | 40 |  | 16712 | 2.1757 | 1 | 2.1757 | 1
- | Lounge | 141 | 9 |  | 409 | 9 | 9 |  | 3272 | 2.5856 | 1 | 2.5856 | 1
- | Main Office | 166 | 11 |  | 605 | 13 | 11 |  | 4840 | 2.0579 | 1 | 2.0579 | 1
- | Music Assembly | 1020 | 68 |  | 2424 | 55 | 55 |  | 19392 | 3.1559 | 1 | 3.1559 | 1
- | Nurse's Office | 44 | 2 |  | 247 | 5 | 2 |  | 1976 | 1.336 | 1 | 1.336 | 1
- | Principal's office | 109 | 7 |  | 280 | 6 | 6 |  | 2240 | 2.9196 | 1 | 2.9196 | 1
- | Science Storage | 60 | 4 |  | 355 | 8 | 4 |  | 2840 | 1.2676 | 1 | 1.2676 | 1
202 | - |  | 0 |  | 585 | 13 | 13 |  | 4680 | unk | unk | unk | unk
203 | - |  | 0 |  | 527 | 11 | 11 |  | 4216 | unk | unk | unk | unk
204 | - |  | 0 |  | 535 | 12 | 13 |  | 4280 | unk | unk | unk | unk
209 | - |  | 0 |  | 535 | 12 | 13 |  | 4280 | unk | unk | unk | unk
- | Roster Chair |  | 0 |  | 156 | 3 | 3 |  | 1248 | unk | unk | unk | unk
306 | - |  | 0 |  | 900 | 20 | 20 |  | 7200 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | Henry W. Lawton Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 956 | 63 |  | 990 | 22 | 22 | UV | 7920 | 7.2424 | 2 | 7.2424 | 2
102 | Classroom | 407 | 27 |  | 990 | 22 | 22 | UV | 7920 | 3.0833 | 1 | 3.0833 | 1
103 | Classroom | 547 | 36 |  | 730 | 16 | 16 | UV | 5840 | 5.6199 | 2 | 5.6199 | 2
104 | Classroom | 327 | 21 |  | 796 | 18 | 18 | UV | 6368 | 3.081 | 1 | 3.081 | 1
105 | Classroom | 464 | 30 |  | 730 | 16 | 16 | UV | 5840 | 4.7671 | 2 | 4.7671 | 2
106 | Classroom | 432 | 28 |  | 796 | 18 | 18 | UV | 6368 | 4.0704 | 2 | 4.0704 | 2
107 | Classroom | 376 | 25 |  | 730 | 16 | 16 | UV | 5840 | 3.863 | 1 | 3.863 | 1
108 | Classroom | 641 | 42 |  | 676 | 15 | 15 | UV | 5408 | 7.1117 | 2 | 7.1117 | 2
109 | Classroom | 519 | 34 |  | 730 | 16 | 16 | UV | 5840 | 5.3322 | 2 | 5.3322 | 2
110 | Classroom | 699 | 46 |  | 676 | 15 | 15 | UV | 5408 | 7.7552 | 2 | 7.7552 | 2
111 | Classroom | 685 | 45 |  | 720 | 16 | 16 | UV | 5760 | 7.1354 | 2 | 7.1354 | 2
112 | Classroom | 929 | 61 |  | 930 | 21 | 21 | UV | 7440 | 7.4919 | 2 | 7.4919 | 2
113 | Classroom | 742 | 49 |  | 720 | 16 | 16 | UV | 5760 | 7.7292 | 2 | 7.7292 | 2
114 | Classroom | 705 | 47 |  | 930 | 21 | 21 | UV | 7440 | 5.6855 | 2 | 5.6855 | 2
115 | Classroom | 712 | 47 |  | 720 | 16 | 16 | UV | 5760 | 7.4167 | 2 | 7.4167 | 2
117 | Classroom | 671 | 44 |  | 720 | 16 | 16 | UV | 5760 | 6.9896 | 2 | 6.9896 | 2
119 | Classroom | 713 | 47 |  | 720 | 16 | 16 | UV | 5760 | 7.4271 | 2 | 7.4271 | 2
121 | Classroom | 571 | 38 |  | 720 | 16 | 16 | UV | 5760 | 5.9479 | 2 | 5.9479 | 2
123 | Classroom | 400 | 26 |  | 720 | 16 | 16 | UV | 5760 | 4.1667 | 2 | 4.1667 | 2
201 | Classroom | 411 | 27 |  | 816 | 18 | 18 | UV | 6528 | 3.7776 | 1 | 3.7776 | 1
202 | Classroom | 658 | 43 |  | 816 | 18 | 18 | UV | 6528 | 6.0478 | 2 | 6.0478 | 2
203 | Classroom | 455 | 30 |  | 816 | 18 | 18 | UV | 6528 | 4.182 | 2 | 4.182 | 2
204 | Classroom | 790 | 52 |  | 816 | 18 | 18 | UV | 6528 | 7.261 | 2 | 7.261 | 2
205 | Classroom | 802 | 53 |  | 816 | 18 | 18 | UV | 6528 | 7.3713 | 2 | 7.3713 | 2
206 | Classroom | 611 | 40 |  | 816 | 18 | 18 | UV | 6528 | 5.6158 | 2 | 5.6158 | 2
207 | Classroom | 814 | 54 |  | 720 | 16 | 16 | UV | 5760 | 8.4792 | 2 | 8.4792 | 2
208 | Classroom | 320 | 21 |  | 816 | 18 | 18 | UV | 6528 | 2.9412 | 1 | 2.9412 | 1
209 | Classroom | 653 | 43 |  | 720 | 16 | 16 | UV | 5760 | 6.8021 | 2 | 6.8021 | 2
211 | Classroom | 707 | 47 |  | 720 | 16 | 16 | UV | 5760 | 7.3646 | 2 | 7.3646 | 2
213 | Classroom | 649 | 43 |  | 720 | 16 | 16 | UV | 5760 | 6.7604 | 2 | 6.7604 | 2
214 | Classroom | 289 | 19 |  | 540 | 12 | 12 | UV | 4320 | 4.0139 | 2 | 4.0139 | 2
215 | Classroom | 730 | 48 |  | 720 | 16 | 16 | UV | 5760 | 7.6042 | 2 | 7.6042 | 2
216 | Classroom | 332 | 22 |  | 768 | 17 | 17 | UV | 6144 | 3.2422 | 1 | 3.2422 | 1
217 | Classroom | 364 | 24 |  | 720 | 16 | 16 | UV | 5760 | 3.7917 | 1 | 3.7917 | 1
218 | Classroom | 716 | 47 |  | 676 | 15 | 15 | UV | 5408 | 7.9438 | 2 | 7.9438 | 2
219 | Classroom | 672 | 44 |  | 720 | 16 | 16 | UV | 5760 | 7 | 2 | 7 | 2
220 | Classroom | 639 | 42 |  | 676 | 15 | 15 | UV | 5408 | 7.0895 | 2 | 7.0895 | 2
222 | Classroom | 683 | 45 |  | 540 | 12 | 12 | UV | 4320 | 9.4861 | 2 | 9.4861 | 2
224 | Classroom | 633 | 42 |  | 720 | 16 | 16 | UV | 5760 | 6.5938 | 2 | 6.5938 | 2
226 | Classroom | 1102 | 73 |  | 540 | 12 | 12 | UV | 4320 | 15.3056 | 3 | 15.3056 | 3
- | Art (Large) | 477 | 31 |  | 1258 | 28 | 28 | UV | 10064 | 2.8438 | 1 | 2.8438 | 1
- | Cafeteria | 632 | 42 |  | 2310 | 52 | 42 | AHU | 18480 | 2.0519 | 1 | 2.0519 | 1
- | Computer | 886 | 59 |  | 1440 | 32 | 32 | UV | 11520 | 4.6146 | 2 | 4.6146 | 2
- | IMC | 426 | 28 |  | 2620 | 59 | 28 | UV | 20960 | 1.2195 | 1 | 1.2195 | 1
- | Main Office | 232 | 15 |  | 275 | 6 | 6 | UV | 2200 | 6.3273 | 2 | 6.3273 | 2
- | Nurse's Office | 283 | 18 |  | 363 | 8 | 8 | UV | 2904 | 5.8471 | 2 | 5.8471 | 2
- | Science (Large) | 375 | 25 |  | 1088 | 24 | 24 | UV | 8704 | 2.585 | 1 | 2.585 | 1
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | Henry C. Lea Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Chadwick | Devine Part 2 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
L1 | Classroom | 166 | 11 |  | 696 | 15 | 11 | UV | 5568 | 1.7888 | 1 | 1.7888 | 1
L3 | Classroom | 0 | 0 |  | 624 | 14 | 0 | UV | 4992 | 0 | 0 | 0 | 0
L4 | Classroom | 191 | 12 |  | 696 | 15 | 12 | UV | 5568 | 2.0582 | 1 | 2.0582 | 1
L5 | Classroom | 208 | 13 |  | 864 | 19 | 13 | UV | 6912 | 1.8056 | 1 | 1.8056 | 1
L7 | Classroom | 247 | 16 |  | 768 | 17 | 16 | UV | 6144 | 2.4121 | 1 | 2.4121 | 1
B2 | Classroom |  | 0 | Yes | 1457 | 33 | 33 |  | 11656 | unk | unk | 20 | 3
101 | Classroom | 312 | 20 |  | 1225 | 27 | 20 | UV | 9800 | 1.9102 | 1 | 1.9102 | 1
102 | Classroom | 319 | 21 |  | 1295 | 29 | 21 | UV | 10360 | 1.8475 | 1 | 1.8475 | 1
103 | Classroom | 284 | 18 |  | 810 | 18 | 18 | AHU | 6480 | 2.6296 | 1 | 2.6296 | 1
105 | Classroom | 287 | 19 |  | 840 | 19 | 19 | AHU | 6720 | 2.5625 | 1 | 2.5625 | 1
106 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
107 | Classroom | 289 | 19 |  | 840 | 19 | 19 | AHU | 6720 | 2.5804 | 1 | 2.5804 | 1
108 | Classroom | 301 | 20 |  | 840 | 19 | 19 | AHU | 6720 | 2.6875 | 1 | 2.6875 | 1
109 | Classroom | 295 | 19 |  | 840 | 19 | 19 | AHU | 6720 | 2.6339 | 1 | 2.6339 | 1
110 | Classroom | 298 | 19 |  | 840 | 19 | 19 | AHU | 6720 | 2.6607 | 1 | 2.6607 | 1
111 | Classroom | 289 | 19 |  | 840 | 19 | 19 | AHU | 6720 | 2.5804 | 1 | 2.5804 | 1
125 | Counselor's Office |  | 0 | Yes | 126 | 2 | 2 |  | 1008 | unk | unk | 20 | 3
127 | Classroom |  | 0 | Yes | 126 | 2 | 2 |  | 1008 | unk | unk | 20 | 3
201 | Classroom | 0 | 0 | Yes | 1015 | 23 | 23 | UV | 8120 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 | Yes | 980 | 22 | 22 | UV | 7840 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | unk | unk | 20 | 3
204 | Classroom |  | 0 | Yes | 840 | 19 | 19 |  | 6720 | unk | unk | 20 | 3
204a | Classroom | 0 | 0 | Yes | 252 | 5 | 5 | AHU | 2016 | 0 | 0 | 20 | 3
205 | Classroom | 0 | 0 | Yes | 810 | 18 | 18 | AHU | 6480 | 0 | 0 | 20 | 3
206 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | AHU | 6960 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
210 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
211 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
212 | Classroom | 0 | 0 | Yes | 212 | 4 | 4 | AHU | 1696 | 0 | 0 | 20 | 3
301/302 | Library | 380 | 25 | Yes | 5400 | 122 | 122 | UV | 43200 | 0.52778 | 0 | 20.5278 | 3
303 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
304 | Classroom | 0 | 0 | Yes | 690 | 15 | 15 | AHU | 5520 | 0 | 0 | 20 | 3
304A | Room |  | 0 | Yes | 266 | 6 | 6 |  | 2128 | unk | unk | 20 | 3
306 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
308 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
310 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
311 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
312 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | AHU | 6720 | 0 | 0 | 20 | 3
313 | Classroom | 0 | 0 |  | 840 | 19 | 0 | AHU | 6720 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 |  | 2296 | 52 | 0 | AHU | 18368 | 0 | 0 | 0 | 0
- | Side Cafeteria | 490 | 32 | Yes | 1800 | 40 | 40 | AHU | 14400 | 2.0417 | 1 | 22.0417 | 3
- | Front Cafeteria | 352 | 23 | Yes | 1560 | 35 | 35 | AHU | 12480 | 1.6923 | 1 | 21.6923 | 3
- | Computer Lab | 276 | 18 |  | 1456 | 33 | 18 | AHU | 11648 | 1.4217 | 1 | 1.4217 | 1
- | Corridor | 156 | 10 |  | 650 | 14 | 10 | UV | 5200 | 1.8 | 1 | 1.8 | 1
- | Gym | 0 | 0 | Yes | 3950 | 89 | 89 | AHU | 31600 | 0 | 0 | 20 | 3
- | Main Office | 212 | 14 |  | 460 | 10 | 10 | AHU | 3680 | 3.4565 | 1 | 3.4565 | 1
- | Nurse's Bathroom | 0 | 0 |  | 28 | 0 | 0 | AHU | 224 | 0 | 0 | 0 | 0
- | Nurse's Office |  | 0 | Yes | 168 | 3 | 3 | AHU | 1344 | unk | unk | 20 | 3
- | Nurse's Exam Room |  | 0 |  | 88 | 2 | 0 | AHU | 704 | unk | unk | unk | unk
- | Office Bathroom | 0 | 0 |  | 25 | 0 | 0 | AHU | 200 | 0 | 0 | 0 | 0
- | Principal's Office | 0 | 0 | Yes | 160 | 3 | 3 | UV | 1280 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-22 | [8 empty] | unk | unk | unk | unk
School: | Amy Northwest @ Levering Middle School | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom |  | 0 |  | 750 | 17 | 0 |  | 6000 | unk | unk | unk | unk
103 | Classroom |  | 0 | Yes | 725 | 16 | 16 |  | 5800 | unk | unk | 20 | 3
106 | Nurse Office |  | 0 | Yes | 668 | 15 | 15 |  | 5344 | unk | unk | 20 | 3
107 | Classroom |  | 0 |  | 666 | 15 | 0 |  | 5328 | unk | unk | unk | unk
109 | IMC |  | 0 | Yes | 1457 | 33 | 33 |  | 11656 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 675 | 15 | 15 |  | 5400 | unk | unk | 20 | 3
204 | Classroom |  | 0 | Yes | 683 | 15 | 15 |  | 5464 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 663 | 15 | 15 |  | 5304 | unk | unk | 20 | 3
206 | Classroom |  | 0 |  | 691 | 15 | 0 |  | 5528 | unk | unk | unk | unk
207 | Classroom |  | 0 |  | 672 | 15 | 0 |  | 5376 | unk | unk | unk | unk
209 | Classroom |  | 0 | Yes | 685 | 15 | 15 |  | 5480 | unk | unk | 20 | 3
210 | Classroom |  | 0 |  | 677 | 15 | 0 |  | 5416 | unk | unk | unk | unk
303/304 | Classroom |  | 0 | Yes | 1253 | 28 | 28 |  | 10024 | unk | unk | 20 | 3
305 | Classroom |  | 0 | Yes | 675 | 15 | 15 |  | 5400 | unk | unk | 20 | 3
306 | Classroom |  | 0 | Yes | 692 | 15 | 15 |  | 5536 | unk | unk | 20 | 3
307 | Classroom |  | 0 | Yes | 670 | 15 | 15 |  | 5360 | unk | unk | 20 | 3
310 | Classroom |  | 0 |  | 1065 | 24 | 0 |  | 8520 | unk | unk | unk | unk
Annex 1 | Classroom |  | 0 | Yes | 733 | 16 | 16 |  | 5864 | unk | unk | 20 | 3
Annex 2 | Classroom |  | 0 | Yes | 709 | 16 | 16 |  | 5672 | unk | unk | 20 | 3
Annex 3 | Classroom |  | 0 |  | 730 | 16 | 0 |  | 5840 | unk | unk | unk | unk
Annex 4 | Classroom |  | 0 | Yes | 707 | 16 | 16 |  | 5656 | unk | unk | 20 | 3
Annex 5 | Classroom |  | 0 | Yes | 723 | 16 | 16 |  | 5784 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-01 | [8 empty] | unk | unk | unk | unk
School: | Abraham Lincoln High School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | EMCOR Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
2 | Room 2 Office | 93 | 6 |  | 576 | 13 | 6 | AHU #7 | 4608 | 1.2109 | 1 | 1.2109 | 1
3 | Room 3 Storage | 99 | 6 |  | 576 | 13 | 6 | AHU #8 | 4608 | 1.2891 | 1 | 1.2891 | 1
4 | Room 4 Electrical | 103 | 6 |  | 576 | 13 | 6 | AHU #9 | 4608 | 1.3411 | 1 | 1.3411 | 1
5 | Room 5 Kitchen | 461 | 30 |  | 576 | 13 | 13 | AHU #10 | 4608 | 6.0026 | 2 | 6.0026 | 2
6 | Child Care | 1116 | 74 |  | 576 | 13 | 13 | AHU #11 | 4608 | 14.5312 | 3 | 14.5312 | 3
8 | Child Care | 2029 | 135 |  | 1665 | 37 | 37 | AHU #12 | 13320 | 9.1396 | 2 | 9.1396 | 2
100 | Classroom | 760 | 50 |  | 363 | 8 | 8 | UV1+UV2+AHU-2 | 2904 | 15.7025 | 3 | 15.7025 | 3
100A | Classroom | 615 | 41 |  |  | 0 | 0 | UV+AHU-2 |  | unk | unk | unk | unk
101 | Classroom | 1715 | 114 |  | 1247 | 28 | 28 | UV1+UV2+AHU-2 | 9976 | 10.3148 | 3 | 10.3148 | 3
102 | Classroom | 1244 | 82 |  | 130 | 2 | 2 | UV+AHU-2 | 1040 | 71.7692 | 5 | 71.7692 | 5
102A | Office | 25 | 1 |  | 140 | 3 | 1 | AHU-2 | 1120 | 1.3393 | 1 | 1.3393 | 1
102B | Office | 35 | 2 |  | 107 | 2 | 2 | AHU-2 | 856 | 2.4533 | 1 | 2.4533 | 1
103 | Classroom | 1636 | 109 |  | 1410 | 32 | 32 | UV1+UV2+AHU-2 | 11280 | 8.7021 | 2 | 8.7021 | 2
104 | Classroom | 1067 | 71 |  | 806 | 18 | 18 | UV1+UV2+AHU-2 | 6448 | 9.9287 | 2 | 9.9287 | 2
105 | Classroom | 1322 | 88 |  | 1140 | 25 | 25 | UV1+UV2+AHU-2 | 9120 | 8.6974 | 2 | 8.6974 | 2
106 | Classroom | 1182 | 78 |  | 957 | 21 | 21 | UV1+UV2+AHU-2 | 7656 | 9.2633 | 2 | 9.2633 | 2
107 | Classroom | 1894 | 126 |  | 1426 | 32 | 32 | UV1+UV2+AHU-2 | 11408 | 9.9614 | 2 | 9.9614 | 2
107A | Storage Room | 300 | 20 |  |  | 0 | 0 | AHU-1 |  | unk | unk | unk | unk
108 | Classroom | 1212 | 80 |  | 899 | 20 | 20 | UV1+UV2+AHU-2 | 7192 | 10.1112 | 3 | 10.1112 | 3
109 | 109 OFFICE | 144 | 9 |  | 99 | 2 | 2 | AHU-2 / FC | 792 | 10.9091 | 3 | 10.9091 | 3
110 | Classroom | 1159 | 77 |  | 868 | 19 | 19 | UV1+UV2+AHU-1 | 6944 | 10.0144 | 3 | 10.0144 | 3
111 | Classroom | 1827 | 121 |  | 1426 | 32 | 32 | UV1+UV2+AHU-1 | 11408 | 9.609 | 2 | 9.609 | 2
112 | Classroom | 990 | 66 |  | 868 | 19 | 19 | UV1+UV2+AHU-1 | 6944 | 8.5541 | 2 | 8.5541 | 2
114 | Classroom | 1114 | 74 |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 6696 | 9.9821 | 2 | 9.9821 | 2
116 | Classroom | 663 | 44 |  | 896 | 20 | 20 | UV1+UV2+AHU-1 | 7168 | 5.5497 | 2 | 5.5497 | 2
118 | Classroom | 932 | 62 |  | 1748 | 39 | 39 | UV1+UV2+AHU-1 | 13984 | 3.9989 | 1 | 3.9989 | 1
120 | Classroom | 1141 | 76 |  | 864 | 19 | 19 | UV1+UV2+AHU-1 | 6912 | 9.9045 | 2 | 9.9045 | 2
121 | Classroom | 1025 | 68 |  | 945 | 21 | 21 | UV1+UV2+AHU-1 | 7560 | 8.1349 | 2 | 8.1349 | 2
122 | Classroom | 941 | 62 |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 6696 | 8.4319 | 2 | 8.4319 | 2
123 | Classroom | 1848 | 123 |  | 2208 | 50 | 50 | UV1+UV2+UV1+UV2+AHU-1 | 17664 | 6.2772 | 2 | 6.2772 | 2
124 | Classroom | 865 | 57 |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 6696 | 7.7509 | 2 | 7.7509 | 2
125 | Classroom | 984 | 65 |  | 888 | 20 | 20 | UV1+UV2+AHU-1 | 7104 | 8.3108 | 2 | 8.3108 | 2
126 | Classroom | 843 | 56 |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 6696 | 7.5538 | 2 | 7.5538 | 2
128 | Classroom | 598 | 39 |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 6696 | 5.3584 | 2 | 5.3584 | 2
129 | Classroom | 740 | 49 |  | 890 | 20 | 20 | UV1+UV2+AHU-1 | 7120 | 6.236 | 2 | 6.236 | 2
130 | Security | 0 | 0 |  | 108 | 2 | 0 | AHU-4 | 864 | 0 | 0 | 0 | 0
131 | Police | 0 | 0 |  | 180 | 4 | 0 | AHU-4 | 1440 | 0 | 0 | 0 | 0
132 | Classroom | 728 | 48 |  |  | 0 | 0 | UV1+UV2+UV3+UV4 |  | unk | unk | unk | unk
133a | book room | 0 | 0 |  |  | 0 | 0 | AHU-4 |  | unk | unk | unk | unk
135 | Classroom | 0 | 0 |  | 840 | 19 | 0 | UV1+UV2 | 6720 | 0 | 0 | 0 | 0
136 | office | 0 | 0 |  | 140 | 3 | 0 | AHU-4 | 1120 | 0 | 0 | 0 | 0
136a | storage | 0 | 0 |  |  | 0 | 0 | AHU-4 |  | unk | unk | unk | unk
137 | storage | 0 | 0 |  |  | 0 | 0 | AHU-4 |  | unk | unk | unk | unk
137a | storage | 0 | 0 |  |  | 0 | 0 | AHU-4 |  | unk | unk | unk | unk
139 | office | 0 | 0 |  | 74.75 | 1 | 0 | AHU-4 | 598 | 0 | 0 | 0 | 0
140 | Main Office and waiting | 0 | 0 |  | 338 | 7 | 0 | AHU-4 | 2704 | 0 | 0 | 0 | 0
141 | Office | 0 | 0 |  |  | 0 | 0 | AHU-4 |  | unk | unk | unk | unk
142 | Office | 0 | 0 |  |  | 0 | 0 | AHU-4 |  | unk | unk | unk | unk
143 | Office | 0 | 0 |  | 99 | 2 | 0 | AHU-4 | 792 | 0 | 0 | 0 | 0
144 | Office | 0 | 0 |  | 105 | 2 | 0 | AHU-4 | 840 | 0 | 0 | 0 | 0
145 | Office | 0 | 0 |  | 110 | 2 | 0 | AHU-4 | 880 | 0 | 0 | 0 | 0
146 | Work Room | 0 | 0 |  | 636 | 14 | 0 | AHU-4 | 5088 | 0 | 0 | 0 | 0
147 | Conference | 0 | 0 |  | 192 | 4 | 0 | AHU-4 | 1536 | 0 | 0 | 0 | 0
147A | records | 0 | 0 |  | 300 | 6 | 0 | AHU-4 | 2400 | 0 | 0 | 0 | 0
149 | Health Suite | 0 | 0 |  | 495 | 11 | 0 | AHU-4 | 3960 | 0 | 0 | 0 | 0
149a | Exam | 0 | 0 |  | 188 | 4 | 0 | AHU-4 | 1504 | 0 | 0 | 0 | 0
149b | Exam | 0 | 0 |  | 197 | 4 | 0 | AHU-4 | 1576 | 0 | 0 | 0 | 0
149c | Office | 0 | 0 |  | 197 | 4 | 0 | AHU-4 | 1576 | 0 | 0 | 0 | 0
149D | Office | 0 | 0 |  | 109 | 2 | 0 | AHU-4 | 872 | 0 | 0 | 0 | 0
149E | Meditation | 0 | 0 |  | 209 | 4 | 0 | AHU-4 | 1672 | 0 | 0 | 0 | 0
150 | office | 0 | 0 |  | 117 | 2 | 0 | AHU-4 | 936 | 0 | 0 | 0 | 0
151 | copy center | 0 | 0 |  | 418 | 9 | 0 | AHU-4 | 3344 | 0 | 0 | 0 | 0
154 | office | 0 | 0 |  | 117 | 2 | 0 | AHU-4 | 936 | 0 | 0 | 0 | 0
155 | office | 0 | 0 |  | 121 | 2 | 0 | AHU-4 | 968 | 0 | 0 | 0 | 0
156 | work room | 0 | 0 |  | 875 | 19 | 0 | AHU-4 | 7000 | 0 | 0 | 0 | 0
157 | Records | 0 | 0 |  | 96 | 2 | 0 | AHU-4 | 768 | 0 | 0 | 0 | 0
158 | Roster Room | 0 | 0 |  | 143 | 3 | 0 | AHU-4 | 1144 | 0 | 0 | 0 | 0
159 | Office | 0 | 0 |  | 96 | 2 | 0 | AHU-4 | 768 | 0 | 0 | 0 | 0
160 | Classroom | 1346 | 89 |  | 1428 | 32 | 32 | UV1+UV2+AHU-3 | 11424 | 7.0693 | 2 | 7.0693 | 2
160's | Men's Staff Restroom | 740 | 49 |  |  | 0 | 0 | AHU-3 |  | unk | unk | unk | unk
160's | Women's Staff Restroom | 685 | 45 |  |  | 0 | 0 | AHU-3 |  | unk | unk | unk | unk
160A | Science Prep | 423 | 28 |  | 891 | 20 | 20 | AHU-3 | 7128 | 3.5606 | 1 | 3.5606 | 1
161 | Classroom | 829 | 55 |  | 891 | 20 | 20 | UV1+UV2+AHU-3 | 7128 | 6.9781 | 2 | 6.9781 | 2
162 | Classroom | 1327 | 88 |  | 688 | 15 | 15 | UV1+UV2+AHU-3 | 5504 | 14.4658 | 3 | 14.4658 | 3
163 | Classroom | 895 | 59 |  | 868 | 19 | 19 | UV1+UV2+AHU-3 | 6944 | 7.7333 | 2 | 7.7333 | 2
164 | Classroom | 1334 | 88 |  | 1419 | 32 | 32 | UV1+UV2+AHU-3 | 11352 | 7.0507 | 2 | 7.0507 | 2
164a | Science Prep | 44 | 2 |  |  | 0 | 0 | AHU-3 |  | unk | unk | unk | unk
165 | Classroom | 942 | 62 |  | 868 | 19 | 19 | UV1+UV2+AHU-3 | 6944 | 8.1394 | 2 | 8.1394 | 2
166 | Classroom | 1071 | 71 |  | 1155 | 26 | 26 | UV1+UV2+AHU-3 | 9240 | 6.9545 | 2 | 6.9545 | 2
167 | Classroom | 458 | 30 |  | 918 | 20 | 20 | UV1+UV2+AHU-3 | 7344 | 3.7418 | 1 | 3.7418 | 1
168 | Classroom | 1150 | 76 |  | 868 | 19 | 19 | UV1+UV2+AHU-3 | 6944 | 9.9366 | 2 | 9.9366 | 2
169 | Classroom | 684 | 45 |  | 952 | 21 | 21 | UV1+UV2+AHU-3 | 7616 | 5.3887 | 2 | 5.3887 | 2
170 | Classroom | 787 | 52 |  | 891 | 20 | 20 | UV+UV+AHU-3 | 7128 | 6.6246 | 2 | 6.6246 | 2
171 | Classroom | 1006 | 67 |  | 918 | 20 | 20 | UV1+UV2+AHU-3 | 7344 | 8.219 | 2 | 8.219 | 2
172 | Classroom | 994 | 66 |  | 891 | 20 | 20 | UV1+UV2+AHU-3 | 7128 | 8.367 | 2 | 8.367 | 2
173 | Classroom | 565 | 37 |  | 891 | 20 | 20 | AHU-3 | 7128 | 4.7559 | 2 | 4.7559 | 2
174 | Classroom | 736 | 49 |  | 896 | 20 | 20 | UV1+UV2+AHU-3 | 7168 | 6.1607 | 2 | 6.1607 | 2
175 | Classroom | 1415 | 94 |  | 891 | 20 | 20 | UV1+UV2+AHU-3 | 7128 | 11.9108 | 3 | 11.9108 | 3
176 | Classroom | 903 | 60 |  | 800 | 18 | 18 | UV1+UV2+AHU-3 | 6400 | 8.4656 | 2 | 8.4656 | 2
177 | Classroom | 867 | 57 |  | 918 | 20 | 20 | UV1+UV2+AHU-3 | 7344 | 7.0833 | 2 | 7.0833 | 2
190 | Music Classroom | 1656 | 110 |  | 1395 | 31 | 31 | AHU-8 | 11160 | 8.9032 | 2 | 8.9032 | 2
190 | Office | 82 | 5 |  | 225 | 5 | 5 | AHU-8 | 1800 | 2.7333 | 1 | 2.7333 | 1
190 | Storage | 52 | 3 |  | 1716 | 39 | 3 | AHU-8 | 13728 | 0.22727 | 0 | 0.22727 | 0
190A | Classroom | 315 | 21 |  | 90 | 2 | 2 | AHU-8 | 720 | 26.25 | 4 | 26.25 | 4
190D | Classroom | 166 | 11 |  | 623 | 14 | 11 | AHU-8 | 4984 | 1.9984 | 1 | 1.9984 | 1
190E | Classroom | 191 | 12 |  | 336 | 7 | 7 | AHU-8 | 2688 | 4.2634 | 2 | 4.2634 | 2
191 | Music Classroom | 1393 | 92 |  | 2100 | 47 | 47 | AHU-8 | 16800 | 4.975 | 2 | 4.975 | 2
191A | Classroom | 68 | 4 |  | 56 | 1 | 1 | AHU-8 | 448 | 9.1071 | 2 | 9.1071 | 2
191B | Classroom | 72 | 4 |  | 90 | 2 | 2 | AHU-8 | 720 | 6 | 2 | 6 | 2
191C | Classroom | 83 | 5 |  | 90 | 2 | 2 | AHU-8 | 720 | 6.9167 | 2 | 6.9167 | 2
192 | Classroom | 998 | 66 |  | 1189 | 27 | 27 | AHU-8 | 9512 | 6.2952 | 2 | 6.2952 | 2
200 | Classroom | 1117 | 74 |  | 1240 | 28 | 28 | UV1+UV2+AHU-2 | 9920 | 6.756 | 2 | 6.756 | 2
201 | Classroom | 1325 | 88 |  | 1485 | 33 | 33 | UV1+UV2+AHU-2 | 11880 | 6.6919 | 2 | 6.6919 | 2
201A | Science Prep | 255 | 17 |  | 1486 | 33 | 17 | AHU-2 | 11888 | 1.287 | 1 | 1.287 | 1
202 | Classroom | 1325 | 88 |  | 2270 | 51 | 51 | UV1+UV2+UV3+AHU-2 | 18160 | 4.3778 | 2 | 4.3778 | 2
202A | Office | 44 | 2 |  | 99 | 2 | 2 | AHU-2 | 792 | 3.3333 | 1 | 3.3333 | 1
203 | Classroom | 1339 | 89 |  | 1575 | 35 | 35 | UV1+UV2+AHU-2 | 12600 | 6.3762 | 2 | 6.3762 | 2
204 | Classroom | 403 | 26 |  | 806 | 18 | 18 | UV1+UV2+AHU-2 | 6448 | 3.75 | 1 | 3.75 | 1
205 | Classroom | 652 | 43 |  | 1395 | 31 | 31 | UV1+UV2+AHU-2 | 11160 | 3.5054 | 1 | 3.5054 | 1
206 | Office Suite toilet |  | 0 |  | 1254 | 28 | 0 | AHU-2 | 10032 | unk | unk | unk | unk
207 | Classroom | 1006 | 67 |  | 891 | 20 | 20 | UV1+UV2+AHU-2 | 7128 | 8.468 | 2 | 8.468 | 2
208 | Classroom | 759 | 50 |  | 1152 | 26 | 26 | UV1+UV2+AHU-2 | 9216 | 4.9414 | 2 | 4.9414 | 2
209 | Classroom | 419 | 27 |  | 864 | 19 | 19 | UV1+UV2+AHU-2 | 6912 | 3.6372 | 1 | 3.6372 | 1
210 | Classroom | 614 | 40 |  | 837 | 19 | 19 | UV1+UV2+AHU-2 | 6696 | 5.5018 | 2 | 5.5018 | 2
211 | Classroom | 994 | 66 |  | 390 | 8 | 8 | UV1+UV2+AHU-1 | 3120 | 19.1154 | 3 | 19.1154 | 3
212 | Classroom | 615 | 41 |  | 858 | 19 | 19 | UV1+UV2+AHU-2 | 6864 | 5.3759 | 2 | 5.3759 | 2
213 | Classroom | 995 | 66 |  | 891 | 20 | 20 | UV1+UV2+AHU-1 | 7128 | 8.3754 | 2 | 8.3754 | 2
214 | Classroom | 625 | 41 |  | 924 | 21 | 21 | UV1+UV2+AHU-1 | 7392 | 5.0731 | 2 | 5.0731 | 2
216 | Classroom | 564 | 37 |  | 918 | 20 | 20 | UV1+UV2+AHU-1 | 7344 | 4.6078 | 2 | 4.6078 | 2
218 | Classroom | 729 | 48 |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 6696 | 6.5323 | 2 | 6.5323 | 2
220 | Classroom | 1242 | 82 |  | 1395 | 31 | 31 | UV1+UV2+AHU-1 | 11160 | 6.6774 | 2 | 6.6774 | 2
221 | Classroom | 653 | 43 |  | 924 | 21 | 21 | UV1+UV2+AHU-1 | 7392 | 5.3003 | 2 | 5.3003 | 2
222 | Classroom | 909 | 60 |  | 891 | 20 | 20 | UV1+UV2+AHU-1 | 7128 | 7.6515 | 2 | 7.6515 | 2
223 | Classroom | 848 | 56 |  | 864 | 19 | 19 | UV1+UV2+AHU-1 | 6912 | 7.3611 | 2 | 7.3611 | 2
224 | Classroom | 2035 | 135 |  | 1972 | 44 | 44 | UV1+UV2+UV3+UV4+AHU-1 | 15776 | 7.7396 | 2 | 7.7396 | 2
224A | Office | 96 | 6 |  | 121 | 2 | 2 | AHU-1 | 968 | 5.9504 | 2 | 5.9504 | 2
225 | Classroom | 639 | 42 |  | 918 | 20 | 20 | UV1+UV2+AHU-1 | 7344 | 5.2206 | 2 | 5.2206 | 2
226 | Classroom | 1282 | 85 |  | 1870 | 42 | 42 | UV1+UV2+UV3+UV4+AHU-1 | 14960 | 5.1417 | 2 | 5.1417 | 2
226A | Office | 41 | 2 |  | 123 | 2 | 2 | AHU-1 | 984 | 2.5 | 1 | 2.5 | 1
227 | Classroom | 825 | 55 |  | 891 | 20 | 20 | UV1+UV2+AHU-1 | 7128 | 6.9444 | 2 | 6.9444 | 2
228 | Classroom | 551 | 36 |  | 924 | 21 | 21 | UV1+UV2+AHU-1 | 7392 | 4.4724 | 2 | 4.4724 | 2
229 | Classroom | 800 | 53 |  | 878 | 19 | 19 | UV1+UV2+AHU-1 | 7024 | 6.8337 | 2 | 6.8337 | 2
- | 2nd floor Corridor | 1498 | 99 |  |  | 0 | 0 | AHU-1 |  | unk | unk | unk | unk
- | Gym | 40145 | 2676 |  | 18327 | 416 | 416 | AHU-9+AHU-10 | 146616 | 16.4286 | 3 | 16.4286 | 3
- | 2nd Floor B Corridor | 543 | 36 |  |  | 0 | 0 | AHU-2 |  | unk | unk | unk | unk
- | 2nd Floor Staff toilet |  | 0 |  |  | 0 | 0 | AHU-2 |  | unk | unk | unk | unk
- | Auditorium | 16961 | 1130 |  | 6745 | 153 | 153 | AHU-6 | 53960 | 18.8595 | 3 | 18.8595 | 3
- | Small Gym | 0 | 0 |  | 6438 | 146 | 0 | AHU-11 | 51504 | 0 | 0 | 0 | 0
- | Weight Room | 0 | 0 |  | 2450 | 55 | 0 | AHU-12 | 19600 | 0 | 0 | 0 | 0
- | Counselor Center | 0 | 0 |  |  | 0 | 0 | AHU-4 |  | unk | unk | unk | unk
- | Child Care- Hallway | 240 | 16 |  |  | 0 | 0 | AHU #13 |  | unk | unk | unk | unk
- | Child Care- Kitchen | 47 | 3 |  | 330 | 7 | 3 | AHU-7 | 2640 | 1.0682 | 1 | 1.0682 | 1
- | Child Care- Lending Library | 96 | 6 | Yes | 1184 | 26 | 26 | AHU-7 | 9472 | 0.60811 | 0 | 20.6081 | 3
- | Library/IMC | 1522 | 101 |  | 8640 | 196 | 101 | AHU #14 | 69120 | 1.3212 | 1 | 1.3212 | 1
- | Child Care Office | 9 | 0 |  | 99 | 2 | 0 | AHU-7 | 792 | 0.68182 | 0 | 0.68182 | 0
- | Admin 140's Area Corridor | 0 | 0 |  | 375 | 8 | 0 | AHU-4 | 3000 | 0 | 0 | 0 | 0
- | Gym Office |  | 0 |  | 343 | 7 | 0 |  | 2744 | unk | unk | unk | unk
- | Gym office 2 |  | 0 |  | 280 | 6 | 0 |  | 2240 | unk | unk | unk | unk
- | Gym office 3 |  | 0 |  | 260 | 5 | 0 |  | 2080 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-12 | [8 empty] | unk | unk | unk | unk
School: | Lingelbach Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Part 2 | Part 3 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 227 | 15 |  | 968 | 22 | 15 | UV | 7744 | 1.7588 | 1 | 1.7588 | 1
102 | Classroom | 477 | 31 |  | 968 | 22 | 22 | UV | 7744 | 3.6958 | 1 | 3.6958 | 1
103 | Classroom | 219 | 14 |  | 889 | 20 | 14 | UV | 7112 | 1.8476 | 1 | 1.8476 | 1
104 | Classroom | 0 | 0 |  | 963 | 21 | 0 | UV | 7704 | 0 | 0 | 0 | 0
105 | Classroom | 268 | 17 |  | 941 | 21 | 17 | UV | 7528 | 2.136 | 1 | 2.136 | 1
106 | Classroom | 293 | 19 |  | 971 | 22 | 19 | UV | 7768 | 2.2631 | 1 | 2.2631 | 1
200 | Classroom | 444 | 29 |  | 1394 | 31 | 29 | UV | 11152 | 2.3888 | 1 | 2.3888 | 1
200A | Classroom | 675 | 45 |  | 1235 | 28 | 28 | UV | 9880 | 4.0992 | 2 | 4.0992 | 2
201 | Classroom | 514 | 34 |  | 969 | 22 | 22 | UV | 7752 | 3.9783 | 1 | 3.9783 | 1
202 | Classroom | 280 | 18 |  | 969 | 22 | 18 | UV | 7752 | 2.1672 | 1 | 2.1672 | 1
203 | Classroom | 278 | 18 |  | 971 | 22 | 18 | UV | 7768 | 2.1473 | 1 | 2.1473 | 1
204 | Classroom | 290 | 19 |  | 971 | 22 | 19 | UV | 7768 | 2.24 | 1 | 2.24 | 1
205 | Classroom | 336 | 22 |  | 955 | 21 | 21 | UV | 7640 | 2.6387 | 1 | 2.6387 | 1
206 | Classroom | 278 | 18 |  | 969 | 22 | 18 | UV | 7752 | 2.1517 | 1 | 2.1517 | 1
301 | Classroom | 285 | 19 |  | 940 | 21 | 19 | UV | 7520 | 2.2739 | 1 | 2.2739 | 1
302 | Classroom | 795 | 53 |  | 937 | 21 | 21 | UV | 7496 | 6.3634 | 2 | 6.3634 | 2
303 | Classroom | 837 | 55 |  | 933 | 21 | 21 | UV | 7464 | 6.7283 | 2 | 6.7283 | 2
303A | Classroom | 357 | 23 |  | 463 | 10 | 10 | UV | 3704 | 5.7829 | 2 | 5.7829 | 2
304 | Classroom | 406 | 27 |  | 464 | 10 | 10 | UV | 3712 | 6.5625 | 2 | 6.5625 | 2
305 | Classroom | 395 | 26 |  | 967 | 21 | 21 | UV | 7736 | 3.0636 | 1 | 3.0636 | 1
306 | Classroom | 906 | 60 |  | 944 | 21 | 21 | UV | 7552 | 7.1981 | 2 | 7.1981 | 2
- | Main Office |  | 0 | Yes | 332 | 7 | 7 |  | 2656 | unk | unk | 20 | 3
- | Principals Office |  | 0 | Yes | 262 | 5 | 5 |  | 2096 | unk | unk | 20 | 3
- | Nurses Office |  | 0 | Yes | 269 | 6 | 6 |  | 2152 | unk | unk | 20 | 3
- | Auditorium | 841 | 56 |  | 2847 | 64 | 56 | AHU | 22776 | 2.2155 | 1 | 2.2155 | 1
- | Gym/Cafeteria | 1451 | 96 |  | 2340 | 53 | 53 | AHU | 18720 | 4.6506 | 2 | 4.6506 | 2
- | North Stairwell | 0 | 0 |  | 168 | 3 | 0 | UV | 1344 | 0 | 0 | 0 | 0
- | South Stairwell | 0 | 0 |  | 168 | 3 | 0 | UV | 1344 | 0 | 0 | 0 | 0
- | Library | 855 | 57 |  | 2312 | 52 | 52 | UV | 18496 | 2.7736 | 1 | 2.7736 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-05 | [8 empty] | unk | unk | unk | unk
School: | Alain Locke Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Brothers Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Auditorium | 2700 | 180 |  | 3658 | 83 | 83 | AHU | 29264 | 5.5358 | 2 | 5.5358 | 2
- | Gym/Cafeteria | 2014 | 134 |  | 4464 | 101 | 101 | AHU | 35712 | 3.3837 | 1 | 3.3837 | 1
- | Library | 585 | 39 |  | 1352 | 30 | 30 | UV | 10816 | 3.2452 | 1 | 3.2452 | 1
- | Main Office | 425 | 28 |  | 1213 | 27 | 27 | UV | 9704 | 2.6278 | 1 | 2.6278 | 1
- | Principals Office | 0 | 0 | Yes | 384 | 8 | 8 | UV | 3072 | 0 | 0 | 20 | 3
100 | Classroom | 421 | 28 |  | 840 | 19 | 19 | UV | 6720 | 3.7589 | 1 | 3.7589 | 1
101 | Classroom | 454 | 30 |  | 840 | 19 | 19 | UV | 6720 | 4.0536 | 2 | 4.0536 | 2
102 | Classroom | 425 | 28 |  | 864 | 19 | 19 | UV | 6912 | 3.6892 | 1 | 3.6892 | 1
103 | Classroom | 318 | 21 |  | 432 | 9 | 9 | UV | 3456 | 5.5208 | 2 | 5.5208 | 2
104 | Classroom | 405 | 27 |  | 744 | 16 | 16 | UV | 5952 | 4.0827 | 2 | 4.0827 | 2
105 | Classroom | 453 | 30 |  | 840 | 19 | 19 | UV | 6720 | 4.0446 | 2 | 4.0446 | 2
107 | Classroom | 435 | 29 |  | 1064 | 24 | 24 | UV | 8512 | 3.0663 | 1 | 3.0663 | 1
108A | Office A Library |  | 0 | Yes | 156 | 3 | 3 |  | 1248 | unk | unk | 20 | 3
108B | Office B Library |  | 0 | Yes | 156 | 3 | 3 |  | 1248 | unk | unk | 20 | 3
109 | Classroom | 428 | 28 |  | 864 | 19 | 19 | UV | 6912 | 3.7153 | 1 | 3.7153 | 1
111 | Classroom | 394 | 26 |  | 840 | 19 | 19 | UV | 6720 | 3.5179 | 1 | 3.5179 | 1
112 | Classroom | 330 | 22 |  | 840 | 19 | 19 | UV | 6720 | 2.9464 | 1 | 2.9464 | 1
113 | Classroom | 416 | 27 |  | 980 | 22 | 22 | UV | 7840 | 3.1837 | 1 | 3.1837 | 1
115 | Classroom | 393 | 26 |  | 1248 | 28 | 26 | UV | 9984 | 2.3618 | 1 | 2.3618 | 1
116A | Counselor Office |  | 0 | Yes | 132 | 3 | 3 |  | 1056 | unk | unk | 20 | 3
116B | COVID Quarantine |  | 0 | Yes | 132 | 3 | 3 |  | 1056 | unk | unk | 20 | 3
117 | Classroom | 321 | 21 |  | 1440 | 32 | 21 | UV | 11520 | 1.6719 | 1 | 1.6719 | 1
200 | Classroom | 592 | 39 |  | 875 | 19 | 19 | UV | 7000 | 5.0743 | 2 | 5.0743 | 2
201 | Classroom | 340 | 22 |  | 864 | 19 | 19 | UV | 6912 | 2.9514 | 1 | 2.9514 | 1
202 | Classroom | 341 | 22 |  | 875 | 19 | 19 | UV | 7000 | 2.9229 | 1 | 2.9229 | 1
203 | Classroom | 485 | 32 |  | 864 | 19 | 19 | UV | 6912 | 4.2101 | 2 | 4.2101 | 2
204 | Classroom | 279 | 18 |  | 875 | 19 | 18 | UV | 7000 | 2.3914 | 1 | 2.3914 | 1
205 | Classroom | 295 | 19 |  | 864 | 19 | 19 | UV | 6912 | 2.5608 | 1 | 2.5608 | 1
207A | Classroom | 0 | 0 | Yes | 168 | 3 | 3 | UV | 1344 | 0 | 0 | 20 | 3
207B | Classroom | 300 | 20 |  | 336 | 7 | 7 | UV | 2688 | 6.6964 | 2 | 6.6964 | 2
208 | Classroom | 349 | 23 |  | 1225 | 27 | 23 | UV | 9800 | 2.1367 | 1 | 2.1367 | 1
209 | Classroom | 348 | 23 |  | 864 | 19 | 19 | UV | 6912 | 3.0208 | 1 | 3.0208 | 1
210 | Classroom | 295 | 19 |  | 480 | 10 | 10 | UV | 3840 | 4.6094 | 2 | 4.6094 | 2
211 | Classroom | 360 | 24 |  | 864 | 19 | 19 | UV | 6912 | 3.125 | 1 | 3.125 | 1
212 | Classroom | 332 | 22 |  | 840 | 19 | 19 | UV | 6720 | 2.9643 | 1 | 2.9643 | 1
213 | Classroom | 297 | 19 |  | 875 | 19 | 19 | UV | 7000 | 2.5457 | 1 | 2.5457 | 1
300 | Classroom | 419 | 27 |  | 840 | 19 | 19 | UV | 6720 | 3.7411 | 1 | 3.7411 | 1
301 | Classroom | 416 | 27 |  | 840 | 19 | 19 | UV | 6720 | 3.7143 | 1 | 3.7143 | 1
302 | Classroom | 375 | 25 |  | 840 | 19 | 19 | UV | 6720 | 3.3482 | 1 | 3.3482 | 1
303 | Classroom | 395 | 26 |  | 840 | 19 | 19 | UV | 6720 | 3.5268 | 1 | 3.5268 | 1
304 | Classroom | 398 | 26 |  | 840 | 19 | 19 | UV | 6720 | 3.5536 | 1 | 3.5536 | 1
305 | Classroom | 411 | 27 |  | 840 | 19 | 19 | UV | 6720 | 3.6696 | 1 | 3.6696 | 1
307A | Office | 205 | 13 |  | 336 | 7 | 7 | UV | 2688 | 4.5759 | 2 | 4.5759 | 2
307B | Office | 0 | 0 | Yes | 168 | 3 | 3 | UV | 1344 | 0 | 0 | 20 | 3
308 | Classroom | 383 | 25 |  | 864 | 19 | 19 | UV | 6912 | 3.3247 | 1 | 3.3247 | 1
309 | Classroom | 365 | 24 |  | 840 | 19 | 19 | UV | 6720 | 3.2589 | 1 | 3.2589 | 1
310 | Classroom | 325 | 21 |  | 875 | 19 | 19 | UV | 7000 | 2.7857 | 1 | 2.7857 | 1
311 | Classroom | 309 | 20 |  | 840 | 19 | 19 | UV | 6720 | 2.7589 | 1 | 2.7589 | 1
312 | Classroom | 419 | 27 |  | 840 | 19 | 19 | UV | 6720 | 3.7411 | 1 | 3.7411 | 1
313 | Classroom | 346 | 23 |  | 840 | 19 | 19 | UV | 6720 | 3.0893 | 1 | 3.0893 | 1
- | Nurses office |  | 0 | Yes | 352 | 8 | 8 | UV | 2816 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-08 | [8 empty] | unk | unk | unk | unk
School: | William Loesche Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Brothers Retest | [7 empty] | unk | unk | unk | unk
| Devine Brothers 2nd Retest | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 286 | 19 |  | 840 | 19 | 19 | UV | 6720 | 2.5536 | 1 | 2.5536 | 1
101 | Classroom | 282 | 18 |  | 840 | 19 | 18 | UV | 6720 | 2.5179 | 1 | 2.5179 | 1
102 | Classroom | 82 | 5 | Yes | 784 | 17 | 17 | UV | 6272 | 0.78444 | 0 | 20.7844 | 3
103 | Classroom | 288 | 19 |  | 840 | 19 | 19 | UV | 6720 | 2.5714 | 1 | 2.5714 | 1
104 | Classroom | 0 | 0 |  | 840 | 19 | 0 | UV | 6720 | 0 | 0 | 0 | 0
105 | Classroom | 300 | 20 |  | 840 | 19 | 19 | UV | 6720 | 2.6786 | 1 | 2.6786 | 1
107 | Classroom | 288 | 19 |  | 840 | 19 | 19 | UV | 6720 | 2.5714 | 1 | 2.5714 | 1
108 | Classroom | 213 | 14 | Yes | 1122 | 25 | 25 | UV | 8976 | 1.4238 | 1 | 21.4238 | 3
109 | Classroom | 185 | 12 |  | 840 | 19 | 12 | UV | 6720 | 1.6518 | 1 | 1.6518 | 1
110 | Classroom | 156 | 10 | Yes | 840 | 19 | 19 | UV | 6720 | 1.3929 | 1 | 21.3929 | 3
111 | Classroom | 190 | 12 | Yes | 882 | 20 | 20 | UV | 7056 | 1.6156 | 1 | 21.6156 | 3
112 | Classroom | 285 | 19 |  | 729 | 16 | 16 | UV | 5832 | 2.9321 | 1 | 2.9321 | 1
200 | Classroom | 258 | 17 |  | 840 | 19 | 17 | UV | 6720 | 2.3036 | 1 | 2.3036 | 1
201 | Classroom | 292 | 19 |  | 840 | 19 | 19 | UV | 6720 | 2.6071 | 1 | 2.6071 | 1
202 | Classroom | 283 | 18 |  | 840 | 19 | 18 | UV | 6720 | 2.5268 | 1 | 2.5268 | 1
203 | Classroom | 158 | 10 | Yes | 840 | 19 | 19 | UV | 6720 | 1.4107 | 1 | 21.4107 | 3
204 | Classroom | 262 | 17 |  | 840 | 19 | 17 | UV | 6720 | 2.3393 | 1 | 2.3393 | 1
205 | Classroom | 205 | 13 | Yes | 840 | 19 | 19 | UV | 6720 | 1.8304 | 1 | 21.8304 | 3
206 | Classroom | 153 | 10 |  | 476 | 10 | 10 | UV | 3808 | 2.4107 | 1 | 2.4107 | 1
207 | Classroom | 297 | 19 |  | 840 | 19 | 19 | UV | 6720 | 2.6518 | 1 | 2.6518 | 1
208 | Classroom | 210 | 14 |  | 840 | 19 | 14 | UV | 6720 | 1.875 | 1 | 1.875 | 1
208A | Classroom | 150 | 10 |  | 252 | 5 | 5 | UV | 2016 | 4.4643 | 2 | 4.4643 | 2
209 | Classroom | 184 | 12 | Yes | 840 | 19 | 19 | UV | 6720 | 1.6429 | 1 | 21.6429 | 3
210 | Classroom | 193 | 12 |  | 780 | 17 | 12 | UV | 6240 | 1.8558 | 1 | 1.8558 | 1
211 | Classroom | 142 | 9 | Yes | 783 | 17 | 17 | UV | 6264 | 1.3602 | 1 | 21.3602 | 3
212 | Classroom | 267 | 17 |  | 840 | 19 | 17 | UV | 6720 | 2.3839 | 1 | 2.3839 | 1
214 | Classroom | 280 | 18 |  | 1212 | 27 | 18 | UV | 9696 | 1.7327 | 1 | 1.7327 | 1
215 | Classroom | 268 | 17 |  | 1232 | 28 | 17 | UV | 9856 | 1.6315 | 1 | 1.6315 | 1
216 | Classroom | 415 | 27 |  | 756 | 17 | 17 | UV | 6048 | 4.1171 | 2 | 4.1171 | 2
217 | Classroom | 276 | 18 |  | 841 | 19 | 18 | UV | 6728 | 2.4614 | 1 | 2.4614 | 1
218 | Classroom | 144 | 9 | Yes | 840 | 19 | 19 | UV | 6720 | 1.2857 | 1 | 21.2857 | 3
219 | Classroom | 106 | 7 | Yes | 840 | 19 | 19 | UV | 6720 | 0.94643 | 0 | 20.9464 | 3
220 | Classroom | 246 | 16 |  | 870 | 19 | 16 | UV | 6960 | 2.1207 | 1 | 2.1207 | 1
221 | Classroom | 140 | 9 |  | 870 | 19 | 9 | UV | 6960 | 1.2069 | 1 | 1.2069 | 1
222 | Classroom | 106 | 7 |  | 840 | 19 | 7 | UV | 6720 | 0.94643 | 0 | 0.94643 | 0
223 | Classroom | 175 | 11 |  | 840 | 19 | 11 | UV | 6720 | 1.5625 | 1 | 1.5625 | 1
224 | Classroom | 94 | 6 |  | 840 | 19 | 6 | UV | 6720 | 0.83929 | 0 | 0.83929 | 0
A-1 | Classroom | 242 | 16 |  | 884 | 20 | 16 | UV | 7072 | 2.0532 | 1 | 2.0532 | 1
A-2 | Classroom | 254 | 16 |  | 884 | 20 | 16 | UV | 7072 | 2.155 | 1 | 2.155 | 1
A-3 | Classroom | 298 | 19 |  | 884 | 20 | 19 | UV | 7072 | 2.5283 | 1 | 2.5283 | 1
A-4 | Classroom | 281 | 18 |  | 884 | 20 | 18 | UV | 7072 | 2.384 | 1 | 2.384 | 1
- | A-wing Mech. Rm | 0 | 0 |  | 358 | 8 | 0 | UV | 2864 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 |  | 3600 | 81 | 0 | AHU | 28800 | 0 | 0 | 0 | 0
B-1 | Classroom | 314 | 20 |  | 806 | 18 | 18 | UV | 6448 | 2.9218 | 1 | 2.9218 | 1
B-2 | Classroom | 311 | 20 |  | 806 | 18 | 18 | UV | 6448 | 2.8939 | 1 | 2.8939 | 1
B-3 | Classroom | 300 | 20 |  | 806 | 18 | 18 | UV | 6448 | 2.7916 | 1 | 2.7916 | 1
B-4 | Classroom | 313 | 20 |  | 806 | 18 | 18 | UV | 6448 | 2.9125 | 1 | 2.9125 | 1
B-5 | Classroom | 287 | 19 |  | 806 | 18 | 18 | UV | 6448 | 2.6706 | 1 | 2.6706 | 1
B-6 | Classroom | 297 | 19 |  | 905 | 20 | 19 | UV | 7240 | 2.4613 | 1 | 2.4613 | 1
B-7 | Classroom | 285 | 19 |  | 905 | 20 | 19 | UV | 7240 | 2.3619 | 1 | 2.3619 | 1
B-8 | Classroom | 304 | 20 |  | 905 | 20 | 20 | UV | 7240 | 2.5193 | 1 | 2.5193 | 1
B-9 | Classroom | 282 | 18 |  | 905 | 20 | 18 | UV | 7240 | 2.337 | 1 | 2.337 | 1
- | Backstage | 0 | 0 |  | 180 | 4 | 0 | UV | 1440 | 0 | 0 | 0 | 0
- | Backstage Dressing Rm. | 172 | 11 |  | 252 | 5 | 5 | UV | 2016 | 5.119 | 2 | 5.119 | 2
- | Cafeteria | 0 | 0 | Yes | 5540 | 125 | 125 | AHU | 44320 | 0 | 0 | 20 | 3
- | GYM | 0 | 0 |  | 4496 | 102 | 0 | AHU | 35968 | 0 | 0 | 0 | 0
- | Library | 0 | 0 |  | 1131 | 25 | 0 | UV | 9048 | 0 | 0 | 0 | 0
- | Main Office | 292 | 19 |  | 992 | 22 | 19 | UV | 7936 | 2.2077 | 1 | 2.2077 | 1
- | Nurse's Office | 94 | 6 |  | 706 | 16 | 6 | UV | 5648 | 0.99858 | 0 | 0.99858 | 0
- | Principal's Office | 148 | 9 |  | 308 | 7 | 7 | UV | 2464 | 3.6039 | 1 | 3.6039 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-24 | [8 empty] | unk | unk | unk | unk
School: | James Logan Elementary-Middle School | House Fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B-1 | Classroom | 1228 | 81 |  | 889 | 20 | 20 | House Fan | 7112 | 10.36 | 3 | 10.36 | 3
B-2 | Classroom | 975 | 65 |  | 737 | 16 | 16 | House Fan | 5896 | 9.922 | 2 | 9.922 | 2
B-3 | Classroom | 1131 | 75 |  | 1017 | 23 | 23 | House Fan | 8136 | 8.3407 | 2 | 8.3407 | 2
101 | Classroom | 539 | 35 |  | 729 | 16 | 16 | House Fan | 5832 | 5.5453 | 2 | 5.5453 | 2
102 | Classroom | 578 | 38 |  | 732 | 16 | 16 | House Fan | 5856 | 5.9221 | 2 | 5.9221 | 2
103 | Classroom | 593 | 39 |  | 724 | 16 | 16 | House Fan | 5792 | 6.143 | 2 | 6.143 | 2
104 | Classroom | 674 | 44 |  | 676 | 15 | 15 | House Fan | 5408 | 7.4778 | 2 | 7.4778 | 2
104A | Office | 0 | 0 |  | 177 | 4 | 0 | House Fan | 1416 | 0 | 0 | 0 | 0
105 | Teacher's Lounge | 617 | 41 |  | 650 | 14 | 14 | House Fan | 5200 | 7.1192 | 2 | 7.1192 | 2
106 | Classroom | 621 | 41 |  | 726 | 16 | 16 | House Fan | 5808 | 6.4153 | 2 | 6.4153 | 2
107 | Classroom | 376 | 25 |  | 722 | 16 | 16 | House Fan | 5776 | 3.9058 | 1 | 3.9058 | 1
108 | Classroom | 849 | 56 |  | 717 | 16 | 16 | House Fan | 5736 | 8.8808 | 2 | 8.8808 | 2
201 | IMC | 509 | 33 |  | 639 | 14 | 14 | House Fan | 5112 | 5.9742 | 2 | 5.9742 | 2
202 | IMC | 632 | 42 |  | 639 | 14 | 14 | House Fan | 5112 | 7.4178 | 2 | 7.4178 | 2
203 | Classroom | 551 | 36 |  | 720 | 16 | 16 | House Fan | 5760 | 5.7396 | 2 | 5.7396 | 2
204 | Office Storage | 0 | 0 |  | 201 | 4 | 0 | House Fan | 1608 | 0 | 0 | 0 | 0
205 | Classroom | 519 | 34 |  | 718 | 16 | 16 | House Fan | 5744 | 5.4213 | 2 | 5.4213 | 2
205A | Office | 0 | 0 |  | 164 | 3 | 0 | House Fan | 1312 | 0 | 0 | 0 | 0
206 | Classroom | 715 | 47 |  | 735 | 16 | 16 | House Fan | 5880 | 7.2959 | 2 | 7.2959 | 2
206A | Counselor | 0 | 0 |  | 231 | 5 | 0 | House Fan | 1848 | 0 | 0 | 0 | 0
207 | Classroom | 394 | 26 |  | 723 | 16 | 16 | House Fan | 5784 | 4.0871 | 2 | 4.0871 | 2
208 | Classroom | 423 | 28 |  | 724 | 16 | 16 | House Fan | 5792 | 4.3819 | 2 | 4.3819 | 2
209 | Classroom | 575 | 38 |  | 725 | 16 | 16 | House Fan | 5800 | 5.9483 | 2 | 5.9483 | 2
209A | Classroom | 0 | 0 |  | 260 | 5 | 0 | House Fan | 2080 | 0 | 0 | 0 | 0
301 | Classroom | 522 | 34 |  | 679 | 15 | 15 | House Fan | 5432 | 5.7658 | 2 | 5.7658 | 2
302 | Classroom | 549 | 36 |  | 679 | 15 | 15 | House Fan | 5432 | 6.0641 | 2 | 6.0641 | 2
303 | Classroom | 458 | 30 |  | 724 | 16 | 16 | House Fan | 5792 | 4.7445 | 2 | 4.7445 | 2
304 | Classroom | 481 | 32 |  | 714 | 16 | 16 | House Fan | 5712 | 5.0525 | 2 | 5.0525 | 2
305 | Classroom | 347 | 23 |  | 890 | 20 | 20 | House Fan | 7120 | 2.9242 | 1 | 2.9242 | 1
306 | Classroom | 381 | 25 |  | 750 | 17 | 17 | House Fan | 6000 | 3.81 | 1 | 3.81 | 1
307 | Classroom | 312 | 20 |  | 992 | 22 | 20 | House Fan | 7936 | 2.3589 | 1 | 2.3589 | 1
308 | Classroom | 466 | 31 |  | 751 | 17 | 17 | House Fan | 6008 | 4.6538 | 2 | 4.6538 | 2
309 | Classroom | 508 | 33 |  | 992 | 22 | 22 | House Fan | 7936 | 3.8407 | 1 | 3.8407 | 1
310 | Classroom | 477 | 31 |  | 720 | 16 | 16 | House Fan | 5760 | 4.9688 | 2 | 4.9688 | 2
311 | Classroom | 409 | 27 |  | 703 | 15 | 15 | House Fan | 5624 | 4.3634 | 2 | 4.3634 | 2
312 | Classroom | 491 | 32 |  | 730 | 16 | 16 | House Fan | 5840 | 5.0445 | 2 | 5.0445 | 2
313 | Classroom | 570 | 38 |  | 721 | 16 | 16 | House Fan | 5768 | 5.9293 | 2 | 5.9293 | 2
- | Auditorium | 2427 | 161 |  | 3685 | 83 | 83 | House Fan | 29480 | 4.9396 | 2 | 4.9396 | 2
- | Boys' Bathroom | 125 | 8 |  | 561 | 12 | 8 | N/A | 4488 | 1.6711 | 1 | 1.6711 | 1
- | Girls' Bathroom | 73 | 4 |  | 547 | 12 | 4 | N/A | 4376 | 1.0009 | 1 | 1.0009 | 1
- | Cafeteria | 1258 | 83 |  | 1726 | 39 | 39 | House Fan | 13808 | 5.4664 | 2 | 5.4664 | 2
- | Speech Classroom | 0 | 0 | Yes | 192 | 4 | 4 | House Fan | 1536 | 0 | 0 | 20 | 3
- | Gym | 0 | 0 | Yes | 3970 | 90 | 90 | N/A | 31760 | 0 | 0 | 20 | 3
- | Nurse's Office | 0 | 0 | Yes | 220 | 5 | 5 | House Fan | 1760 | 0 | 0 | 20 | 3
- | IMC Office | 0 | 0 |  | 158 | 3 | 0 | House Fan | 1264 | 0 | 0 | 0 | 0
- | Main Office | 0 | 0 | Yes | 333 | 7 | 7 | House Fan | 2664 | 0 | 0 | 20 | 3
- | Principal's Office | 0 | 0 | Yes | 342 | 7 | 7 | House Fan | 2736 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-26 | [8 empty] | unk | unk | unk | unk
School: | W.C. Longstreth Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100D | Faculty Dining | 96 | 6 |  | 625 | 14 | 6 | AHU-6 | 5000 | 1.152 | 1 | 1.152 | 1
102 | Main Office | 110 | 7 |  | 646 | 14 | 7 | AHU-6 | 5168 | 1.2771 | 1 | 1.2771 | 1
102C | Principal Office | 77 | 5 |  | 225 | 5 | 5 | AHU-6 | 1800 | 2.5667 | 1 | 2.5667 | 1
102D | Comference Room | 72 | 4 |  | 198 | 4 | 4 | AHU-6 | 1584 | 2.7273 | 1 | 2.7273 | 1
103 | Classroom | 141 | 9 |  | 704 | 16 | 9 | AHU-1 | 5632 | 1.5021 | 1 | 1.5021 | 1
105 | Classroom | 206 | 13 |  | 609 | 13 | 13 | AHU-1 | 4872 | 2.5369 | 1 | 2.5369 | 1
106 | Art Room | 610 | 40 |  | 1333 | 30 | 30 | AHU-2 | 10664 | 3.4321 | 1 | 3.4321 | 1
107 | Classroom | 468 | 31 |  | 1320 | 30 | 30 | AHU-1 | 10560 | 2.6591 | 1 | 2.6591 | 1
109 | Classroom | 469 | 31 |  | 1276 | 29 | 29 | AHU-1 | 10208 | 2.7567 | 1 | 2.7567 | 1
110 | Nurses Suite | 45 | 3 |  | 180 | 4 | 3 | AHU-6 | 1440 | 1.875 | 1 | 1.875 | 1
110C | Nurses Office | 102 | 6 |  | 132 | 3 | 3 | AHU-6 | 1056 | 5.7955 | 2 | 5.7955 | 2
110D | Audio Rm | 101 | 6 |  | 132 | 3 | 3 | AHU-6 | 1056 | 5.7386 | 2 | 5.7386 | 2
110E | Audio Rm | 78 | 5 |  | 48 | 1 | 1 | AHU-6 | 384 | 12.1875 | 3 | 12.1875 | 3
111 | Classroom | 487 | 32 |  | 1232 | 28 | 28 | AHU-1 | 9856 | 2.9647 | 1 | 2.9647 | 1
112A | Building Engineers Office | 90 | 6 |  | 88 | 2 | 2 | AHU-6 | 704 | 7.6705 | 2 | 7.6705 | 2
113 | Classroom | 361 | 24 |  | 1364 | 31 | 24 | AHU-1 | 10912 | 1.985 | 1 | 1.985 | 1
200 | Library | 715 | 47 |  | 2859 | 64 | 47 | AHU-5 | 22872 | 1.8757 | 1 | 1.8757 | 1
200A | Computer Lab | 119 | 7 |  | 704 | 16 | 7 | AHU-5 | 5632 | 1.2678 | 1 | 1.2678 | 1
200B | Consortium | 67 | 4 |  | 552 | 12 | 4 | AHU-5 | 4416 | 0.91033 | 0 | 0.91033 | 0
201 | Classroom | 403 | 26 |  | 818 | 18 | 18 | AHU-1 | 6544 | 3.695 | 1 | 3.695 | 1
202 | Classroom | 360 | 24 |  | 510 | 11 | 11 | AHU-2 | 4080 | 5.2941 | 2 | 5.2941 | 2
203 | Classroom | 321 | 21 |  | 544 | 12 | 12 | AHU-1 | 4352 | 4.4256 | 2 | 4.4256 | 2
204 | Classroom | 206 | 13 | Yes | 510 | 11 | 11 | AHU-2 | 4080 | 3.0294 | 1 | 23.0294 | 3
205 | Classroom | 273 | 18 |  | 544 | 12 | 12 | AHU-1 | 4352 | 3.7638 | 1 | 3.7638 | 1
206 | Classroom | 364 | 24 |  | 510 | 11 | 11 | AHU-2 | 4080 | 5.3529 | 2 | 5.3529 | 2
207 | Classroom | 419 | 27 |  | 544 | 12 | 12 | AHU-1 | 4352 | 5.7767 | 2 | 5.7767 | 2
208 | Classroom | 309 | 20 |  | 510 | 11 | 11 | AHU-2 | 4080 | 4.5441 | 2 | 4.5441 | 2
209 | Classroom | 417 | 27 |  | 544 | 12 | 12 | AHU-1 | 4352 | 5.7491 | 2 | 5.7491 | 2
210 | Classroom | 276 | 18 |  | 510 | 11 | 11 | AHU-2 | 4080 | 4.0588 | 2 | 4.0588 | 2
211 | Classroom | 88 | 5 |  | 576 | 13 | 5 | AHU-1 | 4608 | 1.1458 | 1 | 1.1458 | 1
212 | Classroom | 304 | 20 |  | 765 | 17 | 17 | AHU-2 | 6120 | 2.9804 | 1 | 2.9804 | 1
213 | Classroom | 303 | 20 |  | 810 | 18 | 18 | AHU-1 | 6480 | 2.8056 | 1 | 2.8056 | 1
214 | Classroom - WEIGHT ROOM | 669 | 44 |  | 1204 | 27 | 27 | AHU-2 | 9632 | 4.1674 | 2 | 4.1674 | 2
215 | Classroom | 141 | 9 |  | 285 | 6 | 6 | AHU-1 | 2280 | 3.7105 | 1 | 3.7105 | 1
219 | Classroom | 175 | 11 |  | 220 | 5 | 5 | AHU-1 | 1760 | 5.9659 | 2 | 5.9659 | 2
220 | Classroom | 61 | 4 |  | 612 | 13 | 4 | AHU-2 | 4896 | 0.74755 | 0 | 0.74755 | 0
301 | Classroom | 311 | 20 |  | 595 | 13 | 13 | AHU-1 | 4760 | 3.9202 | 1 | 3.9202 | 1
303 | Classroom | 323 | 21 |  | 561 | 12 | 12 | AHU-1 | 4488 | 4.3182 | 2 | 4.3182 | 2
304 | Classroom | 220 | 14 |  | 570 | 12 | 12 | AHU-2 | 4560 | 2.8947 | 1 | 2.8947 | 1
305 | Classroom | 316 | 21 |  | 577 | 13 | 13 | AHU-1 | 4616 | 4.1075 | 2 | 4.1075 | 2
306 | Classroom | 462 | 30 |  | 510 | 11 | 11 | AHU-2 | 4080 | 6.7941 | 2 | 6.7941 | 2
307 | Classroom | 331 | 22 |  | 577 | 13 | 13 | AHU-1 | 4616 | 4.3024 | 2 | 4.3024 | 2
308 | Classroom | 327 | 21 |  | 510 | 11 | 11 | AHU-2 | 4080 | 4.8088 | 2 | 4.8088 | 2
309 | Classroom | 356 | 23 |  | 594 | 13 | 13 | AHU-1 | 4752 | 4.4949 | 2 | 4.4949 | 2
310 | Classroom | 320 | 21 |  | 527 | 11 | 11 | AHU-2 | 4216 | 4.5541 | 2 | 4.5541 | 2
311 | Classroom | 340 | 22 |  | 576 | 13 | 13 | AHU-1 | 4608 | 4.4271 | 2 | 4.4271 | 2
312 | Classroom | 332 | 22 |  | 544 | 12 | 12 | AHU-2 | 4352 | 4.5772 | 2 | 4.5772 | 2
313 | Classroom | 422 | 28 |  | 840 | 19 | 19 | AHU-1 | 6720 | 3.7679 | 1 | 3.7679 | 1
314 | Classroom | 577 | 38 |  | 1290 | 29 | 29 | AHU-2 | 10320 | 3.3547 | 1 | 3.3547 | 1
315 | Classroom | 145 | 9 |  | 280 | 6 | 6 | AHU-1 | 2240 | 3.8839 | 1 | 3.8839 | 1
319 | Classroom | 129 | 8 |  | 220 | 5 | 5 | AHU-1 | 1760 | 4.3977 | 2 | 4.3977 | 2
320 | Classroom | 171 | 11 |  | 210 | 4 | 4 | AHU-2 | 1680 | 6.1071 | 2 | 6.1071 | 2
- | Auditorium | 1337 | 89 |  | 3540 | 80 | 80 | AHU-3 | 28320 | 2.8326 | 1 | 2.8326 | 1
- | Cafeteria | 2211 | 147 |  | 3658 | 83 | 83 | AHU-4 | 29264 | 4.5332 | 2 | 4.5332 | 2
- | Diagnostic Center | 213 | 14 |  | 306 | 6 | 6 | AHU-6 | 2448 | 5.2206 | 2 | 5.2206 | 2
- | Main Office Admin | 82 | 5 |  | 110 | 2 | 2 | AHU-6 | 880 | 5.5909 | 2 | 5.5909 | 2
- | Main Storage Room | 27 | 1 |  | 192 | 4 | 1 | AHU-6 | 1536 | 1.0547 | 1 | 1.0547 | 1
- | Nurses Suite Laundry | 115 | 7 |  | 372 | 8 | 7 | AHU-6 | 2976 | 2.3185 | 1 | 2.3185 | 1
- | Gym | 0 | 0 |  | 4720 | 107 | 0 | AHU 1 and 2 | 37760 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-26 | [8 empty] | unk | unk | unk | unk
School: | James R. Lowell Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B010A | Boys Bathroom | 725 | 48 |  | 667 | 15 | 15 | N/A | 5336 | 8.1522 | 2 | 8.1522 | 2
B10 | Music | 0 | 0 |  | 925 | 21 | 0 | N/A | 7400 | 0 | 0 | 0 | 0
B11 | Classroom | 346 | 23 |  | 695 | 15 | 15 | House Fan | 5560 | 3.7338 | 1 | 3.7338 | 1
B12 | Girls Bathroom | 305 | 20 |  | 695 | 15 | 15 | House Fan | 5560 | 3.2914 | 1 | 3.2914 | 1
B8 | Classroom | 175 | 11 |  | 576 | 13 | 11 | House Fan | 4608 | 2.2786 | 1 | 2.2786 | 1
B9 | Classroom | 388 | 25 |  | 667 | 15 | 15 | House Fan | 5336 | 4.3628 | 2 | 4.3628 | 2
100 | Classroom | 0 | 0 |  | 240 | 5 | 0 | House Fan | 1920 | 0 | 0 | 0 | 0
101 | Classroom | 285 | 19 |  | 566 | 12 | 12 | House Fan | 4528 | 3.7765 | 1 | 3.7765 | 1
102 | Classroom | 327 | 21 |  | 559 | 12 | 12 | House Fan | 4472 | 4.3873 | 2 | 4.3873 | 2
103 | Classroom | 325 | 21 |  | 100 | 2 | 2 | House Fan | 800 | 24.375 | 4 | 24.375 | 4
104 | Classroom | 102 | 6 |  | 640 | 14 | 6 | House Fan | 5120 | 1.1953 | 1 | 1.1953 | 1
105 | Classroom | 593 | 39 |  | 654 | 14 | 14 | House Fan | 5232 | 6.8005 | 2 | 6.8005 | 2
106 | Classroom | 399 | 26 |  | 566 | 12 | 12 | House Fan | 4528 | 5.2871 | 2 | 5.2871 | 2
107 | Classroom | 0 | 0 |  | 667 | 15 | 0 | House Fan | 5336 | 0 | 0 | 0 | 0
108 | Classroom | 154 | 10 |  | 650 | 14 | 10 | House Fan | 5200 | 1.7769 | 1 | 1.7769 | 1
109 | Classroom | 304 | 20 |  | 602 | 13 | 13 | House Fan | 4816 | 3.7874 | 1 | 3.7874 | 1
110 | Classroom | 0 | 0 |  | 207 | 4 | 0 | House Fan | 1656 | 0 | 0 | 0 | 0
111 | Counselor |  | 0 |  | 154 | 3 | 0 |  | 1232 | unk | unk | unk | unk
200 | Classroom | 0 | 0 |  | 240 | 5 | 0 | House Fan | 1920 | 0 | 0 | 0 | 0
201 | Classroom | 300 | 20 |  | 654 | 14 | 14 | House Fan | 5232 | 3.4404 | 1 | 3.4404 | 1
202 | Computer Room |  | 0 |  | 810 | 18 | 0 |  | 6480 | unk | unk | unk | unk
203 | Classroom | 647 | 43 |  | 654 | 14 | 14 | House Fan | 5232 | 7.4197 | 2 | 7.4197 | 2
204 | Classroom | 457 | 30 |  | 650 | 14 | 14 | House Fan | 5200 | 5.2731 | 2 | 5.2731 | 2
205 | Classroom | 531 | 35 |  | 650 | 14 | 14 | House Fan | 5200 | 6.1269 | 2 | 6.1269 | 2
206 | Classroom | 247 | 16 |  | 695 | 15 | 15 | House Fan | 5560 | 2.6655 | 1 | 2.6655 | 1
207 | Classroom | 102 | 6 |  | 694 | 15 | 6 | House Fan | 5552 | 1.1023 | 1 | 1.1023 | 1
207 | Faculty Room | 0 | 0 |  | 207 | 4 | 0 | N/A | 1656 | 0 | 0 | 0 | 0
208 | Classroom | 200 | 13 |  | 695 | 15 | 13 | House Fan | 5560 | 2.1583 | 1 | 2.1583 | 1
209 | Classroom | 139 | 9 |  | 650 | 14 | 9 | House Fan | 5200 | 1.6038 | 1 | 1.6038 | 1
210 | Classroom | 275 | 18 |  | 560 | 12 | 12 | House Fan | 4480 | 3.683 | 1 | 3.683 | 1
211 | Classroom | 0 | 0 |  | 420 | 9 | 0 | House Fan | 3360 | 0 | 0 | 0 | 0
300 | Classroom | 0 | 0 |  | 240 | 5 | 0 | House Fan | 1920 | 0 | 0 | 0 | 0
301A | Classroom | 132 | 8 |  | 566 | 12 | 8 | House Fan | 4528 | 1.7491 | 1 | 1.7491 | 1
301B | Classroom | 139 | 9 |  | 300 | 6 | 6 | House Fan | 2400 | 3.475 | 1 | 3.475 | 1
302 | Classroom | 145 | 9 |  | 240 | 5 | 5 | House Fan | 1920 | 4.5312 | 2 | 4.5312 | 2
303 | Classroom | 318 | 21 |  | 666 | 15 | 15 | House Fan | 5328 | 3.5811 | 1 | 3.5811 | 1
304 | Classroom | 387 | 25 |  | 610 | 13 | 13 | House Fan | 4880 | 4.7582 | 2 | 4.7582 | 2
305 | Classroom | 432 | 28 |  | 620 | 14 | 14 | House Fan | 4960 | 5.2258 | 2 | 5.2258 | 2
306 | Classroom | 249 | 16 |  | 650 | 14 | 14 | House Fan | 5200 | 2.8731 | 1 | 2.8731 | 1
307 | Classroom | 325 | 21 |  | 650 | 14 | 14 | House Fan | 5200 | 3.75 | 1 | 3.75 | 1
308 | Classroom | 322 | 21 |  | 650 | 14 | 14 | House Fan | 5200 | 3.7154 | 1 | 3.7154 | 1
309 | Classroom | 262 | 17 |  | 654 | 14 | 14 | House Fan | 5232 | 3.0046 | 1 | 3.0046 | 1
310 | Classroom | 203 | 13 |  | 636 | 14 | 13 | House Fan | 5088 | 2.3939 | 1 | 2.3939 | 1
311 | Classroom | 0 | 0 |  | 221 | 5 | 0 | House Fan | 1768 | 0 | 0 | 0 | 0
312 | Classroom | 0 | 0 |  | 273 | 6 | 0 | House Fan | 2184 | 0 | 0 | 0 | 0
- | Library | 213 | 14 |  | 1040 | 23 | 14 | AHU | 8320 | 1.5361 | 1 | 1.5361 | 1
- | Entrance Lobby | 290 | 19 |  | 325 | 7 | 7 | N/A | 2600 | 6.6923 | 2 | 6.6923 | 2
- | Gym | 0 | 0 |  | 4368 | 99 | 0 | AHU | 34944 | 0 | 0 | 0 | 0
- | Music Rm | 127 | 8 |  | 286 | 6 | 6 | Unit Ventilator | 2288 | 3.3304 | 1 | 3.3304 | 1
S-11 | Classroom | 419 | 27 |  | 810 | 18 | 18 | Unit Ventilator | 6480 | 3.8796 | 1 | 3.8796 | 1
S-12 | Classroom | 906 | 60 |  | 692 | 15 | 15 | Unit Ventilator | 5536 | 9.8194 | 2 | 9.8194 | 2
S-13 | Classroom | 635 | 42 |  | 692 | 15 | 15 | Unit Ventilator | 5536 | 6.8822 | 2 | 6.8822 | 2
S-14 | Classroom | 715 | 47 |  | 695 | 15 | 15 | Unit Ventilator | 5560 | 7.7158 | 2 | 7.7158 | 2
S-15 | Classroom | 411 | 27 |  | 692 | 15 | 15 | Unit Ventilator | 5536 | 4.4545 | 2 | 4.4545 | 2
S-16 | Classroom | 502 | 33 |  | 692 | 15 | 15 | Unit Ventilator | 5536 | 5.4408 | 2 | 5.4408 | 2
S-17 | Classroom | 371 | 24 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 3.3605 | 1 | 3.3605 | 1
S-18 | Classroom | 482 | 32 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 4.3659 | 2 | 4.3659 | 2
S-19 | Classroom | 742 | 49 |  | 828 | 18 | 18 | Unit Ventilator | 6624 | 6.721 | 2 | 6.721 | 2
S-21 | Classroom | 429 | 28 |  | 640 | 14 | 14 | Unit Ventilator | 5120 | 5.0273 | 2 | 5.0273 | 2
S-22 | Classroom | 663 | 44 |  | 640 | 14 | 14 | Unit Ventilator | 5120 | 7.7695 | 2 | 7.7695 | 2
S-23 | Classroom | 480 | 32 |  | 654 | 14 | 14 | Unit Ventilator | 5232 | 5.5046 | 2 | 5.5046 | 2
S-24 | Classroom | 333 | 22 |  | 636 | 14 | 14 | Unit Ventilator | 5088 | 3.9269 | 1 | 3.9269 | 1
S-25 | Classroom | 844 | 56 |  | 636 | 14 | 14 | Unit Ventilator | 5088 | 9.9528 | 2 | 9.9528 | 2
S-26 | Classroom | 490 | 32 |  | 654 | 14 | 14 | Unit Ventilator | 5232 | 5.6193 | 2 | 5.6193 | 2
S-27 | Storage | 393 | 26 |  | 610 | 13 | 13 | Unit Ventilator | 4880 | 4.832 | 2 | 4.832 | 2
S-27 | Classroom | 266 | 17 |  | 610 | 13 | 13 | Unit Ventilator | 4880 | 3.2705 | 1 | 3.2705 | 1
S-28 | Classroom | 450 | 30 |  | 610 | 13 | 13 | Unit Ventilator | 4880 | 5.5328 | 2 | 5.5328 | 2
S-29 | Classroom | 260 | 17 |  | 610 | 13 | 13 | Unit Ventilator | 4880 | 3.1967 | 1 | 3.1967 | 1
S-30 | Teacher's Lounge | 378 | 25 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 3.3042 | 1 | 3.3042 | 1
S-31 | Office | 508 | 33 |  | 140 | 3 | 3 | Unit Ventilator | 1120 | 27.2143 | 4 | 27.2143 | 4
- | Main Office |  | 0 |  | 338 | 7 | 0 |  | 2704 | unk | unk | unk | unk
- | Principals Office |  | 0 |  | 364 | 8 | 0 |  | 2912 | unk | unk | unk | unk
- | Nurses Office |  | 0 |  | 240 | 5 | 0 |  | 1920 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | James R. Ludlow Elementary-Middle School | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
3 | Art |  | 0 |  | 667 | 15 | 0 | House Fan | 5336 | unk | unk | unk | unk
100B | Home and School |  | 0 |  | 121 | 2 | 0 | House Fan | 968 | unk | unk | unk | unk
100C | Counselor |  | 0 |  | 195 | 4 | 0 | House Fan | 1560 | unk | unk | unk | unk
101 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | unk | unk | 20 | 3
104 | Classroom |  | 0 | Yes | 638 | 14 | 14 | House Fan | 5104 | unk | unk | 20 | 3
105 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
106 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
107 | Classroom |  | 0 |  | 920 | 20 | 0 | House Fan | 7360 | unk | unk | unk | unk
108 | Classroom |  | 0 | Yes | 638 | 14 | 14 | House Fan | 5104 | unk | unk | 20 | 3
109 | Classroom |  | 0 | Yes | 841 | 19 | 19 | House Fan | 6728 | unk | unk | 20 | 3
110 | Counselor |  | 0 |  | 128 | 2 | 0 | House Fan | 1024 | unk | unk | unk | unk
200 | Classroom |  | 0 | Yes | 552 | 12 | 12 | House Fan | 4416 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
204 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
207 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
208 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
209 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
211 | Classroom |  | 0 | Yes | 841 | 19 | 19 | House Fan | 6728 | unk | unk | 20 | 3
300 | Ladies lounge |  | 0 |  | 276 | 6 | 0 | House Fan | 2208 | unk | unk | unk | unk
300A | Ladies lounge |  | 0 |  | 276 | 6 | 0 | House Fan | 2208 | unk | unk | unk | unk
301 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
302 | Classroom |  | 0 | Yes | 782 | 17 | 17 | House Fan | 6256 | unk | unk | 20 | 3
303 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | unk | unk | 20 | 3
304 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
305 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
306 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
307 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
308 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
309 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
310 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
311 | Classroom |  | 0 | Yes | 406 | 9 | 9 | House Fan | 3248 | unk | unk | 20 | 3
- | Library |  | 0 | Yes | 1298 | 29 | 29 | House Fan | 10384 | unk | unk | 20 | 3
- | Gym |  | 0 | Yes | 5208 | 118 | 118 |  | 41664 | unk | unk | 20 | 3
- | Kitchen |  | 0 | Yes | 1288 | 29 | 29 | House Fan | 10304 | unk | unk | 20 | 3
- | Lunchroom/Cafetorium |  | 0 |  | 3157 | 71 | 0 | House Fan | 25256 | unk | unk | unk | unk
- | Main office |  | 0 | Yes | 322 | 7 | 7 | House Fan | 2576 | unk | unk | 20 | 3
- | Nurses Office |  | 0 | Yes | 128 | 2 | 2 | House Fan | 1024 | unk | unk | 20 | 3
- | Principals office |  | 0 | Yes | 165 | 3 | 3 | House Fan | 1320 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-08 | [8 empty] | unk | unk | unk | unk
School: | John Marshall Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
102 | Classroom | 723 | 48 |  | 832 | 18 | 18 | House Fan | 6656 | 6.5174 | 2 | 6.5174 | 2
103 | Classroom | 653 | 43 |  | 449 | 10 | 10 | House Fan | 3592 | 10.9076 | 3 | 10.9076 | 3
104 | Classroom | 684 | 45 |  | 781 | 17 | 17 | House Fan | 6248 | 6.5685 | 2 | 6.5685 | 2
105 | Classroom | 717 | 47 |  | 738 | 16 | 16 | House Fan | 5904 | 7.2866 | 2 | 7.2866 | 2
106 | Classroom | 624 | 41 |  | 893 | 20 | 20 | House Fan | 7144 | 5.2408 | 2 | 5.2408 | 2
107 | Classroom | 575 | 38 |  | 623 | 14 | 14 | House Fan | 4984 | 6.9222 | 2 | 6.9222 | 2
200 | Classroom | 640 | 42 |  | 790 | 17 | 17 | House Fan | 6320 | 6.0759 | 2 | 6.0759 | 2
201 | Classroom | 692 | 46 |  | 803 | 18 | 18 | House Fan | 6424 | 6.4633 | 2 | 6.4633 | 2
202 | Classroom | 691 | 46 |  | 746 | 16 | 16 | House Fan | 5968 | 6.9471 | 2 | 6.9471 | 2
203 | Classroom | 556 | 37 |  | 770 | 17 | 17 | House Fan | 6160 | 5.4156 | 2 | 5.4156 | 2
204 | Classroom | 678 | 45 |  | 715 | 16 | 16 | House Fan | 5720 | 7.1119 | 2 | 7.1119 | 2
205 | Classroom | 765 | 51 |  | 225 | 5 | 5 | House Fan | 1800 | 25.5 | 4 | 25.5 | 4
206 | Classroom | 535 | 35 |  | 548 | 12 | 12 | House Fan | 4384 | 7.3221 | 2 | 7.3221 | 2
300 | Classroom | 596 | 39 |  | 766 | 17 | 17 | House Fan | 6128 | 5.8355 | 2 | 5.8355 | 2
300A | Classroom |  | 0 | Yes | 510 | 11 | 11 | Wndow Fan | 4080 | unk | unk | 20 | 3
301 | Classroom | 531 | 35 |  | 884 | 20 | 20 | House Fan | 7072 | 4.5051 | 2 | 4.5051 | 2
302 | Classroom | 683 | 45 |  | 766 | 17 | 17 | House Fan | 6128 | 6.6873 | 2 | 6.6873 | 2
303 | Classroom | 785 | 52 |  | 748 | 17 | 17 | House Fan | 5984 | 7.871 | 2 | 7.871 | 2
304 | Classroom | 793 | 52 |  | 779 | 17 | 17 | House Fan | 6232 | 7.6348 | 2 | 7.6348 | 2
305 | Classroom | 668 | 44 |  | 757 | 17 | 17 | House Fan | 6056 | 6.6182 | 2 | 6.6182 | 2
306 | Classroom | 609 | 40 |  | 876 | 19 | 19 | House Fan | 7008 | 5.214 | 2 | 5.214 | 2
- | 1st Fl. Corridor | 1954 | 130 |  | 352 | 8 | 8 | N/A | 2816 | 41.6335 | 4 | 41.6335 | 4
- | Grnd. Fl. Boys Bathrm. | 402 | 26 |  | 234 | 5 | 5 | N/A | 1872 | 12.8846 | 3 | 12.8846 | 3
- | Grnd. Fl. Girls Bathrm. | 333 | 22 |  | 156 | 3 | 3 | N/A | 1248 | 16.0096 | 3 | 16.0096 | 3
- | Main Office | 343 | 22 |  | 298 | 6 | 6 | House Fan | 2384 | 8.6326 | 2 | 8.6326 | 2
- | Nurse / office | 340 | 22 |  | 420 | 9 | 9 | House Fan | 3360 | 6.0714 | 2 | 6.0714 | 2
- | Cafeteria |  | 0 | Yes | 3129 | 71 | 71 | Wndow Fan | 25032 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-24 | [8 empty] | unk | unk | unk | unk
School: | Thurgood Marshall Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 99 | 6 | Yes | 875 | 19 | 19 |  | 7000 | 0.84857 | 0 | 20.8486 | 3
101 | Classroom | 112 | 7 | Yes | 875 | 19 | 19 |  | 7000 | 0.96 | 0 | 20.96 | 3
102 | Classroom | 53 | 3 | Yes | 875 | 19 | 19 |  | 7000 | 0.45429 | 0 | 20.4543 | 3
103 | Classroom | 60 | 4 | Yes | 875 | 19 | 19 |  | 7000 | 0.51429 | 0 | 20.5143 | 3
104 | Classroom | 310 | 20 |  | 589 | 13 | 13 |  | 4712 | 3.9474 | 1 | 3.9474 | 1
105 | Classroom | 143 | 9 | Yes | 624 | 14 | 14 |  | 4992 | 1.7188 | 1 | 21.7188 | 3
106 | Office | 154 | 10 |  | 143 | 3 | 3 |  | 1144 | 8.0769 | 2 | 8.0769 | 2
106A | Office | 0 | 0 |  | 99 | 2 | 0 |  | 792 | 0 | 0 | 0 | 0
106B | Office | 0 | 0 |  | 99 | 2 | 0 |  | 792 | 0 | 0 | 0 | 0
106C | Office | 168 | 11 |  | 99 | 2 | 2 |  | 792 | 12.7273 | 3 | 12.7273 | 3
106D | Office | 180 | 12 |  | 126 | 2 | 2 |  | 1008 | 10.7143 | 3 | 10.7143 | 3
106E | Office | 165 | 11 |  | 130 | 2 | 2 |  | 1040 | 9.5192 | 2 | 9.5192 | 2
106G | Office | 191 | 12 |  | 130 | 2 | 2 |  | 1040 | 11.0192 | 3 | 11.0192 | 3
106H | Hallway | 0 | 0 |  | 528 | 12 | 0 |  | 4224 | 0 | 0 | 0 | 0
106 RR | Office | 513 | 34 |  | 52.5 | 1 | 1 |  | 420 | 73.2857 | 5 | 73.2857 | 5
107 | Classroom | 82 | 5 |  | 720 | 16 | 5 |  | 5760 | 0.85417 | 0 | 0.85417 | 0
107-2 | Classroom | 0 | 0 |  | 215 | 4 | 0 |  | 1720 | 0 | 0 | 0 | 0
107A | Classroom | 89 | 5 |  | 816 | 18 | 5 |  | 6528 | 0.81801 | 0 | 0.81801 | 0
108 | Classroom | 38 | 2 |  | 506 | 11 | 2 |  | 4048 | 0.56324 | 0 | 0.56324 | 0
108A | Classroom | 37 | 2 |  | 128 | 2 | 2 |  | 1024 | 2.168 | 1 | 2.168 | 1
109 | Classroom | 71 | 4 |  | 1196 | 27 | 4 |  | 9568 | 0.44523 | 0 | 0.44523 | 0
110 | Classroom | 382 | 25 |  | 682 | 15 | 15 |  | 5456 | 4.2009 | 2 | 4.2009 | 2
111 | Classroom | 216 | 14 | Yes | 630 | 14 | 14 |  | 5040 | 2.5714 | 1 | 22.5714 | 3
113A | Principals Office | 18 | 1 |  | 340 | 7 | 1 |  | 2720 | 0.39706 | 0 | 0.39706 | 0
113D | Admin Office | 33 | 2 |  | 99 | 2 | 2 |  | 792 | 2.5 | 1 | 2.5 | 1
113E | Admin Office | 24 | 1 |  | 99 | 2 | 1 |  | 792 | 1.8182 | 1 | 1.8182 | 1
113F | Admin Office | 25 | 1 |  | 99 | 2 | 1 |  | 792 | 1.8939 | 1 | 1.8939 | 1
113G | Admin Office | 20 | 1 |  | 99 | 2 | 1 |  | 792 | 1.5152 | 1 | 1.5152 | 1
115 | Classroom | 142 | 9 |  | 782 | 17 | 9 |  | 6256 | 1.3619 | 1 | 1.3619 | 1
200 | Classroom | 88 | 5 |  | 875 | 19 | 5 |  | 7000 | 0.75429 | 0 | 0.75429 | 0
201 | Classroom | 157 | 10 | Yes | 875 | 19 | 19 |  | 7000 | 1.3457 | 1 | 21.3457 | 3
202 | Classroom | 75 | 5 | Yes | 875 | 19 | 19 |  | 7000 | 0.64286 | 0 | 20.6429 | 3
203 | Classroom | 73 | 4 | Yes | 875 | 19 | 19 |  | 7000 | 0.62571 | 0 | 20.6257 | 3
204 | Classroom | 90 | 6 | Yes | 993 | 22 | 22 |  | 7944 | 0.67976 | 0 | 20.6798 | 3
205 | Classroom | 53 | 3 |  | 327.75 | 7 | 3 |  | 2622 | 1.2128 | 1 | 1.2128 | 1
206A | Classroom | 42 | 2 |  | 154 | 3 | 2 |  | 1232 | 2.0455 | 1 | 2.0455 | 1
206B | Classroom | 31 | 2 |  | 270 | 6 | 2 |  | 2160 | 0.86111 | 0 | 0.86111 | 0
206C | Classroom | 49 | 3 |  | 127 | 2 | 2 |  | 1016 | 2.8937 | 1 | 2.8937 | 1
207 | Library | 519 | 34 |  | 2108 | 47 | 34 |  | 16864 | 1.8465 | 1 | 1.8465 | 1
208 | Computer Lab | 73 | 4 | Yes | 1024 | 23 | 23 |  | 8192 | 0.53467 | 0 | 20.5347 | 3
209 | Music Room | 0 | 0 |  | 1171 | 26 | 0 |  | 9368 | 0 | 0 | 0 | 0
215 | Faculty Lounge | 279 | 18 |  | 400 | 9 | 9 |  | 3200 | 5.2313 | 2 | 5.2313 | 2
300 | Classroom | 140 | 9 | Yes | 875 | 19 | 19 |  | 7000 | 1.2 | 1 | 21.2 | 3
301 | Classroom | 125 | 8 | Yes | 875 | 19 | 19 |  | 7000 | 1.0714 | 1 | 21.0714 | 3
302 | Classroom | 200 | 13 | Yes | 875 | 19 | 19 |  | 7000 | 1.7143 | 1 | 21.7143 | 3
303 | Classroom | 37 | 2 |  | 875 | 19 | 2 |  | 7000 | 0.31714 | 0 | 0.31714 | 0
304 | Classroom | 86 | 5 | Yes | 960 | 21 | 21 |  | 7680 | 0.67188 | 0 | 20.6719 | 3
305 | Classroom | 111 | 7 |  | 782 | 17 | 7 |  | 6256 | 1.0646 | 1 | 1.0646 | 1
306 | Classroom | 200 | 13 |  | 782 | 17 | 13 |  | 6256 | 1.9182 | 1 | 1.9182 | 1
307 | Classroom | 132 | 8 |  | 782 | 17 | 8 |  | 6256 | 1.266 | 1 | 1.266 | 1
308 | Classroom | 33 | 2 |  | 782 | 17 | 2 |  | 6256 | 0.3165 | 0 | 0.3165 | 0
310 | Classroom | 65 | 4 |  | 782 | 17 | 4 |  | 6256 | 0.6234 | 0 | 0.6234 | 0
311 | Classroom | 632 | 42 |  | 782 | 17 | 17 |  | 6256 | 6.0614 | 2 | 6.0614 | 2
312 | Classroom | 99 | 6 |  | 782 | 17 | 6 |  | 6256 | 0.94949 | 0 | 0.94949 | 0
313 | Classroom | 76 | 5 |  | 782 | 17 | 5 |  | 6256 | 0.7289 | 0 | 0.7289 | 0
314 | Classroom | 87 | 5 |  | 782 | 17 | 5 |  | 6256 | 0.8344 | 0 | 0.8344 | 0
315 | Classroom | 112 | 7 |  | 782 | 17 | 7 |  | 6256 | 1.0742 | 1 | 1.0742 | 1
404 | Classroom | 90 | 6 |  | 1156 | 26 | 6 |  | 9248 | 0.58391 | 0 | 0.58391 | 0
405 | Classroom | 129 | 8 |  | 782 | 17 | 8 |  | 6256 | 1.2372 | 1 | 1.2372 | 1
405A | Office | 0 | 0 |  | 112 | 2 | 0 |  | 896 | 0 | 0 | 0 | 0
406 | Classroom | 93 | 6 |  | 782 | 17 | 6 |  | 6256 | 0.89194 | 0 | 0.89194 | 0
407 | Classroom | 147 | 9 |  | 782 | 17 | 9 |  | 6256 | 1.4098 | 1 | 1.4098 | 1
408 | Classroom | 40 | 2 |  | 782 | 17 | 2 |  | 6256 | 0.38363 | 0 | 0.38363 | 0
409A | Office | 23 | 1 |  | 140 | 3 | 1 |  | 1120 | 1.2321 | 1 | 1.2321 | 1
410 | Classroom | 0 | 0 |  | 782 | 17 | 0 |  | 6256 | 0 | 0 | 0 | 0
411 | Classroom | 86 | 5 |  | 782 | 17 | 5 |  | 6256 | 0.82481 | 0 | 0.82481 | 0
412 | Classroom | 94 | 6 |  | 782 | 17 | 6 |  | 6256 | 0.90153 | 0 | 0.90153 | 0
413 | Classroom | 76 | 5 |  | 782 | 17 | 5 |  | 6256 | 0.7289 | 0 | 0.7289 | 0
414 | Classroom | 84 | 5 |  | 782 | 17 | 5 |  | 6256 | 0.80563 | 0 | 0.80563 | 0
415 | Classroom | 100 | 6 |  | 782 | 17 | 6 |  | 6256 | 0.95908 | 0 | 0.95908 | 0
- | Auditorium | 369 | 24 |  | 2162 | 49 | 24 |  | 17296 | 1.2801 | 1 | 1.2801 | 1
- | Stage | 0 | 0 |  | 630 | 14 | 0 |  | 5040 | 0 | 0 | 0 | 0
- | Building Engineer Office | 0 | 0 |  | 120 | 2 | 0 |  | 960 | 0 | 0 | 0 | 0
- | Cafeteria | 3225 | 215 |  | 4400 | 100 | 100 |  | 35200 | 5.4972 | 2 | 5.4972 | 2
- | East Kitchen | 0 | 0 |  | 360 | 8 | 0 |  | 2880 | 0 | 0 | 0 | 0
- | West Kitchen | 0 | 0 |  | 1040 | 23 | 0 |  | 8320 | 0 | 0 | 0 | 0
- | Kitchen Office | 75 | 5 |  | 120 | 2 | 2 |  | 960 | 4.6875 | 2 | 4.6875 | 2
- | Gym | 4507 | 300 |  | 5005 | 113 | 113 |  | 40040 | 6.7537 | 2 | 6.7537 | 2
- | Nurses Office | 154 | 10 |  | 143 | 3 | 3 |  | 1144 | 8.0769 | 2 | 8.0769 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-19 | [8 empty] | unk | unk | unk | unk
School: | Jules E. Mastbaum High School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
SDP Building Name | Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room |  | unk | unk | unk | unk
Old Building | 101 | Classroom | 0 | 0 |  | 959 | 21 | 0 |  | unk | unk | unk | unk
Old Building | 102 | Classroom | 0 | 0 |  | 967 | 21 | 0 |  | unk | unk | unk | unk
Old Building | 103 | Classroom | 304 | 20 |  | 1130 | 25 | 20 |  | unk | unk | unk | unk
Old Building | 104 | Classroom | 455 | 30 |  | 801 | 18 | 18 |  | unk | unk | unk | unk
Old Building | 105 | Carpentry Shop |  | 0 | Yes | 2502 | 56 | 56 |  | unk | unk | unk | unk
Old Building | 201 | Classroom | 0 | 0 |  | 585 | 13 | 0 |  | unk | unk | unk | unk
Old Building | 202 | Classroom | 237 | 15 |  | 190 | 4 | 4 |  | unk | unk | unk | unk
Old Building | 206 | Classroom | 569 | 37 |  | 1045 | 23 | 23 |  | unk | unk | unk | unk
Old Building | 207 | Classroom | 0 | 0 |  | 906 | 20 | 0 |  | unk | unk | unk | unk
Old Building | 209 | Classroom | 738 | 49 |  | 603 | 13 | 13 |  | unk | unk | unk | unk
Old Building | 301 | Classroom | 680 | 45 |  | 583 | 13 | 13 |  | unk | unk | unk | unk
Old Building | 302 | Classroom | 271 | 18 |  | 915 | 20 | 18 |  | unk | unk | unk | unk
Old Building | 304 | Classroom | 256 | 17 |  | 943 | 21 | 17 |  | unk | unk | unk | unk
Old Building | 306 | Classroom | 1285 | 85 |  | 1099 | 24 | 24 |  | unk | unk | unk | unk
Old Building | 308 | Classroom | 292 | 19 |  | 971 | 22 | 19 |  | unk | unk | unk | unk
Old Building | 310A | Classroom | 279 | 18 |  | 1015 | 23 | 18 |  | unk | unk | unk | unk
Old Building | 311 | Classroom | 0 | 0 |  | 940 | 21 | 0 |  | unk | unk | unk | unk
Old Building | 313 | Classroom | 572 | 38 |  | 939 | 21 | 21 |  | unk | unk | unk | unk
Old Building | 315 | Classroom | 404 | 26 |  | 611 | 13 | 13 |  | unk | unk | unk | unk
Old Building | 401 | Classroom | 194 | 12 |  | 562 | 12 | 12 |  | unk | unk | unk | unk
Old Building | 402 | Classroom | 588 | 39 |  | 924 | 20 | 20 |  | unk | unk | unk | unk
Old Building | 404 | Classroom | 337 | 22 |  | 936 | 21 | 21 |  | unk | unk | unk | unk
Old Building | 406 | Classroom | 590 | 39 |  | 658 | 14 | 14 |  | unk | unk | unk | unk
Old Building | 407 | Classroom | 0 | 0 |  | 750 | 17 | 0 |  | unk | unk | unk | unk
Old Building | 408 | Classroom | 0 | 0 |  | 677 | 15 | 0 |  | unk | unk | unk | unk
Old Building | 409 | Classroom | 0 | 0 |  | 659 | 14 | 0 |  | unk | unk | unk | unk
Old Building | 410 | Classroom | 737 | 49 |  | 539 | 12 | 12 |  | unk | unk | unk | unk
Old Building | 412 | Classroom | 956 | 63 |  | 935 | 21 | 21 |  | unk | unk | unk | unk
Old Building | 413 | Classroom | 349 | 23 |  | 460 | 10 | 10 |  | unk | unk | unk | unk
Old Building | 414 | Classroom | 446 | 29 |  | 462 | 10 | 10 |  | unk | unk | unk | unk
Old Building | 415 | Classroom | 600 | 40 |  | 601 | 13 | 13 |  | unk | unk | unk | unk
Old Building | 501 | Classroom | 0 | 0 |  | 583 | 13 | 0 |  | unk | unk | unk | unk
Old Building | 505 | Classroom | 1040 | 69 |  | 701 | 15 | 15 |  | unk | unk | unk | unk
Old Building | 506 | Classroom | 0 | 0 |  | 110 | 2 | 0 |  | unk | unk | unk | unk
Old Building | 510 | Classroom | 595 | 39 |  | 652 | 14 | 14 |  | unk | unk | unk | unk
Old Building | 511 | Classroom |  | 0 | Yes | 917 | 20 |  |  | unk | unk | unk | unk
Old Building | 512 | Classroom | 0 | 0 |  | 734 | 16 | 0 |  | unk | unk | unk | unk
Old Building | 513 | Classroom | 708 | 47 |  | 745 | 16 | 16 |  | unk | unk | unk | unk
Old Building | 601 | Classroom | 352 | 23 |  | 562 | 12 | 12 |  | unk | unk | unk | unk
Old Building | 602 | Classroom | 838 | 55 |  | 935 | 21 | 21 |  | unk | unk | unk | unk
Old Building | 603 | Classroom | 1066 | 71 |  | 929 | 21 | 21 |  | unk | unk | unk | unk
Old Building | 604 | Classroom | 604 | 40 |  | 884 | 20 | 20 |  | unk | unk | unk | unk
Old Building | 605 | Classroom | 555 | 37 |  | 964 | 21 | 21 |  | unk | unk | unk | unk
Old Building | 607 | Classroom | 733 | 48 |  | 930 | 21 | 21 |  | unk | unk | unk | unk
Old Building | 609 | Classroom | 350 | 23 |  | 498 | 11 | 11 |  | unk | unk | unk | unk
Old Building | 610 | Classroom | 1042 | 69 |  | 939 | 21 | 21 |  | unk | unk | unk | unk
Old Building | 611 | Classroom | 944 | 62 |  | 943 | 21 | 21 |  | unk | unk | unk | unk
Old Building | 612 | Classroom | 357 | 23 |  | 598 | 13 | 13 |  | unk | unk | unk | unk
Old Building | 613 | Classroom | 312 | 20 |  | 696 | 15 | 15 |  | unk | unk | unk | unk
Old Building | 614 | Classroom | 0 | 0 |  | 823 | 18 | 0 |  | unk | unk | unk | unk
Old Building | 615 | Classroom | 411 | 27 |  | 1008 | 22 | 22 |  | unk | unk | unk | unk
Old Building | 616 | Classroom | 1153 | 76 |  | 901 | 20 | 20 |  | unk | unk | unk | unk
Old Building | 617 | Classroom | 0 | 0 |  | 899 | 20 | 0 |  | unk | unk | unk | unk
Old Building | B1 A | Wood Shop | 475 | 31 |  | 2780 | 63 | 31 |  | unk | unk | unk | unk
Old Building | B2 A | Classroom | 499 | 33 |  | 967 | 21 | 21 |  | unk | unk | unk | unk
Old Building | - | Auditorium | 1222 | 81 |  | 4005 | 91 | 81 |  | unk | unk | unk | unk
Old Building | - | 3rd Flr. Gym | 2212 | 147 |  | 3295 | 74 | 74 |  | unk | unk | unk | unk
Old Building | - | 3rd Flr.Gym Locker Room | 3013 | 200 |  | 1903 | 43 | 43 |  | unk | unk | unk | unk
Old Building | - | Stage | 532 | 35 |  | 993 | 22 | 22 |  | unk | unk | unk | unk
Old Building | - | 1st Floor N Corridor | 301 | 20 |  | 160 | 3 | 3 |  | unk | unk | unk | unk
Old Building | - | 1st Floor E Corridor | 536 | 35 |  | 160 | 3 | 3 |  | unk | unk | unk | unk
Old Building | - | 1st Floor S Corridor | 427 | 28 |  | 2120 | 48 | 28 |  | unk | unk | unk | unk
Old Building | - | 1st Floor W Corridor | 382 | 25 |  | 160 | 3 | 3 |  | unk | unk | unk | unk
Old Building | - | 2nd Floor S Corridor | 438 | 29 |  | 2120 | 48 | 29 |  | unk | unk | unk | unk
Old Building | - | 2nd Floor W Corridor | 465 | 31 |  | 160 | 3 | 3 |  | unk | unk | unk | unk
Old Building | - | 2nd Floor N Corridor | 711 | 47 |  | 2120 | 48 | 47 |  | unk | unk | unk | unk
Old Building | - | 2nd Floor E Corridor | 720 | 48 |  | 160 | 3 | 3 |  | unk | unk | unk | unk
Old Building | - | 3rd Floor E Corridor | 504 | 33 |  |  | 0 | 0 |  | unk | unk | unk | unk
Old Building | - | 3rd Floor N Corridor | 619 | 41 |  | 2120 | 48 | 41 |  | unk | unk | unk | unk
Old Building | - | 3rd Floor W Corridor | 761 | 50 |  |  | 0 | 0 |  | unk | unk | unk | unk
Old Building | - | 3rd Floor S Corridor | 569 | 37 |  | 2120 | 48 | 37 |  | unk | unk | unk | unk
Old Building | - | 4th Floor N Corridor | 502 | 33 |  | 2120 | 48 | 33 |  | unk | unk | unk | unk
Old Building | - | 4th Floor E Corridor | 633 | 42 |  |  | 0 | 0 |  | unk | unk | unk | unk
Old Building | - | 4th Floor S Corridor | 0 | 0 |  | 2120 | 48 | 0 |  | unk | unk | unk | unk
Old Building | - | 4th Floor W Corridor | 0 | 0 |  |  | 0 | 0 |  | unk | unk | unk | unk
Old Building | - | 5th Floor N Corridor | 593 | 39 |  | 2120 | 48 | 39 |  | unk | unk | unk | unk
Old Building | - | 5th Floor Library | 1677 | 111 |  | 2115 | 48 | 48 |  | unk | unk | unk | unk
Old Building | - | 6th Floor S Corridor | 683 | 45 |  | 2120 | 48 | 45 |  | unk | unk | unk | unk
Old Building | - | 6th Floor W Corridor | 918 | 61 |  |  | 0 | 0 |  | unk | unk | unk | unk
Old Building | - | 6th Floor N Corridor | 530 | 35 |  | 2120 | 48 | 35 |  | unk | unk | unk | unk
Old Building | - | 6th Floor E Corridor | 0 | 0 |  |  | 0 | 0 |  | unk | unk | unk | unk
Old Building | - | Café | 1559 | 103 |  | 734 | 16 | 16 |  | unk | unk | unk | unk
New Building | 120 | Auto Shop | 1016 | 67 |  | 2981 | 67 | 67 |  | unk | unk | unk | unk
New Building | 124 | Auto Shop | 8220 | 548 |  | 4344 | 98 | 98 |  | unk | unk | unk | unk
New Building | 220-221 | Electrical Shop | 0 | 0 |  | 1973 | 44 | 0 |  | unk | unk | unk | unk
New Building | 224-223 | Shop | 2067 | 137 |  | 1150 | 26 | 26 |  | unk | unk | unk | unk
New Building | 225-226 | Shop | 2858 | 190 |  | 3743 | 85 | 85 |  | unk | unk | unk | unk
New Building | 324-323 | 324-323 | 877 | 58 |  | 2781 | 63 | 58 |  | unk | unk | unk | unk
New Building | 326-325 | 326-325 | 1135 | 75 |  | 2395 | 54 | 54 |  | unk | unk | unk | unk
New Building | 420 | 420 | 0 | 0 |  | 1250 | 28 | 0 |  | unk | unk | unk | unk
New Building | 421 | 421 | 0 | 0 |  | 1873 | 42 | 0 |  | unk | unk | unk | unk
New Building | 423 | 423 | 487 | 32 |  | 1693 | 38 | 32 |  | unk | unk | unk | unk
New Building | 426 | 426 Plumbing Shop | 1678 | 111 |  | 1265 | 28 | 28 |  | unk | unk | unk | unk
New Building | 427-426 | 427-426 | 0 | 0 |  | 1583 | 35 | 0 |  | unk | unk | unk | unk
New Building | - | Gym | 958 | 63 |  | 7556 | 171 | 63 |  | unk | unk | unk | unk
New Building | - | Gym Locker Rm. | 0 | 0 |  | 5738 | 130 | 0 |  | unk | unk | unk | unk
New Building | 321 | Nursing | 614 | 40 |  | 1898 | 43 | 40 |  | unk | unk | unk | unk
New Building | - | Weld Shop | 2329 | 155 |  | 625 | 14 | 14 |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-07 | [8 empty] | unk | unk | unk | unk
School: | Julia R. Masterman Laboratory and Demonstration High School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
8 | Music Room |  | 0 |  | 630 | 14 | 0 |  | 5040 | unk | unk | unk | unk
9 | Classroom | 0 | 0 |  | 874 | 19 | 0 |  | 6992 | 0 | 0 | 0 | 0
11 | Classroom | 0 | 0 |  | 825 | 18 | 0 | AHU Inoperable | 6600 | 0 | 0 | 0 | 0
11A | Classroom | 0 | 0 |  | 368 | 8 | 0 | AHU Inoperable | 2944 | 0 | 0 | 0 | 0
12 | Classroom | 0 | 0 |  | 832 | 18 | 0 | AHU Inoperable | 6656 | 0 | 0 | 0 | 0
14 | Art Room |  | 0 |  | 1023 | 23 | 0 | AHU Inoperable | 8184 | unk | unk | unk | unk
15 | Classroom | 0 | 0 |  | 1148 | 26 | 0 |  | 9184 | 0 | 0 | 0 | 0
101 | Classroom | 0 | 0 | Yes | 704 | 16 | 16 | AHU Inoperable | 5632 | 0 | 0 | 20 | 3
102 | Music Room | 0 | 0 |  | 836 | 19 | 0 | AHU Inoperable | 6688 | 0 | 0 | 0 | 0
103 | Classroom | 0 | 0 |  | 638 | 14 | 0 | AHU Inoperable | 5104 | 0 | 0 | 0 | 0
104 | Classroom | 0 | 0 |  | 660 | 15 | 0 | AHU Inoperable | 5280 | 0 | 0 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 704 | 16 | 16 | AHU Inoperable | 5632 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0 | 0 | 0
203 | Classroom | 0 | 0 | Yes | 644 | 14 | 14 | AHU Inoperable | 5152 | 0 | 0 | 20 | 3
204 | Library | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0 | 0 | 0
205 | Fitness Storage | 0 | 0 | Yes | 690 | 15 | 15 | AHU Inoperable | 5520 | 0 | 0 | 20 | 3
206 | Fitness Storage | 0 | 0 |  | 704 | 16 | 0 | AHU Inoperable | 5632 | 0 | 0 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 660 | 15 | 15 | AHU Inoperable | 5280 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0 | 0 | 0
209 | Classroom | 0 | 0 |  | 187 | 4 | 0 | AHU Inoperable | 1496 | 0 | 0 | 0 | 0
210 | Classroom | 0 | 0 |  | 187 | 4 | 0 | AHU Inoperable | 1496 | 0 | 0 | 0 | 0
211 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | AHU Inoperable | 5456 | 0 | 0 | 20 | 3
212 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0 | 0 | 0
213 | Classroom | 0 | 0 |  | 374 | 8 | 0 | AHU Inoperable | 2992 | 0 | 0 | 0 | 0
214 | Classroom | 0 | 0 |  | 374 | 8 | 0 | AHU Inoperable | 2992 | 0 | 0 | 0 | 0
218 | Main Office |  | 0 | Yes | 210 | 4 | 4 | AHU Inoperable | 1680 | unk | unk | 20 | 3
301 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 |  | 5456 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0 | 0 | 0
303 | Classroom | 0 | 0 |  | 660 | 15 | 0 | AHU Inoperable | 5280 | 0 | 0 | 0 | 0
304 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0 | 0 | 0
305 | Classroom | 0 | 0 | Yes | 638 | 14 | 14 | AHU Inoperable | 5104 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 |  | 144 | 3 | 0 | AHU Inoperable | 1152 | 0 | 0 | 0 | 0
307 | Classroom |  | 0 |  | 726 | 16 | 0 | AHU Inoperable | 5808 | unk | unk | unk | unk
307A | Office |  | 0 |  | 264 | 6 | 0 |  | 2112 | unk | unk | unk | unk
308 | Classroom | 0 | 0 |  | 1210 | 27 | 0 |  | 9680 | 0 | 0 | 0 | 0
309 | Office | 0 | 0 |  | 300 | 6 | 0 | AHU Inoperable | 2400 | 0 | 0 | 0 | 0
310 | Classroom | 0 | 0 |  | 96 | 2 | 0 | AHU Inoperable | 768 | 0 | 0 | 0 | 0
311 | Classroom | 0 | 0 |  | 682 | 15 | 0 | AHU Inoperable | 5456 | 0 | 0 | 0 | 0
312 | Classroom | 0 | 0 |  | 1078 | 24 | 0 | AHU Inoperable | 8624 | 0 | 0 | 0 | 0
313 | Room |  | 0 |  | 374 | 8 | 0 | AHU Inoperable | 2992 | unk | unk | unk | unk
402 | Classroom | 0 | 0 |  | 880 | 20 | 0 |  | 7040 | 0 | 0 | 0 | 0
404 | Classroom | 0 | 0 |  | 704 | 16 | 0 | AHU Inoperable | 5632 | 0 | 0 | 0 | 0
406 | Classroom | 0 | 0 |  | 504 | 11 | 0 | AHU Inoperable | 4032 | 0 | 0 | 0 | 0
408 | Classroom | 0 | 0 |  | 672 | 15 | 0 | AHU Inoperable | 5376 | 0 | 0 | 0 | 0
410 | Classroom | 0 | 0 |  | 1008 | 22 | 0 | AHU Inoperable | 8064 | 0 | 0 | 0 | 0
412 | Office | 0 | 0 |  | 205 | 4 | 0 | AHU Inoperable | 1640 | 0 | 0 | 0 | 0
502 | Classroom | 0 | 0 |  | 880 | 20 | 0 | AHU Inoperable | 7040 | 0 | 0 | 0 | 0
506 | Classroom | 0 | 0 |  | 690 | 15 | 0 | AHU Inoperable | 5520 | 0 | 0 | 0 | 0
- | Game Room |  | 0 |  | 790 | 17 | 0 | AHU Inoperable | 6320 | unk | unk | unk | unk
- | Auditorium | 0 | 0 |  | 5850 | 132 | 0 |  | 46800 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 |  | 3600 | 81 | 0 | AHU Inoperable | 28800 | 0 | 0 | 0 | 0
- | Counselor's Office |  | 0 |  | 110 | 2 | 0 | AHU Inoperable | 880 | unk | unk | unk | unk
- | Counselor's Office |  | 0 |  | 110 | 2 | 0 |  | 880 | unk | unk | unk | unk
- | Faculty Cafeteria | 0 | 0 |  | 726 | 16 | 0 |  | 5808 | 0 | 0 | 0 | 0
- | Gym | 0 | 0 | Yes | 6208 | 141 | 141 | AHU Inoperable | 49664 | 0 | 0 | 20 | 3
- | Boy's Locker Room |  | 0 |  | 580 | 13 | 0 |  | 4640 | unk | unk | unk | unk
- | Girl's Locker Room |  | 0 |  | 209 | 4 | 0 |  | 1672 | unk | unk | unk | unk
- | Health room |  | 0 |  | 100 | 2 | 0 |  | 800 | unk | unk | unk | unk
- | Kitchen | 0 | 0 |  | 828 | 18 | 0 | AHU Inoperable | 6624 | 0 | 0 | 0 | 0
- | LIbrary Room |  | 0 |  | 620 | 14 | 0 |  | 4960 | unk | unk | unk | unk
- | Library Office |  | 0 |  | 231 | 5 | 0 |  | 1848 | unk | unk | unk | unk
- | Library A |  | 0 |  | 506 | 11 | 0 |  | 4048 | unk | unk | unk | unk
- | Library B |  | 0 |  | 651 | 14 | 0 |  | 5208 | unk | unk | unk | unk
- | Library C |  | 0 |  | 230 | 5 | 0 |  | 1840 | unk | unk | unk | unk
- | Nurse Office | 0 | 0 | Yes | 170 | 3 | 3 | AHU Inoperable | 1360 | 0 | 0 | 20 | 3
| Nurse Examining |  | 0 | Yes | 100 | 2 | 2 |  | 800 | unk | unk | 20 | 3
| Nurse Roster Room |  | 0 | Yes | 288 | 6 | 6 |  | 2304 | unk | unk | 20 | 3
- | Robotics | 0 | 0 |  | 420 | 9 | 0 | AHU Inoperable | 3360 | 0 | 0 | 0 | 0
- | Science Office |  | 0 |  | 187 | 4 | 0 |  | 1496 | unk | unk | unk | unk
- | Principal 's Office |  | 0 |  | 210 | 4 | 0 |  | 1680 | unk | unk | unk | unk
- | Assant Principal's Office |  | 0 |  | 140 | 3 | 0 |  | 1120 | unk | unk | unk | unk
- | Operations Office |  | 0 |  | 56 | 1 | 0 |  | 448 | unk | unk | unk | unk
- | Office Waiting Area |  | 0 |  | 275 | 6 | 0 |  | 2200 | unk | unk | unk | unk
- | Roster Office |  | 0 |  | 136 | 3 | 0 |  | 1088 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Mayfair Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Part 2 | Devine Part 3 | [6 empty] | unk | unk | unk | unk
Vendor: | Capital | Capital Update | Capital Part 2 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 207 | 13 |  | 696 | 15 | 13 | Unit Ventilator | 5568 | 2.2306 | 1 | 2.2306 | 1
101 | Classroom | 201 | 13 |  | 696 | 15 | 13 | Unit Ventilator | 5568 | 2.1659 | 1 | 2.1659 | 1
102 | Classroom | 197 | 13 |  | 598 | 13 | 13 | Unit Ventilator | 4784 | 2.4707 | 1 | 2.4707 | 1
103 | Classroom | 189 | 12 |  | 720 | 16 | 12 | Unit Ventilator | 5760 | 1.9688 | 1 | 1.9688 | 1
104 | Classroom | 355 | 23 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.8587 | 1 | 3.8587 | 1
105 | Classroom | 231 | 15 |  | 624 | 14 | 14 | Unit Ventilator | 4992 | 2.7764 | 1 | 2.7764 | 1
106 | Classroom | 237 | 15 |  | 720 | 16 | 15 | Unit Ventilator | 5760 | 2.4688 | 1 | 2.4688 | 1
107 | Classroom | 458 | 30 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 4.7708 | 2 | 4.7708 | 2
108 | Classroom | 115 | 7 |  | 600 | 13 | 7 | Unit Ventilator | 4800 | 1.4375 | 1 | 1.4375 | 1
109 | Classroom | 186 | 12 |  | 744 | 16 | 12 | Unit Ventilator | 5952 | 1.875 | 1 | 1.875 | 1
110 | Classroom | 418 | 27 |  | 696 | 15 | 15 | Unit Ventilator | 5568 | 4.5043 | 2 | 4.5043 | 2
111 | Classroom | 202 | 13 |  | 624 | 14 | 13 | Unit Ventilator | 4992 | 2.4279 | 1 | 2.4279 | 1
112 | Classroom | 461 | 30 |  | 1032 | 23 | 23 | Unit Ventilator | 8256 | 3.3503 | 1 | 3.3503 | 1
113 | Classroom | 211 | 14 |  | 720 | 16 | 14 | Unit Ventilator | 5760 | 2.1979 | 1 | 2.1979 | 1
114 | Classroom | 377 | 25 |  | 644 | 14 | 14 | Unit Ventilator | 5152 | 4.3905 | 2 | 4.3905 | 2
115 | Classroom | 271 | 18 |  | 620 | 14 | 14 | Unit Ventilator | 4960 | 3.2782 | 1 | 3.2782 | 1
116 | Classroom | 395 | 26 |  | 989 | 22 | 22 | Unit Ventilator | 7912 | 2.9954 | 1 | 2.9954 | 1
118 | Classroom | 384 | 25 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.1739 | 2 | 4.1739 | 2
119 | Classroom | 320 | 21 |  | 624 | 14 | 14 | Unit Ventilator | 4992 | 3.8462 | 1 | 3.8462 | 1
120 | Classroom | 311 | 20 |  | 1610 | 36 | 20 | Unit Ventilator | 12880 | 1.4488 | 1 | 1.4488 | 1
200 | Classroom |  | 0 | Yes | 205 | 4 | 4 |  | 1640 | unk | unk | 20 | 3
201 | Classroom | 286 | 19 |  | 696 | 15 | 15 | Unit Ventilator | 5568 | 3.0819 | 1 | 3.0819 | 1
202 | Classroom | 560 | 37 |  | 696 | 15 | 15 | Unit Ventilator | 5568 | 6.0345 | 2 | 6.0345 | 2
203 | Classroom | 381 | 25 |  | 725 | 16 | 16 | Unit Ventilator | 5800 | 3.9414 | 1 | 3.9414 | 1
204 | Classroom | 323 | 21 |  | 884 | 20 | 20 | Unit Ventilator | 7072 | 2.7404 | 1 | 2.7404 | 1
205 | Classroom | 271 | 18 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.6058 | 1 | 2.6058 | 1
206 | Classroom | 316 | 21 |  | 806 | 18 | 18 | Unit Ventilator | 6448 | 2.9404 | 1 | 2.9404 | 1
207 | Classroom | 295 | 19 |  | 806 | 18 | 18 | Unit Ventilator | 6448 | 2.745 | 1 | 2.745 | 1
207A | Asst. Principal Office | 0 | 0 | Yes | 293 | 6 | 6 | Unit Ventilator | 2344 | 0 | 0 | 20 | 3
208 | Classroom | 305 | 20 |  | 528 | 12 | 12 | Unit Ventilator | 4224 | 4.3324 | 2 | 4.3324 | 2
209 | Classroom | 560 | 37 |  | 884 | 20 | 20 | Unit Ventilator | 7072 | 4.7511 | 2 | 4.7511 | 2
210 | Classroom | 290 | 19 |  | 1118 | 25 | 19 | Unit Ventilator | 8944 | 1.9454 | 1 | 1.9454 | 1
211 | Classroom | 307 | 20 |  | 648 | 14 | 14 | Unit Ventilator | 5184 | 3.5532 | 1 | 3.5532 | 1
212 | Classroom | 483 | 32 |  | 665 | 15 | 15 | Unit Ventilator | 5320 | 5.4474 | 2 | 5.4474 | 2
213 | Classroom | 590 | 39 |  | 806 | 18 | 18 | Unit Ventilator | 6448 | 5.4901 | 2 | 5.4901 | 2
214 | Classroom | 300 | 20 |  | 806 | 18 | 18 | Unit Ventilator | 6448 | 2.7916 | 1 | 2.7916 | 1
215 | Classroom | 294 | 19 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 3.0288 | 1 | 3.0288 | 1
216 | Classroom | 317 | 21 |  | 648 | 14 | 14 | Unit Ventilator | 5184 | 3.669 | 1 | 3.669 | 1
217 | Classroom | 350 | 23 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 3.3568 | 1 | 3.3568 | 1
218 | Classroom | 271 | 18 |  | 621 | 14 | 14 | Unit Ventilator | 4968 | 3.2729 | 1 | 3.2729 | 1
219 | Classroom | 137 | 9 |  | 648 | 14 | 9 | Unit Ventilator | 5184 | 1.5856 | 1 | 1.5856 | 1
220 | Classroom | 235 | 15 |  | 648 | 14 | 14 | Unit Ventilator | 5184 | 2.7199 | 1 | 2.7199 | 1
221 | Classroom | 325 | 21 |  | 744 | 16 | 16 | Unit Ventilator | 5952 | 3.2762 | 1 | 3.2762 | 1
222 | Classroom | 180 | 12 |  | 648 | 14 | 12 | Unit Ventilator | 5184 | 2.0833 | 1 | 2.0833 | 1
301 | Classroom | 325 | 21 |  | 720 | 16 | 16 | ERU | 5760 | 3.3854 | 1 | 3.3854 | 1
302 | Classroom | 304 | 20 |  | 720 | 16 | 16 | ERU | 5760 | 3.1667 | 1 | 3.1667 | 1
303 | Classroom | 270 | 18 |  | 720 | 16 | 16 | ERU | 5760 | 2.8125 | 1 | 2.8125 | 1
304 | Classroom | 435 | 29 |  | 720 | 16 | 16 | ERU | 5760 | 4.5312 | 2 | 4.5312 | 2
305 | Classroom | 453 | 30 |  | 720 | 16 | 16 | ERU | 5760 | 4.7188 | 2 | 4.7188 | 2
306 | Classroom | 480 | 32 |  | 720 | 16 | 16 | ERU | 5760 | 5 | 2 | 5 | 2
401 | Classroom | 320 | 21 |  | 720 | 16 | 16 | ERU | 5760 | 3.3333 | 1 | 3.3333 | 1
402 | Classroom | 282 | 18 |  | 720 | 16 | 16 | ERU | 5760 | 2.9375 | 1 | 2.9375 | 1
403 | Classroom | 551 | 36 |  | 720 | 16 | 16 | ERU | 5760 | 5.7396 | 2 | 5.7396 | 2
404 | Classroom | 412 | 27 |  | 720 | 16 | 16 | ERU | 5760 | 4.2917 | 2 | 4.2917 | 2
405 | Classroom | 412 | 27 |  | 720 | 16 | 16 | ERU | 5760 | 4.2917 | 2 | 4.2917 | 2
406 | Classroom | 406 | 27 |  | 720 | 16 | 16 | ERU | 5760 | 4.2292 | 2 | 4.2292 | 2
510 | Classroom | 282 | 18 |  | 754 | 17 | 17 | ERU | 6032 | 2.805 | 1 | 2.805 | 1
511 | Classroom | 430 | 28 |  | 754 | 17 | 17 | ERU | 6032 | 4.2772 | 2 | 4.2772 | 2
512 | Classroom | 447 | 29 |  | 754 | 17 | 17 | ERU | 6032 | 4.4463 | 2 | 4.4463 | 2
513 | Classroom | 543 | 36 |  | 754 | 17 | 17 | ERU | 6032 | 5.4012 | 2 | 5.4012 | 2
515 | Classroom | 652 | 43 |  | 754 | 17 | 17 | ERU | 6032 | 6.4854 | 2 | 6.4854 | 2
516 | Classroom | 519 | 34 |  | 754 | 17 | 17 | ERU | 6032 | 5.1625 | 2 | 5.1625 | 2
517 | Classroom | 605 | 40 |  | 754 | 17 | 17 | ERU | 6032 | 6.0179 | 2 | 6.0179 | 2
520 | Classroom | 500 | 33 |  | 754 | 17 | 17 | ERU | 6032 | 4.9735 | 2 | 4.9735 | 2
521 | Classroom | 548 | 36 |  | 754 | 17 | 17 | ERU | 6032 | 5.4509 | 2 | 5.4509 | 2
522 | Classroom | 530 | 35 |  | 754 | 17 | 17 | ERU | 6032 | 5.2719 | 2 | 5.2719 | 2
523 | Classroom | 509 | 33 |  | 754 | 17 | 17 | ERU | 6032 | 5.063 | 2 | 5.063 | 2
525 | Classroom | 676 | 45 |  | 754 | 17 | 17 | ERU | 6032 | 6.7241 | 2 | 6.7241 | 2
526 | Classroom | 646 | 43 |  | 754 | 17 | 17 | ERU | 6032 | 6.4257 | 2 | 6.4257 | 2
527 | Classroom | 568 | 37 |  | 774 | 17 | 17 | ERU | 6192 | 5.5039 | 2 | 5.5039 | 2
- | Main Office |  | 0 | Yes | 493 | 11 | 11 |  | 3944 | unk | unk | 20 | 3
- | Counselor Office |  | 0 | Yes | 126 | 2 | 2 |  | 1008 | unk | unk | 20 | 3
- | Counselor Office |  | 0 | Yes | 231 | 5 | 5 |  | 1848 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 196 | 4 | 4 |  | 1568 | unk | unk | 20 | 3
- | Special Education |  | 0 | Yes | 275 | 6 | 6 |  | 2200 | unk | unk | 20 | 3
- | Conference Room |  | 0 | Yes | 135 | 3 | 3 |  | 1080 | unk | unk | 20 | 3
- | Faculty Room |  | 0 | Yes | 171 | 3 | 3 |  | 1368 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 372 | 8 | 8 |  | 2976 | unk | unk | 20 | 3
- | Asst. Principal 1 |  | 0 | Yes | 86 | 1 | 1 |  | 688 | unk | unk | 20 | 3
- | Asst. Principal 2 |  | 0 | Yes | 97 | 2 | 2 |  | 776 | unk | unk | 20 | 3
- | Auditorium |  | 0 |  | 4920 | 111 | 0 | AHU | 39360 | unk | unk | unk | unk
| Auditorium Room 1 |  | 0 | Yes | 263 | 5 | 5 |  | 2104 | unk | unk | 20 | 3
| Auditorium Room 2 |  | 0 | Yes | 254 | 5 | 5 |  | 2032 | unk | unk | 20 | 3
Music 1 | Room |  | 0 | Yes | 354 | 8 | 8 |  | 2832 | unk | unk | 20 | 3
Music 2 | Room |  | 0 | Yes | 711 | 16 | 16 |  | 5688 | unk | unk | 20 | 3
- | Cafeteria | 998 | 66 |  | 3257 | 74 | 66 | RTU | 26056 | 2.2981 | 1 | 2.2981 | 1
- | Gym |  | 0 | Yes | 3982 | 90 | 90 | AHU | 31856 | unk | unk | 20 | 3
School Police | Office |  | 0 | Yes | 54 | 1 | 1 |  | 432 | unk | unk | 20 | 3
- | Nurse Office | 292 | 19 |  | 372 | 8 | 8 | Unit Ventilator | 2976 | 5.8871 | 2 | 5.8871 | 2
1 | Mobile Classroom | 326 | 21 |  | 594 | 13 | 13 | AHU | 4752 | 4.1162 | 2 | 4.1162 | 2
2 | Mobile Classroom | 328 | 21 |  | 594 | 13 | 13 | AHU | 4752 | 4.1414 | 2 | 4.1414 | 2
3 | Mobile Classroom | 644 | 42 |  | 594 | 13 | 13 | AHU | 4752 | 8.1313 | 2 | 8.1313 | 2
4 | Mobile Classroom | 451 | 30 |  | 594 | 13 | 13 | AHU | 4752 | 5.6944 | 2 | 5.6944 | 2
5 | Mobile Classroom | 580 | 38 |  | 594 | 13 | 13 | AHU | 4752 | 7.3232 | 2 | 7.3232 | 2
6 | Mobile Classroom | 438 | 29 |  | 594 | 13 | 13 | AHU | 4752 | 5.5303 | 2 | 5.5303 | 2
7 | Mobile Classroom | 414 | 27 |  | 594 | 13 | 13 | AHU | 4752 | 5.2273 | 2 | 5.2273 | 2
8 | Mobile Classroom | 574 | 38 |  | 594 | 13 | 13 | AHU | 4752 | 7.2475 | 2 | 7.2475 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-06 | [8 empty] | unk | unk | unk | unk
School: | General George A. McCall Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | 2nd Retest | 3rd Retest | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
0 | Classroom | 0 | 0 | Yes | 572 | 13 | 13 | N/A | 4576 | 0 | 0 | 20 | 3
1 | Classroom | 370 | 24 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 3.0032 | 1 | 3.0032 | 1
2 | Music Room | 453 | 30 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 4.064 | 2 | 4.064 | 2
4 | Classroom | 1631 | 108 |  | 660 | 15 | 15 | AHU | 5280 | 18.5341 | 3 | 18.5341 | 3
5 | Classroom | 478 | 31 |  | 1012 | 23 | 23 | AHU | 8096 | 3.5425 | 1 | 3.5425 | 1
6 | Classroom | 535 | 35 |  | 1100 | 25 | 25 | AHU | 8800 | 3.6477 | 1 | 3.6477 | 1
101 | Office | 0 | 0 | Yes | 276 | 6 | 6 | N/A | 2208 | 0 | 0 | 20 | 3
101A | Office | 182 | 12 | Yes | 440 | 10 | 10 | Unit Ventilator | 3520 | 3.1023 | 1 | 23.1023 | 3
102 | Classroom | 332 | 22 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.9785 | 1 | 2.9785 | 1
103 | Classroom | 283 | 18 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.4119 | 1 | 22.4119 | 3
105 | Classroom | 278 | 18 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.3693 | 1 | 22.3693 | 3
106 | Classroom | 340 | 22 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.7597 | 1 | 2.7597 | 1
107 | Classroom | 292 | 19 | Yes | 968 | 22 | 22 | Unit Ventilator | 7744 | 2.2624 | 1 | 22.2624 | 3
108 | Classroom | 303 | 20 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.7183 | 1 | 2.7183 | 1
109 | Classroom | 375 | 25 |  | 880 | 20 | 20 | Unit Ventilator | 7040 | 3.196 | 1 | 3.196 | 1
110 | Classroom | 0 | 0 | Yes | 220 | 5 | 5 | N/A | 1760 | 0 | 0 | 20 | 3
110A | Office | 336 | 22 |  | 440 | 10 | 10 | Unit Ventilator | 3520 | 5.7273 | 2 | 5.7273 | 2
209 | Classroom | 0 | 0 | Yes | 440 | 10 | 10 | Unit Ventilator | 3520 | 0 | 0 | 20 | 3
210 | Classroom | 273 | 18 | Yes | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.3267 | 1 | 22.3267 | 3
211 | Classroom | 293 | 19 | Yes | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.3782 | 1 | 22.3782 | 3
212 | Classroom | 294 | 19 |  | 880 | 20 | 19 | Unit Ventilator | 7040 | 2.5057 | 1 | 2.5057 | 1
213 | Classroom | 320 | 21 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.5974 | 1 | 2.5974 | 1
214 | Classroom | 376 | 25 |  | 880 | 20 | 20 | Unit Ventilator | 7040 | 3.2045 | 1 | 3.2045 | 1
216A | Office | 0 | 0 | Yes | 480 | 10 | 10 | N/A | 3840 | 0 | 0 | 20 | 3
217 | Classroom | 297 | 19 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.8125 | 1 | 2.8125 | 1
218 | Classroom | 309 | 20 |  | 924 | 21 | 20 | Unit Ventilator | 7392 | 2.5081 | 1 | 2.5081 | 1
219 | Classroom | 313 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.964 | 1 | 2.964 | 1
318 | Classroom | 172 | 11 | Yes | 748 | 17 | 17 | Unit Ventilator | 5984 | 1.7246 | 1 | 21.7246 | 3
319 | Classroom | 368 | 24 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.987 | 1 | 2.987 | 1
320 | Classroom | 401 | 26 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 3.5975 | 1 | 3.5975 | 1
321 | Classroom | 329 | 21 |  | 880 | 20 | 20 | Unit Ventilator | 7040 | 2.804 | 1 | 2.804 | 1
322 | Classroom | 292 | 19 |  | 924 | 21 | 19 | Unit Ventilator | 7392 | 2.3701 | 1 | 2.3701 | 1
323 | Classroom | 351 | 23 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.849 | 1 | 2.849 | 1
324 | Classroom | 284 | 18 |  | 880 | 20 | 18 | Unit Ventilator | 7040 | 2.4205 | 1 | 2.4205 | 1
325 | Classroom | 396 | 26 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 3.2143 | 1 | 3.2143 | 1
326 | Classroom | 309 | 20 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.7721 | 1 | 2.7721 | 1
327 | Classroom | 345 | 23 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 3.267 | 1 | 3.267 | 1
327A | Classroom | 261 | 17 |  | 484 | 11 | 11 | Unit Ventilator | 3872 | 4.0444 | 2 | 4.0444 | 2
- | Auditorium | 1451 | 96 |  | 4224 | 96 | 96 | AHU | 33792 | 2.5763 | 1 | 2.5763 | 1
- | Gym/Cafeteria | 1279 | 85 |  | 3740 | 85 | 85 | AHU | 29920 | 2.5648 | 1 | 2.5648 | 1
- | Main Office | 311 | 20 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 2.9451 | 1 | 2.9451 | 1
- | Library | 492 | 32 |  | 1584 | 36 | 32 | Unit Ventilator | 12672 | 2.3295 | 1 | 2.3295 | 1
- | Engineer Office | 0 | 0 |  | 432 | 9 | 0 | N/A | 3456 | 0 | 0 | 0 | 0
- | Gym Office | 0 | 0 |  | 110 | 2 | 0 | AHU | 880 | 0 | 0 | 0 | 0
- | Kitchen | 9 | 0 | Yes | 384 | 8 | 8 | AHU | 3072 | 0.17578 | 0 | 20.1758 | 3
- | Principals Office | 0 | 0 | Yes | 493 | 11 | 11 | AHU | 3944 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-13 | [8 empty] | unk | unk | unk | unk
School: | John F. McCloskey Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Part 2 | Part 3 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
2 | IMC |  | 0 | Yes | 1044 | 23 | 23 | Unit Ventilator | 8352 | unk | unk | 20 | 3
7 | Recovery. room |  | 0 | Yes | 180 | 4 | 4 | Convector | 1440 | unk | unk | 20 | 3
101 | Classroom | 229 | 15 |  | 936 | 21 | 15 | Unit Ventilator | 7488 | 1.8349 | 1 | 1.8349 | 1
102 | Classroom | 192 | 12 |  | 936 | 21 | 12 | Unit Ventilator | 7488 | 1.5385 | 1 | 1.5385 | 1
103 | Classroom | 394 | 26 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 3.1571 | 1 | 3.1571 | 1
104 | Classroom | 155 | 10 | Yes | 1056 | 24 | 24 | Unit Ventilator | 8448 | 1.1009 | 1 | 21.1009 | 3
105 | Classroom | 342 | 22 |  | 897 | 20 | 20 | Unit Ventilator | 7176 | 2.8595 | 1 | 2.8595 | 1
106 | Classroom | 203 | 13 |  | 936 | 21 | 13 | Unit Ventilator | 7488 | 1.6266 | 1 | 1.6266 | 1
107 | Classroom | 206 | 13 |  | 936 | 21 | 13 | Unit Ventilator | 7488 | 1.6506 | 1 | 1.6506 | 1
108 | Classroom | 390 | 26 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 3.125 | 1 | 3.125 | 1
109 | Classroom | 282 | 18 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 2.8736 | 1 | 2.8736 | 1
111 | Classroom | 356 | 23 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 3.6277 | 1 | 3.6277 | 1
113 | Classroom | 320 | 21 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 3.2609 | 1 | 3.2609 | 1
114 | Classroom | 319 | 21 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 3.2507 | 1 | 3.2507 | 1
201 | Classroom |  | 0 |  | 916 | 20 | 0 | Unit Ventilator | 7328 | unk | unk | unk | unk
202 | Classroom | 200 | 13 |  | 936 | 21 | 13 | Unit Ventilator | 7488 | 1.6026 | 1 | 1.6026 | 1
203 | Classroom | 194 | 12 |  | 936 | 21 | 12 | Unit Ventilator | 7488 | 1.5545 | 1 | 1.5545 | 1
204 | Classroom | 378 | 25 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 3.0288 | 1 | 3.0288 | 1
205 | Classroom | 342 | 22 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 2.7404 | 1 | 2.7404 | 1
206 | Classroom | 487 | 32 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 3.9022 | 1 | 3.9022 | 1
208 | Classroom | 346 | 23 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 2.7724 | 1 | 2.7724 | 1
209 | Classroom | 514 | 34 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 4.1186 | 2 | 4.1186 | 2
210 | Classroom | 247 | 16 |  | 936 | 21 | 16 | Unit Ventilator | 7488 | 1.9792 | 1 | 1.9792 | 1
211 | Classroom | 374 | 24 |  | 936 | 21 | 21 | Unit Ventilator | 7488 | 2.9968 | 1 | 2.9968 | 1
- | Auditorium |  | 0 |  | 2700 | 61 | 0 | AHU | 21600 | unk | unk | unk | unk
- | Computer Room | 40 | 2 |  | 1080 | 24 | 2 | Unit Ventilator | 8640 | 0.27778 | 0 | 0.27778 | 0
- | Gym |  | 0 | Yes | 3744 | 85 | 85 | AHU | 29952 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 338 | 7 | 7 | Convector | 2704 | unk | unk | 20 | 3
- | Prin. Office |  | 0 | Yes | 312 | 7 | 7 | Convector | 2496 | unk | unk | 20 | 3
- | Nurse. Office |  | 0 | Yes | 225 | 5 | 5 | Convector | 1800 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | Alexander K. McClure Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Retest | 2nd Retest | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
0 | Building Engineer | 0 | 0 |  |  | 0 | 0 | N/A |  | unk | unk | unk | unk
1 | Gym | 650 | 43 |  | 2486 | 56 | 43 | House Fan | 19888 | 1.961 | 1 | 1.961 | 1
6 | Art | 302 | 20 |  | 894 | 20 | 20 | House Fan | 7152 | 2.5336 | 1 | 2.5336 | 1
7 | Classroom | 559 | 37 |  | 839 | 19 | 19 | House Fan | 6712 | 4.997 | 2 | 4.997 | 2
11 | Classroom | 523 | 34 |  | 821 | 18 | 18 | House Fan | 6568 | 4.7777 | 2 | 4.7777 | 2
101 | Classroom | 603 | 40 |  | 887 | 20 | 20 | House Fan | 7096 | 5.0986 | 2 | 5.0986 | 2
106 | Classroom | 419 | 27 |  | 927 | 21 | 21 | House Fan | 7416 | 3.39 | 1 | 3.39 | 1
106A | Asst. Principal | 0 | 0 | Yes | 104 | 2 | 2 | House Fan | 832 | 0 | 0 | 20 | 3
107 | Classroom | 505 | 33 |  | 753 | 17 | 17 | House Fan | 6024 | 5.0299 | 2 | 5.0299 | 2
108 | Classroom | 329 | 21 |  | 849 | 19 | 19 | House Fan | 6792 | 2.9064 | 1 | 2.9064 | 1
109 | Classroom | 454 | 30 |  | 791 | 17 | 17 | House Fan | 6328 | 4.3047 | 2 | 4.3047 | 2
110 | Classroom | 603 | 40 |  | 725 | 16 | 16 | House Fan | 5800 | 6.2379 | 2 | 6.2379 | 2
111 | Classroom | 537 | 35 |  | 699 | 15 | 15 | House Fan | 5592 | 5.7618 | 2 | 5.7618 | 2
201 | Classroom | 585 | 39 |  | 847 | 19 | 19 | House Fan | 6776 | 5.18 | 2 | 5.18 | 2
202 | Classroom | 597 | 39 |  | 883 | 20 | 20 | House Fan | 7064 | 5.0708 | 2 | 5.0708 | 2
203 | Classroom | 423 | 28 |  | 903 | 20 | 20 | House Fan | 7224 | 3.5133 | 1 | 3.5133 | 1
204 | Classroom | 461 | 30 |  | 887 | 20 | 20 | House Fan | 7096 | 3.898 | 1 | 3.898 | 1
205 | Classroom | 482 | 32 |  | 945 | 21 | 21 | House Fan | 7560 | 3.8254 | 1 | 3.8254 | 1
206 | Library | 431 | 28 |  | 890 | 20 | 20 | House Fan | 7120 | 3.632 | 1 | 3.632 | 1
206A | Nurse Office | 0 | 0 |  | 194 | 4 | 0 | N/A | 1552 | 0 | 0 | 0 | 0
206B | Nurse Exam | 0 | 0 | Yes | 362 | 8 | 8 | House Fan | 2896 | 0 | 0 | 20 | 3
207 | Classroom | 442 | 29 |  | 869 | 19 | 19 | House Fan | 6952 | 3.8147 | 1 | 3.8147 | 1
208 | Classroom | 309 | 20 |  | 812 | 18 | 18 | House Fan | 6496 | 2.8541 | 1 | 2.8541 | 1
209 | Classroom | 412 | 27 |  | 823 | 18 | 18 | House Fan | 6584 | 3.7546 | 1 | 3.7546 | 1
210 | Classroom | 602 | 40 |  | 714 | 16 | 16 | House Fan | 5712 | 6.3235 | 2 | 6.3235 | 2
211 | Classroom | 595 | 39 |  | 740 | 16 | 16 | House Fan | 5920 | 6.0304 | 2 | 6.0304 | 2
301 | Classroom | 559 | 37 |  | 882 | 20 | 20 | House Fan | 7056 | 4.7534 | 2 | 4.7534 | 2
302 | Classroom | 501 | 33 |  | 902 | 20 | 20 | House Fan | 7216 | 4.1657 | 2 | 4.1657 | 2
303 | Classroom | 377 | 25 |  | 900 | 20 | 20 | House Fan | 7200 | 3.1417 | 1 | 3.1417 | 1
304 | Classroom | 483 | 32 |  | 875 | 19 | 19 | House Fan | 7000 | 4.14 | 2 | 4.14 | 2
305 | Classroom | 469 | 31 |  | 910 | 20 | 20 | House Fan | 7280 | 3.8654 | 1 | 3.8654 | 1
306 | Classroom | 402 | 26 |  | 894 | 20 | 20 | House Fan | 7152 | 3.3725 | 1 | 3.3725 | 1
306A | Office | 0 | 0 | Yes | 185 | 4 | 4 | House Fan | 1480 | 0 | 0 | 20 | 3
307 | Classroom | 470 | 31 |  | 932 | 21 | 21 | House Fan | 7456 | 3.7822 | 1 | 3.7822 | 1
308 | Classroom | 301 | 20 |  | 815 | 18 | 18 | House Fan | 6520 | 2.7699 | 1 | 2.7699 | 1
309 | Classroom | 313 | 20 |  | 851 | 19 | 19 | House Fan | 6808 | 2.7585 | 1 | 2.7585 | 1
310 | Classroom | 396 | 26 |  | 726 | 16 | 16 | House Fan | 5808 | 4.0909 | 2 | 4.0909 | 2
311 | Classroom | 406 | 27 |  | 732 | 16 | 16 | House Fan | 5856 | 4.1598 | 2 | 4.1598 | 2
312 | Classroom | 0 | 0 | Yes | 435 | 9 | 9 | N/A | 3480 | 0 | 0 | 20 | 3
- | 4th Floor Office N | 0 | 0 |  |  | 0 | 0 | N/A |  | unk | unk | unk | unk
- | 4th Floor Office S | 0 | 0 |  |  | 0 | 0 | N/A |  | unk | unk | unk | unk
- | Cafeteria | 1876 | 125 |  | 2974 | 67 | 67 | House Fan | 23792 | 4.731 | 2 | 4.731 | 2
- | Main Office | 0 | 0 | Yes | 262 | 5 | 5 | N/A | 2096 | 0 | 0 | 20 | 3
- | Principal Office | 0 | 0 | Yes | 194 | 4 | 4 | N/A | 1552 | 0 | 0 | 20 | 3
- | Portable Classroom | 289 | 19 |  | 1290 | 29 | 19 | Unit Ventilators | 10320 | 1.6802 | 1 | 1.6802 | 1
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Delaplaine McDaniel Elementary-Middle School | [8 empty] | unk | unk | unk | unk
| McDaniel Annex (St. Edmunds) | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
McDaniel Main | [9 empty] | unk | unk | unk | unk
102 | Classroom | 865 | 57 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 9.8295 | 2 | 9.8295 | 2
103 | Classroom | 250 | 16 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 2.8409 | 1 | 2.8409 | 1
104 | Classroom | 340 | 22 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 3.0502 | 1 | 3.0502 | 1
105 | Classroom | 275 | 18 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 3.125 | 1 | 3.125 | 1
107 | Classroom | 1025 | 68 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 11.6477 | 3 | 11.6477 | 3
108 | Classroom |  | 0 | Yes | 464 | 10 | 10 |  | 3712 | unk | unk | 20 | 3
109 | Classroom | 550 | 36 |  | 1260 | 28 | 28 | Unit Ventilator | 10080 | 3.2738 | 1 | 3.2738 | 1
200 | Classroom | 430 | 28 |  | 1260 | 28 | 28 | Unit Ventilator | 10080 | 2.5595 | 1 | 2.5595 | 1
201 | Classroom | 0 | 0 |  | 396 | 9 | 0 | Unit Ventilator | 3168 | 0 | 0 | 0 | 0
203 | Classroom | 635 | 42 |  | 630 | 14 | 14 | Unit Ventilator | 5040 | 7.5595 | 2 | 7.5595 | 2
204 | Computer Lab | 949 | 63 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 7.7029 | 2 | 7.7029 | 2
205 | Classroom | 635 | 42 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 7.2159 | 2 | 7.2159 | 2
206 | Classroom | 475 | 31 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 4.1521 | 2 | 4.1521 | 2
207 | Classroom | 0 | 0 |  | 783 | 17 | 0 | Unit Ventilator | 6264 | 0 | 0 | 0 | 0
209 | Classroom | 0 | 0 |  | 777 | 17 | 0 | Unit Ventilator | 6216 | 0 | 0 | 0 | 0
300 | Classroom | 0 | 0 | Yes | 819 | 18 | 18 | Unit Ventilator | 6552 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 |  | 691 | 15 | 0 | Unit Ventilator | 5528 | 0 | 0 | 0 | 0
303 | Classroom | 428 | 28 |  | 945 | 21 | 21 | Unit Ventilator | 7560 | 3.3968 | 1 | 3.3968 | 1
304 | Classroom | 134 | 8 |  | 704 | 16 | 8 | Unit Ventilator | 5632 | 1.4276 | 1 | 1.4276 | 1
305 | Classroom | 374 | 24 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 4.3966 | 2 | 4.3966 | 2
306 | Classroom | 185 | 12 |  | 638 | 14 | 12 | Unit Ventilator | 5104 | 2.1748 | 1 | 2.1748 | 1
307 | Classroom | 570 | 38 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 6.7006 | 2 | 6.7006 | 2
308 | Classroom | 470 | 31 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 5.5251 | 2 | 5.5251 | 2
309 | Classroom | 400 | 26 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 4.7022 | 2 | 4.7022 | 2
310 | Classroom | 494 | 32 |  | 880 | 20 | 20 | Unit Ventilator | 7040 | 4.2102 | 2 | 4.2102 | 2
311 | Classroom | 430 | 28 |  | 638 | 14 | 14 | Unit Ventilator | 5104 | 5.0549 | 2 | 5.0549 | 2
313 | Classroom | 1099 | 73 |  | 814 | 18 | 18 | Unit Ventilator | 6512 | 10.1259 | 3 | 10.1259 | 3
- | Gym | 0 | 0 | Yes | 3300 | 75 | 75 | AHU | 26400 | 0 | 0 | 20 | 3
- | Gym Office |  | 0 | Yes | 77 | 1 | 1 |  | 616 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 280 | 6 | 6 |  | 2240 | unk | unk | 20 | 3
- | Media Center | 700 | 46 |  | 1078 | 24 | 24 | Unit Ventilator | 8624 | 4.8701 | 2 | 4.8701 | 2
- | Kitchen |  | 0 | Yes | 294 | 6 | 6 |  | 2352 | unk | unk | 20 | 3
- | School Police |  | 0 | Yes | 90 | 2 | 2 |  | 720 | unk | unk | 20 | 3
- | Counselor Office |  | 0 | Yes | 117 | 2 | 2 |  | 936 | unk | unk | 20 | 3
- | Principals Office |  | 0 | Yes | 196 | 4 | 4 |  | 1568 | unk | unk | 20 | 3
- | Vice Principal |  | 0 | Yes | 187 | 4 | 4 |  | 1496 | unk | unk | 20 | 3
- | Office | 0 | 0 | Yes | 392 | 8 | 8 | AHU | 3136 | 0 | 0 | 20 | 3
McDaniel Annex (St. Edmunds) | [9 empty] | unk | unk | unk | unk
K-1 | Classroom | 269 | 17 |  | 516 | 11 | 11 | Unit Ventilator | 4128 | 3.9099 | 1 | 3.9099 | 1
K-2 | Classroom | 449 | 29 |  | 616 | 14 | 14 | Unit Ventilator | 4928 | 5.4667 | 2 | 5.4667 | 2
K-3 | Classroom | 407 | 27 |  | 616 | 14 | 14 | Unit Ventilator | 4928 | 4.9554 | 2 | 4.9554 | 2
K-4 | Classroom | 348 | 23 |  | 516 | 11 | 11 | Unit Ventilator | 4128 | 5.0581 | 2 | 5.0581 | 2
206 | Classroom | 350 | 23 |  | 616 | 14 | 14 | Unit Ventilator | 4928 | 4.2614 | 2 | 4.2614 | 2
207 | Classroom | 530 | 35 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 5.0189 | 2 | 5.0189 | 2
208 | Classroom | 632 | 42 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 7.1818 | 2 | 7.1818 | 2
209 | Classroom | 495 | 33 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 5.625 | 2 | 5.625 | 2
210 | Classroom | 375 | 25 |  | 440 | 10 | 10 | Unit Ventilator | 3520 | 6.392 | 2 | 6.392 | 2
213 | Classroom | 447 | 29 |  | 440 | 10 | 10 | Unit Ventilator | 3520 | 7.6193 | 2 | 7.6193 | 2
215 | Classroom | 640 | 42 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 6.0606 | 2 | 6.0606 | 2
306 | Classroom | 525 | 35 |  | 616 | 14 | 14 | Unit Ventilator | 4928 | 6.392 | 2 | 6.392 | 2
307 | Classroom | 653 | 43 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 6.1837 | 2 | 6.1837 | 2
308 | Classroom | 425 | 28 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 4.8295 | 2 | 4.8295 | 2
309 | Classroom | 630 | 42 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 7.1591 | 2 | 7.1591 | 2
310 | Classroom | 471 | 31 |  | 660 | 15 | 15 | Unit Ventilator | 5280 | 5.3523 | 2 | 5.3523 | 2
312 | Classroom | 481 | 32 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 5.1243 | 2 | 5.1243 | 2
313 | Classroom | 611 | 40 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 6.5092 | 2 | 6.5092 | 2
- | Cafeteria / Gym | 14007 | 933 |  | 3960 | 90 | 90 | AHU | 31680 | 26.5284 | 4 | 26.5284 | 4
- | Classroom | 15010 | 1000 |  | 1431 | 32 | 32 | AHU | 11448 | 78.6688 | 5 | 78.6688 | 5
Sheet Last Modified: | 2021-04-06 | [8 empty] | unk | unk | unk | unk
School: | William McKinley Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | A1/11 | 529 | 35 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 4.6241 | 2 | 4.6241 | 2
- | A2/12 | 627 | 41 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 5.652 | 2 | 5.652 | 2
- | A3/13 | 298 | 19 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 2.6049 | 1 | 2.6049 | 1
- | A4/14 | 512 | 34 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 4.4755 | 2 | 4.4755 | 2
- | Autistic Support 8 | 231 | 15 |  | 726 | 16 | 15 | Unit Ventilator | 5808 | 2.3864 | 1 | 2.3864 | 1
- | B1/21 | 711 | 47 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 6.733 | 2 | 6.733 | 2
- | B2/22 | 630 | 42 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 6.2666 | 2 | 6.2666 | 2
- | B3/23 | 660 | 44 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 6.565 | 2 | 6.565 | 2
- | B4/24 | 538 | 35 |  | 744 | 16 | 16 | Unit Ventilator | 5952 | 5.4234 | 2 | 5.4234 | 2
- | C1/31 | 604 | 40 |  | 726 | 16 | 16 | Unit Ventilator | 5808 | 6.2397 | 2 | 6.2397 | 2
- | C2/32 | 271 | 18 |  | 675 | 15 | 15 | Unit Ventilator | 5400 | 3.0111 | 1 | 3.0111 | 1
- | C3/33 | 605 | 40 |  | 700 | 15 | 15 | Unit Ventilator | 5600 | 6.4821 | 2 | 6.4821 | 2
- | C4/34 | 669 | 44 |  | 720 | 16 | 16 | Unit Ventilator | 5760 | 6.9688 | 2 | 6.9688 | 2
- | CCTC 11 | 1062 | 70 |  | 1215 | 27 | 27 | Unit Ventilator | 9720 | 6.5556 | 2 | 6.5556 | 2
- | D1 | 426 | 28 |  | 858 | 19 | 19 | Unit Ventilator | 6864 | 3.7238 | 1 | 3.7238 | 1
- | D2 | 553 | 36 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 5.3173 | 2 | 5.3173 | 2
- | D3 | 290 | 19 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.7885 | 1 | 2.7885 | 1
- | D4 | 310 | 20 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.9808 | 1 | 2.9808 | 1
- | Gymnasium | 1525 | 101 |  | 2860 | 65 | 65 | AHU | 22880 | 3.9991 | 1 | 3.9991 | 1
- | Kindergarten 1 | 355 | 23 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.8815 | 1 | 2.8815 | 1
- | Kindergarten 2 | 290 | 19 | Yes | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.3539 | 1 | 22.3539 | 3
- | Kindergarten 3 | 282 | 18 | Yes | 924 | 21 | 21 | Unit Ventilator | 7392 | 2.289 | 1 | 22.289 | 3
- | Pre K 4 | 739 | 49 |  | 924 | 21 | 21 | Unit Ventilator | 7392 | 5.9984 | 2 | 5.9984 | 2
- | Room 5 | 611 | 40 |  | 726 | 16 | 16 | Unit Ventilator | 5808 | 6.312 | 2 | 6.312 | 2
-- | Room 6 | 467 | 31 |  | 726 | 16 | 16 | Unit Ventilator | 5808 | 4.8244 | 2 | 4.8244 | 2
- | Room 9 / Visual Arts | 748 | 49 |  | 726 | 16 | 16 | AHU | 5808 | 7.7273 | 2 | 7.7273 | 2
- | Room 12 | 587 | 39 |  | 809 | 18 | 18 | AHU | 6472 | 5.4419 | 2 | 5.4419 | 2
A-0 | Small Classroom | 37 | 2 |  | 150 | 3 | 2 | AHU | 1200 | 1.85 | 1 | 1.85 | 1
7 | Teachers Lounge | 59 | 3 | Yes | 351 | 7 | 7 | AHU | 2808 | 1.2607 | 1 | 21.2607 | 3
- | Nurse Exam Large | 69 | 4 | Yes | 252 | 5 | 5 | AHU | 2016 | 2.0536 | 1 | 22.0536 | 3
- | Nurse Office | 38 | 2 |  | 119 | 2 | 2 | AHU | 952 | 2.395 | 1 | 2.395 | 1
- | Nurse Exam | 59 | 3 |  | 153 | 3 | 3 | AHU | 1224 | 2.8922 | 1 | 2.8922 | 1
- | Storage Large | 61 | 4 |  | 216 | 4 | 4 | AHU | 1728 | 2.1181 | 1 | 2.1181 | 1
- | Storage | 24 | 1 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | Auditorium | 1667 | 111 |  | 2453 | 55 | 55 | AHU | 19624 | 5.0968 | 2 | 5.0968 | 2
- | Music Room | 319 | 21 |  | 727 | 16 | 16 | AHU | 5816 | 3.2909 | 1 | 3.2909 | 1
- | Library | 1047 | 69 |  | 3888 | 88 | 69 | AHU | 31104 | 2.0197 | 1 | 2.0197 | 1
- | Cafeteria | 894 | 59 |  | 2331 | 52 | 52 | AHU | 18648 | 2.8764 | 1 | 2.8764 | 1
D-0 | Small Classroom | 36 | 2 |  | 150 | 3 | 2 | AHU | 1200 | 1.8 | 1 | 1.8 | 1
C-0 | Small Classroom | 21 | 1 |  | 150 | 3 | 1 | AHU | 1200 | 1.05 | 1 | 1.05 | 1
B-0 | Small Classroom | 53 | 3 |  | 150 | 3 | 3 | AHU | 1200 | 2.65 | 1 | 2.65 | 1
10 | Small Classroom | 26 | 1 | Yes | 364 | 8 | 8 | AHU | 2912 | 0.53571 | 0 | 20.5357 | 3
- | Main Office | 50 | 3 | Yes | 817 | 18 | 18 | AHU | 6536 | 0.459 | 0 | 20.459 | 3
- | Admin Office 1 | 52 | 3 |  | 128 | 2 | 2 | AHU | 1024 | 3.0469 | 1 | 3.0469 | 1
- | Admin Office 2 | 73 | 4 |  | 128 | 2 | 2 | AHU | 1024 | 4.2773 | 2 | 4.2773 | 2
- | Admin Office 3 | 43 | 2 |  | 128 | 2 | 2 | AHU | 1024 | 2.5195 | 1 | 2.5195 | 1
- | Admin Office 5 | 50 | 3 |  | 160 | 3 | 3 | AHU | 1280 | 2.3438 | 1 | 2.3438 | 1
- | Admin Office 6 | 49 | 3 |  | 285 | 6 | 3 | AHU | 2280 | 1.2895 | 1 | 1.2895 | 1
- | Admin Office 7 | 22 | 1 | Yes | 120 | 2 | 2 | AHU | 960 | 1.375 | 1 | 21.375 | 3
- | Equip Storage | 0 | 0 |  | 120 | 2 | 0 | AHU | 960 | 0 | 0 | 0 | 0
- | Corridor | 35 | 2 |  | 440 | 10 | 2 | AHU | 3520 | 0.59659 | 0 | 0.59659 | 0
- | Principals Office | 35 | 2 | Yes | 180 | 4 | 4 | AHU | 1440 | 1.4583 | 1 | 21.4583 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Morton McMichael Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Part 2 | Part 3 | [6 empty] | unk | unk | unk | unk
| Part 4 | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Staff Lounge | 125 | 8 |  | 468 | 10 | 8 | Unit Ventilator | 3744 | 2.0032 | 1 | 2.0032 | 1
101 | Admin | 281 | 18 |  | 1056 | 24 | 18 | Unit Ventilator | 8448 | 1.9957 | 1 | 1.9957 | 1
102 | Superintendants | 284 | 18 |  | 600 | 13 | 13 | Unit Ventilator | 4800 | 3.55 | 1 | 3.55 | 1
- | IT Office |  | 0 |  | 459 | 10 | 0 |  | 3672 | unk | unk | unk | unk
104 | Small Conf/Assis. Super | 110 | 7 |  | 252 | 5 | 5 | Unit Ventilator | 2016 | 3.2738 | 1 | 3.2738 | 1
105 | Large Conference | 319 | 21 |  | 1188 | 27 | 21 | Unit Ventilator | 9504 | 2.0139 | 1 | 2.0139 | 1
108 | Classroom | 375 | 25 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 3.2552 | 1 | 3.2552 | 1
110 | Classroom | 279 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4911 | 1 | 2.4911 | 1
114 | Classroom | 284 | 18 |  | 576 | 13 | 13 | Unit Ventilator | 4608 | 3.6979 | 1 | 3.6979 | 1
200 | Classroom | 340 | 22 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.0357 | 1 | 3.0357 | 1
201 | Classroom | 328 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9286 | 1 | 2.9286 | 1
201A | Classroom | 320 | 21 |  | 336 | 7 | 7 | Unit Ventilator | 2688 | 7.1429 | 2 | 7.1429 | 2
202 | Classroom | 292 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6071 | 1 | 2.6071 | 1
204 | Classroom | 272 | 18 |  | 2592 | 58 | 18 | Unit Ventilator | 20736 | 0.78704 | 0 | 0.78704 | 0
205 | Classroom | 326 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9107 | 1 | 2.9107 | 1
206 | Classroom | 275 | 18 |  | 2592 | 58 | 18 | Unit Ventilator | 20736 | 0.79572 | 0 | 0.79572 | 0
207 | Classroom | 318 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.8393 | 1 | 2.8393 | 1
208 | Classroom | 249 | 16 |  | 2592 | 58 | 16 | Unit Ventilator | 20736 | 0.72049 | 0 | 0.72049 | 0
210 | Classroom | 351 | 23 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.1339 | 1 | 3.1339 | 1
212 | Classroom | 363 | 24 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.2411 | 1 | 3.2411 | 1
214 | Classroom | 282 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.5179 | 1 | 2.5179 | 1
216 | Classroom | 262 | 17 |  | 864 | 19 | 17 | Unit Ventilator | 6912 | 2.2743 | 1 | 2.2743 | 1
217 | Classroom | 368 | 24 |  | 1944 | 44 | 24 | Unit Ventilator | 15552 | 1.4198 | 1 | 1.4198 | 1
218 | Classroom | 320 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.8571 | 1 | 2.8571 | 1
219 | Classroom | 351 | 23 |  | 1944 | 44 | 23 | Unit Ventilator | 15552 | 1.3542 | 1 | 1.3542 | 1
220 | Classroom | 403 | 26 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.5982 | 1 | 3.5982 | 1
222 | Classroom | 280 | 18 |  | 504 | 11 | 11 | Unit Ventilator | 4032 | 4.1667 | 2 | 4.1667 | 2
224 | Classroom |  | 0 |  | 840 | 19 | 0 | Unit Ventilator | 6720 | unk | unk | unk | unk
226 | Classroom | 240 | 16 |  | 840 | 19 | 16 | Unit Ventilator | 6720 | 2.1429 | 1 | 2.1429 | 1
300 | Classroom | 239 | 15 |  | 840 | 19 | 15 | Unit Ventilator | 6720 | 2.1339 | 1 | 2.1339 | 1
301 | Classroom | 291 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.5982 | 1 | 2.5982 | 1
302 | Classroom | 302 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.6964 | 1 | 2.6964 | 1
303 | Classroom | 288 | 19 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.5714 | 1 | 2.5714 | 1
305 | Classroom | 317 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.8304 | 1 | 2.8304 | 1
306 | Classroom | 546 | 36 |  | 1248 | 28 | 28 | Unit Ventilator | 9984 | 3.2812 | 1 | 3.2812 | 1
307 | Classroom | 274 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4464 | 1 | 2.4464 | 1
308 | Classroom | 273 | 18 |  | 864 | 19 | 18 | Unit Ventilator | 6912 | 2.3698 | 1 | 2.3698 | 1
310 | Classroom | 272 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4286 | 1 | 2.4286 | 1
312 | Classroom | 281 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.5089 | 1 | 2.5089 | 1
314 | Classroom | 306 | 20 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.7321 | 1 | 2.7321 | 1
316 | Classroom | 315 | 21 |  | 864 | 19 | 19 | Unit Ventilator | 6912 | 2.7344 | 1 | 2.7344 | 1
317 | Classroom | 392 | 26 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 3.5 | 1 | 3.5 | 1
318 | Classroom | 274 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4464 | 1 | 2.4464 | 1
319 | Classroom | 276 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.4643 | 1 | 2.4643 | 1
320 | Classroom | 281 | 18 |  | 840 | 19 | 18 | Unit Ventilator | 6720 | 2.5089 | 1 | 2.5089 | 1
322 | Classroom | 270 | 18 |  | 576 | 13 | 13 | Unit Ventilator | 4608 | 3.5156 | 1 | 3.5156 | 1
323 | Classroom | 279 | 18 |  | 864 | 19 | 18 | Unit Ventilator | 6912 | 2.4219 | 1 | 2.4219 | 1
324 | Classroom | 326 | 21 |  | 840 | 19 | 19 | Unit Ventilator | 6720 | 2.9107 | 1 | 2.9107 | 1
325 | Classroom | 285 | 19 |  | 888 | 20 | 19 | Unit Ventilator | 7104 | 2.4071 | 1 | 2.4071 | 1
326 | Classroom | 262 | 17 |  | 864 | 19 | 17 | Unit Ventilator | 6912 | 2.2743 | 1 | 2.2743 | 1
- | Auditorium | 520 | 34 |  | 4914 | 111 | 34 | AHU | 39312 | 0.79365 | 0 | 0.79365 | 0
- | Cafe | 590 | 39 |  | 2485 | 56 | 39 | AHU | 19880 | 1.7807 | 1 | 1.7807 | 1
- | Gym | 690 | 46 |  | 3621 | 82 | 46 | AHU | 28968 | 1.4292 | 1 | 1.4292 | 1
- | Main Office |  | 0 | Yes | 1401 | 31 | 31 |  | 11208 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-06 | [8 empty] | unk | unk | unk | unk
School: | General George G. Meade Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
15 | Classroom | 378 | 25 | Yes | 644 | 14 | 14 | Unit Ventilator | 5152 | 4.4022 | 2 | 24.4022 | 4
16 | Classroom | 336 | 22 |  | 833 | 18 | 18 | Unit Ventilator | 6664 | 3.0252 | 1 | 3.0252 | 1
17 | Classroom | 184 | 12 |  | 330 | 7 | 7 | Unit Ventilator | 2640 | 4.1818 | 2 | 4.1818 | 2
18 | Classroom | 686 | 45 | Yes | 1101 | 25 | 25 | Unit Ventilator | 8808 | 4.673 | 2 | 24.673 | 4
101 | Classroom | 294 | 19 |  | 892 | 20 | 19 | Unit Ventilator | 7136 | 2.472 | 1 | 2.472 | 1
102 | Classroom | 299 | 19 | Yes | 765 | 17 | 17 | Unit Ventilator | 6120 | 2.9314 | 1 | 22.9314 | 3
103 | Classroom | 360 | 24 | Yes | 823 | 18 | 18 | Unit Ventilator | 6584 | 3.2807 | 1 | 23.2807 | 3
104 | Classroom | 281 | 18 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 2.9894 | 1 | 2.9894 | 1
105 | Classroom | 445 | 29 |  | 674 | 15 | 15 | Unit Ventilator | 5392 | 4.9518 | 2 | 4.9518 | 2
106 | Classroom | 405 | 27 |  | 846 | 19 | 19 | Unit Ventilator | 6768 | 3.5904 | 1 | 3.5904 | 1
107 | Classroom | 332 | 22 |  | 526 | 11 | 11 | Unit Ventilator | 4208 | 4.7338 | 2 | 4.7338 | 2
108 | Classroom | 294 | 19 |  | 670 | 15 | 15 | Unit Ventilator | 5360 | 3.291 | 1 | 3.291 | 1
109 | Classroom | 279 | 18 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 2.9681 | 1 | 2.9681 | 1
115 | Classroom | 640 | 42 | Yes | 865 | 19 | 19 | Unit Ventilator | 6920 | 5.5491 | 2 | 25.5491 | 4
116 | Classroom | 325 | 21 | Yes | 413 | 9 | 9 | Unit Ventilator | 3304 | 5.9019 | 2 | 25.9019 | 4
117 | Classroom | 433 | 28 | Yes | 837 | 19 | 19 | Unit Ventilator | 6696 | 3.8799 | 1 | 23.8799 | 3
118 | Classroom | 664 | 44 | Yes | 849 | 19 | 19 | Unit Ventilator | 6792 | 5.8657 | 2 | 25.8657 | 4
200 | Classroom | 193 | 12 |  | 349 | 7 | 7 | Unit Ventilator | 2792 | 4.1476 | 2 | 4.1476 | 2
201 | Classroom | 414 | 27 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 4.6552 | 2 | 4.6552 | 2
202 | Classroom | 53 | 3 |  | 673 | 15 | 3 | Unit Ventilator | 5384 | 0.59064 | 0 | 0.59064 | 0
203 | Classroom | 275 | 18 |  | 666 | 15 | 15 | Unit Ventilator | 5328 | 3.0968 | 1 | 3.0968 | 1
204 | Classroom | 360 | 24 |  | 669 | 15 | 15 | Unit Ventilator | 5352 | 4.0359 | 2 | 4.0359 | 2
205 | Classroom | 343 | 22 |  | 701 | 15 | 15 | Unit Ventilator | 5608 | 3.6698 | 1 | 3.6698 | 1
206 | Classroom | 280 | 18 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 2.9787 | 1 | 2.9787 | 1
207 | Classroom | 303 | 20 |  | 671 | 15 | 15 | Unit Ventilator | 5368 | 3.3867 | 1 | 3.3867 | 1
208 | Classroom | 259 | 17 |  | 576 | 13 | 13 | Unit Ventilator | 4608 | 3.3724 | 1 | 3.3724 | 1
209 | Classroom | 0 | 0 |  | 540 | 12 | 0 | Unit Ventilator | 4320 | 0 | 0 | 0 | 0
210 | Classroom | 311 | 20 |  | 511 | 11 | 11 | Unit Ventilator | 4088 | 4.5646 | 2 | 4.5646 | 2
211 | Classroom | 222 | 14 |  | 720 | 16 | 14 | Unit Ventilator | 5760 | 2.3125 | 1 | 2.3125 | 1
215 | Classroom | 550 | 36 |  | 843 | 19 | 19 | Unit Ventilator | 6744 | 4.8932 | 2 | 4.8932 | 2
216 | Classroom | 306 | 20 |  | 855 | 19 | 19 | Unit Ventilator | 6840 | 2.6842 | 1 | 2.6842 | 1
217 | Classroom | 169 | 11 |  | 842 | 19 | 11 | Unit Ventilator | 6736 | 1.5053 | 1 | 1.5053 | 1
218 | Classroom | 631 | 42 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 5.5546 | 2 | 5.5546 | 2
285 | Classroom | 273 | 18 |  | 0 | 0 | 0 | Unit Ventilator | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
301 | Classroom | 883 | 58 |  | 2031 | 46 | 46 | Unit Ventilator | 16248 | 3.2607 | 1 | 3.2607 | 1
304 | Classroom | 276 | 18 |  | 670 | 15 | 15 | Unit Ventilator | 5360 | 3.0896 | 1 | 3.0896 | 1
305 | Classroom | 346 | 23 |  | 702 | 15 | 15 | Unit Ventilator | 5616 | 3.6966 | 1 | 3.6966 | 1
306 | Classroom | 319 | 21 |  | 706 | 16 | 16 | Unit Ventilator | 5648 | 3.3888 | 1 | 3.3888 | 1
307 | Classroom | 347 | 23 |  | 670 | 15 | 15 | Unit Ventilator | 5360 | 3.8843 | 1 | 3.8843 | 1
308 | Classroom | 112 | 7 |  | 852 | 19 | 7 | Unit Ventilator | 6816 | 0.98592 | 0 | 0.98592 | 0
309 | Classroom | 333 | 22 |  | 309 | 7 | 7 | Unit Ventilator | 2472 | 8.0825 | 2 | 8.0825 | 2
310 | Classroom | 247 | 16 |  | 510 | 11 | 11 | Unit Ventilator | 4080 | 3.6324 | 1 | 3.6324 | 1
311 | Classroom | 351 | 23 |  | 706 | 16 | 16 | Unit Ventilator | 5648 | 3.7288 | 1 | 3.7288 | 1
312 | Classroom | 305 | 20 |  | 514 | 11 | 11 | Unit Ventilator | 4112 | 4.4504 | 2 | 4.4504 | 2
315 | Classroom | 289 | 19 |  | 838 | 19 | 19 | Unit Ventilator | 6704 | 2.5865 | 1 | 2.5865 | 1
316 | Classroom | 285 | 19 |  | 855 | 19 | 19 | Unit Ventilator | 6840 | 2.5 | 1 | 2.5 | 1
317 | Classroom | 548 | 36 |  | 847 | 19 | 19 | Unit Ventilator | 6776 | 4.8524 | 2 | 4.8524 | 2
318 | Classroom | 647 | 43 |  | 852 | 19 | 19 | Unit Ventilator | 6816 | 5.6954 | 2 | 5.6954 | 2
- | Main Office |  | 0 | Yes | 305.08 | 6 | 6 |  | 2440.64 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 242.55 | 5 | 5 |  | 1940.4 | unk | unk | 20 | 3
- | 1st Floor Hall | 310 | 20 |  | 2688 | 61 | 20 | Unit Ventilator | 21504 | 0.86496 | 0 | 0.86496 | 0
- | 1st Floor Nurse RR | 0 | 0 |  | 244 | 5 | 0 | N/A | 1952 | 0 | 0 | 0 | 0
- | 1st Floor Staff Womens RR | 0 | 0 |  | 393 | 8 | 0 | N/A | 3144 | 0 | 0 | 0 | 0
- | 2nd Floor Hall | 0 | 0 |  | 2066 | 46 | 0 | Unit Ventilator | 16528 | 0 | 0 | 0 | 0
- | 2nd Floor Mens RR | 99 | 6 |  | 355 | 8 | 6 | N/A | 2840 | 2.0915 | 1 | 2.0915 | 1
- | 2nd Floor Womens RR | 236 | 15 |  | 328 | 7 | 7 | N/A | 2624 | 5.3963 | 2 | 5.3963 | 2
- | 3rd Floor Hall | 289 | 19 |  | 2661 | 60 | 19 | Unit Ventilator | 21288 | 0.81454 | 0 | 0.81454 | 0
- | 3rd Floor Mens RR | 95 | 6 |  | 259 | 5 | 5 | N/A | 2072 | 2.751 | 1 | 2.751 | 1
- | 3rd Floor Womens RR | 219 | 14 |  | 328 | 7 | 7 | N/A | 2624 | 5.0076 | 2 | 5.0076 | 2
- | Cafeteria | 754 | 50 |  | 5223 | 118 | 50 | Unit Ventilator | 41784 | 1.0827 | 1 | 1.0827 | 1
- | Bsmt: Boys RR | 0 | 0 |  | 765 | 17 | 0 | N/A | 6120 | 0 | 0 | 0 | 0
- | Bsmt: Grils RR | 0 | 0 |  | 697 | 15 | 0 | N/A | 5576 | 0 | 0 | 0 | 0
- | Staff Restroom: 1st Floor | 0 | 0 |  | 168 | 3 | 0 | N/A | 1344 | 0 | 0 | 0 | 0
- | Library | 0 | 0 |  | 2062.2 | 46 | 0 | Unit Ventilator | 16497.6 | 0 | 0 | 0 | 0
- | Staff Restroom: 2nd Floor | 0 | 0 |  | 305 | 6 | 0 | N/A | 2440 | 0 | 0 | 0 | 0
- | Staff Restroom: 3rd Floor | 0 | 0 |  | 308 | 7 | 0 | N/A | 2464 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-08 | [8 empty] | unk | unk | unk | unk
School: | Austin Meehan Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
3 | Classroom | 280 | 18 |  | 1537 | 34 | 18 | Unit Ventilator | 12296 | 1.3663 | 1 | 1.3663 | 1
111 | Classroom | 323 | 21 |  | 917 | 20 | 20 | Unit Ventilator | 7336 | 2.6418 | 1 | 2.6418 | 1
112 | Classroom | 309 | 20 |  | 1490 | 33 | 20 | Unit Ventilator | 11920 | 1.5554 | 1 | 1.5554 | 1
113 | Classroom | 287 | 19 |  | 208 | 4 | 4 | Unit Ventilator | 1664 | 10.3486 | 3 | 10.3486 | 3
114 | Classroom | 307 | 20 |  | 1193 | 27 | 20 | Unit Ventilator | 9544 | 1.93 | 1 | 1.93 | 1
115 | Classroom | 274 | 18 |  | 1192 | 27 | 18 | Unit Ventilator | 9536 | 1.724 | 1 | 1.724 | 1
121 | Classroom | 0 | 0 |  | 944 | 21 | 0 | Unit Ventilator | 7552 | 0 | 0 | 0 | 0
122 | Classroom | 503 | 33 |  | 1085 | 24 | 24 | Unit Ventilator | 8680 | 3.477 | 1 | 3.477 | 1
123 | Classroom | 350 | 23 |  | 1175 | 26 | 23 | Unit Ventilator | 9400 | 2.234 | 1 | 2.234 | 1
124 | Classroom | 283 | 18 |  | 1123 | 25 | 18 | Unit Ventilator | 8984 | 1.89 | 1 | 1.89 | 1
125 | Classroom | 413 | 27 |  | 1156 | 26 | 26 | Unit Ventilator | 9248 | 2.6795 | 1 | 2.6795 | 1
126 | Classroom | 400 | 26 |  | 1064 | 24 | 24 | Unit Ventilator | 8512 | 2.8195 | 1 | 2.8195 | 1
127 | Classroom | 333 | 22 |  | 1198 | 27 | 22 | Unit Ventilator | 9584 | 2.0847 | 1 | 2.0847 | 1
128 | Classroom | 343 | 22 |  | 933 | 21 | 21 | Unit Ventilator | 7464 | 2.7572 | 1 | 2.7572 | 1
211 | Classroom | 327 | 21 |  | 867 | 19 | 19 | Unit Ventilator | 6936 | 2.8287 | 1 | 2.8287 | 1
212 | Classroom | 382 | 25 |  | 1630 | 37 | 25 | Unit Ventilator | 13040 | 1.7577 | 1 | 1.7577 | 1
213 | Classroom | 281 | 18 |  | 269 | 6 | 6 | Unit Ventilator | 2152 | 7.8346 | 2 | 7.8346 | 2
214 | Classroom | 372 | 24 |  | 1317 | 29 | 24 | Unit Ventilator | 10536 | 2.1185 | 1 | 2.1185 | 1
215 | Classroom | 396 | 26 |  | 1199 | 27 | 26 | Unit Ventilator | 9592 | 2.4771 | 1 | 2.4771 | 1
221 | Classroom | 0 | 0 |  | 1054 | 23 | 0 | Unit Ventilator | 8432 | 0 | 0 | 0 | 0
222 | Classroom | 337 | 22 |  | 1286 | 29 | 22 | Unit Ventilator | 10288 | 1.9654 | 1 | 1.9654 | 1
223 | Classroom | 343 | 22 |  | 1230 | 27 | 22 | Unit Ventilator | 9840 | 2.0915 | 1 | 2.0915 | 1
224 | Classroom | 0 | 0 |  | 1091 | 24 | 0 | Unit Ventilator | 8728 | 0 | 0 | 0 | 0
225 | Classroom | 420 | 28 |  | 1151 | 26 | 26 | Unit Ventilator | 9208 | 2.7368 | 1 | 2.7368 | 1
226 | Classroom | 397 | 26 |  | 1175 | 26 | 26 | Unit Ventilator | 9400 | 2.534 | 1 | 2.534 | 1
227 | Classroom | 327 | 21 |  | 1292 | 29 | 21 | Unit Ventilator | 10336 | 1.8982 | 1 | 1.8982 | 1
228 | Classroom | 0 | 0 |  | 931 | 21 | 0 | Unit Ventilator | 7448 | 0 | 0 | 0 | 0
311 | Classroom | 310 | 20 |  | 1041 | 23 | 20 | Unit Ventilator | 8328 | 2.2334 | 1 | 2.2334 | 1
312 | Classroom | 309 | 20 |  | 1602 | 36 | 20 | Unit Ventilator | 12816 | 1.4466 | 1 | 1.4466 | 1
313 | Classroom | 0 | 0 |  | 756 | 17 | 0 | Unit Ventilator | 6048 | 0 | 0 | 0 | 0
314 | Classroom | 0 | 0 |  | 1279 | 29 | 0 | Unit Ventilator | 10232 | 0 | 0 | 0 | 0
315 | Classroom | 0 | 0 |  | 1219 | 27 | 0 | Unit Ventilator | 9752 | 0 | 0 | 0 | 0
321 | Classroom | 0 | 0 |  | 1064 | 24 | 0 | Unit Ventilator | 8512 | 0 | 0 | 0 | 0
322 | Classroom | 460 | 30 |  | 1199 | 27 | 27 | Unit Ventilator | 9592 | 2.8774 | 1 | 2.8774 | 1
323 | Classroom | 0 | 0 |  | 1365 | 31 | 0 | Unit Ventilator | 10920 | 0 | 0 | 0 | 0
324 | Classroom | 377 | 25 |  | 1039 | 23 | 23 | Unit Ventilator | 8312 | 2.7214 | 1 | 2.7214 | 1
325 | Classroom | 270 | 18 |  | 1247 | 28 | 18 | Unit Ventilator | 9976 | 1.6239 | 1 | 1.6239 | 1
326 | Classroom | 493 | 32 |  | 1322 | 30 | 30 | Unit Ventilator | 10576 | 2.7969 | 1 | 2.7969 | 1
327 | Classroom | 417 | 27 |  | 1184 | 26 | 26 | Unit Ventilator | 9472 | 2.6415 | 1 | 2.6415 | 1
328 | Classroom | 397 | 26 |  | 955 | 21 | 21 | Unit Ventilator | 7640 | 3.1178 | 1 | 3.1178 | 1
411 | Classroom | 576 | 38 |  | 947 | 21 | 21 | Unit Ventilator | 7576 | 4.5618 | 2 | 4.5618 | 2
412 | Classroom | 352 | 23 |  | 1474 | 33 | 23 | Unit Ventilator | 11792 | 1.791 | 1 | 1.791 | 1
413 | Classroom | 307 | 20 |  | 208 | 4 | 4 | Unit Ventilator | 1664 | 11.0697 | 3 | 11.0697 | 3
414 | Classroom | 313 | 20 |  | 1255 | 28 | 20 | Unit Ventilator | 10040 | 1.8705 | 1 | 1.8705 | 1
415 | Classroom | 347 | 23 |  | 1215 | 27 | 23 | Unit Ventilator | 9720 | 2.142 | 1 | 2.142 | 1
421 | Classroom |  | 0 | Yes | 1058 | 24 | 24 | N/A | 8464 | unk | unk | 20 | 3
422 | Classroom | 463 | 30 |  | 1199 | 27 | 27 | Unit Ventilator | 9592 | 2.8962 | 1 | 2.8962 | 1
423 | Classroom | 363 | 24 |  | 1327 | 30 | 24 | Unit Ventilator | 10616 | 2.0516 | 1 | 2.0516 | 1
424 | Classroom | 300 | 20 |  | 1365 | 31 | 20 | Unit Ventilator | 10920 | 1.6484 | 1 | 1.6484 | 1
425 | Classroom | 383 | 25 |  | 1350 | 30 | 25 | Unit Ventilator | 10800 | 2.1278 | 1 | 2.1278 | 1
426 | Classroom | 450 | 30 |  | 1201 | 27 | 27 | Unit Ventilator | 9608 | 2.8102 | 1 | 2.8102 | 1
427 | Classroom | 357 | 23 |  | 1242 | 28 | 23 | Unit Ventilator | 9936 | 2.1558 | 1 | 2.1558 | 1
428 | Classroom | 390 | 26 |  | 1054 | 23 | 23 | Unit Ventilator | 8432 | 2.7751 | 1 | 2.7751 | 1
A-01 A | Art | 599 | 39 |  | 1692 | 38 | 38 | Unit Ventilator | 13536 | 2.6551 | 1 | 2.6551 | 1
A-02 | Art | 288 | 19 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
A-03 A | Art | 648 | 43 |  | 1692 | 38 | 38 | Unit Ventilator | 13536 | 2.8723 | 1 | 2.8723 | 1
- | Boys Locker Room | 1404 | 93 |  | 700 | 15 | 15 | AHU | 5600 | 15.0429 | 3 | 15.0429 | 3
- | Girls Locker Room | 1531 | 102 |  | 700 | 15 | 15 | AHU | 5600 | 16.4036 | 3 | 16.4036 | 3
Ground Level Pod #1 | Auditorium Control room | 0 | 0 |  | 102 | 2 | 0 | AHU | 816 | 0 | 0 | 0 | 0
Ground Level Pod #1 | Center Core | 163 | 10 |  | 528 | 12 | 10 | AHU | 4224 | 2.3153 | 1 | 2.3153 | 1
Ground Level Pod #1 | Center Core | 297 | 19 |  | 1012 | 23 | 19 | AHU | 8096 | 2.2011 | 1 | 2.2011 | 1
Ground Level Pod #1 | Conference | 38 | 2 |  | 150 | 3 | 2 | AHU | 1200 | 1.9 | 1 | 1.9 | 1
Ground Level Pod #1 | Counselor | 0 | 0 |  | 80 | 1 | 0 | AHU | 640 | 0 | 0 | 0 | 0
Ground Level Pod #1 | Entryway | 0 | 0 |  | 238 | 5 | 0 | AHU | 1904 | 0 | 0 | 0 | 0
Ground Level Pod #1 | Entryway | 32 | 2 |  | 238 | 5 | 2 | AHU | 1904 | 1.0084 | 1 | 1.0084 | 1
Ground Level Pod #1 | Lobby | 113 | 7 |  | 1625 | 36 | 7 | AHU | 13000 | 0.52154 | 0 | 0.52154 | 0
Ground Level Pod #1 | Lobby Entryway | 55 | 3 |  | 238 | 5 | 3 | AHU | 1904 | 1.7332 | 1 | 1.7332 | 1
Ground Level Pod #1 | Main Office - Waiting | 143 | 9 |  | 1550 | 35 | 9 | AHU | 12400 | 0.69194 | 0 | 0.69194 | 0
Ground Level Pod #1 | Main Office 1 | 63 | 4 |  | 130 | 2 | 2 | AHU | 1040 | 3.6346 | 1 | 3.6346 | 1
Ground Level Pod #1 | Main Office 2 | 74 | 4 |  | 231 | 5 | 4 | AHU | 1848 | 2.4026 | 1 | 2.4026 | 1
Ground Level Pod #1 | Main Office 3 | 41 | 2 |  | 110 | 2 | 2 | AHU | 880 | 2.7955 | 1 | 2.7955 | 1
Ground Level Pod #1 | Main Office 4 | 135 | 9 |  | 156 | 3 | 3 | AHU | 1248 | 6.4904 | 2 | 6.4904 | 2
Ground Level Pod #1 | Office | 28 | 1 |  | 143 | 3 | 1 | AHU | 1144 | 1.4685 | 1 | 1.4685 | 1
Ground Level Pod #1 | Office Floor | 0 | 0 |  | 500 | 11 | 0 | AHU | 4000 | 0 | 0 | 0 | 0
Ground Level Pod #1 | Ticket Booth | 0 | 0 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
Ground level Pod #2 | Cafeteria | 374 | 24 |  | 2900 | 65 | 24 | AHU | 23200 | 0.96724 | 0 | 0.96724 | 0
Ground level Pod #2 | Center Core | 68 | 4 |  | 400 | 9 | 4 | AHU | 3200 | 1.275 | 1 | 1.275 | 1
Ground level Pod #2 | Entryway | 32 | 2 |  | 300 | 6 | 2 | AHU | 2400 | 0.8 | 0 | 0.8 | 0
Ground level Pod #2 | Office | 8 | 0 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
Ground level Pod #2 | Pod Center Core | 116 | 7 |  | 925 | 21 | 7 | AHU | 7400 | 0.94054 | 0 | 0.94054 | 0
Ground Level Pod #3 | Cafeteria | 59 | 3 |  | 2900 | 65 | 3 | AHU | 23200 | 0.15259 | 0 | 0.15259 | 0
Ground Level Pod #3 | Center Core | 272 | 18 |  | 425 | 9 | 9 | AHU | 3400 | 4.8 | 2 | 4.8 | 2
Ground Level Pod #3 | Entryway | 68 | 4 |  | 460 | 10 | 4 | AHU | 3680 | 1.1087 | 1 | 1.1087 | 1
Ground Level Pod #3 | Pod Center Core | 174 | 11 |  | 900 | 20 | 11 | AHU | 7200 | 1.45 | 1 | 1.45 | 1
Ground Level Pod #3 | Pod Center Prep | 30 | 2 |  | 945 | 21 | 2 | AHU | 7560 | 0.2381 | 0 | 0.2381 | 0
Ground level Pod #4 | Center Ring - Counselor | 34 | 2 |  | 110 | 2 | 2 | AHU | 880 | 2.3182 | 1 | 2.3182 | 1
Ground level Pod #4 | Center Ring - Police | 0 | 0 |  | 187 | 4 | 0 | AHU | 1496 | 0 | 0 | 0 | 0
Ground level Pod #4 | Center Ring - Social Work | 36 | 2 |  | 110 | 2 | 2 | AHU | 880 | 2.4545 | 1 | 2.4545 | 1
Ground Level Pod #4 | Mayfair Center Core | 63 | 4 |  | 425 | 9 | 4 | AHU | 3400 | 1.1118 | 1 | 1.1118 | 1
Ground Level Pod #4 | Mayfair Conference | 27 | 1 |  | 156 | 3 | 1 | AHU | 1248 | 1.2981 | 1 | 1.2981 | 1
Ground Level Pod #4 | Mayfair Entry way | 0 | 0 |  | 204 | 4 | 0 | AHU | 1632 | 0 | 0 | 0 | 0
Ground Level Pod #4 | Mayfair Nurse Office | 0 | 0 |  | 216 | 4 | 0 | AHU | 1728 | 0 | 0 | 0 | 0
Ground Level Pod #4 | Mayfair Office | 0 | 0 |  | 144 | 3 | 0 | AHU | 1152 | 0 | 0 | 0 | 0
Ground Level Pod #4 | Mayfair Pod Center Core | 21 | 1 |  | 969 | 22 | 1 | AHU | 7752 | 0.16254 | 0 | 0.16254 | 0
Ground Level Pod #4 | Mayfair Pod Center Prep | 0 | 0 |  | 646 | 14 | 0 | AHU | 5168 | 0 | 0 | 0 | 0
Ground Level Pod #4 | Mayfair Principal Office | 0 | 0 |  | 190 | 4 | 0 | AHU | 1520 | 0 | 0 | 0 | 0
Ground Level Pod #4 | Nurse Exam | 62 | 4 |  | 54 | 1 | 1 | AHU | 432 | 8.6111 | 2 | 8.6111 | 2
Ground Level Pod #4 | Nurse Office | 93 | 6 |  | 420 | 9 | 6 | AHU | 3360 | 1.6607 | 1 | 1.6607 | 1
Ground Level Pod #4 | Roster Area Entry | 134 | 8 |  | 150 | 3 | 3 | AHU | 1200 | 6.7 | 2 | 6.7 | 2
Ground Level Pod #4 | Roster Room | 64 | 4 |  | 80 | 1 | 1 | AHU | 640 | 6 | 2 | 6 | 2
- | Gym | 3715 | 247 |  | 3700 | 84 | 84 | AHU | 29600 | 7.5304 | 2 | 7.5304 | 2
Lower Level Pod #2 | M-1 Band - Ensemble | 60 | 4 |  | 459 | 10 | 4 | AHU | 3672 | 0.98039 | 0 | 0.98039 | 0
Lower Level Pod #2 | M-1 Band - Office | 30 | 2 |  | 600 | 13 | 2 | AHU | 4800 | 0.375 | 0 | 0.375 | 0
Lower Level Pod #2 | M-1 Band - Practice 1 | 59 | 3 |  | 450 | 10 | 3 | AHU | 3600 | 0.98333 | 0 | 0.98333 | 0
Lower Level Pod #2 | Math Rm - Office | 30 | 2 |  | 104 | 2 | 2 | AHU | 832 | 2.1635 | 1 | 2.1635 | 1
Lower Level Pod #2 | Math Rm - Storage | 0 | 0 |  | 50 | 1 | 0 | AHU | 400 | 0 | 0 | 0 | 0
Lower Level Pod #2 | Storage | 0 | 0 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
Lower Level Pod #2 | Visual Com. Lab - Darkroom | 58 | 3 |  | 380 | 8 | 3 | AHU | 3040 | 1.1447 | 1 | 1.1447 | 1
Lower Level Pod #4 | Center Core Art-01,02,03 | 60 | 4 |  | 1692 | 38 | 4 | AHU | 13536 | 0.26596 | 0 | 0.26596 | 0
Lower Level Pod #4 | Center Core Storage | 21 | 1 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
Lower Level Pod #4 | Classroom #3 Office | 25 | 1 |  | 144 | 3 | 1 | AHU | 1152 | 1.3021 | 1 | 1.3021 | 1
Lower Level Pod #4 | Classroom #3 Prep | 27 | 1 |  | 50 | 1 | 1 | AHU | 400 | 4.05 | 2 | 4.05 | 2
Lower Level Pod #4 | Classroom #3 Storage | 24 | 1 |  | 126 | 2 | 1 | AHU | 1008 | 1.4286 | 1 | 1.4286 | 1
Lower Level Pod #4 | M-5 Band Rm Ensemble | 46 | 3 |  | 1734 | 39 | 3 | AHU | 13872 | 0.19896 | 0 | 0.19896 | 0
Lower Level Pod #4 | M-5 Band Rm Office | 0 | 0 |  | 100 | 2 | 0 | AHU | 800 | 0 | 0 | 0 | 0
Lower Level Pod #4 | M-5 Band Rm Practice 1 | 0 | 0 |  | 40 | 0 | 0 | AHU | 320 | 0 | 0 | 0 | 0
Lower Level Pod #4 | M-5 Band Rm Practice 2 | 0 | 0 |  | 40 | 0 | 0 | AHU | 320 | 0 | 0 | 0 | 0
M-1 B | Band Room | 323 | 21 |  | 1178 | 26 | 21 | Unit Ventilator | 9424 | 2.0565 | 1 | 2.0565 | 1
M-5 | Band Room | 0 | 0 |  | 1734 | 39 | 0 | Unit Ventilator | 13872 | 0 | 0 | 0 | 0
Math Lab | Classroom | 338 | 22 |  | 1337 | 30 | 22 | Unit Ventilator | 10696 | 1.896 | 1 | 1.896 | 1
S-01 A | Power Tech Lab | 312 | 20 |  | 1472 | 33 | 20 | Unit Ventilator | 11776 | 1.5897 | 1 | 1.5897 | 1
S-02 A | Engineering Lab | 797 | 53 |  | 1985 | 45 | 45 | Unit Ventilator | 15880 | 3.0113 | 1 | 3.0113 | 1
S-03 | Visual Comm. Lab | 321 | 21 |  | 1379 | 31 | 21 | Unit Ventilator | 11032 | 1.7458 | 1 | 1.7458 | 1
Technology Lab | Classroom | 326 | 21 |  | 1025 | 23 | 21 | Unit Ventilator | 8200 | 2.3854 | 1 | 2.3854 | 1
- | Auditorium | 4818 | 321 |  | 4485 | 101 | 101 | AHU | 35880 | 8.0569 | 2 | 8.0569 | 2
Upper Level | Mayfair Multi-Purpose Room | 835 | 55 |  | 5781 | 131 | 55 | AHU | 46248 | 1.0833 | 1 | 1.0833 | 1
129A | Upper Level Pod #1 Classroom | 264 | 17 |  | 731 | 16 | 16 | AHU | 5848 | 2.7086 | 1 | 2.7086 | 1
Upper Level Pod #1 | Core | 309 | 20 |  | 540 | 12 | 12 | AHU | 4320 | 4.2917 | 2 | 4.2917 | 2
Upper Level Pod #1 | Deans Office | 355 | 23 |  | 480 | 10 | 10 | AHU | 3840 | 5.5469 | 2 | 5.5469 | 2
Upper Level Pod #1 | Pod Center Core | 0 | 0 |  | 616 | 14 | 0 | AHU | 4928 | 0 | 0 | 0 | 0
430 | Upper Level Multi-Purpose Mayfair Classroom | 90 | 6 | Yes | 1249 | 28 | 28 | AHU | 9992 | 0.54043 | 0 | 20.5404 | 3
431 | Upper Level Multi-Purpose Mayfair Classroom | 136 | 9 | Yes | 789 | 17 | 17 | AHU | 6312 | 1.2928 | 1 | 21.2928 | 3
Upper Level Pod #2 | Core | 0 | 0 |  | 425 | 9 | 0 | AHU | 3400 | 0 | 0 | 0 | 0
432 | Upper Level Pod #2 Lab B/C (Mayfair Room) | 212 | 14 | Yes | 928 | 21 | 21 | AHU | 7424 | 1.7134 | 1 | 21.7134 | 3
433 | Upper Level Pod #2 Mayfair Kindergarten (Mayfair Room) | 184 | 12 | Yes | 1145 | 26 | 26 | AHU | 9160 | 1.2052 | 1 | 21.2052 | 3
Upper Level Pod #2 | Pod Center Core | 0 | 0 |  | 2968 | 67 | 0 | AHU | 23744 | 0 | 0 | 0 | 0
Upper Level Pod #3 | Center Core | 0 | 0 |  | 616 | 14 | 0 | AHU | 4928 | 0 | 0 | 0 | 0
Upper Level Pod #3 | Lab C Classroom | 187 | 12 |  | 806 | 18 | 12 | AHU | 6448 | 1.7401 | 1 | 1.7401 | 1
Upper Level Pod #3 | Lab Office | 28 | 1 |  | 120 | 2 | 1 | AHU | 960 | 1.75 | 1 | 1.75 | 1
Upper Level Pod #3 | Pod Center Core | 0 | 0 |  | 2968 | 67 | 0 | AHU | 23744 | 0 | 0 | 0 | 0
Upper Level Pod #4 | Mayfair Center Core | 174 | 11 |  | 4366 | 99 | 11 | AHU | 34928 | 0.2989 | 0 | 0.2989 | 0
429 | Upper Level Pod #4 Mayfair Classroom | 263 | 17 |  | 1008 | 22 | 17 | AHU | 8064 | 1.9568 | 1 | 1.9568 | 1
Upper Level Pod #4 | Mayfair Counselor Office | 79 | 5 |  | 132 | 3 | 3 | AHU | 1056 | 4.4886 | 2 | 4.4886 | 2
Upper Level Pod #4 | Mayfair Multi-Purpose Room | 424 | 28 |  | 4662 | 105 | 28 | AHU | 37296 | 0.68211 | 0 | 0.68211 | 0
Upper Level Pod #4 | Mayfair Principal Office | 83 | 5 |  | 180 | 4 | 4 | AHU | 1440 | 3.4583 | 1 | 3.4583 | 1
Weight Room | Classroom | 107 | 7 |  | 210 | 4 | 4 | AHU | 1680 | 3.8214 | 1 | 3.8214 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | William M. Meredith Elementary-Middle School | [8 empty] | unk | unk | unk | unk
| William M. Meredith Elementary-Middle School Modular Building | [8 empty] | unk | unk | unk | unk
Vendor: | Capital | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Main Building | [9 empty] | unk | unk | unk | unk
B5 | Classroom |  | 0 | Yes | 696 | 15 | 15 |  | 5568 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 690 | 15 | 15 |  | 5520 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 690 | 15 | 15 |  | 5520 | unk | unk | 20 | 3
104 | Classroom |  | 0 | Yes | 690 | 15 | 15 |  | 5520 | unk | unk | 20 | 3
105 | Classroom |  | 0 | Yes | 920 | 20 | 20 |  | 7360 | unk | unk | 20 | 3
106 | Classroom |  | 0 | Yes | 816 | 18 | 18 |  | 6528 | unk | unk | 20 | 3
107 | Classroom |  | 0 | Yes | 664 | 15 | 15 |  | 5312 | unk | unk | 20 | 3
108 | Classroom |  | 0 | Yes | 664 | 15 | 15 |  | 5312 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 690 | 15 | 15 |  | 5520 | unk | unk | 20 | 3
204.5 | Classroom |  | 0 | Yes | 425 | 9 | 9 |  | 3400 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 782 | 17 | 17 |  | 6256 | unk | unk | 20 | 3
206 | Classroom |  | 0 | Yes | 759 | 17 | 17 |  | 6072 | unk | unk | 20 | 3
206A | Classroom |  | 0 | Yes | 368 | 8 | 8 |  | 2944 | unk | unk | 20 | 3
207 | Classroom |  | 0 | Yes | 506 | 11 | 11 |  | 4048 | unk | unk | 20 | 3
208 | Classroom |  | 0 | Yes | 664 | 15 | 15 |  | 5312 | unk | unk | 20 | 3
301 | Classroom |  | 0 | Yes | 696 | 15 | 15 |  | 5568 | unk | unk | 20 | 3
302 | Classroom |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | unk | unk | 20 | 3
303 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | unk | unk | 20 | 3
304 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
305 | Classroom |  | 0 | Yes | 1210 | 27 | 27 |  | 9680 | unk | unk | 20 | 3
306 | Classroom |  | 0 | Yes | 782 | 17 | 17 |  | 6256 | unk | unk | 20 | 3
307 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
308 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
309 | Classroom |  | 0 | Yes | 648 | 14 | 14 |  | 5184 | unk | unk | 20 | 3
309A | Classroom |  | 0 |  | 420 | 9 | 0 |  | 3360 | unk | unk | unk | unk
- | Auditorium |  | 0 |  | 3185 | 72 | 0 |  | 25480 | unk | unk | unk | unk
- | Counselors Office |  | 0 | Yes | 375 | 8 | 8 |  | 3000 | unk | unk | 20 | 3
- | Gym |  | 0 |  | 3723 | 84 | 0 |  | 29784 | unk | unk | unk | unk
- | Library |  | 0 | Yes | 1298 | 29 | 29 |  | 10384 | unk | unk | 20 | 3
- | Lunchroom |  | 0 |  | 2250 | 51 | 0 |  | 18000 | unk | unk | unk | unk
- | Main office |  | 0 | Yes | 368 | 8 | 8 |  | 2944 | unk | unk | 20 | 3
- | Nurses Office |  | 0 | Yes | 168 | 3 | 3 |  | 1344 | unk | unk | 20 | 3
- | Principals office |  | 0 | Yes | 256 | 5 | 5 |  | 2048 | unk | unk | 20 | 3
- | Psych Office #1 |  | 0 |  | 138 | 3 | 0 |  | 1104 | unk | unk | unk | unk
- | Psych Office #2 |  | 0 |  | 88 | 2 | 0 |  | 704 | unk | unk | unk | unk
- | Teachers Lounge |  | 0 |  | 322 | 7 | 0 |  | 2576 | unk | unk | unk | unk
Modular Building | [9 empty] | unk | unk | unk | unk
1 | Classroom | 368 | 24 |  | 720 | 16 | 16 | AHU | 5760 | 3.8333 | 1 | 3.8333 | 1
2 | Classroom | 378 | 25 |  | 720 | 16 | 16 | AHU | 5760 | 3.9375 | 1 | 3.9375 | 1
3 | Classroom | 381 | 25 |  | 720 | 16 | 16 | AHU | 5760 | 3.9688 | 1 | 3.9688 | 1
4 | Classroom | 374 | 24 |  | 720 | 16 | 16 | AHU | 5760 | 3.8958 | 1 | 3.8958 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | Thomas Mifflin Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | Part 2 | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 253 | 16 | Yes | 794 | 18 | 18 | Unit Ventilator | 6352 | 2.3898 | 1 | 22.3898 | 3
102 | Classroom | 555 | 37 |  | 1040 | 23 | 23 | Unit Ventilator | 8320 | 4.0024 | 2 | 4.0024 | 2
103 | Classroom | 288 | 19 |  | 375 | 8 | 8 | Unit Ventilator | 3000 | 5.76 | 2 | 5.76 | 2
104 | Classroom | 270 | 18 |  | 537 | 12 | 12 | Unit Ventilator | 4296 | 3.7709 | 1 | 3.7709 | 1
105 | Classroom | 395 | 26 |  | 484 | 11 | 11 | Unit Ventilator | 3872 | 6.1209 | 2 | 6.1209 | 2
106 | Classroom | 422 | 28 |  | 682 | 15 | 15 | Unit Ventilator | 5456 | 4.6408 | 2 | 4.6408 | 2
107 | Classroom | 330 | 22 |  | 658 | 14 | 14 | Unit Ventilator | 5264 | 3.7614 | 1 | 3.7614 | 1
108 | Classroom | 439 | 29 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.7717 | 2 | 4.7717 | 2
109 | Classroom | 230 | 15 |  | 662 | 15 | 15 | Unit Ventilator | 5296 | 2.6057 | 1 | 2.6057 | 1
110 | Classroom | 348 | 23 |  | 669 | 15 | 15 | Unit Ventilator | 5352 | 3.9013 | 1 | 3.9013 | 1
111 | Classroom | 587 | 39 |  | 531 | 12 | 12 | Unit Ventilator | 4248 | 8.291 | 2 | 8.291 | 2
114 | Classroom | 0 | 0 | Yes | 630 | 14 | 14 | Unit Ventilator | 5040 | 0 | 0 | 20 | 3
115 | Classroom | 0 | 0 | Yes | 684 | 15 | 15 | Unit Ventilator | 5472 | 0 | 0 | 20 | 3
128 (117) | Counselor Office | 376 | 25 |  | 350 | 7 | 7 | Unit Ventilator | 2800 | 8.0571 | 2 | 8.0571 | 2
201 | Classroom | 595 | 39 |  | 775 | 17 | 17 | Unit Ventilator | 6200 | 5.7581 | 2 | 5.7581 | 2
202 | Classroom | 638 | 42 |  | 764 | 17 | 17 | Unit Ventilator | 6112 | 6.2631 | 2 | 6.2631 | 2
203 | Classroom | 300 | 20 |  | 340 | 7 | 7 | Unit Ventilator | 2720 | 6.6176 | 2 | 6.6176 | 2
204 | Classroom | 354 | 23 |  | 639 | 14 | 14 | Unit Ventilator | 5112 | 4.1549 | 2 | 4.1549 | 2
205 | Classroom | 458 | 30 |  | 682 | 15 | 15 | Unit Ventilator | 5456 | 5.0367 | 2 | 5.0367 | 2
206 | Classroom | 432 | 28 |  | 688 | 15 | 15 | Unit Ventilator | 5504 | 4.7093 | 2 | 4.7093 | 2
207 | Classroom | 606 | 40 |  | 686 | 15 | 15 | Unit Ventilator | 5488 | 6.6254 | 2 | 6.6254 | 2
209 | Classroom | 241 | 16 |  | 686 | 15 | 15 | Unit Ventilator | 5488 | 2.6348 | 1 | 2.6348 | 1
210 | Classroom | 598 | 39 |  | 1380 | 31 | 31 | Unit Ventilator | 11040 | 3.25 | 1 | 3.25 | 1
211 | Classroom | 408 | 27 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 4.4348 | 2 | 4.4348 | 2
212 | Meeting Room | 1055 | 70 |  | 312 | 7 | 7 | Unit Ventilator | 2496 | 25.3606 | 4 | 25.3606 | 4
215 | Classroom |  | 0 | Yes | 323 | 7 | 7 | Unit Ventilator | 2584 | unk | unk | 20 | 3
- | Auditorium | 0 | 0 |  | 3837 | 87 | 0 | House Fan | 30696 | 0 | 0 | 0 | 0
- | Cafeteria | 270 | 18 | Yes | 2128 | 48 | 48 | Unit Ventilator | 17024 | 0.9516 | 0 | 20.9516 | 3
- | Cafeteria Hall | 0 | 0 |  | 738 | 16 | 0 | Unit Ventilator | 5904 | 0 | 0 | 0 | 0
- | Library | 403 | 26 |  | 3024 | 68 | 26 | Unit Ventilator | 24192 | 0.9995 | 0 | 0.9995 | 0
- | Music Room | 425 | 28 |  | 966 | 21 | 21 | Unit Ventilator | 7728 | 3.2997 | 1 | 3.2997 | 1
Pre-K 3 | Classroom | 489 | 32 |  | 972 | 22 | 22 | Unit Ventilator | 7776 | 3.7731 | 1 | 3.7731 | 1
Pre-K 4 | Classroom | 335 | 22 |  | 920 | 20 | 20 | Unit Ventilator | 7360 | 2.731 | 1 | 2.731 | 1
- | Main Office |  | 0 | Yes | 552 | 12 | 12 |  | 4416 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 390 | 8 | 8 |  | 3120 | unk | unk | 20 | 3
- | Nurses Office |  | 0 | Yes | 192 | 4 | 4 |  | 1536 | unk | unk | 20 | 3
- | Gym | 4205 | 280 |  | 5280 | 120 | 120 | RTU | 42240 | 5.973 | 2 | 5.973 | 2
6 | Speech |  | 0 | Yes | 544 | 12 | 12 |  | 4352 | unk | unk | 20 | 3
8 | Classroom |  | 0 | Yes | 851 | 19 | 19 |  | 6808 | unk | unk | 20 | 3
20 | Special Needs |  | 0 | Yes | 661 | 15 | 15 |  | 5288 | unk | unk | 20 | 3
- | Spanish Classroom | 0 | 0 | Yes | 900 | 20 | 20 | Unit Ventilator | 7200 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-28 | [8 empty] | unk | unk | unk | unk
School: | E. Spencer Miller- Philadelphia Learning Academy South (9-12) and Crossroads Acelerated Academy (7-8) | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
153 | Office | 0 | 0 |  | 187 | 4 | 0 |  | 1496 | 0 | 0 | 0 | 0
158 | School Police Office | 267 | 17 |  | 540 | 12 | 12 |  | 4320 | 3.7083 | 1 | 3.7083 | 1
167 | Staff Lounge | 0 | 0 |  | 532 | 12 | 0 |  | 4256 | 0 | 0 | 0 | 0
170 | Office | 0 | 0 |  | 99 | 2 | 0 |  | 792 | 0 | 0 | 0 | 0
175 | Office | 0 | 0 |  | 154 | 3 | 0 |  | 1232 | 0 | 0 | 0 | 0
181 | Office | 49 | 3 |  | 344 | 7 | 3 |  | 2752 | 1.0683 | 1 | 1.0683 | 1
183 | Office | 10 | 0 |  | 110 | 2 | 0 |  | 880 | 0.68182 | 0 | 0.68182 | 0
184 | Office | 7 | 0 |  | 100 | 2 | 0 |  | 800 | 0.525 | 0 | 0.525 | 0
185 | Office | 17 | 1 |  | 220 | 5 | 1 |  | 1760 | 0.57955 | 0 | 0.57955 | 0
186 | Office | 27 | 1 |  | 208 | 4 | 1 |  | 1664 | 0.97356 | 0 | 0.97356 | 0
188 | Office | 201 | 13 |  | 77 | 1 | 1 |  | 616 | 19.5779 | 3 | 19.5779 | 3
192 | Office | 289 | 19 |  | 111 | 2 | 2 |  | 888 | 19.527 | 3 | 19.527 | 3
245 | Office | 17 | 1 |  | 170 | 3 | 1 |  | 1360 | 0.75 | 0 | 0.75 | 0
246 | Office | 41 | 2 |  | 131 | 2 | 2 |  | 1048 | 2.3473 | 1 | 2.3473 | 1
247 | Office | 33 | 2 |  | 167 | 3 | 2 |  | 1336 | 1.482 | 1 | 1.482 | 1
248 | Office | 0 | 0 |  | 152 | 3 | 0 |  | 1216 | 0 | 0 | 0 | 0
252 | Office | 0 | 0 |  | 516 | 11 | 0 |  | 4128 | 0 | 0 | 0 | 0
254 | Office | 166 | 11 |  | 231 | 5 | 5 |  | 1848 | 5.3896 | 2 | 5.3896 | 2
255 | Office | 46 | 3 |  | 98 | 2 | 2 |  | 784 | 3.5204 | 1 | 3.5204 | 1
256 | Office | 94 | 6 |  | 140 | 3 | 3 |  | 1120 | 5.0357 | 2 | 5.0357 | 2
257 | Office | 396 | 26 |  | 120 | 2 | 2 |  | 960 | 24.75 | 4 | 24.75 | 4
258 | Office | 58 | 3 |  | 531 | 12 | 3 |  | 4248 | 0.81921 | 0 | 0.81921 | 0
262 | Office | 111 | 7 |  | 102 | 2 | 2 |  | 816 | 8.1618 | 2 | 8.1618 | 2
266 | Office | 762 | 50 |  | 381 | 8 | 8 |  | 3048 | 15 | 3 | 15 | 3
267 | Office | 949 | 63 |  | 437 | 9 | 9 |  | 3496 | 16.2872 | 3 | 16.2872 | 3
274 | Office | 192 | 12 |  | 148 | 3 | 3 |  | 1184 | 9.7297 | 2 | 9.7297 | 2
275 | Office | 130 | 8 |  | 117 | 2 | 2 |  | 936 | 8.3333 | 2 | 8.3333 | 2
276 | Office | 72 | 4 |  | 101 | 2 | 2 |  | 808 | 5.3465 | 2 | 5.3465 | 2
277 | Office | 176 | 11 |  | 147 | 3 | 3 |  | 1176 | 8.9796 | 2 | 8.9796 | 2
278 | Office | 107 | 7 |  | 109 | 2 | 2 |  | 872 | 7.3624 | 2 | 7.3624 | 2
279 | Office | 104 | 6 |  | 106 | 2 | 2 |  | 848 | 7.3585 | 2 | 7.3585 | 2
280 | Office | 287 | 19 |  | 254 | 5 | 5 |  | 2032 | 8.4744 | 2 | 8.4744 | 2
282 | Office | 311 | 20 |  | 272 | 6 | 6 |  | 2176 | 8.5754 | 2 | 8.5754 | 2
286 | Office | 636 | 42 |  | 290 | 6 | 6 |  | 2320 | 16.4483 | 3 | 16.4483 | 3
287 | Office | 104 | 6 |  | 107 | 2 | 2 |  | 856 | 7.2897 | 2 | 7.2897 | 2
290 | Office | 108 | 7 |  | 132 | 3 | 3 |  | 1056 | 6.1364 | 2 | 6.1364 | 2
291 | Office | 107 | 7 |  | 151 | 3 | 3 |  | 1208 | 5.3146 | 2 | 5.3146 | 2
292 | Office | 210 | 14 |  | 150 | 3 | 3 |  | 1200 | 10.5 | 3 | 10.5 | 3
293 | Office | 186 | 12 |  | 153 | 3 | 3 |  | 1224 | 9.1176 | 2 | 9.1176 | 2
- | 1st Flr Computer Room | 0 | 0 |  | 240 | 5 | 0 |  | 1920 | 0 | 0 | 0 | 0
- | 1st Flr Corrider by B & E Section | 0 | 0 |  | 320 | 7 | 0 |  | 2560 | 0 | 0 | 0 | 0
- | 1st Flr Kitchen | 8316 | 554 |  | 924 | 21 | 21 |  | 7392 | 67.5 | 5 | 67.5 | 5
- | 1st Flr Kitchen Dry Food Area | 171 | 11 |  | 187 | 4 | 4 |  | 1496 | 6.8583 | 2 | 6.8583 | 2
- | 1st Flr Kitchen Freezer Area | 85 | 5 |  | 420 | 9 | 5 |  | 3360 | 1.5179 | 1 | 1.5179 | 1
- | 1st Flr Mechanical Room | 19 | 1 |  | 336 | 7 | 1 |  | 2688 | 0.42411 | 0 | 0.42411 | 0
- | 2nd Floor Conference Room | 359 | 23 |  | 216 | 4 | 4 |  | 1728 | 12.4653 | 3 | 12.4653 | 3
- | 2nd Floor Corridor by Elevator | 363 | 24 |  | 463 | 10 | 10 |  | 3704 | 5.8801 | 2 | 5.8801 | 2
- | 2nd Floor Meeting Room | 139 | 9 |  | 79 | 1 | 1 |  | 632 | 13.1962 | 3 | 13.1962 | 3
- | 2nd Floor Mens Restroom by Elevator | 138 | 9 |  | 255 | 5 | 5 |  | 2040 | 4.0588 | 2 | 4.0588 | 2
- | 2nd Floor Restroom Vestibule by Elevator | 157 | 10 |  | 73 | 1 | 1 |  | 584 | 16.1301 | 3 | 16.1301 | 3
- | 2nd Floor Womans Restroom by Elevator | 114 | 7 |  | 167 | 3 | 3 |  | 1336 | 5.1198 | 2 | 5.1198 | 2
- | 2nd Flr Corridor by Admin Office | 195 | 13 |  | 218 | 4 | 4 |  | 1744 | 6.7087 | 2 | 6.7087 | 2
- | 2nd Flr Corridor by G Section | 45 | 3 |  | 458 | 10 | 3 |  | 3664 | 0.7369 | 0 | 0.7369 | 0
- | 2nd Flr Reception Office | 170 | 11 |  | 116 | 2 | 2 |  | 928 | 10.9914 | 3 | 10.9914 | 3
- | 1st Flr A - Common Area | 48 | 3 |  | 1251 | 28 | 3 |  | 10008 | 0.28777 | 0 | 0.28777 | 0
A1 | Classroom | 58 | 3 |  | 960 | 21 | 3 |  | 7680 | 0.45312 | 0 | 0.45312 | 0
A2 | Classroom | 66 | 4 |  | 990 | 22 | 4 |  | 7920 | 0.5 | 0 | 0.5 | 0
A3 | Classroom | 60 | 4 |  | 990 | 22 | 4 |  | 7920 | 0.45455 | 0 | 0.45455 | 0
A4 | Classroom | 56 | 3 |  | 997 | 22 | 3 |  | 7976 | 0.42126 | 0 | 0.42126 | 0
- | 1st Flr B - Common Area | 747 | 49 |  | 960 | 21 | 21 |  | 7680 | 5.8359 | 2 | 5.8359 | 2
B1 | Classroom | 304 | 20 |  | 868 | 19 | 19 |  | 6944 | 2.6267 | 1 | 2.6267 | 1
B2 | Classroom | 488 | 32 |  | 945 | 21 | 21 |  | 7560 | 3.873 | 1 | 3.873 | 1
B3 | Classroom | 942 | 62 |  | 980 | 22 | 22 |  | 7840 | 7.2092 | 2 | 7.2092 | 2
B4 | Classroom | 961 | 64 |  | 910 | 20 | 20 |  | 7280 | 7.9203 | 2 | 7.9203 | 2
- | C - Common Area 1st Flr | 1014 | 67 |  | 1285 | 29 | 29 |  | 10280 | 5.9183 | 2 | 5.9183 | 2
C-1 | Classroom | 885 | 59 |  | 816 | 18 | 18 |  | 6528 | 8.1342 | 2 | 8.1342 | 2
C-2 | Classroom | 1047 | 69 |  | 840 | 19 | 19 |  | 6720 | 9.3482 | 2 | 9.3482 | 2
C-3 | Classroom | 1200 | 80 |  | 840 | 19 | 19 |  | 6720 | 10.7143 | 3 | 10.7143 | 3
C-4 | Classroom | 828 | 55 |  | 868 | 19 | 19 |  | 6944 | 7.1544 | 2 | 7.1544 | 2
- | Climate Masters Office | 150 | 10 |  | 821 | 18 | 10 |  | 6568 | 1.3703 | 1 | 1.3703 | 1
- | Computer Support Specialist Office | 102 | 6 |  | 88 | 2 | 2 |  | 704 | 8.6932 | 2 | 8.6932 | 2
- | Corridor 2nd Floor near office 252 | 0 | 0 |  | 376 | 8 | 0 |  | 3008 | 0 | 0 | 0 | 0
- | 1st Flr Corridor By B Section | 0 | 0 |  | 360 | 8 | 0 |  | 2880 | 0 | 0 | 0 | 0
- | Corridor by D Section | 713 | 47 |  | 438 | 9 | 9 |  | 3504 | 12.2089 | 3 | 12.2089 | 3
- | Corridor by Main Office | 38 | 2 |  | 610 | 13 | 2 |  | 4880 | 0.46721 | 0 | 0.46721 | 0
- | Corridor by Office 258 | 107 | 7 |  | 160 | 3 | 3 |  | 1280 | 5.0156 | 2 | 5.0156 | 2
- | 2nd Flr D - Common Area | 202 | 13 |  | 910 | 20 | 13 |  | 7280 | 1.6648 | 1 | 1.6648 | 1
D1 | Classroom | 206 | 13 |  | 960 | 21 | 13 |  | 7680 | 1.6094 | 1 | 1.6094 | 1
D2 | Classroom | 132 | 8 |  | 901 | 20 | 8 |  | 7208 | 1.0988 | 1 | 1.0988 | 1
D3 | Classroom | 268 | 17 |  | 1007 | 22 | 17 |  | 8056 | 1.996 | 1 | 1.996 | 1
D4 | Classroom | 209 | 13 |  | 972 | 22 | 13 |  | 7776 | 1.6127 | 1 | 1.6127 | 1
- | Dr. Graham Principal Office | 111 | 7 |  | 823 | 18 | 7 |  | 6584 | 1.0115 | 1 | 1.0115 | 1
- | 2nd Flr E - Common Area | 431 | 28 |  | 934 | 21 | 21 |  | 7472 | 3.4609 | 1 | 3.4609 | 1
E1 | Classroom | 633 | 42 |  | 919 | 20 | 20 |  | 7352 | 5.1659 | 2 | 5.1659 | 2
E2 | Classroom | 593 | 39 |  | 1021 | 23 | 23 |  | 8168 | 4.356 | 2 | 4.356 | 2
E3 | Classroom | 594 | 39 |  | 1046 | 23 | 23 |  | 8368 | 4.2591 | 2 | 4.2591 | 2
E4 | Classroom | 647 | 43 |  | 984 | 22 | 22 |  | 7872 | 4.9314 | 2 | 4.9314 | 2
- | 2nd Flr G - Common Area | 12 | 0 |  | 1214 | 27 | 0 |  | 9712 | 0.074135 | 0 | 0.074135 | 0
G1 | Classroom | 40 | 2 |  | 862 | 19 | 2 |  | 6896 | 0.34803 | 0 | 0.34803 | 0
G2 | Classroom | 29 | 1 |  | 878 | 19 | 1 |  | 7024 | 0.24772 | 0 | 0.24772 | 0
G3 | Classroom | 26 | 1 |  | 884 | 20 | 1 |  | 7072 | 0.22059 | 0 | 0.22059 | 0
G4 | Classroom | 33 | 2 |  | 872 | 19 | 2 |  | 6976 | 0.28383 | 0 | 0.28383 | 0
- | 1 st Flr Gym | 5785 | 385 |  | 3888 | 88 | 88 |  | 31104 | 11.1593 | 3 | 11.1593 | 3
- | Late Check Office | 0 | 0 |  | 96 | 2 | 0 |  | 768 | 0 | 0 | 0 | 0
- | Main Entrance | 5 | 0 |  | 64 | 1 | 0 |  | 512 | 0.58594 | 0 | 0.58594 | 0
- | 1st Flr Media Room | 524 | 34 |  | 1539 | 34 | 34 |  | 12312 | 2.5536 | 1 | 2.5536 | 1
- | Meeting Room | 21 | 1 |  | 90 | 2 | 1 |  | 720 | 1.75 | 1 | 1.75 | 1
- | Mens Restroom by Elevator | 26 | 1 |  | 190 | 4 | 1 |  | 1520 | 1.0263 | 1 | 1.0263 | 1
- | Nurses Office | 584 | 38 |  | 412 | 9 | 9 |  | 3296 | 10.6311 | 3 | 10.6311 | 3
- | Office Corridor | 228 | 15 |  | 702 | 15 | 15 |  | 5616 | 2.4359 | 1 | 2.4359 | 1
- | Parking Lot Entry | 0 | 0 |  | 135 | 3 | 0 |  | 1080 | 0 | 0 | 0 | 0
- | Reception | 47 | 3 |  | 521 | 11 | 3 |  | 4168 | 0.67658 | 0 | 0.67658 | 0
- | Restroom Vestibule Between A1/A2 | 6 | 0 |  | 56 | 1 | 0 |  | 448 | 0.80357 | 0 | 0.80357 | 0
- | Restroom Vestibule Between A3/A4 | 4 | 0 |  | 56 | 1 | 0 |  | 448 | 0.53571 | 0 | 0.53571 | 0
- | Restroom Vestibule Between B1/B2 | 83 | 5 |  | 63 | 1 | 1 |  | 504 | 9.881 | 2 | 9.881 | 2
- | Restroom Vestibule Between B3/B4 | 49 | 3 |  | 63 | 1 | 1 |  | 504 | 5.8333 | 2 | 5.8333 | 2
- | Restroom Vestibule Between C1/C2 | 89 | 5 |  | 56 | 1 | 1 |  | 448 | 11.9196 | 3 | 11.9196 | 3
- | Restroom Vestibule Between C3/C4 | 93 | 6 |  | 63 | 1 | 1 |  | 504 | 11.0714 | 3 | 11.0714 | 3
- | Restroom Vestibule Between D1/D2 | 20 | 1 |  | 50 | 1 | 1 |  | 400 | 3 | 1 | 3 | 1
- | Restroom Vestibule Between D3/D4 | 27 | 1 |  | 51 | 1 | 1 |  | 408 | 3.9706 | 1 | 3.9706 | 1
- | Restroom Vestibule Between E1/E2 | 55 | 3 |  | 51 | 1 | 1 |  | 408 | 8.0882 | 2 | 8.0882 | 2
- | Restroom Vestibule Between E3/E4 | 54 | 3 |  | 51 | 1 | 1 |  | 408 | 7.9412 | 2 | 7.9412 | 2
- | Restroom Vestibule Between G1/G2 | 3 | 0 |  | 50 | 1 | 0 |  | 400 | 0.45 | 0 | 0.45 | 0
- | Restroom Vestibule Between G3/G4 | 2 | 0 |  | 51 | 1 | 0 |  | 408 | 0.29412 | 0 | 0.29412 | 0
- | 1st Flr Storage Room | 61 | 4 |  | 475 | 10 | 4 |  | 3800 | 0.96316 | 0 | 0.96316 | 0
- | Truancy Office 1st Floor | 0 | 0 |  | 727 | 16 | 0 |  | 5816 | 0 | 0 | 0 | 0
- | Vestibule by stairs/Rooms 266 & 267 | 153 | 10 |  | 219 | 4 | 4 |  | 1752 | 5.2397 | 2 | 5.2397 | 2
- | Vistibule by Meeting Room | 132 | 8 |  | 252 | 5 | 5 |  | 2016 | 3.9286 | 1 | 3.9286 | 1
- | Womans Restroom by 1st Floor Elevator | 26 | 1 |  | 169 | 3 | 1 |  | 1352 | 1.1538 | 1 | 1.1538 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-05-03 | [8 empty] | unk | unk | unk | unk
School: | Mitchell Elementary School | [8 empty] | unk | unk | unk | unk
| EMCOR | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
104 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
105 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
106 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
107 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
108 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
109 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
110 | Counselor's Office |  | 0 | Yes | 255 | 5 | 5 | House Fan | 2040 | unk | unk | 20 | 3
111 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
112 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
213 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
214 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
215 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
216 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
217 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
218 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
219 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
220 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
221 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
222 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
223 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
225 | Nurse |  | 0 | Yes | 378 | 8 | 8 | House Fan | 3024 | unk | unk | 20 | 3
324 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
325 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
326 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
327 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
328 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
329 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
330 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
331 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
332 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
333 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
334 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
B1 | Classroom |  | 0 | Yes | 756 | 17 | 17 | Unit Ventilator | 6048 | unk | unk | 20 | 3
B2 | B.E. Office |  | 0 | Yes | 200 | 4 | 4 |  | 1600 | unk | unk | 20 | 3
B3 | Classroom |  | 0 | Yes | 609 | 13 | 13 | Unit Ventilator | 4872 | unk | unk | 20 | 3
B4 | Classroom |  | 0 | Yes | 980 | 22 | 22 | Unit Ventilator | 7840 | unk | unk | 20 | 3
B6 | Classroom |  | 0 | Yes | 1344 | 30 | 30 | Unit Ventilator | 10752 | unk | unk | 20 | 3
- | SP Office |  | 0 | Yes | 88 | 2 | 2 |  | 704 | unk | unk | 20 | 3
- | Library |  | 0 | Yes | 1504 | 34 | 34 |  | 12032 | unk | unk | 20 | 3
- | Gym |  | 0 | Yes | 3495 | 79 | 79 | House Fan | 27960 | unk | unk | 20 | 3
- | Cafeteria Office |  | 0 | Yes | 134 | 3 | 3 |  | 1072 | unk | unk | 20 | 3
- | Cafeteria |  | 0 | Yes | 2452 | 55 | 55 | House Fan | 19616 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 494 | 11 | 11 | House Fan | 3952 | unk | unk | 20 | 3
- | Principal's Office |  | 0 | Yes | 216 | 4 | 4 | House Fan | 1728 | unk | unk | 20 | 3
110C | Vice Principal's Office |  | 0 | Yes | 101 | 2 | 2 |  | 808 | unk | unk | 20 | 3
110A | Administrative Assistant's Office |  | 0 | Yes | 191 | 4 | 4 |  | 1528 | unk | unk | 20 | 3
- | Teacher's Lounge/Multipurpose |  | 0 | Yes | 390 | 8 | 8 | House Fan | 3120 | unk | unk | 20 | 3
110B | Counselor's Office |  | 0 | Yes | 242 | 5 | 5 | House Fan | 1936 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-19 | [8 empty] | unk | unk | unk | unk
School: | The Promise Academy @ Martin Luther King High School | [8 empty] | unk | unk | unk | unk
Vendor: | Meehan (Auditorium) | Chadwick (Building) | Exhaust | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 464 | 30 |  | 828 | 18 | 18 |  | 6624 | 4.2029 | 2 | 4.2029 | 2
102 | Classroom | 315 | 21 |  | 828 | 18 | 18 |  | 6624 | 2.8533 | 1 | 2.8533 | 1
104 | Classroom | 260 | 17 |  | 900 | 20 | 17 |  | 7200 | 2.1667 | 1 | 2.1667 | 1
105 | Classroom | 162 | 10 |  | 1050 | 23 | 10 |  | 8400 | 1.1571 | 1 | 1.1571 | 1
106 | Classroom | 476 | 31 |  | 900 | 20 | 20 |  | 7200 | 3.9667 | 1 | 3.9667 | 1
107 | Classroom | 229 | 15 |  | 864 | 19 | 15 |  | 6912 | 1.9878 | 1 | 1.9878 | 1
108 | Classroom | 489 | 32 |  | 850 | 19 | 19 |  | 6800 | 4.3147 | 2 | 4.3147 | 2
109 | Classroom | 304 | 20 |  | 896 | 20 | 20 |  | 7168 | 2.5446 | 1 | 2.5446 | 1
110 | Classroom |  | 0 |  | 800 | 18 | 0 |  | 6400 | unk | unk | unk | unk
116 | Classroom |  | 0 |  | 800 | 18 | 0 |  | 6400 | unk | unk | unk | unk
117 | Classroom | 296 | 19 |  | 924 | 21 | 19 |  | 7392 | 2.4026 | 1 | 2.4026 | 1
118 | Classroom | 278 | 18 |  | 864 | 19 | 18 |  | 6912 | 2.4132 | 1 | 2.4132 | 1
120 | Classroom | 105 | 7 |  | 864 | 19 | 7 |  | 6912 | 0.91146 | 0 | 0.91146 | 0
121 | Classroom | 176 | 11 |  | 864 | 19 | 11 |  | 6912 | 1.5278 | 1 | 1.5278 | 1
122 | Classroom | 420 | 28 |  | 1152 | 26 | 26 |  | 9216 | 2.7344 | 1 | 2.7344 | 1
123 | Classroom | 86 | 5 |  | 864 | 19 | 5 |  | 6912 | 0.74653 | 0 | 0.74653 | 0
124 | Classroom | 252 | 16 |  | 900 | 20 | 16 |  | 7200 | 2.1 | 1 | 2.1 | 1
125 | Classroom | 203 | 13 |  | 864 | 19 | 13 |  | 6912 | 1.7622 | 1 | 1.7622 | 1
201 | Classroom | 215 | 14 |  | 828 | 18 | 14 |  | 6624 | 1.9475 | 1 | 1.9475 | 1
202 | Classroom | 201 | 13 |  | 864 | 19 | 13 |  | 6912 | 1.7448 | 1 | 1.7448 | 1
204 | Classroom |  | 0 |  | 900 | 20 | 0 |  | 7200 | unk | unk | unk | unk
205 | Classroom | 416 | 27 |  | 1050 | 23 | 23 |  | 8400 | 2.9714 | 1 | 2.9714 | 1
206 | Classroom | 47 | 3 |  | 900 | 20 | 3 |  | 7200 | 0.39167 | 0 | 0.39167 | 0
207 | Classroom | 90 | 6 |  | 864 | 19 | 6 |  | 6912 | 0.78125 | 0 | 0.78125 | 0
208 | Classroom | 212 | 14 |  | 850 | 19 | 14 |  | 6800 | 1.8706 | 1 | 1.8706 | 1
209 | Classroom | 360 | 24 |  | 896 | 20 | 20 |  | 7168 | 3.0134 | 1 | 3.0134 | 1
210 | Classroom | 0 | 0 |  | 800 | 18 | 0 |  | 6400 | 0 | 0 | 0 | 0
216 | Classroom | 469 | 31 |  | 800 | 18 | 18 |  | 6400 | 4.3969 | 2 | 4.3969 | 2
217 | Classroom | 130 | 8 |  | 924 | 21 | 8 |  | 7392 | 1.0552 | 1 | 1.0552 | 1
218 | Classroom | 293 | 19 |  | 864 | 19 | 19 |  | 6912 | 2.5434 | 1 | 2.5434 | 1
220 | Classroom | 318 | 21 |  | 864 | 19 | 19 |  | 6912 | 2.7604 | 1 | 2.7604 | 1
221 | Classroom | 204 | 13 |  | 864 | 19 | 13 |  | 6912 | 1.7708 | 1 | 1.7708 | 1
222 | Classroom | 210 | 14 |  | 1152 | 26 | 14 |  | 9216 | 1.3672 | 1 | 1.3672 | 1
223 | Classroom | 170 | 11 |  | 864 | 19 | 11 |  | 6912 | 1.4757 | 1 | 1.4757 | 1
224 | Classroom | 207 | 13 |  | 900 | 20 | 13 |  | 7200 | 1.725 | 1 | 1.725 | 1
225 | Classroom | 150 | 10 |  | 864 | 19 | 10 |  | 6912 | 1.3021 | 1 | 1.3021 | 1
301 | Classroom | 161 | 10 |  | 828 | 18 | 10 |  | 6624 | 1.4583 | 1 | 1.4583 | 1
302 | Classroom | 178 | 11 |  | 864 | 19 | 11 |  | 6912 | 1.5451 | 1 | 1.5451 | 1
303 | Classroom |  | 0 | Yes | 805 | 18 | 18 |  | 6440 | unk | unk | 20 | 3
304 | Classroom | 391 | 26 |  | 900 | 20 | 20 |  | 7200 | 3.2583 | 1 | 3.2583 | 1
305 | Classroom | 244 | 16 |  | 1050 | 23 | 16 |  | 8400 | 1.7429 | 1 | 1.7429 | 1
306 | Classroom | 347 | 23 |  | 900 | 20 | 20 |  | 7200 | 2.8917 | 1 | 2.8917 | 1
307 | Classroom | 99 | 6 |  | 864 | 19 | 6 |  | 6912 | 0.85938 | 0 | 0.85938 | 0
308 | Classroom | 217 | 14 |  | 850 | 19 | 14 |  | 6800 | 1.9147 | 1 | 1.9147 | 1
309 | Classroom | 65 | 4 |  | 896 | 20 | 4 |  | 7168 | 0.54408 | 0 | 0.54408 | 0
310 | Classroom | 347 | 23 |  | 800 | 18 | 18 |  | 6400 | 3.2531 | 1 | 3.2531 | 1
313 | Classroom |  | 0 | Yes | 1368 | 31 | 31 |  | 10944 | unk | unk | 20 | 3
316 | Classroom | 297 | 19 |  | 800 | 18 | 18 |  | 6400 | 2.7844 | 1 | 2.7844 | 1
317 | Classroom | 201 | 13 |  | 924 | 21 | 13 |  | 7392 | 1.6315 | 1 | 1.6315 | 1
318 | Classroom | 275 | 18 |  | 864 | 19 | 18 |  | 6912 | 2.3872 | 1 | 2.3872 | 1
320 | Classroom | 303 | 20 |  | 864 | 19 | 19 |  | 6912 | 2.6302 | 1 | 2.6302 | 1
321 | Classroom | 85 | 5 |  | 864 | 19 | 5 |  | 6912 | 0.73785 | 0 | 0.73785 | 0
322 | Classroom | 310 | 20 |  | 1152 | 26 | 20 |  | 9216 | 2.0182 | 1 | 2.0182 | 1
323 | Classroom | 310 | 20 |  | 864 | 19 | 19 |  | 6912 | 2.691 | 1 | 2.691 | 1
324 | Classroom | 213 | 14 |  | 900 | 20 | 14 |  | 7200 | 1.775 | 1 | 1.775 | 1
325 | Classroom | 84 | 5 |  | 864 | 19 | 5 |  | 6912 | 0.72917 | 0 | 0.72917 | 0
327 | Classroom |  | 0 | Yes | 1824 | 41 | 41 |  | 14592 | unk | unk | 20 | 3
- | Auditorium | 13590 | 906 |  | 4350 | 98 | 98 |  | 34800 | 23.431 | 3 | 23.431 | 3
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | John Moffet Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101A | Classroom | 97 | 6 |  | 360 | 8 | 6 | AHU | 2880 | 2.0208 | 1 | 2.0208 | 1
104 | Classroom | 225 | 15 |  | 704 | 16 | 15 | Unit Ventilator | 5632 | 2.397 | 1 | 2.397 | 1
105 | Classroom | 205 | 13 |  | 575 | 13 | 13 | Unit Ventilator | 4600 | 2.6739 | 1 | 2.6739 | 1
107 | Classroom | 271 | 18 |  | 805 | 18 | 18 | Unit Ventilator | 6440 | 2.5248 | 1 | 2.5248 | 1
108 | Classroom | 327 | 21 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 3.1362 | 1 | 3.1362 | 1
112 | Classroom | 524 | 34 |  | 896 | 20 | 20 | Unit Ventilator | 7168 | 4.3862 | 2 | 4.3862 | 2
113 | Classroom | 293 | 19 |  | 928 | 21 | 19 | Unit Ventilator | 7424 | 2.368 | 1 | 2.368 | 1
114 | Classroom | 441 | 29 |  | 986 | 22 | 22 | Unit Ventilator | 7888 | 3.3545 | 1 | 3.3545 | 1
115 | Classroom | 337 | 22 |  | 868 | 19 | 19 | Unit Ventilator | 6944 | 2.9119 | 1 | 2.9119 | 1
119 | Nurse | 178 | 11 |  | 77 | 1 | 1 | AHU | 616 | 17.3377 | 3 | 17.3377 | 3
201 | Classroom | 105 | 7 |  | 315 | 7 | 7 | Unit Ventilator | 2520 | 2.5 | 1 | 2.5 | 1
202 | Classroom | 745 | 49 |  | 891 | 20 | 20 | Unit Ventilator | 7128 | 6.271 | 2 | 6.271 | 2
203 | Classroom | 301 | 20 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 2.994 | 1 | 2.994 | 1
204 | Classroom | 357 | 23 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 3.5511 | 1 | 3.5511 | 1
205 | Classroom | 267 | 17 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 3.0022 | 1 | 3.0022 | 1
208 | Classroom | 183 | 12 |  | 924 | 21 | 12 | Unit Ventilator | 7392 | 1.4854 | 1 | 1.4854 | 1
209 | Classroom | 542 | 36 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 6.0945 | 2 | 6.0945 | 2
211 | Classroom | 543 | 36 |  | 648 | 14 | 14 | Unit Ventilator | 5184 | 6.2847 | 2 | 6.2847 | 2
213 | Classroom | 114 | 7 |  | 352 | 8 | 7 | Unit Ventilator | 2816 | 2.429 | 1 | 2.429 | 1
214 | Classroom | 210 | 14 |  | 957 | 21 | 14 | Unit Ventilator | 7656 | 1.6458 | 1 | 1.6458 | 1
215 | Classroom | 261 | 17 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 2.5962 | 1 | 2.5962 | 1
216 | Classroom | 470 | 31 |  | 754 | 17 | 17 | Unit Ventilator | 6032 | 4.6751 | 2 | 4.6751 | 2
217 | Classroom | 666 | 44 |  | 957 | 21 | 21 | Unit Ventilator | 7656 | 5.2194 | 2 | 5.2194 | 2
218 | Classroom | 260 | 17 |  | 330 | 7 | 7 | Unit Ventilator | 2640 | 5.9091 | 2 | 5.9091 | 2
219 | Classroom | 0 | 0 |  | 1100 | 25 | 0 | Unit Ventilator | 8800 | 0 | 0 | 0 | 0
221 | Classroom | 449 | 29 |  | 884 | 20 | 20 | Unit Ventilator | 7072 | 3.8094 | 1 | 3.8094 | 1
223 | Classroom | 403 | 26 |  | 340 | 7 | 7 | AHU | 2720 | 8.8897 | 2 | 8.8897 | 2
225 | Classroom | 266 | 17 |  | 858 | 19 | 17 | Unit Ventilator | 6864 | 2.3252 | 1 | 2.3252 | 1
228A | Classroom | 60 | 4 |  | 252 | 5 | 4 | AHU | 2016 | 1.7857 | 1 | 1.7857 | 1
229 | Classroom | 47 | 3 |  | 336 | 7 | 3 | AHU | 2688 | 1.0491 | 1 | 1.0491 | 1
- | Auditorium | 773 | 51 |  | 2478 | 56 | 51 | AHU | 19824 | 2.3396 | 1 | 2.3396 | 1
- | Faculty Lounge | 125 | 8 |  | 361 | 8 | 8 | Unit Ventilator | 2888 | 2.597 | 1 | 2.597 | 1
- | Library | 1025 | 68 |  | 1674 | 38 | 38 | AHU | 13392 | 4.5923 | 2 | 4.5923 | 2
- | Office | 110 | 7 |  | 70 | 1 | 1 | AHU | 560 | 11.7857 | 3 | 11.7857 | 3
- | Main Office | 87 | 5 |  | 496 | 11 | 5 | Unit Ventilator | 3968 | 1.3155 | 1 | 1.3155 | 1
- | Principals Office | 140 | 9 |  | 294 | 6 | 6 | Unit Ventilator | 2352 | 3.5714 | 1 | 3.5714 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | J. Hampton Moore Elementary School | [8 empty] | unk | unk | unk | unk
| Mobile Classrooms | Main Building | Little School House | [6 empty] | unk | unk | unk | unk
Vendor: | Devine | Main Retest | LSH Retest | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Moore Main | [9 empty] | unk | unk | unk | unk
- | Auditorium | 224 | 14 |  | 3015 | 68 | 14 | AHU | 24120 | 0.55721 | 0 | 0.55721 | 0
- | Gym | 145 | 9 | Yes | 4500 | 102 | 102 | AHU | 36000 | 0.24167 | 0 | 20.2417 | 3
101 | Classroom | 518 | 34 |  | 1055 | 23 | 23 | Univent | 8440 | 3.6825 | 1 | 3.6825 | 1
102 | Classroom | 504 | 33 |  | 1055 | 23 | 23 | Univent | 8440 | 3.5829 | 1 | 3.5829 | 1
103 | Classroom | 364 | 24 |  | 624 | 14 | 14 | Univent | 4992 | 4.375 | 2 | 4.375 | 2
104 | Classroom | 116 | 7 | Yes | 458 | 10 | 10 | Univent | 3664 | 1.8996 | 1 | 21.8996 | 3
105 | Classroom | 408 | 27 |  | 1082 | 24 | 24 | Univent | 8656 | 2.8281 | 1 | 2.8281 | 1
106 | Classroom | 237 | 15 | Yes | 951 | 21 | 21 | Univent | 7608 | 1.8691 | 1 | 21.8691 | 3
107 | Classroom | 535 | 35 |  | 951 | 21 | 21 | Univent | 7608 | 4.2192 | 2 | 4.2192 | 2
108 | Classroom | 503 | 33 |  | 951 | 21 | 21 | Univent | 7608 | 3.9669 | 1 | 3.9669 | 1
109 | Classroom | 220 | 14 | Yes | 951 | 21 | 21 | Univent | 7608 | 1.735 | 1 | 21.735 | 3
110 | Classroom | 113 | 7 | Yes | 951 | 21 | 21 | Univent | 7608 | 0.89117 | 0 | 20.8912 | 3
110A | Classroom | 237 | 15 |  | 951 | 21 | 15 | Univent | 7608 | 1.8691 | 1 | 1.8691 | 1
112 | Classroom | 325 | 21 |  | 951 | 21 | 21 | Univent | 7608 | 2.5631 | 1 | 2.5631 | 1
113 | Classroom | 472 | 31 |  | 951 | 21 | 21 | Univent | 7608 | 3.7224 | 1 | 3.7224 | 1
114 | Classroom | 487 | 32 |  | 951 | 21 | 21 | Univent | 7608 | 3.8407 | 1 | 3.8407 | 1
115 | Classroom | 236 | 15 |  | 383 | 8 | 8 | Univent | 3064 | 4.6214 | 2 | 4.6214 | 2
201 | Classroom | 480 | 32 |  | 976 | 22 | 22 | Univent | 7808 | 3.6885 | 1 | 3.6885 | 1
202 | Classroom | 319 | 21 |  | 976 | 22 | 21 | Univent | 7808 | 2.4513 | 1 | 2.4513 | 1
203 | Classroom | 251 | 16 | Yes | 951 | 21 | 21 | Univent | 7608 | 1.9795 | 1 | 21.9795 | 3
203B | Classroom |  | 0 | Yes | 624 | 14 | 14 |  | 4992 | unk | unk | 20 | 3
204 | Classroom | 291 | 19 | Yes | 951 | 21 | 21 | Univent | 7608 | 2.295 | 1 | 22.295 | 3
205A | Classroom | 261 | 17 | Yes | 452 | 10 | 10 | Univent | 3616 | 4.3308 | 2 | 24.3308 | 4
205B | Classroom | 130 | 8 | Yes | 642 | 14 | 14 | Univent | 5136 | 1.5187 | 1 | 21.5187 | 3
206 | Classroom | 326 | 21 |  | 970 | 22 | 21 | Univent | 7760 | 2.5206 | 1 | 2.5206 | 1
207 | Classroom | 424 | 28 |  | 951 | 21 | 21 | Univent | 7608 | 3.3438 | 1 | 3.3438 | 1
207A | Classroom |  | 0 | Yes | 239 | 5 | 5 | N/A | 1912 | unk | unk | 20 | 3
208 | Classroom | 527 | 35 |  | 951 | 21 | 21 | Univent | 7608 | 4.1562 | 2 | 4.1562 | 2
209 | Classroom | 399 | 26 |  | 951 | 21 | 21 | Univent | 7608 | 3.1467 | 1 | 3.1467 | 1
210A | Classroom | 108 | 7 | Yes | 458 | 10 | 10 | Univent | 3664 | 1.7686 | 1 | 21.7686 | 3
210B | Classroom | 335 | 22 | Yes | 458 | 10 | 10 | Univent | 3664 | 5.4858 | 2 | 25.4858 | 4
211 | Classroom | 433 | 28 |  | 951 | 21 | 21 | Univent | 7608 | 3.4148 | 1 | 3.4148 | 1
212 | Classroom | 244 | 16 | Yes | 951 | 21 | 21 | Univent | 7608 | 1.9243 | 1 | 21.9243 | 3
213 | Classroom | 0 | 0 | Yes | 951 | 21 | 21 | Univent | 7608 | 0 | 0 | 20 | 3
214 | Classroom | 64 | 4 | Yes | 820 | 18 | 18 | Univent | 6560 | 0.58537 | 0 | 20.5854 | 3
215 | Classroom | 454 | 30 |  | 951 | 21 | 21 | Univent | 7608 | 3.5804 | 1 | 3.5804 | 1
216 | Classroom | 444 | 29 |  | 951 | 21 | 21 | Univent | 7608 | 3.5016 | 1 | 3.5016 | 1
217 | Classroom | 520 | 34 |  | 951 | 21 | 21 | Univent | 7608 | 4.1009 | 2 | 4.1009 | 2
218 | Classroom | 347 | 23 |  | 951 | 21 | 21 | Univent | 7608 | 2.7366 | 1 | 2.7366 | 1
219 | Counselor Office |  | 0 | Yes | 170 | 3 | 3 |  | 1360 | unk | unk | 20 | 3
- | Principals Office | 0 | 0 | Yes | 400 | 9 | 9 |  | 3200 | 0 | 0 | 20 | 3
Assistant Principal | Office |  | 0 | Yes | 172 | 3 | 3 |  | 1376 | unk | unk | 20 | 3
Teachers Lounge | Room |  | 0 | Yes | 170 | 3 | 3 |  | 1360 | unk | unk | 20 | 3
2nd Floor Copy Room | Room |  | 0 | Yes | 172 | 3 | 3 |  | 1376 | unk | unk | 20 | 3
- | Nurse Office | 0 | 0 | Yes | 800 | 18 | 18 | Univent | 6400 | 0 | 0 | 20 | 3
Moore LSH | [9 empty] | unk | unk | unk | unk
- | Office | 224 | 14 |  | 200 | 4 | 4 | FCU | 1600 | 8.4 | 2 | 8.4 | 2
- | Kitchen | 145 | 9 |  | 624 | 14 | 9 | FCU | 4992 | 1.7428 | 1 | 1.7428 | 1
- | Faculty Lounge | 130 | 8 | Yes | 200 | 4 | 4 | FCU | 1600 | 4.875 | 2 | 24.875 | 4
P101 | Classroom |  | 0 | Yes | 120 | 2 | 2 |  | 960 | unk | unk | 20 | 3
P102 | Classroom |  | 0 | Yes | 120 | 2 | 2 |  | 960 | unk | unk | 20 | 3
P110 | Classroom | 361 | 24 |  | 950 | 21 | 21 | Univent | 7600 | 2.85 | 1 | 2.85 | 1
P111 | Classroom | 593 | 39 |  | 950 | 21 | 21 | Univent | 7600 | 4.6816 | 2 | 4.6816 | 2
P112 | Classroom | 379 | 25 |  | 950 | 21 | 21 | Univent | 7600 | 2.9921 | 1 | 2.9921 | 1
P113 | Classroom | 463 | 30 |  | 950 | 21 | 21 | Univent | 7600 | 3.6553 | 1 | 3.6553 | 1
P114 | Classroom | 747 | 49 |  | 950 | 21 | 21 | Univent | 7600 | 5.8974 | 2 | 5.8974 | 2
P114 | Hallway | 130 | 8 |  | 780 | 17 | 8 | FCU | 6240 | 1.25 | 1 | 1.25 | 1
P115 | Classroom | 361 | 24 |  | 950 | 21 | 21 | Univent | 7600 | 2.85 | 1 | 2.85 | 1
P116 | Classroom | 491 | 32 |  | 950 | 21 | 21 | Univent | 7600 | 3.8763 | 1 | 3.8763 | 1
P117 | Classroom | 430 | 28 |  | 950 | 21 | 21 | Univent | 7600 | 3.3947 | 1 | 3.3947 | 1
P124 | Classroom | 999 | 66 |  | 950 | 21 | 21 | Univent | 7600 | 7.8868 | 2 | 7.8868 | 2
P124 | Hallway | 80 | 5 |  | 1122 | 25 | 5 | FCU | 8976 | 0.53476 | 0 | 0.53476 | 0
P125 | Classroom | 476 | 31 |  | 950 | 21 | 21 | Univent | 7600 | 3.7579 | 1 | 3.7579 | 1
P126 | Classroom | 304 | 20 |  | 950 | 21 | 20 | Univent | 7600 | 2.4 | 1 | 2.4 | 1
P127 | Classroom | 1009 | 67 |  | 950 | 21 | 21 | Univent | 7600 | 7.9658 | 2 | 7.9658 | 2
Moore Modular | [9 empty] | unk | unk | unk | unk
A-1 | Classroom | 568 | 37 |  | 781 | 17 | 17 | Univent | 6248 | 5.4545 | 2 | 5.4545 | 2
A-2 | Classroom | 453 | 30 |  | 781 | 17 | 17 | Univent | 6248 | 4.3502 | 2 | 4.3502 | 2
A-3 | Classroom | 441 | 29 |  | 781 | 17 | 17 | Univent | 6248 | 4.235 | 2 | 4.235 | 2
A-4 | Classroom | 360 | 24 |  | 781 | 17 | 17 | Univent | 6248 | 3.4571 | 1 | 3.4571 | 1
A-5 | Classroom | 214 | 14 | Yes | 781 | 17 | 17 | Univent | 6248 | 2.0551 | 1 | 22.0551 | 3
A-6 | Classroom | 125 | 8 | Yes | 781 | 17 | 17 | Univent | 6248 | 1.2004 | 1 | 21.2004 | 3
A-7 | Classroom | 465 | 31 |  | 781 | 17 | 17 | Univent | 6248 | 4.4654 | 2 | 4.4654 | 2
A-8 | Classroom | 629 | 41 |  | 781 | 17 | 17 | Univent | 6248 | 6.0403 | 2 | 6.0403 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-12 | [8 empty] | unk | unk | unk | unk
School: | Robert Morris Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 192 | 12 | Yes | 1284 | 29 | 29 | Univent | 10272 | 1.1215 | 1 | 21.1215 | 3
101 | Classroom | 171 | 11 | Yes | 1410 | 32 | 32 | Univent | 11280 | 0.90957 | 0 | 20.9096 | 3
200 | Classroom | 185 | 12 | Yes | 858 | 19 | 19 | Univent | 6864 | 1.6171 | 1 | 21.6171 | 3
201 | Classroom | 72 | 4 | Yes | 603 | 13 | 13 | Univent | 4824 | 0.89552 | 0 | 20.8955 | 3
202 | Classroom | 218 | 14 |  | 849 | 19 | 14 | Univent | 6792 | 1.9258 | 1 | 1.9258 | 1
203 | Classroom | 200 | 13 | Yes | 821 | 18 | 18 | Univent | 6568 | 1.827 | 1 | 21.827 | 3
204 | Classroom | 163 | 10 | Yes | 846 | 19 | 19 | Univent | 6768 | 1.445 | 1 | 21.445 | 3
206 | Classroom | 85 | 5 |  | 847 | 19 | 5 | Univent | 6776 | 0.75266 | 0 | 0.75266 | 0
208 | Classroom | 152 | 10 |  | 830 | 18 | 10 | Univent | 6640 | 1.3735 | 1 | 1.3735 | 1
210 | Classroom | 0 | 0 |  | 837 | 19 | 0 | Univent | 6696 | 0 | 0 | 0 | 0
212 | Lunch Room | 137 | 9 |  | 876 | 19 | 9 | Univent | 7008 | 1.1729 | 1 | 1.1729 | 1
213 | Classroom | 74 | 4 |  | 875 | 19 | 4 | Univent | 7000 | 0.63429 | 0 | 0.63429 | 0
214 | Classroom | 125 | 8 |  | 848 | 19 | 8 | Univent | 6784 | 1.1055 | 1 | 1.1055 | 1
215 | Classroom | 286 | 19 |  | 840 | 19 | 19 | Univent | 6720 | 2.5536 | 1 | 2.5536 | 1
216 | Classroom | 94 | 6 |  | 848 | 19 | 6 | Univent | 6784 | 0.83137 | 0 | 0.83137 | 0
217 | Classroom | 114 | 7 | Yes | 463 | 10 | 10 | Univent | 3704 | 1.8467 | 1 | 21.8467 | 3
218 | Classroom | 283 | 18 |  | 1037 | 23 | 18 | Univent | 8296 | 2.0468 | 1 | 2.0468 | 1
219 | Kitchen | 261 | 17 |  | 1204 | 27 | 17 | Univent | 9632 | 1.6258 | 1 | 1.6258 | 1
300 | Classroom | 86 | 5 | Yes | 856 | 19 | 19 | Univent | 6848 | 0.7535 | 0 | 20.7535 | 3
301 | Classroom | 273 | 18 |  | 601 | 13 | 13 | Univent | 4808 | 3.4068 | 1 | 3.4068 | 1
302 | Classroom | 225 | 15 |  | 848 | 19 | 15 | Univent | 6784 | 1.99 | 1 | 1.99 | 1
303 | Classroom | 266 | 17 |  | 818 | 18 | 17 | Univent | 6544 | 2.4389 | 1 | 2.4389 | 1
304 | Classroom | 86 | 5 |  | 843 | 19 | 5 | Univent | 6744 | 0.76512 | 0 | 0.76512 | 0
306 | Classroom | 169 | 11 |  | 849 | 19 | 11 | Univent | 6792 | 1.4929 | 1 | 1.4929 | 1
308 | Classroom | 129 | 8 | Yes | 828 | 18 | 18 | Univent | 6624 | 1.1685 | 1 | 21.1685 | 3
310/312/314 | Library | 734 | 48 |  | 2102 | 47 | 47 | Univent | 16816 | 2.6189 | 1 | 2.6189 | 1
313 | Classroom | 264 | 17 |  | 975 | 22 | 17 | Univent | 7800 | 2.0308 | 1 | 2.0308 | 1
315 | Classroom | 217 | 14 |  | 1220 | 27 | 14 | Univent | 9760 | 1.334 | 1 | 1.334 | 1
316 | Classroom | 139 | 9 |  | 845 | 19 | 9 | Univent | 6760 | 1.2337 | 1 | 1.2337 | 1
317 | Classroom | 152 | 10 | Yes | 462 | 10 | 10 | Univent | 3696 | 2.4675 | 1 | 22.4675 | 3
319 | Art Room | 0 | 0 | Yes | 1042 | 23 | 23 | Univent | 8336 | 0 | 0 | 20 | 3
400 | Classroom | 58 | 3 |  | 857 | 19 | 3 | Univent | 6856 | 0.50758 | 0 | 0.50758 | 0
401 | Classroom | 121 | 8 | Yes | 602 | 13 | 13 | Univent | 4816 | 1.5075 | 1 | 21.5075 | 3
402 | Classroom | 169 | 11 |  | 846 | 19 | 11 | Univent | 6768 | 1.4982 | 1 | 1.4982 | 1
403 | Classroom | 498 | 33 |  | 817 | 18 | 18 | Univent | 6536 | 4.5716 | 2 | 4.5716 | 2
404 | Classroom | 92 | 6 |  | 848 | 19 | 6 | Univent | 6784 | 0.81368 | 0 | 0.81368 | 0
406 | Classroom | 60 | 4 |  | 845 | 19 | 4 | Univent | 6760 | 0.53254 | 0 | 0.53254 | 0
408 | Classroom | 55 | 3 | Yes | 829 | 18 | 18 | Univent | 6632 | 0.49759 | 0 | 20.4976 | 3
410 | Classroom | 0 | 0 |  | 849 | 19 | 0 | Univent | 6792 | 0 | 0 | 0 | 0
412 | Lunch Room | 106 | 7 |  | 858 | 19 | 7 | Univent | 6864 | 0.92657 | 0 | 0.92657 | 0
413 | Classroom | 313 | 20 |  | 871 | 19 | 19 | Univent | 6968 | 2.6952 | 1 | 2.6952 | 1
414 | Classroom | 291 | 19 |  | 847 | 19 | 19 | Univent | 6776 | 2.5767 | 1 | 2.5767 | 1
415 | Classroom | 147 | 9 | Yes | 836 | 19 | 19 | Univent | 6688 | 1.3188 | 1 | 21.3188 | 3
416 | Classroom | 106 | 7 | Yes | 847 | 19 | 19 | Univent | 6776 | 0.93861 | 0 | 20.9386 | 3
417 | Faculty | 158 | 10 |  | 446 | 10 | 10 | Univent | 3568 | 2.657 | 1 | 2.657 | 1
418 | Classroom | 34 | 2 | Yes | 1044 | 23 | 23 | Univent | 8352 | 0.24425 | 0 | 20.2443 | 3
419 | Music Room | 511 | 34 |  | 1040 | 23 | 23 | Univent | 8320 | 3.6851 | 1 | 3.6851 | 1
- | Auditorium | 1066 | 71 |  | 5308 | 120 | 71 | Univent | 42464 | 1.5062 | 1 | 1.5062 | 1
- | Counselor's Office | 70 | 4 |  | 474 | 10 | 4 | Univent | 3792 | 1.1076 | 1 | 1.1076 | 1
- | Gymnasium | 1100 | 73 |  | 3688 | 83 | 73 | Univent | 29504 | 2.237 | 1 | 2.237 | 1
- | Nurse's Office |  | 0 | Yes | 261 | 5 | 5 | N/A | 2088 | unk | unk | 20 | 3
- | Principal's Office |  | 0 | Yes | 294 | 6 | 6 | N/A | 2352 | unk | unk | 20 | 3
- | Main Office | 387 | 25 |  | 1373 | 31 | 25 | Univent | 10984 | 2.114 | 1 | 2.114 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | Andrew Morrison Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | EMCOR Retest 1-15-21 | Retest 2-22-21 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
5 | Music Rm |  | 0 | Yes | 813 | 18 | 18 | House Fan | 6504 | unk | unk | 20 | 3
8 | Art Rm |  | 0 | Yes | 886 | 20 | 20 | House Fan | 7088 | unk | unk | 20 | 3
101A | Nurse |  | 0 | Yes | 376 | 8 | 8 | House Fan | 3008 | unk | unk | 20 | 3
101B | Counselor |  | 0 |  | 341 | 7 | 0 | House Fan | 2728 | unk | unk | unk | unk
102 | Classroom |  | 0 | Yes | 701 | 15 | 15 | House Fan | 5608 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 734 | 16 | 16 | House Fan | 5872 | unk | unk | 20 | 3
104 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
106 | Lounge |  | 0 | Yes | 526 | 11 | 11 | House Fan | 4208 | unk | unk | 20 | 3
107 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
108 | Classroom |  | 0 | Yes | 566 | 12 | 12 | House Fan | 4528 | unk | unk | 20 | 3
109 | Classroom | 376 | 25 |  | 765 | 17 | 17 | Univent | 6120 | 3.6863 | 1 | 3.6863 | 1
110 | Classroom | 427 | 28 |  | 792 | 18 | 18 | Univent | 6336 | 4.0436 | 2 | 4.0436 | 2
111 | Classroom | 408 | 27 |  | 781 | 17 | 17 | Univent | 6248 | 3.9181 | 1 | 3.9181 | 1
112 | Classroom | 469 | 31 |  | 792 | 18 | 18 | Univent | 6336 | 4.4413 | 2 | 4.4413 | 2
113 | Classroom | 380 | 25 |  | 767 | 17 | 17 | Univent | 6136 | 3.7158 | 1 | 3.7158 | 1
114 | Office / Classroom | 271 | 18 |  | 351 | 7 | 7 | Univent | 2808 | 5.7906 | 2 | 5.7906 | 2
115 | Gym |  | 0 |  | 4693 | 106 | 0 | House Fan | 37544 | unk | unk | unk | unk
200 | Office |  | 0 |  | 168 | 3 | 0 | House Fan | 1344 | unk | unk | unk | unk
201 | Classroom |  | 0 |  | 726 | 16 | 0 | House Fan | 5808 | unk | unk | unk | unk
202 | Classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
203 | Classroom |  | 0 |  | 731 | 16 | 0 | House Fan | 5848 | unk | unk | unk | unk
204 | Classroom |  | 0 |  | 718 | 16 | 0 | House Fan | 5744 | unk | unk | unk | unk
204A | Office |  | 0 |  | 322 | 7 | 0 | House Fan | 2576 | unk | unk | unk | unk
204B | Office |  | 0 | Yes | 150 | 3 | 3 | N/A | 1200 | unk | unk | 20 | 3
204C | Office |  | 0 |  | 84 | 1 | 0 | N/A | 672 | unk | unk | unk | unk
205 | Classroom |  | 0 |  | 698 | 15 | 0 | House Fan | 5584 | unk | unk | unk | unk
206 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
207 | Classroom |  | 0 |  | 698 | 15 | 0 | House Fan | 5584 | unk | unk | unk | unk
208 | Classroom |  | 0 |  | 643 | 14 | 0 | House Fan | 5144 | unk | unk | unk | unk
212 | Classroom | 48 | 3 |  | 398 | 9 | 3 | Univent | 3184 | 0.90452 | 0 | 0.90452 | 0
213 | Classroom | 194 | 12 |  | 742 | 16 | 12 | Univent | 5936 | 1.9609 | 1 | 1.9609 | 1
214 | Classroom | 197 | 13 |  | 864 | 19 | 13 | Univent | 6912 | 1.7101 | 1 | 1.7101 | 1
215 | Office | 0 | 0 |  | 100 | 2 | 0 | Univent | 800 | 0 | 0 | 0 | 0
216 | Classroom | 411 | 27 |  | 762 | 17 | 17 | Univent | 6096 | 4.0453 | 2 | 4.0453 | 2
217 | Classroom | 365 | 24 |  | 734 | 16 | 16 | Univent | 5872 | 3.7296 | 1 | 3.7296 | 1
218 | Office / Classroom | 269 | 17 |  | 356 | 8 | 8 | Univent | 2848 | 5.6671 | 2 | 5.6671 | 2
300 | Classroom |  | 0 |  | 644 | 14 | 0 | House Fan | 5152 | unk | unk | unk | unk
301a | Office |  | 0 |  | 163 | 3 | 0 | House Fan | 1304 | unk | unk | unk | unk
302 | Classroom |  | 0 |  | 688 | 15 | 0 | House Fan | 5504 | unk | unk | unk | unk
303 | Classroom |  | 0 |  | 736 | 16 | 0 | House Fan | 5888 | unk | unk | unk | unk
304 | Classroom |  | 0 |  | 666 | 15 | 0 | House Fan | 5328 | unk | unk | unk | unk
306 | Classroom |  | 0 |  | 1085 | 24 | 0 | House Fan | 8680 | unk | unk | unk | unk
306A | Library |  | 0 |  | 1166 | 26 | 0 | House Fan | 9328 | unk | unk | unk | unk
307 | Classroom |  | 0 |  | 687 | 15 | 0 | House Fan | 5496 | unk | unk | unk | unk
308 | Classroom |  | 0 |  | 798 | 18 | 0 | House Fan | 6384 | unk | unk | unk | unk
312 | Classroom | 224 | 14 |  | 1070 | 24 | 14 | Rooftop Unit | 8560 | 1.5701 | 1 | 1.5701 | 1
313 | Classroom | 0 | 0 |  | 944 | 21 | 0 | Rooftop Unit | 7552 | 0 | 0 | 0 | 0
314 | Classroom | 332 | 22 |  | 1117 | 25 | 22 | Rooftop Unit | 8936 | 2.2292 | 1 | 2.2292 | 1
314 | Office | 0 | 0 |  | 372 | 8 | 0 | Univent | 2976 | 0 | 0 | 0 | 0
314A | Office |  | 0 |  | 372 | 8 | 0 | House Fan | 2976 | unk | unk | unk | unk
315A | Teacher's Lounge | 0 | 0 |  | 294 | 6 | 0 | Univent | 2352 | 0 | 0 | 0 | 0
316 | Office / Classroom | 130 | 8 |  | 356 | 8 | 8 | Rooftop Unit | 2848 | 2.7388 | 1 | 2.7388 | 1
- | Auditorium |  | 0 |  | 3657 | 83 | 0 | House Fan | 29256 | unk | unk | unk | unk
- | Gym | 857 | 57 |  | 4693 | 106 | 57 | Univent | 37544 | 1.3696 | 1 | 1.3696 | 1
- | Lunch Rm |  | 0 |  | 4331 | 98 | 0 | House Fan | 34648 | unk | unk | unk | unk
- | Main Office |  | 0 | Yes | 395 | 8 | 8 | House Fan | 3160 | unk | unk | 20 | 3
- | Principals Office |  | 0 | Yes | 269 | 6 | 6 | House Fan | 2152 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Thomas G. Morton Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 0 | 0 | Yes | 988 | 22 | 22 | Univent | 7904 | 0 | 0 | 20 | 3
101 | Classroom | 0 | 0 | Yes | 875 | 19 | 19 | Univent | 7000 | 0 | 0 | 20 | 3
102 | Classroom | 374 | 24 |  | 792 | 18 | 18 | Air Coil Unit | 6336 | 3.5417 | 1 | 3.5417 | 1
104B | Storage | 77 | 5 |  | 84 | 1 | 1 | Univent | 672 | 6.875 | 2 | 6.875 | 2
108A | Nurse Office | 125 | 8 |  | 90 | 2 | 2 | Univent | 720 | 10.4167 | 3 | 10.4167 | 3
108B | Audio | 40 | 2 |  | 224 | 5 | 2 | Univent | 1792 | 1.3393 | 1 | 1.3393 | 1
108C | Examination | 36 | 2 |  | 234 | 5 | 2 | Univent | 1872 | 1.1538 | 1 | 1.1538 | 1
110 | Classroom | 0 | 0 |  | 513 | 11 | 0 | Univent | 4104 | 0 | 0 | 0 | 0
111 | Classroom | 309 | 20 | Yes | 252 | 5 | 5 | Univent | 2016 | 9.1964 | 2 | 29.1964 | 4
200 | Classroom | 0 | 0 | Yes | 1071 | 24 | 24 | Univent | 8568 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 754 | 17 | 17 | Univent | 6032 | 0 | 0 | 20 | 3
202 | Classroom | 432 | 28 | Yes | 754 | 17 | 17 | Univent | 6032 | 4.2971 | 2 | 24.2971 | 4
203 | Classroom | 475 | 31 |  | 8112 | 184 | 31 | Univent | 64896 | 0.43916 | 0 | 0.43916 | 0
204 | Classroom | 399 | 26 |  | 438 | 9 | 9 | Univent | 3504 | 6.8322 | 2 | 6.8322 | 2
205 | Classroom | 0 | 0 | Yes | 1015 | 23 | 23 | Univent | 8120 | 0 | 0 | 20 | 3
206 | Classroom | 0 | 0 | Yes | 1305 | 29 | 29 | Univent | 10440 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 1305 | 29 | 29 | Univent | 10440 | 0 | 0 | 20 | 3
208 | Classroom | 329 | 21 | Yes | 1015 | 23 | 23 | Univent | 8120 | 2.431 | 1 | 22.431 | 3
209 | Classroom | 280 | 18 | Yes | 408 | 9 | 9 | Univent | 3264 | 5.1471 | 2 | 25.1471 | 4
210 | Classroom | 0 | 0 | Yes | 725 | 16 | 16 | Univent | 5800 | 0 | 0 | 20 | 3
211 | Classroom | 0 | 0 | Yes | 841 | 19 | 19 | Univent | 6728 | 0 | 0 | 20 | 3
212 | Classroom | 0 | 0 | Yes | 264 | 6 | 6 | Univent | 2112 | 0 | 0 | 20 | 3
213 | Classroom | 437 | 29 |  | 725 | 16 | 16 | Univent | 5800 | 4.5207 | 2 | 4.5207 | 2
214A | Classroom | 94 | 6 |  | 190 | 4 | 4 | Univent | 1520 | 3.7105 | 1 | 3.7105 | 1
214B | Classroom | 162 | 10 |  | 624 | 14 | 10 | Univent | 4992 | 1.9471 | 1 | 1.9471 | 1
300 | Classroom | 309 | 20 |  | 780 | 17 | 17 | Univent | 6240 | 2.9712 | 1 | 2.9712 | 1
301 | Classroom | 0 | 0 |  | 725 | 16 | 0 | Univent | 5800 | 0 | 0 | 0 | 0
302 | Classroom | 685 | 45 |  | 240 | 5 | 5 | Univent | 1920 | 21.4062 | 3 | 21.4062 | 3
303 | Classroom | 486 | 32 |  | 754 | 17 | 17 | Univent | 6032 | 4.8342 | 2 | 4.8342 | 2
304 | Classroom | 448 | 29 | Yes | 725 | 16 | 16 | Univent | 5800 | 4.6345 | 2 | 24.6345 | 4
305 | Classroom | 291 | 19 |  | 312 | 7 | 7 | Univent | 2496 | 6.9952 | 2 | 6.9952 | 2
306 | Classroom | 483 | 32 | Yes | 754 | 17 | 17 | Univent | 6032 | 4.8044 | 2 | 24.8044 | 4
307 | Classroom | 415 | 27 | Yes | 756 | 17 | 17 | Univent | 6048 | 4.1171 | 2 | 24.1171 | 4
308 | Library | 1124 | 74 |  | 2975 | 67 | 67 | Univent | 23800 | 2.8336 | 1 | 2.8336 | 1
308 | Library Office | 0 | 0 |  | 462 | 10 | 0 | Univent | 3696 | 0 | 0 | 0 | 0
309 | Classroom | 283 | 18 | Yes | 806 | 18 | 18 | Univent | 6448 | 2.6334 | 1 | 22.6334 | 3
310 | Classroom | 628 | 41 |  | 700 | 15 | 15 | Univent | 5600 | 6.7286 | 2 | 6.7286 | 2
311 | Classroom | 294 | 19 |  | 754 | 17 | 17 | Univent | 6032 | 2.9244 | 1 | 2.9244 | 1
312 | Classroom | 349 | 23 |  | 754 | 17 | 17 | Univent | 6032 | 3.4715 | 1 | 3.4715 | 1
313 | Classroom | 547 | 36 |  | 486 | 11 | 11 | Univent | 3888 | 8.4414 | 2 | 8.4414 | 2
315 | Classroom | 544 | 36 |  | 754 | 17 | 17 | Univent | 6032 | 5.4111 | 2 | 5.4111 | 2
316 | Classroom | 324 | 21 |  | 754 | 17 | 17 | Univent | 6032 | 3.2228 | 1 | 3.2228 | 1
317 | Classroom | 431 | 28 |  | 870 | 19 | 19 | Univent | 6960 | 3.7155 | 1 | 3.7155 | 1
318 | Classroom | 305 | 20 |  | 312 | 7 | 7 | Univent | 2496 | 7.3317 | 2 | 7.3317 | 2
319 | Classroom | 0 | 0 | Yes | 650 | 14 | 14 | Univent | 5200 | 0 | 0 | 20 | 3
320 | Classroom | 431 | 28 |  | 728 | 16 | 16 | Univent | 5824 | 4.4402 | 2 | 4.4402 | 2
- | Auditorium | 5700 | 380 |  | 2646 | 60 | 60 | Air Coil Unit | 21168 | 16.1565 | 3 | 16.1565 | 3
- | Cafeteria | 2196 | 146 | Yes | 2726 | 61 | 61 | Air Coil Unit | 21808 | 6.0418 | 2 | 26.0418 | 4
- | Conference | 83 | 5 |  | 171 | 3 | 3 | Univent | 1368 | 3.6404 | 1 | 3.6404 | 1
- | Counselors Office A | 87 | 5 |  | 99 | 2 | 2 | Univent | 792 | 6.5909 | 2 | 6.5909 | 2
- | Counselors Office B | 91 | 6 |  | 128 | 2 | 2 | Univent | 1024 | 5.332 | 2 | 5.332 | 2
- | Counselors Office C | 148 | 9 |  | 100 | 2 | 2 | Univent | 800 | 11.1 | 3 | 11.1 | 3
- | Gym | 1927 | 128 |  | 4640 | 105 | 105 | Air Coil Unit | 37120 | 3.1148 | 1 | 3.1148 | 1
- | Lounge | 311 | 20 |  | 351 | 7 | 7 | Univent | 2808 | 6.6453 | 2 | 6.6453 | 2
- | Main Office | 285 | 19 |  | 380 | 8 | 8 | Univent | 3040 | 5.625 | 2 | 5.625 | 2
- | Copy Room | 53 | 3 |  | 60 | 1 | 1 | Univent | 480 | 6.625 | 2 | 6.625 | 2
- | Nurse | 83 | 5 |  | 123 | 2 | 2 | Univent | 984 | 5.061 | 2 | 5.061 | 2
- | Principal Office | 159 | 10 |  | 228 | 5 | 5 | Univent | 1824 | 5.2303 | 2 | 5.2303 | 2
- | Vice Principal Office | 54 | 3 |  | 99 | 2 | 2 | Univent | 792 | 4.0909 | 2 | 4.0909 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Motivation High School KIPP Turner West Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Capital | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Devine Part 2 | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
A-PreK Corridor | Corridor | 314 | 20 |  | 600 | 13 | 13 | Univent | 4800 | 3.925 | 1 | 3.925 | 1
A-PreK North Entrance-A | Corridor | 490 | 32 |  | 243 | 5 | 5 | Univent | 1944 | 15.1235 | 3 | 15.1235 | 3
A-PreK North Entrance-B | Corridor | 548 | 36 |  | 480 | 10 | 10 | Univent | 3840 | 8.5625 | 2 | 8.5625 | 2
A-PreK South Corridor | Corridor | 324 | 21 |  | 550 | 12 | 12 | Univent | 4400 | 4.4182 | 2 | 4.4182 | 2
A-Wing Head Start Mech. Rm | Head Start PreK A169 & A170 | 349 | 23 |  | 1440 | 32 | 23 | Air Handling Unit | 11520 | 1.8177 | 1 | 1.8177 | 1
A-Wing-Café Mech. Rm | 2nd & 3rd Flr. Staff Seminar Rms | 1734 | 115 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
A-Wing-Café Mech. Rm | 3rd Flr |  | 0 |  | 50 | 1 | 0 | Air Handling Unit | 400 | unk | unk | unk | unk
A-Wing-Café Mech. Rm | 2nd Flr |  | 0 |  | 50 | 1 | 0 | Air Handling Unit | 400 | unk | unk | unk | unk
A-Wing-Café Mech. Rm | Ground Flr. Administration | 351 | 23 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
A130 | Gym | 410 | 27 |  | 2552 | 58 | 27 | Heating Ventilation Unit | 20416 | 1.2049 | 1 | 1.2049 | 1
A108 Locker Rm | A108 | 0 | 0 |  |  | 0 | 0 | Heating Ventilation Unit |  | unk | unk | unk | unk
A152 Locker Rm | A152 | 1340 | 89 |  | 690 | 15 | 15 | Heating Ventilation Unit | 5520 | 14.5652 | 3 | 14.5652 | 3
A162 Storage | A154 Corrective Gym | 306 | 20 |  | 5192 | 118 | 20 | Heating Ventilation Unit | 41536 | 0.44203 | 0 | 0.44203 | 0
A165 | Storage | 0 | 0 |  | 5192 | 118 | 0 | Heating Ventilation Unit | 41536 | 0 | 0 | 0 | 0
B-157 | B-155 Fitness Rm | 1593 | 106 |  | 1150 | 26 | 26 | Univent | 9200 | 10.3891 | 3 | 10.3891 | 3
MER Rm B146 | B-Wing | 555 | 37 |  | 1012 | 23 | 23 | Air Handling Unit | 8096 | 4.1131 | 2 | 4.1131 | 2
B-Wing B137 | B-139 A, B, C, D | 2003 | 133 |  | 4134 | 93 | 93 | Air Handling Unit | 33072 | 3.6339 | 1 | 3.6339 | 1
B101 Cafeteria | B-Wing Roof | 320 | 21 |  | 9405 | 213 | 21 | Air Handling Unit | 75240 | 0.25518 | 0 | 0.25518 | 0
House Coord North 3rd & 2nd Flr | B-Wing Roof | 67 | 4 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
B318 | B-Wing Roof |  | 0 |  | 800 | 18 | 0 | Air Handling Unit | 6400 | unk | unk | unk | unk
B218 | B-Wing Roof |  | 0 |  | 800 | 18 | 0 | Air Handling Unit | 6400 | unk | unk | unk | unk
House Coord South 3rd & 2nd Flr | B-Wing Roof | 126 | 8 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
B306 | B-Wing Roof |  | 0 |  | 800 | 18 | 0 | Air Handling Unit | 6400 | unk | unk | unk | unk
B206 | B-Wing Roof |  | 0 |  | 800 | 18 | 0 | Air Handling Unit | 6400 | unk | unk | unk | unk
B325 IMC Library | B-Wing Roof | 7 | 0 |  | 851 | 19 | 0 | Air Handling Unit | 6808 | 0.061692 | 0 | 0.061692 | 0
139A | Classroom |  | 0 |  | 880 | 20 | 0 |  | 7040 | unk | unk | unk | unk
139B | Classroom |  | 0 |  | 987 | 22 | 0 |  | 7896 | unk | unk | unk | unk
139C | Classroom |  | 0 |  | 884 | 20 | 0 |  | 7072 | unk | unk | unk | unk
139D | Classroom |  | 0 |  | 1035 | 23 | 0 |  | 8280 | unk | unk | unk | unk
151 | Classroom |  | 0 | Yes | 1824 | 41 | 41 |  | 14592 | unk | unk | 20 | 3
152 | Classroom |  | 0 | Yes | 1170 | 26 | 26 |  | 9360 | unk | unk | 20 | 3
B196 | Classroom | 376 | 25 |  | 567 | 12 | 12 | Univent | 4536 | 4.9735 | 2 | 4.9735 | 2
B197 | Classroom | 755 | 50 |  | 962 | 21 | 21 | Univent | 7696 | 5.8862 | 2 | 5.8862 | 2
B198 | Classroom | 739 | 49 |  | 792 | 18 | 18 | Univent | 6336 | 6.9981 | 2 | 6.9981 | 2
B200 | Classroom | 1468 | 97 |  | 1564 | 35 | 35 | Univent | 12512 | 7.0396 | 2 | 7.0396 | 2
B201 | Classroom | 673 | 44 |  | 850 | 19 | 19 | Univent | 6800 | 5.9382 | 2 | 5.9382 | 2
B202 | Classroom | 172 | 11 |  | 748 | 17 | 11 | Univent | 5984 | 1.7246 | 1 | 1.7246 | 1
B203 | Classroom | 673 | 44 |  | 748 | 17 | 17 | Univent | 5984 | 6.748 | 2 | 6.748 | 2
B204 | Classroom | 143 | 9 |  | 759 | 17 | 9 | Univent | 6072 | 1.413 | 1 | 1.413 | 1
B205 | Classroom | 555 | 37 |  | 720 | 16 | 16 | Univent | 5760 | 5.7812 | 2 | 5.7812 | 2
B207 | Classroom | 629 | 41 |  | 748 | 17 | 17 | Univent | 5984 | 6.3068 | 2 | 6.3068 | 2
B208 | Classroom | 640 | 42 |  | 759 | 17 | 17 | Univent | 6072 | 6.3241 | 2 | 6.3241 | 2
B209 | Classroom | 108 | 7 |  | 816 | 18 | 7 | Univent | 6528 | 0.99265 | 0 | 0.99265 | 0
B210 | Classroom | 630 | 42 |  | 720 | 16 | 16 | Univent | 5760 | 6.5625 | 2 | 6.5625 | 2
B211 | Classroom | 350 | 23 |  | 720 | 16 | 16 | Univent | 5760 | 3.6458 | 1 | 3.6458 | 1
B212 | Classroom | 538 | 35 |  | 1326 | 30 | 30 | Univent | 10608 | 3.043 | 1 | 3.043 | 1
B213 | Classroom | 244 | 16 |  | 759 | 17 | 16 | Univent | 6072 | 2.4111 | 1 | 2.4111 | 1
B214 | Classroom | 0 | 0 |  | 759 | 17 | 0 | Univent | 6072 | 0 | 0 | 0 | 0
B215 | Classroom | 341 | 22 |  | 748 | 17 | 17 | Univent | 5984 | 3.4191 | 1 | 3.4191 | 1
B216 | Classroom | 339 | 22 |  | 748 | 17 | 17 | Univent | 5984 | 3.3991 | 1 | 3.3991 | 1
B217 | Classroom | 273 | 18 |  | 624 | 14 | 14 | Univent | 4992 | 3.2812 | 1 | 3.2812 | 1
B219 | Classroom | 378 | 25 |  | 748 | 17 | 17 | Univent | 5984 | 3.7901 | 1 | 3.7901 | 1
B220 | Classroom | 242 | 16 |  | 759 | 17 | 16 | Univent | 6072 | 2.3913 | 1 | 2.3913 | 1
B221 | Classroom | 456 | 30 |  | 816 | 18 | 18 | Univent | 6528 | 4.1912 | 2 | 4.1912 | 2
B222 | Classroom | 633 | 42 |  | 598 | 13 | 13 | Univent | 4784 | 7.939 | 2 | 7.939 | 2
B223 | Classroom | 642 | 42 |  | 690 | 15 | 15 | Univent | 5520 | 6.9783 | 2 | 6.9783 | 2
B301 | Classroom | 200 | 13 |  | 850 | 19 | 13 | Univent | 6800 | 1.7647 | 1 | 1.7647 | 1
B302 | Classroom | 129 | 8 |  | 748 | 17 | 8 | Univent | 5984 | 1.2934 | 1 | 1.2934 | 1
B304 | Classroom | 630 | 42 |  | 1564 | 35 | 35 | Univent | 12512 | 3.0211 | 1 | 3.0211 | 1
B305 | Classroom | 150 | 10 |  | 720 | 16 | 10 | Univent | 5760 | 1.5625 | 1 | 1.5625 | 1
306 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | unk | unk | 20 | 3
B307 | Classroom | 193 | 12 |  | 748 | 17 | 12 | Univent | 5984 | 1.9352 | 1 | 1.9352 | 1
B308 | Classroom | 110 | 7 |  | 759 | 17 | 7 | Univent | 6072 | 1.087 | 1 | 1.087 | 1
B309 | Classroom | 186 | 12 |  | 816 | 18 | 12 | Univent | 6528 | 1.7096 | 1 | 1.7096 | 1
B310 | Classroom | 196 | 13 |  | 720 | 16 | 13 | Univent | 5760 | 2.0417 | 1 | 2.0417 | 1
B311 | Classroom | 222 | 14 |  | 720 | 16 | 14 | Univent | 5760 | 2.3125 | 1 | 2.3125 | 1
B312 | Classroom | 691 | 46 |  | 1326 | 30 | 30 | Univent | 10608 | 3.9084 | 1 | 3.9084 | 1
B313 | Classroom | 264 | 17 |  | 759 | 17 | 17 | Univent | 6072 | 2.6087 | 1 | 2.6087 | 1
B314 | Classroom | 436 | 29 |  | 759 | 17 | 17 | Univent | 6072 | 4.3083 | 2 | 4.3083 | 2
B315 | Classroom | 198 | 13 |  | 748 | 17 | 13 | Univent | 5984 | 1.9853 | 1 | 1.9853 | 1
B316 | Classroom | 160 | 10 |  | 748 | 17 | 10 | Univent | 5984 | 1.6043 | 1 | 1.6043 | 1
B317 | Classroom | 198 | 13 |  | 624 | 14 | 13 | Univent | 4992 | 2.3798 | 1 | 2.3798 | 1
318 | Classroom |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | unk | unk | 20 | 3
B319 | Classroom | 304 | 20 |  | 748 | 17 | 17 | Univent | 5984 | 3.0481 | 1 | 3.0481 | 1
B320 | Classroom | 144 | 9 |  | 759 | 17 | 9 | Univent | 6072 | 1.4229 | 1 | 1.4229 | 1
B321 | Classroom | 290 | 19 |  | 816 | 18 | 18 | Univent | 6528 | 2.6654 | 1 | 2.6654 | 1
B322 | Classroom | 213 | 14 |  | 598 | 13 | 13 | Univent | 4784 | 2.6714 | 1 | 2.6714 | 1
B323 | Classroom | 156 | 10 |  | 690 | 15 | 10 | Univent | 5520 | 1.6957 | 1 | 1.6957 | 1
B324 | Classroom | 577 | 38 |  | 1435 | 32 | 32 | Univent | 11480 | 3.0157 | 1 | 3.0157 | 1
Main Office | Main Office |  | 0 | Yes | 950 | 21 | 21 |  | 7600 | unk | unk | 20 | 3
Teachers Lounge | Lounge |  | 0 | Yes | 728 | 16 | 16 |  | 5824 | unk | unk | 20 | 3
Nurse | Office |  | 0 | Yes | 910 | 20 | 20 |  | 7280 | unk | unk | 20 | 3
C-Wing | Auditorium | 346 | 23 | Yes | 1476 | 33 | 33 | Air Handling Unit | 11808 | 1.7581 | 1 | 21.7581 | 3
| Music Rm | [8 empty] | unk | unk | unk | unk
C-Wing | Auditorium Comm. Rm. | 1811 | 120 |  | 7392 | 168 | 120 | Air Handling Unit | 59136 | 1.8375 | 1 | 1.8375 | 1
C-Wing | Auditorium/ Auditorium Stage | 3862 | 257 |  | 1890 | 42 | 42 | Air Handling Unit | 15120 | 15.3254 | 3 | 15.3254 | 3
Head Start | B110 Learning Lab & B104 Student Store | 457 | 30 |  | 81 | 1 | 1 | Air Handling Unit | 648 | 42.3148 | 4 | 42.3148 | 4
Mech Rm. | [9 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-05-03 | [8 empty] | unk | unk | unk | unk
School: | Luis Munoz – Marin Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100B | CORRIDOR | 149 | 9 |  | 618 | 14 | 9 | Air Handling Unit | 4944 | 1.8083 | 1 | 1.8083 | 1
100E | CORRIDOR | 115 | 7 |  | 1780 | 40 | 7 | Air Handling Unit | 14240 | 0.48455 | 0 | 0.48455 | 0
100F | CORRIDOR | 250 | 16 |  | 1210 | 27 | 16 | Air Handling Unit | 9680 | 1.5496 | 1 | 1.5496 | 1
100G | CORRIDOR | 142 | 9 |  | 1404 | 31 | 9 | Air Handling Unit | 11232 | 0.75855 | 0 | 0.75855 | 0
100H | CORRIDOR |  | 0 |  | 1780 | 40 | 0 | Air Handling Unit | 14240 | unk | unk | unk | unk
102 | Classroom | 193 | 12 |  | 792 | 18 | 12 | Air Handling Unit | 6336 | 1.8277 | 1 | 1.8277 | 1
104 | Classroom | 225 | 15 | Yes | 805 | 18 | 18 | Air Handling Unit | 6440 | 2.0963 | 1 | 22.0963 | 3
105 | Classroom | 195 | 13 | Yes | 713 | 16 | 16 | Air Handling Unit | 5704 | 2.0512 | 1 | 22.0512 | 3
106 | Classroom | 213 | 14 | Yes | 713 | 16 | 16 | Air Handling Unit | 5704 | 2.2405 | 1 | 22.2405 | 3
107 | Classroom | 170 | 11 | Yes | 682 | 15 | 15 | Air Handling Unit | 5456 | 1.8695 | 1 | 21.8695 | 3
108 | Classroom | 202 | 13 | Yes | 682 | 15 | 15 | Air Handling Unit | 5456 | 2.2214 | 1 | 22.2214 | 3
109 | Classroom | 227 | 15 |  | 682 | 15 | 15 | Air Handling Unit | 5456 | 2.4963 | 1 | 2.4963 | 1
110 | Classroom | 212 | 14 | Yes | 682 | 15 | 15 | Air Handling Unit | 5456 | 2.3314 | 1 | 22.3314 | 3
111 | Classroom | 469 | 31 |  | 700 | 15 | 15 | Air Handling Unit | 5600 | 5.025 | 2 | 5.025 | 2
115 | LOBBY | 648 | 43 |  | 1368 | 31 | 31 | Air Handling Unit | 10944 | 3.5526 | 1 | 3.5526 | 1
116 | - | 215 | 14 |  | 609 | 13 | 13 | Air Handling Unit | 4872 | 2.6478 | 1 | 2.6478 | 1
118 | - | 177 | 11 | Yes | 672 | 15 | 15 | Air Handling Unit | 5376 | 1.9754 | 1 | 21.9754 | 3
120 | - | 188 | 12 | Yes | 768 | 17 | 17 | Air Handling Unit | 6144 | 1.8359 | 1 | 21.8359 | 3
121 | HEALTH | 87 | 5 |  | 816 | 18 | 5 | Air Handling Unit | 6528 | 0.79963 | 0 | 0.79963 | 0
124A | OFFICE | 19 | 1 |  | 120 | 2 | 1 | Air Handling Unit | 960 | 1.1875 | 1 | 1.1875 | 1
125 | SPE. | 17 | 1 | Yes | 336 | 7 | 7 | Air Handling Unit | 2688 | 0.37946 | 0 | 20.3795 | 3
125 | OCC | 51 | 3 |  | 272 | 6 | 3 | Air Handling Unit | 2176 | 1.4062 | 1 | 1.4062 | 1
126 | FAM MGMT | 272 | 18 |  | 1215 | 27 | 18 | Air Handling Unit | 9720 | 1.679 | 1 | 1.679 | 1
127 | CLASSROOM | 56 | 3 |  | 670 | 15 | 3 | Air Handling Unit | 5360 | 0.62687 | 0 | 0.62687 | 0
127B |  | 15 |  |  | 39 |  | 0 | Air Handling Unit | 312 | 2.8846 | 1 | 2.8846 | 1
127C |  | 18 |  |  | 149 |  | 0 | Air Handling Unit | 1192 | 0.90604 | 0 | 0.90604 | 0
160 | Classroom | 27 | 1 |  | 39 | 0 | 0 | Air Handling Unit | 312 | 5.1923 | 2 | 5.1923 | 2
161 | Classroom | 33 | 2 |  | 375 | 8 | 2 | Air Handling Unit | 3000 | 0.66 | 0 | 0.66 | 0
162 | Classroom | 55 | 3 |  | 114 | 2 | 2 | Air Handling Unit | 912 | 3.6184 | 1 | 3.6184 | 1
163 | Classroom | 62 | 4 |  | 114 | 2 | 2 | Air Handling Unit | 912 | 4.0789 | 2 | 4.0789 | 2
164 | Classroom | 33 | 2 |  | 117 | 2 | 2 | Air Handling Unit | 936 | 2.1154 | 1 | 2.1154 | 1
166 | Classroom | 23 | 1 |  | 102 | 2 | 1 | Air Handling Unit | 816 | 1.6912 | 1 | 1.6912 | 1
168 | Classroom | 33 | 2 |  | 109 | 2 | 2 | Air Handling Unit | 872 | 2.2706 | 1 | 2.2706 | 1
169 | Classroom | 23 | 1 |  | 81 | 1 | 1 | Air Handling Unit | 648 | 2.1296 | 1 | 2.1296 | 1
170 | Classroom | 35 | 2 |  | 134 | 3 | 2 | Air Handling Unit | 1072 | 1.959 | 1 | 1.959 | 1
171 | OFFICE | 223 | 14 |  | 148 | 3 | 3 | Air Handling Unit | 1184 | 11.3007 | 3 | 11.3007 | 3
172 | - | 58 | 3 |  | 148 | 3 | 3 | Air Handling Unit | 1184 | 2.9392 | 1 | 2.9392 | 1
173 | PRINCIPAL | 87 | 5 |  | 304 | 6 | 5 | Air Handling Unit | 2432 | 2.1464 | 1 | 2.1464 | 1
176 | - | 114 | 7 |  | 148 | 3 | 3 | Air Handling Unit | 1184 | 5.777 | 2 | 5.777 | 2
177 | - | 69 | 4 |  | 134 | 3 | 3 | Air Handling Unit | 1072 | 3.8619 | 1 | 3.8619 | 1
180 | CONFR | 54 | 3 |  | 244 | 5 | 3 | Air Handling Unit | 1952 | 1.6598 | 1 | 1.6598 | 1
181 | ASS PRINC | 100 | 6 |  | 188 | 4 | 4 | Air Handling Unit | 1504 | 3.9894 | 1 | 3.9894 | 1
181A | OFFICE | 42 | 2 |  | 125 | 2 | 2 | Air Handling Unit | 1000 | 2.52 | 1 | 2.52 | 1
182 | - | 42 | 2 |  | 131 | 2 | 2 | Air Handling Unit | 1048 | 2.4046 | 1 | 2.4046 | 1
183 | - | 42 | 2 |  | 97 | 2 | 2 | Air Handling Unit | 776 | 3.2474 | 1 | 3.2474 | 1
200A | CORRIDOR | 160 | 10 |  | 1780 | 40 | 10 | Air Handling Unit | 14240 | 0.67416 | 0 | 0.67416 | 0
200C | CORRIDOR | 148 | 9 |  | 1780 | 40 | 9 | Air Handling Unit | 14240 | 0.6236 | 0 | 0.6236 | 0
200D | CORRIDOR | 240 | 16 |  | 1359 | 30 | 16 | Air Handling Unit | 10872 | 1.3245 | 1 | 1.3245 | 1
200E | CORRIDOR | 100 | 6 |  | 1404 | 31 | 6 | Air Handling Unit | 11232 | 0.53419 | 0 | 0.53419 | 0
200F | - | 156 | 10 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 11.7 | 3 | 11.7 | 3
201 | Classroom | 204 | 13 | Yes | 714 | 16 | 16 | Univent and Air Handling Unit | 5712 | 2.1429 | 1 | 22.1429 | 3
202 | Classroom | 94 | 6 | Yes | 713 | 16 | 16 | Univent and Air Handling Unit | 5704 | 0.98878 | 0 | 20.9888 | 3
203 | Classroom | 68 | 4 | Yes | 704 | 16 | 16 | Univent and Air Handling Unit | 5632 | 0.72443 | 0 | 20.7244 | 3
204 | Classroom | 418 | 27 |  | 764 | 17 | 17 | Univent and Air Handling Unit | 6112 | 4.1034 | 2 | 4.1034 | 2
205 | Classroom | 152 | 10 | Yes | 764 | 17 | 17 | Univent and Air Handling Unit | 6112 | 1.4921 | 1 | 21.4921 | 3
206 | Classroom | 241 | 16 | Yes | 764 | 17 | 17 | Univent and Air Handling Unit | 6112 | 2.3658 | 1 | 22.3658 | 3
207 | Classroom | 148 | 9 |  | 648 | 14 | 9 | Univent and Air Handling Unit | 5184 | 1.713 | 1 | 1.713 | 1
208 | IMC | 338 | 22 |  | 1757 | 39 | 22 | Air Handling Unit | 14056 | 1.4428 | 1 | 1.4428 | 1
209 | Classroom | 272 | 18 |  | 648 | 14 | 14 | Univent and Air Handling Unit | 5184 | 3.1481 | 1 | 3.1481 | 1
213 | Classroom | 155 | 10 |  | 764 | 17 | 10 | Univent and Air Handling Unit | 6112 | 1.5216 | 1 | 1.5216 | 1
214 | Classroom | 140 | 9 |  | 118 | 2 | 2 | Univent | 944 | 8.8983 | 2 | 8.8983 | 2
214 | IMC | 311 | 20 |  | 1405 | 31 | 20 | Air Handling Unit | 11240 | 1.6601 | 1 | 1.6601 | 1
214A | WORK | 32 | 2 |  | 118 | 2 | 2 | Air Handling Unit | 944 | 2.0339 | 1 | 2.0339 | 1
215 | Classroom | 232 | 15 | Yes | 840 | 19 | 19 | Univent and Air Handling Unit | 6720 | 2.0714 | 1 | 22.0714 | 3
216A | OFFICE | 64 | 4 |  | 165 | 3 | 3 | Air Handling Unit | 1320 | 2.9091 | 1 | 2.9091 | 1
217 | Classroom | 200 | 13 |  | 782 | 17 | 13 | Univent and Air Handling Unit | 6256 | 1.9182 | 1 | 1.9182 | 1
218 | Classroom | 120 | 8 |  | 374 | 8 | 8 | Univent | 2992 | 2.4064 | 1 | 2.4064 | 1
218B | STR. | 65 | 4 | Yes | 2255 | 51 | 51 | Air Handling Unit | 18040 | 0.21619 | 0 | 20.2162 | 3
218S | Classroom | 71 | 4 |  | 241 | 5 | 4 | Air Handling Unit | 1928 | 2.2095 | 1 | 2.2095 | 1
219 | Classroom | 153 | 10 | Yes | 7825 | 177 | 177 | Univent and Air Handling Unit | 62600 | 0.14665 | 0 | 20.1466 | 3
220 | Classroom | 117 | 7 | Yes | 648 | 14 | 14 | Univent and Air Handling Unit | 5184 | 1.3542 | 1 | 21.3542 | 3
221 | Classroom | 253 | 16 | Yes | 764 | 17 | 17 | Univent and Air Handling Unit | 6112 | 2.4836 | 1 | 22.4836 | 3
222 | OFFICE | 50 | 3 |  | 1105 | 25 | 3 | Air Handling Unit | 8840 | 0.33937 | 0 | 0.33937 | 0
223 | Classroom | 188 | 12 | Yes | 690 | 15 | 15 | Univent and Air Handling Unit | 5520 | 2.0435 | 1 | 22.0435 | 3
225 | Classroom | 73 | 4 | Yes | 870 | 19 | 19 | Univent | 6960 | 0.62931 | 0 | 20.6293 | 3
225 | COMP. | 124 | 8 |  | 96 | 2 | 2 | Air Handling Unit | 768 | 9.6875 | 2 | 9.6875 | 2
226 | TECH. | 94 | 6 | Yes | 906 | 20 | 20 | Air Handling Unit | 7248 | 0.77815 | 0 | 20.7781 | 3
226 (right) | Classroom | 104 | 6 |  | 343 | 7 | 6 | Univent | 2744 | 2.2741 | 1 | 2.2741 | 1
226(left) | Classroom | 191 | 12 |  | 104 | 2 | 2 | Univent | 832 | 13.774 | 3 | 13.774 | 3
226C | SHOP | 91 | 6 |  | 104 | 2 | 2 | Air Handling Unit | 832 | 6.5625 | 2 | 6.5625 | 2
227 | Classroom | 150 | 10 |  | 660 | 15 | 10 | Univent and Air Handling Unit | 5280 | 1.7045 | 1 | 1.7045 | 1
300b | Corridor | 191 | 12 |  | 1404 | 31 | 12 | Air Handling Unit | 11232 | 1.0203 | 1 | 1.0203 | 1
300d | Corridor | 225 | 15 |  | 1359 | 30 | 15 | Air Handling Unit | 10872 | 1.2417 | 1 | 1.2417 | 1
301 | Classroom | 224 | 14 | Yes | 714 | 16 | 16 | Univent and Air Handling Unit | 5712 | 2.3529 | 1 | 22.3529 | 3
302 | Classroom | 229 | 15 | Yes | 757 | 17 | 17 | Univent and Air Handling Unit | 6056 | 2.2688 | 1 | 22.2688 | 3
303 | Classroom | 188 | 12 | Yes | 704 | 16 | 16 | Univent and Air Handling Unit | 5632 | 2.0028 | 1 | 22.0028 | 3
304 | Classroom | 194 | 12 | Yes | 757 | 17 | 17 | Univent and Air Handling Unit | 6056 | 1.9221 | 1 | 21.9221 | 3
305 | Classroom | 232 | 15 | Yes | 704 | 16 | 16 | Univent and Air Handling Unit | 5632 | 2.4716 | 1 | 22.4716 | 3
306 | Classroom | 243 | 16 | Yes | 757 | 17 | 17 | Univent and Air Handling Unit | 6056 | 2.4075 | 1 | 22.4075 | 3
307 | Classroom | 139 | 9 | Yes | 648 | 14 | 14 | Univent and Air Handling Unit | 5184 | 1.6088 | 1 | 21.6088 | 3
308 | Classroom | 86 | 5 |  | 734 | 16 | 5 | Univent and Air Handling Unit | 5872 | 0.87875 | 0 | 0.87875 | 0
309 | Classroom | 120 | 8 | Yes | 648 | 14 | 14 | Univent and Air Handling Unit | 5184 | 1.3889 | 1 | 21.3889 | 3
313 | Classroom | 156 | 10 | Yes | 1160 | 26 | 26 | Univent and Air Handling Unit | 9280 | 1.0086 | 1 | 21.0086 | 3
314 | Classroom | 119 | 7 | Yes | 1163 | 26 | 26 | Univent and Air Handling Unit | 9304 | 0.76741 | 0 | 20.7674 | 3
315 | Classroom | 107 | 7 | Yes | 713 | 16 | 16 | Univent and Air Handling Unit | 5704 | 1.1255 | 1 | 21.1255 | 3
316 | Classroom | 49 | 3 | Yes | 782 | 17 | 17 | Univent and Air Handling Unit | 6256 | 0.46995 | 0 | 20.4699 | 3
317 | Classroom | 99 | 6 | Yes | 782 | 17 | 17 | Univent and Air Handling Unit | 6256 | 0.94949 | 0 | 20.9495 | 3
318 | Classroom | 118 | 7 | Yes | 684 | 15 | 15 | Univent and Air Handling Unit | 5472 | 1.2939 | 1 | 21.2939 | 3
319 | Classroom | 358 | 23 |  | 782 | 17 | 17 | Univent and Air Handling Unit | 6256 | 3.4335 | 1 | 3.4335 | 1
320 | Classroom | 252 | 16 |  | 648 | 14 | 14 | Univent and Air Handling Unit | 5184 | 2.9167 | 1 | 2.9167 | 1
321 | Classroom | 454 | 30 |  | 648 | 14 | 14 | Univent and Air Handling Unit | 5184 | 5.2546 | 2 | 5.2546 | 2
322 | OFFICE | 0 | 0 |  | 100 | 2 | 0 | Air Handling Unit | 800 | 0 | 0 | 0 | 0
- | AUDITORIUM | 2082 | 138 |  | 2938 | 66 | 66 | Air Handling Unit | 23504 | 5.3148 | 2 | 5.3148 | 2
- | CAFETERIA | 251 | 16 | Yes | 4402 | 100 | 100 | Air Handling Unit | 35216 | 0.42765 | 0 | 20.4276 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | George W. Nebinger Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom |  | 0 | Yes | 44 | 1 | 1 | House Fan | 352 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 880 | 20 | 20 | House Fan | 7040 | unk | unk | 20 | 3
103 | Classroom |  | 0 |  | 644 | 14 | 0 | House Fan | 5152 | unk | unk | unk | unk
104 | Classroom |  | 0 |  | 644 | 14 | 0 | House Fan | 5152 | unk | unk | unk | unk
105 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | unk | unk | 20 | 3
106 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | unk | unk | 20 | 3
107 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | unk | unk | 20 | 3
204 | Classroom |  | 0 | Yes | 899 | 20 | 20 | House Fan | 7192 | unk | unk | 20 | 3
204A | Classroom |  | 0 | Yes | 285 | 6 | 6 | House Fan | 2280 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 330 | 7 | 7 | House Fan | 2640 | unk | unk | 20 | 3
206 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | unk | unk | 20 | 3
207 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
208 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
301 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
302 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
303 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | unk | unk | 20 | 3
304 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | unk | unk | 20 | 3
305 | Classroom |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
305A | Classroom |  | 0 |  | 450 | 10 | 0 | House Fan | 3600 | unk | unk | unk | unk
306 | Classroom |  | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | unk | unk | 20 | 3
307 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
308 | Classroom |  | 0 | Yes | 750 | 17 | 17 | House Fan | 6000 | unk | unk | 20 | 3
401 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
402 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
- | Gym |  | 0 |  | 2870 | 65 | 0 | House Fan | 22960 | unk | unk | unk | unk
- | Main Office |  | 0 | Yes | 330 | 7 | 7 | House Fan | 2640 | unk | unk | 20 | 3
- | Principal's Office |  | 0 | Yes | 247 | 5 | 5 | House Fan | 1976 | unk | unk | 20 | 3
- | Health Room |  | 0 | Yes | 99 | 2 | 2 | House Fan | 792 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | Northeast High School | [8 empty] | unk | unk | unk | unk
Vendor: | Capital Programs | Devine Brothers | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Devine Brothers Data | [9 empty] | unk | unk | unk | unk
1 | Classroom | 591 | 39 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 6.2872 | 2 | 6.2872 | 2
2 | Classroom | 520 | 34 |  | 619 | 14 | 14 | Unit Ventilator | 4952 | 6.3005 | 2 | 6.3005 | 2
3 | Classroom | 546 | 36 |  | 759 | 17 | 17 | Unit Ventilator | 6072 | 5.3953 | 2 | 5.3953 | 2
4 | Classroom | 545 | 36 |  | 749 | 17 | 17 | Unit Ventilator | 5992 | 5.4573 | 2 | 5.4573 | 2
5 | Classroom | 586 | 39 |  | 807 | 18 | 18 | Unit Ventilator | 6456 | 5.4461 | 2 | 5.4461 | 2
6 | Classroom | 564 | 37 |  | 782 | 17 | 17 | Unit Ventilator | 6256 | 5.4092 | 2 | 5.4092 | 2
7 | Classroom | 572 | 38 |  | 761 | 17 | 17 | Unit Ventilator | 6088 | 5.6373 | 2 | 5.6373 | 2
8 | Classroom | 539 | 35 |  | 775 | 17 | 17 | Unit Ventilator | 6200 | 5.2161 | 2 | 5.2161 | 2
9 | Classroom | 280 | 18 |  | 762 | 17 | 17 | Unit Ventilator | 6096 | 2.7559 | 1 | 2.7559 | 1
10 | Classroom | 271 | 18 |  | 749 | 17 | 17 | Unit Ventilator | 5992 | 2.7136 | 1 | 2.7136 | 1
11 | Classroom | 337 | 22 |  | 770 | 17 | 17 | Unit Ventilator | 6160 | 3.2825 | 1 | 3.2825 | 1
12 | Classroom | 633 | 42 |  | 1673 | 38 | 38 | Unit Ventilator | 13384 | 2.8377 | 1 | 2.8377 | 1
13 | Classroom | 541 | 36 |  | 1744 | 39 | 36 | Unit Ventilator | 13952 | 2.3265 | 1 | 2.3265 | 1
14 | Classroom | 334 | 22 |  | 1047 | 23 | 22 | Unit Ventilator | 8376 | 2.3926 | 1 | 2.3926 | 1
15 | Classroom | 507 | 33 |  | 1526 | 34 | 33 | Unit Ventilator | 12208 | 2.4918 | 1 | 2.4918 | 1
16A | Classroom | 238 | 15 |  | 731 | 16 | 15 | Unit Ventilator | 5848 | 2.4419 | 1 | 2.4419 | 1
16B | Classroom | 264 | 17 |  | 885 | 20 | 17 | Unit Ventilator | 7080 | 2.2373 | 1 | 2.2373 | 1
17A | Classroom | 380 | 25 |  | 661 | 15 | 15 | Unit Ventilator | 5288 | 4.3116 | 2 | 4.3116 | 2
17B | Classroom | 419 | 27 |  | 853 | 19 | 19 | Unit Ventilator | 6824 | 3.6841 | 1 | 3.6841 | 1
17C | Classroom | 259 | 17 |  | 1050 | 23 | 17 | Unit Ventilator | 8400 | 1.85 | 1 | 1.85 | 1
18B | Classroom | 0 | 0 |  | 962 | 21 | 0 | Unit Ventilator | 7696 | 0 | 0 | 0 | 0
18D | Classroom | 0 | 0 |  | 843 | 19 | 0 | Unit Ventilator | 6744 | 0 | 0 | 0 | 0
19B | Classroom | 374 | 24 |  | 862 | 19 | 19 | Unit Ventilator | 6896 | 3.2541 | 1 | 3.2541 | 1
21 | Offices | 0 | 0 |  | 1233 | 28 | 0 | Vertical Fan Coil Unit | 9864 | 0 | 0 | 0 | 0
22 | Office | 230 | 15 |  | 172 | 3 | 3 | Unit Ventilator | 1376 | 10.0291 | 3 | 10.0291 | 3
23 | Classroom | 260 | 17 |  | 741 | 16 | 16 | Unit Ventilator | 5928 | 2.6316 | 1 | 2.6316 | 1
24 | Classroom | 129 | 8 |  | 370 | 8 | 8 | Unit Ventilator | 2960 | 2.6149 | 1 | 2.6149 | 1
27 | Teacher's Lounge | 378 | 25 |  | 1205 | 27 | 25 | Unit Ventilator | 9640 | 2.3527 | 1 | 2.3527 | 1
31 | Classroom | 0 | 0 |  | 562 | 12 | 0 | Unit Ventilator | 4496 | 0 | 0 | 0 | 0
32 | Classrm. Lab | 2251 | 150 |  | 824 | 18 | 18 | Unit Ventilator | 6592 | 20.4885 | 3 | 20.4885 | 3
32A | Classrm. Lab | 0 | 0 |  | 435 | 9 | 0 | Unit Ventilator | 3480 | 0 | 0 | 0 | 0
34A | Office | 0 | 0 |  | 187 | 4 | 0 | Unit Ventilator | 1496 | 0 | 0 | 0 | 0
33 | Classroom | 499 | 33 |  | 571 | 12 | 12 | Unit Ventilator | 4568 | 6.5543 | 2 | 6.5543 | 2
35 | Office | 0 | 0 |  | 459 | 10 | 0 | Unit Ventilator | 3672 | 0 | 0 | 0 | 0
105 | Offices | 517 | 34 |  | 519 | 11 | 11 | Unit Ventilator | 4152 | 7.4711 | 2 | 7.4711 | 2
106 | Classroom | 748 | 49 |  | 1031 | 23 | 23 | Unit Ventilator | 8248 | 5.4413 | 2 | 5.4413 | 2
108 | Classroom | 739 | 49 |  | 948 | 21 | 21 | Unit Ventilator | 7584 | 5.8465 | 2 | 5.8465 | 2
109 | Classroom | 508 | 33 |  | 940 | 21 | 21 | Unit Ventilator | 7520 | 4.0532 | 2 | 4.0532 | 2
110 | Library | 610 | 40 |  | 386 | 8 | 8 | Unit Ventilator | 3088 | 11.8523 | 3 | 11.8523 | 3
111 | Classroom | 553 | 36 |  | 993 | 22 | 22 | Unit Ventilator | 7944 | 4.1767 | 2 | 4.1767 | 2
112 | Classroom | 602 | 40 |  | 980 | 22 | 22 | Unit Ventilator | 7840 | 4.6071 | 2 | 4.6071 | 2
113 | Classroom | 535 | 35 |  | 883 | 20 | 20 | Unit Ventilator | 7064 | 4.5442 | 2 | 4.5442 | 2
114 | Classroom | 363 | 24 |  | 717 | 16 | 16 | Unit Ventilator | 5736 | 3.7971 | 1 | 3.7971 | 1
115 | Room | 541 | 36 |  | 965 | 21 | 21 | Unit Ventilator | 7720 | 4.2047 | 2 | 4.2047 | 2
116 | Classroom | 623 | 41 |  | 745 | 16 | 16 | Unit Ventilator | 5960 | 6.2718 | 2 | 6.2718 | 2
117 | Classroom | 0 | 0 |  | 686 | 15 | 0 | Unit Ventilator | 5488 | 0 | 0 | 0 | 0
118 | Classroom | 543 | 36 |  | 842 | 19 | 19 | Unit Ventilator | 6736 | 4.8367 | 2 | 4.8367 | 2
119 | Classroom | 436 | 29 |  | 766 | 17 | 17 | Unit Ventilator | 6128 | 4.2689 | 2 | 4.2689 | 2
120 | Classroom | 370 | 24 |  | 741 | 16 | 16 | Unit Ventilator | 5928 | 3.7449 | 1 | 3.7449 | 1
121 | Classroom | 370 | 24 |  | 767 | 17 | 17 | Unit Ventilator | 6136 | 3.618 | 1 | 3.618 | 1
122 | Classroom | 495 | 33 |  | 1571 | 35 | 33 | Unit Ventilator | 12568 | 2.3631 | 1 | 2.3631 | 1
123 | Classroom | 403 | 26 |  | 738 | 16 | 16 | Unit Ventilator | 5904 | 4.0955 | 2 | 4.0955 | 2
124 | Classroom | 458 | 30 |  | 1410 | 32 | 30 | Unit Ventilator | 11280 | 2.4362 | 1 | 2.4362 | 1
125 | Classroom | 392 | 26 |  | 802 | 18 | 18 | Unit Ventilator | 6416 | 3.6658 | 1 | 3.6658 | 1
126 | Classroom | 326 | 21 |  | 698 | 15 | 15 | Unit Ventilator | 5584 | 3.5029 | 1 | 3.5029 | 1
127 | Classroom | 425 | 28 |  | 751 | 17 | 17 | Unit Ventilator | 6008 | 4.2443 | 2 | 4.2443 | 2
130 | Classroom | 481 | 32 |  | 1091 | 24 | 24 | Unit Ventilator | 8728 | 3.3066 | 1 | 3.3066 | 1
131 | Classroom | 409 | 27 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 4.3022 | 2 | 4.3022 | 2
132 | Classroom | 726 | 48 |  | 1038 | 23 | 23 | Unit Ventilator | 8304 | 5.2457 | 2 | 5.2457 | 2
133 | Classroom | 679 | 45 |  | 1627 | 36 | 36 | Unit Ventilator | 13016 | 3.13 | 1 | 3.13 | 1
133A | Office | 0 | 0 |  | 293 | 6 | 0 | Unit Ventilator | 2344 | 0 | 0 | 0 | 0
134 | Classroom | 181 | 12 |  | 402 | 9 | 9 | Unit Ventilator | 3216 | 3.3769 | 1 | 3.3769 | 1
136 | Classroom | 712 | 47 |  | 1206 | 27 | 27 | Unit Ventilator | 9648 | 4.4279 | 2 | 4.4279 | 2
137 | Classroom | 537 | 35 |  | 773 | 17 | 17 | Unit Ventilator | 6184 | 5.2102 | 2 | 5.2102 | 2
138 | Classroom | 453 | 30 |  | 1240 | 28 | 28 | Unit Ventilator | 9920 | 2.7399 | 1 | 2.7399 | 1
139 | Classroom | 601 | 40 |  | 798 | 18 | 18 | Unit Ventilator | 6384 | 5.6485 | 2 | 5.6485 | 2
140 | Classroom | 356 | 23 |  | 694 | 15 | 15 | Unit Ventilator | 5552 | 3.8473 | 1 | 3.8473 | 1
141 | Classroom | 510 | 34 |  | 773 | 17 | 17 | Unit Ventilator | 6184 | 4.9483 | 2 | 4.9483 | 2
143 | Classroom | 368 | 24 |  | 778 | 17 | 17 | Unit Ventilator | 6224 | 3.5476 | 1 | 3.5476 | 1
150 | Classroom | 118 | 7 |  | 845 | 19 | 7 | Unit Ventilator | 6760 | 1.0473 | 1 | 1.0473 | 1
152 | Classroom | 127 | 8 |  | 881 | 20 | 8 | Unit Ventilator | 7048 | 1.0812 | 1 | 1.0812 | 1
154 | Classroom | 0 | 0 |  | 874 | 19 | 0 | Unit Ventilator | 6992 | 0 | 0 | 0 | 0
156 | Classroom | 132 | 8 |  | 815 | 18 | 8 | Unit Ventilator | 6520 | 1.2147 | 1 | 1.2147 | 1
158 | Classroom | 160 | 10 |  | 849 | 19 | 10 | Unit Ventilator | 6792 | 1.4134 | 1 | 1.4134 | 1
160 | Classroom | 158 | 10 |  | 835 | 18 | 10 | Unit Ventilator | 6680 | 1.4192 | 1 | 1.4192 | 1
162 | Classroom | 0 | 0 |  | 711 | 16 | 0 | Unit Ventilator | 5688 | 0 | 0 | 0 | 0
175 | Classroom | 480 | 32 |  | 1223 | 27 | 27 | Unit Ventilator | 9784 | 2.9436 | 1 | 2.9436 | 1
200 | Classroom | 137 | 9 |  | 715 | 16 | 9 | Unit Ventilator | 5720 | 1.4371 | 1 | 1.4371 | 1
201 | Classroom | 548 | 36 |  | 728 | 16 | 16 | Unit Ventilator | 5824 | 5.6456 | 2 | 5.6456 | 2
202 | Classroom | 525 | 35 |  | 755 | 17 | 17 | Unit Ventilator | 6040 | 5.2152 | 2 | 5.2152 | 2
203 | Classroom | 232 | 15 |  | 555 | 12 | 12 | Unit Ventilator | 4440 | 3.1351 | 1 | 3.1351 | 1
203A | Classroom | 418 | 27 |  | 546 | 12 | 12 | Unit Ventilator | 4368 | 5.7418 | 2 | 5.7418 | 2
204 | Classroom | 523 | 34 |  | 572 | 13 | 13 | Unit Ventilator | 4576 | 6.8575 | 2 | 6.8575 | 2
205 | Classroom | 441 | 29 |  | 1073 | 24 | 24 | Unit Ventilator | 8584 | 3.0825 | 1 | 3.0825 | 1
206 | Classroom | 463 | 30 |  | 677 | 15 | 15 | Unit Ventilator | 5416 | 5.1292 | 2 | 5.1292 | 2
207 | Classroom | 790 | 52 |  | 651 | 14 | 14 | Unit Ventilator | 5208 | 9.1014 | 2 | 9.1014 | 2
208 | Classroom | 704 | 46 |  | 724 | 16 | 16 | Unit Ventilator | 5792 | 7.2928 | 2 | 7.2928 | 2
209 | Classroom | 769 | 51 |  | 1069 | 24 | 24 | Unit Ventilator | 8552 | 5.3952 | 2 | 5.3952 | 2
210 | Classroom | 410 | 27 |  | 730 | 16 | 16 | Unit Ventilator | 5840 | 4.2123 | 2 | 4.2123 | 2
211 | Classroom | 730 | 48 |  | 1069 | 24 | 24 | Unit Ventilator | 8552 | 5.1216 | 2 | 5.1216 | 2
212 | Classroom | 504 | 33 |  | 662 | 15 | 15 | Unit Ventilator | 5296 | 5.71 | 2 | 5.71 | 2
213 | Classroom | 650 | 43 |  | 1100 | 25 | 25 | Unit Ventilator | 8800 | 4.4318 | 2 | 4.4318 | 2
214 | Classroom | 522 | 34 |  | 713 | 16 | 16 | Unit Ventilator | 5704 | 5.4909 | 2 | 5.4909 | 2
215 A&B | Offices | 842 | 56 |  | 410 | 9 | 9 | Unit Ventilator | 3280 | 15.4024 | 3 | 15.4024 | 3
215 C&D | Offices | 833 | 55 |  | 410 | 9 | 9 | Unit Ventilator | 3280 | 15.2378 | 3 | 15.2378 | 3
216 | Classroom | 552 | 36 |  | 678 | 15 | 15 | Unit Ventilator | 5424 | 6.1062 | 2 | 6.1062 | 2
218 | Classroom | 527 | 35 |  | 677 | 15 | 15 | Unit Ventilator | 5416 | 5.8383 | 2 | 5.8383 | 2
219A | Classroom | 313 | 20 |  | 607 | 13 | 13 | Unit Ventilator | 4856 | 3.8674 | 1 | 3.8674 | 1
219B | Classroom | 322 | 21 |  | 446 | 10 | 10 | Unit Ventilator | 3568 | 5.4148 | 2 | 5.4148 | 2
220 | Classroom | 534 | 35 |  | 662 | 15 | 15 | Unit Ventilator | 5296 | 6.0498 | 2 | 6.0498 | 2
221A | Classroom | 307 | 20 |  | 717 | 16 | 16 | Unit Ventilator | 5736 | 3.2113 | 1 | 3.2113 | 1
221B | Classroom | 334 | 22 |  | 391 | 8 | 8 | Unit Ventilator | 3128 | 6.4066 | 2 | 6.4066 | 2
222 | Classroom | 547 | 36 |  | 792 | 18 | 18 | Unit Ventilator | 6336 | 5.1799 | 2 | 5.1799 | 2
223A | Classroom | 267 | 17 |  | 598 | 13 | 13 | Unit Ventilator | 4784 | 3.3487 | 1 | 3.3487 | 1
223C | Classroom | 426 | 28 |  | 373 | 8 | 8 | Unit Ventilator | 2984 | 8.5657 | 2 | 8.5657 | 2
225 | Classroom | 708 | 47 |  | 1445 | 32 | 32 | Unit Ventilator | 11560 | 3.6747 | 1 | 3.6747 | 1
227A | Classroom | 311 | 20 |  | 590 | 13 | 13 | Unit Ventilator | 4720 | 3.9534 | 1 | 3.9534 | 1
227B | Classroom | 298 | 19 |  | 494 | 11 | 11 | Unit Ventilator | 3952 | 4.5243 | 2 | 4.5243 | 2
228 | Classroom | 525 | 35 |  | 784 | 17 | 17 | Unit Ventilator | 6272 | 5.0223 | 2 | 5.0223 | 2
229B | Classroom | 165 | 11 |  | 525 | 11 | 11 | Unit Ventilator | 4200 | 2.3571 | 1 | 2.3571 | 1
229C | Classroom | 325 | 21 |  | 570 | 12 | 12 | Unit Ventilator | 4560 | 4.2763 | 2 | 4.2763 | 2
230 | Classroom | 503 | 33 |  | 657 | 14 | 14 | Unit Ventilator | 5256 | 5.742 | 2 | 5.742 | 2
231 | Classroom | 562 | 37 |  | 751 | 17 | 17 | Unit Ventilator | 6008 | 5.6125 | 2 | 5.6125 | 2
232 | Classroom | 592 | 39 |  | 691 | 15 | 15 | Unit Ventilator | 5528 | 6.4255 | 2 | 6.4255 | 2
233 | Classroom | 557 | 37 |  | 705 | 16 | 16 | Unit Ventilator | 5640 | 5.9255 | 2 | 5.9255 | 2
234 | Classroom | 532 | 35 |  | 703 | 15 | 15 | Unit Ventilator | 5624 | 5.6757 | 2 | 5.6757 | 2
235 | Classroom | 458 | 30 |  | 704 | 16 | 16 | Unit Ventilator | 5632 | 4.8793 | 2 | 4.8793 | 2
236 | Classroom | 405 | 27 |  | 701 | 15 | 15 | Unit Ventilator | 5608 | 4.3331 | 2 | 4.3331 | 2
237 | Room | 148 | 9 |  | 384 | 8 | 8 | Unit Ventilator | 3072 | 2.8906 | 1 | 2.8906 | 1
238 | Classroom | 389 | 25 |  | 675 | 15 | 15 | Unit Ventilator | 5400 | 4.3222 | 2 | 4.3222 | 2
240 | Classroom | 411 | 27 |  | 685 | 15 | 15 | Unit Ventilator | 5480 | 4.5 | 2 | 4.5 | 2
242 | Classroom | 479 | 31 |  | 711 | 16 | 16 | Unit Ventilator | 5688 | 5.0527 | 2 | 5.0527 | 2
244 | Classroom | 518 | 34 |  | 634 | 14 | 14 | Unit Ventilator | 5072 | 6.1278 | 2 | 6.1278 | 2
1st Fl. Corridor | Corridor | 0 | 0 |  | 892 | 20 | 0 | Unit Ventilator | 7136 | 0 | 0 | 0 | 0
2nd Fl. Corr. | 2nd Fl. Corr. | 0 | 0 |  | 9100 | 206 | 0 | Unit Ventilator | 72800 | 0 | 0 | 0 | 0
- | Auditorium | 1799 | 119 |  | 12288 | 279 | 119 | Heating Ventilation Unit | 98304 | 1.098 | 1 | 1.098 | 1
- | Band Room | 254 | 16 |  | 1028 | 23 | 16 | Heating Ventilation Unit | 8224 | 1.8531 | 1 | 1.8531 | 1
Boys Gym #1 | Gym | 336 | 22 |  | 3701 | 84 | 22 | Heating Ventilation Unit | 29608 | 0.6809 | 0 | 0.6809 | 0
Boys Gym #1 | Gym | 307 | 20 |  | 3701 | 84 | 20 | Heating Ventilation Unit | 29608 | 0.62213 | 0 | 0.62213 | 0
Boys Gym #2 | Gym | 2587 | 172 |  | 3701 | 84 | 84 | Heating Ventilation Unit | 29608 | 5.2425 | 2 | 5.2425 | 2
Boys Gym #2 | Gym | 1367 | 91 |  | 3701 | 84 | 84 | Heating Ventilation Unit | 29608 | 2.7702 | 1 | 2.7702 | 1
Boys Lckr. Rm. | Locker Rm. | 1229 | 81 |  | 5966 | 135 | 81 | Heating Ventilation Unit | 47728 | 1.545 | 1 | 1.545 | 1
Cafeteria | Cafeteria | 1685 | 112 |  | 12073 | 274 | 112 | Heating Ventilation Unit | 96584 | 1.0468 | 1 | 1.0468 | 1
Girls Gym #1 | Gym | 317 | 21 |  | 3514 | 79 | 21 | Heating Ventilation Unit | 28112 | 0.67658 | 0 | 0.67658 | 0
Girls Gym #1 | Gym | 397 | 26 |  | 3514 | 79 | 26 | Heating Ventilation Unit | 28112 | 0.84732 | 0 | 0.84732 | 0
Girls Gym #2 | Gym | 187 | 12 |  | 3514 | 79 | 12 | Heating Ventilation Unit | 28112 | 0.39912 | 0 | 0.39912 | 0
Girls Lckr. Rm. | Locker Rm. | 0 | 0 |  | 3920 | 89 | 0 | Heating Ventilation Unit | 31360 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  | 3443 | 78 | 0 | Unit Ventilator | 27544 | 0 | 0 | 0 | 0
Library | Library | 2751 | 183 |  | 1816 | 41 | 41 | Heating Ventilation Unit | 14528 | 11.3615 | 3 | 11.3615 | 3
Library | Library | 453 | 30 |  | 454 | 10 | 10 | Unit Ventilator | 3632 | 7.4835 | 2 | 7.4835 | 2
Library | Library | 525 | 35 |  | 454 | 10 | 10 | Unit Ventilator | 3632 | 8.6729 | 2 | 8.6729 | 2
Library | Library | 509 | 33 |  | 454 | 10 | 10 | Unit Ventilator | 3632 | 8.4086 | 2 | 8.4086 | 2
Library | Library | 477 | 31 |  | 454 | 10 | 10 | Unit Ventilator | 3632 | 7.88 | 2 | 7.88 | 2
Main office | Offices | 446 | 29 |  | 2450 | 55 | 29 | Unit Ventilator | 19600 | 1.3653 | 1 | 1.3653 | 1
Stage | Stage | 235 | 15 |  | 1743 | 39 | 15 | Unit Ventilator | 13944 | 1.0112 | 1 | 1.0112 | 1
Stage | Stage | 262 | 17 |  | 1743 | 39 | 17 | Unit Ventilator | 13944 | 1.1274 | 1 | 1.1274 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Olney Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Main Building ABR | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Main Building | [9 empty] | unk | unk | unk | unk
101 | Classroom | 180 | 12 |  | 520 | 11 | 11 | AIr Handling Unit | 4160 | 2.5962 | 1 | 2.5962 | 1
102 | Classroom | 122 | 8 |  | 520 | 11 | 8 | AIr Handling Unit | 4160 | 1.7596 | 1 | 1.7596 | 1
103 | Classroom | 142 | 9 |  | 520 | 11 | 9 | AIr Handling Unit | 4160 | 2.0481 | 1 | 2.0481 | 1
104 | Classroom | 527 | 35 |  | 520 | 11 | 11 | AIr Handling Unit | 4160 | 7.601 | 2 | 7.601 | 2
107 | Classroom | 63 | 4 |  | 667 | 15 | 4 | Univent | 5336 | 0.7084 | 0 | 0.7084 | 0
108 | Classroom | 235 | 15 |  | 840 | 19 | 15 | Univent | 6720 | 2.0982 | 1 | 2.0982 | 1
111 | Classroom | 88 | 5 |  | 378 | 8 | 5 | Univent | 3024 | 1.746 | 1 | 1.746 | 1
201 | Classroom | 289 | 19 |  | 682 | 15 | 15 | Univent | 5456 | 3.1782 | 1 | 3.1782 | 1
203 | Classroom | 327 | 21 |  | 928 | 21 | 21 | Univent | 7424 | 2.6428 | 1 | 2.6428 | 1
204 | Classroom | 286 | 19 |  | 756 | 17 | 17 | Univent | 6048 | 2.8373 | 1 | 2.8373 | 1
205 | Classroom | 303 | 20 |  | 784 | 17 | 17 | Univent | 6272 | 2.8986 | 1 | 2.8986 | 1
206 | Classroom | 296 | 19 |  | 812 | 18 | 18 | Univent | 6496 | 2.734 | 1 | 2.734 | 1
207 | Classroom | 309 | 20 |  | 594 | 13 | 13 | Univent | 4752 | 3.9015 | 1 | 3.9015 | 1
208 | Classroom | 324 | 21 |  | 748 | 17 | 17 | Univent | 5984 | 3.2487 | 1 | 3.2487 | 1
209 | Classroom | 282 | 18 |  | 1232 | 28 | 18 | Univent | 9856 | 1.7167 | 1 | 1.7167 | 1
210 | Classroom | 327 | 21 |  | 330 | 7 | 7 | Univent | 2640 | 7.4318 | 2 | 7.4318 | 2
211 | Classroom | 326 | 21 |  | 756 | 17 | 17 | Univent | 6048 | 3.2341 | 1 | 3.2341 | 1
301 | Classroom | 0 | 0 |  | 682 | 15 | 0 | Univent | 5456 | 0 | 0 | 0 | 0
302 | Classroom | 328 | 21 |  | 682 | 15 | 15 | Univent | 5456 | 3.607 | 1 | 3.607 | 1
303 | Classroom | 281 | 18 |  | 899 | 20 | 18 | Univent | 7192 | 2.3443 | 1 | 2.3443 | 1
304 | Classroom | 280 | 18 |  | 729 | 16 | 16 | Univent | 5832 | 2.8807 | 1 | 2.8807 | 1
305 | Classroom | 324 | 21 |  | 812 | 18 | 18 | Univent | 6496 | 2.9926 | 1 | 2.9926 | 1
306 | Classroom | 285 | 19 |  | 783 | 17 | 17 | Univent | 6264 | 2.7299 | 1 | 2.7299 | 1
307 | Classroom | 279 | 18 |  | 594 | 13 | 13 | Univent | 4752 | 3.5227 | 1 | 3.5227 | 1
308 | Classroom | 291 | 19 |  | 782 | 17 | 17 | Univent | 6256 | 2.7909 | 1 | 2.7909 | 1
309 | Classroom | 325 | 21 |  | 638 | 14 | 14 | Univent | 5104 | 3.8205 | 1 | 3.8205 | 1
310 | Classroom | 328 | 21 |  | 638 | 14 | 14 | Univent | 5104 | 3.8558 | 1 | 3.8558 | 1
311 | Classroom | 309 | 20 |  | 756 | 17 | 17 | Univent | 6048 | 3.0655 | 1 | 3.0655 | 1
- | Main Office |  | 0 |  | 480 | 10 | 0 |  | 3840 | unk | unk | unk | unk
- | Principal's Office | 173 | 11 |  | 396 | 9 | 9 | Univent | 3168 | 3.2765 | 1 | 3.2765 | 1
- | Boys' Cafeteria |  | 0 | Yes | 1271 | 28 |  | Active Pure | 10168 | unk | unk | 20 | 3
- | Girls' Cafeteria |  | 0 | Yes | 943 | 21 |  | Active Pure | 7544 | unk | unk | 20 | 3
Annex | [9 empty] | unk | unk | unk | unk
1 | Classroom |  | 0 | Yes | 684 | 15 | 15 |  | 5472 | unk | unk | 20 | 3
2 | Classroom |  | 0 | Yes | 1050 | 23 | 23 |  | 8400 | unk | unk | 20 | 3
3 | Classroom |  | 0 | Yes | 792 | 18 | 18 |  | 6336 | unk | unk | 20 | 3
4 | Classroom |  | 0 | Yes | 840 | 19 | 19 |  | 6720 | unk | unk | 20 | 3
5 | Classroom |  | 0 | Yes | 1104 | 25 | 25 |  | 8832 | unk | unk | 20 | 3
6 | Classroom |  | 0 | Yes | 700 | 15 | 15 |  | 5600 | unk | unk | 20 | 3
7 | Classroom |  | 0 | Yes | 1050 | 23 | 23 |  | 8400 | unk | unk | 20 | 3
8 | Classroom |  | 0 | Yes | 816 | 18 | 18 |  | 6528 | unk | unk | 20 | 3
9 | Classroom |  | 0 | Yes | 840 | 19 | 19 |  | 6720 | unk | unk | 20 | 3
10 | Classroom |  | 0 | Yes | 875 | 19 | 19 |  | 7000 | unk | unk | 20 | 3
- | Lobby |  | 0 | Yes | 180 | 4 | 4 |  | 1440 | unk | unk | 20 | 3
- | Counselor Office |  | 0 | Yes | 108 | 2 | 2 |  | 864 | unk | unk | 20 | 3
- | Asst Principal's Office |  | 0 | Yes | 89 | 2 | 2 |  | 712 | unk | unk | 20 | 3
- | Gym |  | 0 | Yes | 4328 | 98 | 98 | Hydroxyl Unit | 34624 | unk | unk | 20 | 3
- | Nurse Open area (Office D) and Early Lit |  | 0 | Yes | 547 | 12 | 12 |  | 4376 | unk | unk | 20 | 3
- | Conference room (medical waiting) |  | 0 | Yes | 141 | 3 | 3 |  | 1128 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | One Bright Ray- Elmwood | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 313 | 20 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
102 | Classroom | 189 | 12 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
103 | Classroom | 249 | 16 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
104 | Classroom | 215 | 14 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
105 | Classroom | 250 | 16 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
105 | Principal's Office | 58 | 3 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Dean of Students Office | 56 | 3 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Faculty Lounge | 69 | 4 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Foyer / Hallway | 147 | 9 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Open Space / Classroom | 475 | 31 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | SW Office | 48 | 3 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | Overbrook Educational Center Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | Retest | [7 empty] | unk | unk | unk | unk
School: | Overbrook Education Center Annex | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Main Building | [9 empty] | unk | unk | unk | unk
- | Boiler Room | 602 | 40 |  | 1496 | 34 | 34 | AHU | 11968 | 3.018 | 1 | 3.018 | 1
- | BE Office |  | 0 |  | 491 | 11 | 0 | AHU | 3928 | unk | unk | unk | unk
- | Cafeteria | 233 | 15 | Yes | 1936 | 44 | 44 | AHU | 15488 | 0.90263 | 0 | 20.9026 | 3
- | Corridor | 49 | 3 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | Kitchen | 53 | 3 |  | 440 | 10 | 3 | AHU | 3520 | 0.90341 | 0 | 0.90341 | 0
- | Music Room | 204 | 13 |  | 748 | 17 | 13 | AHU | 5984 | 2.0455 | 1 | 2.0455 | 1
- | Computer Room | 79 | 5 |  | 176 | 4 | 4 | AHU | 1408 | 3.3665 | 1 | 3.3665 | 1
- | 1st Flr Entryway | 42 | 2 |  | 396 | 9 | 2 | AHU | 3168 | 0.79545 | 0 | 0.79545 | 0
- | Exam Office | 32 | 2 |  | 176 | 4 | 2 | AHU | 1408 | 1.3636 | 1 | 1.3636 | 1
- | Gym Office | 28 | 1 |  | 132 | 3 | 1 | AHU | 1056 | 1.5909 | 1 | 1.5909 | 1
- | Gym /Stage | 1257 | 83 |  | 2332 | 53 | 53 | AHU | 18656 | 4.0427 | 2 | 4.0427 | 2
- | Gym Lobby | 109 | 7 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
1st flr Hallway | Corridor | 20 | 1 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
1st flr Lobby | Main Lobby | 71 | 4 |  | 396 | 9 | 4 | AHU | 3168 | 1.3447 | 1 | 1.3447 | 1
1st flr Main Office | Administration | 65 | 4 |  | 220 | 5 | 4 | AHU | 1760 | 2.2159 | 1 | 2.2159 | 1
1st flr Nurse's Office | Medical | 38 | 2 |  | 264 | 6 | 2 | AHU | 2112 | 1.0795 | 1 | 1.0795 | 1
1st flr Office | Principal | 49 | 3 |  | 220 | 5 | 3 | AHU | 1760 | 1.6705 | 1 | 1.6705 | 1
1st flr Office | Copy Room | 19 | 1 |  | 88 | 2 | 1 | AHU | 704 | 1.6193 | 1 | 1.6193 | 1
1st flr Office | Conference Room | 47 | 3 |  | 176 | 4 | 3 | AHU | 1408 | 2.0028 | 1 | 2.0028 | 1
201 | Faculty Lounge | 161 | 10 |  | 220 | 5 | 5 | AHU | 1760 | 5.4886 | 2 | 5.4886 | 2
204 | Office | 171 | 11 | Yes | 176 | 4 | 4 | RTU | 1408 | 7.2869 | 2 | 27.2869 | 4
206 | Classroom | 370 | 24 |  | 660 | 15 | 15 | Univent | 5280 | 4.2045 | 2 | 4.2045 | 2
207 | Classroom | 353 | 23 |  | 748 | 17 | 17 | Univent | 5984 | 3.5394 | 1 | 3.5394 | 1
208 | Classroom | 446 | 29 |  | 748 | 17 | 17 | Univent | 5984 | 4.4719 | 2 | 4.4719 | 2
209 | Classroom | 475 | 31 |  | 572 | 13 | 13 | Univent | 4576 | 6.2281 | 2 | 6.2281 | 2
210 | Classroom | 425 | 28 |  | 660 | 15 | 15 | Univent | 5280 | 4.8295 | 2 | 4.8295 | 2
211 | Classroom (Life Skills) | 536 | 35 |  | 748 | 17 | 17 | Univent | 5984 | 5.3743 | 2 | 5.3743 | 2
2nd flr Library | Library | 344 | 22 |  | 1496 | 34 | 22 | AHU | 11968 | 1.7246 | 1 | 1.7246 | 1
2nd flr Art | Classroom | 74 | 4 |  | 924 | 21 | 4 | AHU | 7392 | 0.60065 | 0 | 0.60065 | 0
2nd Flr Hallway | Corridor | 197 | 13 |  |  | 0 | 0 | AAON unit |  | unk | unk | unk | unk
2nd flr Science | Classroom | 84 | 5 |  | 836 | 19 | 5 | AHU | 6688 | 0.75359 | 0 | 0.75359 | 0
301 | Classroom | 452 | 30 |  | 220 | 5 | 5 | RTU | 1760 | 15.4091 | 3 | 15.4091 | 3
302 | Office | 284 | 18 |  | 176 | 4 | 4 | AHU | 1408 | 12.1023 | 3 | 12.1023 | 3
304 | Classroom | 463 | 30 |  | 660 | 15 | 15 | Univent | 5280 | 5.2614 | 2 | 5.2614 | 2
305 | Classroom | 517 | 34 |  | 748 | 17 | 17 | Univent | 5984 | 5.1838 | 2 | 5.1838 | 2
306 | Classroom | 550 | 36 |  | 704 | 16 | 16 | Univent | 5632 | 5.8594 | 2 | 5.8594 | 2
307 | Classroom | 596 | 39 |  | 572 | 13 | 13 | Univent | 4576 | 7.8147 | 2 | 7.8147 | 2
308 | Classroom | 461 | 30 |  | 660 | 15 | 15 | Univent | 5280 | 5.2386 | 2 | 5.2386 | 2
309 | Classroom | 1030 | 68 |  | 748 | 17 | 17 | Univent | 5984 | 10.3275 | 3 | 10.3275 | 3
316 | Classroom |  | 0 | Yes | 695 | 15 | 15 |  | 5560 | unk | unk | 20 | 3
Annex Building | [9 empty] | unk | unk | unk | unk
5 | Kitchen |  | 0 | Yes | 157 | 3 | 3 |  | 1256 | unk | unk | 20 | 3
6 | Office |  | 0 | Yes | 122 | 2 | 2 |  | 976 | unk | unk | 20 | 3
7 | Lobby |  | 0 |  | 890 | 20 | 0 |  | 7120 | unk | unk | unk | unk
1 | Classroom |  | 0 | Yes | 1077 | 24 | 24 |  | 8616 | unk | unk | 20 | 3
2 | Classroom |  | 0 | Yes | 404 | 9 | 9 |  | 3232 | unk | unk | 20 | 3
25 | Classroom |  | 0 | Yes | 555 | 12 | 12 |  | 4440 | unk | unk | 20 | 3
24 | Office |  | 0 | Yes | 177 | 4 | 4 |  | 1416 | unk | unk | 20 | 3
22 | Classroom |  | 0 | Yes | 902 | 20 | 20 |  | 7216 | unk | unk | 20 | 3
21 | Classroom |  | 0 | Yes | 297 | 6 | 6 |  | 2376 | unk | unk | 20 | 3
31 | Classroom |  | 0 | Yes | 304 | 6 | 6 |  | 2432 | unk | unk | 20 | 3
32 | Classroom |  | 0 | Yes | 909 | 20 | 20 |  | 7272 | unk | unk | 20 | 3
34 | Classroom |  | 0 |  | 232 | 5 | 0 |  | 1856 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | Overbrook Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Classroom | 825 | 55 |  | 720 | 16 | 16 | House fan | 5760 | 8.5938 | 2 | 8.5938 | 2
2 | Classroom | 798 | 53 |  | 720 | 16 | 16 | House fan | 5760 | 8.3125 | 2 | 8.3125 | 2
3 | Classroom | 872 | 58 |  | 720 | 16 | 16 | House fan | 5760 | 9.0833 | 2 | 9.0833 | 2
4 | Classroom | 838 | 55 |  | 528 | 12 | 12 | House fan | 4224 | 11.9034 | 3 | 11.9034 | 3
5 | Classroom | 579 | 38 |  | 720 | 16 | 16 | House fan | 5760 | 6.0312 | 2 | 6.0312 | 2
6 | Classroom | 499 | 33 |  | 720 | 16 | 16 | House fan | 5760 | 5.1979 | 2 | 5.1979 | 2
7 | Classroom | 816 | 54 |  | 768 | 17 | 17 | House fan | 6144 | 7.9688 | 2 | 7.9688 | 2
8 | Classroom | 614 | 40 |  | 768 | 17 | 17 | House fan | 6144 | 5.9961 | 2 | 5.9961 | 2
9 | Classroom | 788 | 52 |  | 768 | 17 | 17 | House fan | 6144 | 7.6953 | 2 | 7.6953 | 2
12 | Classroom | 522 | 34 |  | 720 | 16 | 16 | House fan | 5760 | 5.4375 | 2 | 5.4375 | 2
13 | Classroom | 581 | 38 |  | 720 | 16 | 16 | House fan | 5760 | 6.0521 | 2 | 6.0521 | 2
14 | Classroom | 472 | 31 |  | 720 | 16 | 16 | House fan | 5760 | 4.9167 | 2 | 4.9167 | 2
15 | Classroom | 412 | 27 |  | 720 | 16 | 16 | House fan | 5760 | 4.2917 | 2 | 4.2917 | 2
16 | Classroom | 505 | 33 |  | 720 | 16 | 16 | House fan | 5760 | 5.2604 | 2 | 5.2604 | 2
17 | Classroom | 524 | 34 |  | 720 | 16 | 16 | House fan | 5760 | 5.4583 | 2 | 5.4583 | 2
18 | Classroom | 508 | 33 |  | 768 | 17 | 17 | House fan | 6144 | 4.9609 | 2 | 4.9609 | 2
19 | Classroom | 654 | 43 |  | 768 | 17 | 17 | House fan | 6144 | 6.3867 | 2 | 6.3867 | 2
20 | Classroom | 498 | 33 |  | 768 | 17 | 17 | House fan | 6144 | 4.8633 | 2 | 4.8633 | 2
- | Boys Bathroom | 826 | 55 |  | 736 | 16 | 16 | House fan | 5888 | 8.4171 | 2 | 8.4171 | 2
- | Cafeteria | 1236 | 82 |  | 1560 | 35 | 35 | House fan | 12480 | 5.9423 | 2 | 5.9423 | 2
- | Faculty bathroom | 40 | 2 |  | 64 | 1 | 1 | House fan | 512 | 4.6875 | 2 | 4.6875 | 2
- | Girls Bathroom | 445 | 29 |  | 340 | 7 | 7 | House fan | 2720 | 9.8162 | 2 | 9.8162 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | Overbrook High School | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
10 | - |  | 0 |  | 1041 | 23 | 0 |  | 8328 | unk | unk | unk | unk
11 | - |  | 0 |  | 1450 | 32 | 0 |  | 11600 | unk | unk | unk | unk
100 | Classroom |  | 0 |  | 1409 | 32 | 0 |  | 11272 | unk | unk | unk | unk
100A | Classroom |  | 0 | Yes | 435 | 9 | 9 |  | 3480 | unk | unk | 20 | 3
100B | Classroom |  | 0 | Yes | 479 | 10 | 10 |  | 3832 | unk | unk | 20 | 3
100C | Classroom |  | 0 | Yes | 1407 | 31 | 31 |  | 11256 | unk | unk | 20 | 3
101 | Classroom |  | 0 | Yes | 832 | 18 | 18 |  | 6656 | unk | unk | 20 | 3
102 | Classroom |  | 0 |  | 742 | 16 | 0 |  | 5936 | unk | unk | unk | unk
103 | Classroom |  | 0 |  | 692 | 15 | 0 |  | 5536 | unk | unk | unk | unk
104 | Classroom |  | 0 |  | 649 | 14 | 0 |  | 5192 | unk | unk | unk | unk
105 | Classroom |  | 0 |  | 990 | 22 | 0 |  | 7920 | unk | unk | unk | unk
105A | Classroom |  | 0 |  | 228 | 5 | 0 |  | 1824 | unk | unk | unk | unk
106A | Classroom |  | 0 |  | 535 | 12 | 0 |  | 4280 | unk | unk | unk | unk
160B | Classroom |  | 0 |  | 534 | 12 | 0 |  | 4272 | unk | unk | unk | unk
107 | Classroom |  | 0 |  | 703 | 15 | 0 |  | 5624 | unk | unk | unk | unk
108 | Classroom |  | 0 |  | 677 | 15 | 0 |  | 5416 | unk | unk | unk | unk
109A | Classroom |  | 0 |  | 551 | 12 | 0 |  | 4408 | unk | unk | unk | unk
109B | Classroom |  | 0 |  | 507 | 11 | 0 |  | 4056 | unk | unk | unk | unk
110 | Classroom |  | 0 |  | 931 | 21 | 0 |  | 7448 | unk | unk | unk | unk
117 | Classroom |  | 0 |  | 515 | 11 | 0 |  | 4120 | unk | unk | unk | unk
118 | Classroom |  | 0 |  | 556 | 12 | 0 |  | 4448 | unk | unk | unk | unk
119 | Classroom |  | 0 |  | 753 | 17 | 0 |  | 6024 | unk | unk | unk | unk
120 | Classroom |  | 0 |  | 1026 | 23 | 0 |  | 8208 | unk | unk | unk | unk
121 | Classroom |  | 0 |  | 1048 | 23 | 0 |  | 8384 | unk | unk | unk | unk
200 | Classroom |  | 0 |  | 304 | 6 | 0 |  | 2432 | unk | unk | unk | unk
201 | Classroom |  | 0 |  | 496 | 11 | 0 |  | 3968 | unk | unk | unk | unk
201 | Classroom |  | 0 |  | 490 | 11 | 0 |  | 3920 | unk | unk | unk | unk
202 | Classroom |  | 0 |  | 486 | 11 | 0 |  | 3888 | unk | unk | unk | unk
204 | Classroom |  | 0 |  | 881 | 20 | 0 |  | 7048 | unk | unk | unk | unk
205 | Classroom |  | 0 |  | 733 | 16 | 0 |  | 5864 | unk | unk | unk | unk
206 | Classroom |  | 0 |  | 1003 | 22 | 0 |  | 8024 | unk | unk | unk | unk
207 | Classroom |  | 0 |  | 718 | 16 | 0 |  | 5744 | unk | unk | unk | unk
209 | Classroom |  | 0 |  | 337 | 7 | 0 |  | 2696 | unk | unk | unk | unk
210 | Classroom |  | 0 |  | 460 | 10 | 0 |  | 3680 | unk | unk | unk | unk
211 | Classroom |  | 0 |  | 713 | 16 | 0 |  | 5704 | unk | unk | unk | unk
212 | Classroom |  | 0 |  | 728 | 16 | 0 |  | 5824 | unk | unk | unk | unk
213 | Classroom |  | 0 |  | 902 | 20 | 0 |  | 7216 | unk | unk | unk | unk
214 | Classroom |  | 0 |  | 796 | 18 | 0 |  | 6368 | unk | unk | unk | unk
215 | Classroom |  | 0 |  | 3413 | 77 | 0 |  | 27304 | unk | unk | unk | unk
216 | Classroom |  | 0 |  | 850 | 19 | 0 |  | 6800 | unk | unk | unk | unk
217 | Classroom |  | 0 |  | 712 | 16 | 0 |  | 5696 | unk | unk | unk | unk
218 | Classroom |  | 0 |  | 700 | 15 | 0 |  | 5600 | unk | unk | unk | unk
219 | Classroom |  | 0 |  | 719 | 16 | 0 |  | 5752 | unk | unk | unk | unk
220 | Classroom |  | 0 |  | 359 | 8 | 0 |  | 2872 | unk | unk | unk | unk
221 | Classroom |  | 0 |  | 877 | 19 | 0 |  | 7016 | unk | unk | unk | unk
222 | Classroom |  | 0 |  | 877 | 19 | 0 |  | 7016 | unk | unk | unk | unk
223 | Classroom |  | 0 |  | 729 | 16 | 0 |  | 5832 | unk | unk | unk | unk
224 | Classroom |  | 0 |  | 731 | 16 | 0 |  | 5848 | unk | unk | unk | unk
225 | Classroom |  | 0 |  | 694 | 15 | 0 |  | 5552 | unk | unk | unk | unk
300 | Classroom |  | 0 |  | 747 | 16 | 0 |  | 5976 | unk | unk | unk | unk
301 | Classroom |  | 0 |  | 724 | 16 | 0 |  | 5792 | unk | unk | unk | unk
302 | Classroom |  | 0 |  | 737 | 16 | 0 |  | 5896 | unk | unk | unk | unk
303 | Classroom |  | 0 |  | 907 | 20 | 0 |  | 7256 | unk | unk | unk | unk
304 | Classroom |  | 0 |  | 941 | 21 | 0 |  | 7528 | unk | unk | unk | unk
305 | Classroom |  | 0 |  | 724 | 16 | 0 |  | 5792 | unk | unk | unk | unk
306 | Classroom |  | 0 |  | 738 | 16 | 0 |  | 5904 | unk | unk | unk | unk
307 | Classroom |  | 0 |  | 739 | 16 | 0 |  | 5912 | unk | unk | unk | unk
308 | Classroom |  | 0 |  | 834 | 18 | 0 |  | 6672 | unk | unk | unk | unk
309 | Classroom |  | 0 |  | 733 | 16 | 0 |  | 5864 | unk | unk | unk | unk
311 | Classroom |  | 0 |  | 721 | 16 | 0 |  | 5768 | unk | unk | unk | unk
312 | Classroom |  | 0 |  | 704 | 16 | 0 |  | 5632 | unk | unk | unk | unk
313 | Classroom |  | 0 |  | 491 | 11 | 0 |  | 3928 | unk | unk | unk | unk
314 | Classroom |  | 0 |  | 669 | 15 | 0 |  | 5352 | unk | unk | unk | unk
315 | Classroom |  | 0 |  | 673 | 15 | 0 |  | 5384 | unk | unk | unk | unk
316 | Classroom |  | 0 | Yes | 762 | 17 | 17 |  | 6096 | unk | unk | 20 | 3
317 | Classroom |  | 0 | Yes | 917 | 20 | 20 |  | 7336 | unk | unk | 20 | 3
318 | Classroom |  | 0 |  | 669 | 15 | 0 |  | 5352 | unk | unk | unk | unk
319 | Classroom |  | 0 |  | 681 | 15 | 0 |  | 5448 | unk | unk | unk | unk
320 | Classroom |  | 0 |  | 724 | 16 | 0 |  | 5792 | unk | unk | unk | unk
321 | Classroom |  | 0 |  | 712 | 16 | 0 |  | 5696 | unk | unk | unk | unk
322 | Classroom |  | 0 |  | 499 | 11 | 0 |  | 3992 | unk | unk | unk | unk
323 | Classroom |  | 0 |  | 437 | 9 | 0 |  | 3496 | unk | unk | unk | unk
324 | Classroom |  | 0 |  | 801 | 18 | 0 |  | 6408 | unk | unk | unk | unk
325 | Classroom |  | 0 |  | 936 | 21 | 0 |  | 7488 | unk | unk | unk | unk
326 | Classroom |  | 0 |  | 690 | 15 | 0 |  | 5520 | unk | unk | unk | unk
327 | Classroom |  | 0 |  | 191 | 4 | 0 |  | 1528 | unk | unk | unk | unk
328 | Classroom |  | 0 |  | 683 | 15 | 0 |  | 5464 | unk | unk | unk | unk
329 | Classroom |  | 0 |  | 711 | 16 | 0 |  | 5688 | unk | unk | unk | unk
330 | Classroom |  | 0 |  | 690 | 15 | 0 |  | 5520 | unk | unk | unk | unk
331 | Classroom |  | 0 |  | 204 | 4 | 0 |  | 1632 | unk | unk | unk | unk
332 | Classroom |  | 0 |  | 687 | 15 | 0 |  | 5496 | unk | unk | unk | unk
333 | Classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | unk | unk | unk | unk
334 | Classroom |  | 0 |  | 817 | 18 | 0 |  | 6536 | unk | unk | unk | unk
- | Main Office |  | 0 |  | 1057 | 24 | 0 |  | 8456 | unk | unk | unk | unk
- | Principal Office |  | 0 |  | 562 | 12 | 0 |  | 4496 | unk | unk | unk | unk
- | Auditorium Balcony |  | 0 |  | 1436 | 32 | 0 |  | 11488 | unk | unk | unk | unk
- | Auditorium |  | 0 |  | 8711 | 197 | 0 |  | 69688 | unk | unk | unk | unk
- | Teachers Lounge |  | 0 |  | 310 | 7 | 0 |  | 2480 | unk | unk | unk | unk
- | Cafeteria A |  | 0 |  | 2778 | 63 | 0 |  | 22224 | unk | unk | unk | unk
- | Cafeteria B |  | 0 |  | 4516 | 102 | 0 |  | 36128 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Academy @ Palumbo High School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
103 | Graphics Arts | 1248 | 83 |  | 1058 | 24 | 24 | Air Handling Unit | 8464 | 8.8469 | 2 | 8.8469 | 2
104 | Fine Arts | 271 | 18 |  | 782 | 17 | 17 | Air Handling Unit | 6256 | 2.5991 | 1 | 2.5991 | 1
118 | Conference Room | 1440 | 96 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 15.6522 | 3 | 15.6522 | 3
129 | Main Office | 723 | 48 |  | 528 | 12 | 12 | Air Handling Unit | 4224 | 10.2699 | 3 | 10.2699 | 3
132 | Mixed Choir | 736 | 49 |  | 966 | 21 | 21 | Air Handling Unit | 7728 | 5.7143 | 2 | 5.7143 | 2
134 | Music Theory | 1170 | 78 |  | 946 | 21 | 21 | Air Handling Unit | 7568 | 9.2759 | 2 | 9.2759 | 2
135 | Intro to Music | 1709 | 113 |  | 968 | 22 | 22 | Air Handling Unit | 7744 | 13.2412 | 3 | 13.2412 | 3
136 | Music Equipment Storage | 609 | 40 |  | 396 | 9 | 9 | Air Handling Unit | 3168 | 11.5341 | 3 | 11.5341 | 3
204 | Creative Writing | 843 | 56 |  | 660 | 15 | 15 | Air Handling Unit | 5280 | 9.5795 | 2 | 9.5795 | 2
205 | Computer Lab | 653 | 43 |  | 768 | 17 | 17 | Air Handling Unit | 6144 | 6.377 | 2 | 6.377 | 2
206 | Environment Club | 713 | 47 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 7.75 | 2 | 7.75 | 2
207 | Language & Journalism | 1069 | 71 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 11.6196 | 3 | 11.6196 | 3
212 | Visitor's Locker Room | 615 | 41 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 6.4062 | 2 | 6.4062 | 2
221 | History | 618 | 41 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 6.7174 | 2 | 6.7174 | 2
223 | Literature | 750 | 50 |  | 1104 | 25 | 25 | Air Handling Unit | 8832 | 5.0951 | 2 | 5.0951 | 2
224 | English / History | 113 | 7 |  | 660 | 15 | 7 | Air Handling Unit | 5280 | 1.2841 | 1 | 1.2841 | 1
231 | Office | 595 | 39 |  | 484 | 11 | 11 | Air Handling Unit | 3872 | 9.22 | 2 | 9.22 | 2
301 | Forensics / Algebra 2 | 604 | 40 |  | 528 | 12 | 12 | Air Handling Unit | 4224 | 8.5795 | 2 | 8.5795 | 2
302 | Dean's Office | 1510 | 100 |  | 440 | 10 | 10 | Air Handling Unit | 3520 | 25.7386 | 4 | 25.7386 | 4
305 | History | 257 | 17 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 2.7935 | 1 | 2.7935 | 1
306 | Spanish | 554 | 36 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 6.0217 | 2 | 6.0217 | 2
307 | American History | 282 | 18 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 3.0652 | 1 | 3.0652 | 1
312 | Cardio & Weight Lifting | 615 | 41 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 6.4062 | 2 | 6.4062 | 2
321 | Spanish | 666 | 44 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 7.2391 | 2 | 7.2391 | 2
321 | History | 532 | 35 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 5.7826 | 2 | 5.7826 | 2
322 | History | 1582 | 105 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 17.1957 | 3 | 17.1957 | 3
323 | Spanish | 567 | 37 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 6.163 | 2 | 6.163 | 2
332 | Black History | 84 | 5 |  | 638 | 14 | 5 | Air Handling Unit | 5104 | 0.98746 | 0 | 0.98746 | 0
333 | History | 1066 | 71 |  | 792 | 18 | 18 | Air Handling Unit | 6336 | 10.0947 | 3 | 10.0947 | 3
334 | Psychologist | 0 | 0 |  | 567 | 12 | 0 | Air Handling Unit | 4536 | 0 | 0 | 0 | 0
336 | Spanish | 0 | 0 |  | 1058 | 24 | 0 | Air Handling Unit | 8464 | 0 | 0 | 0 | 0
403 | Physics Lab | 322 | 21 |  | 1056 | 24 | 21 | Air Handling Unit | 8448 | 2.2869 | 1 | 2.2869 | 1
407 | Biology Lab | 587 | 39 |  | 1440 | 32 | 32 | Air Handling Unit | 11520 | 3.0573 | 1 | 3.0573 | 1
411 | Chemistry | 651 | 43 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 6.7812 | 2 | 6.7812 | 2
412 | Unknown | 668 | 44 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 6.9583 | 2 | 6.9583 | 2
421 | Spanish | 117 | 7 |  | 690 | 15 | 7 | Air Handling Unit | 5520 | 1.2717 | 1 | 1.2717 | 1
422 | Chinese | 965 | 64 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 10.4891 | 3 | 10.4891 | 3
423 | English 1 | 628 | 41 |  | 690 | 15 | 15 | Air Handling Unit | 5520 | 6.8261 | 2 | 6.8261 | 2
432 | Literature | 484 | 32 |  | 760 | 17 | 17 | Air Handling Unit | 6080 | 4.7763 | 2 | 4.7763 | 2
433 | History | 142 | 9 |  | 760 | 17 | 9 | Air Handling Unit | 6080 | 1.4013 | 1 | 1.4013 | 1
436 | Science | 769 | 51 |  | 1058 | 24 | 24 | Air Handling Unit | 8464 | 5.4513 | 2 | 5.4513 | 2
437 | Geometry | 723 | 48 |  | 552 | 12 | 12 | Air Handling Unit | 4416 | 9.8234 | 2 | 9.8234 | 2
501 | Algebra 2 | 677 | 45 |  | 768 | 17 | 17 | Air Handling Unit | 6144 | 6.6113 | 2 | 6.6113 | 2
502 | Forensics / Algebra | 415 | 27 |  | 768 | 17 | 17 | Air Handling Unit | 6144 | 4.0527 | 2 | 4.0527 | 2
503 | Statistics | 483 | 32 |  | 768 | 17 | 17 | Air Handling Unit | 6144 | 4.7168 | 2 | 4.7168 | 2
504 | Algebra | 190 | 12 |  | 768 | 17 | 12 | Air Handling Unit | 6144 | 1.8555 | 1 | 1.8555 | 1
506 | Algebra | 707 | 47 |  | 768 | 17 | 17 | Air Handling Unit | 6144 | 6.9043 | 2 | 6.9043 | 2
507 | Computer Science | 420 | 28 |  | 768 | 17 | 17 | Air Handling Unit | 6144 | 4.1016 | 2 | 4.1016 | 2
521 | Algebra | 190 | 12 |  | 690 | 15 | 12 | Air Handling Unit | 5520 | 2.0652 | 1 | 2.0652 | 1
522 | Math | 2026 | 135 |  | 968 | 22 | 22 | Air Handling Unit | 7744 | 15.6973 | 3 | 15.6973 | 3
524 | Algebra | 1222 | 81 |  | 770 | 17 | 17 | Air Handling Unit | 6160 | 11.9026 | 3 | 11.9026 | 3
529 | Film | 493 | 32 |  | 660 | 15 | 15 | Air Handling Unit | 5280 | 5.6023 | 2 | 5.6023 | 2
201A | Exercise | 323 | 21 |  | 23 | 0 | 0 | Air Handling Unit | 184 | 105.3261 | 5 | 105.3261 | 5
201B | Exercise | 627 | 41 |  | 1771 | 40 | 40 | Air Handling Unit | 14168 | 2.6553 | 1 | 2.6553 | 1
304A | Computer Lab | 571 | 38 |  | 500 | 11 | 11 | Air Handling Unit | 4000 | 8.565 | 2 | 8.565 | 2
304B | Computer Lab | 637 | 42 |  | 446 | 10 | 10 | Air Handling Unit | 3568 | 10.7119 | 3 | 10.7119 | 3
329A | Admin. Office | 605 | 40 |  | 660 | 15 | 15 | Air Handling Unit | 5280 | 6.875 | 2 | 6.875 | 2
329B | Admin. Office | 196 | 13 |  | 660 | 15 | 13 | Air Handling Unit | 5280 | 2.2273 | 1 | 2.2273 | 1
337A | Study Skills / AS | 860 | 57 |  | 337 | 7 | 7 | Air Handling Unit | 2696 | 19.1395 | 3 | 19.1395 | 3
337B | Study Skills / AS | 975 | 65 |  | 552 | 12 | 12 | Air Handling Unit | 4416 | 13.2473 | 3 | 13.2473 | 3
404A | Chemistry Lab | 230 | 15 |  | 720 | 16 | 15 | Air Handling Unit | 5760 | 2.3958 | 1 | 2.3958 | 1
404B | Chemistry Lab | 2087 | 139 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 21.7396 | 3 | 21.7396 | 3
409A | Office | 43 | 2 |  | 280 | 6 | 2 | Air Handling Unit | 2240 | 1.1518 | 1 | 1.1518 | 1
409B | Office | 123 | 8 |  | 280 | 6 | 6 | Air Handling Unit | 2240 | 3.2946 | 1 | 3.2946 | 1
429A | Robotics | 574 | 38 |  | 1320 | 30 | 30 | Air Handling Unit | 10560 | 3.2614 | 1 | 3.2614 | 1
429B | Robotics | 652 | 43 |  | 429 | 9 | 9 | Air Handling Unit | 3432 | 11.3986 | 3 | 11.3986 | 3
434A | Algebra | 541 | 36 |  | 434 | 9 | 9 | Air Handling Unit | 3472 | 9.3491 | 2 | 9.3491 | 2
434B | Algebra | 276 | 18 |  | 1188 | 27 | 18 | Air Handling Unit | 9504 | 1.7424 | 1 | 1.7424 | 1
B14 | Storage | 594 | 39 |  | 374 | 8 | 8 | Air Handling Unit | 2992 | 11.9118 | 3 | 11.9118 | 3
B15 | Storage | 237 | 15 |  | 384 | 8 | 8 | Air Handling Unit | 3072 | 4.6289 | 2 | 4.6289 | 2
B16 | Storage | 37 | 2 |  | 90 | 2 | 2 | Air Handling Unit | 720 | 3.0833 | 1 | 3.0833 | 1
B17 | Storage | 326 | 21 |  | 364 | 8 | 8 | Air Handling Unit | 2912 | 6.717 | 2 | 6.717 | 2
B19 | Storage | 723 | 48 |  | 1013 | 23 | 23 | Air Handling Unit | 8104 | 5.3529 | 2 | 5.3529 | 2
B24-A | Storage | 723 | 48 |  | 1013 | 23 | 23 | Air Handling Unit | 8104 | 5.3529 | 2 | 5.3529 | 2
B24-B | Storage | 461 | 30 |  | 1013 | 23 | 23 | Air Handling Unit | 8104 | 3.4131 | 1 | 3.4131 | 1
- | Auditorium | 16042 | 1069 |  | 12420 | 282 | 282 | Air Handling Unit | 99360 | 9.6872 | 2 | 9.6872 | 2
- | Gyms and Cafeteria | 7343 | 489 |  | 21078 | 479 | 479 | Air Handling Unit | 168624 | 2.6128 | 1 | 2.6128 | 1
- | Home Locker Room | 417 | 27 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 4.3438 | 2 | 4.3438 | 2
- | Locker Room | 417 | 27 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 4.3438 | 2 | 4.3438 | 2
- | Main Library | 1095 | 73 |  | 4608 | 104 | 73 | Air Handling Unit | 36864 | 1.7822 | 1 | 1.7822 | 1
- | Library A | 1256 | 83 |  | 238 | 5 | 5 | Air Handling Unit | 1904 | 39.5798 | 4 | 39.5798 | 4
- | Library B | 1078 | 71 |  | 238 | 5 | 5 | Air Handling Unit | 1904 | 33.9706 | 4 | 33.9706 | 4
- | Library Storage | 917 | 61 |  | 288 | 6 | 6 | Air Handling Unit | 2304 | 23.8802 | 3 | 23.8802 | 3
- | Men's Room | 50 | 3 |  | 252 | 5 | 3 | Air Handling Unit | 2016 | 1.4881 | 1 | 1.4881 | 1
- | Ladies Room | 46 | 3 |  | 252 | 5 | 3 | Air Handling Unit | 2016 | 1.369 | 1 | 1.369 | 1
- | Safe Room | 1158 | 77 |  | 675 | 15 | 15 | Air Handling Unit | 5400 | 12.8667 | 3 | 12.8667 | 3
B18 | Storage | 477 | 31 |  | 723 | 16 | 16 |  | 5784 | 4.9481 | 2 | 4.9481 | 2
B20 | Storage | 461 | 30 |  | 1013 | 23 | 23 |  | 8104 | 3.4131 | 1 | 3.4131 | 1
B21 | Storage | 736 | 49 |  | 966 | 21 | 21 |  | 7728 | 5.7143 | 2 | 5.7143 | 2
B22 | Storage | 723 | 48 |  | 528 | 12 | 12 |  | 4224 | 10.2699 | 3 | 10.2699 | 3
B23 | Storage | 323 | 21 |  | 23 | 0 | 0 |  | 184 | 105.3261 | 5 | 105.3261 | 5
B24 | Storage | 627 | 41 |  | 1771 | 40 | 40 |  | 14168 | 2.6553 | 1 | 2.6553 | 1
B25 | Storage | 843 | 56 |  | 660 | 15 | 15 |  | 5280 | 9.5795 | 2 | 9.5795 | 2
B26 | Storage | 113 | 7 |  | 660 | 15 | 7 |  | 5280 | 1.2841 | 1 | 1.2841 | 1
B27 | Storage | 595 | 39 |  | 484 | 11 | 11 |  | 3872 | 9.22 | 2 | 9.22 | 2
B28 | Storage | 604 | 40 |  | 528 | 12 | 12 |  | 4224 | 8.5795 | 2 | 8.5795 | 2
B29 | Storage | 1510 | 100 |  | 440 | 10 | 10 |  | 3520 | 25.7386 | 4 | 25.7386 | 4
B30 | Storage | 571 | 38 |  | 500 | 11 | 11 |  | 4000 | 8.565 | 2 | 8.565 | 2
B31 | Storage | 637 | 42 |  | 446 | 10 | 10 |  | 3568 | 10.7119 | 3 | 10.7119 | 3
B32 | Storage | 666 | 44 |  | 690 | 15 | 15 |  | 5520 | 7.2391 | 2 | 7.2391 | 2
B33 | Storage | 567 | 37 |  | 690 | 15 | 15 |  | 5520 | 6.163 | 2 | 6.163 | 2
B34 | Storage | 605 | 40 |  | 660 | 15 | 15 |  | 5280 | 6.875 | 2 | 6.875 | 2
B35 | Storage | 196 | 13 |  | 660 | 15 | 13 |  | 5280 | 2.2273 | 1 | 2.2273 | 1
B36 | Storage | 84 | 5 |  | 638 | 14 | 5 |  | 5104 | 0.98746 | 0 | 0.98746 | 0
B37 | Storage | 1066 | 71 |  | 792 | 18 | 18 |  | 6336 | 10.0947 | 3 | 10.0947 | 3
B38 | Storage | 0 | 0 |  | 567 | 12 | 0 |  | 4536 | 0 | 0 | 0 | 0
B39 | Storage | 0 | 0 |  | 1058 | 24 | 0 |  | 8464 | 0 | 0 | 0 | 0
B40 | Storage | 860 | 57 |  | 337 | 7 | 7 |  | 2696 | 19.1395 | 3 | 19.1395 | 3
B41 | Storage | 975 | 65 |  | 552 | 12 | 12 |  | 4416 | 13.2473 | 3 | 13.2473 | 3
B42 | Storage | 322 | 21 |  | 1056 | 24 | 21 |  | 8448 | 2.2869 | 1 | 2.2869 | 1
B43 | Storage | 230 | 15 |  | 720 | 16 | 15 |  | 5760 | 2.3958 | 1 | 2.3958 | 1
B44 | Storage | 2087 | 139 |  | 720 | 16 | 16 |  | 5760 | 21.7396 | 3 | 21.7396 | 3
B45 | Storage | 628 | 41 |  | 690 | 15 | 15 |  | 5520 | 6.8261 | 2 | 6.8261 | 2
B46 | Storage | 574 | 38 |  | 1320 | 30 | 30 |  | 10560 | 3.2614 | 1 | 3.2614 | 1
B47 | Storage | 652 | 43 |  | 429 | 9 | 9 |  | 3432 | 11.3986 | 3 | 11.3986 | 3
B48 | Storage | 484 | 32 |  | 760 | 17 | 17 |  | 6080 | 4.7763 | 2 | 4.7763 | 2
B49 | Storage | 142 | 9 |  | 760 | 17 | 9 |  | 6080 | 1.4013 | 1 | 1.4013 | 1
B50 | Storage | 541 | 36 |  | 434 | 9 | 9 |  | 3472 | 9.3491 | 2 | 9.3491 | 2
B51 | Storage | 276 | 18 |  | 1188 | 27 | 18 |  | 9504 | 1.7424 | 1 | 1.7424 | 1
B52 | Storage | 769 | 51 |  | 1058 | 24 | 24 |  | 8464 | 5.4513 | 2 | 5.4513 | 2
B53 | Storage | 723 | 48 |  | 552 | 12 | 12 |  | 4416 | 9.8234 | 2 | 9.8234 | 2
B54 | Storage | 677 | 45 |  | 768 | 17 | 17 |  | 6144 | 6.6113 | 2 | 6.6113 | 2
B55 | Storage | 415 | 27 |  | 768 | 17 | 17 |  | 6144 | 4.0527 | 2 | 4.0527 | 2
B56 | Storage | 483 | 32 |  | 768 | 17 | 17 |  | 6144 | 4.7168 | 2 | 4.7168 | 2
B57 | Storage | 1222 | 81 |  | 770 | 17 | 17 |  | 6160 | 11.9026 | 3 | 11.9026 | 3
B58 | Storage | 493 | 32 |  | 660 | 15 | 15 |  | 5280 | 5.6023 | 2 | 5.6023 | 2
B59 | Storage | 1158 | 77 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
B60 | Storage | 26166 | 1744 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
B61 | Storage | 594 | 39 |  | 374 | 8 | 8 |  | 2992 | 11.9118 | 3 | 11.9118 | 3
B62 | Storage | 237 | 15 |  | 384 | 8 | 8 |  | 3072 | 4.6289 | 2 | 4.6289 | 2
B63 | Storage | 37 | 2 |  | 90 | 2 | 2 |  | 720 | 3.0833 | 1 | 3.0833 | 1
B64 | Storage | 1170 | 78 |  | 946 | 21 | 21 |  | 7568 | 9.2759 | 2 | 9.2759 | 2
B65 | Storage | 1709 | 113 |  | 968 | 22 | 22 |  | 7744 | 13.2412 | 3 | 13.2412 | 3
B66 | Storage | 609 | 40 |  | 396 | 9 | 9 |  | 3168 | 11.5341 | 3 | 11.5341 | 3
B67 | Storage | 1248 | 83 |  | 1058 | 24 | 24 |  | 8464 | 8.8469 | 2 | 8.8469 | 2
B68 | Storage | 271 | 18 |  | 782 | 17 | 17 |  | 6256 | 2.5991 | 1 | 2.5991 | 1
B69 | Storage | 1440 | 96 |  | 690 | 15 | 15 |  | 5520 | 15.6522 | 3 | 15.6522 | 3
B70 | Storage | 653 | 43 |  | 768 | 17 | 17 |  | 6144 | 6.377 | 2 | 6.377 | 2
B71 | Storage | 713 | 47 |  | 690 | 15 | 15 |  | 5520 | 7.75 | 2 | 7.75 | 2
B72 | Storage | 1069 | 71 |  | 690 | 15 | 15 |  | 5520 | 11.6196 | 3 | 11.6196 | 3
B73 | Storage | 615 | 41 |  | 720 | 16 | 16 |  | 5760 | 6.4062 | 2 | 6.4062 | 2
B74 | Storage | 417 | 27 |  | 720 | 16 | 16 |  | 5760 | 4.3438 | 2 | 4.3438 | 2
B75 | Storage | 618 | 41 |  | 690 | 15 | 15 |  | 5520 | 6.7174 | 2 | 6.7174 | 2
B76 | Storage | 750 | 50 |  | 1104 | 25 | 25 |  | 8832 | 5.0951 | 2 | 5.0951 | 2
B77 | Storage | 257 | 17 |  | 690 | 15 | 15 |  | 5520 | 2.7935 | 1 | 2.7935 | 1
B78 | Storage | 554 | 36 |  | 690 | 15 | 15 |  | 5520 | 6.0217 | 2 | 6.0217 | 2
B79 | Storage | 282 | 18 |  | 690 | 15 | 15 |  | 5520 | 3.0652 | 1 | 3.0652 | 1
B80 | Storage | 615 | 41 |  | 720 | 16 | 16 |  | 5760 | 6.4062 | 2 | 6.4062 | 2
B81 | Storage | 532 | 35 |  | 690 | 15 | 15 |  | 5520 | 5.7826 | 2 | 5.7826 | 2
B82 | Storage | 1582 | 105 |  | 690 | 15 | 15 |  | 5520 | 17.1957 | 3 | 17.1957 | 3
B83 | Storage | 917 | 61 |  | N/A | 0 | 0 |  |  | unk | unk | unk | unk
B84 | Storage | 1256 | 83 |  | N/A | 0 | 0 |  |  | unk | unk | unk | unk
B85 | Storage | 1078 | 71 |  | N/A | 0 | 0 |  |  | unk | unk | unk | unk
B86 | Storage | 587 | 39 |  | 1440 | 32 | 32 |  | 11520 | 3.0573 | 1 | 3.0573 | 1
B87 | Storage | 651 | 43 |  | 720 | 16 | 16 |  | 5760 | 6.7812 | 2 | 6.7812 | 2
B88 | Storage | 668 | 44 |  | 720 | 16 | 16 |  | 5760 | 6.9583 | 2 | 6.9583 | 2
B89 | Storage | 117 | 7 |  | 690 | 15 | 7 |  | 5520 | 1.2717 | 1 | 1.2717 | 1
B90 | Storage | 965 | 64 |  | 690 | 15 | 15 |  | 5520 | 10.4891 | 3 | 10.4891 | 3
B91 | Storage | 417 | 27 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
B92 | Storage | 190 | 12 |  | 768 | 17 | 12 |  | 6144 | 1.8555 | 1 | 1.8555 | 1
B93 | Storage | 707 | 47 |  | 768 | 17 | 17 |  | 6144 | 6.9043 | 2 | 6.9043 | 2
B94 | Storage | 420 | 28 |  | 768 | 17 | 17 |  | 6144 | 4.1016 | 2 | 4.1016 | 2
B95 | Storage | 190 | 12 |  | 690 | 15 | 12 |  | 5520 | 2.0652 | 1 | 2.0652 | 1
B96 | Storage | 2026 | 135 |  | 968 | 22 | 22 |  | 7744 | 15.6973 | 3 | 15.6973 | 3
B97 | Storage | 16042 | 1069 |  | 12420 | 282 | 282 |  | 99360 | 9.6872 | 2 | 9.6872 | 2
B98 | Storage | 7343 | 489 |  | 21078 | 479 | 479 |  | 168624 | 2.6128 | 1 | 2.6128 | 1
B99 | Storage | 1095 | 73 |  | 4608 | 104 | 73 |  | 36864 | 1.7822 | 1 | 1.7822 | 1
B100 | Storage | 43 | 2 |  | 280 | 6 | 2 |  | 2240 | 1.1518 | 1 | 1.1518 | 1
B101 | Storage | 123 | 8 |  | 280 | 6 | 6 |  | 2240 | 3.2946 | 1 | 3.2946 | 1
B102 | Storage | 50 | 3 |  | 252 | 5 | 3 |  | 2016 | 1.4881 | 1 | 1.4881 | 1
B103 | Storage | 46 | 3 |  | 252 | 5 | 3 |  | 2016 | 1.369 | 1 | 1.369 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | Parkway Northwest High School former Hill, JE (Hill-Freedman) | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | Goldner Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
108 | Room | 676 | 45 |  | 676 | 15 | 15 | Univent | 5408 | 7.5 | 2 | 7.5 | 2
109 | Room | 333 | 22 |  | 714 | 16 | 16 | Fan Coil Unit | 5712 | 3.4979 | 1 | 3.4979 | 1
110 | Room | 168 | 11 |  | 1015 | 23 | 11 | Univent | 8120 | 1.2414 | 1 | 1.2414 | 1
130 | Room | 564 | 37 |  | 630 | 14 | 14 | Univent | 5040 | 6.7143 | 2 | 6.7143 | 2
131 | Room | 476 | 31 |  | 580 | 13 | 13 | Univent | 4640 | 6.1552 | 2 | 6.1552 | 2
132 | Room | 528 | 35 |  | 580 | 13 | 13 | Univent | 4640 | 6.8276 | 2 | 6.8276 | 2
133 | Room | 452 | 30 |  | 469 | 10 | 10 | Univent | 3752 | 7.2281 | 2 | 7.2281 | 2
134 | Room | 496 | 33 |  | 1015 | 23 | 23 | Univent | 8120 | 3.665 | 1 | 3.665 | 1
135 | Room | 304 | 20 |  | 812 | 18 | 18 | Univent | 6496 | 2.8079 | 1 | 2.8079 | 1
136 | Room | 424 | 28 |  | 424 | 9 | 9 | Univent | 3392 | 7.5 | 2 | 7.5 | 2
203 | Room | 409 | 27 |  | 600 | 13 | 13 | Univent | 4800 | 5.1125 | 2 | 5.1125 | 2
204 | Room | 363 | 24 |  | 667 | 15 | 15 | Univent | 5336 | 4.0817 | 2 | 4.0817 | 2
205 | Room | 376 | 25 |  | 720 | 16 | 16 | Univent | 5760 | 3.9167 | 1 | 3.9167 | 1
206 | Room | 350 | 23 |  | 810 | 18 | 18 | Univent | 6480 | 3.2407 | 1 | 3.2407 | 1
207 | Room | 371 | 24 |  | 783 | 17 | 17 | Univent | 6264 | 3.5536 | 1 | 3.5536 | 1
210 | Room | 482 | 32 |  | 1116 | 25 | 25 | Fan Coil Unit | 8928 | 3.2392 | 1 | 3.2392 | 1
211 | Room | 329 | 21 |  | 957 | 21 | 21 | Univent | 7656 | 2.5784 | 1 | 2.5784 | 1
221 | Room | 300 | 20 |  | 580 | 13 | 13 | Univent | 4640 | 3.8793 | 1 | 3.8793 | 1
222 | Room | 75 | 5 |  | 580 | 13 | 5 | Univent | 4640 | 0.96983 | 0 | 0.96983 | 0
223 | Room | 523 | 34 |  | 580 | 13 | 13 | Univent | 4640 | 6.7629 | 2 | 6.7629 | 2
224 | Room | 717 | 47 |  | 580 | 13 | 13 | Univent | 4640 | 9.2716 | 2 | 9.2716 | 2
225 | Room | 250 | 16 |  | 580 | 13 | 13 | Univent | 4640 | 3.2328 | 1 | 3.2328 | 1
226 | Room | 163 | 10 |  | 580 | 13 | 10 | Univent | 4640 | 2.1078 | 1 | 2.1078 | 1
- | Auditurium | 912 | 60 |  | 1050 | 23 | 23 | Univent | 8400 | 6.5143 | 2 | 6.5143 | 2
- | Gym | 969 | 64 |  | 2460 | 55 | 55 | Univent | 19680 | 2.9543 | 1 | 2.9543 | 1
- | Main Office | 0 | 0 |  | 399 | 9 | 0 |  | 3192 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | John M. Patterson Elementary School | House fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers Retest | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Classroom |  | 0 | Yes | 648 | 14 | 14 | House Fan | 5184 | unk | unk | 20 | 3
2 | Classroom |  | 0 | Yes | 648 | 14 | 14 | House Fan | 5184 | unk | unk | 20 | 3
3 | Classroom |  | 0 | Yes | 648 | 14 | 14 | House Fan | 5184 | unk | unk | 20 | 3
100 | Office | 0 | 0 |  | 143 | 3 | 0 | House Fan | 1144 | 0 | 0 | 0 | 0
101 | Classroom | 659 | 43 |  | 704 | 16 | 16 | House Fan | 5632 | 7.0206 | 2 | 7.0206 | 2
102 | Classroom | 568 | 37 |  | 616 | 14 | 14 | House Fan | 4928 | 6.9156 | 2 | 6.9156 | 2
103 | Classroom | 403 | 26 |  | 616 | 14 | 14 | House Fan | 4928 | 4.9067 | 2 | 4.9067 | 2
104 | Classroom | 663 | 44 |  | 616 | 14 | 14 | House Fan | 4928 | 8.0722 | 2 | 8.0722 | 2
105 | Classroom | 518 | 34 |  | 616 | 14 | 14 | House Fan | 4928 | 6.3068 | 2 | 6.3068 | 2
106 | Classroom | 639 | 42 |  | 616 | 14 | 14 | House Fan | 4928 | 7.78 | 2 | 7.78 | 2
107 | Classroom | 698 | 46 |  | 616 | 14 | 14 | House Fan | 4928 | 8.4984 | 2 | 8.4984 | 2
108 | Classroom | 656 | 43 |  | 704 | 16 | 16 | House Fan | 5632 | 6.9886 | 2 | 6.9886 | 2
109 | Classroom | 658 | 43 |  | 704 | 16 | 16 | House Fan | 5632 | 7.0099 | 2 | 7.0099 | 2
110 | Classroom | 722 | 48 |  | 704 | 16 | 16 | House Fan | 5632 | 7.6918 | 2 | 7.6918 | 2
200 | Classroom | 0 | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0 | 0 | 20 | 3
200A | Counselor | 0 | 0 |  | 240 | 5 | 0 | House Fan | 1920 | 0 | 0 | 0 | 0
201 | Classroom | 373 | 24 |  | 704 | 16 | 16 | House Fan | 5632 | 3.9737 | 1 | 3.9737 | 1
202 | Classroom | 578 | 38 |  | 703 | 15 | 15 | House Fan | 5624 | 6.1664 | 2 | 6.1664 | 2
203 | Classroom | 504 | 33 |  | 616 | 14 | 14 | House Fan | 4928 | 6.1364 | 2 | 6.1364 | 2
204 | Classroom | 474 | 31 |  | 616 | 14 | 14 | House Fan | 4928 | 5.7711 | 2 | 5.7711 | 2
205 | Classroom | 421 | 28 |  | 616 | 14 | 14 | House Fan | 4928 | 5.1258 | 2 | 5.1258 | 2
206 | Classroom | 541 | 36 |  | 616 | 14 | 14 | House Fan | 4928 | 6.5869 | 2 | 6.5869 | 2
207 | Classroom | 637 | 42 |  | 616 | 14 | 14 | House Fan | 4928 | 7.7557 | 2 | 7.7557 | 2
208 | Classroom | 209 | 13 |  | 704 | 16 | 13 | House Fan | 5632 | 2.2266 | 1 | 2.2266 | 1
209 | Classroom | 585 | 39 |  | 704 | 16 | 16 | House Fan | 5632 | 6.2322 | 2 | 6.2322 | 2
210 | Classroom | 583 | 38 |  | 410 | 9 | 9 | House Fan | 3280 | 10.6646 | 3 | 10.6646 | 3
300 | Classroom | 394 | 26 |  | 704 | 16 | 16 | House Fan | 5632 | 4.1974 | 2 | 4.1974 | 2
301 | Classroom | 530 | 35 |  | 704 | 16 | 16 | House Fan | 5632 | 5.6463 | 2 | 5.6463 | 2
302 | Classroom | 511 | 34 |  | 704 | 16 | 16 | House Fan | 5632 | 5.4439 | 2 | 5.4439 | 2
303 | Classroom | 576 | 38 |  | 704 | 16 | 16 | House Fan | 5632 | 6.1364 | 2 | 6.1364 | 2
304 | Classroom | 359 | 23 |  | 616 | 14 | 14 | House Fan | 4928 | 4.3709 | 2 | 4.3709 | 2
305 | Classroom | 561 | 37 |  | 616 | 14 | 14 | House Fan | 4928 | 6.8304 | 2 | 6.8304 | 2
306 | Classroom | 604 | 40 |  | 616 | 14 | 14 | House Fan | 4928 | 7.3539 | 2 | 7.3539 | 2
307 | Classroom | 103 | 6 |  | 616 | 14 | 6 | House Fan | 4928 | 1.2541 | 1 | 1.2541 | 1
308 | Classroom | 418 | 27 |  | 704 | 16 | 16 | House Fan | 5632 | 4.4531 | 2 | 4.4531 | 2
309 | Classroom | 101 | 6 |  | 704 | 16 | 6 | House Fan | 5632 | 1.076 | 1 | 1.076 | 1
310 | Classroom | 429 | 28 |  | 704 | 16 | 16 | House Fan | 5632 | 4.5703 | 2 | 4.5703 | 2
- | Auditorium | 5125 | 341 |  | 2880 | 65 | 65 | House Fan | 23040 | 13.3464 | 3 | 13.3464 | 3
- | Admin Office | 0 | 0 | Yes | 88 | 2 | 2 | House Fan | 704 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | unk | unk | 20 | 3
- | Book Room Storage | 0 | 0 |  | 230 | 5 | 0 | House Fan | 1840 | 0 | 0 | 0 | 0
- | Boiler Rm. | 22650 | 1510 |  | 1440 | 32 | 32 | House Fan | 11520 | 117.9688 | 5 | 117.9688 | 5
- | Small Cafeteria | 689 | 45 |  | 1232 | 28 | 28 | House Fan | 9856 | 4.1944 | 2 | 4.1944 | 2
- | Kitchen | 212 | 14 |  | 200 | 4 | 4 | House Fan | 1600 | 7.95 | 2 | 7.95 | 2
- | Gym/Cafeteria | 0 | 0 | Yes | 3762 | 85 | 85 | House Fan | 30096 | 0 | 0 | 20 | 3
- | Storage | 574 | 38 |  |  | 0 | 0 | House Fan |  | unk | unk | unk | unk
- | Music | 375 | 25 |  | 560 | 12 | 12 | House Fan | 4480 | 5.0223 | 2 | 5.0223 | 2
- | Nurse's Room | 0 | 0 | Yes | 336 | 7 | 7 | House Fan | 2688 | 0 | 0 | 20 | 3
- | Teacher's Lounge | 0 | 0 | Yes | 410 | 9 | 9 | House Fan | 3280 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-20 | [8 empty] | unk | unk | unk | unk
School: | Penn Alexander Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Part 2 | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B24 | Classroom | 37 | 2 |  | 130 | 2 | 2 | Air Handling Unit | 1040 | 2.1346 | 1 | 2.1346 | 1
B26 | Classroom | 120 | 8 |  | 216 | 4 | 4 | Air Handling Unit | 1728 | 4.1667 | 2 | 4.1667 | 2
B28 | Classroom | 483 | 32 |  | 722 | 16 | 16 | Air Handling Unit | 5776 | 5.0173 | 2 | 5.0173 | 2
106 | Classroom | 1065 | 71 |  | 806 | 18 | 18 | Air Handling Unit | 6448 | 9.91 | 2 | 9.91 | 2
108 | Classroom | 310 | 20 |  | 842 | 19 | 19 | Univent | 6736 | 2.7613 | 1 | 2.7613 | 1
109 | Classroom | 311 | 20 |  | 759 | 17 | 17 | Univent | 6072 | 3.0731 | 1 | 3.0731 | 1
110 | Classroom | 305 | 20 |  | 693 | 15 | 15 | Univent | 5544 | 3.3009 | 1 | 3.3009 | 1
113 | Classroom | 220 | 14 |  | 222 | 5 | 5 | Air Handling Unit | 1776 | 7.4324 | 2 | 7.4324 | 2
117 | Classroom | 285 | 19 |  | 741 | 16 | 16 | Univent | 5928 | 2.8846 | 1 | 2.8846 | 1
118 | Classroom | 329 | 21 |  | 759 | 17 | 17 | Univent | 6072 | 3.251 | 1 | 3.251 | 1
119 | Classroom | 315 | 21 |  | 683 | 15 | 15 | Univent | 5464 | 3.459 | 1 | 3.459 | 1
123 | Classroom | 0 | 0 |  | 150 | 3 | 0 | Air Handling Unit | 1200 | 0 | 0 | 0 | 0
125 | Classroom | 73 | 4 |  | 209 | 4 | 4 | Air Handling Unit | 1672 | 2.6196 | 1 | 2.6196 | 1
126 | Classroom | 13 | 0 |  | 99 | 2 | 0 | Air Handling Unit | 792 | 0.98485 | 0 | 0.98485 | 0
127 | Classroom | 14 | 0 |  | 99 | 2 | 0 | Air Handling Unit | 792 | 1.0606 | 1 | 1.0606 | 1
128 | Classroom | 10 | 0 | Yes | 99 | 2 | 2 | Air Handling Unit | 792 | 0.75758 | 0 | 20.7576 | 3
129 | Classroom | 84 | 5 | Yes | 291 | 6 | 6 | Air Handling Unit | 2328 | 2.1649 | 1 | 22.1649 | 3
131 | Classroom | 302 | 20 |  | 694 | 15 | 15 | Univent | 5552 | 3.2637 | 1 | 3.2637 | 1
133 | Classroom | 0 | 0 | Yes | 644 | 14 | 14 | Univent | 5152 | 0 | 0 | 20 | 3
134 | Classroom | 330 | 22 |  | 683 | 15 | 15 | Univent | 5464 | 3.6237 | 1 | 3.6237 | 1
201 | Classroom | 491 | 32 |  | 875 | 19 | 19 | Air Handling Unit | 7000 | 4.2086 | 2 | 4.2086 | 2
202 | Classroom | 74 | 4 |  | 324 | 7 | 4 | Air Handling Unit | 2592 | 1.713 | 1 | 1.713 | 1
208 | Classroom | 0 | 0 | Yes | 842 | 19 | 19 | Univent | 6736 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 | Yes | 759 | 17 | 17 | Univent | 6072 | 0 | 0 | 20 | 3
210 | Classroom | 0 | 0 | Yes | 693 | 15 | 15 | Univent | 5544 | 0 | 0 | 20 | 3
213 | Classroom | 75 | 5 |  | 222 | 5 | 5 | Air Handling Unit | 1776 | 2.5338 | 1 | 2.5338 | 1
217 | Classroom | 0 | 0 | Yes | 741 | 16 | 16 | Univent | 5928 | 0 | 0 | 20 | 3
218 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | Univent | 5824 | 0 | 0 | 20 | 3
219 | Classroom | 0 | 0 | Yes | 683 | 15 | 15 | Univent | 5464 | 0 | 0 | 20 | 3
220 | Classroom | 241 | 16 |  | 224 | 5 | 5 | Air Handling Unit | 1792 | 8.0692 | 2 | 8.0692 | 2
221 | Classroom | 0 | 0 | Yes | 96 | 2 | 2 | Air Handling Unit | 768 | 0 | 0 | 20 | 3
222 | Classroom | 0 | 0 |  | 169 | 3 | 0 | Air Handling Unit | 1352 | 0 | 0 | 0 | 0
225 | Classroom | 0 | 0 | Yes | 209 | 4 | 4 | Air Handling Unit | 1672 | 0 | 0 | 20 | 3
227 | Classroom | 0 | 0 |  | 99 | 2 | 0 | Air Handling Unit | 792 | 0 | 0 | 0 | 0
228 | Classroom | 0 | 0 |  | 154 | 3 | 0 | Air Handling Unit | 1232 | 0 | 0 | 0 | 0
229 | Classroom | 0 | 0 |  | 108 | 2 | 0 | Air Handling Unit | 864 | 0 | 0 | 0 | 0
230 | Classroom | 318 | 21 |  | 736 | 16 | 16 | Univent | 5888 | 3.2405 | 1 | 3.2405 | 1
231 | Classroom | 301 | 20 |  | 840 | 19 | 19 | Univent | 6720 | 2.6875 | 1 | 2.6875 | 1
233 | Classroom | 266 | 17 |  | 739 | 16 | 16 | Univent | 5912 | 2.6996 | 1 | 2.6996 | 1
234 | Classroom | 328 | 21 |  | 671 | 15 | 15 | Univent | 5368 | 3.6662 | 1 | 3.6662 | 1
301 | Classroom | 1176 | 78 |  | 1005 | 22 | 22 | Air Handling Unit | 8040 | 8.7761 | 2 | 8.7761 | 2
302 | Classroom | 0 | 0 |  | 324 | 7 | 0 | Univent | 2592 | 0 | 0 | 0 | 0
308 | Classroom | 0 | 0 | Yes | 842 | 19 | 19 | Univent | 6736 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | Univent | 5704 | 0 | 0 | 20 | 3
310 | Classroom | 0 | 0 | Yes | 693 | 15 | 15 | Univent | 5544 | 0 | 0 | 20 | 3
317 | Classroom | 0 | 0 | Yes | 741 | 16 | 16 | Univent | 5928 | 0 | 0 | 20 | 3
318 | Classroom | 0 | 0 | Yes | 759 | 17 | 17 | Univent | 6072 | 0 | 0 | 20 | 3
319 | Classroom | 0 | 0 | Yes | 683 | 15 | 15 | Univent | 5464 | 0 | 0 | 20 | 3
320 | Classroom | 0 | 0 |  | 320 | 7 | 0 | Air Handling Unit | 2560 | 0 | 0 | 0 | 0
- | Cafeteria | 7801 | 520 |  | 3766 | 85 | 85 | Air Handling Unit | 30128 | 15.5357 | 3 | 15.5357 | 3
- | GYM | 1362 | 90 |  | 4271 | 97 | 90 | Air Handling Unit | 34168 | 2.3917 | 1 | 2.3917 | 1
- | Library | 550 | 36 |  | 2658 | 60 | 36 | Air Handling Unit | 21264 | 1.5519 | 1 | 1.5519 | 1
- | Main Office | 205 | 13 |  | 1063 | 24 | 13 | Air Handling Unit | 8504 | 1.4464 | 1 | 1.4464 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-28 | [8 empty] | unk | unk | unk | unk
School: | Penn Treaty High School | [8 empty] | unk | unk | unk | unk
Vendor: | Meehan | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | classroom |  | 0 | Yes | 624 | 14 | 14 | House Fan | 4992 | unk | unk | 20 | 3
102 | Administration |  | 0 | Yes | 336 | 7 | 7 | House Fan | 2688 | unk | unk | 20 | 3
102A | classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | unk | unk | 20 | 3
104 | classroom |  | 0 | Yes | 1539 | 34 | 34 | House Fan | 12312 | unk | unk | 20 | 3
105 | classroom |  | 0 | Yes | 594 | 13 | 13 | House Fan | 4752 | unk | unk | 20 | 3
106 | classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan | 6912 | unk | unk | 20 | 3
107 | classroom |  | 0 | Yes | 920 | 20 | 20 | House Fan | 7360 | unk | unk | 20 | 3
108 | Administration |  | 0 | Yes | 780 | 17 | 17 | House Fan | 6240 | unk | unk | 20 | 3
109 | classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan | 6912 | unk | unk | 20 | 3
110 | classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | unk | unk | 20 | 3
110A | classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | unk | unk | 20 | 3
111 | classroom |  | 0 |  | 650 | 14 | 0 | House Fan | 5200 | unk | unk | unk | unk
115 | Auditorium |  | 0 |  | 3594 | 81 | 0 | House Fan | 28752 | unk | unk | unk | unk
H11A | Main office |  | 0 |  | 560 | 12 | 0 | House Fan | 4480 | unk | unk | unk | unk
H11b | Main office |  | 0 |  | 576 | 13 | 0 | House Fan | 4608 | unk | unk | unk | unk
H12 | Main office |  | 0 |  | 1150 | 26 | 0 | House Fan | 9200 | unk | unk | unk | unk
H13 | Main office |  | 0 |  | 792 | 18 | 0 | House Fan | 6336 | unk | unk | unk | unk
H13a | Main office |  | 0 |  | 312 | 7 | 0 | House Fan | 2496 | unk | unk | unk | unk
H13b | Main office |  | 0 |  | 814 | 18 | 0 | House Fan | 6512 | unk | unk | unk | unk
H13c | Main office |  | 0 |  | 275 | 6 | 0 | House Fan | 2200 | unk | unk | unk | unk
H13d | Main office |  | 0 |  | 1150 | 26 | 0 | House Fan | 9200 | unk | unk | unk | unk
201 | classroom |  | 0 |  | 650 | 14 | 0 | House Fan | 5200 | unk | unk | unk | unk
202 | classroom |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
203 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
203A | classroom |  | 0 |  | 253 | 5 | 0 | House Fan | 2024 | unk | unk | unk | unk
204 | classroom |  | 0 |  | 130 | 2 | 0 | House Fan | 1040 | unk | unk | unk | unk
204A | classroom |  | 0 |  | 552 | 12 | 0 | House Fan | 4416 | unk | unk | unk | unk
205 | Nurse |  | 0 | Yes | 325 | 7 | 7 | House Fan | 2600 | unk | unk | 20 | 3
207 | Main office |  | 0 | Yes | 667 | 15 | 15 | House Fan | 5336 | unk | unk | 20 | 3
207A | Speech |  | 0 | Yes | 70 | 1 | 1 | House Fan | 560 | unk | unk | 20 | 3
207B | Office |  | 0 |  | 120 | 2 | 0 | House Fan | 960 | unk | unk | unk | unk
207D | Principal Office |  | 0 | Yes | 300 | 6 | 6 | House Fan | 2400 | unk | unk | 20 | 3
207G | Conference Room |  | 0 | Yes | 144 | 3 | 3 | House Fan | 1152 | unk | unk | 20 | 3
208 | classroom |  | 0 |  | 1056 | 24 | 0 | House Fan | 8448 | unk | unk | unk | unk
209 | classroom |  | 0 |  | 1032 | 23 | 0 | House Fan | 8256 | unk | unk | unk | unk
210 | IMC |  | 0 | Yes | 2352 | 53 | 53 | House Fan | 18816 | unk | unk | 20 | 3
213 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
214 | classroom |  | 0 |  | 624 | 14 | 0 | House Fan | 4992 | unk | unk | unk | unk
217 | Auditorium |  | 0 |  | 2304 | 52 | 0 | House Fan | 18432 | unk | unk | unk | unk
301 | classroom |  | 0 |  | 650 | 14 | 0 | House Fan | 5200 | unk | unk | unk | unk
301A | Administration |  | 0 |  | 375 | 8 | 0 | House Fan | 3000 | unk | unk | unk | unk
303 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
303A | Admin |  | 0 |  | 275 | 6 | 0 | House Fan | 2200 | unk | unk | unk | unk
304 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
305 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
305A | classroom |  | 0 |  | 912 | 20 | 0 | House Fan | 7296 | unk | unk | unk | unk
307 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
308 | classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | unk | unk | unk | unk
309 | classroom |  | 0 |  | 744 | 16 | 0 | House Fan | 5952 | unk | unk | unk | unk
310 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
311 | classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | unk | unk | unk | unk
312 | classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | unk | unk | unk | unk
313 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
314 | classroom |  | 0 |  | 624 | 14 | 0 | House Fan | 4992 | unk | unk | unk | unk
315 | Admin |  | 0 |  | 238 | 5 | 0 | House Fan | 1904 | unk | unk | unk | unk
316 | classroom |  | 0 |  | 696 | 15 | 0 | House Fan | 5568 | unk | unk | unk | unk
317 | classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | unk | unk | unk | unk
401 | classroom |  | 0 |  | 624 | 14 | 0 | House Fan | 4992 | unk | unk | unk | unk
402A | Admin |  | 0 |  | 828 | 18 | 0 | House Fan | 6624 | unk | unk | unk | unk
402 | classroom |  | 0 |  | 322 | 7 | 0 | House Fan | 2576 | unk | unk | unk | unk
403 | classroom |  | 0 |  | 1032 | 23 | 0 | House Fan | 8256 | unk | unk | unk | unk
404 | classroom |  | 0 |  | 984 | 22 | 0 | House Fan | 7872 | unk | unk | unk | unk
405 | classroom |  | 0 |  | 984 | 22 | 0 | House Fan | 7872 | unk | unk | unk | unk
406 | classroom |  | 0 |  | 984 | 22 | 0 | House Fan | 7872 | unk | unk | unk | unk
407 | classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | unk | unk | unk | unk
408 | classroom |  | 0 |  | 1008 | 22 | 0 | House Fan | 8064 | unk | unk | unk | unk
409 | classroom |  | 0 |  | 1008 | 22 | 0 | House Fan | 8064 | unk | unk | unk | unk
410 | classroom |  | 0 |  | 1008 | 22 | 0 | House Fan | 8064 | unk | unk | unk | unk
412 | Admin |  | 0 |  | 506 | 11 | 0 | House Fan | 4048 | unk | unk | unk | unk
412A | classroom |  | 0 |  | 768 | 17 | 0 | House Fan | 6144 | unk | unk | unk | unk
412b | classroom |  | 0 |  | 84 | 1 | 0 | House Fan | 672 | unk | unk | unk | unk
412c | Admin |  | 0 |  | 484 | 11 | 0 | House Fan | 3872 | unk | unk | unk | unk
413 | classroom |  | 0 |  | 720 | 16 | 0 | House Fan | 5760 | unk | unk | unk | unk
414 | classroom |  | 0 |  | 650 | 14 | 0 | House Fan | 5200 | unk | unk | unk | unk
415 | Cafe |  | 0 |  | 2200 | 50 | 0 | House Fan | 17600 | unk | unk | unk | unk
417 | Kitchen |  | 0 | Yes | 455 | 10 | 10 | House Fan | 3640 | unk | unk | 20 | 3
417A | kitchen |  | 0 |  | 700 | 15 | 0 | House Fan | 5600 | unk | unk | unk | unk
419 | Cafe |  | 0 |  | 2150 | 48 | 0 | House Fan | 17200 | unk | unk | unk | unk
- | boys gym |  | 0 |  | 4725 | 107 | 0 | House Fan | 37800 | unk | unk | unk | unk
- | girls gym |  | 0 |  | 4725 | 107 | 0 | House Fan | 37800 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-24 | [8 empty] | unk | unk | unk | unk
School: | Joseph Pennell Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | - | 0 | 0 | Yes | 1152 | 26 | 26 | Univent | 9216 | 0 | 0 | 20 | 3
2 | - | 0 | 0 | Yes | 1152 | 26 | 26 | Univent | 9216 | 0 | 0 | 20 | 3
101 | Classroom | 0 | 0 |  | 288 | 6 | 0 | Air Handling Unit | 2304 | 0 | 0 | 0 | 0
102 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | Air Handling Unit | 5760 | 0 | 0 | 20 | 3
103 | Classroom | 0 | 0 | Yes | 875 | 19 | 19 | Air Handling Unit | 7000 | 0 | 0 | 20 | 3
104 | Classroom | 0 | 0 | Yes | 175 | 3 | 3 | Air Handling Unit | 1400 | 0 | 0 | 20 | 3
104A | Classroom | 0 | 0 |  | 375 | 8 | 0 | Air Handling Unit | 3000 | 0 | 0 | 0 | 0
104B | Classroom | 0 | 0 |  | 175 | 3 | 0 | Air Handling Unit | 1400 | 0 | 0 | 0 | 0
104C | Classroom | 0 | 0 |  | 125 | 2 | 0 | Air Handling Unit | 1000 | 0 | 0 | 0 | 0
105 | Classroom | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit | 7200 | 0 | 0 | 0 | 0
106 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Air Handling Unit | 6528 | 0 | 0 | 20 | 3
107 | Classroom | 0 | 0 | Yes | 1025 | 23 | 23 | Air Handling Unit | 8200 | 0 | 0 | 20 | 3
110 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | Air Handling Unit | 6960 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Air Handling Unit | 6528 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Air Handling Unit | 6528 | 0 | 0 | 20 | 3
203 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0 | 0 | 0
204 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0 | 0 | 0
205 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0 | 0 | 0
206 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Air Handling Unit | 6528 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 984 | 22 | 22 | Air Handling Unit | 7872 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit | 6960 | 0 | 0 | 0 | 0
210 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit | 6960 | 0 | 0 | 0 | 0
211 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit | 6960 | 0 | 0 | 0 | 0
301 | Classroom | 0 | 0 |  | 816 | 18 | 0 | Air Handling Unit | 6528 | 0 | 0 | 0 | 0
302 | Classroom | 0 | 0 |  | 816 | 18 | 0 | Air Handling Unit | 6528 | 0 | 0 | 0 | 0
303 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0 | 0 | 0
304 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0 | 0 | 0
305 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Air Handling Unit | 7000 | 0 | 0 | 0 | 0
306 | Classroom | 0 | 0 | Yes | 875 | 19 | 19 | Air Handling Unit | 7000 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 |  | 816 | 18 | 0 | Air Handling Unit | 6528 | 0 | 0 | 0 | 0
308 | Classroom | 0 | 0 | Yes | 910 | 20 | 20 | Air Handling Unit | 7280 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit | 6960 | 0 | 0 | 0 | 0
310 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit | 6960 | 0 | 0 | 0 | 0
311 | Classroom | 0 | 0 |  | 870 | 19 | 0 | Air Handling Unit | 6960 | 0 | 0 | 0 | 0
- | Basement Boys Room | 0 | 0 |  | 650 | 14 | 0 | Air Handling Unit | 5200 | 0 | 0 | 0 | 0
- | Basement Corridor | 0 | 0 |  | 352 | 8 | 0 | Air Handling Unit | 2816 | 0 | 0 | 0 | 0
- | Gym | 0 | 0 | Yes | 5096 | 115 | 115 | Air Handling Unit | 40768 | 0 | 0 | 20 | 3
- | Library | 0 | 0 |  | 1593 | 36 | 0 | Air Handling Unit | 12744 | 0 | 0 | 0 | 0
- | Nurse | 0 | 0 | Yes | 384 | 8 | 8 | Air Handling Unit | 3072 | 0 | 0 | 20 | 3
- | Counselor Office |  | 0 |  | 384 | 8 | 0 |  | 3072 | unk | unk | unk | unk
- | Office |  | 0 | Yes | 456 | 10 | 10 |  | 3648 | unk | unk | 20 | 3
- | Principal's Office |  | 0 | Yes | 234 | 5 | 5 |  | 1872 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | Samuel Pennypacker Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B2 | Classroom | 0 | 0 | Yes | 928 | 21 | 21 | House Fan | 7424 | 0 | 0 | 20 | 3
B3 | Classroom | 923 | 61 |  | 1160 | 26 | 26 | House Fan | 9280 | 5.9677 | 2 | 5.9677 | 2
B4 | Classroom | 0 | 0 | Yes | 1260 | 28 | 28 | House Fan | 10080 | 0 | 0 | 20 | 3
B8 | Classroom | 488 | 32 |  | 576 | 13 | 13 | House Fan | 4608 | 6.3542 | 2 | 6.3542 | 2
B9 | Classroom | 439 | 29 |  | 460 | 10 | 10 | House Fan | 3680 | 7.1576 | 2 | 7.1576 | 2
B10 | Classroom | 425 | 28 |  | 576 | 13 | 13 | House Fan | 4608 | 5.5339 | 2 | 5.5339 | 2
101 | Classroom | 545 | 36 |  | 1131 | 25 | 25 | House Fan | 9048 | 3.6141 | 1 | 3.6141 | 1
102 | Classroom | 440 | 29 |  | 841 | 19 | 19 | House Fan | 6728 | 3.9239 | 1 | 3.9239 | 1
103 | Classroom | 545 | 36 |  | 870 | 19 | 19 | House Fan | 6960 | 4.6983 | 2 | 4.6983 | 2
104 | Classroom | 611 | 40 |  | 870 | 19 | 19 | House Fan | 6960 | 5.2672 | 2 | 5.2672 | 2
105 | Classroom | 340 | 22 |  | 841 | 19 | 19 | House Fan | 6728 | 3.0321 | 1 | 3.0321 | 1
106 | Classroom | 395 | 26 |  | 841 | 19 | 19 | House Fan | 6728 | 3.5226 | 1 | 3.5226 | 1
107 | Classroom | 503 | 33 |  | 841 | 19 | 19 | House Fan | 6728 | 4.4857 | 2 | 4.4857 | 2
108 | Classroom | 650 | 43 |  | 899 | 20 | 20 | House Fan | 7192 | 5.4227 | 2 | 5.4227 | 2
109 | Classroom | 437 | 29 |  | 841 | 19 | 19 | House Fan | 6728 | 3.8971 | 1 | 3.8971 | 1
110 | Classroom | 459 | 30 |  | 899 | 20 | 20 | House Fan | 7192 | 3.8293 | 1 | 3.8293 | 1
201 | Classroom | 351 | 23 |  | 899 | 20 | 20 | House Fan | 7192 | 2.9283 | 1 | 2.9283 | 1
202 | Classroom | 424 | 28 |  | 841 | 19 | 19 | House Fan | 6728 | 3.7812 | 1 | 3.7812 | 1
203 | Classroom | 390 | 26 |  | 870 | 19 | 19 | House Fan | 6960 | 3.3621 | 1 | 3.3621 | 1
204 | Classroom | 338 | 22 |  | 841 | 19 | 19 | House Fan | 6728 | 3.0143 | 1 | 3.0143 | 1
205 | Classroom | 649 | 43 |  | 841 | 19 | 19 | House Fan | 6728 | 5.7878 | 2 | 5.7878 | 2
208 | Classroom | 586 | 39 |  | 899 | 20 | 20 | House Fan | 7192 | 4.8888 | 2 | 4.8888 | 2
209 | Classroom | 508 | 33 |  | 841 | 19 | 19 | House Fan | 6728 | 4.5303 | 2 | 4.5303 | 2
210 | Classroom | 356 | 23 |  | 899 | 20 | 20 | House Fan | 7192 | 2.97 | 1 | 2.97 | 1
212 | Storage | 0 | 0 |  | 360 | 8 | 0 | House Fan | 2880 | 0 | 0 | 0 | 0
301 | Classroom | 382 | 25 |  | 899 | 20 | 20 | House Fan | 7192 | 3.1869 | 1 | 3.1869 | 1
302 | Classroom | 653 | 43 |  | 841 | 19 | 19 | House Fan | 6728 | 5.8234 | 2 | 5.8234 | 2
303 | Classroom | 355 | 23 |  | 870 | 19 | 19 | House Fan | 6960 | 3.0603 | 1 | 3.0603 | 1
304 | Classroom | 407 | 27 |  | 841 | 19 | 19 | House Fan | 6728 | 3.6296 | 1 | 3.6296 | 1
305 | Classroom | 583 | 38 |  | 841 | 19 | 19 | House Fan | 6728 | 5.1992 | 2 | 5.1992 | 2
306 | Classroom | 554 | 36 |  | 870 | 19 | 19 | House Fan | 6960 | 4.7759 | 2 | 4.7759 | 2
307 | Classroom | 513 | 34 |  | 841 | 19 | 19 | House Fan | 6728 | 4.5749 | 2 | 4.5749 | 2
308 | Classroom | 515 | 34 |  | 899 | 20 | 20 | House Fan | 7192 | 4.2964 | 2 | 4.2964 | 2
309 | Classroom | 676 | 45 |  | 841 | 19 | 19 | House Fan | 6728 | 6.0285 | 2 | 6.0285 | 2
310 | Classroom | 422 | 28 |  | 899 | 20 | 20 | House Fan | 7192 | 3.5206 | 1 | 3.5206 | 1
311 | Classroom | 550 | 36 |  | 720 | 16 | 16 | House Fan | 5760 | 5.7292 | 2 | 5.7292 | 2
312 | Classroom | 0 | 0 | Yes | 138 | 3 | 3 | House Fan | 1104 | 0 | 0 | 20 | 3
- | Auditorium | 1967 | 131 |  | 4272 | 97 | 97 | House Fan | 34176 | 3.4533 | 1 | 3.4533 | 1
- | Counselor's Office | 0 | 0 | Yes | 386 | 8 | 8 | House Fan | 3088 | 0 | 0 | 20 | 3
- | Gym/Café | 0 | 0 | Yes | 3608 | 82 | 82 | House Fan | 28864 | 0 | 0 | 20 | 3
- | Nurse | 0 | 0 | Yes | 361 | 8 | 8 | House Fan | 2888 | 0 | 0 | 20 | 3
- | Library | 928 | 61 |  | 1620 | 36 | 36 | House Fan | 12960 | 4.2963 | 2 | 4.2963 | 2
- | Main Office | 0 | 0 | Yes | 342 | 7 | 7 | House Fan | 2736 | 0 | 0 | 20 | 3
- | Principals Office | 0 | 0 | Yes | 346 | 7 | 7 | House Fan | 2768 | 0 | 0 | 20 | 3
- | Teacher's Lounge | 0 | 0 |  | 105 | 2 | 0 | House Fan | 840 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Penrose Elementary School- Main Building | [8 empty] | unk | unk | unk | unk
| Main Exhaust Report | [8 empty] | unk | unk | unk | unk
School: | Penrose Little School House | [8 empty] | unk | unk | unk | unk
| Penrose LSH Exhaust Report | LSH Part 2 and Exhaust | LSH Part 3 and Exhaust | [6 empty] | unk | unk | unk | unk
School: | TB Read – former Motivation High School Building | [8 empty] | unk | unk | unk | unk
| TB Read Exhaust Report | TB Read Exhaust Retest | [7 empty] | unk | unk | unk | unk
Vendor: | Chadwick | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Penrose Main Building | [9 empty] | unk | unk | unk | unk
101 | Classroom | 373 | 24 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.1646 | 1 | 3.1646 | 1
102 | Classroom | 387 | 25 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.2834 | 1 | 3.2834 | 1
103 | Classroom | 359 | 23 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.0458 | 1 | 3.0458 | 1
104 | Classroom | 505 | 33 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 4.2845 | 2 | 4.2845 | 2
105 | Classroom | 469 | 31 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.9791 | 1 | 3.9791 | 1
106 | office | 119 | 7 |  | 315 | 7 | 7 | Rooftop Unit | 2520 | 2.8333 | 1 | 2.8333 | 1
106a | principal | 26 | 1 |  | 72 | 1 | 1 | Rooftop Unit | 576 | 2.7083 | 1 | 2.7083 | 1
106b | council | 36 | 2 |  | 176 | 4 | 2 | Rooftop Unit | 1408 | 1.5341 | 1 | 1.5341 | 1
107 | Classroom | 99 | 6 |  | 884 | 20 | 6 | Rooftop Unit | 7072 | 0.83993 | 0 | 0.83993 | 0
111 | Classroom | 233 | 15 |  | 884 | 20 | 15 | Rooftop Unit | 7072 | 1.9768 | 1 | 1.9768 | 1
113 | Classroom | 256 | 17 |  | 884 | 20 | 17 | Rooftop Unit | 7072 | 2.1719 | 1 | 2.1719 | 1
115 | Classroom | 287 | 19 |  | 884 | 20 | 19 | Rooftop Unit | 7072 | 2.435 | 1 | 2.435 | 1
116 | cafe | 330 | 22 |  | 1794 | 40 | 22 | Rooftop Unit | 14352 | 1.3796 | 1 | 1.3796 | 1
116 | Classroom | 387 | 25 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.2834 | 1 | 3.2834 | 1
117 | Classroom | 337 | 22 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 2.8592 | 1 | 2.8592 | 1
118 | Classroom | 306 | 20 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 2.5962 | 1 | 2.5962 | 1
119 | Classroom | 297 | 19 |  | 884 | 20 | 19 | Rooftop Unit | 7072 | 2.5198 | 1 | 2.5198 | 1
121 | Classroom | 291 | 19 |  | 884 | 20 | 19 | Rooftop Unit | 7072 | 2.4689 | 1 | 2.4689 | 1
201 | Classroom | 704 | 46 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 5.9729 | 2 | 5.9729 | 2
202 | Classroom | 475 | 31 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 4.03 | 2 | 4.03 | 2
203 | Classroom | 697 | 46 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 5.9135 | 2 | 5.9135 | 2
204 | Classroom | 457 | 30 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.8773 | 1 | 3.8773 | 1
205 | Classroom | 292 | 19 |  | 884 | 20 | 19 | Rooftop Unit | 7072 | 2.4774 | 1 | 2.4774 | 1
206 | Classroom | 399 | 26 |  | 496 | 11 | 11 | Rooftop Unit | 3968 | 6.0333 | 2 | 6.0333 | 2
207 | Classroom | 574 | 38 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 4.8699 | 2 | 4.8699 | 2
211 | Classroom | 423 | 28 |  | 884 | 20 | 20 | Rooftop Unit | 7072 | 3.5888 | 1 | 3.5888 | 1
213 | Classroom | 159 | 10 |  | 884 | 20 | 10 | Rooftop Unit | 7072 | 1.349 | 1 | 1.349 | 1
214 | Classroom | 202 | 13 |  | 884 | 20 | 13 | Rooftop Unit | 7072 | 1.7138 | 1 | 1.7138 | 1
215 | Classroom | 208 | 13 |  | 884 | 20 | 13 | Rooftop Unit | 7072 | 1.7647 | 1 | 1.7647 | 1
216 | Classroom | 144 | 9 |  | 884 | 20 | 9 | Rooftop Unit | 7072 | 1.2217 | 1 | 1.2217 | 1
217 | Classroom | 142 | 9 |  | 884 | 20 | 9 | Rooftop Unit | 7072 | 1.2048 | 1 | 1.2048 | 1
218 | Classroom | 153 | 10 |  | 1768 | 40 | 10 | Rooftop Unit | 14144 | 0.64904 | 0 | 0.64904 | 0
219 | Classroom | 131 | 8 |  | 884 | 20 | 8 | Rooftop Unit | 7072 | 1.1114 | 1 | 1.1114 | 1
221 | Classroom | 151 | 10 |  | 884 | 20 | 10 | Rooftop Unit | 7072 | 1.2811 | 1 | 1.2811 | 1
Penrose Little School House | [9 empty] | unk | unk | unk | unk
1 | Classroom | 289 | 19 |  | 978 | 22 | 19 | Blower Coil Unit | 7824 | 2.2163 | 1 | 2.2163 | 1
2 | Classroom | 340 | 22 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 2.6074 | 1 | 2.6074 | 1
3 | Classroom | 289 | 19 |  | 978 | 22 | 19 | Blower Coil Unit | 7824 | 2.2163 | 1 | 2.2163 | 1
4 | Classroom | 340 | 22 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 2.6074 | 1 | 2.6074 | 1
5 | Classroom | 350 | 23 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 2.684 | 1 | 2.684 | 1
6 | Classroom | 374 | 24 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 2.8681 | 1 | 2.8681 | 1
7 | Classroom | 374 | 24 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 2.8681 | 1 | 2.8681 | 1
8 | Classroom | 493 | 32 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 3.7807 | 1 | 3.7807 | 1
9 | Classroom | 311 | 20 |  | 978 | 22 | 20 | Blower Coil Unit | 7824 | 2.385 | 1 | 2.385 | 1
10 | Classroom | 493 | 32 |  | 978 | 22 | 22 | Blower Coil Unit | 7824 | 3.7807 | 1 | 3.7807 | 1
11 | Classroom | 311 | 20 |  | 978 | 22 | 20 | Blower Coil Unit | 7824 | 2.385 | 1 | 2.385 | 1
- | multipurpose | 2960 | 197 |  | 2067 | 46 | 46 | Blower Coil Unit | 16536 | 10.7402 | 3 | 10.7402 | 3
- | Corridor | 58 | 3 |  | 684 | 15 | 3 | Blower Coil Unit | 5472 | 0.63596 | 0 | 0.63596 | 0
- | Boy's Restroom | 59 | 3 |  | 200 | 4 | 3 | Blower Coil Unit | 1600 | 2.2125 | 1 | 2.2125 | 1
- | Girl's Rest Room | 64 | 4 |  | 200 | 4 | 4 | Blower Coil Unit | 1600 | 2.4 | 1 | 2.4 | 1
- | General Office |  | 0 |  | 146 | 3 | 0 | Blower Coil Unit | 1168 | unk | unk | unk | unk
- | Principal's Office |  | 0 |  | 72 | 1 | 0 | Blower Coil Unit | 576 | unk | unk | unk | unk
- | Psychiastrist's Office |  | 0 |  | 72 | 1 | 0 | Blower Coil Unit | 576 | unk | unk | unk | unk
TB Read | [9 empty] | unk | unk | unk | unk
101 | Classroom | 324 | 21 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 3.0682 | 1 | 3.0682 | 1
102 | Classroom | 101 | 6 | Yes | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 0.95644 | 0 | 20.9564 | 3
103 | Classroom | 492 | 32 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 4.6591 | 2 | 4.6591 | 2
104 | Classroom | 584 | 38 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 5.5303 | 2 | 5.5303 | 2
105 | Classroom | 400 | 26 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 3.7879 | 1 | 3.7879 | 1
201 | Classroom | 443 | 29 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 4.1951 | 2 | 4.1951 | 2
202 | Classroom | 1636 | 109 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 15.4924 | 3 | 15.4924 | 3
203 | Classroom | 717 | 47 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 6.7898 | 2 | 6.7898 | 2
204 | Classroom | 948 | 63 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 8.9773 | 2 | 8.9773 | 2
205 | Classroom | 397 | 26 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 3.7595 | 1 | 3.7595 | 1
14 | Computer Lab | 473 | 31 |  | 792 | 18 | 18 | Heating Ventilation Unit | 6336 | 4.4792 | 2 | 4.4792 | 2
- | Corridor #1 | 795 | 53 |  | 1298 | 29 | 29 | Heating Ventilation Unit | 10384 | 4.5936 | 2 | 4.5936 | 2
- | Corridor #2 | 413 | 27 |  | 1600 | 36 | 27 | Heating Ventilation Unit | 12800 | 1.9359 | 1 | 1.9359 | 1
- | GYM | 7270 | 484 |  | 8969 | 203 | 203 | Heating Ventilation Unit | 71752 | 6.0793 | 2 | 6.0793 | 2
- | Library | 442 | 29 |  | 874 | 19 | 19 | Heating Ventilation Unit | 6992 | 3.7929 | 1 | 3.7929 | 1
Sheet Last Modified: | 2021-05-03 | [8 empty] | unk | unk | unk | unk
School: | Philadelphia Learning Academy North/ Camelot Academy East/ Crossroads Academy at Hunting Park (former CEP Hunting Park) Alternative School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
3 | Room (Split Level South) | 25 | 1 |  | 86 | 1 | 1 | Rooftop Unit | 688 | 2.1802 | 1 | 2.1802 | 1
5 | Room (Split Level South) | 141 | 9 |  | 396 | 9 | 9 | Rooftop Unit | 3168 | 2.6705 | 1 | 2.6705 | 1
005A | Room (Split Level South) | 20 | 1 |  | 87 | 1 | 1 | Rooftop Unit | 696 | 1.7241 | 1 | 1.7241 | 1
6 | Room | 27 | 1 |  | 83 | 1 | 1 | Rooftop Unit | 664 | 2.4398 | 1 | 2.4398 | 1
006A | Room | 14 | 0 |  | 80 | 1 | 0 | Rooftop Unit | 640 | 1.3125 | 1 | 1.3125 | 1
006B | Room | 13 | 0 |  | 79 | 1 | 0 | Rooftop Unit | 632 | 1.2342 | 1 | 1.2342 | 1
10 | Room | 7 | 0 |  | 84 | 1 | 0 | Rooftop Unit | 672 | 0.625 | 0 | 0.625 | 0
010A | Room | 53 | 3 |  | 80 | 1 | 1 | Rooftop Unit | 640 | 4.9688 | 2 | 4.9688 | 2
103 | Room | 20 | 1 |  | 87 | 1 | 1 | Rooftop Unit | 696 | 1.7241 | 1 | 1.7241 | 1
104 | Room | 19 | 1 |  | 85 | 1 | 1 | Rooftop Unit | 680 | 1.6765 | 1 | 1.6765 | 1
105 | Room | 27 | 1 |  | 81 | 1 | 1 | Rooftop Unit | 648 | 2.5 | 1 | 2.5 | 1
106 | Room | 22 | 1 |  | 83 | 1 | 1 | Rooftop Unit | 664 | 1.988 | 1 | 1.988 | 1
108 | Room | 14 | 0 |  | 89 | 2 | 0 | Rooftop Unit | 712 | 1.1798 | 1 | 1.1798 | 1
109 | Room | 13 | 0 |  | 92 | 2 | 0 | Rooftop Unit | 736 | 1.0598 | 1 | 1.0598 | 1
110 | Room | 15 | 0 |  | 269 | 6 | 0 | Rooftop Unit | 2152 | 0.41822 | 0 | 0.41822 | 0
113 | Room (Split Level South) | 56 | 3 |  | 134 | 3 | 3 | Rooftop Unit | 1072 | 3.1343 | 1 | 3.1343 | 1
114 | Room (Split Level South) | 26 | 1 |  | 136 | 3 | 1 | Rooftop Unit | 1088 | 1.4338 | 1 | 1.4338 | 1
115 | Room (Split Level South) | 41 | 2 |  | 139 | 3 | 2 | Rooftop Unit | 1112 | 2.2122 | 1 | 2.2122 | 1
116 | Room (Split Level South) | 25 | 1 |  | 139 | 3 | 1 | Rooftop Unit | 1112 | 1.3489 | 1 | 1.3489 | 1
117 | Room (Split Level South) | 80 | 5 |  | 355 | 8 | 5 | Rooftop Unit | 2840 | 1.6901 | 1 | 1.6901 | 1
120 | Admin Office | -231 | -15 |  | 92 | 2 | -15 | Rooftop Unit | 736 | 18.8315 | 3 | 18.8315 | 3
121 | Admin Office | 145 | 9 |  | 396 | 9 | 9 | Rooftop Unit | 3168 | 2.7462 | 1 | 2.7462 | 1
122 | Admin Office | 208 | 13 |  | 94 | 2 | 2 | Rooftop Unit | 752 | 16.5957 | 3 | 16.5957 | 3
123 | Admin Office | 97 | 6 |  | 92 | 2 | 2 | Rooftop Unit | 736 | 7.9076 | 2 | 7.9076 | 2
124 | Admin Office | -65 | -4 |  | 92 | 2 | -4 | Rooftop Unit | 736 | 5.2989 | 2 | 5.2989 | 2
126 | Admin Office | 57 | 3 |  | 139 | 3 | 3 | Rooftop Unit | 1112 | 3.0755 | 1 | 3.0755 | 1
127 | Admin Office | -417 | -27 |  | 95 | 2 | -27 | Rooftop Unit | 760 | 32.9211 | 4 | 32.9211 | 4
129 | Admin Office | -65 | -4 |  | 355 | 8 | -4 | Rooftop Unit | 2840 | 1.3732 | 1 | 1.3732 | 1
130 | Admin Office | -52 | -3 | Yes | 140 | 3 | 3 | Rooftop Unit | 1120 | 2.7857 | 1 | 17.2143 | 3
133 | Admin Office | 104 | 6 |  | 266 | 6 | 6 | Rooftop Unit | 2128 | 2.9323 | 1 | 2.9323 | 1
133A | Admin Office | 322 | 21 |  | 927 | 21 | 21 | Rooftop Unit | 7416 | 2.6052 | 1 | 2.6052 | 1
133B | Admin Office | 316 | 21 |  | 927 | 21 | 21 | Rooftop Unit | 7416 | 2.5566 | 1 | 2.5566 | 1
134 | Media Room | 195 | 13 |  | 1769 | 40 | 13 | Rooftop Unit | 14152 | 0.82674 | 0 | 0.82674 | 0
135 | Admin Office | 253 | 16 |  | 709 | 16 | 16 | Rooftop Unit | 5672 | 2.6763 | 1 | 2.6763 | 1
136 | Media Room | 465 | 31 |  | 407 | 9 | 9 | Rooftop Unit | 3256 | 8.5688 | 2 | 8.5688 | 2
142 | Admin Office | 339 | 22 |  | 225 | 5 | 5 | Rooftop Unit | 1800 | 11.3 | 3 | 11.3 | 3
147 | AEP Office | 146 | 9 |  | 413 | 9 | 9 | Rooftop Unit | 3304 | 2.6513 | 1 | 2.6513 | 1
148 | AEP Office | -245 | -16 |  | 92 | 2 | -16 | Rooftop Unit | 736 | 19.9728 | 3 | 19.9728 | 3
149 | AEP Office | -104 | -6 |  | 94 | 2 | -6 | Rooftop Unit | 752 | 8.2979 | 2 | 8.2979 | 2
150 | AEP Office | -38 | -2 |  | 136 | 3 | -2 | Rooftop Unit | 1088 | 2.0956 | 1 | 2.0956 | 1
151 | AEP Office | 178 | 11 |  | 179 | 4 | 4 | Rooftop Unit | 1432 | 7.4581 | 2 | 7.4581 | 2
152 | AEP Office | 10 | 0 |  | 91 | 2 | 0 | Rooftop Unit | 728 | 0.82418 | 0 | 0.82418 | 0
153 | AEP Office | 36 | 2 |  | 92 | 2 | 2 | Rooftop Unit | 736 | 2.9348 | 1 | 2.9348 | 1
154 | AEP Office | 69 | 4 |  | 96 | 2 | 2 | Rooftop Unit | 768 | 5.3906 | 2 | 5.3906 | 2
155 | AEP Office | 179 | 11 |  | 184 | 4 | 4 | Rooftop Unit | 1472 | 7.2962 | 2 | 7.2962 | 2
156 | AEP Office | -34 | -2 |  | 80 | 1 | -2 | Rooftop Unit | 640 | 3.1875 | 1 | 3.1875 | 1
157 | AEP Office | 70 | 4 |  | 79 | 1 | 1 | Rooftop Unit | 632 | 6.6456 | 2 | 6.6456 | 2
158 | AEP Office | 119 | 7 |  | 85 | 1 | 1 | Rooftop Unit | 680 | 10.5 | 3 | 10.5 | 3
159 | AEP Office | 21 | 1 |  | 84 | 1 | 1 | Rooftop Unit | 672 | 1.875 | 1 | 1.875 | 1
160 | AEP Office | 184 | 12 |  | 142 | 3 | 3 | Rooftop Unit | 1136 | 9.7183 | 2 | 9.7183 | 2
161 | Library Office | -59 | -3 |  | 91 | 2 | -3 | Rooftop Unit | 728 | 4.8626 | 2 | 4.8626 | 2
162 | Library Office | -99 | -6 |  | 269 | 6 | -6 | Rooftop Unit | 2152 | 2.7602 | 1 | 2.7602 | 1
164 | Main Library | 980 | 65 |  | 973 | 22 | 22 | Rooftop Unit | 7784 | 7.554 | 2 | 7.554 | 2
174 | Office | -270 | -18 |  | 83 | 1 | -18 | Rooftop Unit | 664 | 24.3976 | 4 | 24.3976 | 4
175 | Office | 80 | 5 |  | 82 | 1 | 1 | Rooftop Unit | 656 | 7.3171 | 2 | 7.3171 | 2
180 | Office | 87 | 5 |  | 93 | 2 | 2 | Rooftop Unit | 744 | 7.0161 | 2 | 7.0161 | 2
181 | Office | -31 | -2 |  | 92 | 2 | -2 | Rooftop Unit | 736 | 2.5272 | 1 | 2.5272 | 1
182 | Office | 166 | 11 |  | 92 | 2 | 2 | Rooftop Unit | 736 | 13.5326 | 3 | 13.5326 | 3
184 | Office | 122 | 8 |  | 93 | 2 | 2 | Rooftop Unit | 744 | 9.8387 | 2 | 9.8387 | 2
185 | Office | 27 | 1 |  | 92 | 2 | 1 | Rooftop Unit | 736 | 2.2011 | 1 | 2.2011 | 1
186A | Office | -272 | -18 |  | 449 | 10 | -18 | Rooftop Unit | 3592 | 4.5434 | 2 | 4.5434 | 2
186B | Office | -47 | -3 |  | 449 | 10 | -3 | Rooftop Unit | 3592 | 0.78508 | 0 | 0.78508 | 0
187 | Office | -182 | -12 |  | 94 | 2 | -12 | Rooftop Unit | 752 | 14.5213 | 3 | 14.5213 | 3
188 | Office | 100 | 6 |  | 92 | 2 | 2 | Rooftop Unit | 736 | 8.1522 | 2 | 8.1522 | 2
189 | Office | 78 | 5 |  | 227 | 5 | 5 | Rooftop Unit | 1816 | 2.5771 | 1 | 2.5771 | 1
192 | Office | -269 | -17 |  | 72 | 1 | -17 | Rooftop Unit | 576 | 28.0208 | 4 | 28.0208 | 4
193 | Office | 283 | 18 |  | 82 | 1 | 1 | Rooftop Unit | 656 | 25.8841 | 4 | 25.8841 | 4
194 | Office | 106 | 7 |  | 48 | 1 | 1 | Rooftop Unit | 384 | 16.5625 | 3 | 16.5625 | 3
195 | Office | 78 | 5 |  | 232 | 5 | 5 | Rooftop Unit | 1856 | 2.5216 | 1 | 2.5216 | 1
196 | Classroom | 190 | 12 |  | 528 | 12 | 12 | Rooftop Unit | 4224 | 2.6989 | 1 | 2.6989 | 1
201 | Classroom | 248 | 16 |  | 712 | 16 | 16 | Rooftop Unit | 5696 | 2.6124 | 1 | 2.6124 | 1
204 | Electrical Closet | 13 | 0 |  | 80 | 1 | 0 | Rooftop Unit | 640 | 1.2188 | 1 | 1.2188 | 1
205 | IT Room | -3 | 0 |  | 84 | 1 | 0 | Rooftop Unit | 672 | 0.26786 | 0 | 0.26786 | 0
207 | Closet | 0 | 0 |  | 136 | 3 | 0 | Rooftop Unit | 1088 | 0 | 0 | 0 | 0
210 | Office | -127 | -8 |  | 96 | 2 | -8 | Rooftop Unit | 768 | 9.9219 | 2 | 9.9219 | 2
211 | Office | -20 | -1 |  | 94 | 2 | -1 | Rooftop Unit | 752 | 1.5957 | 1 | 1.5957 | 1
212 | Office | 0 | 0 |  | 96 | 2 | 0 | Rooftop Unit | 768 | 0 | 0 | 0 | 0
213 | Room |  | 0 | Yes | 880 | 20 | 20 |  | 7040 | unk | unk | 20 | 3
213A | Office | 63 | 4 |  | 180 | 4 | 4 | Rooftop Unit | 1440 | 2.625 | 1 | 2.625 | 1
213B | Office | 284 | 18 |  | 792 | 18 | 18 | Rooftop Unit | 6336 | 2.6894 | 1 | 2.6894 | 1
214 | Office | -12 | 0 |  | 89 | 2 | 0 | Rooftop Unit | 712 | 1.0112 | 1 | 1.0112 | 1
215 | Office | 0 | 0 |  | 92 | 2 | 0 | Rooftop Unit | 736 | 0 | 0 | 0 | 0
217 | Office | -31 | -2 |  | 96 | 2 | -2 | Rooftop Unit | 768 | 2.4219 | 1 | 2.4219 | 1
218 | Office | -23 | -1 |  | 86 | 1 | -1 | Rooftop Unit | 688 | 2.0058 | 1 | 2.0058 | 1
219 | Office | 0 | 0 |  | 93 | 2 | 0 | Rooftop Unit | 744 | 0 | 0 | 0 | 0
221 | IT Room | 13 | 0 |  | 52 | 1 | 0 | Rooftop Unit | 416 | 1.875 | 1 | 1.875 | 1
222 | Electrical Closet | 195 | 13 |  | 94 | 2 | 2 | Rooftop Unit | 752 | 15.5585 | 3 | 15.5585 | 3
223 | Closet | 0 | 0 |  | 55 | 1 | 0 | Rooftop Unit | 440 | 0 | 0 | 0 | 0
303 | Room (Split Level South) | 45 | 2 |  | 86 | 1 | 1 | Rooftop Unit | 688 | 3.9244 | 1 | 3.9244 | 1
304 | Room (Split Level South) | 124 | 8 |  | 231 | 5 | 5 | Rooftop Unit | 1848 | 4.026 | 2 | 4.026 | 2
307 | Room (Split Level South) | 118 | 7 |  | 312 | 7 | 7 | Rooftop Unit | 2496 | 2.8365 | 1 | 2.8365 | 1
311 | Room (Split Level South) | 13 | 0 |  | 136 | 3 | 0 | Rooftop Unit | 1088 | 0.71691 | 0 | 0.71691 | 0
311A | Room (Split Level South) | 20 | 1 |  | 63 | 1 | 1 | Rooftop Unit | 504 | 2.381 | 1 | 2.381 | 1
311B | Room (Split Level South) | 12 | 0 |  | 86 | 1 | 0 | Rooftop Unit | 688 | 1.0465 | 1 | 1.0465 | 1
313 | Room | 20 | 1 |  | 98 | 2 | 1 | Rooftop Unit | 784 | 1.5306 | 1 | 1.5306 | 1
314 | Room | 21 | 1 |  | 85 | 1 | 1 | Rooftop Unit | 680 | 1.8529 | 1 | 1.8529 | 1
316 | Room | 62 | 4 |  | 449 | 10 | 4 | Rooftop Unit | 3592 | 1.0356 | 1 | 1.0356 | 1
320 | Room | 19 | 1 |  | 87 | 1 | 1 | Rooftop Unit | 696 | 1.6379 | 1 | 1.6379 | 1
321 | Room | 16 | 1 |  | 89 | 2 | 1 | Rooftop Unit | 712 | 1.3483 | 1 | 1.3483 | 1
322 | Room | 17 | 1 |  | 87 | 1 | 1 | Rooftop Unit | 696 | 1.4655 | 1 | 1.4655 | 1
H01 | Room (Split Level South) | 34 | 2 |  | 89 | 2 | 2 | Rooftop Unit | 712 | 2.8652 | 1 | 2.8652 | 1
H01 | Room | 15 | 0 |  | 72 | 1 | 0 | Rooftop Unit | 576 | 1.5625 | 1 | 1.5625 | 1
H21 | Room (Split Level South) | 159 | 10 |  | 446 | 10 | 10 | Rooftop Unit | 3568 | 2.6738 | 1 | 2.6738 | 1
H21 | Room | 7 | 0 |  | 52 | 1 | 0 | Rooftop Unit | 416 | 1.0096 | 1 | 1.0096 | 1
L4/L5 | Room | 84 | 5 |  | 225 | 5 | 5 | Rooftop Unit | 1800 | 2.8 | 1 | 2.8 | 1
A1 | Classroom | 594 | 39 | Yes | 794 | 18 | 18 | Rooftop Unit | 6352 | 5.6108 | 2 | 25.6108 | 4
A2 | Classroom | 876 | 58 |  | 793 | 18 | 18 | Rooftop Unit | 6344 | 8.285 | 2 | 8.285 | 2
A3 | Classroom | 219 | 14 |  | 795 | 18 | 14 | Rooftop Unit | 6360 | 2.066 | 1 | 2.066 | 1
A4 | Classroom | 905 | 60 |  | 796 | 18 | 18 | Rooftop Unit | 6368 | 8.527 | 2 | 8.527 | 2
B1 | Classroom | 430 | 28 |  | 793 | 18 | 18 | Rooftop Unit | 6344 | 4.0668 | 2 | 4.0668 | 2
B2 | Classroom | 1048 | 69 |  | 792 | 18 | 18 | Rooftop Unit | 6336 | 9.9242 | 2 | 9.9242 | 2
B3 | Classroom | 84 | 5 |  | 794 | 18 | 5 | Rooftop Unit | 6352 | 0.79345 | 0 | 0.79345 | 0
B4 | Classroom | 769 | 51 |  | 794 | 18 | 18 | Rooftop Unit | 6352 | 7.2639 | 2 | 7.2639 | 2
C1 | Classroom | 551 | 36 |  | 797 | 18 | 18 | Rooftop Unit | 6376 | 5.1851 | 2 | 5.1851 | 2
C2 | Classroom | 927 | 61 |  | 795 | 18 | 18 | Rooftop Unit | 6360 | 8.7453 | 2 | 8.7453 | 2
C3 | Classroom | 115 | 7 |  | 794 | 18 | 7 | Rooftop Unit | 6352 | 1.0863 | 1 | 1.0863 | 1
C4 | Classroom | 70 | 4 |  | 795 | 18 | 4 | Rooftop Unit | 6360 | 0.66038 | 0 | 0.66038 | 0
D1 | Classroom | 587 | 39 |  | 797 | 18 | 18 | Rooftop Unit | 6376 | 5.5238 | 2 | 5.5238 | 2
D2 | Classroom | 935 | 62 |  | 795 | 18 | 18 | Rooftop Unit | 6360 | 8.8208 | 2 | 8.8208 | 2
D3 | Classroom | 14 | 0 |  | 793 | 18 | 0 | Rooftop Unit | 6344 | 0.13241 | 0 | 0.13241 | 0
D4 | Classroom | 617 | 41 |  | 796 | 18 | 18 | Rooftop Unit | 6368 | 5.8134 | 2 | 5.8134 | 2
E1 | Classroom | 312 | 20 | Yes | 794 | 18 | 18 | Rooftop Unit | 6352 | 2.9471 | 1 | 22.9471 | 3
E2 | Classroom | 752 | 50 | Yes | 796 | 18 | 18 | Rooftop Unit | 6368 | 7.0854 | 2 | 27.0854 | 4
E3 | Classroom | 269 | 17 |  | 793 | 18 | 17 | Rooftop Unit | 6344 | 2.5441 | 1 | 2.5441 | 1
E4 | Classroom | 715 | 47 | Yes | 795 | 18 | 18 | Rooftop Unit | 6360 | 6.7453 | 2 | 26.7453 | 4
G1 | Classroom | 66 | 4 | Yes | 794 | 18 | 18 | Rooftop Unit | 6352 | 0.62343 | 0 | 20.6234 | 3
G2 | Classroom | 857 | 57 | Yes | 796 | 18 | 18 | Rooftop Unit | 6368 | 8.0747 | 2 | 28.0747 | 4
G3 | Classroom | 197 | 13 | Yes | 793 | 18 | 18 | Rooftop Unit | 6344 | 1.8632 | 1 | 21.8632 | 3
G4 | Classroom | 813 | 54 | Yes | 797 | 18 | 18 | Rooftop Unit | 6376 | 7.6506 | 2 | 27.6506 | 4
Gym | Recreational Area 1 | 442 | 29 |  | 1276 | 29 | 29 | Rooftop Unit | 10208 | 2.598 | 1 | 2.598 | 1
Gym | Gym Cafeteria | 306 | 20 |  | 886 | 20 | 20 | Rooftop Unit | 7088 | 2.5903 | 1 | 2.5903 | 1
Gym | Recreational Area 1 | 630 | 42 |  | 1848 | 42 | 42 | Rooftop Unit | 14784 | 2.5568 | 1 | 2.5568 | 1
Gym | Gym 2A | 716 | 47 |  | 9196 | 209 | 47 | Rooftop Unit | 73568 | 0.58395 | 0 | 0.58395 | 0
Gym | Gym 2B | 601 | 40 |  | 9196 | 209 | 40 | Rooftop Unit | 73568 | 0.49016 | 0 | 0.49016 | 0
Gym | Vestibule | 0 | 0 |  | 176 | 4 | 0 | Rooftop Unit | 1408 | 0 | 0 | 0 | 0
H1 | Classroom | 807 | 53 |  | 796 | 18 | 18 | Rooftop Unit | 6368 | 7.6036 | 2 | 7.6036 | 2
H17 | Hallway | 91 | 6 |  | 264 | 6 | 6 | Rooftop Unit | 2112 | 2.5852 | 1 | 2.5852 | 1
H2 | Classroom | 706 | 47 |  | 794 | 18 | 18 | Rooftop Unit | 6352 | 6.6688 | 2 | 6.6688 | 2
H3 | Classroom | -660 | -44 |  | 793 | 18 | -44 | Rooftop Unit | 6344 | 6.2421 | 2 | 6.2421 | 2
H4 | Classroom | 11 | 0 |  | 795 | 18 | 0 | Rooftop Unit | 6360 | 0.10377 | 0 | 0.10377 | 0
Hallway | Hallway (Split Level South) | 48 | 3 |  | 136 | 3 | 3 | Rooftop Unit | 1088 | 2.6471 | 1 | 2.6471 | 1
Hunter | Office | 229 | 15 |  | 664 | 15 | 15 | Rooftop Unit | 5312 | 2.5866 | 1 | 2.5866 | 1
Hunting Park | Lobby | 1738 | 115 |  | 5069 | 115 | 115 | Rooftop Unit | 40552 | 2.5715 | 1 | 2.5715 | 1
J | Hallway | 0 | 0 |  | 616 | 14 | 0 | Rooftop Unit | 4928 | 0 | 0 | 0 | 0
J1 | Classroom | -493 | -32 | Yes | 529 | 12 | 12 | Rooftop Unit | 4232 | 6.9896 | 2 | 13.0104 | 3
J2 | Classroom | 381 | 25 |  | 792 | 18 | 18 | Rooftop Unit | 6336 | 3.608 | 1 | 3.608 | 1
J3 | Classroom | 493 | 32 |  | 528 | 12 | 12 | Rooftop Unit | 4224 | 7.0028 | 2 | 7.0028 | 2
J4 | Classroom | 1208 | 80 |  | 528 | 12 | 12 | Rooftop Unit | 4224 | 17.1591 | 3 | 17.1591 | 3
K | Hallway | 0 | 0 |  | 616 | 14 | 0 | Rooftop Unit | 4928 | 0 | 0 | 0 | 0
K1 | Classroom | 189 | 12 |  | 792 | 18 | 12 | Rooftop Unit | 6336 | 1.7898 | 1 | 1.7898 | 1
K2 | Classroom | 682 | 45 |  | 794 | 18 | 18 | Rooftop Unit | 6352 | 6.4421 | 2 | 6.4421 | 2
K3 | Classroom | 130 | 8 | Yes | 796 | 18 | 18 | Rooftop Unit | 6368 | 1.2249 | 1 | 21.2249 | 3
K4 | Classroom | 617 | 41 |  | 797 | 18 | 18 | Rooftop Unit | 6376 | 5.8061 | 2 | 5.8061 | 2
Kitchen | Kitchen | 1953 | 130 |  | 880 | 20 | 20 | Rooftop Unit | 7040 | 16.6449 | 3 | 16.6449 | 3
Kitchen | Lounge | -3 | 0 |  | 73 | 1 | 0 | Rooftop Unit | 584 | 0.30822 | 0 | 0.30822 | 0
L | Hallway | 0 | 0 |  | 704 | 16 | 0 | Rooftop Unit | 5632 | 0 | 0 | 0 | 0
L1 | Classroom | 79 | 5 | Yes | 794 | 18 | 18 | Rooftop Unit | 6352 | 0.74622 | 0 | 20.7462 | 3
L2 | Classroom | 636 | 42 |  | 793 | 18 | 18 | Rooftop Unit | 6344 | 6.0151 | 2 | 6.0151 | 2
L3 | Classroom | 109 | 7 | Yes | 792 | 18 | 18 | Rooftop Unit | 6336 | 1.0322 | 1 | 21.0322 | 3
L4 | Classroom | 707 | 47 |  | 797 | 18 | 18 | Rooftop Unit | 6376 | 6.6531 | 2 | 6.6531 | 2
Lobby | Main Lobby North | 147 | 9 |  | 410 | 9 | 9 | Rooftop Unit | 3280 | 2.689 | 1 | 2.689 | 1
M | Hallway | 0 | 0 |  | 704 | 16 | 0 | Rooftop Unit | 5632 | 0 | 0 | 0 | 0
M1 | Classroom | 226 | 15 |  | 794 | 18 | 15 | Rooftop Unit | 6352 | 2.1348 | 1 | 2.1348 | 1
M2 | Classroom | 855 | 57 |  | 796 | 18 | 18 | Rooftop Unit | 6368 | 8.0559 | 2 | 8.0559 | 2
M3 | Classroom | 17 | 1 |  | 793 | 18 | 1 | Rooftop Unit | 6344 | 0.16078 | 0 | 0.16078 | 0
M4 | Classroom | 684 | 45 |  | 795 | 18 | 18 | Rooftop Unit | 6360 | 6.4528 | 2 | 6.4528 | 2
Men's Bathroom | Men's Bathroom | 0 | 0 |  | 132 | 3 | 0 | Rooftop Unit | 1056 | 0 | 0 | 0 | 0
MS0S1 | Office | 432 | 28 |  | 528 | 12 | 12 | Rooftop Unit | 4224 | 6.1364 | 2 | 6.1364 | 2
MS0S2 | Office | 1153 | 76 |  | 880 | 20 | 20 | Rooftop Unit | 7040 | 9.8267 | 2 | 9.8267 | 2
MS2 | MS2 (Woodshop) | 480 | 32 |  | 1408 | 32 | 32 | Rooftop Unit | 11264 | 2.5568 | 1 | 2.5568 | 1
MS2 | MS2 (Woodshop) | 768 | 51 |  | 1408 | 32 | 32 | Rooftop Unit | 11264 | 4.0909 | 2 | 4.0909 | 2
MS6 | Office | 107 | 7 |  | 176 | 4 | 4 | Rooftop Unit | 1408 | 4.5597 | 2 | 4.5597 | 2
MS7 | Office | 0 | 0 |  | 132 | 3 | 0 | Rooftop Unit | 1056 | 0 | 0 | 0 | 0
N1 | Classroom | 612 | 40 |  | 794 | 18 | 18 | Rooftop Unit | 6352 | 5.7809 | 2 | 5.7809 | 2
N2 | Classroom (with office) | 100 | 6 |  | 796 | 18 | 6 | Rooftop Unit | 6368 | 0.94221 | 0 | 0.94221 | 0
N3 | Classroom (with office) | 1490 | 99 |  | 795 | 18 | 18 | Rooftop Unit | 6360 | 14.0566 | 3 | 14.0566 | 3
N4 | Classroom | 781 | 52 |  | 796 | 18 | 18 | Rooftop Unit | 6368 | 7.3587 | 2 | 7.3587 | 2
Office | Office | 12 | 0 |  | 132 | 3 | 0 | Rooftop Unit | 1056 | 0.68182 | 0 | 0.68182 | 0
S11 | AEP Office | -244 | -16 |  | 396 | 9 | -16 | Rooftop Unit | 3168 | 4.6212 | 2 | 4.6212 | 2
- | Staff Lounge | 243 | 16 |  | 528 | 12 | 12 | Rooftop Unit | 4224 | 3.4517 | 1 | 3.4517 | 1
- | Women's Bathroom | 0 | 0 |  | 132 | 3 | 0 | Rooftop Unit | 1056 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Robert B. Pollock Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCORE Fluidics | Retest Report | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Classroom | 313 | 20 |  | 945 | 21 | 20 | Perimeter Heater | 7560 | 2.4841 | 1 | 2.4841 | 1
2 | Classroom | 385 | 25 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 3.0556 | 1 | 3.0556 | 1
3 | Classroom | 141 | 9 | Yes | 945 | 21 | 21 | Perimeter Heater | 7560 | 1.119 | 1 | 21.119 | 3
4 | Classroom | 406 | 27 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 3.2222 | 1 | 3.2222 | 1
5 | Classroom | 222 | 14 | Yes | 945 | 21 | 21 | Perimeter Heater | 7560 | 1.7619 | 1 | 21.7619 | 3
6 | Classroom | 278 | 18 |  | 720 | 16 | 16 | Perimeter Heater | 5760 | 2.8958 | 1 | 2.8958 | 1
7 | Classroom | 270 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1429 | 1 | 2.1429 | 1
8 | Classroom | 329 | 21 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 2.6111 | 1 | 2.6111 | 1
9 | Classroom | 301 | 20 |  | 945 | 21 | 20 | Perimeter Heater | 7560 | 2.3889 | 1 | 2.3889 | 1
10 | Classroom | 482 | 32 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 3.8254 | 1 | 3.8254 | 1
11 | Classroom | 0 | 0 | Yes | 945 | 21 | 21 | Perimeter Heater | 7560 | 0 | 0 | 20 | 3
12 | Classroom | 369 | 24 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 2.9286 | 1 | 2.9286 | 1
13 | Classroom | 282 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.2381 | 1 | 2.2381 | 1
14 | Classroom | 338 | 22 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 2.6825 | 1 | 2.6825 | 1
15 | Classroom | 275 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1825 | 1 | 2.1825 | 1
16 | Classroom | 311 | 20 |  | 840 | 19 | 19 | Perimeter Heater | 6720 | 2.7768 | 1 | 2.7768 | 1
17 | Classroom | 294 | 19 |  | 945 | 21 | 19 | Perimeter Heater | 7560 | 2.3333 | 1 | 2.3333 | 1
101 | Classroom | 505 | 33 |  | 1450 | 32 | 32 | Perimeter Heater | 11600 | 2.6121 | 1 | 2.6121 | 1
102 | Classroom | 280 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.2222 | 1 | 2.2222 | 1
103 | Classroom | 305 | 20 |  | 945 | 21 | 20 | Perimeter Heater | 7560 | 2.4206 | 1 | 2.4206 | 1
104 | Classroom | 277 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1984 | 1 | 2.1984 | 1
105 | Classroom | 273 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1667 | 1 | 2.1667 | 1
106 | Classroom | 707 | 47 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 5.6111 | 2 | 5.6111 | 2
107 | Classroom |  | 0 | Yes | 945 | 21 | 21 |  | 7560 | unk | unk | 20 | 3
108 | Classroom | 315 | 21 |  | 594 | 13 | 13 | Perimeter Heater | 4752 | 3.9773 | 1 | 3.9773 | 1
110 | Classroom | 301 | 20 | Yes | 945 | 21 | 21 | Perimeter Heater | 7560 | 2.3889 | 1 | 22.3889 | 3
111 | Classroom | 276 | 18 |  | 480 | 10 | 10 | Perimeter Heater | 3840 | 4.3125 | 2 | 4.3125 | 2
112 | Classroom | 276 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1905 | 1 | 2.1905 | 1
113 | Classroom | 272 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1587 | 1 | 2.1587 | 1
114 | Classroom | 277 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1984 | 1 | 2.1984 | 1
115 | Classroom | 275 | 18 |  | 945 | 21 | 18 | Perimeter Heater | 7560 | 2.1825 | 1 | 2.1825 | 1
116 | Classroom | 289 | 19 |  | 945 | 21 | 19 | Perimeter Heater | 7560 | 2.2937 | 1 | 2.2937 | 1
117A | Classroom | 579 | 38 |  | 1890 | 42 | 38 | Perimeter Heater | 15120 | 2.2976 | 1 | 2.2976 | 1
118 | Classroom | 323 | 21 |  | 945 | 21 | 21 | Perimeter Heater | 7560 | 2.5635 | 1 | 2.5635 | 1
- | Main Office |  | 0 | Yes | 674 | 15 | 15 |  | 5392 | unk | unk | 20 | 3
- | Principals Office |  | 0 | Yes | 96 | 2 | 2 |  | 768 | unk | unk | 20 | 3
- | Nurses Office |  | 0 | Yes | 96 | 2 | 2 |  | 768 | unk | unk | 20 | 3
- | Office |  | 0 | Yes | 108 | 2 | 2 |  | 864 | unk | unk | 20 | 3
- | Auditorium | 5528 | 368 |  | 4240 | 96 | 96 | Air Handling Unit | 33920 | 9.7783 | 2 | 9.7783 | 2
- | Cafeteria | 5093 | 339 |  | 4032 | 91 | 91 | Air Handling Unit | 32256 | 9.4736 | 2 | 9.4736 | 2
- | Confrence Room | 275 | 18 |  | 374 | 8 | 8 | Perimeter Heater | 2992 | 5.5147 | 2 | 5.5147 | 2
- | Gym | 3930 | 262 |  | 3901 | 88 | 88 | Air Handling Unit | 31208 | 7.5558 | 2 | 7.5558 | 2
- | Kindergarten Classroom | 438 | 29 |  | 1450 | 32 | 29 | Perimeter Heater | 11600 | 2.2655 | 1 | 2.2655 | 1
- | First Flr Office | 0 | 0 |  | 674 | 15 | 0 | Perimeter Heater | 5392 | 0 | 0 | 0 | 0
- | P1 Bungalow Building | 527 | 35 |  | 1248 | 28 | 28 | Perimeter Heater | 9984 | 3.1671 | 1 | 3.1671 | 1
- | P2 Bungalow Building | 298 | 19 |  | 806 | 18 | 18 | Perimeter Heater | 6448 | 2.773 | 1 | 2.773 | 1
- | P3 Bungalow Building | 385 | 25 |  | 1040 | 23 | 23 | Perimeter Heater | 8320 | 2.7764 | 1 | 2.7764 | 1
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-21 | [8 empty] | unk | unk | unk | unk
School: | Potter Thomas Promise Academy Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | Retest | [7 empty] | unk | unk | unk | unk
| Devine 2nd Retest 2-15-21 | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 322 | 21 |  | 1350 | 30 | 21 | Univent | 10800 | 1.7889 | 1 | 1.7889 | 1
102 | Classroom | 387 | 25 |  | 1590 | 36 | 25 | Univent | 12720 | 1.8255 | 1 | 1.8255 | 1
103 | Classroom | 374 | 24 |  | 1590 | 36 | 24 | Univent | 12720 | 1.7642 | 1 | 1.7642 | 1
104 | Classroom | 817 | 54 |  | 1590 | 36 | 36 | Univent | 12720 | 3.8538 | 1 | 3.8538 | 1
105 | Classroom | 296 | 19 |  | 1024 | 23 | 19 | Univent | 8192 | 2.168 | 1 | 2.168 | 1
106 | Music Room | 216 | 14 |  | 754 | 17 | 14 | Univent | 6032 | 2.1485 | 1 | 2.1485 | 1
106 | Computer Lab | 149 | 9 | Yes | 1989 | 45 | 45 | Univent | 15912 | 0.56184 | 0 | 20.5618 | 3
201 | Classroom | 245 | 16 |  | 812 | 18 | 16 | Univent | 6496 | 2.2629 | 1 | 2.2629 | 1
202 | Classroom | 275 | 18 |  | 870 | 19 | 18 | Univent | 6960 | 2.3707 | 1 | 2.3707 | 1
203 | Classroom | 329 | 21 |  | 870 | 19 | 19 | Univent | 6960 | 2.8362 | 1 | 2.8362 | 1
204 | Classroom | 350 | 23 |  | 870 | 19 | 19 | Univent | 6960 | 3.0172 | 1 | 3.0172 | 1
205 | Classroom | 356 | 23 |  | 870 | 19 | 19 | Univent | 6960 | 3.069 | 1 | 3.069 | 1
206 | Classroom | 338 | 22 |  | 783 | 17 | 17 | Univent | 6264 | 3.2375 | 1 | 3.2375 | 1
207 | Classroom | 469 | 31 |  | 841 | 19 | 19 | Univent | 6728 | 4.1825 | 2 | 4.1825 | 2
208 | Classroom | 397 | 26 |  | 870 | 19 | 19 | Univent | 6960 | 3.4224 | 1 | 3.4224 | 1
209 | Classroom | 257 | 17 |  | 870 | 19 | 17 | Univent | 6960 | 2.2155 | 1 | 2.2155 | 1
210 | Classroom | 368 | 24 |  | 870 | 19 | 19 | Univent | 6960 | 3.1724 | 1 | 3.1724 | 1
211 | Classroom | 348 | 23 |  | 870 | 19 | 19 | Univent | 6960 | 3 | 1 | 3 | 1
212 | Classroom | 291 | 19 |  | 870 | 19 | 19 | Univent | 6960 | 2.5086 | 1 | 2.5086 | 1
213 | Classroom | 280 | 18 |  | 870 | 19 | 18 | Univent | 6960 | 2.4138 | 1 | 2.4138 | 1
214 | Classroom | 319 | 21 |  | 870 | 19 | 19 | Univent | 6960 | 2.75 | 1 | 2.75 | 1
215 | Classroom | 297 | 19 |  | 870 | 19 | 19 | Univent | 6960 | 2.5603 | 1 | 2.5603 | 1
216 | Classroom | 286 | 19 |  | 870 | 19 | 19 | Univent | 6960 | 2.4655 | 1 | 2.4655 | 1
217 | Classroom | 392 | 26 |  | 896 | 20 | 20 | Univent | 7168 | 3.2812 | 1 | 3.2812 | 1
218 | Classroom | 296 | 19 |  | 870 | 19 | 19 | Univent | 6960 | 2.5517 | 1 | 2.5517 | 1
219 | Classroom | 307 | 20 |  | 870 | 19 | 19 | Univent | 6960 | 2.6466 | 1 | 2.6466 | 1
220 | Classroom | 235 | 15 |  | 870 | 19 | 15 | Univent | 6960 | 2.0259 | 1 | 2.0259 | 1
221 | Classroom | 293 | 19 |  | 870 | 19 | 19 | Univent | 6960 | 2.5259 | 1 | 2.5259 | 1
222 | Classroom | 312 | 20 |  | 783 | 17 | 17 | Univent | 6264 | 2.9885 | 1 | 2.9885 | 1
223 | Classroom | 238 | 15 |  | 870 | 19 | 15 | Univent | 6960 | 2.0517 | 1 | 2.0517 | 1
224 | Classroom | 300 | 20 |  | 870 | 19 | 19 | Univent | 6960 | 2.5862 | 1 | 2.5862 | 1
226 | Classroom | 365 | 24 |  | 942 | 21 | 21 | Univent | 7536 | 2.9061 | 1 | 2.9061 | 1
226A | - |  | 0 | Yes | 269 | 6 | 6 |  | 2152 | unk | unk | 20 | 3
228 | Classroom | 364 | 24 |  | 942 | 21 | 21 | Univent | 7536 | 2.8981 | 1 | 2.8981 | 1
228A | - |  | 0 | Yes | 269 | 6 | 6 |  | 2152 | unk | unk | 20 | 3
- | Art room | 642 | 42 |  | 1800 | 40 | 40 | Univent | 14400 | 2.675 | 1 | 2.675 | 1
| Art Room B |  | 0 |  | 260 | 5 | 0 |  | 2080 | unk | unk | unk | unk
- | Cafeteria/Theatre | 0 | 0 | Yes | 5280 | 120 | 120 | Air Handling Unit | 42240 | 0 | 0 | 20 | 3
| ESOL Suite |  | 0 | Yes | 119 | 2 | 2 |  | 952 | unk | unk | 20 | 3
- | Community Room | 239 | 15 |  | 839 | 19 | 15 | Univent | 6712 | 2.1365 | 1 | 2.1365 | 1
- | Gym | 0 | 0 |  | 5016 | 114 | 0 | Air Handling Unit | 40128 | 0 | 0 | 0 | 0
- | Gym Offices | 0 | 0 | Yes | 200 | 4 | 4 | Air Handling Unit | 1600 | 0 | 0 | 20 | 3
- | Kitchen | 273 | 18 |  | 1332 | 30 | 18 | Air Handling Unit | 10656 | 1.5372 | 1 | 1.5372 | 1
- | Library | 5562 | 370 |  | 1944 | 44 | 44 | Air Handling Unit | 15552 | 21.4583 | 3 | 21.4583 | 3
Counselor | Office |  | 0 | Yes | 261 | 5 | 5 |  | 2088 | unk | unk | 20 | 3
- | Main Office | 1418 | 94 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | 5.9083 | 2 | 5.9083 | 2
- | Faculty lounge |  | 0 |  | 840 | 19 | 0 |  | 6720 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Powel/SLAMS Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Capital Retest 3-31-2021 | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Report Classroom ID / Area ID Number | Posted Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room |  | unk | unk | unk | unk
26 | 26 | Electrical room |  | 0 |  | 502 | 11 | 0 |  | unk | unk | unk | unk
21 | 21 | Lockers | 98 | 6 |  | 114 | 2 | 2 |  | unk | unk | unk | unk
23 | 23 | Lockers | 101 | 6 |  | 149 | 3 | 3 |  | unk | unk | unk | unk
17 | 17 | Storage | 203 | 13 |  | 330 | 7 | 7 |  | unk | unk | unk | unk
18 | 18 | Workshop | 362 | 24 |  | 305 | 6 | 6 |  | unk | unk | unk | unk
103 | 101 | Cafeteria | 3580 | 238 |  | 3579 | 81 | 81 |  | unk | unk | unk | unk
104 | - | Corridor | 498 | 33 |  | 977 | 22 | 22 |  | unk | unk | unk | unk
105 | 100 | Waiting Area | 241 | 16 |  | 404 | 9 | 9 |  | unk | unk | unk | unk
112 | 100A | Conselor's Office | 15 | 1 |  | 104 | 2 | 1 |  | unk | unk | unk | unk
113 | 100G | Office | 16 | 1 |  | 123 | 2 | 1 |  | unk | unk | unk | unk
114 | 100B | Dean's Office | 16 | 1 |  | 104 | 2 | 1 |  | unk | unk | unk | unk
115 | 100F | Records | 14 | 0 |  | 101 | 2 | 0 |  | unk | unk | unk | unk
115 | - | Open Office Space | 29 | 1 |  | 332 | 7 | 1 |  | unk | unk | unk | unk
116 | 100C | Principal's Office | 30 | 2 |  | 166 | 3 | 2 |  | unk | unk | unk | unk
118 | 100D | Conference Room | 67 | 4 |  | 186 | 4 | 4 |  | unk | unk | unk | unk
119 | 101F | Kitchen Storage | 36 | 2 |  | 152 | 3 | 2 |  | unk | unk | unk | unk
121 | 101E | Kitchen | 535 | 35 |  | 841 | 19 | 19 |  | unk | unk | unk | unk
123 | - | Servery | 270 | 18 |  | 486 | 11 | 11 |  | unk | unk | unk | unk
124 | 101B | Office | 33 | 2 |  | 91 | 2 | 2 |  | unk | unk | unk | unk
126 | - | Corridor | 251 | 16 |  | 2146 | 48 | 16 |  | unk | unk | unk | unk
127 | 102 | Kindergarten Classroom | 314 | 20 |  | 1023 | 23 | 20 |  | unk | unk | unk | unk
128 | 103 | Classroom | 302 | 20 |  | 853 | 19 | 19 |  | unk | unk | unk | unk
129 | 104 | Kindergarten Classroom | 317 | 21 |  | 1022 | 23 | 21 |  | unk | unk | unk | unk
130 | 105 | Classroom | 318 | 21 |  | 851 | 19 | 19 |  | unk | unk | unk | unk
131 | 106 | Kindergarten Classroom | 321 | 21 |  | 1022 | 23 | 21 |  | unk | unk | unk | unk
132 | 107 | Classroom | 322 | 21 |  | 853 | 19 | 19 |  | unk | unk | unk | unk
133 | 108 | Special Education Classroom | 147 | 9 |  | 378 | 8 | 8 |  | unk | unk | unk | unk
134 | 109 | Classroom | 314 | 20 |  | 853 | 19 | 19 |  | unk | unk | unk | unk
135 | 110 | Classroom | 326 | 21 |  | 852 | 19 | 19 |  | unk | unk | unk | unk
136 | 111 | Classroom | 322 | 21 |  | 853 | 19 | 19 |  | unk | unk | unk | unk
137 | 112 | Classroom | 323 | 21 |  | 842 | 19 | 19 |  | unk | unk | unk | unk
138 | 113 | Classroom | 310 | 20 |  | 842 | 19 | 19 |  | unk | unk | unk | unk
139 | 114 | Classroom | 317 | 21 |  | 844 | 19 | 19 |  | unk | unk | unk | unk
140 | 115 | Classroom | 318 | 21 |  | 844 | 19 | 19 |  | unk | unk | unk | unk
141 | 116 | Classroom | 325 | 21 |  | 851 | 19 | 19 |  | unk | unk | unk | unk
142 | 117 | Classroom | 313 | 20 |  | 853 | 19 | 19 |  | unk | unk | unk | unk
143 | 118 | Special Education Classroom | 151 | 10 |  | 388 | 8 | 8 |  | unk | unk | unk | unk
145 | 119 | Library | 546 | 36 |  | 1712 | 38 | 36 |  | unk | unk | unk | unk
146 | 119B | Conference Room | 32 | 2 |  | 261 | 5 | 2 |  | unk | unk | unk | unk
147 | 119A | Work Room | 19 | 1 |  | 270 | 6 | 1 |  | unk | unk | unk | unk
148 | 120/121 | Art Classroom | 379 | 25 |  | 956 | 21 | 21 |  | unk | unk | unk | unk
149 | 120A | Art Storage Room | 50 | 3 |  | 61 | 1 | 1 |  | unk | unk | unk | unk
150 | 121/123 | Music Classroom | 200 | 13 |  | 1083 | 24 | 13 |  | unk | unk | unk | unk
152 | 123A | Music Studio | 53 | 3 |  | 237 | 5 | 3 |  | unk | unk | unk | unk
161 | - | Lobby | 208 | 13 |  | 475 | 10 | 10 |  | unk | unk | unk | unk
162 | 122 | Gym | 4453 | 296 |  | 5236 | 119 | 119 |  | unk | unk | unk | unk
163 | 125A | Office | 55 | 3 |  | 161 | 3 | 3 |  | unk | unk | unk | unk
164 | 125B | Storage | 35 | 2 |  | 141 | 3 | 2 |  | unk | unk | unk | unk
167 | - | Small Group | 1288 | 85 |  | 963 | 21 | 21 |  | unk | unk | unk | unk
168 | - | Open Space/Corridor | 196 | 13 |  | 324 | 7 | 7 |  | unk | unk | unk | unk
201 | - | Corridor | 472 | 31 |  | 563 | 12 | 12 |  | unk | unk | unk | unk
212 | 200A | Conselor's Office | 22 | 1 |  | 104 | 2 | 1 |  | unk | unk | unk | unk
214 | 200B | Principal's Office | 33 | 2 |  | 166 | 3 | 2 |  | unk | unk | unk | unk
216 | 200C | Conference Room | 65 | 4 |  | 189 | 4 | 4 |  | unk | unk | unk | unk
217 | 200D | Small Meeting Room | 20 | 1 |  | 96 | 2 | 1 |  | unk | unk | unk | unk
218 | 200E | Small Meeting Room | 20 | 1 |  | 96 | 2 | 1 |  | unk | unk | unk | unk
219 | 200F | Records | 8 | 0 |  | 180 | 4 | 0 |  | unk | unk | unk | unk
202 | 201 | Nurse's Suite | 23 | 1 |  | 221 | 5 | 1 |  | unk | unk | unk | unk
203 | 201D | Exam Room | 12 | 0 |  | 81 | 1 | 0 |  | unk | unk | unk | unk
204 | 201A | Exam Room | 13 | 0 |  | 102 | 2 | 0 |  | unk | unk | unk | unk
205 | 200 | Waiting Area | 161 | 10 |  | 359 | 8 | 8 |  | unk | unk | unk | unk
213 | 201E | Building Storage | 44 | 2 |  | 494 | 11 | 2 |  | unk | unk | unk | unk
215 | - | Open Office | 121 | 8 |  | 1263 | 28 | 8 |  | unk | unk | unk | unk
220 | - | Corridor | 11 | 0 |  | 266 | 6 | 0 |  | unk | unk | unk | unk
221 | 201H | Faculty Lounge | 126 | 8 |  | 419 | 9 | 8 |  | unk | unk | unk | unk
226 | - | Corridor | 233 | 15 |  | 3096 | 70 | 15 |  | unk | unk | unk | unk
227 | 202 | Classroom | 421 | 28 |  | 858 | 19 | 19 |  | unk | unk | unk | unk
228 | 203 | Classroom | 446 | 29 |  | 860 | 19 | 19 |  | unk | unk | unk | unk
229 | 204 | Classroom | 427 | 28 |  | 856 | 19 | 19 |  | unk | unk | unk | unk
230 | 205 | Classroom | 416 | 27 |  | 858 | 19 | 19 |  | unk | unk | unk | unk
231 | 206 | Classroom | 426 | 28 |  | 858 | 19 | 19 |  | unk | unk | unk | unk
232 | 207 | Classroom | 417 | 27 |  | 860 | 19 | 19 |  | unk | unk | unk | unk
233 | 208 | Special Education Classroom | 195 | 13 |  | 377 | 8 | 8 |  | unk | unk | unk | unk
234 | 209 | Classroom | 438 | 29 |  | 860 | 19 | 19 |  | unk | unk | unk | unk
235 | 210 | Art Classroom | 494 | 32 |  | 1235 | 28 | 28 |  | unk | unk | unk | unk
237 | 210A | Storage | 18 | 1 |  | 48 | 1 | 1 |  | unk | unk | unk | unk
239 | 210B | Storage | 33 | 2 |  | 113 | 2 | 2 |  | unk | unk | unk | unk
236 | 211 | Classroom | 435 | 29 |  | 860 | 19 | 19 |  | unk | unk | unk | unk
241 | 212 | Classroom | 450 | 30 |  | 852 | 19 | 19 |  | unk | unk | unk | unk
238 | 213 | Classroom | 425 | 28 |  | 851 | 19 | 19 |  | unk | unk | unk | unk
243 | 214 | Classroom | 447 | 29 |  | 859 | 19 | 19 |  | unk | unk | unk | unk
240 | 215 | Classroom | 456 | 30 |  | 852 | 19 | 19 |  | unk | unk | unk | unk
244 | 216 | Small Group Classroom | 119 | 7 |  | 388 | 8 | 7 |  | unk | unk | unk | unk
242 | 217 | Pre-Eng. Classroom | 417 | 27 |  | 860 | 19 | 19 |  | unk | unk | unk | unk
245 | 219 | Makerspace | 677 | 45 |  | 165 | 3 | 3 |  | unk | unk | unk | unk
248 | 220 | Science Classroom | 1385 | 92 |  | 1289 | 29 | 29 |  | unk | unk | unk | unk
249 | 220B | Prep Room | 739 | 49 |  | 403 | 9 | 9 |  | unk | unk | unk | unk
250 | 221 | Classroom | 1356 | 90 |  | 1285 | 29 | 29 |  | unk | unk | unk | unk
256 | 221C | Storage | 0 | 0 |  | 50 | 1 | 0 |  | unk | unk | unk | unk
253 | 221C | Room | 489 | 32 |  | 632 | 14 | 14 |  | unk | unk | unk | unk
254 | 225 | Office | 50 | 3 |  | 173 | 3 | 3 |  | unk | unk | unk | unk
266 | - | West Hallway | 208 | 13 |  | 779 | 17 | 13 |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-31 | [8 empty] | unk | unk | unk | unk
School: | Anna B. Pratt Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Capital | Devine ABR | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
106 | Classroom / Swing Space | 597 | 39 |  | 936 | 21 | 21 | Univent | 7488 | 4.7837 | 2 | 4.7837 | 2
109 | Classroom | 651 | 43 |  | 936 | 21 | 21 | Univent | 7488 | 5.2163 | 2 | 5.2163 | 2
110 | Classroom | 327 | 21 |  | 936 | 21 | 21 | Univent | 7488 | 2.6202 | 1 | 2.6202 | 1
111 | Classroom | 320 | 21 |  | 936 | 21 | 21 | Univent | 7488 | 2.5641 | 1 | 2.5641 | 1
112 | Classroom | 393 | 26 |  | 936 | 21 | 21 | Univent | 7488 | 3.149 | 1 | 3.149 | 1
113 | Special Education | 453 | 30 |  | 936 | 21 | 21 | Univent | 7488 | 3.6298 | 1 | 3.6298 | 1
114 | Classroom | 442 | 29 |  | 936 | 21 | 21 | Univent | 7488 | 3.5417 | 1 | 3.5417 | 1
201 | Classroom / Swing Space | 473 | 31 |  | 936 | 21 | 21 | Univent | 7488 | 3.7901 | 1 | 3.7901 | 1
200 / 202 | Library | 776 | 51 |  | 1848 | 42 | 42 | Univent | 14784 | 3.1494 | 1 | 3.1494 | 1
208 | Classroom | 367 | 24 |  | 936 | 21 | 21 | Univent | 7488 | 2.9407 | 1 | 2.9407 | 1
209 | Classroom | 489 | 32 |  | 936 | 21 | 21 | Univent | 7488 | 3.9183 | 1 | 3.9183 | 1
210 | Technology Classroom | 422 | 28 |  | 936 | 21 | 21 | Univent | 7488 | 3.3814 | 1 | 3.3814 | 1
211 | Classroom | 313 | 20 |  | 936 | 21 | 20 | Univent | 7488 | 2.508 | 1 | 2.508 | 1
212 | Classroom | 526 | 35 |  | 936 | 21 | 21 | Univent | 7488 | 4.2147 | 2 | 4.2147 | 2
213 | Classroom | 468 | 31 |  | 936 | 21 | 21 | Univent | 7488 | 3.75 | 1 | 3.75 | 1
214 | Data Room | 433 | 28 |  | 399 | 9 | 9 | Univent | 3192 | 8.1391 | 2 | 8.1391 | 2
301 | Music Room | 327 | 21 |  | 936 | 21 | 21 | Univent | 7488 | 2.6202 | 1 | 2.6202 | 1
302 | Classroom | 311 | 20 |  | 936 | 21 | 20 | Univent | 7488 | 2.492 | 1 | 2.492 | 1
308 | Classroom | 386 | 25 |  | 936 | 21 | 21 | Univent | 7488 | 3.0929 | 1 | 3.0929 | 1
309 | Special Education | 459 | 30 |  | 936 | 21 | 21 | Univent | 7488 | 3.6779 | 1 | 3.6779 | 1
310 | Special Education | 447 | 29 |  | 936 | 21 | 21 | Univent | 7488 | 3.5817 | 1 | 3.5817 | 1
311 | Classroom | 430 | 28 |  | 936 | 21 | 21 | Univent | 7488 | 3.4455 | 1 | 3.4455 | 1
312 | Classroom | 615 | 41 |  | 936 | 21 | 21 | Univent | 7488 | 4.9279 | 2 | 4.9279 | 2
313 | Classroom | 330 | 22 |  | 936 | 21 | 21 | Univent | 7488 | 2.6442 | 1 | 2.6442 | 1
314 | Classroom | 522 | 34 |  | 936 | 21 | 21 | Univent | 7488 | 4.1827 | 2 | 4.1827 | 2
315 | Staff Room | 361 | 24 |  | 399 | 9 | 9 | Univent | 3192 | 6.7857 | 2 | 6.7857 | 2
- | Main Office |  | 0 | Yes | 352 | 8 | 8 |  | 2816 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 228 | 5 | 5 |  | 1824 | unk | unk | 20 | 3
- | AS Office |  | 0 | Yes | 192 | 4 | 4 |  | 1536 | unk | unk | 20 | 3
- | Nurses Office |  | 0 | Yes | 156 | 3 | 3 |  | 1248 | unk | unk | 20 | 3
- | Climate Office |  | 0 | Yes | 156 | 3 | 3 |  | 1248 | unk | unk | 20 | 3
- | Counselors Office |  | 0 | Yes | 156 | 3 | 3 |  | 1248 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Prince Hall Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Retest | Gymnasium | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
1 | Classroom | 380 | 25 |  | 1200 | 27 | 25 | Univent | 9600 | 2.375 | 1 | 2.375 | 1
2 | Classroom | 321 | 21 |  | 1200 | 27 | 21 | Univent | 9600 | 2.0063 | 1 | 2.0063 | 1
3 | Classroom | 387 | 25 |  | 1200 | 27 | 25 | Univent | 9600 | 2.4188 | 1 | 2.4188 | 1
4 | Classroom | 304 | 20 |  | 1200 | 27 | 20 | Univent | 9600 | 1.9 | 1 | 1.9 | 1
5 | Classroom | 313 | 20 |  | 900 | 20 | 20 | Univent | 7200 | 2.6083 | 1 | 2.6083 | 1
6 | Classroom | 268 | 17 | Yes | 900 | 20 | 20 | Univent | 7200 | 2.2333 | 1 | 22.2333 | 3
7 | Classroom | 351 | 23 |  | 836 | 19 | 19 | Univent | 6688 | 3.1489 | 1 | 3.1489 | 1
8 | Classroom | 334 | 22 |  | 874 | 19 | 19 | Univent | 6992 | 2.8661 | 1 | 2.8661 | 1
9 | Classroom | 235 | 15 | Yes | 1050 | 23 | 23 | Univent | 8400 | 1.6786 | 1 | 21.6786 | 3
10 | Classroom | 375 | 25 |  | 888 | 20 | 20 | Univent | 7104 | 3.1672 | 1 | 3.1672 | 1
11 | Classroom | 242 | 16 | Yes | 1066 | 24 | 24 | Univent | 8528 | 1.7026 | 1 | 21.7026 | 3
12 | Classroom | 234 | 15 | Yes | 1134 | 25 | 25 | Univent | 9072 | 1.5476 | 1 | 21.5476 | 3
13 | Classroom | 227 | 15 | Yes | 1100 | 25 | 25 | Univent | 8800 | 1.5477 | 1 | 21.5477 | 3
103 | Classroom | 601 | 40 |  | 1280 | 29 | 29 | Univent | 10240 | 3.5215 | 1 | 3.5215 | 1
104 | Classroom | 696 | 46 |  | 1280 | 29 | 29 | Univent | 10240 | 4.0781 | 2 | 4.0781 | 2
105 | Classroom | 664 | 44 |  | 1360 | 30 | 30 | Univent | 10880 | 3.6618 | 1 | 3.6618 | 1
106 | Classroom | 739 | 49 |  | 1280 | 29 | 29 | Univent | 10240 | 4.3301 | 2 | 4.3301 | 2
112 | Classroom |  | 0 | Yes | 1360 | 30 | 30 |  | 10880 | unk | unk | 20 | 3
116 | Classroom | 279 | 18 |  | 400 | 9 | 9 | Univent | 3200 | 5.2313 | 2 | 5.2313 | 2
117 | Classroom | 322 | 21 |  | 700 | 15 | 15 | Univent | 5600 | 3.45 | 1 | 3.45 | 1
201 | Classroom | 418 | 27 |  | 1200 | 27 | 27 | Univent | 9600 | 2.6125 | 1 | 2.6125 | 1
202 | Classroom | 292 | 19 | Yes | 1200 | 27 | 27 | Univent | 9600 | 1.825 | 1 | 21.825 | 3
203 | Classroom | 311 | 20 |  | 1200 | 27 | 20 | Univent | 9600 | 1.9438 | 1 | 1.9438 | 1
204 | Classroom | 259 | 17 | Yes | 1200 | 27 | 27 | Univent | 9600 | 1.6187 | 1 | 21.6187 | 3
205 | Classroom | 377 | 25 |  | 900 | 20 | 20 | Univent | 7200 | 3.1417 | 1 | 3.1417 | 1
206 | Classroom | 338 | 22 |  | 900 | 20 | 20 | Univent | 7200 | 2.8167 | 1 | 2.8167 | 1
207 | Classroom | 238 | 15 |  | 836 | 19 | 15 | Univent | 6688 | 2.1352 | 1 | 2.1352 | 1
208 | Classroom | 312 | 20 |  | 874 | 19 | 19 | Univent | 6992 | 2.6773 | 1 | 2.6773 | 1
209 | Classroom | 244 | 16 | Yes | 1050 | 23 | 23 | Univent | 8400 | 1.7429 | 1 | 21.7429 | 3
210 | Classroom | 240 | 16 |  | 888 | 20 | 16 | Univent | 7104 | 2.027 | 1 | 2.027 | 1
211 | Classroom | 263 | 17 |  | 1066 | 24 | 17 | Univent | 8528 | 1.8504 | 1 | 1.8504 | 1
212 | Classroom | 332 | 22 |  | 1170 | 26 | 22 | Univent | 9360 | 2.1282 | 1 | 2.1282 | 1
213 | Classroom | 614 | 40 |  | 988 | 22 | 22 | Univent | 7904 | 4.6609 | 2 | 4.6609 | 2
- | AUDITORIUM | 1185 | 79 |  | 3363 | 76 | 76 | Air Handling Unit | 26904 | 2.6427 | 1 | 2.6427 | 1
- | Admin. Main Office | 56 | 3 |  | 255 | 5 | 3 | Univent | 2040 | 1.6471 | 1 | 1.6471 | 1
- | Admin. Office | 28 | 1 |  | 126 | 2 | 1 | Univent | 1008 | 1.6667 | 1 | 1.6667 | 1
- | Main Office | 301 | 20 |  | 720 | 16 | 16 | Univent | 5760 | 3.1354 | 1 | 3.1354 | 1
- | Principal's Office |  | 0 | Yes | 255 | 5 | 5 |  | 2040 | unk | unk | 20 | 3
- | Copy Room Office | 16 | 1 |  | 98 | 2 | 1 | Univent | 784 | 1.2245 | 1 | 1.2245 | 1
- | Counselor's Office | 107 | 7 |  | 416 | 9 | 7 | Univent | 3328 | 1.9291 | 1 | 1.9291 | 1
- | Computer Room Classroom | 380 | 25 |  | 1600 | 36 | 25 | Univent | 12800 | 1.7812 | 1 | 1.7812 | 1
- | IMC Classroom | 1021 | 68 |  | 4335 | 98 | 68 | Univent | 34680 | 1.7664 | 1 | 1.7664 | 1
- | Gym | 0 | 0 |  | 4800 | 109 | 0 | Air Handling Unit | 38400 | 0 | 0 | 0 | 0
- | Gym Locker Rooms | 335 | 22 |  | 403 | 9 | 9 | Air Handling Unit | 3224 | 6.2345 | 2 | 6.2345 | 2
- | Main Entrance | 68 | 4 |  | 150 | 3 | 3 | Univent | 1200 | 3.4 | 1 | 3.4 | 1
- | Multi-Purpose/Cafe | 2016 | 134 |  | 2760 | 62 | 62 | Air Handling Unit | 22080 | 5.4783 | 2 | 5.4783 | 2
- | Nurse's Office 1 | 50 | 3 |  | 90 | 2 | 2 | Univent | 720 | 4.1667 | 2 | 4.1667 | 2
- | Nurse's Office 2 | 40 | 2 |  | 110 | 2 | 2 | Univent | 880 | 2.7273 | 1 | 2.7273 | 1
- | Nurse's Office | 71 | 4 | Yes | 160 | 3 | 3 | Univent | 1280 | 3.3281 | 1 | 23.3281 | 3
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | A. Philip Randolph Career and Technical High School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
20 | Classroom | 1172 | 78 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
21 | Classroom | 1124 | 74 |  | 600 | 13 | 13 | Air Coil Unit | 4800 | 14.05 | 3 | 14.05 | 3
23 | Classroom | 1177 | 78 |  | 720 | 16 | 16 | Air Coil Unit | 5760 | 12.2604 | 3 | 12.2604 | 3
24 | Classroom | 889 | 59 |  | 792 | 18 | 18 | Air Coil Unit | 6336 | 8.4186 | 2 | 8.4186 | 2
36 | Classroom | 93 | 6 |  |  | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
37 | Classroom | 176 | 11 |  | 704 | 16 | 11 | Rooftop Unit | 5632 | 1.875 | 1 | 1.875 | 1
38 | DENTAL SHOP | 236 | 15 |  | 1596 | 36 | 15 | Rooftop Unit | 12768 | 1.109 | 1 | 1.109 | 1
38 | DENTAL IMAGE ROOM | 8 | 0 |  |  | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
38 | DENTAL X-RAY ROOM | 12 | 0 |  |  | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
39 | Classroom | 73 | 4 |  |  | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
50 | Art Room | 694 | 46 |  | 1008 | 22 | 22 | Air Coil Unit | 8064 | 5.1637 | 2 | 5.1637 | 2
51 | Classroom | 199 | 13 |  | 510 | 11 | 11 | Air Coil Unit | 4080 | 2.9265 | 1 | 2.9265 | 1
52 | Classroom | 435 | 29 |  | 420 | 9 | 9 | Air Coil Unit | 3360 | 7.7679 | 2 | 7.7679 | 2
53 | Classroom | 483 | 32 |  | 612 | 13 | 13 | Air Coil Unit | 4896 | 5.9191 | 2 | 5.9191 | 2
54 | Classroom | 784 | 52 |  | 798 | 18 | 18 | Air Coil Unit | 6384 | 7.3684 | 2 | 7.3684 | 2
55 | Classroom | 149 | 9 |  | 660 | 15 | 9 | Air Coil Unit | 5280 | 1.6932 | 1 | 1.6932 | 1
56 | Classroom | 570 | 38 |  | 1190 | 27 | 27 | Air Coil Unit | 9520 | 3.5924 | 1 | 3.5924 | 1
57 | Classroom | 505 | 33 |  | 522 | 11 | 11 | Air Coil Unit | 4176 | 7.2557 | 2 | 7.2557 | 2
71 | Room | 262 | 17 |  | 480 | 10 | 10 | Air Coil Unit | 3840 | 4.0938 | 2 | 4.0938 | 2
72 | Room | 289 | 19 |  | 510 | 11 | 11 | Air Coil Unit | 4080 | 4.25 | 2 | 4.25 | 2
73 | Classroom | 0 | 0 |  | 616 | 14 | 0 | Air Coil Unit | 4928 | 0 | 0 | 0 | 0
74 | Room | 0 | 0 |  | 572 | 13 | 0 | Air Coil Unit | 4576 | 0 | 0 | 0 | 0
75 | Classroom | 0 | 0 |  | 660 | 15 | 0 | Air Coil Unit | 5280 | 0 | 0 | 0 | 0
76 | Classroom | 0 | 0 |  | 600 | 13 | 0 | Air Coil Unit | 4800 | 0 | 0 | 0 | 0
94 | Room | 88 | 5 |  | 72 | 1 | 1 | Air Coil Unit | 576 | 9.1667 | 2 | 9.1667 | 2
100 | Classroom | 197 | 13 |  | 396 | 9 | 9 | Air Coil Unit | 3168 | 3.7311 | 1 | 3.7311 | 1
- | Automotive | 80 | 5 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
- | AV storage | 96 | 6 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
- | BEHAVIORAL THERAPIST OFFICE | 26 | 1 |  |  | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
- | Boys Bathroom | 0 | 0 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
- | Break Room | 168 | 11 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
- | CAFETERIA | 2027 | 135 |  | 3828 | 87 | 87 | Rooftop Unit | 30624 | 3.9714 | 1 | 3.9714 | 1
- | Cafeteria | 2027 | 135 |  | 704 | 16 | 16 | Air Coil Unit | 5632 | 21.5945 | 3 | 21.5945 | 3
- | Classrooms | 392 | 26 |  | 600 | 13 | 13 | Air Coil Unit | 4800 | 4.9 | 2 | 4.9 | 2
- | Classrooms | 5734 | 382 |  | 720 | 16 | 16 | Air Coil Unit | 5760 | 59.7292 | 5 | 59.7292 | 5
- | Classrooms | 4521 | 301 |  | 792 | 18 | 18 | Air Coil Unit | 6336 | 42.8125 | 4 | 42.8125 | 4
- | Classrooms | 0 | 0 |  | 572 | 13 | 0 | Air Coil Unit | 4576 | 0 | 0 | 0 | 0
- | COUNSELORS OFFICE | 19 | 1 |  |  | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
- | Engineers Office | 238 | 15 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
- | Girls Bathroom | 0 | 0 |  | 200 | 4 | 0 | Air Coil Unit | 1600 | 0 | 0 | 0 | 0
- | Hallway | 245 | 16 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
- | IMC side area | 657 | 43 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
- | IMC area | 118 | 7 |  | 1664 | 37 | 7 | Air Coil Unit | 13312 | 0.53185 | 0 | 0.53185 | 0
- | INSPECTORS OFFICE | 0 | 0 |  |  | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
- | IT ROOM | 40 | 2 |  |  | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
- | kitchen | 1766 | 117 |  | 722 | 16 | 16 | Air Coil Unit | 5776 | 18.3449 | 3 | 18.3449 | 3
- | Kitchen | 3575 | 238 |  | 722 | 16 | 16 | Air Coil Unit | 5776 | 37.1364 | 4 | 37.1364 | 4
- | Kitchen Dining | 93 | 6 |  | 252 | 5 | 5 | Air Coil Unit | 2016 | 2.7679 | 1 | 2.7679 | 1
- | Library | 29 | 1 |  | 1664 | 37 | 1 | Air Coil Unit | 13312 | 0.13071 | 0 | 0.13071 | 0
- | MAIL ROOM | 50 | 3 |  | 384 | 8 | 3 | Rooftop Unit | 3072 | 0.97656 | 0 | 0.97656 | 0
- | MAIN OFFICE | 113 | 7 |  | 134 | 3 | 3 | Rooftop Unit | 1072 | 6.3246 | 2 | 6.3246 | 2
- | CONFERENCE ROOM | 23 | 1 |  | 247 | 5 | 1 | Rooftop Unit | 1976 | 0.69838 | 0 | 0.69838 | 0
Main office, classrooms | Main office, classrooms | 1328 | 88 |  | 285 | 6 | 6 | Air Coil Unit | 2280 | 34.9474 | 4 | 34.9474 | 4
- | Ms. SMALLEY OFFICE | 7 | 0 |  | 120 | 2 | 0 | Rooftop Unit | 960 | 0.4375 | 0 | 0.4375 | 0
- | NURSES OFFICE | 156 | 10 |  | 196 | 4 | 4 | Rooftop Unit | 1568 | 5.9694 | 2 | 5.9694 | 2
- | office next to electrical room | 136 | 9 |  | 140 | 3 | 3 | Air Coil Unit | 1120 | 7.2857 | 2 | 7.2857 | 2
office diffuser s1 | office | 223 | 14 |  | 140 | 3 | 3 | Air Coil Unit | 1120 | 11.9464 | 3 | 11.9464 | 3
- | kitchen office | 21 | 1 |  | 320 | 7 | 1 | Air Coil Unit | 2560 | 0.49219 | 0 | 0.49219 | 0
- | VP office | 0 | 0 |  | 130 | 2 | 0 | Air Coil Unit | 1040 | 0 | 0 | 0 | 0
office Diffuser S6 | office | 0 | 0 |  | 192 | 4 | 0 | Air Coil Unit | 1536 | 0 | 0 | 0 | 0
office Diffuser S1 | office | 0 | 0 |  | 320 | 7 | 0 | Air Coil Unit | 2560 | 0 | 0 | 0 | 0
office diffuser s18 | office | 78 | 5 |  | 120 | 2 | 2 | Air Coil Unit | 960 | 4.875 | 2 | 4.875 | 2
office diffuser s17 | office | 84 | 5 |  | 308 | 7 | 5 | Air Coil Unit | 2464 | 2.0455 | 1 | 2.0455 | 1
office diffuser s16 | office | 108 | 7 |  | 280 | 6 | 6 | Air Coil Unit | 2240 | 2.8929 | 1 | 2.8929 | 1
OFFICE IN BACK OF MAIN OFFICE | OFFICE IN BACK OF MAIN OFFICE | 0 | 0 |  | 110 | 2 | 0 | Rooftop Unit | 880 | 0 | 0 | 0 | 0
OFFICE NEXT TO RM 39 | OFFICE NEXT TO RM 39 | 23 | 1 |  | 216 | 4 | 1 | Rooftop Unit | 1728 | 0.79861 | 0 | 0.79861 | 0
- | Paint shop | 0 | 0 |  | 320 | 7 | 0 | H2-7 | 2560 | 0 | 0 | 0 | 0
- | Paint shop | 0 | 0 |  |  | 0 | 0 | H2-8 |  | unk | unk | unk | unk
PRINCIPLE OFFICE | PRINCIPLE OFFICE | 49 | 3 |  | 16 | 0 | 0 | Rooftop Unit | 128 | 22.9688 | 3 | 22.9688 | 3
security | office diffuser s4 | 180 | 12 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
- | Shop area | 408 | 27 |  |  | 0 | 0 | H2-5 |  | unk | unk | unk | unk
- | Shop area | 1346 | 89 |  |  | 0 | 0 | H1-4 |  | unk | unk | unk | unk
- | Shop area | 591 | 39 |  |  | 0 | 0 | H1-3 |  | unk | unk | unk | unk
- | Shop area | 450 | 30 |  |  | 0 | 0 | H4-14 |  | unk | unk | unk | unk
- | Shop area | 0 | 0 |  |  | 0 | 0 | H4-13 |  | unk | unk | unk | unk
- | Shop area | 0 | 0 |  |  | 0 | 0 | H4-12 |  | unk | unk | unk | unk
- | Shop area | 0 | 0 |  |  | 0 | 0 | H3-10 |  | unk | unk | unk | unk
- | Shop area | 0 | 0 |  |  | 0 | 0 | H3-11 |  | unk | unk | unk | unk
- | Shop Classrooms | 2065 | 137 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
- | SPEECH THERAPIST NEXT TO PRINCIPLE OFFICE | 60 | 4 |  |  | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
- | SPEECH THERAPIST OFFICE | 20 | 1 |  |  | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
storage diffuser s11 | storage | 53 | 3 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
storage diffuser s10 | storage | 192 | 12 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
storage diffuser s9 | storage | 170 | 11 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
storage diffuser s2 | storage | 120 | 8 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
storage diffuser s1 | storage | 115 | 7 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
storage diffuser S19 | storage | 0 | 0 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
storage diffuser S17 | storage | 0 | 0 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
storage diffuser S16 | storage | 0 | 0 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
Storage Diffuser S5 | Storage | 0 | 0 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
storage diffuser s6 | storage | 76 | 5 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
storage diffuser s4 | storage | 64 | 4 |  |  | 0 | 0 | Air Coil Unit |  | unk | unk | unk | unk
- | STORAGE ROOM IN MAIN OFFICE | 16 | 1 |  |  | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
teacher lounge diffuser S19 | teachers lounge | 37 | 2 |  | 572 | 13 | 2 | Air Coil Unit | 4576 | 0.48514 | 0 | 0.48514 | 0
- | TOM MCLAUGHLIN OFFICE | 29 | 1 |  | 572 | 13 | 1 | Rooftop Unit | 4576 | 0.38024 | 0 | 0.38024 | 0
- | vending machine shop | 0 | 0 |  |  | 0 | 0 | H1-1 |  | unk | unk | unk | unk
- | welding shop | 0 | 0 |  |  | 0 | 0 | H2-9 |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-07 | [8 empty] | unk | unk | unk | unk
School: | Rhawnhurst Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Part 2 | Part 3 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 301 | 20 |  | 1485 | 33 | 20 | Univent | 11880 | 1.5202 | 1 | 1.5202 | 1
101 | Classroom | 341 | 22 |  | 1056 | 24 | 22 | Univent | 8448 | 2.4219 | 1 | 2.4219 | 1
102 | Classroom | 296 | 19 |  | 1056 | 24 | 19 | Univent | 8448 | 2.1023 | 1 | 2.1023 | 1
102B | Office |  | 0 | Yes | 110 | 2 | 2 | Univent | 880 | unk | unk | 20 | 3
103 | Classroom | 297 | 19 |  | 1056 | 24 | 19 | Univent | 8448 | 2.1094 | 1 | 2.1094 | 1
104 | Classroom | 335 | 22 |  | 1056 | 24 | 22 | Univent | 8448 | 2.3793 | 1 | 2.3793 | 1
105 | Classroom | 307 | 20 |  | 1073 | 24 | 20 | Univent | 8584 | 2.1459 | 1 | 2.1459 | 1
106 | Classroom | 624 | 41 |  | 1020 | 23 | 23 | Univent | 8160 | 4.5882 | 2 | 4.5882 | 2
107 | Classroom | 321 | 21 |  | 1056 | 24 | 21 | Univent | 8448 | 2.2798 | 1 | 2.2798 | 1
108 | Classroom | 313 | 20 |  | 1056 | 24 | 20 | Univent | 8448 | 2.223 | 1 | 2.223 | 1
109 | Classroom | 302 | 20 |  | 1056 | 24 | 20 | Univent | 8448 | 2.1449 | 1 | 2.1449 | 1
110 | Classroom | 301 | 20 |  | 1056 | 24 | 20 | Univent | 8448 | 2.1378 | 1 | 2.1378 | 1
200 | Classroom | 520 | 34 |  | 1056 | 24 | 24 | Univent | 8448 | 3.6932 | 1 | 3.6932 | 1
201 | Classroom | 259 | 17 |  | 1056 | 24 | 17 | Univent | 8448 | 1.8395 | 1 | 1.8395 | 1
202 | Classroom | 306 | 20 |  | 1056 | 24 | 20 | Univent | 8448 | 2.1733 | 1 | 2.1733 | 1
203 | Classroom | 586 | 39 |  | 1056 | 24 | 24 | Univent | 8448 | 4.1619 | 2 | 4.1619 | 2
203A | Office |  | 0 | Yes | 275 | 6 | 6 | Univent | 2200 | unk | unk | 20 | 3
203B | Office |  | 0 | Yes | 198 | 4 | 4 | Univent | 1584 | unk | unk | 20 | 3
204 | Classroom | 452 | 30 |  | 1056 | 24 | 24 | Univent | 8448 | 3.2102 | 1 | 3.2102 | 1
Annex 301 | Classroom | 246 | 16 |  | 792 | 18 | 16 | Univent | 6336 | 2.3295 | 1 | 2.3295 | 1
Annex 302 | Classroom | 291 | 19 |  | 792 | 18 | 18 | Univent | 6336 | 2.7557 | 1 | 2.7557 | 1
Annex 303 | Classroom | 303 | 20 |  | 792 | 18 | 18 | Univent | 6336 | 2.8693 | 1 | 2.8693 | 1
Annex 304 | Classroom | 198 | 13 | Yes | 792 | 18 | 18 | Univent | 6336 | 1.875 | 1 | 21.875 | 3
Annex 305 | Classroom | 248 | 16 |  | 792 | 18 | 16 | Univent | 6336 | 2.3485 | 1 | 2.3485 | 1
Annex 306 | Classroom | 216 | 14 | Yes | 792 | 18 | 18 | Univent | 6336 | 2.0455 | 1 | 22.0455 | 3
- | Main Office |  | 0 | Yes | 240 | 5 | 5 | Univent | 1920 | unk | unk | 20 | 3
Principal | Office |  | 0 | Yes | 264 | 6 | 6 | Univent | 2112 | unk | unk | 20 | 3
- | Nurses Office |  | 0 | Yes | 460 | 10 | 10 | Univent | 3680 | unk | unk | 20 | 3
- | Special Education Office |  | 0 | Yes | 360 | 8 | 8 | Univent | 2880 | unk | unk | 20 | 3
- | Counselor Office |  | 0 | Yes | 241 | 5 | 5 | Univent | 1928 | unk | unk | 20 | 3
- | Auditorium | 2049 | 136 |  | 3431 | 77 | 77 | Air Handling Unit | 27448 | 4.479 | 2 | 4.479 | 2
- | Cafeteria | 362 | 24 |  | 2814 | 63 | 24 | Univent | 22512 | 0.96482 | 0 | 0.96482 | 0
- | Gym | 116 | 7 |  | 3969 | 90 | 7 | Air Handling Unit | 31752 | 0.2192 | 0 | 0.2192 | 0
- | Library | 140 | 9 | Yes | 1134 | 25 | 25 | Univent | 9072 | 0.92593 | 0 | 20.9259 | 3
- | Trailer | 286 | 19 |  | 649 | 14 | 14 | Air Handling Unit | 5192 | 3.3051 | 1 | 3.3051 | 1
A1 | Annex | 75 | 5 |  | 792 | 18 | 5 | Univent | 6336 | 0.71023 | 0 | 0.71023 | 0
A2 | Annex | 95 | 6 |  | 792 | 18 | 6 | Univent | 6336 | 0.89962 | 0 | 0.89962 | 0
A3 | Annex | 54 | 3 |  | 792 | 18 | 3 | Univent | 6336 | 0.51136 | 0 | 0.51136 | 0
A4 | Annex | 62 | 4 |  | 792 | 18 | 4 | Univent | 6336 | 0.58712 | 0 | 0.58712 | 0
A5 | Annex | 63 | 4 |  | 792 | 18 | 4 | Univent | 6336 | 0.59659 | 0 | 0.59659 | 0
A6 | Annex | 70 | 4 |  | 792 | 18 | 4 | Univent | 6336 | 0.66288 | 0 | 0.66288 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-15 | [8 empty] | unk | unk | unk | unk
School: | James Rhoads Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 122 | 8 |  | 552 | 12 | 8 | Univent | 4416 | 1.6576 | 1 | 1.6576 | 1
102 | Classroom | 87 | 5 | Yes | 968 | 22 | 22 | Univent | 7744 | 0.67407 | 0 | 20.6741 | 3
104 | Classroom | 136 | 9 | Yes | 968 | 22 | 22 | Univent | 7744 | 1.0537 | 1 | 21.0537 | 3
200 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0 | 0 | 0
201 | Classroom | 190 | 12 | Yes | 805 | 18 | 18 | Univent | 6440 | 1.7702 | 1 | 21.7702 | 3
202 | Classroom | 237 | 15 |  | 805 | 18 | 15 | Univent | 6440 | 2.2081 | 1 | 2.2081 | 1
203 | Classroom | 212 | 14 | Yes | 805 | 18 | 18 | Univent | 6440 | 1.9752 | 1 | 21.9752 | 3
204 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent | 6440 | 0 | 0 | 20 | 3
205 | Classroom | 162 | 10 | Yes | 805 | 18 | 18 | Univent | 6440 | 1.5093 | 1 | 21.5093 | 3
206 | Classroom | 201 | 13 | Yes | 805 | 18 | 18 | Univent | 6440 | 1.8727 | 1 | 21.8727 | 3
207 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0 | 0 | 0
208 | Classroom | 236 | 15 |  | 805 | 18 | 15 | Univent | 6440 | 2.1988 | 1 | 2.1988 | 1
209 | Classroom | 174 | 11 | Yes | 805 | 18 | 18 | Univent | 6440 | 1.6211 | 1 | 21.6211 | 3
210 | Classroom | 212 | 14 |  | 805 | 18 | 14 | Univent | 6440 | 1.9752 | 1 | 1.9752 | 1
300 | Classroom | 318 | 21 |  | 805 | 18 | 18 | Univent | 6440 | 2.9627 | 1 | 2.9627 | 1
301 | Classroom | 202 | 13 |  | 805 | 18 | 13 | Univent | 6440 | 1.882 | 1 | 1.882 | 1
302 | Classroom | 197 | 13 |  | 805 | 18 | 13 | Univent | 6440 | 1.8354 | 1 | 1.8354 | 1
303 | Classroom | 300 | 20 |  | 805 | 18 | 18 | Univent | 6440 | 2.795 | 1 | 2.795 | 1
304 | Classroom | 203 | 13 |  | 805 | 18 | 13 | Univent | 6440 | 1.8913 | 1 | 1.8913 | 1
305 | Classroom | 205 | 13 |  | 805 | 18 | 13 | Univent | 6440 | 1.9099 | 1 | 1.9099 | 1
306 | Classroom | 169 | 11 |  | 805 | 18 | 11 | Univent | 6440 | 1.5745 | 1 | 1.5745 | 1
307 | Classroom | 233 | 15 |  | 805 | 18 | 15 | Univent | 6440 | 2.1708 | 1 | 2.1708 | 1
308 | Classroom | 201 | 13 |  | 805 | 18 | 13 | Univent | 6440 | 1.8727 | 1 | 1.8727 | 1
309 | Classroom | 174 | 11 |  | 805 | 18 | 11 | Univent | 6440 | 1.6211 | 1 | 1.6211 | 1
310 | Classroom | 342 | 22 |  | 805 | 18 | 18 | Univent | 6440 | 3.1863 | 1 | 3.1863 | 1
400 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0 | 0 | 0
401 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0 | 0 | 0
402 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0 | 0 | 0
403 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0 | 0 | 0
404 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent | 6440 | 0 | 0 | 20 | 3
405 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent | 6440 | 0 | 0 | 20 | 3
406 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent | 6440 | 0 | 0 | 20 | 3
407 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent | 6440 | 0 | 0 | 20 | 3
408 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0 | 0 | 0
409 | Classroom | 0 | 0 | Yes | 805 | 18 | 18 | Univent | 6440 | 0 | 0 | 20 | 3
410 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0 | 0 | 0
- | Main Office |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 300 | 6 | 6 |  | 2400 | unk | unk | 20 | 3
- | Nurse Office |  | 0 | Yes | 120 | 2 | 2 |  | 960 | unk | unk | 20 | 3
- | Auditorium | 0 | 0 |  | 1800 | 40 | 0 | Air Handling Unit | 14400 | 0 | 0 | 0 | 0
- | Café/Gym | 0 | 0 |  | 6480 | 147 | 0 | Air Handling Unit | 51840 | 0 | 0 | 0 | 0
- | IMC | 0 | 0 |  | 897 | 20 | 0 | Univent | 7176 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-08 | [8 empty] | unk | unk | unk | unk
School: | E. Washington Rhodes Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | 1ST/2ND FLR A&B POD AREAS | 0 | 0 |  | 1829 | 41 | 0 | Air Handling Unit | 14632 | 0 | 0 | 0 | 0
- | 1ST/2ND FLR C&D POD AREAS | 0 | 0 |  | 1829 | 41 | 0 | Air Handling Unit | 14632 | 0 | 0 | 0 | 0
A1 | CLASSROOM | 365 | 24 |  | 850 | 19 | 19 | Univent | 6800 | 3.2206 | 1 | 3.2206 | 1
A2 | CLASSROOM | 326 | 21 |  | 850 | 19 | 19 | Univent | 6800 | 2.8765 | 1 | 2.8765 | 1
A3 | CLASSROOM | 0 | 0 |  | 850 | 19 | 0 | Univent | 6800 | 0 | 0 | 0 | 0
A4 | CLASSROOM | 0 | 0 |  | 1085 | 24 | 0 | Univent | 8680 | 0 | 0 | 0 | 0
A5 | CLASSROOM | 289 | 19 |  | 720 | 16 | 16 | Univent | 5760 | 3.0104 | 1 | 3.0104 | 1
A6 | CLASSROOM | 308 | 20 |  | 890 | 20 | 20 | Univent | 7120 | 2.5955 | 1 | 2.5955 | 1
A7 | CLASSROOM | 0 | 0 |  | 0 | 0 | 0 | Univent | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
A101 | CLASSROOM | 283 | 18 |  | 850 | 19 | 18 | Univent | 6800 | 2.4971 | 1 | 2.4971 | 1
A102 | CLASSROOM | 369 | 24 |  | 850 | 19 | 19 | Univent | 6800 | 3.2559 | 1 | 3.2559 | 1
A103 | CLASSROOM | 279 | 18 |  | 816 | 18 | 18 | Univent | 6528 | 2.5643 | 1 | 2.5643 | 1
A104 | CLASSROOM | 238 | 15 |  | 1120 | 25 | 15 | Univent | 8960 | 1.5938 | 1 | 1.5938 | 1
A105 | CLASSROOM | 296 | 19 |  | 744 | 16 | 16 | Univent | 5952 | 2.9839 | 1 | 2.9839 | 1
A106 | CLASSROOM | 227 | 15 |  | 1100 | 25 | 15 | Univent | 8800 | 1.5477 | 1 | 1.5477 | 1
B1 | CLASSROOM | 275 | 18 |  | 850 | 19 | 18 | Univent | 6800 | 2.4265 | 1 | 2.4265 | 1
B2 | CLASSROOM | 308 | 20 |  | 850 | 19 | 19 | Univent | 6800 | 2.7176 | 1 | 2.7176 | 1
B3 | CLASSROOM | 338 | 22 |  | 850 | 19 | 19 | Univent | 6800 | 2.9824 | 1 | 2.9824 | 1
B4 | CLASSROOM | 300 | 20 |  | 1085 | 24 | 20 | Univent | 8680 | 2.0737 | 1 | 2.0737 | 1
B5 | CLASSROOM | 233 | 15 |  | 720 | 16 | 15 | Univent | 5760 | 2.4271 | 1 | 2.4271 | 1
B6 | CLASSROOM | 296 | 19 |  | 890 | 20 | 19 | Univent | 7120 | 2.4944 | 1 | 2.4944 | 1
B101 | CLASSROOM | 237 | 15 |  | 850 | 19 | 15 | Univent | 6800 | 2.0912 | 1 | 2.0912 | 1
B102 | CLASSROOM | 325 | 21 |  | 850 | 19 | 19 | Univent | 6800 | 2.8676 | 1 | 2.8676 | 1
B103 | CLASSROOM | 275 | 18 |  | 816 | 18 | 18 | Univent | 6528 | 2.5276 | 1 | 2.5276 | 1
B104 | CLASSROOM | 307 | 20 |  | 1120 | 25 | 20 | Univent | 8960 | 2.0558 | 1 | 2.0558 | 1
B105 | CLASSROOM | 301 | 20 |  | 744 | 16 | 16 | Univent | 5952 | 3.0343 | 1 | 3.0343 | 1
B106 | CLASSROOM | 297 | 19 |  | 1100 | 25 | 19 | Univent | 8800 | 2.025 | 1 | 2.025 | 1
C1 | CLASSROOM | 297 | 19 |  | 850 | 19 | 19 | Univent | 6800 | 2.6206 | 1 | 2.6206 | 1
C2 | CLASSROOM | 0 | 0 | Yes | 850 | 19 | 19 | Univent | 6800 | 0 | 0 | 20 | 3
C3 | CLASSROOM | 0 | 0 | Yes | 850 | 19 | 19 | Univent | 6800 | 0 | 0 | 20 | 3
C4 | CLASSROOM | 367 | 24 |  | 1085 | 24 | 24 | Univent | 8680 | 2.5369 | 1 | 2.5369 | 1
C5 | CLASSROOM | 368 | 24 |  | 720 | 16 | 16 | Univent | 5760 | 3.8333 | 1 | 3.8333 | 1
C6 | CLASSROOM | 333 | 22 |  | 890 | 20 | 20 | Univent | 7120 | 2.8062 | 1 | 2.8062 | 1
C7 | CLASSROOM | 293 | 19 |  | 0 | 0 | 0 | Univent | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
C101 | CLASSROOM | 253 | 16 |  | 850 | 19 | 16 | Univent | 6800 | 2.2324 | 1 | 2.2324 | 1
C102 | CLASSROOM | 404 | 26 |  | 850 | 19 | 19 | Univent | 6800 | 3.5647 | 1 | 3.5647 | 1
C103 | CLASSROOM | 230 | 15 |  | 816 | 18 | 15 | Univent | 6528 | 2.114 | 1 | 2.114 | 1
C104 | CLASSROOM | 353 | 23 |  | 1120 | 25 | 23 | Univent | 8960 | 2.3638 | 1 | 2.3638 | 1
C105 | CLASSROOM | 290 | 19 |  | 744 | 16 | 16 | Univent | 5952 | 2.9234 | 1 | 2.9234 | 1
C106 | CLASSROOM | 241 | 16 |  | 1100 | 25 | 16 | Univent | 8800 | 1.6432 | 1 | 1.6432 | 1
D1 | CLASSROOM | 274 | 18 |  | 850 | 19 | 18 | Univent | 6800 | 2.4176 | 1 | 2.4176 | 1
D2 | CLASSROOM | 449 | 29 |  | 850 | 19 | 19 | Univent | 6800 | 3.9618 | 1 | 3.9618 | 1
D3 | CLASSROOM | 314 | 20 |  | 850 | 19 | 19 | Univent | 6800 | 2.7706 | 1 | 2.7706 | 1
D4 | CLASSROOM | 293 | 19 |  | 1085 | 24 | 19 | Univent | 8680 | 2.0253 | 1 | 2.0253 | 1
D5 | CLASSROOM | 273 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.8438 | 1 | 2.8438 | 1
D6 | CLASSROOM | 405 | 27 |  | 890 | 20 | 20 | Univent | 7120 | 3.4129 | 1 | 3.4129 | 1
D101 | CLASSROOM | 283 | 18 |  | 850 | 19 | 18 | Univent | 6800 | 2.4971 | 1 | 2.4971 | 1
D102 | CLASSROOM | 304 | 20 |  | 850 | 19 | 19 | Univent | 6800 | 2.6824 | 1 | 2.6824 | 1
D103 | CLASSROOM | 326 | 21 |  | 816 | 18 | 18 | Univent | 6528 | 2.9963 | 1 | 2.9963 | 1
D104 | CLASSROOM | 244 | 16 |  | 1120 | 25 | 16 | Univent | 8960 | 1.6339 | 1 | 1.6339 | 1
D105 | CLASSROOM | 235 | 15 |  | 744 | 16 | 15 | Univent | 5952 | 2.369 | 1 | 2.369 | 1
D106 | CLASSROOM | 0 | 0 |  | 1100 | 25 | 0 | Univent | 8800 | 0 | 0 | 0 | 0
D200 | MUSIC CLASSROOM 2 | 729 | 48 |  | 1600 | 36 | 36 | Univent | 12800 | 3.4172 | 1 | 3.4172 | 1
D205 | MUSIC CLASSROOM 1 | 620 | 41 |  | 1600 | 36 | 36 | Univent | 12800 | 2.9062 | 1 | 2.9062 | 1
E12 | SCIENCE CLASSROOM | 0 | 0 |  | 1232 | 28 | 0 | Univent | 9856 | 0 | 0 | 0 | 0
E-147 | BREAK ROOM, OFFICE AREA | 0 | 0 |  | 120 | 2 | 0 | Univent | 960 | 0 | 0 | 0 | 0
E-148 | VICE PRINCIPAL OFFICE | 0 | 0 |  | 120 | 2 | 0 | Univent | 960 | 0 | 0 | 0 | 0
E-149 | CONFERENCE AREA | 47 | 3 |  | 260 | 5 | 3 | Univent | 2080 | 1.3558 | 1 | 1.3558 | 1
E-150 | PRINCIPAL OFFICE | 36 | 2 |  | 225 | 5 | 2 | Univent | 1800 | 1.2 | 1 | 1.2 | 1
E204 | EARLY CHILDROOM ED CLASSROOM | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
E205 | CREATIVE WRITING CLASSROOM (LEFT) | 577 | 38 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
E207 | COMPUTER LAB | 3 | 0 |  | 2070 | 47 | 0 | Univent | 16560 | 0.01087 | 0 | 0.01087 | 0
- | GIRLS GYM | 0 | 0 |  | 4897 | 111 | 0 | Air Handling Unit | 39176 | 0 | 0 | 0 | 0
- | BOYS GYM | 0 | 0 |  | 4897 | 111 | 0 | Air Handling Unit | 39176 | 0 | 0 | 0 | 0
- | IMC - LIBRARY | 0 | 0 |  | 3985 | 90 | 0 | Air Handling Unit | 31880 | 0 | 0 | 0 | 0
- | INDUSTRIAL ART (WOODSHOP) | 0 | 0 |  | 1564 | 35 | 0 | Air Handling Unit | 12512 | 0 | 0 | 0 | 0
- | SWIMMING POOL | 0 | 0 |  | 10200 | 231 | 0 | Air Handling Unit | 81600 | 0 | 0 | 0 | 0
- | ADMIN + HEALTH OFFICE | 0 | 0 |  | 130 | 2 | 0 | Air Handling Unit | 1040 | 0 | 0 | 0 | 0
- | ART STUDIOS | 0 | 0 |  | 3860 | 87 | 0 | Air Handling Unit | 30880 | 0 | 0 | 0 | 0
- | AUDITORIUM + STAGE | 0 | 0 |  | 12450 | 282 | 0 | Air Handling Unit | 99600 | 0 | 0 | 0 | 0
- | CLASSROOM (YMCA 2) | 0 | 0 |  | 704 | 16 | 0 | Air Handling Unit | 5632 | 0 | 0 | 0 | 0
- | CLASSROOM (YMCA OST1) | 0 | 0 |  | 544 | 12 | 0 | Air Handling Unit | 4352 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-05 | [8 empty] | unk | unk | unk | unk
School: | Richmond Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
3 | - |  | 0 |  | 1000 | 22 | 0 | Radiators/House fan | 8000 | unk | unk | unk | unk
8 | - |  | 0 |  | 1200 | 27 | 0 | Radiators/House fan | 9600 | unk | unk | unk | unk
101 | Classroom |  | 0 | Yes | 759 | 17 | 17 | Radiators/House fan | 6072 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 759 | 17 | 17 | Radiators/House fan | 6072 | unk | unk | 20 | 3
102A | Nurse |  | 0 | Yes | 216 | 4 | 4 | Radiators/House fan | 1728 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 812 | 18 | 18 | Radiators/House fan | 6496 | unk | unk | 20 | 3
104 | Classroom |  | 0 | Yes | 812 | 18 | 18 | Radiators/House fan | 6496 | unk | unk | 20 | 3
105 | Main Office |  | 0 | Yes | 416 | 9 | 9 | Radiators/House fan | 3328 | unk | unk | 20 | 3
106 | Classroom |  | 0 | Yes | 762 | 17 | 17 | Radiators/House fan | 6096 | unk | unk | 20 | 3
107 | Classroom |  | 0 | Yes | 742 | 16 | 16 | Radiators/House fan | 5936 | unk | unk | 20 | 3
108 | Faculty Lounge |  | 0 |  | 440 | 10 | 0 | Radiators/House fan | 3520 | unk | unk | unk | unk
109 | Classroom |  | 0 | Yes | 1180 | 26 | 26 | Radiators/House fan | 9440 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 759 | 17 | 17 | Radiators/House fan | 6072 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 759 | 17 | 17 | Radiators/House fan | 6072 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 960 | 21 | 21 | Radiators/House fan | 7680 | unk | unk | 20 | 3
203A | Counselor Office |  | 0 |  | 167 | 3 | 0 | Radiators/House fan | 1336 | unk | unk | unk | unk
204 | Classroom |  | 0 | Yes | 960 | 21 | 21 | Radiators/House fan | 7680 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 896 | 20 | 20 | Radiators/House fan | 7168 | unk | unk | 20 | 3
206 | - |  | 0 |  | 896 | 20 | 0 | Radiators/House fan | 7168 | unk | unk | unk | unk
207 | - |  | 0 | Yes | 792 | 18 | 18 | Radiators/House fan | 6336 | unk | unk | 20 | 3
208 | - |  | 0 |  | 792 | 18 | 0 | Radiators/House fan | 6336 | unk | unk | unk | unk
209 | - |  | 0 | Yes | 841 | 19 | 19 | Radiators/House fan | 6728 | unk | unk | 20 | 3
210 | - |  | 0 |  | 202 | 4 | 0 | Radiators/House fan | 1616 | unk | unk | unk | unk
301 | - |  | 0 |  | 792 | 18 | 0 | Radiators/House fan | 6336 | unk | unk | unk | unk
302 | Classroom |  | 0 |  | 792 | 18 | 0 | Radiators/House fan | 6336 | unk | unk | unk | unk
303 | - |  | 0 |  | 840 | 19 | 0 | Radiators/House fan | 6720 | unk | unk | unk | unk
303A | - |  | 0 |  | 390 | 8 | 0 | Radiators/House fan | 3120 | unk | unk | unk | unk
304 | - |  | 0 |  | 900 | 20 | 0 | Radiators/House fan | 7200 | unk | unk | unk | unk
305 | - |  | 0 |  | 840 | 19 | 0 | Radiators/House fan | 6720 | unk | unk | unk | unk
306 | Classroom |  | 0 |  | 870 | 19 | 0 | Radiators/House fan | 6960 | unk | unk | unk | unk
307 | - |  | 0 |  | 850 | 19 | 0 | Radiators/House fan | 6800 | unk | unk | unk | unk
308 | - |  | 0 |  | 850 | 19 | 0 | Radiators/House fan | 6800 | unk | unk | unk | unk
309 | - |  | 0 |  | 900 | 20 | 0 | Radiators/House fan | 7200 | unk | unk | unk | unk
310 | - |  | 0 |  | 202 | 4 | 0 | Radiators/House fan | 1616 | unk | unk | unk | unk
- | Principal's Office |  | 0 |  | 448 | 10 | 0 | Radiators/House fan | 3584 | unk | unk | unk | unk
- | Gym |  | 0 |  | 2760 | 62 | 0 | Heating Ventalation Unit | 22080 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-01 | [8 empty] | unk | unk | unk | unk
School: | Rivera (Bright Futures) Early Childhood Center | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Basement | Cafeteria | 1016 | 67 |  | 4000 | 90 | 67 | Air Handling Unit | 32000 | 1.905 | 1 | 1.905 | 1
Basement | VVT's in the small Building | 138 | 9 |  | 247 | 5 | 5 | Air Handling Unit | 1976 | 4.1903 | 2 | 4.1903 | 2
2nd floor | Common area vvt's(tall Building) | 131 | 8 |  | 247 | 5 | 5 | Air Handling Unit | 1976 | 3.9777 | 1 | 3.9777 | 1
4th for upper building | Zoned AH for 5 zone floor | 0 | 0 |  | 247 | 5 | 0 | Air Handling Unit | 1976 | 0 | 0 | 0 | 0
5th floor upper building | Zoned AH for 6 zone floor | 1 | 0 |  | 247 | 5 | 0 | Air Handling Unit | 1976 | 0.030364 | 0 | 0.030364 | 0
- | Zone1( group learning room) | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit | 1080 | 0 | 0 | 0 | 0
- | Zone2 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit | 1080 | 0 | 0 | 0 | 0
- | Zone3 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit | 1080 | 0 | 0 | 0 | 0
- | Zone4 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit | 1080 | 0 | 0 | 0 | 0
- | Zone5 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit | 1080 | 0 | 0 | 0 | 0
- | Zone6 | 0 | 0 |  | 135 | 3 | 0 | Air Handling Unit | 1080 | 0 | 0 | 0 | 0
Zone1 | Group learning open area 1 | 804 | 53 |  | 280 | 6 | 6 | Air Handling Unit | 2240 | 21.5357 | 3 | 21.5357 | 3
Zone 1 | Group learning open area 2 | 0 | 0 |  | 270 | 6 | 0 | Air Handling Unit | 2160 | 0 | 0 | 0 | 0
Zone 1 | Group learning office | 0 | 0 |  | 276 | 6 | 0 | Air Handling Unit | 2208 | 0 | 0 | 0 | 0
Zone 1 | Large storage | 0 | 0 |  | 112 | 2 | 0 | Air Handling Unit | 896 | 0 | 0 | 0 | 0
Zone 1 | Small storage | 21 | 1 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 1.9688 | 1 | 1.9688 | 1
Zone 2 | Office 1 | 85 | 5 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 7.9688 | 2 | 7.9688 | 2
Zone 2 | Office 2 | 72 | 4 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 6.75 | 2 | 6.75 | 2
Zone 2 | Office 3 | 37 | 2 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 3.4688 | 1 | 3.4688 | 1
Zone 2 | Spare room | 83 | 5 |  | 85 | 1 | 1 | Air Handling Unit | 680 | 7.3235 | 2 | 7.3235 | 2
Zone 2 | Hallway | 0 | 0 |  | 110 | 2 | 0 | Air Handling Unit | 880 | 0 | 0 | 0 | 0
Zone 2 | Copy room | 38 | 2 |  | 84 | 1 | 1 | Air Handling Unit | 672 | 3.3929 | 1 | 3.3929 | 1
Zone 3 | Conference room vent 1 | 314 | 20 |  | 1344 | 30 | 20 | Air Handling Unit | 10752 | 1.7522 | 1 | 1.7522 | 1
Zone 3 | Conference room vent 2 | 0 | 0 |  | 1344 | 30 | 0 | Air Handling Unit | 10752 | 0 | 0 | 0 | 0
Zone 3 | Conference room vent 3 | 0 | 0 |  | 1344 | 30 | 0 | Air Handling Unit | 10752 | 0 | 0 | 0 | 0
Zone 4 | Admin open area 1 | 307 | 20 |  | 182 | 4 | 4 | Air Handling Unit | 1456 | 12.6511 | 3 | 12.6511 | 3
Zone 4 | Admin open area 2 | 0 | 0 |  | 182 | 4 | 0 | Air Handling Unit | 1456 | 0 | 0 | 0 | 0
Zone 4 | copy room | 57 | 3 |  | 84 | 1 | 1 | Air Handling Unit | 672 | 5.0893 | 2 | 5.0893 | 2
Zone 4 | elevator hallway | 0 | 0 |  | 144 | 3 | 0 | Air Handling Unit | 1152 | 0 | 0 | 0 | 0
Zone 4 | admin waiting area | 0 | 0 |  | 380 | 8 | 0 | Air Handling Unit | 3040 | 0 | 0 | 0 | 0
Zone 4 | Vacant office 1 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 4 | Vacant office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 4 | Supply Room | 0 | 0 |  | 110 | 2 | 0 | Air Handling Unit | 880 | 0 | 0 | 0 | 0
Zone 5 | Office 1 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 5 | Office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 5 | Zone 5 meeting Room 1 | 42 | 2 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 3.9375 | 1 | 3.9375 | 1
Zone 5 | Zone 5 meeting Room 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 6 | Storage | 110 | 7 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 10.3125 | 3 | 10.3125 | 3
Zone 6 | Office 1 | 272 | 18 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 25.5 | 4 | 25.5 | 4
Zone 6 | Office 2 | 121 | 8 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 11.3438 | 3 | 11.3438 | 3
Zone 6 | Office 3 | 115 | 7 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 10.7812 | 3 | 10.7812 | 3
Zone 6 | Office 4 | 198 | 13 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 18.5625 | 3 | 18.5625 | 3
Zone 6 | Office 5 | 147 | 9 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 13.7812 | 3 | 13.7812 | 3
- | Zone 1 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Zone 2 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Zone 3 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Zone 4 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Zone 5 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
Zone 1 | Group learning area. Diffuser 1 | 91 | 6 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
Zone 1 | Group learning area. Diffuser 2 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
Zone 1 | Group learning area. Diffuser 3 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
Zone 1 | Group learning area. Diffuser 4 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
Zone 1 | Group learning area. Diffuser 5 | 0 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
Zone 1 | Office 1 | 18 | 1 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 1.6875 | 1 | 1.6875 | 1
Zone 1 | Office 2 | 19 | 1 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 1.7812 | 1 | 1.7812 | 1
Zone 1 | Office 3 | 12 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 1.125 | 1 | 1.125 | 1
Zone 2 | Elevator lobby | 0 | 0 |  | 144 | 3 | 0 | Air Handling Unit | 1152 | 0 | 0 | 0 | 0
Zone 2 | Reception diffuser 1 | 34 | 2 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
Zone 2 | Reception diffuser 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 2 | Office 1 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 2 | Office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 3 | Office 1 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 3 | Office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 3 | Office 3 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 3 | Kitchen 1 | 0 | 0 |  | 214 | 4 | 0 | Air Handling Unit | 1712 | 0 | 0 | 0 | 0
Zone 3 | Kitchen 2 | 0 | 0 |  | 214 | 4 | 0 | Air Handling Unit | 1712 | 0 | 0 | 0 | 0
Zone 3 | Hallway 1 | 0 | 0 |  | 276 | 6 | 0 | Air Handling Unit | 2208 | 0 | 0 | 0 | 0
Zone 3 | Hallway 2 | 0 | 0 |  | 168 | 3 | 0 | Air Handling Unit | 1344 | 0 | 0 | 0 | 0
Zone 4 | Office 411 | 0 | 0 |  | 75 | 1 | 0 | Air Handling Unit | 600 | 0 | 0 | 0 | 0
Zone 4 | Office 2 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 4 | Office 3 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 4 | Storage 415 | 0 | 0 |  | 39 | 0 | 0 | Air Handling Unit | 312 | 0 | 0 | 0 | 0
Zone 4 | Hallway | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 4 | Assistant Superintendent | 0 | 0 |  | 460 | 10 | 0 | Air Handling Unit | 3680 | 0 | 0 | 0 | 0
Zone 4 | Assistant Superintendent | 0 | 0 |  | 460 | 10 | 0 | Air Handling Unit | 3680 | 0 | 0 | 0 | 0
Zone 4 | Assistant Superintendent | 0 | 0 |  | 460 | 10 | 0 | Air Handling Unit | 3680 | 0 | 0 | 0 | 0
Zone 4 | Storage 408 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 5 | Office 403 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 5 | Office 403 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 5 | Office 404 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 5 | Office | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 5 | Office | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 5 | Conference room 406 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 5 | Conference room 406 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
Zone 5 | Office 407 | 0 | 0 |  | 142 | 3 | 0 | Air Handling Unit | 1136 | 0 | 0 | 0 | 0
Zone 5 | Office 409 | 0 | 0 |  | 80 | 1 | 0 | Air Handling Unit | 640 | 0 | 0 | 0 | 0
3rd floor. VVT#11 | Commons area total | 50 | 3 |  | 247 | 5 | 3 | Air Handling Unit | 1976 | 1.5182 | 1 | 1.5182 | 1
- | Elevator hall | 9 | 0 |  | 400 | 9 | 0 | Air Handling Unit | 3200 | 0.16875 | 0 | 0.16875 | 0
- | Elevator hall | 0 | 0 |  | 602 | 13 | 0 | Air Handling Unit | 4816 | 0 | 0 | 0 | 0
- | Commons Area Diffuser | 11 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Commons Area Diffuser | 11 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Commons Area Diffuser | 11 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Commons Area Diffuser | 12 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Commons Area Office | 2 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
2nd floor. VVT#8 | Commons Are Total | 58 | 3 |  | 247 | 5 | 3 | Air Handling Unit | 1976 | 1.7611 | 1 | 1.7611 | 1
- | Elevator hall | 2 | 0 |  | 400 | 9 | 0 | Air Handling Unit | 3200 | 0.0375 | 0 | 0.0375 | 0
- | Commons Area Diffuser | 14 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Commons Area Diffuser | 14 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Commons Area Diffuser | 12 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Commons Area Diffuser | 8 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Commons area office | 3 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Class bathroom | 3 | 0 |  | 75 | 1 | 0 | Air Handling Unit | 600 | 0.3 | 0 | 0.3 | 0
- | Staff Bathroom | 2 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Elevator hall | 2 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
1st floor VVT#4 | 1st floor Commons Area Total | 46 | 3 |  | 247 | 5 | 3 | Air Handling Unit | 1976 | 1.3968 | 1 | 1.3968 | 1
- | elevator hall | 14 | 0 |  | 480 | 10 | 0 | Air Handling Unit | 3840 | 0.21875 | 0 | 0.21875 | 0
- | elevator hall | 7 | 0 |  | 700 | 15 | 0 | Air Handling Unit | 5600 | 0.075 | 0 | 0.075 | 0
- | Commons area diffuser | 7 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Commons area diffuser | 8 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Commons area diffuser | 2 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Commons area diffuser | 4 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Commons area office | 3 | 0 |  | 126 | 2 | 0 | Air Handling Unit | 1008 | 0.17857 | 0 | 0.17857 | 0
- | Class bathroom | 0 | 0 |  | 75 | 1 | 0 | Air Handling Unit | 600 | 0 | 0 | 0 | 0
- | Staff bathroom | 2 | 0 |  | 48 | 1 | 0 | Air Handling Unit | 384 | 0.3125 | 0 | 0.3125 | 0
Room110 | Classroom | 400 | 26 |  | 900 | 20 | 20 | Univent | 7200 | 3.3333 | 1 | 3.3333 | 1
Room 111 | Classroom | 335 | 22 |  | 900 | 20 | 20 | Univent | 7200 | 2.7917 | 1 | 2.7917 | 1
Room 112 | Classroom | 410 | 27 |  | 900 | 20 | 20 | Univent | 7200 | 3.4167 | 1 | 3.4167 | 1
Room 113 | Classroom | 375 | 25 |  | 900 | 20 | 20 | Univent | 7200 | 3.125 | 1 | 3.125 | 1
205A | Office space | 290 | 19 |  | 480 | 10 | 10 | Univent | 3840 | 4.5312 | 2 | 4.5312 | 2
205B | Office space | 484 | 32 |  | 613 | 13 | 13 | Univent | 4904 | 5.9217 | 2 | 5.9217 | 2
Room 212 | Classroom | 259 | 17 |  | 900 | 20 | 17 | Univent | 7200 | 2.1583 | 1 | 2.1583 | 1
Room 213 | Classroom | 502 | 33 |  | 900 | 20 | 20 | Univent | 7200 | 4.1833 | 2 | 4.1833 | 2
Room 214 | Classroom | 277 | 18 |  | 900 | 20 | 18 | Univent | 7200 | 2.3083 | 1 | 2.3083 | 1
Room 215 | Classroom | 544 | 36 |  | 900 | 20 | 20 | Univent | 7200 | 4.5333 | 2 | 4.5333 | 2
Room303 | Office space | 482 | 32 |  | 1414 | 32 | 32 | Univent | 11312 | 2.5566 | 1 | 2.5566 | 1
Room 303B | Office space | 256 | 17 |  | 360 | 8 | 8 | Univent | 2880 | 5.3333 | 2 | 5.3333 | 2
Room 309 | Classroom | 517 | 34 |  | 1110 | 25 | 25 | Univent | 8880 | 3.4932 | 1 | 3.4932 | 1
Room 310 | Classroom | 290 | 19 |  | 900 | 20 | 19 | Univent | 7200 | 2.4167 | 1 | 2.4167 | 1
Room 311 | Classroom | 326 | 21 |  | 900 | 20 | 20 | Univent | 7200 | 2.7167 | 1 | 2.7167 | 1
Room 312 | Classroom | 394 | 26 |  | 900 | 20 | 20 | Univent | 7200 | 3.2833 | 1 | 3.2833 | 1
VVT 9 | Total | 10 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Office | 3 | 0 |  | 144 | 3 | 0 | Air Handling Unit | 1152 | 0.15625 | 0 | 0.15625 | 0
- | Office | 4 | 0 |  | 144 | 3 | 0 | Air Handling Unit | 1152 | 0.20833 | 0 | 0.20833 | 0
- | Hallway | 4 | 0 |  | 688 | 15 | 0 | Air Handling Unit | 5504 | 0.043605 | 0 | 0.043605 | 0
VVT 10 | Total | 43 | 2 |  | 688 | 15 | 2 | Air Handling Unit | 5504 | 0.46875 | 0 | 0.46875 | 0
- | Teachers Lounge | 16 | 1 |  | 390 | 8 | 1 | Air Handling Unit | 3120 | 0.30769 | 0 | 0.30769 | 0
- | Bathroom | 4 | 0 |  | 48 | 1 | 0 | Air Handling Unit | 384 | 0.625 | 0 | 0.625 | 0
- | Women's Room | 8 | 0 |  | 112 | 2 | 0 | Air Handling Unit | 896 | 0.53571 | 0 | 0.53571 | 0
- | Men's Room | 3 | 0 |  | 112 | 2 | 0 | Air Handling Unit | 896 | 0.20089 | 0 | 0.20089 | 0
- | Hallway | 11 | 0 |  | 688 | 15 | 0 | Air Handling Unit | 5504 | 0.11991 | 0 | 0.11991 | 0
VVT 6 | Total | 18 | 1 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | office | 6 | 0 |  | 100 | 2 | 0 | Air Handling Unit | 800 | 0.45 | 0 | 0.45 | 0
- | Office | 5 | 0 |  | 100 | 2 | 0 | Air Handling Unit | 800 | 0.375 | 0 | 0.375 | 0
- | Office | 5 | 0 |  | 100 | 2 | 0 | Air Handling Unit | 800 | 0.375 | 0 | 0.375 | 0
- | Hallway | 2 | 0 |  | 688 | 15 | 0 | Air Handling Unit | 5504 | 0.021802 | 0 | 0.021802 | 0
VVT 7 | Total | 32 | 2 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Men's room | 7 | 0 |  | 112 | 2 | 0 | Air Handling Unit | 896 | 0.46875 | 0 | 0.46875 | 0
- | Women's room | 11 | 0 |  | 112 | 2 | 0 | Air Handling Unit | 896 | 0.73661 | 0 | 0.73661 | 0
- | Staff bathroom | 4 | 0 |  | 52 | 1 | 0 | Air Handling Unit | 416 | 0.57692 | 0 | 0.57692 | 0
- | Hallway | 4 | 0 |  | 688 | 15 | 0 | Air Handling Unit | 5504 | 0.043605 | 0 | 0.043605 | 0
- | Hallway | 4 | 0 |  | 688 | 15 | 0 | Air Handling Unit | 5504 | 0.043605 | 0 | 0.043605 | 0
VVT1 | Total | 29 | 1 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | kitchen | 6 | 0 |  | 288 | 6 | 0 | Air Handling Unit | 2304 | 0.15625 | 0 | 0.15625 | 0
- | Storage | 4 | 0 |  | 450 | 10 | 0 | Air Handling Unit | 3600 | 0.066667 | 0 | 0.066667 | 0
- | Men's room | 4 | 0 |  | 77 | 1 | 0 | Air Handling Unit | 616 | 0.38961 | 0 | 0.38961 | 0
- | Women's room | 6 | 0 |  | 77 | 1 | 0 | Air Handling Unit | 616 | 0.58442 | 0 | 0.58442 | 0
- | Unisex bathroom | 3 | 0 |  | 77 | 1 | 0 | Air Handling Unit | 616 | 0.29221 | 0 | 0.29221 | 0
VVT 3 | Total | 0 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | storage | 0 | 0 |  | 328 | 7 | 0 | Air Handling Unit | 2624 | 0 | 0 | 0 | 0
- | storage | 0 | 0 |  | 450 | 10 | 0 | Air Handling Unit | 3600 | 0 | 0 | 0 | 0
- | storage | 0 | 0 |  | 250 | 5 | 0 | Air Handling Unit | 2000 | 0 | 0 | 0 | 0
- | storage | 0 | 0 |  | 175 | 3 | 0 | Air Handling Unit | 1400 | 0 | 0 | 0 | 0
VVT 5 | Total | 41 | 2 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | hallway | 7 | 0 |  | 425 | 9 | 0 | Air Handling Unit | 3400 | 0.12353 | 0 | 0.12353 | 0
- | Lobby | 11 | 0 |  | 375 | 8 | 0 | Air Handling Unit | 3000 | 0.22 | 0 | 0.22 | 0
- | Guard office | 8 | 0 |  | 120 | 2 | 0 | Air Handling Unit | 960 | 0.5 | 0 | 0.5 | 0
- | Staff lockers | 4 | 0 |  | 450 | 10 | 0 | Air Handling Unit | 3600 | 0.066667 | 0 | 0.066667 | 0
- | Hallway | 4 | 0 |  | 800 | 18 | 0 | Air Handling Unit | 6400 | 0.0375 | 0 | 0.0375 | 0
- | Hallway | 8 | 0 |  | 168 | 3 | 0 | Air Handling Unit | 1344 | 0.35714 | 0 | 0.35714 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | Paul Robeson High School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B-2 | Classroom | 0 | 0 |  | 1073 | 24 | 0 | Fan Coil Unit | 8584 | 0 | 0 | 0 | 0
100 | Classroom | 380 | 25 |  | 940 | 21 | 21 | Univent | 7520 | 3.0319 | 1 | 3.0319 | 1
106 | Classroom | 470 | 31 |  | 840 | 19 | 19 | Univent | 6720 | 4.1964 | 2 | 4.1964 | 2
108 | Classroom | 11 | 0 |  | 828 | 18 | 0 | Univent | 6624 | 0.099638 | 0 | 0.099638 | 0
200 | Classroom | 89 | 5 |  | 696 | 15 | 5 | Univent | 5568 | 0.95905 | 0 | 0.95905 | 0
202 | Classroom | 231 | 15 |  | 696 | 15 | 15 | Univent | 5568 | 2.4892 | 1 | 2.4892 | 1
204 | Classroom | 301 | 20 |  | 696 | 15 | 15 | Univent | 5568 | 3.2435 | 1 | 3.2435 | 1
205 | Classroom | 304 | 20 |  | 672 | 15 | 15 | Univent | 5376 | 3.3929 | 1 | 3.3929 | 1
206 | Classroom | 200 | 13 |  | 696 | 15 | 13 | Univent | 5568 | 2.1552 | 1 | 2.1552 | 1
207 | Classroom | 191 | 12 |  | 696 | 15 | 12 | Univent | 5568 | 2.0582 | 1 | 2.0582 | 1
208 | Classroom | 125 | 8 |  | 696 | 15 | 8 | Univent | 5568 | 1.347 | 1 | 1.347 | 1
209 | Classroom | 178 | 11 |  | 384 | 8 | 8 | Univent | 3072 | 3.4766 | 1 | 3.4766 | 1
210 | Classroom | 200 | 13 |  | 690 | 15 | 13 | Univent | 5520 | 2.1739 | 1 | 2.1739 | 1
211 | Classroom | 262 | 17 |  | 851 | 19 | 17 | Univent | 6808 | 2.309 | 1 | 2.309 | 1
212 | Classroom | 280 | 18 |  | 875 | 19 | 18 | Univent | 7000 | 2.4 | 1 | 2.4 | 1
213 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Univent | 7000 | 0 | 0 | 0 | 0
- | AUDITORIUM | 0 | 0 |  | 2793 | 63 | 0 | Air Handling Unit | 22344 | 0 | 0 | 0 | 0
- | Cafeteria | 862 | 57 |  | 2343 | 53 | 53 | Univent | 18744 | 2.7593 | 1 | 2.7593 | 1
- | GYM | 812 | 54 |  | 3478 | 79 | 54 | Air Handling Unit | 27824 | 1.751 | 1 | 1.751 | 1
- | MAIN OFFICE | 0 | 0 |  | 552 | 12 | 0 | Univent | 4416 | 0 | 0 | 0 | 0
- | Student Lounge | 64 | 4 |  | 552 | 12 | 4 | Univent | 4416 | 0.86957 | 0 | 0.86957 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-05-03 | [8 empty] | unk | unk | unk | unk
School: | Roosevelt Elementary School | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom |  | 0 | Yes | 1035 | 23 | 23 | House Fan | 8280 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 1012 | 23 | 23 | House Fan | 8096 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 650 | 14 | 14 | House Fan | 5200 | unk | unk | 20 | 3
104 | Main Office |  | 0 | Yes | 1225 | 27 | 27 | House Fan | 9800 | unk | unk | 20 | 3
105 | Classroom |  | 0 | Yes | 660 | 15 | 15 | House Fan | 5280 | unk | unk | 20 | 3
106 & 106a | Classroom |  | 0 | Yes | 1298 | 29 | 29 | House Fan | 10384 | unk | unk | 20 | 3
107 | Parent Liason |  | 0 | Yes | 550 | 12 | 12 | House Fan | 4400 | unk | unk | 20 | 3
108 | Classroom |  | 0 | Yes | 814 | 18 | 18 | House Fan | 6512 | unk | unk | 20 | 3
109 | Classroom |  | 0 | Yes | 1104 | 25 | 25 | House Fan | 8832 | unk | unk | 20 | 3
110 | Classroom |  | 0 | Yes | 960 | 21 | 21 | House Fan | 7680 | unk | unk | 20 | 3
- | Lunchroom A |  | 0 | Yes | 2881 | 65 | 65 | House Fan | 23048 | unk | unk | 20 | 3
- | Lunchroom B |  | 0 | Yes | 2898 | 65 | 65 | House Fan | 23184 | unk | unk | 20 | 3
200A | Counselor |  | 0 | Yes | 342 | 7 | 7 | House Fan | 2736 | unk | unk | 20 | 3
200B | Counselor |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | unk | unk | unk | unk
200C | Counselor |  | 0 | Yes | 342 | 7 | 7 | House Fan | 2736 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 638 | 14 | 14 | House Fan | 5104 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 748 | 17 | 17 | House Fan | 5984 | unk | unk | 20 | 3
205 | IMC |  | 0 | Yes | 1320 | 30 | 30 | House Fan | 10560 | unk | unk | 20 | 3
206A | Counselor |  | 0 | Yes | 140 | 3 | 3 | House Fan | 1120 | unk | unk | 20 | 3
206B | Counselor |  | 0 | Yes | 116 | 2 | 2 | House Fan | 928 | unk | unk | 20 | 3
206C | Counselor |  | 0 | Yes | 115 | 2 | 2 | House Fan | 920 | unk | unk | 20 | 3
206D | Counselor |  | 0 | Yes | 142 | 3 | 3 | House Fan | 1136 | unk | unk | 20 | 3
206E | Counselor |  | 0 | Yes | 126 | 2 | 2 | House Fan | 1008 | unk | unk | 20 | 3
207A | Room |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | unk | unk | 20 | 3
207B | Room |  | 0 |  | 145 | 3 | 0 | House Fan | 1160 | unk | unk | unk | unk
207C | Room |  | 0 | Yes | 108 | 2 | 2 | House Fan | 864 | unk | unk | 20 | 3
207D | Room |  | 0 |  | 103 | 2 | 0 | House Fan | 824 | unk | unk | unk | unk
207E | Room |  | 0 | Yes | 132 | 3 | 3 | House Fan | 1056 | unk | unk | 20 | 3
208 | Art Room |  | 0 | Yes | 1152 | 26 | 26 | House Fan | 9216 | unk | unk | 20 | 3
209 | Faculty Lounge |  | 0 | Yes | 696 | 15 | 15 | House Fan | 5568 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 629 | 14 | 14 | House Fan | 5032 | unk | unk | 20 | 3
- | Nurse Suite |  | 0 | Yes | 552 | 12 | 12 | House Fan | 4416 | unk | unk | 20 | 3
210 | Science Lab |  | 0 | Yes | 700 | 15 | 15 | House Fan | 5600 | unk | unk | 20 | 3
211 | Music |  | 0 | Yes | 858 | 19 | 19 | House Fan | 6864 | unk | unk | 20 | 3
212 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | unk | unk | 20 | 3
213 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
214 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | unk | unk | 20 | 3
215 | Classroom |  | 0 | Yes | 572 | 13 | 13 | House Fan | 4576 | unk | unk | 20 | 3
216 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | unk | unk | 20 | 3
217 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
218 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
219 | Classroom |  | 0 | Yes | 704 | 16 | 16 | House Fan | 5632 | unk | unk | 20 | 3
220 | Classroom |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | unk | unk | unk | unk
221A | Classroom |  | 0 | Yes | 342 | 7 | 7 | House Fan | 2736 | unk | unk | 20 | 3
221B | Classroom |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | unk | unk | unk | unk
221C | Classroom |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | unk | unk | unk | unk
222 | Classroom |  | 0 |  | 336 | 7 | 0 | House Fan | 2688 | unk | unk | unk | unk
300A | Counselor // Storage |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | unk | unk | unk | unk
300B | Counselor // Storage |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | unk | unk | unk | unk
300C | Counselor // Storage |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | unk | unk | unk | unk
301 | Vice Principals Office |  | 0 | Yes | 629 | 14 | 14 | House Fan | 5032 | unk | unk | 20 | 3
302 | Classroom |  | 0 | Yes | 735 | 16 | 16 | House Fan | 5880 | unk | unk | 20 | 3
303 | Classroom |  | 0 | Yes | 789 | 17 | 17 | House Fan | 6312 | unk | unk | 20 | 3
304 | Classroom |  | 0 | Yes | 734 | 16 | 16 | House Fan | 5872 | unk | unk | 20 | 3
305 | Classroom |  | 0 | Yes | 789 | 17 | 17 | House Fan | 6312 | unk | unk | 20 | 3
306 | Classroom |  | 0 |  | 1170 | 26 | 0 | House Fan | 9360 | unk | unk | unk | unk
307 | Classroom |  | 0 | Yes | 936 | 21 | 21 | House Fan | 7488 | unk | unk | 20 | 3
308 | Classroom |  | 0 | Yes | 735 | 16 | 16 | House Fan | 5880 | unk | unk | 20 | 3
309 | Classroom |  | 0 |  | 952 | 21 | 0 | House Fan | 7616 | unk | unk | unk | unk
310 | Classroom |  | 0 | Yes | 840 | 19 | 19 | House Fan | 6720 | unk | unk | 20 | 3
311 | Classroom |  | 0 |  | 836 | 19 | 0 | House Fan | 6688 | unk | unk | unk | unk
312 | Classroom |  | 0 |  | 792 | 18 | 0 | House Fan | 6336 | unk | unk | unk | unk
313 | Classroom |  | 0 |  | 920 | 20 | 0 | House Fan | 7360 | unk | unk | unk | unk
314 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan | 5704 | unk | unk | unk | unk
315 | Classroom |  | 0 |  | 667 | 15 | 0 | House Fan | 5336 | unk | unk | unk | unk
316 | Classroom |  | 0 |  | 713 | 16 | 0 | House Fan | 5704 | unk | unk | unk | unk
317 | Classroom |  | 0 |  | 638 | 14 | 0 | House Fan | 5104 | unk | unk | unk | unk
318 | Classroom |  | 0 |  | 868 | 19 | 0 | House Fan | 6944 | unk | unk | unk | unk
319 | Classroom |  | 0 | Yes | 868 | 19 | 19 | House Fan | 6944 | unk | unk | 20 | 3
320 | Classroom |  | 0 | Yes | 868 | 19 | 19 | House Fan | 6944 | unk | unk | 20 | 3
324A | Counselor, School Police |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | unk | unk | unk | unk
324B | Counselor, School Police |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | unk | unk | unk | unk
324C | Counselor, School Police |  | 0 |  | 342 | 7 | 0 | House Fan | 2736 | unk | unk | unk | unk
322 | Classroom |  | 0 | Yes | 868 | 19 | 19 | House Fan | 6944 | unk | unk | 20 | 3
321 | Classroom |  | 0 | Yes | 861 | 19 | 19 | House Fan | 6888 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | William Rowen Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | EMCOR Part 2 | Devine | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Auditorium | 0 | 0 |  | 4256 | 96 | 0 | House Fan | 34048 | 0 | 0 | 0 | 0
- | Cafeteria/Gym | 0 | 0 | Yes | 5220 | 118 | 118 | Univent | 41760 | 0 | 0 | 20 | 3
- | Library | 328 | 21 |  | 1456 | 33 | 21 | Univent | 11648 | 1.6896 | 1 | 1.6896 | 1
101 | Classroom | 457 | 30 |  | 1128 | 25 | 25 | Univent | 9024 | 3.0386 | 1 | 3.0386 | 1
102 | Classroom | 545 | 36 |  | 1128 | 25 | 25 | Univent | 9024 | 3.6237 | 1 | 3.6237 | 1
103 | Classroom | 42 | 2 | Yes | 266 | 6 | 6 | Univent | 2128 | 1.1842 | 1 | 21.1842 | 3
104 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Univent | 6528 | 0 | 0 | 20 | 3
105 | Classroom | 304 | 20 |  | 816 | 18 | 18 | Univent | 6528 | 2.7941 | 1 | 2.7941 | 1
106 | Classroom | 0 | 0 | Yes | 816 | 18 | 18 | Univent | 6528 | 0 | 0 | 20 | 3
107 | Classroom | 299 | 19 |  | 816 | 18 | 18 | Univent | 6528 | 2.7482 | 1 | 2.7482 | 1
108 | Classroom | 0 | 0 | Yes | 720 | 16 | 16 | Univent | 5760 | 0 | 0 | 20 | 3
109 | Classroom | 234 | 15 |  | 720 | 16 | 15 | Univent | 5760 | 2.4375 | 1 | 2.4375 | 1
110 | Classroom | 399 | 26 |  | 720 | 16 | 16 | Univent | 5760 | 4.1562 | 2 | 4.1562 | 2
111 | Classroom | 440 | 29 |  | 720 | 16 | 16 | Univent | 5760 | 4.5833 | 2 | 4.5833 | 2
112 | Classroom | 68 | 4 |  | 720 | 16 | 4 | Univent | 5760 | 0.70833 | 0 | 0.70833 | 0
113 | Classroom | 235 | 15 |  | 720 | 16 | 15 | Univent | 5760 | 2.4479 | 1 | 2.4479 | 1
- | Nurse's Office | 235 | 15 |  | 192 | 4 | 4 | Univent | 1536 | 9.1797 | 2 | 9.1797 | 2
201 | Classroom | 373 | 24 |  | 920 | 20 | 20 | Univent | 7360 | 3.0408 | 1 | 3.0408 | 1
202 | Classroom | 396 | 26 |  | 920 | 20 | 20 | Univent | 7360 | 3.2283 | 1 | 3.2283 | 1
203 | Classroom | 307 | 20 |  | 442 | 10 | 10 | Univent | 3536 | 5.2093 | 2 | 5.2093 | 2
204 | Classroom | 299 | 19 |  | 384 | 8 | 8 | Univent | 3072 | 5.8398 | 2 | 5.8398 | 2
205 | Classroom | 309 | 20 |  | 720 | 16 | 16 | Univent | 5760 | 3.2188 | 1 | 3.2188 | 1
206 | Classroom | 230 | 15 |  | 720 | 16 | 15 | Univent | 5760 | 2.3958 | 1 | 2.3958 | 1
207 | Classroom | 327 | 21 |  | 720 | 16 | 16 | Univent | 5760 | 3.4062 | 1 | 3.4062 | 1
208 | Classroom | 272 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.8333 | 1 | 2.8333 | 1
209 | Classroom | 324 | 21 |  | 720 | 16 | 16 | Univent | 5760 | 3.375 | 1 | 3.375 | 1
210 | Classroom | 276 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.875 | 1 | 2.875 | 1
211 | Classroom | 336 | 22 |  | 720 | 16 | 16 | Univent | 5760 | 3.5 | 1 | 3.5 | 1
212 | Classroom | 272 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.8333 | 1 | 2.8333 | 1
213 | Classroom | 284 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.9583 | 1 | 2.9583 | 1
214 | Classroom | 271 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.8229 | 1 | 2.8229 | 1
215 | Classroom | 280 | 18 |  | 720 | 16 | 16 | Univent | 5760 | 2.9167 | 1 | 2.9167 | 1
216 | Classroom | 300 | 20 |  | 744 | 16 | 16 | Univent | 5952 | 3.0242 | 1 | 3.0242 | 1
- | Main Office |  | 0 | Yes | 552 | 12 | 12 |  | 4416 | unk | unk | 20 | 3
- | Principal |  | 0 | Yes | 270 | 6 | 6 |  | 2160 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Roxborough High School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
114 | Classroom | 0 | 0 |  | 857 | 19 | 0 | Univent | 6856 | 0 | 0 | 0 | 0
115 | Classroom | 30 | 2 |  | 870 | 19 | 2 | Univent | 6960 | 0.25862 | 0 | 0.25862 | 0
116 | Classroom | 45 | 3 |  | 690 | 15 | 3 | Univent | 5520 | 0.48913 | 0 | 0.48913 | 0
117 | Weight Room | 30 | 2 |  | 814 | 18 | 2 | Univent | 6512 | 0.27641 | 0 | 0.27641 | 0
118 | Classroom | 55 | 3 |  | 702 | 15 | 3 | Univent | 5616 | 0.58761 | 0 | 0.58761 | 0
119 | Classroom | 270 | 18 |  | 877 | 19 | 18 | Univent | 7016 | 2.309 | 1 | 2.309 | 1
120 | Classroom | 85 | 5 |  | 694 | 15 | 5 | Univent | 5552 | 0.91859 | 0 | 0.91859 | 0
121 | Classroom | 40 | 2 |  | 1207 | 27 | 2 | Univent | 9656 | 0.24855 | 0 | 0.24855 | 0
124A-1 | Classroom | 55 | 3 |  | 621 | 14 | 3 | Univent | 4968 | 0.66425 | 0 | 0.66425 | 0
124B-1 | Classroom | 30 | 2 |  | 672 | 15 | 2 | Univent | 5376 | 0.33482 | 0 | 0.33482 | 0
126 | Classroom | 0 | 0 |  | 1841 | 41 | 0 | Univent | 14728 | 0 | 0 | 0 | 0
128 | Classroom | 50 | 3 |  | 1501 | 34 | 3 | Univent | 12008 | 0.24983 | 0 | 0.24983 | 0
203 | Classroom |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | unk | unk | 20 | 3
215 | Classroom | 0 | 0 |  | 829 | 18 | 0 | Univent | 6632 | 0 | 0 | 0 | 0
216 | Classroom | 50 | 3 |  | 834 | 18 | 3 | Univent | 6672 | 0.44964 | 0 | 0.44964 | 0
217 | Classroom | 0 | 0 |  | 686 | 15 | 0 | Univent | 5488 | 0 | 0 | 0 | 0
218 | Classroom | 0 | 0 |  | 724 | 16 | 0 | Univent | 5792 | 0 | 0 | 0 | 0
219 | Classroom | 55 | 3 |  | 842 | 19 | 3 | Univent | 6736 | 0.4899 | 0 | 0.4899 | 0
220 | Classroom | 60 | 4 |  | 616 | 14 | 4 | Univent | 4928 | 0.73052 | 0 | 0.73052 | 0
221 | Classroom | 35 | 2 |  | 845 | 19 | 2 | Univent | 6760 | 0.31065 | 0 | 0.31065 | 0
223 | Classroom | 55 | 3 |  | 1072 | 24 | 3 | Univent | 8576 | 0.38479 | 0 | 0.38479 | 0
224 | Classroom | 55 | 3 |  | 1010 | 22 | 3 | Univent | 8080 | 0.40842 | 0 | 0.40842 | 0
235 | Classroom |  | 0 | Yes | 839 | 19 | 19 |  | 6712 | unk | unk | 20 | 3
309 | Classroom |  | 0 | Yes | 997 | 22 | 22 |  | 7976 | unk | unk | 20 | 3
312 | Classroom |  | 0 | Yes | 1071 | 24 | 24 |  | 8568 | unk | unk | 20 | 3
319 | Classroom | 40 | 2 |  | 644 | 14 | 2 | Univent | 5152 | 0.46584 | 0 | 0.46584 | 0
320 | Classroom | 40 | 2 |  | 721 | 16 | 2 | Univent | 5768 | 0.41609 | 0 | 0.41609 | 0
321 | Classroom | 55 | 3 |  | 924 | 21 | 3 | Univent | 7392 | 0.44643 | 0 | 0.44643 | 0
322 | Classroom | 30 | 2 |  | 723 | 16 | 2 | Univent | 5784 | 0.3112 | 0 | 0.3112 | 0
323 | Classroom | 60 | 4 |  | 777 | 17 | 4 | Univent | 6216 | 0.57915 | 0 | 0.57915 | 0
324 | Classroom | 55 | 3 |  | 942 | 21 | 3 | Univent | 7536 | 0.4379 | 0 | 0.4379 | 0
325 | Classroom | 45 | 3 | Yes | 325 | 7 | 7 | Univent | 2600 | 1.0385 | 1 | 21.0385 | 3
326 | Classroom | 55 | 3 |  | 1000 | 22 | 3 | Univent | 8000 | 0.4125 | 0 | 0.4125 | 0
- | Gymnasium | 740 | 49 |  | 11475 | 260 | 49 | Air Handling Unit | 91800 | 0.48366 | 0 | 0.48366 | 0
- | Library | 2335 | 155 |  | 2622 | 59 | 59 | Air Handling Unit | 20976 | 6.6791 | 2 | 6.6791 | 2
East Office | Office | 75 | 5 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
West Office | Office | 110 | 7 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Alumni Room | 255 | 17 |  | 377 | 8 | 8 | Air Handling Unit | 3016 | 5.0729 | 2 | 5.0729 | 2
- | Computer Lab | 1285 | 85 |  | 870 | 19 | 19 | Air Handling Unit | 6960 | 11.0776 | 3 | 11.0776 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | Arts Academy @ Benjamin Rush High School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | Devine Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
103 | Lab Classroom | 465 | 31 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 4.6624 | 2 | 4.6624 | 2
103 | Lab Classroom | 465 | 31 |  |  | 0 | 0 | Univent & Air Handling Unit |  | unk | unk | unk | unk
104 | GraphicArts Classroom | 928 | 61 |  | 1840 | 41 | 41 | Univent & Air Handling Unit | 14720 | 3.7826 | 1 | 3.7826 | 1
104 | Graphic Arts Classroom | 946 | 63 |  |  | 0 | 0 | Univent & Air Handling Unit |  | unk | unk | unk | unk
105 | IMC Classroom | 2959 | 197 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
105D | Student Property Office | 281 | 18 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
105E | IMC Copy Office | 960 | 64 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
105F | Cart Storage | 368 | 24 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
105G | Tech Equip Office | 255 | 17 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
105H | IMC Office | 201 | 13 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
105J | IMC Storage room | 252 | 16 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
105K | IMC Conference Rm | 312 | 20 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
106 | Art Studio Classroom | 1326 | 88 |  | 1020 | 23 | 23 | Air Handling Unit | 8160 | 9.75 | 2 | 9.75 | 2
107 | storage room | 275 | 18 |  | 280 | 6 | 6 | Air Handling Unit | 2240 | 7.3661 | 2 | 7.3661 | 2
122 | Art Studio Classroom | 1689 | 112 |  | 1496 | 34 | 34 | Air Handling Unit | 11968 | 8.4676 | 2 | 8.4676 | 2
123 | Production Studio Classroom | 2228 | 148 |  | 1254 | 28 | 28 | Air Handling Unit | 10032 | 13.3254 | 3 | 13.3254 | 3
126A | Boys Locker Room | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
127A | Girls Locker Room | 0 | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
129 | Production Booth Classroom | 842 | 56 |  | 264 | 6 | 6 | Air Handling Unit | 2112 | 23.9205 | 3 | 23.9205 | 3
131A | Changing Room Classroom | 238 | 15 |  | 72 | 1 | 1 | Air Handling Unit | 576 | 24.7917 | 4 | 24.7917 | 4
131B | Changing Room Classroom | 175 | 11 |  | 192 | 4 | 4 | Air Handling Unit | 1536 | 6.8359 | 2 | 6.8359 | 2
133 | Storage Room | 428 | 28 |  | 580 | 13 | 13 | Air Handling Unit | 4640 | 5.5345 | 2 | 5.5345 | 2
134 | Music Classroom | 1076 | 71 |  | 748 | 17 | 17 | Air Handling Unit | 5984 | 10.7888 | 3 | 10.7888 | 3
135 | Music Classroom | 1097 | 73 |  | 748 | 17 | 17 | Air Handling Unit | 5984 | 10.9993 | 3 | 10.9993 | 3
136 | Practice Classroom | 113 | 7 |  | 36 | 0 | 0 | Air Handling Unit | 288 | 23.5417 | 3 | 23.5417 | 3
137 | Practice Classroom | 116 | 7 |  | 36 | 0 | 0 | Air Handling Unit | 288 | 24.1667 | 4 | 24.1667 | 4
138 | Library | 88 | 5 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
140 | Vocal Music Classroom | 3597 | 239 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
141 | Scene Shop Classroom | 994 | 66 |  |  | 0 | 0 | Univent & Air Handling Unit |  | unk | unk | unk | unk
142 | Vocal Theory Classroom | 347 | 23 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 3.4793 | 1 | 3.4793 | 1
143 | Music Theory Classroom | 963 | 64 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 9.6557 | 2 | 9.6557 | 2
144 | Music Tech Lab Classroom | 699 | 46 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.0087 | 2 | 7.0087 | 2
145A | Clerical Office | 362 | 24 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 3.7708 | 1 | 3.7708 | 1
145B | Roster Office | 161 | 10 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 15.0938 | 3 | 15.0938 | 3
145D | Copier Office | 219 | 14 |  | 75 | 1 | 1 | Air Handling Unit | 600 | 21.9 | 3 | 21.9 | 3
145E | Conference Office | 341 | 22 |  | 128 | 2 | 2 | Air Handling Unit | 1024 | 19.9805 | 3 | 19.9805 | 3
145F | Principal Office | 328 | 21 |  | 247 | 5 | 5 | Air Handling Unit | 1976 | 9.9595 | 2 | 9.9595 | 2
145J | Asset Princ.Office | 114 | 7 |  | 272 | 6 | 6 | Air Handling Unit | 2176 | 3.1434 | 1 | 3.1434 | 1
145K | Asset Princ.Office | 67 | 4 |  | 180 | 4 | 4 | Air Handling Unit | 1440 | 2.7917 | 1 | 2.7917 | 1
146A | Clinic Office | 45 | 3 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 2.8125 | 1 | 2.8125 | 1
146B | ClinicWaitingoffice | 506 | 33 |  | 221 | 5 | 5 | Air Handling Unit | 1768 | 17.1719 | 3 | 17.1719 | 3
146D | Exam Room | 328 | 21 |  | 60 | 1 | 1 | Air Handling Unit | 480 | 41 | 4 | 41 | 4
147 | Counselor Waiting Area | 450 | 30 |  | 288 | 6 | 6 | Air Handling Unit | 2304 | 11.7188 | 3 | 11.7188 | 3
147B | Counselor Office | 149 | 9 |  | 221 | 5 | 5 | Air Handling Unit | 1768 | 5.0566 | 2 | 5.0566 | 2
147D | Counselor's Office | 283 | 18 |  | 60 | 1 | 1 | Air Handling Unit | 480 | 35.375 | 4 | 35.375 | 4
147E | Counselor Office | 157 | 10 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 9.8125 | 2 | 9.8125 | 2
147F | Counselor Conference Office | 311 | 20 |  | 169 | 3 | 3 | Air Handling Unit | 1352 | 13.8018 | 3 | 13.8018 | 3
147G | Counselor's Office | 383 | 25 |  | 180 | 4 | 4 | Air Handling Unit | 1440 | 15.9583 | 3 | 15.9583 | 3
148A | Camera office | 565 | 37 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 35.3125 | 4 | 35.3125 | 4
148B | Storage Room | 121 | 8 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
148C | Records Office | 118 | 7 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
148D | Security Office | 125 | 8 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
148E | Operations Office | 372 | 24 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
200 | General Classroom | 649 | 43 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.5074 | 2 | 6.5074 | 2
201 | General Classroom | 532 | 35 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 5.3342 | 2 | 5.3342 | 2
202 | General Classroom | 692 | 46 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.9385 | 2 | 6.9385 | 2
204 | General Classroom | 447 | 29 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 4.482 | 2 | 4.482 | 2
205 | General Classroom | 566 | 37 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 5.6751 | 2 | 5.6751 | 2
209 | Social Ed. Classroom | 779 | 51 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.8108 | 2 | 7.8108 | 2
210 | General Classroom | 662 | 44 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.6377 | 2 | 6.6377 | 2
211 | General Classroom | 562 | 37 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 5.635 | 2 | 5.635 | 2
212 | General Classroom | 423 | 28 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 4.2413 | 2 | 4.2413 | 2
213 | General Classroom | 597 | 39 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 5.986 | 2 | 5.986 | 2
214 | General Classroom | 868 | 57 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 8.7032 | 2 | 8.7032 | 2
215 | General Classroom | 442 | 29 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit |  | unk | unk | unk | unk
216 | Physical Science Classroom | 970 | 64 |  | 1344 | 30 | 30 | Fan Coil Unit & Air Handling Unit | 10752 | 5.4129 | 2 | 5.4129 | 2
217 | Prep Classroom | 299 | 19 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit |  | unk | unk | unk | unk
219 | Physics Classroom | 630 | 42 |  | 1344 | 30 | 30 | Fan Coil Unit & Air Handling Unit | 10752 | 3.5156 | 1 | 3.5156 | 1
220 | Storage room | 418 | 27 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
221 | General Classroom | 324 | 21 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit |  | unk | unk | unk | unk
221B | Storage Room | 135 | 9 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
221C | Storage Room | 130 | 8 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
222 | Biology Classroom | 633 | 42 |  | 1764 | 40 | 40 | Fan Coil Unit & Air Handling Unit | 14112 | 2.6913 | 1 | 2.6913 | 1
223 | Prep Classroom | 322 | 21 |  | 312 | 7 | 7 | Fan Coil Unit & Air Handling Unit | 2496 | 7.7404 | 2 | 7.7404 | 2
224 | Chemistry Classroom | 616 | 41 |  | 1716 | 39 | 39 | Fan Coil Unit & Air Handling Unit | 13728 | 2.6923 | 1 | 2.6923 | 1
224A | Storage Room | 135 | 9 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
225 | Instructional Room | 483 | 32 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit |  | unk | unk | unk | unk
234 | Lab Classroom | 1107 | 73 |  | 850 | 19 | 19 | Fan Coil Unit & Air Handling Unit | 6800 | 9.7676 | 2 | 9.7676 | 2
235 | Lab Classroom | 595 | 39 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit |  | unk | unk | unk | unk
235 | Lab Classroom | 465 | 31 |  |  | 0 | 0 | Univent & Air Handling Unit |  | unk | unk | unk | unk
236 | Multipurpose Classroom | 636 | 42 |  | 1156 | 26 | 26 | Fan Coil Unit & Air Handling Unit | 9248 | 4.1263 | 2 | 4.1263 | 2
237 | Foreign Language Classroom | 613 | 40 |  | 1156 | 26 | 26 | Fan Coil Unit & Air Handling Unit | 9248 | 3.9771 | 1 | 3.9771 | 1
240 | Commercial Art Classroom | 845 | 56 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit |  | unk | unk | unk | unk
241 | General Classroom | 664 | 44 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit |  | unk | unk | unk | unk
242 | Instructional Room | 551 | 36 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit |  | unk | unk | unk | unk
243 | General Classroom | 518 | 34 |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit |  | unk | unk | unk | unk
244 | General Classroom | 737 | 49 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.3897 | 2 | 7.3897 | 2
245 | General Classroom | 586 | 39 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 5.8757 | 2 | 5.8757 | 2
246 | General Classroom | 719 | 47 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.2092 | 2 | 7.2092 | 2
247 | General Classroom | 705 | 47 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.0689 | 2 | 7.0689 | 2
248 | General Classroom | 909 | 60 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 9.1143 | 2 | 9.1143 | 2
249 | General Classroom | 779 | 51 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.8108 | 2 | 7.8108 | 2
251 | General Classroom | 671 | 44 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.7279 | 2 | 6.7279 | 2
252 | General Classroom | 876 | 58 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 8.7834 | 2 | 8.7834 | 2
253 | General Classroom | 608 | 40 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.0963 | 2 | 6.0963 | 2
254 | General Classroom | 633 | 42 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.3469 | 2 | 6.3469 | 2
255 | General Classroom | 738 | 49 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 7.3997 | 2 | 7.3997 | 2
256 | General Classroom | 684 | 45 |  | 748 | 17 | 17 | Univent & Air Handling Unit | 5984 | 6.8583 | 2 | 6.8583 | 2
- | Auditorium | 18527 | 1235 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Cafeteria | 10458 | 697 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Studios Area and Assoc. Corridors, fresh air vent in rooms | 18369 | 1224 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Instrumental Music Area | 14678 | 978 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Gym | 8904 | 593 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | ICM Classroom Area | 11044 | 736 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | Walter Biddle Saul High School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
A1 | A1 | 732 | 48 |  | 864 | 19 | 19 | Air Handling Unit | 6912 | 6.3542 | 2 | 6.3542 | 2
A1/A2 | Storage | 288 | 19 |  | 255 | 5 | 5 | Air Handling Unit | 2040 | 8.4706 | 2 | 8.4706 | 2
A2 | A2 | 703 | 46 |  | 864 | 19 | 19 | Air Handling Unit | 6912 | 6.1024 | 2 | 6.1024 | 2
A3 | A3 | 395 | 26 |  | 792 | 18 | 18 | Univent | 6336 | 3.7405 | 1 | 3.7405 | 1
A5 | A5 | 1123 | 74 |  | 740 | 16 | 16 | Univent | 5920 | 11.3818 | 3 | 11.3818 | 3
A21 | A21 | 0 | 0 |  | 570 | 12 | 0 | Air Handling Unit | 4560 | 0 | 0 | 0 | 0
A22 | A22 | 487 | 32 |  | 620 | 14 | 14 | Univent | 4960 | 5.8911 | 2 | 5.8911 | 2
A23 | A23 | 699 | 46 |  | 888 | 20 | 20 | Univent | 7104 | 5.9037 | 2 | 5.9037 | 2
A24 | A24 | 1147 | 76 |  | 888 | 20 | 20 | Univent | 7104 | 9.6875 | 2 | 9.6875 | 2
A25 | A25 | 878 | 58 |  | 888 | 20 | 20 | Univent | 7104 | 7.4155 | 2 | 7.4155 | 2
A26 | A26 | 449 | 29 |  | 888 | 20 | 20 | Univent | 7104 | 3.7922 | 1 | 3.7922 | 1
A29 | A29 |  | 0 | Yes | 864 | 19 | 19 |  | 6912 | unk | unk | 20 | 3
1 | 1 | 240 | 16 |  | 864 | 19 | 19 | Univent | 6912 | 2.0833 | 1 | 2.0833 | 1
2 | 2 | 70 | 4 |  | 551 | 12 | 12 | Univent | 4408 | 0.95281 | 0 | 0.95281 | 0
3 | 3 | 900 | 60 |  | 1134 | 25 | 25 | Univent | 9072 | 5.9524 | 2 | 5.9524 | 2
4 | 4 | 0 | 0 |  | 896 | 20 | 0 | Univent | 7168 | 0 | 0 | 0 | 0
100 | 100 | 215 | 14 |  | 620 | 14 | 14 | Univent | 4960 | 2.6008 | 1 | 2.6008 | 1
102 | 102 | 342 | 22 |  | 620 | 14 | 14 | Univent | 4960 | 4.1371 | 2 | 4.1371 | 2
103 | 103 | 206 | 13 |  | 780 | 17 | 17 | Univent | 6240 | 1.9808 | 1 | 1.9808 | 1
104 | 104 | 265 | 17 |  | 640 | 14 | 14 | Univent | 5120 | 3.1055 | 1 | 3.1055 | 1
200 | 200 | 258 | 17 |  | 620 | 14 | 14 | Univent | 4960 | 3.121 | 1 | 3.121 | 1
201 | 201 | 244 | 16 |  | 620 | 14 | 14 | Univent | 4960 | 2.9516 | 1 | 2.9516 | 1
202 | 202 | 251 | 16 |  | 620 | 14 | 14 | Univent | 4960 | 3.0363 | 1 | 3.0363 | 1
203 | 203 | 173 | 11 |  | 620 | 14 | 14 | Univent | 4960 | 2.0927 | 1 | 2.0927 | 1
204 | 204 | 226 | 15 |  | 620 | 14 | 14 | Univent | 4960 | 2.7339 | 1 | 2.7339 | 1
205 | 205 | 468 | 31 |  | 660 | 15 | 15 | Univent | 5280 | 5.3182 | 2 | 5.3182 | 2
206 | 206 | 560 | 37 |  | 110 | 2 | 2 | Univent | 880 | 38.1818 | 4 | 38.1818 | 4
208 | 208 | 232 | 15 |  | 600 | 13 | 13 | Univent | 4800 | 2.9 | 1 | 2.9 | 1
210 | 210 | 244 | 16 |  | 465 | 10 | 10 | Univent | 3720 | 3.9355 | 1 | 3.9355 | 1
Food Science | Laboratory |  | 0 |  | 560 | 12 | 12 |  | 4480 | unk | unk | unk | unk
- | Nurse | 316 | 21 |  | 260 | 5 | 5 | Univent | 2080 | 9.1154 | 2 | 9.1154 | 2
- | Staff Lounge | 0 | 0 |  | 384 | 8 | 0 | Univent | 3072 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-05-03 | [8 empty] | unk | unk | unk | unk
School: | William L. Sayre High School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 518 | 34 |  | 720 | 16 | 16 | Univent | 5760 | 5.3958 | 2 | 5.3958 | 2
102 | Lounge | 229 | 15 |  | 408 | 9 | 9 | Univent | 3264 | 4.2096 | 2 | 4.2096 | 2
103 | Music | 327 | 21 |  | 1260 | 28 | 28 | Univent | 10080 | 1.9464 | 1 | 1.9464 | 1
104 | Office | 0 | 0 |  | 360 | 8 | 0 | Univent | 2880 | 0 | 0 | 0 | 0
105 | Classroom | 375 | 25 |  | 1504 | 34 | 34 | Univent | 12032 | 1.87 | 1 | 1.87 | 1
106 | Classroom | 389 | 25 |  | 768 | 17 | 17 | Univent | 6144 | 3.7988 | 1 | 3.7988 | 1
107 | Classroom | 517 | 34 |  | 1408 | 32 | 32 | Univent | 11264 | 2.7539 | 1 | 2.7539 | 1
108 | Classroom | 0 | 0 |  | 768 | 17 | 0 | Univent | 6144 | 0 | 0 | 0 | 0
109 | Classroom | 0 | 0 | Yes | 1120 | 25 | 25 | Univent | 8960 | 0 | 0 | 20 | 3
110 | Classroom | 351 | 23 |  | 768 | 17 | 17 | Univent | 6144 | 3.4277 | 1 | 3.4277 | 1
111 | Classroom | 638 | 42 |  | 1363 | 30 | 30 | Univent | 10904 | 3.5106 | 1 | 3.5106 | 1
115 | Classroom | 369 | 24 |  | 896 | 20 | 20 | Univent | 7168 | 3.0887 | 1 | 3.0887 | 1
117 | Classroom | 0 | 0 | Yes | 756 | 17 | 17 | Univent | 6048 | 0 | 0 | 20 | 3
119 | Classroom | 192 | 12 |  | 868 | 19 | 19 | Univent | 6944 | 1.659 | 1 | 1.659 | 1
131 | Classroom | 402 | 26 |  | 729 | 16 | 16 | Univent | 5832 | 4.1358 | 2 | 4.1358 | 2
133 | Office | 357 | 23 |  | 288 | 6 | 6 | Univent | 2304 | 9.2969 | 2 | 9.2969 | 2
135 | Boy's Infirmary | 287 | 19 |  | 132 | 3 | 3 | Univent | 1056 | 16.3068 | 3 | 16.3068 | 3
137 | Girl's Infirmary | 142 | 9 |  | 285 | 6 | 6 | Univent | 2280 | 3.7368 | 1 | 3.7368 | 1
139 | Classroom | 202 | 13 |  | 1024 | 23 | 23 | Univent | 8192 | 1.4795 | 1 | 1.4795 | 1
141 | Classroom | 384 | 25 |  | 1188 | 27 | 27 | Univent | 9504 | 2.4242 | 1 | 2.4242 | 1
200 | Youth Court | 693 | 46 |  | 744 | 16 | 16 | Univent | 5952 | 6.9859 | 2 | 6.9859 | 2
200 | Classroom | 410 | 27 |  | 592 | 13 | 13 | Univent | 4736 | 5.1943 | 2 | 5.1943 | 2
203 | Classroom | 808 | 53 |  | 1504 | 34 | 34 | Univent | 12032 | 4.0293 | 2 | 4.0293 | 2
204 | Classroom | 294 | 19 |  | 744 | 16 | 16 | Univent | 5952 | 2.9637 | 1 | 2.9637 | 1
205 | Classroom | 762 | 50 |  | 1504 | 34 | 34 | Univent | 12032 | 3.7999 | 1 | 3.7999 | 1
206 | Classroom | 473 | 31 |  | 696 | 15 | 15 | Univent | 5568 | 5.097 | 2 | 5.097 | 2
207 | Classroom | 702 | 46 |  | 1280 | 29 | 29 | Univent | 10240 | 4.1133 | 2 | 4.1133 | 2
208 | Classroom | 548 | 36 |  | 744 | 16 | 16 | Univent | 5952 | 5.5242 | 2 | 5.5242 | 2
210 | Classroom | 246 | 16 |  | 744 | 16 | 16 | Univent | 5952 | 2.4798 | 1 | 2.4798 | 1
211 | Classroom | 835 | 55 |  | 1344 | 30 | 30 | Univent | 10752 | 4.6596 | 2 | 4.6596 | 2
212 | Classroom | 367 | 24 |  | 744 | 16 | 16 | Univent | 5952 | 3.6996 | 1 | 3.6996 | 1
215 | Classroom | 0 | 0 |  | 621 | 14 | 0 | Univent | 4968 | 0 | 0 | 0 | 0
216 | Classroom | 731 | 48 |  | 864 | 19 | 19 | Univent | 6912 | 6.3455 | 2 | 6.3455 | 2
217 | Classroom | 81 | 5 |  | 990 | 22 | 22 | Univent | 7920 | 0.61364 | 0 | 0.61364 | 0
219 | Classroom | 0 | 0 |  | 1008 | 22 | 0 | Univent | 8064 | 0 | 0 | 0 | 0
220 | Classroom | 301 | 20 |  | 744 | 16 | 16 | Univent | 5952 | 3.0343 | 1 | 3.0343 | 1
221 | Classroom | 92 | 6 |  | 987 | 22 | 22 | Univent | 7896 | 0.69909 | 0 | 0.69909 | 0
222 | Classroom | 623 | 41 |  | 744 | 16 | 16 | Univent | 5952 | 6.2802 | 2 | 6.2802 | 2
223 | Classroom | 0 | 0 |  | 902 | 20 | 0 | Univent | 7216 | 0 | 0 | 0 | 0
224 | Classroom | 419 | 27 |  | 744 | 16 | 16 | Univent | 5952 | 4.2238 | 2 | 4.2238 | 2
225 | Classroom | 264 | 17 |  | 725 | 16 | 16 | Univent | 5800 | 2.731 | 1 | 2.731 | 1
226 | Classroom | 0 | 0 |  | 744 | 16 | 0 | Univent | 5952 | 0 | 0 | 0 | 0
228 | Classroom | 202 | 13 |  | 840 | 19 | 19 | Univent | 6720 | 1.8036 | 1 | 1.8036 | 1
229 | Classroom | 401 | 26 |  | 1458 | 33 | 33 | Univent | 11664 | 2.0628 | 1 | 2.0628 | 1
230 | Classroom | 797 | 53 |  | 792 | 18 | 18 | Univent | 6336 | 7.5473 | 2 | 7.5473 | 2
231 | Classroom | 509 | 33 |  | 999 | 22 | 22 | Univent | 7992 | 3.8213 | 1 | 3.8213 | 1
232 | Classroom | 1571 | 104 |  | 960 | 21 | 21 | Univent | 7680 | 12.2734 | 3 | 12.2734 | 3
234 | Classroom | 1041 | 69 |  | 816 | 18 | 18 | Univent | 6528 | 9.568 | 2 | 9.568 | 2
235 | Classroom | 778 | 51 |  | 1400 | 31 | 31 | Univent | 11200 | 4.1679 | 2 | 4.1679 | 2
236 | Classroom | 809 | 53 |  | 744 | 16 | 16 | Univent | 5952 | 8.1552 | 2 | 8.1552 | 2
240 | Classroom | 683 | 45 |  | 696 | 15 | 15 | Univent | 5568 | 7.3599 | 2 | 7.3599 | 2
242 | Classroom | 274 | 18 |  | 912 | 20 | 20 | Univent | 7296 | 2.2533 | 1 | 2.2533 | 1
244 | Classroom | 0 | 0 |  | 768 | 17 | 0 | Univent | 6144 | 0 | 0 | 0 | 0
246 | Classroom | 415 | 27 |  | 936 | 21 | 21 | Univent | 7488 | 3.3253 | 1 | 3.3253 | 1
248 | Classroom | 0 | 0 |  | 666 | 15 | 0 | Univent | 5328 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 |  | 10250 | 232 | 0 | House Fan | 82000 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 |  | 10540 | 239 | 0 | House Fan | 84320 | 0 | 0 | 0 | 0
- | Counseling Office | 234 | 15 |  | 187 | 4 | 4 | Univent | 1496 | 9.385 | 2 | 9.385 | 2
- | Girls Gym | 0 | 0 | Yes | 7630 | 173 | 173 | House Fan | 61040 | 0 | 0 | 20 | 3
- | Boys Gym | 0 | 0 | Yes | 7630 | 173 | 173 | House Fan | 61040 | 0 | 0 | 20 | 3
- | Handball Court | 0 | 0 |  | 800 | 18 | 0 | Air Handling Unit | 6400 | 0 | 0 | 0 | 0
- | Library | 0 | 0 |  | 3432 | 78 | 0 | Univent | 27456 | 0 | 0 | 0 | 0
- | IMC Computer | 0 | 0 |  | 744 | 16 | 0 | Univent | 5952 | 0 | 0 | 0 | 0
- | Kitchen Cooler room | 0 | 0 |  | 182 | 4 | 0 | Univent | 1456 | 0 | 0 | 0 | 0
- | Locker room | 0 | 0 |  | 180 | 4 | 0 | Air Handling Unit & Univent | 1440 | 0 | 0 | 0 | 0
- | Boys Locker Rm | 0 | 0 |  | 7470 | 169 | 0 | Whole House | 59760 | 0 | 0 | 0 | 0
[8 empty] | Return Air Fan & Air Handling Unit |  | unk | unk | unk | unk
- | Girls Locker Rm | 0 | 0 |  | 7470 | 169 | 0 | Whole House | 59760 | 0 | 0 | 0 | 0
[8 empty] | Return Air Fan & Air Handling Unit |  | unk | unk | unk | unk
- | Main Office | 153 | 10 |  | 1128 | 25 | 25 | Univent | 9024 | 1.0173 | 1 | 1.0173 | 1
- | Office | 0 | 0 |  | 198 | 4 | 0 | Univent | 1584 | 0 | 0 | 0 | 0
- | Rec Room | 0 | 0 |  | 9780 | 222 | 0 | House Fan | 78240 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | High School of the Future | [8 empty] | unk | unk | unk | unk
Vendor: | Meehan | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Auditorium | 4278 | 285 |  | 4935 | 112 | 112 | Air Handling Unit | 39480 | 6.5015 | 2 | 6.5015 | 2
10 | Mens Room | 139 | 9 |  | 205 | 4 | 4 | Air Handling Unit | 1640 | 5.0854 | 2 | 5.0854 | 2
12 | Womens Room | 88 | 5 |  | 215 | 4 | 4 | Air Handling Unit | 1720 | 3.0698 | 1 | 3.0698 | 1
14 | Storage | 26 | 1 |  | 275 | 6 | 6 | Air Handling Unit | 2200 | 0.70909 | 0 | 0.70909 | 0
16 | IDF | 15 | 1 |  | 165 | 3 | 3 | Air Handling Unit | 1320 | 0.68182 | 0 | 0.68182 | 0
17 | Electrical room | 40 | 2 |  | 75 | 1 | 1 | Air Handling Unit | 600 | 4 | 1 | 4 | 1
19 | Music Library | 30 | 2 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 1.875 | 1 | 1.875 | 1
21 | Instrument stroage | 96 | 6 |  | 370 | 8 | 8 | Air Handling Unit | 2960 | 1.9459 | 1 | 1.9459 | 1
22 | Uniform Room | 49 | 3 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 3.675 | 1 | 3.675 | 1
23 | Practice room | 41 | 2 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 3.075 | 1 | 3.075 | 1
24 | Practice room | 42 | 2 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 3.15 | 1 | 3.15 | 1
25 | Practice room | 43 | 2 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 3.225 | 1 | 3.225 | 1
26 | Vocal Music Room | 184 | 12 |  | 1400 | 31 | 31 | Air Handling Unit | 11200 | 0.98571 | 0 | 0.98571 | 0
27 | Practice Room | 27 | 1 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 2.025 | 1 | 2.025 | 1
28 | Practice Room | 36 | 2 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 2.7 | 1 | 2.7 | 1
29 | Practice Room | 41 | 2 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 3.075 | 1 | 3.075 | 1
30 | Dressing Room | 45 | 3 |  | 1300 | 29 | 29 | Air Handling Unit | 10400 | 0.25962 | 0 | 0.25962 | 0
31 | Music Intrrument room | 966 | 64 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | 4.025 | 2 | 4.025 | 2
32 | Dressing Room | 104 | 6 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.86667 | 0 | 0.86667 | 0
33 | Dressing Room | 45 | 3 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | 1.125 | 1 | 1.125 | 1
34 | Scene shop | 537 | 35 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 3.3563 | 1 | 3.3563 | 1
58 | Kitchen |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
101 | Vestibule | 102 | 6 |  | 555 | 12 | 12 | Air Handling Unit | 4440 | 1.3784 | 1 | 1.3784 | 1
103 | Camera Room | 49 | 3 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 3.675 | 1 | 3.675 | 1
104 | Security Room | 59 | 3 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 2.2125 | 1 | 2.2125 | 1
105 | Corridor |  | 0 |  | 50 | 1 | 1 | Air Handling Unit | 400 | unk | unk | unk | unk
106 | Electric room | 63 | 4 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 3.5 | 1 | 3.5 | 1
107 | Equipment room | 55 | 3 |  | 205 | 4 | 4 | Air Handling Unit | 1640 | 2.0122 | 1 | 2.0122 | 1
110 | waiting room | 101 | 6 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 3.7875 | 1 | 3.7875 | 1
112 | clerical office | 315 | 21 |  | 635 | 14 | 14 | Air Handling Unit | 5080 | 3.7205 | 1 | 3.7205 | 1
113 | work/ conf room | 97 | 6 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 3.6375 | 1 | 3.6375 | 1
114 | Admin conf room | 81 | 5 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 3.0375 | 1 | 3.0375 | 1
115 | Principal office | 80 | 5 |  | 255 | 5 | 5 | Air Handling Unit | 2040 | 2.3529 | 1 | 2.3529 | 1
115A | Principal bathroom | 8 | 0 |  | 60 | 1 | 1 | Air Handling Unit | 480 | 1 | 0 | 1 | 0
117 | Operations office | 24 | 1 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 1.5 | 1 | 1.5 | 1
118 | vault room | 25 | 1 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 0.9375 | 0 | 0.9375 | 0
119 | supply room | 12 | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 0.75 | 0 | 0.75 | 0
121 | Nurse | 38 | 2 |  | 95 | 2 | 2 | Air Handling Unit | 760 | 3 | 1 | 3 | 1
121 | Waiting room | 17 | 1 |  | 95 | 2 | 2 | Air Handling Unit | 760 | 1.3421 | 1 | 1.3421 | 1
123 | Nurse office | 14 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
125 | Exam room B | 14 | 0 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 1.05 | 1 | 1.05 | 1
125 | Exam room A | 13 | 0 |  | 100 | 2 | 2 | Air Handling Unit | 800 | 0.975 | 0 | 0.975 | 0
130 | Parent volunteer room | 13 | 0 |  | 480 | 10 | 10 | Air Handling Unit | 3840 | 0.20312 | 0 | 0.20312 | 0
130 | Parent volunteer room | 13 | 0 |  | 480 | 10 | 10 | Air Handling Unit | 3840 | 0.20312 | 0 | 0.20312 | 0
131 | Plasma screen room | 9 | 0 |  | 45 | 1 | 1 | Air Handling Unit | 360 | 1.5 | 1 | 1.5 | 1
131 | Janitor closet |  | 0 |  | 30 | 0 | 0 | Air Handling Unit | 240 | unk | unk | unk | unk
132 | Womens room | 25 | 1 |  | 220 | 5 | 5 | Air Handling Unit | 1760 | 0.85227 | 0 | 0.85227 | 0
132 | Womens Room | 20 | 1 |  | 220 | 5 | 5 | Air Handling Unit | 1760 | 0.68182 | 0 | 0.68182 | 0
132 | Womens room |  | 0 |  | 220 | 5 | 5 | Air Handling Unit | 1760 | unk | unk | unk | unk
132 | Womens room |  | 0 |  | 220 | 5 | 5 | Air Handling Unit | 1760 | unk | unk | unk | unk
133 | Mens room | 49 | 3 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | 1.5 | 1 | 1.5 | 1
133 | Mens room | 38 | 2 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | 1.1633 | 1 | 1.1633 | 1
135 | Mens Room |  | 0 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | unk | unk | unk | unk
135 | Mens Room |  | 0 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | unk | unk | unk | unk
139 | Mens locker | 14 | 0 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0.28 | 0 | 0.28 | 0
139 | Mens Locker | 14 | 0 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0.28 | 0 | 0.28 | 0
139 | Mens Locker | 15 | 1 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0.3 | 0 | 0.3 | 0
139 | Mens Locker | 15 | 1 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0.3 | 0 | 0.3 | 0
139 | Mens Locker room |  | 0 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | unk | unk | unk | unk
139 | Mens locaker room |  | 0 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | unk | unk | unk | unk
140 | office | 48 | 3 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | 1.2 | 1 | 1.2 | 1
140 | office |  | 0 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | unk | unk | unk | unk
141 | toilet room | 9 | 0 |  | 90 | 2 | 2 | Air Handling Unit | 720 | 0.75 | 0 | 0.75 | 0
141 | toilet room |  | 0 |  | 90 | 2 | 2 | Air Handling Unit | 720 | unk | unk | unk | unk
142 | Training room | 20 | 1 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0.4 | 0 | 0.4 | 0
142 | Training room | 22 | 1 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | 0.44 | 0 | 0.44 | 0
142 | training room |  | 0 |  | 375 | 8 | 8 | Air Handling Unit | 3000 | unk | unk | unk | unk
143 | Womens Locker | 14 | 0 |  | 750 | 17 | 14 | Air Handling Unit | 6000 | 0.14 | 0 | 0.14 | 0
143 | Womens Locker | 14 | 0 |  | 750 | 17 | 14 | Air Handling Unit | 6000 | 0.14 | 0 | 0.14 | 0
143 | Womens Locker | 15 | 1 |  | 750 | 17 | 15 | Air Handling Unit | 6000 | 0.15 | 0 | 0.15 | 0
143 | Womens LOcker | 16 | 1 |  | 750 | 17 | 16 | Air Handling Unit | 6000 | 0.16 | 0 | 0.16 | 0
143 | Womens locker room |  | 0 |  | 750 | 17 | 17 | Air Handling Unit | 6000 | unk | unk | unk | unk
143 | Womens locker room |  | 0 |  | 750 | 17 | 17 | Air Handling Unit | 6000 | unk | unk | unk | unk
144 | Office | 44 | 2 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | 1.1 | 1 | 1.1 | 1
144 | office |  | 0 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | unk | unk | unk | unk
145 | Toilet Room | 9 | 0 |  | 65 | 1 | 1 | Air Handling Unit | 520 | 1.0385 | 1 | 1.0385 | 1
145 | toilet room |  | 0 |  | 65 | 1 | 1 | Air Handling Unit | 520 | unk | unk | unk | unk
146 | Corridor | 6 | 0 |  | 150 | 3 | 3 | Air Handling Unit | 1200 | 0.3 | 0 | 0.3 | 0
146 | corridor |  | 0 |  | 150 | 3 | 3 | Air Handling Unit | 1200 | unk | unk | unk | unk
147 | Fitness center | 44 | 2 |  | 1545 | 35 | 35 | Air Handling Unit | 12360 | 0.21359 | 0 | 0.21359 | 0
147 | Fitness center | 62 | 4 |  | 1545 | 35 | 35 | Air Handling Unit | 12360 | 0.30097 | 0 | 0.30097 | 0
147 | Fitness center | 47 | 3 |  | 1545 | 35 | 35 | Air Handling Unit | 12360 | 0.22816 | 0 | 0.22816 | 0
147 | Fitness center |  | 0 |  | 1545 | 35 | 35 | Air Handling Unit | 12360 | unk | unk | unk | unk
147 | Fitness center |  | 0 |  | 1545 | 35 | 35 | Air Handling Unit | 12360 | unk | unk | unk | unk
147 | Fitness center |  | 0 |  | 1545 | 35 | 35 | Air Handling Unit | 12360 | unk | unk | unk | unk
148 | Visitor locker room | 39 | 2 |  | 485 | 11 | 11 | Air Handling Unit | 3880 | 0.60309 | 0 | 0.60309 | 0
148 | Visitor locker room | 44 | 2 |  | 485 | 11 | 11 | Air Handling Unit | 3880 | 0.68041 | 0 | 0.68041 | 0
148 | visitor locaker room |  | 0 |  | 485 | 11 | 11 | Air Handling Unit | 3880 | unk | unk | unk | unk
148 | Visitor locaker room |  | 0 |  | 485 | 11 | 11 | Air Handling Unit | 3880 | unk | unk | unk | unk
148 | visitor locker room |  | 0 |  | 485 | 11 | 11 | Air Handling Unit | 3880 | unk | unk | unk | unk
149 | IDF | 15 | 1 |  | 50 | 1 | 1 | Air Handling Unit | 400 | 2.25 | 1 | 2.25 | 1
149 | IDF |  | 0 |  | 50 | 1 | 1 | Air Handling Unit | 400 | unk | unk | unk | unk
150 | work shop |  | 0 |  | 155 | 3 | 3 | Air Handling Unit | 1240 | unk | unk | unk | unk
151 | Custodial office |  | 0 |  | 155 | 3 | 3 | Air Handling Unit | 1240 | unk | unk | unk | unk
152 | Corridor | 34 | 2 |  | 2055 | 46 | 34 | Air Handling Unit | 16440 | 0.12409 | 0 | 0.12409 | 0
152 | Corridor | 28 | 1 |  | 2055 | 46 | 28 | Air Handling Unit | 16440 | 0.10219 | 0 | 0.10219 | 0
152 | Corridor | 28 | 1 |  | 2055 | 46 | 28 | Air Handling Unit | 16440 | 0.10219 | 0 | 0.10219 | 0
155 | Corridor |  | 0 |  | 145 | 3 | 3 | Air Handling Unit | 1160 | unk | unk | unk | unk
156 | Locker room |  | 0 |  | 60 | 1 | 1 | Air Handling Unit | 480 | unk | unk | unk | unk
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | unk | unk | unk | unk
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | unk | unk | unk | unk
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | unk | unk | unk | unk
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | unk | unk | unk | unk
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | unk | unk | unk | unk
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | unk | unk | unk | unk
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | unk | unk | unk | unk
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | unk | unk | unk | unk
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | unk | unk | unk | unk
158 | Dishwashing |  | 0 |  | 390 | 8 | 8 | Air Handling Unit | 3120 | unk | unk | unk | unk
158 | Kitchen |  | 0 |  | 1485 | 33 | 33 | Air Handling Unit | 11880 | unk | unk | unk | unk
160 | Dishwashing |  | 0 |  | 390 | 8 | 8 | Air Handling Unit | 3120 | unk | unk | unk | unk
161 | Serving |  | 0 |  | 695 | 15 | 15 | Air Handling Unit | 5560 | unk | unk | unk | unk
161 | Serving |  | 0 |  | 695 | 15 | 15 | Air Handling Unit | 5560 | unk | unk | unk | unk
161 | Serving |  | 0 |  | 695 | 15 | 15 | Air Handling Unit | 5560 | unk | unk | unk | unk
162 | Kitchen office |  | 0 |  | 80 | 1 | 1 | Air Handling Unit | 640 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
163 | Cafeteria |  | 0 |  | 7850 | 178 | 178 | Air Handling Unit | 62800 | unk | unk | unk | unk
164 | Faculty dining |  | 0 |  | 610 | 13 | 13 | Air Handling Unit | 4880 | unk | unk | unk | unk
164 | Faculty dining |  | 0 |  | 610 | 13 | 13 | Air Handling Unit | 4880 | unk | unk | unk | unk
166 | Mens Room | 71 | 4 |  | 220 | 5 | 5 | Air Handling Unit | 1760 | 2.4205 | 1 | 2.4205 | 1
167 | Womens Room | 50 | 3 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | 1.5306 | 1 | 1.5306 | 1
170 | Special Education | 24 | 1 |  | 1205 | 27 | 24 | Air Handling Unit | 9640 | 0.14938 | 0 | 0.14938 | 0
170 | Special Education | 21 | 1 |  | 1205 | 27 | 21 | Air Handling Unit | 9640 | 0.13071 | 0 | 0.13071 | 0
170 | Special Education | 31 | 2 |  | 1205 | 27 | 27 | Air Handling Unit | 9640 | 0.19295 | 0 | 0.19295 | 0
170 | Special Education | 30 | 2 |  | 1205 | 27 | 27 | Air Handling Unit | 9640 | 0.18672 | 0 | 0.18672 | 0
173 | Driver education lab | 70 | 4 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0.4375 | 0 | 0.4375 | 0
173 | Driver education lab | 70 | 4 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0.4375 | 0 | 0.4375 | 0
173 | Driver education lab | 69 | 4 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0.43125 | 0 | 0.43125 | 0
173 | Driver education lab | 65 | 4 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | 0.40625 | 0 | 0.40625 | 0
174 | Science Prep | 59 | 3 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 2.2125 | 1 | 2.2125 | 1
175 | Science Lab | 55 | 3 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.27409 | 0 | 0.27409 | 0
175 | Science LAB | 54 | 3 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.2691 | 0 | 0.2691 | 0
175 | science lab | 47 | 3 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.23422 | 0 | 0.23422 | 0
175 | science lab | 41 | 2 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.20432 | 0 | 0.20432 | 0
175 | science lab | 59 | 3 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.29402 | 0 | 0.29402 | 0
175 | science lab | 63 | 4 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.31395 | 0 | 0.31395 | 0
177 | table storage | 0 | 0 |  | 610 | 13 | 0 | Air Handling Unit | 4880 | 0 | 0 | 0 | 0
177 | table storage | 0 | 0 |  | 610 | 13 | 0 | Air Handling Unit | 4880 | 0 | 0 | 0 | 0
178 | teacher storage | 0 | 0 |  | 125 | 2 | 0 | Air Handling Unit | 1000 | 0 | 0 | 0 | 0
179 | services room | 0 | 0 |  | 160 | 3 | 0 | Air Handling Unit | 1280 | 0 | 0 | 0 | 0
180 | IDF closet | 0 | 0 |  | 155 | 3 | 0 | Air Handling Unit | 1240 | 0 | 0 | 0 | 0
181 | School store | 0 | 0 |  | 200 | 4 | 0 | Air Handling Unit | 1600 | 0 | 0 | 0 | 0
183 | Computer lab |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | unk | unk | unk | unk
183 | Computer lab | 374 | 24 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 3.1167 | 1 | 3.1167 | 1
183 | Computer lab | 362 | 24 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 3.0167 | 1 | 3.0167 | 1
183 | Computer lab | 477 | 31 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 3.975 | 1 | 3.975 | 1
183 | Computer lab | 477 | 31 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 3.975 | 1 | 3.975 | 1
184 | Interactive learning center | 667 | 44 |  | 2800 | 63 | 63 | Air Handling Unit | 22400 | 1.7866 | 1 | 1.7866 | 1
184 | Interactive learning center | 473 | 31 |  | 2800 | 63 | 63 | Air Handling Unit | 22400 | 1.267 | 1 | 1.267 | 1
184 | Interactive learning center | 570 | 38 |  | 2800 | 63 | 63 | Air Handling Unit | 22400 | 1.5268 | 1 | 1.5268 | 1
184 | Interactive learning center | 536 | 35 |  | 2800 | 63 | 63 | Air Handling Unit | 22400 | 1.4357 | 1 | 1.4357 | 1
184 | Interactive learning center | 417 | 27 |  | 2800 | 63 | 63 | Air Handling Unit | 22400 | 1.117 | 1 | 1.117 | 1
185 | Individual reading | 37 | 2 |  | 390 | 8 | 8 | Air Handling Unit | 3120 | 0.71154 | 0 | 0.71154 | 0
185 | Individual reading | 32 | 2 |  | 390 | 8 | 8 | Air Handling Unit | 3120 | 0.61538 | 0 | 0.61538 | 0
185 | Individual reading | 27 | 1 |  | 390 | 8 | 8 | Air Handling Unit | 3120 | 0.51923 | 0 | 0.51923 | 0
185 | Individual reading | 31 | 2 |  | 390 | 8 | 8 | Air Handling Unit | 3120 | 0.59615 | 0 | 0.59615 | 0
186 | Literacy Nook | 35 | 2 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.29167 | 0 | 0.29167 | 0
186 | Literacy Nook | 28 | 1 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.23333 | 0 | 0.23333 | 0
186 | Literacy Nook | 20 | 1 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.16667 | 0 | 0.16667 | 0
186 | Literacy Nook | 20 | 1 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.16667 | 0 | 0.16667 | 0
186 | Literacy Nook | 20 | 1 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.16667 | 0 | 0.16667 | 0
186 | Literacy Nook | 20 | 1 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.16667 | 0 | 0.16667 | 0
186 | Literacy Nook | 30 | 2 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.25 | 0 | 0.25 | 0
186 | Literacy Nook | 14 | 0 |  | 900 | 20 | 14 | Air Handling Unit | 7200 | 0.11667 | 0 | 0.11667 | 0
187 | Copy Room | 111 | 7 |  | 250 | 5 | 5 | Air Handling Unit | 2000 | 3.33 | 1 | 3.33 | 1
187 | Copy Room | 86 | 5 |  | 250 | 5 | 5 | Air Handling Unit | 2000 | 2.58 | 1 | 2.58 | 1
188 | Conference room | 87 | 5 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 3.2625 | 1 | 3.2625 | 1
188 | Conferenceroom | 90 | 6 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 3.375 | 1 | 3.375 | 1
189 | Visitor room | 165 | 11 |  | 605 | 13 | 13 | Air Handling Unit | 4840 | 2.0455 | 1 | 2.0455 | 1
189 | Visitor room | 202 | 13 |  | 605 | 13 | 13 | Air Handling Unit | 4840 | 2.5041 | 1 | 2.5041 | 1
189 | Visitor room | 177 | 11 |  | 605 | 13 | 13 | Air Handling Unit | 4840 | 2.1942 | 1 | 2.1942 | 1
190 | ILC office | 120 | 8 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 6.6667 | 2 | 6.6667 | 2
191 | storage | 112 | 7 |  | 170 | 3 | 3 | Air Handling Unit | 1360 | 4.9412 | 2 | 4.9412 | 2
192 |  | 1210 |  |  |  |  | 1210 | Air Handling Unit |  | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
192 | School street |  | 0 |  | 9910 | 225 | 225 | Air Handling Unit | 79280 | unk | unk | unk | unk
201 | Computer tech |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | unk | unk | unk | unk
201 | Computer tech |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | unk | unk | unk | unk
201 | Computer tech |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | unk | unk | unk | unk
203 | Teachers Copy center |  | 0 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | unk | unk | unk | unk
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit | 9520 | unk | unk | unk | unk
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit | 9520 | unk | unk | unk | unk
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit | 9520 | unk | unk | unk | unk
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit | 9520 | unk | unk | unk | unk
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit | 9520 | unk | unk | unk | unk
204 | IT Web Design |  | 0 |  | 1190 | 27 | 27 | Air Handling Unit | 9520 | unk | unk | unk | unk
205 | Storage |  | 0 |  | 150 | 3 | 3 | Air Handling Unit | 1200 | unk | unk | unk | unk
207 | Clerical |  | 0 |  | 100 | 2 | 2 | Air Handling Unit | 800 | unk | unk | unk | unk
207 | Clerical |  | 0 |  | 100 | 2 | 2 | Air Handling Unit | 800 | unk | unk | unk | unk
208 | Office |  | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | unk | unk | unk | unk
209 | Roster Room |  | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | unk | unk | unk | unk
210 |  |  |  |  | 200 |  | 0 | Air Handling Unit | 1600 | unk | unk | unk | unk
211 |  |  |  |  | 200 |  | 0 | Air Handling Unit | 1600 | unk | unk | unk | unk
212 | Staff Room |  | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | unk | unk | unk | unk
213 | Staff Room |  | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | unk | unk | unk | unk
214 | Assistant Principle office |  | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | unk | unk | unk | unk
215 |  |  |  |  | 120 |  | 0 | Air Handling Unit | 960 | unk | unk | unk | unk
216 | Rest Room |  | 0 |  | 50 | 1 | 1 | Air Handling Unit | 400 | unk | unk | unk | unk
217 | Records |  | 0 |  | 300 | 6 | 6 | Air Handling Unit | 2400 | unk | unk | unk | unk
218 |  |  |  |  | 120 |  | 0 | Air Handling Unit | 960 | unk | unk | unk | unk
219 | PE Director |  | 0 |  | 150 | 3 | 3 | Air Handling Unit | 1200 | unk | unk | unk | unk
220 |  |  |  |  | 150 |  | 0 | Air Handling Unit | 1200 | unk | unk | unk | unk
221 |  |  |  |  | 120 |  | 0 | Air Handling Unit | 960 | unk | unk | unk | unk
222 |  |  |  |  | 120 |  | 0 | Air Handling Unit | 960 | unk | unk | unk | unk
223 | Counselor office |  | 0 |  | 120 | 2 | 2 | Air Handling Unit | 960 | unk | unk | unk | unk
224 | Success center |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | unk | unk | unk | unk
224 | Success center |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | unk | unk | unk | unk
224 | Success center |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | unk | unk | unk | unk
224 | Success center |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | unk | unk | unk | unk
225 |  |  |  |  | 450 |  | 0 | Air Handling Unit | 3600 | unk | unk | unk | unk
225 |  |  |  |  | 450 |  | 0 | Air Handling Unit | 3600 | unk | unk | unk | unk
226 | Computer flex lab |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | unk | unk | unk | unk
226 | Computer flex lab |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | unk | unk | unk | unk
226 | Computer flex lab |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | unk | unk | unk | unk
226 | Computer flex lab |  | 0 |  | 1200 | 27 | 27 | Air Handling Unit | 9600 | unk | unk | unk | unk
227 | General classroom |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | unk | unk | unk | unk
227 | General Classroom |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | unk | unk | unk | unk
227 | General Classroom |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | unk | unk | unk | unk
227 | General Classroom |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | unk | unk | unk | unk
228 | Art Storage |  | 0 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | unk | unk | unk | unk
229 | [6 empty] | 0 | Air Handling Unit |  | unk | unk | unk | unk
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | unk | unk | unk | unk
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | unk | unk | unk | unk
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | unk | unk | unk | unk
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | unk | unk | unk | unk
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | unk | unk | unk | unk
230 | Art room |  | 0 |  | 1800 | 40 | 40 | Air Handling Unit | 14400 | unk | unk | unk | unk
231A | [6 empty] | 0 | Air Handling Unit |  | unk | unk | unk | unk
231A | [6 empty] | 0 | Air Handling Unit |  | unk | unk | unk | unk
231B | Special education |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | unk | unk | unk | unk
231B | Special education |  | 0 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | unk | unk | unk | unk
237 | Mens Room | 57 | 3 |  | 250 | 5 | 5 | Air Handling Unit | 2000 | 1.71 | 1 | 1.71 | 1
240 | Womens Room | 76 | 5 |  | 255 | 5 | 5 | Air Handling Unit | 2040 | 2.2353 | 1 | 2.2353 | 1
241 | Storage | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit | 7200 | 0 | 0 | 0 | 0
241 | Storage | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit | 7200 | 0 | 0 | 0 | 0
241 | Storage | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit | 7200 | 0 | 0 | 0 | 0
241 | Storage | 0 | 0 |  | 900 | 20 | 0 | Air Handling Unit | 7200 | 0 | 0 | 0 | 0
242 | chemistry classroom | 53 | 3 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0.265 | 0 | 0.265 | 0
242 | chemistry classroom | 47 | 3 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0.235 | 0 | 0.235 | 0
242 | chemistry classroom | 51 | 3 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0.255 | 0 | 0.255 | 0
242 | chemistry classroom | 56 | 3 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0.28 | 0 | 0.28 | 0
242 | chemistry classroom | 56 | 3 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0.28 | 0 | 0.28 | 0
242 | chemistry classroom | 41 | 2 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | 0.205 | 0 | 0.205 | 0
243 | Storage | 84 | 5 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 3.15 | 1 | 3.15 | 1
244 | Planning | 72 | 4 |  | 290 | 6 | 6 | Air Handling Unit | 2320 | 1.8621 | 1 | 1.8621 | 1
245 | Biology class | 97 | 6 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | 2.9694 | 1 | 2.9694 | 1
245 | Biology class | 97 | 6 |  | 1290 | 29 | 29 | Air Handling Unit | 10320 | 0.56395 | 0 | 0.56395 | 0
245 | Biology class | 78 | 5 |  | 1290 | 29 | 29 | Air Handling Unit | 10320 | 0.45349 | 0 | 0.45349 | 0
245 | Biology class | 83 | 5 |  | 1290 | 29 | 29 | Air Handling Unit | 10320 | 0.48256 | 0 | 0.48256 | 0
245 | Biology class | 93 | 6 |  | 1290 | 29 | 29 | Air Handling Unit | 10320 | 0.5407 | 0 | 0.5407 | 0
245 | Biology class | 51 | 3 |  | 1290 | 29 | 29 | Air Handling Unit | 10320 | 0.29651 | 0 | 0.29651 | 0
246 | General classroom | 67 | 4 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.55833 | 0 | 0.55833 | 0
246 | General classroom | 50 | 3 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.41667 | 0 | 0.41667 | 0
246 | General classroom | 66 | 4 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.55 | 0 | 0.55 | 0
246 | General classroom | 63 | 4 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.525 | 0 | 0.525 | 0
247 | General classroom | 68 | 4 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.56667 | 0 | 0.56667 | 0
247 | General classroom | 72 | 4 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.6 | 0 | 0.6 | 0
247 | General classroom | 69 | 4 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.575 | 0 | 0.575 | 0
247 | General classroom | 81 | 5 |  | 900 | 20 | 20 | Air Handling Unit | 7200 | 0.675 | 0 | 0.675 | 0
248 | N/A | 107 | 7 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 5.9444 | 2 | 5.9444 | 2
249 | General classroom | 59 | 3 |  | 745 | 16 | 16 | Air Handling Unit | 5960 | 0.59396 | 0 | 0.59396 | 0
249 | General classroom | 62 | 4 |  | 745 | 16 | 16 | Air Handling Unit | 5960 | 0.62416 | 0 | 0.62416 | 0
249 | General classroom | 90 | 6 |  | 745 | 16 | 16 | Air Handling Unit | 5960 | 0.90604 | 0 | 0.90604 | 0
249 | General classroom | 77 | 5 |  | 745 | 16 | 16 | Air Handling Unit | 5960 | 0.77517 | 0 | 0.77517 | 0
250 | General classroom | 68 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.64151 | 0 | 0.64151 | 0
250 | General classroom | 60 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.56604 | 0 | 0.56604 | 0
250 | General classroom | 80 | 5 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.75472 | 0 | 0.75472 | 0
250 | General classroom | 83 | 5 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.78302 | 0 | 0.78302 | 0
251 | N/A | 173 | 11 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
252 | General classroom | 57 | 3 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.53438 | 0 | 0.53438 | 0
252 | General classroom | 56 | 3 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.525 | 0 | 0.525 | 0
252 | General classroom | 88 | 5 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.825 | 0 | 0.825 | 0
252 | General classroom | 79 | 5 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.74062 | 0 | 0.74062 | 0
253 | Corridor | 26 | 1 |  | 6010 | 136 | 26 | Air Handling Unit | 48080 | 0.032446 | 0 | 0.032446 | 0
253 | Corridor | 25 | 1 |  | 6010 | 136 | 25 | Air Handling Unit | 48080 | 0.031198 | 0 | 0.031198 | 0
253 | Corridor | 28 | 1 |  | 6010 | 136 | 28 | Air Handling Unit | 48080 | 0.034942 | 0 | 0.034942 | 0
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
254 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
301 | General classroom |  | 0 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | unk | unk | unk | unk
301 | General classroom |  | 0 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | unk | unk | unk | unk
301 | General classroom |  | 0 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | unk | unk | unk | unk
301 | General classroom |  | 0 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | unk | unk | unk | unk
302 | SPR |  | 0 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
303 | General classroom |  | 0 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | unk | unk | unk | unk
305 | SPR |  | 0 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | unk | unk | unk | unk
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | unk | unk | unk | unk
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | unk | unk | unk | unk
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | unk | unk | unk | unk
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | unk | unk | unk | unk
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | unk | unk | unk | unk
307 | Multi purpose classroom |  | 0 |  | 1500 | 34 | 34 | Air Handling Unit | 12000 | unk | unk | unk | unk
308 | Teacher storage |  | 0 |  | 90 | 2 | 2 | Air Handling Unit | 720 | unk | unk | unk | unk
309 | Resource room |  | 0 |  | 645 | 14 | 14 | Air Handling Unit | 5160 | unk | unk | unk | unk
309 | Resource room |  | 0 |  | 645 | 14 | 14 | Air Handling Unit | 5160 | unk | unk | unk | unk
309 | Resource room |  | 0 |  | 645 | 14 | 14 | Air Handling Unit | 5160 | unk | unk | unk | unk
309 | Resource room |  | 0 |  | 645 | 14 | 14 | Air Handling Unit | 5160 | unk | unk | unk | unk
315 | Electrical room | 27 | 1 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 1.6875 | 1 | 1.6875 | 1
316 | IDF closet | 29 | 1 |  | 170 | 3 | 3 | Air Handling Unit | 1360 | 1.2794 | 1 | 1.2794 | 1
317 | Deans Office | 32 | 2 |  | 140 | 3 | 3 | Air Handling Unit | 1120 | 1.7143 | 1 | 1.7143 | 1
318 | Mens room | 107 | 7 |  | 245 | 5 | 5 | Air Handling Unit | 1960 | 3.2755 | 1 | 3.2755 | 1
321 | Womens Room | 110 | 7 |  | 250 | 5 | 5 | Air Handling Unit | 2000 | 3.3 | 1 | 3.3 | 1
322 | General classroom | 102 | 6 |  | 815 | 18 | 18 | Air Handling Unit | 6520 | 0.93865 | 0 | 0.93865 | 0
322 | General classroom | 105 | 7 |  | 815 | 18 | 18 | Air Handling Unit | 6520 | 0.96626 | 0 | 0.96626 | 0
322 | General classroom | 65 | 4 |  | 815 | 18 | 18 | Air Handling Unit | 6520 | 0.59816 | 0 | 0.59816 | 0
322 | General classroom | 73 | 4 |  | 815 | 18 | 18 | Air Handling Unit | 6520 | 0.67178 | 0 | 0.67178 | 0
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit | 12600 | 0 | 0 | 0 | 0
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit | 12600 | 0 | 0 | 0 | 0
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit | 12600 | 0 | 0 | 0 | 0
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit | 12600 | 0 | 0 | 0 | 0
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit | 12600 | 0 | 0 | 0 | 0
323 | Physics classroom | 0 | 0 |  | 1575 | 35 | 0 | Air Handling Unit | 12600 | 0 | 0 | 0 | 0
324 | Science Prep | 54 | 3 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 2.025 | 1 | 2.025 | 1
324 | Science Prep | 53 | 3 |  | 200 | 4 | 4 | Air Handling Unit | 1600 | 1.9875 | 1 | 1.9875 | 1
325 | Physics classroom | 16 | 1 |  | 1505 | 34 | 16 | Air Handling Unit | 12040 | 0.079734 | 0 | 0.079734 | 0
325 | Physics classroom | 116 | 7 |  | 1505 | 34 | 34 | Air Handling Unit | 12040 | 0.57807 | 0 | 0.57807 | 0
325 | Physics classroom | 14 | 0 |  | 1505 | 34 | 14 | Air Handling Unit | 12040 | 0.069767 | 0 | 0.069767 | 0
325 | Physics classroom | 13 | 0 |  | 1505 | 34 | 13 | Air Handling Unit | 12040 | 0.064784 | 0 | 0.064784 | 0
325 | Physics classroom | 13 | 0 |  | 1505 | 34 | 13 | Air Handling Unit | 12040 | 0.064784 | 0 | 0.064784 | 0
325 | Physics classroom | 14 | 0 |  | 1505 | 34 | 14 | Air Handling Unit | 12040 | 0.069767 | 0 | 0.069767 | 0
326 | General classroom | 86 | 5 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | 0.78182 | 0 | 0.78182 | 0
326 | General classroom | 85 | 5 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | 0.77273 | 0 | 0.77273 | 0
326 | General classroom | 99 | 6 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | 0.9 | 0 | 0.9 | 0
326 | General classroom | 47 | 3 |  | 825 | 18 | 18 | Air Handling Unit | 6600 | 0.42727 | 0 | 0.42727 | 0
327 | General classroom | 64 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.60377 | 0 | 0.60377 | 0
327 | General classroom | 58 | 3 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.54717 | 0 | 0.54717 | 0
327 | General classroom | 62 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.58491 | 0 | 0.58491 | 0
327 | General classroom | 43 | 2 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.40566 | 0 | 0.40566 | 0
328 | N/A | 159 | 10 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 8.8333 | 2 | 8.8333 | 2
329 | General classroom | 64 | 4 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.6 | 0 | 0.6 | 0
329 | General classroom | 59 | 3 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.55312 | 0 | 0.55312 | 0
329 | General classroom | 65 | 4 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 3.6111 | 1 | 3.6111 | 1
329 | General classroom | 68 | 4 |  | 800 | 18 | 18 | Air Handling Unit | 6400 | 0.6375 | 0 | 0.6375 | 0
330 | General classroom | 70 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.66038 | 0 | 0.66038 | 0
330 | General classroom | 64 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.60377 | 0 | 0.60377 | 0
330 | General classroom | 74 | 4 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.69811 | 0 | 0.69811 | 0
330 | General classroom | 81 | 5 |  | 795 | 18 | 18 | Air Handling Unit | 6360 | 0.76415 | 0 | 0.76415 | 0
331 | General classroom | 62 | 4 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 3.4444 | 1 | 3.4444 | 1
331 | General classroom | 69 | 4 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 3.8333 | 1 | 3.8333 | 1
331 | General classroom | 73 | 4 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 4.0556 | 2 | 4.0556 | 2
331 | General classroom | 73 | 4 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 4.0556 | 2 | 4.0556 | 2
333 | Corridor | 79 | 5 |  | 5535 | 125 | 79 | Air Handling Unit | 44280 | 0.10705 | 0 | 0.10705 | 0
333 | Corridor | 66 | 4 |  | 5535 | 125 | 66 | Air Handling Unit | 44280 | 0.089431 | 0 | 0.089431 | 0
333 | Corridor | 81 | 5 |  | 5535 | 125 | 81 | Air Handling Unit | 44280 | 0.10976 | 0 | 0.10976 | 0
360 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
360 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
360 | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Corridor | 9 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Vending machines |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Corridor | 28 | 1 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Corridor | 11 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Kitchen storage |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Gymnasium | 5058 | 337 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Storage |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Fitness center |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Fitness center |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-22 | [8 empty] | unk | unk | unk | unk
School: | George W. Sharswood Elementary School | House fan Abated | [7 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Building Engineer | 0 | 0 |  | 1288 | 29 | 0 | House Fan | 10304 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 | Yes | 2000 | 45 | 45 | House Fan | 16000 | 0 | 0 | 20 | 3
- | Kitchen Storage | 0 | 0 |  | 121 | 2 | 0 | House Fan | 968 | 0 | 0 | 0 | 0
- | Art Room | 1817 | 121 |  | 1242 | 28 | 28 | House Fan | 9936 | 10.9722 | 3 | 10.9722 | 3
B9A & B9B | Classroom | 2017 | 134 |  | 1242 | 28 | 28 | House Fan | 9936 | 12.18 | 3 | 12.18 | 3
- | Gym | 2219 | 147 |  | 2160 | 49 | 49 | House Fan | 17280 | 7.7049 | 2 | 7.7049 | 2
- | Main Office | 0 | 0 | Yes | 552 | 12 | 12 | House Fan | 4416 | 0 | 0 | 20 | 3
- | Nurse Office | 0 | 0 | Yes | 550 | 12 | 12 | House Fan | 4400 | 0 | 0 | 20 | 3
- | Nurse Exam | 0 | 0 | Yes | 299 | 6 | 6 | House Fan | 2392 | 0 | 0 | 20 | 3
- | Principal's Office | 0 | 0 | Yes | 288 | 6 | 6 | House Fan | 2304 | 0 | 0 | 20 | 3
101 | Classroom | 1018 | 67 |  | 550 | 12 | 12 | House Fan | 4400 | 13.8818 | 3 | 13.8818 | 3
102 | Classroom | 932 | 62 |  | 550 | 12 | 12 | House Fan | 4400 | 12.7091 | 3 | 12.7091 | 3
103 | Classroom | 484 | 32 |  | 550 | 12 | 12 | House Fan | 4400 | 6.6 | 2 | 6.6 | 2
104 | Classroom |  | 0 | Yes | 276 | 6 | 6 | House Fan | 2208 | unk | unk | 20 | 3
105 | Classroom | 0 | 0 | Yes | 840 | 19 | 19 | House Fan | 6720 | 0 | 0 | 20 | 3
106 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | House Fan | 5824 | 0 | 0 | 20 | 3
107 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | House Fan | 5824 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 728 | 16 | 16 | House Fan | 5824 | 0 | 0 | 20 | 3
109 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0 | 20 | 3
114 | Classroom | 0 | 0 | Yes | 748 | 17 | 17 | House Fan | 5984 | 0 | 0 | 20 | 3
- | Auditorium | 0 | 0 |  | 2350 | 53 | 0 | House Fan | 18800 | 0 | 0 | 0 | 0
216 | Music Rm | 0 | 0 | Yes | 1500 | 34 | 34 | House Fan | 12000 | 0 | 0 | 20 | 3
- | Teacher's Lounge | 0 | 0 |  | 440 | 10 | 0 | House Fan | 3520 | 0 | 0 | 0 | 0
217 | Classroom | 0 | 0 | Yes | 644 | 14 | 14 | House Fan | 5152 | 0 | 0 | 20 | 3
219 | Classroom | 0 | 0 | Yes | 744 | 16 | 16 | House Fan | 5952 | 0 | 0 | 20 | 3
223 | Classroom | 0 | 0 | Yes | 713 | 16 | 16 | House Fan | 5704 | 0 | 0 | 20 | 3
224 | Classroom | 0 | 0 | Yes | 684 | 15 | 15 | House Fan | 5472 | 0 | 0 | 20 | 3
225 | Classroom | 695 | 46 |  | 684 | 15 | 15 | House Fan | 5472 | 7.6206 | 2 | 7.6206 | 2
226 | Classroom | 881 | 58 |  | 684 | 15 | 15 | House Fan | 5472 | 9.6601 | 2 | 9.6601 | 2
227 | Classroom | 429 | 28 |  | 684 | 15 | 15 | House Fan | 5472 | 4.7039 | 2 | 4.7039 | 2
228 | Classroom | 0 | 0 | Yes | 682 | 15 | 15 | House Fan | 5456 | 0 | 0 | 20 | 3
329 | Classroom | 281 | 18 |  | 696 | 15 | 15 | House Fan | 5568 | 3.028 | 1 | 3.028 | 1
329A | Office | 0 | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | 0 | 0 | 20 | 3
330 | Classroom | 811 | 54 |  | 696 | 15 | 15 | House Fan | 5568 | 8.7392 | 2 | 8.7392 | 2
331 | Classroom | 276 | 18 |  | 696 | 15 | 15 | House Fan | 5568 | 2.9741 | 1 | 2.9741 | 1
332 | Classroom | 0 | 0 | Yes | 576 | 13 | 13 | House Fan | 4608 | 0 | 0 | 20 | 3
333 | Classroom | 0 | 0 | Yes | 775 | 17 | 17 | House Fan | 6200 | 0 | 0 | 20 | 3
334 | Classroom | 0 | 0 | Yes | 783 | 17 | 17 | House Fan | 6264 | 0 | 0 | 20 | 3
335 | Classroom | 0 | 0 | Yes | 783 | 17 | 17 | House Fan | 6264 | 0 | 0 | 20 | 3
336 | Classroom | 0 | 0 | Yes | 783 | 17 | 17 | House Fan | 6264 | 0 | 0 | 20 | 3
337 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0 | 20 | 3
338 | Classroom | 0 | 0 | Yes | 552 | 12 | 12 | House Fan | 4416 | 0 | 0 | 20 | 3
339 | Classroom | 368 | 24 |  | 672 | 15 | 15 | House Fan | 5376 | 4.1071 | 2 | 4.1071 | 2
340 | Classroom | 326 | 21 |  | 576 | 13 | 13 | House Fan | 4608 | 4.2448 | 2 | 4.2448 | 2
341 | Classroom | 156 | 10 |  | 576 | 13 | 10 | House Fan | 4608 | 2.0312 | 1 | 2.0312 | 1
341A | Classroom | 0 | 0 |  | 120 | 2 | 0 | House Fan | 960 | 0 | 0 | 0 | 0
342A | Classroom | 0 | 0 |  | 288 | 6 | 0 | House Fan | 2304 | 0 | 0 | 0 | 0
342B | Classroom | 0 | 0 | Yes | 432 | 9 | 9 | House Fan | 3456 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | Shawmont Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | Retest | 2nd Retest | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | CLASS | 0 | 0 | Yes | 1033 | 23 | 23 | Univent | 8264 | 0 | 0 | 20 | 3
103 | CLASS | 323 | 21 |  | 687 | 15 | 15 | Univent | 5496 | 3.5262 | 1 | 3.5262 | 1
104 | CLASS | 337 | 22 |  | 568 | 12 | 12 | Univent | 4544 | 4.4498 | 2 | 4.4498 | 2
105 | Office | 0 | 0 | Yes | 359 | 8 | 8 |  | 2872 | 0 | 0 | 20 | 3
106 | CLASS | 336 | 22 |  | 687 | 15 | 15 | Univent | 5496 | 3.6681 | 1 | 3.6681 | 1
107 | CLASS | 327 | 21 |  | 705 | 16 | 16 | Univent | 5640 | 3.4787 | 1 | 3.4787 | 1
108 | CLASS | 308 | 20 |  | 750 | 17 | 17 | Univent | 6000 | 3.08 | 1 | 3.08 | 1
201 | CLASS | 312 | 20 |  | 670 | 15 | 15 | Univent | 5360 | 3.4925 | 1 | 3.4925 | 1
202 | CLASS | 323 | 21 |  | 536 | 12 | 12 | Univent | 4288 | 4.5196 | 2 | 4.5196 | 2
203 | CLASS | 372 | 24 |  | 794 | 18 | 18 | Univent | 6352 | 3.5139 | 1 | 3.5139 | 1
204 | CLASS | 273 | 18 |  | 794 | 18 | 18 | Univent | 6352 | 2.5787 | 1 | 2.5787 | 1
205 | Therapy | 340 | 22 |  | 370 | 8 | 8 | Univent | 2960 | 6.8919 | 2 | 6.8919 | 2
206 | CLASS | 325 | 21 |  | 670 | 15 | 15 | Univent | 5360 | 3.6381 | 1 | 3.6381 | 1
207 | CLASS | 222 | 14 | Yes | 675 | 15 | 15 | Univent | 5400 | 2.4667 | 1 | 22.4667 | 3
208 | CLASS | 272 | 18 |  | 675 | 15 | 15 | Univent | 5400 | 3.0222 | 1 | 3.0222 | 1
209 | CLASS | 252 | 16 |  | 670 | 15 | 15 | Univent | 5360 | 2.8209 | 1 | 2.8209 | 1
300 | CLASS | 281 | 18 |  | 503 | 11 | 11 | Univent | 4024 | 4.1899 | 2 | 4.1899 | 2
301 | CLASS | 312 | 20 |  | 690 | 15 | 15 | Univent | 5520 | 3.3913 | 1 | 3.3913 | 1
302 | CLASS | 287 | 19 |  | 704 | 16 | 16 | Univent | 5632 | 3.0575 | 1 | 3.0575 | 1
303 | CLASS | 276 | 18 |  | 695 | 15 | 15 | Univent | 5560 | 2.9784 | 1 | 2.9784 | 1
304 | CLASS | 371 | 24 |  | 797 | 18 | 18 | Univent | 6376 | 3.4912 | 1 | 3.4912 | 1
305 | Office | 96 | 6 | Yes | 448 | 10 | 10 | Univent | 3584 | 1.6071 | 1 | 21.6071 | 3
305-A | Classroom | 313 | 20 |  | 814 | 18 | 18 | Univent | 6512 | 2.8839 | 1 | 2.8839 | 1
306 | CLASS | 296 | 19 |  | 675 | 15 | 15 | Univent | 5400 | 3.2889 | 1 | 3.2889 | 1
307 | CLASS | 279 | 18 |  | 675 | 15 | 15 | Univent | 5400 | 3.1 | 1 | 3.1 | 1
308 | CLASS | 0 | 0 | Yes | 695 | 15 | 15 | Univent | 5560 | 0 | 0 | 20 | 3
309 | CLASS | 370 | 24 |  | 690 | 15 | 15 | Univent | 5520 | 4.0217 | 2 | 4.0217 | 2
310 | CLASS | 275 | 18 | Yes | 1103 | 25 | 25 | Univent | 8824 | 1.8699 | 1 | 21.8699 | 3
311 | CLASS | 292 | 19 |  | 935 | 21 | 19 | Univent | 7480 | 2.3422 | 1 | 2.3422 | 1
312 | CLASS | 0 | 0 | Yes | 1039 | 23 | 23 | Univent | 8312 | 0 | 0 | 20 | 3
313 | CLASS | 0 | 0 | Yes | 1036 | 23 | 23 | Univent | 8288 | 0 | 0 | 20 | 3
314 | CLASS | 433 | 28 |  | 1012 | 23 | 23 | Univent | 8096 | 3.209 | 1 | 3.209 | 1
315 | CLASS | 388 | 25 |  | 1184 | 26 | 25 | Univent | 9472 | 2.4578 | 1 | 2.4578 | 1
- | AUDITORIUM | 1331 | 88 |  | 3193 | 72 | 72 | Air Handling Unit | 25544 | 3.1264 | 1 | 3.1264 | 1
- | BAND RM | 0 | 0 | Yes | 934 | 21 | 21 | Univent | 7472 | 0 | 0 | 20 | 3
- | COMPUTER LAB | 0 | 0 | Yes | 1103 | 25 | 25 | Univent | 8824 | 0 | 0 | 20 | 3
- | GYM | 5749 | 383 | Yes | 2610 | 59 | 59 | Air Handling Unit | 20880 | 16.5201 | 3 | 36.5201 | 4
- | LIBRARY | 750 | 50 |  | 1804 | 41 | 41 | Univent | 14432 | 3.1181 | 1 | 3.1181 | 1
B-1 | Strings Room | 343 | 22 |  | 641 | 14 | 14 | Univent | 5128 | 4.0133 | 2 | 4.0133 | 2
B-2 | Music Room | 0 | 0 | Yes | 518 | 11 | 11 | Univent | 4144 | 0 | 0 | 20 | 3
B-3 | Band Room | 396 | 26 |  | 153 | 3 | 3 | Univent | 1224 | 19.4118 | 3 | 19.4118 | 3
B-4 | Band Room | 281 | 18 |  | 940 | 21 | 18 | Univent | 7520 | 2.242 | 1 | 2.242 | 1
B-6 | Classroom | 395 | 26 |  | 803 | 18 | 18 | Univent | 6424 | 3.6893 | 1 | 3.6893 | 1
- | Cafeteria | 1132 | 75 |  | 4090 | 92 | 75 | Univent | 32720 | 2.0758 | 1 | 2.0758 | 1
- | Staff Lounge | 0 | 0 | Yes | 364 | 8 | 8 | Univent | 2912 | 0 | 0 | 20 | 3
- | Nurse |  | 0 | Yes | 287 | 6 | 6 |  | 2296 | unk | unk | 20 | 3
- | Principal's Office |  | 0 | Yes | 210 | 4 | 4 |  | 1680 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 379 | 8 | 8 |  | 3032 | unk | unk | 20 | 3
Sheet Last Modified: | 2021-04-06 | [8 empty] | unk | unk | unk | unk
School: | Isaac A. Sheppard Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 661 | 44 |  | 768 | 17 | 17 | House Fan | 6144 | 6.4551 | 2 | 6.4551 | 2
101 | Classroom | 894 | 59 |  | 682 | 15 | 15 | House Fan | 5456 | 9.8314 | 2 | 9.8314 | 2
102 | Classroom | 910 | 60 |  | 682 | 15 | 15 | House Fan | 5456 | 10.0073 | 3 | 10.0073 | 3
103 | Classroom | 578 | 38 |  | 682 | 15 | 15 | House Fan | 5456 | 6.3563 | 2 | 6.3563 | 2
200 | Classroom | 665 | 44 |  | 704 | 16 | 16 | House Fan | 5632 | 7.0845 | 2 | 7.0845 | 2
201 | Classroom | 595 | 39 |  | 704 | 16 | 16 | House Fan | 5632 | 6.3388 | 2 | 6.3388 | 2
202 | Classroom | 1004 | 66 |  | 682 | 15 | 15 | House Fan | 5456 | 11.0411 | 3 | 11.0411 | 3
203 | Classroom | 951 | 63 |  | 682 | 15 | 15 | House Fan | 5456 | 10.4582 | 3 | 10.4582 | 3
204 | Classroom | 949 | 63 |  | 682 | 15 | 15 | House Fan | 5456 | 10.4362 | 3 | 10.4362 | 3
205 | Classroom | 661 | 44 |  | 682 | 15 | 15 | House Fan | 5456 | 7.2691 | 2 | 7.2691 | 2
206 | Classroom | 844 | 56 |  | 704 | 16 | 16 | House Fan | 5632 | 8.9915 | 2 | 8.9915 | 2
300 | Classroom | 840 | 56 |  | 875 | 19 | 19 | House Fan | 7000 | 7.2 | 2 | 7.2 | 2
301 | Classroom | 717 | 47 |  | 875 | 19 | 19 | House Fan | 7000 | 6.1457 | 2 | 6.1457 | 2
302 | Classroom | 963 | 64 |  | 836 | 19 | 19 | House Fan | 6688 | 8.6394 | 2 | 8.6394 | 2
303 | Classroom | 762 | 50 |  | 836 | 19 | 19 | House Fan | 6688 | 6.8361 | 2 | 6.8361 | 2
304 | Classroom | 998 | 66 |  | 704 | 16 | 16 | House Fan | 5632 | 10.6321 | 3 | 10.6321 | 3
305 | Classroom | 847 | 56 |  | 704 | 16 | 16 | House Fan | 5632 | 9.0234 | 2 | 9.0234 | 2
306 | Classroom | 636 | 42 |  | 704 | 16 | 16 | House Fan | 5632 | 6.7756 | 2 | 6.7756 | 2
- | Auditorium | 1843 | 122 |  | 1176 | 26 | 26 | House Fan | 9408 | 11.7538 | 3 | 11.7538 | 3
Main Office | Office |  | 0 | Yes | 255 | 5 | 5 | Air Purifier | 2040 | unk | unk | 20 | 3
Nurse Office | Office |  | 0 | Yes | 122 | 2 | 2 | Air Purifier | 976 | unk | unk | 20 | 3
Principal Office | Office |  | 0 | Yes | 183 | 4 | 4 | Air Purifier | 1464 | unk | unk | 20 | 3
- | Library | 1317 | 87 |  | 851 | 19 | 19 | House Fan | 6808 | 11.6069 | 3 | 11.6069 | 3
- | Lunch Room/Cafeteria | 1498 | 99 |  | 1311 | 29 | 29 | House Fan | 10488 | 8.5698 | 2 | 8.5698 | 2
- | Server Room | 0 | 0 |  | 0 | 0 | 0 | Minisplit Air Handling Unit | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Sheet Last Modified: | 2021-04-07 | [8 empty] | unk | unk | unk | unk
School: | Philip Sheridan Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Meehan | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Room | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0 | 20 | 3
102 | Room | 1116 | 74 |  | 768 | 17 | 17 | House Fan | 6144 | 10.8984 | 3 | 10.8984 | 3
103 | Room | 921 | 61 |  | 768 | 17 | 17 | House Fan | 6144 | 8.9941 | 2 | 8.9941 | 2
104 | Room | 749 | 49 |  | 720 | 16 | 16 | House Fan | 5760 | 7.8021 | 2 | 7.8021 | 2
105 | Room | 693 | 46 |  | 720 | 16 | 16 | House Fan | 5760 | 7.2188 | 2 | 7.2188 | 2
106 | Classroom | 1006 | 67 |  | 768 | 17 | 17 | House Fan | 6144 | 9.8242 | 2 | 9.8242 | 2
107 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0 | 20 | 3
109 | Classroom | 861 | 57 |  | 768 | 17 | 17 | House Fan | 6144 | 8.4082 | 2 | 8.4082 | 2
110 | Classroom | 376 | 25 |  | 768 | 17 | 17 | House Fan | 6144 | 3.6719 | 1 | 3.6719 | 1
Main Office | Office |  | 0 | Yes | 448 | 10 | 10 | House Fan | 3584 | unk | unk | 20 | 3
110 | Principal office | 597 | 39 |  | 216 | 4 | 4 | House Fan | 1728 | 20.7292 | 3 | 20.7292 | 3
111 | Nurse | 0 | 0 | Yes | 312 | 7 | 7 | House Fan | 2496 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0 | 20 | 3
202 | Classroom | 877 | 58 |  | 768 | 17 | 17 | House Fan | 6144 | 8.5645 | 2 | 8.5645 | 2
203 | Classroom | 981 | 65 |  | 720 | 16 | 16 | House Fan | 5760 | 10.2188 | 3 | 10.2188 | 3
204 | Classroom | 760 | 50 |  | 720 | 16 | 16 | House Fan | 5760 | 7.9167 | 2 | 7.9167 | 2
205 | Classroom | 737 | 49 |  | 720 | 16 | 16 | House Fan | 5760 | 7.6771 | 2 | 7.6771 | 2
206 | Classroom | 999 | 66 |  | 768 | 17 | 17 | House Fan | 6144 | 9.7559 | 2 | 9.7559 | 2
207 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0 | 20 | 3
209 | Classroom | 1162 | 77 |  | 768 | 17 | 17 | House Fan | 6144 | 11.3477 | 3 | 11.3477 | 3
209.5 | Office |  | 0 | Yes | 220 | 5 | 5 | House Fan | 1760 | unk | unk | 20 | 3
210 | Classroom | 926 | 61 |  | 768 | 17 | 17 | House Fan | 6144 | 9.043 | 2 | 9.043 | 2
210.5 | Office |  | 0 |  | 220 | 5 | 0 | House Fan | 1760 | unk | unk | unk | unk
211 | Classroom | 0 | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0 | 0 | 0
302 | Classroom | 1253 | 83 |  | 768 | 17 | 17 | House Fan | 6144 | 12.2363 | 3 | 12.2363 | 3
303 | Classroom | 1038 | 69 |  | 720 | 16 | 16 | House Fan | 5760 | 10.8125 | 3 | 10.8125 | 3
304 | Classroom | 746 | 49 |  | 720 | 16 | 16 | House Fan | 5760 | 7.7708 | 2 | 7.7708 | 2
305 | Classroom | 811 | 54 |  | 720 | 16 | 16 | House Fan | 5760 | 8.4479 | 2 | 8.4479 | 2
306 | Classroom | 1007 | 67 |  | 768 | 17 | 17 | House Fan | 6144 | 9.834 | 2 | 9.834 | 2
307 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0 | 0 | 0
308 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0 | 0 | 0
309 | Classroom | 894 | 59 |  | 768 | 17 | 17 | House Fan | 6144 | 8.7305 | 2 | 8.7305 | 2
310 | Classroom | 1334 | 88 |  | 768 | 17 | 17 | House Fan | 6144 | 13.0273 | 3 | 13.0273 | 3
311 | Classroom | 0 | 0 |  | 768 | 17 | 0 | House Fan | 6144 | 0 | 0 | 0 | 0
- | Basement East Side |  | 0 |  | 567 | 12 | 0 | House Fan | 4536 | unk | unk | unk | unk
- | Basement West Side |  | 0 |  | 567 | 12 | 0 | House Fan | 4536 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-19 | [8 empty] | unk | unk | unk | unk
School: | SLA @ Beeber | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom |  | 0 |  | 1200 | 27 | 0 |  | 9600 | unk | unk | unk | unk
101 | Classroom |  | 0 |  | 1150 | 26 | 0 |  | 9200 | unk | unk | unk | unk
102 | Classroom |  | 0 |  | 925 | 21 | 0 |  | 7400 | unk | unk | unk | unk
102A | Classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | unk | unk | unk | unk
103 | Classroom |  | 0 |  | 1636 | 37 | 0 |  | 13088 | unk | unk | unk | unk
104 | Classroom |  | 0 |  | 875 | 19 | 0 |  | 7000 | unk | unk | unk | unk
105 | Classroom |  | 0 |  | 909 | 20 | 0 |  | 7272 | unk | unk | unk | unk
106 | Classroom |  | 0 | Yes | 966 | 21 | 21 |  | 7728 | unk | unk | 20 | 3
106A | Classroom |  | 0 | Yes | 610 | 13 | 13 |  | 4880 | unk | unk | 20 | 3
107 | Classroom |  | 0 |  | 912 | 20 | 0 |  | 7296 | unk | unk | unk | unk
107A | Classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | unk | unk | unk | unk
107B | Classroom |  | 0 |  | 360 | 8 | 0 |  | 2880 | unk | unk | unk | unk
108 | Classroom |  | 0 |  | 912 | 20 | 0 |  | 7296 | unk | unk | unk | unk
109 | Classroom |  | 0 |  | 700 | 15 | 0 |  | 5600 | unk | unk | unk | unk
200 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | unk | unk | 20 | 3
201 | Office |  | 0 | Yes | 187 | 4 | 4 |  | 1496 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 1128 | 25 | 25 |  | 9024 | unk | unk | 20 | 3
203 | Classroom |  | 0 |  | 1128 | 25 | 0 |  | 9024 | unk | unk | unk | unk
203A | Classroom |  | 0 | Yes | 720 | 16 | 16 |  | 5760 | unk | unk | 20 | 3
203B | Classroom |  | 0 | Yes | 360 | 8 | 8 |  | 2880 | unk | unk | 20 | 3
204 | Classroom |  | 0 | Yes | 664 | 15 | 15 |  | 5312 | unk | unk | 20 | 3
204A | Nurse office |  | 0 |  | 187 | 4 | 0 |  | 1496 | unk | unk | unk | unk
205 | Office |  | 0 | Yes | 360 | 8 | 8 |  | 2880 | unk | unk | 20 | 3
206-208 | Office |  | 0 |  | 996 | 22 | 0 |  | 7968 | unk | unk | unk | unk
- | Main Office |  | 0 | Yes | 335 | 7 | 7 |  | 2680 | unk | unk | 20 | 3
- | Principal Office |  | 0 |  | 660 | 15 | 0 |  | 5280 | unk | unk | unk | unk
Secretary | Office |  | 0 | Yes |  | 0 | 0 |  |  | unk | unk | 20 | 3
Conference Room | Conference Room |  | 0 | Yes |  | 0 | 0 |  |  | unk | unk | 20 | 3
Cafeteria | Cafeteria |  | 0 |  | 7014 | 159 | 0 |  | 56112 | unk | unk | unk | unk
209-210 | Library |  | 0 | Yes | 1872 | 42 | 42 |  | 14976 | unk | unk | 20 | 3
211 | Classroom |  | 0 |  | 984 | 22 | 0 |  | 7872 | unk | unk | unk | unk
212 | Classroom |  | 0 |  | 720 | 16 | 0 |  | 5760 | unk | unk | unk | unk
213-214 | Classroom |  | 0 |  | 1518 | 34 | 0 |  | 12144 | unk | unk | unk | unk
214A-B | Classroom |  | 0 |  | 1021 | 23 | 0 |  | 8168 | unk | unk | unk | unk
215 | Office |  | 0 |  | 187 | 4 | 0 |  | 1496 | unk | unk | unk | unk
216 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
217 | Classroom |  | 0 |  | 816 | 18 | 0 |  | 6528 | unk | unk | unk | unk
218 | Classroom |  | 0 | Yes | 744 | 16 | 16 |  | 5952 | unk | unk | 20 | 3
219 | Classroom |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | unk | unk | 20 | 3
220 | Classroom |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | unk | unk | 20 | 3
221 | Classroom |  | 0 | Yes | 768 | 17 | 17 |  | 6144 | unk | unk | 20 | 3
222 | Classroom |  | 0 | Yes | 816 | 18 | 18 |  | 6528 | unk | unk | 20 | 3
223 | Classroom |  | 0 | Yes |  | 0 | 0 |  |  | unk | unk | 20 | 3
224 | Classroom |  | 0 | Yes |  | 0 | 0 |  |  | unk | unk | 20 | 3
316 | Office |  | 0 |  | 187 | 4 | 0 |  | 1496 | unk | unk | unk | unk
317 | Classroom |  | 0 |  | 665 | 15 | 0 |  | 5320 | unk | unk | unk | unk
318 | Classroom |  | 0 |  | 836 | 19 | 0 |  | 6688 | unk | unk | unk | unk
319-320 | Classroom |  | 0 |  | 1488 | 33 | 0 |  | 11904 | unk | unk | unk | unk
321 | Classroom |  | 0 |  | 749 | 17 | 0 |  | 5992 | unk | unk | unk | unk
322 | Classroom |  | 0 |  | 766 | 17 | 0 |  | 6128 | unk | unk | unk | unk
323 | Classroom |  | 0 |  | 808 | 18 | 0 |  | 6464 | unk | unk | unk | unk
324 | Classroom |  | 0 |  | 668 | 15 | 0 |  | 5344 | unk | unk | unk | unk
300 | Office |  | 0 |  | 187 | 4 | 0 |  | 1496 | unk | unk | unk | unk
301-303 | Classroom |  | 0 | Yes | 2072 | 47 | 47 |  | 16576 | unk | unk | 20 | 3
302 | Classroom |  | 0 | Yes | 720 | 16 | 16 |  | 5760 | unk | unk | 20 | 3
303A-B | Classroom |  | 0 | Yes | 1072 | 24 | 24 |  | 8576 | unk | unk | 20 | 3
304 | Classroom |  | 0 | Yes | 1009 | 22 | 22 |  | 8072 | unk | unk | 20 | 3
305 | Classroom |  | 0 |  | 989 | 22 | 0 |  | 7912 | unk | unk | unk | unk
306 | Classroom |  | 0 |  | 1001 | 22 | 0 |  | 8008 | unk | unk | unk | unk
307 | Classroom |  | 0 |  | 1361 | 30 | 0 |  | 10888 | unk | unk | unk | unk
308 | Office |  | 0 |  | 200 | 4 | 0 |  | 1600 | unk | unk | unk | unk
309-310 | Classroom |  | 0 | Yes | 2085 | 47 | 47 |  | 16680 | unk | unk | 20 | 3
311 | Office |  | 0 | Yes | 651 | 14 | 14 |  | 5208 | unk | unk | 20 | 3
312 | Office |  | 0 |  | 300 | 6 | 0 |  | 2400 | unk | unk | unk | unk
313-315 | Classroom |  | 0 |  | 2227 | 50 | 0 |  | 17816 | unk | unk | unk | unk
314A | Classroom |  | 0 |  | 1126 | 25 | 0 |  | 9008 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | Solis-Cohen Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Main Exhaust | Main Exhaust Part 2 | [6 empty] | unk | unk | unk | unk
School: | Solis-Cohen Elementary School- Little School House | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Chadwick Part 2 | Chadwick Part 3 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Solis-Cohen Main Building | [9 empty] | unk | unk | unk | unk
- | Main Office |  | 0 |  | 120 | 2 | 0 | N/A | 960 | unk | unk | unk | unk
1 | classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | unk | unk | unk | unk
2 | classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | unk | unk | unk | unk
3 | Classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | unk | unk | unk | unk
4 | classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | unk | unk | unk | unk
5 | classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | unk | unk | unk | unk
6 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | unk | unk | unk | unk
7 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | unk | unk | unk | unk
8 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | unk | unk | unk | unk
9 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | unk | unk | unk | unk
9A | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | unk | unk | unk | unk
10 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | unk | unk | unk | unk
11 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | unk | unk | unk | unk
12 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | unk | unk | unk | unk
13 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | unk | unk | unk | unk
14 | classroom |  | 0 |  | 731 | 16 | 0 | N/A | 5848 | unk | unk | unk | unk
26 | Classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | unk | unk | unk | unk
27 | Classroom |  | 0 |  | 914 | 20 | 0 | N/A | 7312 | unk | unk | unk | unk
- | Esol Room |  | 0 |  | 806 | 18 | 0 | N/A | 6448 | unk | unk | unk | unk
- | Nurses Office |  | 0 |  | 1116 | 25 | 0 | N/A | 8928 | unk | unk | unk | unk
- | Gym |  | 0 |  | 5355 | 121 | 0 | N/A | 42840 | unk | unk | unk | unk
- | Cafeteria |  | 0 |  | 2660 | 60 | 0 | N/A | 21280 | unk | unk | unk | unk
- | Auditorium |  | 0 |  | 5036 | 114 | 0 | N/A | 40288 | unk | unk | unk | unk
- | Counselors Office A |  | 0 |  | 352 | 8 | 0 | N/A | 2816 | unk | unk | unk | unk
- | Counselors Office B |  | 0 |  | 352 | 8 | 0 | N/A | 2816 | unk | unk | unk | unk
Solis-Cohen LSH | [9 empty] | unk | unk | unk | unk
100B | Lobby | 88 | 5 |  | 196 | 4 | 4 | Air Handling Unit | 1568 | 3.3673 | 1 | 3.3673 | 1
101A | Reception Office | 30 | 2 |  | 256 | 5 | 2 | Air Handling Unit | 2048 | 0.87891 | 0 | 0.87891 | 0
101B | Clerical Office | 56 | 3 |  | 336 | 7 | 3 | Air Handling Unit | 2688 | 1.25 | 1 | 1.25 | 1
101C | Asst. Principals Office | 32 | 2 |  | 598 | 13 | 2 | Air Handling Unit | 4784 | 0.40134 | 0 | 0.40134 | 0
101D | Nurses Office | 32 | 2 |  | 256 | 5 | 2 | Air Handling Unit | 2048 | 0.9375 | 0 | 0.9375 | 0
102 | Classroom | 287 | 19 |  | 858 | 19 | 19 | Univent | 6864 | 2.5087 | 1 | 2.5087 | 1
103 | Classroom | 276 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.4126 | 1 | 2.4126 | 1
104 | Classroom | 276 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.4126 | 1 | 2.4126 | 1
105 | Classroom | 292 | 19 |  | 858 | 19 | 19 | Univent | 6864 | 2.5524 | 1 | 2.5524 | 1
106 | Classroom | 280 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.4476 | 1 | 2.4476 | 1
107 | Classroom | 274 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.3951 | 1 | 2.3951 | 1
108 | Classroom | 275 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.4038 | 1 | 2.4038 | 1
110 | Faculty Dining | 45 | 3 |  | 640 | 14 | 3 | Air Handling Unit | 5120 | 0.52734 | 0 | 0.52734 | 0
121 | Classroom | 282 | 18 |  | 1092 | 24 | 18 | Univent | 8736 | 1.9368 | 1 | 1.9368 | 1
122 | Classroom | 289 | 19 |  | 1092 | 24 | 19 | Univent | 8736 | 1.9849 | 1 | 1.9849 | 1
123 | Classroom | 290 | 19 |  | 1092 | 24 | 19 | Univent | 8736 | 1.9918 | 1 | 1.9918 | 1
124 | Classroom | 292 | 19 |  | 1092 | 24 | 19 | Univent | 8736 | 2.0055 | 1 | 2.0055 | 1
125 | Classroom | 320 | 21 |  | 598 | 13 | 13 | Univent | 4784 | 4.0134 | 2 | 4.0134 | 2
126 | Classroom | 287 | 19 |  | 1092 | 24 | 19 | Univent | 8736 | 1.9712 | 1 | 1.9712 | 1
- | Lunch Room |  | 0 | Yes | 2160 | 49 | 49 | Air Handling Unit | 17280 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | South Philly HS | [8 empty] | unk | unk | unk | unk
Vendor: | Meehan (Auditoriums) | EMCOR (School) | Chadwick Retest | [6 empty] | unk | unk | unk | unk
Vendor: | EMCOR (Gym) | EMCOR Retest 2 | EMCOR Retest 3 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Pre Engineering Shop Class A | 0 | 0 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
- | Pre Engineering Shop Class B | 281 | 18 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
- | Computer Lab | 296 | 19 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
004A | Engineering Tech. | 308 | 20 |  | 1716 | 39 | 20 | Nesbitt Unit Ventilator | 13728 | 1.3462 | 1 | 1.3462 | 1
004B | Engineering Tech. | 0 | 0 |  | 880 | 20 | 0 | Nesbitt Unit Ventilator | 7040 | 0 | 0 | 0 | 0
004C | Engineering Tech. | 313 | 20 |  | 2640 | 60 | 20 | Nesbitt Unit Ventilator | 21120 | 0.8892 | 0 | 0.8892 | 0
- | Cafeteria | 7225 | 481 |  | 11200 | 254 | 254 | Nesbitt Unit Ventilator | 89600 | 4.8382 | 2 | 4.8382 | 2
- | Cafeteria | 5887 | 392 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Culinary Kitchen Hood MAU | 0 | 0 |  |  | 0 | 0 | Make-up Air Unit |  | unk | unk | unk | unk
- | Cafeteria Kitchen Hood | 4929 | 328 |  |  | 0 | 0 | Cafeteria Kitchen Hood |  | unk | unk | unk | unk
005A | Room | 0 | 0 |  | 2204 | 50 | 0 | Nesbitt Unit Ventilator | 17632 | 0 | 0 | 0 | 0
005B | Room | 0 | 0 |  | 984 | 22 | 0 | Nesbitt Unit Ventilator | 7872 | 0 | 0 | 0 | 0
- | General Office A | 461 | 30 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
- | General Office B | 394 | 26 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
100 | Room | 384 | 25 |  | 1100 | 25 | 25 | Nesbitt Unit Ventilator | 8800 | 2.6182 | 1 | 2.6182 | 1
101 | Room | 345 | 23 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 5520 | 3.75 | 1 | 3.75 | 1
104 | Room | 276 | 18 |  | 620 | 14 | 14 | Nesbitt Unit Ventilator | 4960 | 3.3387 | 1 | 3.3387 | 1
105A | Room | 0 | 0 |  | 2709 | 61 | 0 | Nesbitt Unit Ventilator | 21672 | 0 | 0 | 0 | 0
105B | Room | 207 | 13 |  | 260 | 5 | 5 | Nesbitt Unit Ventilator | 2080 | 5.9712 | 2 | 5.9712 | 2
106 | Room | 400 | 26 |  | 667 | 15 | 15 | Nesbitt Unit Ventilator | 5336 | 4.4978 | 2 | 4.4978 | 2
108A | Room | 0 | 0 |  | 2280 | 51 | 0 | Nesbitt Unit Ventilator | 18240 | 0 | 0 | 0 | 0
108B | Room | 386 | 25 |  | 528 | 12 | 12 | Nesbitt Unit Ventilator | 4224 | 5.483 | 2 | 5.483 | 2
108C | Room | 417 | 27 |  | 276 | 6 | 6 | Nesbitt Unit Ventilator | 2208 | 11.3315 | 3 | 11.3315 | 3
109 | Room | 0 | 0 |  | 812 | 18 | 0 | Nesbitt Unit Ventilator | 6496 | 0 | 0 | 0 | 0
- | Studio 1 | 308 | 20 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
- | Studio 2 | 419 | 27 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
- | Community Closet | 352 | 23 |  | 899 | 20 | 20 | Nesbitt Unit Ventilator | 7192 | 2.9366 | 1 | 2.9366 | 1
200 | Room | 371 | 24 |  | 840 | 19 | 19 |  | 6720 | 3.3125 | 1 | 3.3125 | 1
201 | Room | 363 | 24 |  | 1008 | 22 | 22 | Nesbitt Unit Ventilator | 8064 | 2.7009 | 1 | 2.7009 | 1
202 | Room | 465 | 31 |  | 1247 | 28 | 28 | Nesbitt Unit Ventilator | 9976 | 2.7967 | 1 | 2.7967 | 1
203 | Room | 278 | 18 |  | 579 | 13 | 13 | Nesbitt Unit Ventilator | 4632 | 3.601 | 1 | 3.601 | 1
204 | Room | 549 | 36 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 5520 | 5.9674 | 2 | 5.9674 | 2
205A | Room | 0 | 0 |  | 86.25 | 1 | 0 | Nesbitt Unit Ventilator | 690 | 0 | 0 | 0 | 0
205B | Room | 415 | 27 |  | 150 | 3 | 3 | Nesbitt Unit Ventilator | 1200 | 20.75 | 3 | 20.75 | 3
206 | Room | 479 | 31 |  | 705 | 16 | 16 | Nesbitt Unit Ventilator | 5640 | 5.0957 | 2 | 5.0957 | 2
207 | Room | 426 | 28 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 5520 | 4.6304 | 2 | 4.6304 | 2
208 | Room | 373 | 24 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 5520 | 4.0543 | 2 | 4.0543 | 2
209 | Room | 419 | 27 |  | 242 | 5 | 5 | Nesbitt Unit Ventilator | 1936 | 12.9855 | 3 | 12.9855 | 3
210 | Room | 297 | 19 |  | 900 | 20 | 19 | Nesbitt Unit Ventilator | 7200 | 2.475 | 1 | 2.475 | 1
211 | Room | 320 | 21 |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 5520 | 3.4783 | 1 | 3.4783 | 1
214A | Music Room | 350 | 23 |  | 2142 | 48 | 23 | Nesbitt Unit Ventilator | 17136 | 1.2255 | 1 | 1.2255 | 1
214B | Music Room | 323 | 21 |  | 170 | 3 | 3 | Nesbitt Unit Ventilator | 1360 | 14.25 | 3 | 14.25 | 3
217A | Room | 382 | 25 |  | 2560 | 58 | 25 | Nesbitt Unit Ventilator | 20480 | 1.1191 | 1 | 1.1191 | 1
217B | Room | 411 | 27 |  | 1312 | 29 | 27 | Nesbitt Unit Ventilator | 10496 | 2.3495 | 1 | 2.3495 | 1
219A | Room | 367 | 24 |  | 899 | 20 | 20 | Nesbitt Unit Ventilator | 7192 | 3.0617 | 1 | 3.0617 | 1
220 | Room | 380 | 25 |  | 667 | 15 | 15 | Nesbitt Unit Ventilator | 5336 | 4.2729 | 2 | 4.2729 | 2
221A | Room | 320 | 21 |  | 1984 | 45 | 21 | Nesbitt Unit Ventilator | 15872 | 1.2097 | 1 | 1.2097 | 1
221B | Room | 279 | 18 |  | 127.5 | 2 | 2 | Nesbitt Unit Ventilator | 1020 | 16.4118 | 3 | 16.4118 | 3
222A | Room | 329 | 21 |  | 1705 | 38 | 21 | Nesbitt Unit Ventilator | 13640 | 1.4472 | 1 | 1.4472 | 1
222B | Room | 286 | 19 |  | 110.5 | 2 | 2 | Nesbitt Unit Ventilator | 884 | 19.4118 | 3 | 19.4118 | 3
223A | Room | 259 | 17 |  | 1519 | 34 | 17 | Nesbitt Unit Ventilator | 12152 | 1.2788 | 1 | 1.2788 | 1
223B | Room | 217 | 14 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
- | Culinary Arts A | 0 | 0 |  | 130.5 | 2 | 0 | Nesbitt Unit Ventilator | 1044 | 0 | 0 | 0 | 0
- | Culinary Arts B | 0 | 0 |  | 215 | 4 | 0 | Nesbitt Unit Ventilator | 1720 | 0 | 0 | 0 | 0
300A | Room | 0 | 0 |  | 112 | 2 | 0 | Nesbitt Unit Ventilator | 896 | 0 | 0 | 0 | 0
300B | Room | 367 | 24 |  | 149 | 3 | 3 | Nesbitt Unit Ventilator | 1192 | 18.4732 | 3 | 18.4732 | 3
301 | Room | 416 | 27 |  | 1207 | 27 | 27 | Nesbitt Unit Ventilator | 9656 | 2.5849 | 1 | 2.5849 | 1
302 | Room | 393 | 26 |  | 1167 | 26 | 26 | Nesbitt Unit Ventilator | 9336 | 2.5257 | 1 | 2.5257 | 1
303 | Room | 338 | 22 |  | 875 | 19 | 19 | Nesbitt Unit Ventilator | 7000 | 2.8971 | 1 | 2.8971 | 1
304A | Room | 413 | 27 |  | 193 | 4 | 4 | Nesbitt Unit Ventilator | 1544 | 16.0492 | 3 | 16.0492 | 3
304B | Room | 427 | 28 |  | 1027 | 23 | 23 | Nesbitt Unit Ventilator | 8216 | 3.1183 | 1 | 3.1183 | 1
305A | Room | 371 | 24 |  | 259 | 5 | 5 | Nesbitt Unit Ventilator | 2072 | 10.7432 | 3 | 10.7432 | 3
305B | Room | 365 | 24 |  | 140 | 3 | 3 | Nesbitt Unit Ventilator | 1120 | 19.5536 | 3 | 19.5536 | 3
306A | Room | 358 | 23 |  | 193 | 4 | 4 | Nesbitt Unit Ventilator | 1544 | 13.9119 | 3 | 13.9119 | 3
306B | Room | 310 | 20 |  | 948 | 21 | 20 | Nesbitt Unit Ventilator | 7584 | 2.4525 | 1 | 2.4525 | 1
307A | Room | 298 | 19 |  | 959 | 21 | 19 | Nesbitt Unit Ventilator | 7672 | 2.3306 | 1 | 2.3306 | 1
308 | Library A | 322 | 21 |  | 6124 | 139 | 21 | Nesbitt Unit Ventilator | 48992 | 0.39435 | 0 | 0.39435 | 0
308 | Library B | 429 | 28 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
308 | Library C | 381 | 25 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
308 | Library Office | 361 | 24 |  | 84 | 1 | 1 | Nesbitt Unit Ventilator | 672 | 32.2321 | 4 | 32.2321 | 4
308 | Library Archive Room | 0 | 0 |  | 360 | 8 | 0 | Nesbitt Unit Ventilator | 2880 | 0 | 0 | 0 | 0
311A | Room | 347 | 23 |  | 973 | 22 | 22 | Nesbitt Unit Ventilator | 7784 | 2.6747 | 1 | 2.6747 | 1
311B | Room | 374 | 24 |  | 1054 | 23 | 23 | Nesbitt Unit Ventilator | 8432 | 2.6613 | 1 | 2.6613 | 1
313B | Room | 0 | 0 |  | 526 | 11 | 0 | Nesbitt Unit Ventilator | 4208 | 0 | 0 | 0 | 0
316 | Room | 686 | 45 |  | 722 | 16 | 16 | Nesbitt Unit Ventilator | 5776 | 7.126 | 2 | 7.126 | 2
400A | Room | 314 | 20 |  | 203 | 4 | 4 | Nesbitt Unit Ventilator | 1624 | 11.601 | 3 | 11.601 | 3
400B | Room | 208 | 13 |  | 1092 | 24 | 13 | Nesbitt Unit Ventilator | 8736 | 1.4286 | 1 | 1.4286 | 1
401A | Room | 342 | 22 |  | 878 | 19 | 19 | Nesbitt Unit Ventilator | 7024 | 2.9214 | 1 | 2.9214 | 1
401B | Room | 318 | 21 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
402A | Room | 0 | 0 |  | 894 | 20 | 0 | Nesbitt Unit Ventilator | 7152 | 0 | 0 | 0 | 0
402B | Room | 296 | 19 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
403A | Room | 0 | 0 |  | 994 | 22 | 0 | Nesbitt Unit Ventilator | 7952 | 0 | 0 | 0 | 0
403B | Room | 307 | 20 |  | 458 | 10 | 10 |  | 3664 | 5.0273 | 2 | 5.0273 | 2
404A | Room | 0 | 0 |  | 952 | 21 | 0 | Nesbitt Unit Ventilator | 7616 | 0 | 0 | 0 | 0
404B | Room | 297 | 19 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
405A | Room | 306 | 20 |  | 893 | 20 | 20 | Nesbitt Unit Ventilator | 7144 | 2.57 | 1 | 2.57 | 1
405B | Room | 0 | 0 |  |  | 0 | 0 | Nesbitt Unit Ventilator |  | unk | unk | unk | unk
406 | Room | 339 | 22 |  | 708 | 16 | 16 | Nesbitt Unit Ventilator | 5664 | 3.5911 | 1 | 3.5911 | 1
407 | Room | 298 | 19 |  | 715 | 16 | 16 | Nesbitt Unit Ventilator | 5720 | 3.1259 | 1 | 3.1259 | 1
408 | Room | 321 | 21 |  | 708 | 16 | 16 | Nesbitt Unit Ventilator | 5664 | 3.4004 | 1 | 3.4004 | 1
409 | Room | 278 | 18 |  | 675 | 15 | 15 | Nesbitt Unit Ventilator | 5400 | 3.0889 | 1 | 3.0889 | 1
410 | Room | 288 | 19 |  | 694 | 15 | 15 | Nesbitt Unit Ventilator | 5552 | 3.1124 | 1 | 3.1124 | 1
411 | Room | 333 | 22 |  | 707 | 16 | 16 | Nesbitt Unit Ventilator | 5656 | 3.5325 | 1 | 3.5325 | 1
412 | Room | 276 | 18 |  | 701 | 15 | 15 | Nesbitt Unit Ventilator | 5608 | 2.9529 | 1 | 2.9529 | 1
412A | Room | 222 | 14 |  | 471 | 10 | 10 | Nesbitt Unit Ventilator | 3768 | 3.535 | 1 | 3.535 | 1
413 | Room | 284 | 18 |  | 711 | 16 | 16 | Nesbitt Unit Ventilator | 5688 | 2.9958 | 1 | 2.9958 | 1
414 | Room | 0 | 0 |  | 580 | 13 | 0 | Nesbitt Unit Ventilator | 4640 | 0 | 0 | 0 | 0
415 | Room | 416 | 27 |  | 691 | 15 | 15 | Nesbitt Unit Ventilator | 5528 | 4.5152 | 2 | 4.5152 | 2
416 | Room | 337 | 22 |  | 660 | 15 | 15 | Nesbitt Unit Ventilator | 5280 | 3.8295 | 1 | 3.8295 | 1
417 | Room | 349 | 23 |  | 694 | 15 | 15 | Nesbitt Unit Ventilator | 5552 | 3.7716 | 1 | 3.7716 | 1
418 | Room | 343 | 22 |  | 698 | 15 | 15 | Nesbitt Unit Ventilator | 5584 | 3.6855 | 1 | 3.6855 | 1
418A | Room | 277 | 18 |  | 341 | 7 | 7 | Nesbitt Unit Ventilator | 2728 | 6.0924 | 2 | 6.0924 | 2
419A | Room | 0 | 0 |  | 1126 | 25 | 0 | Nesbitt Unit Ventilator | 9008 | 0 | 0 | 0 | 0
419B | Room | 0 | 0 |  | 135 | 3 | 0 | Nesbitt Unit Ventilator | 1080 | 0 | 0 | 0 | 0
420A | Room | 322 | 21 |  | 1082 | 24 | 21 | Nesbitt Unit Ventilator | 8656 | 2.232 | 1 | 2.232 | 1
420B | Room | 337 | 22 |  | 85 | 1 | 1 | Nesbitt Unit Ventilator | 680 | 29.7353 | 4 | 29.7353 | 4
421 | Room | 328 | 21 |  | 673 | 15 | 15 | Nesbitt Unit Ventilator | 5384 | 3.6553 | 1 | 3.6553 | 1
422 | Room | 343 | 22 |  | 673 | 15 | 15 | Nesbitt Unit Ventilator | 5384 | 3.8224 | 1 | 3.8224 | 1
423 | Room | 322 | 21 |  | 673 | 15 | 15 | Nesbitt Unit Ventilator | 5384 | 3.5884 | 1 | 3.5884 | 1
424 | Room | 272 | 18 |  | 705 | 16 | 16 | Nesbitt Unit Ventilator | 5640 | 2.8936 | 1 | 2.8936 | 1
425 | Room | 310 | 20 |  | 706 | 16 | 16 | Nesbitt Unit Ventilator | 5648 | 3.2932 | 1 | 3.2932 | 1
426 | Room | 285 | 19 |  | 681 | 15 | 15 | Nesbitt Unit Ventilator | 5448 | 3.1388 | 1 | 3.1388 | 1
427 | Room | 295 | 19 |  | 670 | 15 | 15 | Nesbitt Unit Ventilator | 5360 | 3.3022 | 1 | 3.3022 | 1
428 | Room | 400 | 26 |  | 681 | 15 | 15 | Nesbitt Unit Ventilator | 5448 | 4.4053 | 2 | 4.4053 | 2
429 | Room | 309 | 20 |  | 716 | 16 | 16 | Nesbitt Unit Ventilator | 5728 | 3.2367 | 1 | 3.2367 | 1
432 | Room | 972 | 64 |  | 664 | 15 | 15 | Nesbitt Unit Ventilator | 5312 | 10.9789 | 3 | 10.9789 | 3
433 | Room | 401 | 26 |  | 705 | 16 | 16 | Nesbitt Unit Ventilator | 5640 | 4.266 | 2 | 4.266 | 2
434 | Room | 544 | 36 |  | 677 | 15 | 15 | Nesbitt Unit Ventilator | 5416 | 6.0266 | 2 | 6.0266 | 2
435 | Room | 503 | 33 |  | 705 | 16 | 16 | Nesbitt Unit Ventilator | 5640 | 5.3511 | 2 | 5.3511 | 2
500 | Classroom | 0 | 0 |  | 937 | 21 | 0 | Nesbitt Unit Ventilator | 7496 | 0 | 0 | 0 | 0
500A | Classroom | 0 | 0 |  | 36 | 0 | 0 | Univent | 288 | 0 | 0 | 0 | 0
500B | Classroom | 158 | 10 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
501 A | Classroom | 0 | 0 |  | 845 | 19 | 0 | Univent | 6760 | 0 | 0 | 0 | 0
501 B | Classroom | 351 | 23 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
502 A | Classroom | 208 | 13 |  | 969 | 22 | 13 | Univent | 7752 | 1.6099 | 1 | 1.6099 | 1
502 B | Classroom | 266 | 17 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
503 A | Classroom | 157 | 10 |  | 1035 | 23 | 10 | Univent | 8280 | 1.1377 | 1 | 1.1377 | 1
503 B | Classroom | 67 | 4 |  | 200 | 4 | 4 | Univent | 1600 | 2.5125 | 1 | 2.5125 | 1
504 A | Classroom | 330 | 22 |  | 982 | 22 | 22 | Univent | 7856 | 2.5204 | 1 | 2.5204 | 1
504 B | Classroom | 160 | 10 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
505 A | Classroom |  | 0 |  | 942 | 21 | 0 | Univent | 7536 | unk | unk | unk | unk
505 B | Classroom |  | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
506 | Classroom | 320 | 21 |  | 690 | 15 | 15 | Univent | 5520 | 3.4783 | 1 | 3.4783 | 1
507 | Classroom | 212 | 14 |  | 690 | 15 | 14 | Univent | 5520 | 2.3043 | 1 | 2.3043 | 1
508 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Univent | 5520 | 0 | 0 | 0 | 0
509 | Classroom | 192 | 12 |  | 690 | 15 | 12 | Univent | 5520 | 2.087 | 1 | 2.087 | 1
510 A | Classroom | 183 | 12 |  | 990 | 22 | 12 | Univent | 7920 | 1.3864 | 1 | 1.3864 | 1
510 B | Classroom | 353 | 23 |  | 102 | 2 | 2 | Univent | 816 | 25.9559 | 4 | 25.9559 | 4
511 | Classroom | 286 | 19 |  | 690 | 15 | 15 | Univent | 5520 | 3.1087 | 1 | 3.1087 | 1
512 | Classroom | 159 | 10 |  | 690 | 15 | 10 | Univent | 5520 | 1.7283 | 1 | 1.7283 | 1
513 | Classroom | 183 | 12 |  | 690 | 15 | 12 | Univent | 5520 | 1.9891 | 1 | 1.9891 | 1
514 | Classroom | 182 | 12 |  | 690 | 15 | 12 | Univent | 5520 | 1.9783 | 1 | 1.9783 | 1
515 | Classroom | 205 | 13 |  | 690 | 15 | 13 | Univent | 5520 | 2.2283 | 1 | 2.2283 | 1
516 | Classroom | 65 | 4 |  | 713 | 16 | 4 | Univent | 5704 | 0.68373 | 0 | 0.68373 | 0
517 | Classroom | 334 | 22 |  | 552 | 12 | 12 | Univent | 4416 | 4.538 | 2 | 4.538 | 2
518 | Classroom | 0 | 0 |  | 713 | 16 | 0 | Univent | 5704 | 0 | 0 | 0 | 0
519 | Classroom | 177 | 11 |  | 616 | 14 | 11 | Univent | 4928 | 2.155 | 1 | 2.155 | 1
520 | Classroom | 196 | 13 |  | 616 | 14 | 13 | Univent | 4928 | 2.3864 | 1 | 2.3864 | 1
521 | Classroom | 155 | 10 |  | 616 | 14 | 10 | Univent | 4928 | 1.8872 | 1 | 1.8872 | 1
522 | Classroom | 0 | 0 |  | 616 | 14 | 0 | Univent | 4928 | 0 | 0 | 0 | 0
523 | Classroom | 153 | 10 |  | 705 | 16 | 10 | Univent | 5640 | 1.6277 | 1 | 1.6277 | 1
524 | Classroom | 63 | 4 |  | 690 | 15 | 4 | Univent | 5520 | 0.68478 | 0 | 0.68478 | 0
525 | Classroom | 76 | 5 |  | 690 | 15 | 5 | Univent | 5520 | 0.82609 | 0 | 0.82609 | 0
526 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Univent | 5520 | 0 | 0 | 0 | 0
527 | Classroom | 167 | 11 |  | 690 | 15 | 11 | Univent | 5520 | 1.8152 | 1 | 1.8152 | 1
528 | Classroom | 223 | 14 |  | 690 | 15 | 14 | Univent | 5520 | 2.4239 | 1 | 2.4239 | 1
529 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Univent | 5520 | 0 | 0 | 0 | 0
530 | Classroom | 0 | 0 |  | 690 | 15 | 0 | Univent | 5520 | 0 | 0 | 0 | 0
531 | Classroom | 4 | 0 |  | 690 | 15 | 0 | Univent | 5520 | 0.043478 | 0 | 0.043478 | 0
532 | Classroom | 0 | 0 |  | 705 | 16 | 0 | Univent | 5640 | 0 | 0 | 0 | 0
533 | Classroom | 163 | 10 |  | 705 | 16 | 10 | Univent | 5640 | 1.734 | 1 | 1.734 | 1
534 | Classroom | 0 | 0 |  | 705 | 16 | 0 | Univent | 5640 | 0 | 0 | 0 | 0
535 | Classroom | 380 | 25 |  | 705 | 16 | 16 | Univent | 5640 | 4.0426 | 2 | 4.0426 | 2
- | Auditorium | 10918 | 727 |  | 11536 | 262 | 262 | Nesbitt Unit Ventilator | 92288 | 7.0982 | 2 | 7.0982 | 2
- | Gym | 24019 | 1601 |  | 20384 | 463 | 463 | Air Handling Unit | 163072 | 8.8374 | 2 | 8.8374 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-05-03 | [8 empty] | unk | unk | unk | unk
School: | Southwark Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B4 | Office | 0 | 0 | Yes | 952 | 21 | 21 | House Fan | 7616 | 0 | 0 | 20 | 3
B5 | Music Room | 1241 | 82 |  | 1800 | 40 | 40 | House Fan | 14400 | 5.1708 | 2 | 5.1708 | 2
B20 | Basement | 584 | 38 |  | 960 | 21 | 21 | House Fan | 7680 | 4.5625 | 2 | 4.5625 | 2
B21 | Basement | 515 | 34 |  | 1728 | 39 | 34 | House Fan | 13824 | 2.2352 | 1 | 2.2352 | 1
102 | First Floor | 532 | 35 |  | 528 | 12 | 12 | House Fan | 4224 | 7.5568 | 2 | 7.5568 | 2
103 | First Floor | 268 | 17 |  | 660 | 15 | 15 | House Fan | 5280 | 3.0455 | 1 | 3.0455 | 1
107 | First Floor | 739 | 49 |  | 704 | 16 | 16 | House Fan | 5632 | 7.8729 | 2 | 7.8729 | 2
112 | Classroom | 579 | 38 |  | 864 | 19 | 19 | House Fan | 6912 | 5.026 | 2 | 5.026 | 2
113 | First Floor | 679 | 45 |  | 704 | 16 | 16 | House Fan | 5632 | 7.2337 | 2 | 7.2337 | 2
114 | Classroom | 716 | 47 |  | 864 | 19 | 19 | House Fan | 6912 | 6.2153 | 2 | 6.2153 | 2
115 | First Floor | 417 | 27 |  | 792 | 18 | 18 | House Fan | 6336 | 3.9489 | 1 | 3.9489 | 1
116 | Classroom | 575 | 38 |  | 864 | 19 | 19 | House Fan | 6912 | 4.9913 | 2 | 4.9913 | 2
117 | Classroom |  | 0 | Yes | 414 | 9 | 9 | House Fan | 3312 | unk | unk | 20 | 3
201 | Second Floor | 772 | 51 |  | 748 | 17 | 17 | House Fan | 5984 | 7.7406 | 2 | 7.7406 | 2
202 | Classroom | 486 | 32 |  | 864 | 19 | 19 | House Fan | 6912 | 4.2188 | 2 | 4.2188 | 2
203 | Classroom | 297 | 19 |  | 704 | 16 | 16 | House Fan | 5632 | 3.1641 | 1 | 3.1641 | 1
204 | Library |  | 0 | Yes | 696 | 15 | 15 | House Fan | 5568 | unk | unk | 20 | 3
205 | Library |  | 0 | Yes | 696 | 15 | 15 | House Fan | 5568 | unk | unk | 20 | 3
206 | Second Floor | 615 | 41 |  | 704 | 16 | 16 | House Fan | 5632 | 6.5518 | 2 | 6.5518 | 2
207 | Classroom | 633 | 42 |  | 864 | 19 | 19 | House Fan | 6912 | 5.4948 | 2 | 5.4948 | 2
208 | Second Floor | 332 | 22 |  | 792 | 18 | 18 | House Fan | 6336 | 3.1439 | 1 | 3.1439 | 1
209 | Classroom | 990 | 66 |  | 864 | 19 | 19 | House Fan | 6912 | 8.5938 | 2 | 8.5938 | 2
210 | Second Floor | 236 | 15 |  | 660 | 15 | 15 | House Fan | 5280 | 2.6818 | 1 | 2.6818 | 1
211 | Classroom |  | 0 | Yes | 792 | 18 | 18 | House Fan | 6336 | unk | unk | 20 | 3
212 | Classroom | 1033 | 68 |  | 864 | 19 | 19 | House Fan | 6912 | 8.967 | 2 | 8.967 | 2
213 | Second Floor | 675 | 45 |  | 792 | 18 | 18 | House Fan | 6336 | 6.392 | 2 | 6.392 | 2
214 | Classroom | 453 | 30 |  | 864 | 19 | 19 | House Fan | 6912 | 3.9323 | 1 | 3.9323 | 1
215 | Second Floor | 532 | 35 |  | 748 | 17 | 17 | House Fan | 5984 | 5.3342 | 2 | 5.3342 | 2
216 | Classroom | 562 | 37 |  | 864 | 19 | 19 | House Fan | 6912 | 4.8785 | 2 | 4.8785 | 2
217 | Room |  | 0 | Yes | 272 | 6 | 6 | House Fan | 2176 | unk | unk | 20 | 3
300 | Classroom |  | 0 | Yes | 480 | 10 | 10 | House Fan | 3840 | unk | unk | 20 | 3
301 | Classroom |  | 0 | Yes | 800 | 18 | 18 | House Fan | 6400 | unk | unk | 20 | 3
302 | Third Floor | 415 | 27 |  | 748 | 17 | 17 | House Fan | 5984 | 4.1611 | 2 | 4.1611 | 2
303 | Classroom | 291 | 19 |  | 864 | 19 | 19 | House Fan | 6912 | 2.526 | 1 | 2.526 | 1
304 | Room |  | 0 | Yes | 336 | 7 | 7 | House Fan | 2688 | unk | unk | 20 | 3
305 | Third Floor | 589 | 39 |  | 704 | 16 | 16 | House Fan | 5632 | 6.2749 | 2 | 6.2749 | 2
306 | Classroom | 276 | 18 |  | 864 | 19 | 18 | House Fan | 6912 | 2.3958 | 1 | 2.3958 | 1
307 | Classroom |  | 0 | Yes | 480 | 10 | 10 | House Fan | 3840 | unk | unk | 20 | 3
308 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
309 | Third Floor | 98 | 6 | Yes | 704 | 16 | 16 | House Fan | 5632 | 1.044 | 1 | 21.044 | 3
310 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
311 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
312 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
313 | Third Floor | 66 | 4 | Yes | 704 | 16 | 16 | House Fan | 5632 | 0.70312 | 0 | 20.7031 | 3
314 | Classroom |  | 0 | Yes | 800 | 18 | 18 | House Fan | 6400 | unk | unk | 20 | 3
315 | Classroom | 214 | 14 | Yes | 864 | 19 | 19 | House Fan | 6912 | 1.8576 | 1 | 21.8576 | 3
316 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | unk | unk | 20 | 3
- | Auditorium | 1586 | 105 |  | 1584 | 36 | 36 | House Fan | 12672 | 7.5095 | 2 | 7.5095 | 2
- | Boy's Bathroom | 541 | 36 |  | 792 | 18 | 18 | House Fan | 6336 | 5.1231 | 2 | 5.1231 | 2
- | Girl's Bathroom | 582 | 38 |  | 704 | 16 | 16 | House Fan | 5632 | 6.2003 | 2 | 6.2003 | 2
- | Music Room | 1241 | 82 |  | 1496 | 34 | 34 | House Fan | 11968 | 6.2216 | 2 | 6.2216 | 2
- | Nurses | 1184 | 78 |  | 150 | 3 | 3 | House Fan | 1200 | 59.2 | 5 | 59.2 | 5
- | Gym | 1915 | 127 |  | 1560 | 35 | 35 | House Fan | 12480 | 9.2067 | 2 | 9.2067 | 2
- | Main Office | 0 | 0 | Yes | 416 | 9 | 9 | House Fan | 3328 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 294 | 6 | 6 | House Fan | 2352 | unk | unk | 20 | 3
- | Cafeteria |  | 0 | Yes | 1890 | 42 | 42 | House Fan | 15120 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | Spring Garden | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom |  | 0 | Yes | 475 | 10 | 10 |  | 3800 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | unk | unk | 20 | 3
103 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | unk | unk | 20 | 3
104A | storage |  | 0 |  | 50 | 1 | 0 |  | 400 | unk | unk | unk | unk
104B | office |  | 0 | Yes | 80 | 1 | 1 |  | 640 | unk | unk | 20 | 3
104C | office |  | 0 | Yes | 110 | 2 | 2 |  | 880 | unk | unk | 20 | 3
104D | office |  | 0 | Yes | 99 | 2 | 2 |  | 792 | unk | unk | 20 | 3
105A | Classroom |  | 0 | Yes | 483 | 10 | 10 |  | 3864 | unk | unk | 20 | 3
105B | Classroom |  | 0 | Yes | 420 | 9 | 9 |  | 3360 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | unk | unk | 20 | 3
204 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | unk | unk | 20 | 3
206 | Classroom |  | 0 | Yes | 483 | 10 | 10 |  | 3864 | unk | unk | 20 | 3
207 | Classroom |  | 0 | Yes | 572 | 13 | 13 |  | 4576 | unk | unk | 20 | 3
301 | Classroom |  | 0 | Yes | 741 | 16 | 16 |  | 5928 | unk | unk | 20 | 3
303 | Classroom |  | 0 | Yes | 532 | 12 | 12 |  | 4256 | unk | unk | 20 | 3
304 | Classroom |  | 0 | Yes | 578 | 13 | 13 |  | 4624 | unk | unk | 20 | 3
305 | Classroom |  | 0 | Yes | 720 | 16 | 16 |  | 5760 | unk | unk | 20 | 3
306 | Classroom |  | 0 | Yes | 494 | 11 | 11 |  | 3952 | unk | unk | 20 | 3
307 | Classroom |  | 0 | Yes | 608 | 13 | 13 |  | 4864 | unk | unk | 20 | 3
308 | IMC |  | 0 | Yes | 874 | 19 | 19 |  | 6992 | unk | unk | 20 | 3
310 | Classroom |  | 0 | Yes | 380 | 8 | 8 |  | 3040 | unk | unk | 20 | 3
- | Auditorium |  | 0 | Yes | 2265 | 51 | 51 |  | 18120 | unk | unk | 20 | 3
- | Gym |  | 0 | Yes | 1800 | 40 | 40 |  | 14400 | unk | unk | 20 | 3
- | Lunchroom |  | 0 | Yes | 1520 | 34 | 34 |  | 12160 | unk | unk | 20 | 3
- | Main office |  | 0 | Yes | 231 | 5 | 5 |  | 1848 | unk | unk | 20 | 3
- | Nurses Office |  | 0 | Yes | 189 | 4 | 4 |  | 1512 | unk | unk | 20 | 3
- | Principal Office |  | 0 | Yes | 210 | 4 | 4 |  | 1680 | unk | unk | 20 | 3
- | Staff lounge |  | 0 | Yes | 168 | 3 | 3 |  | 1344 | unk | unk | 20 | 3
- | Teachers lounge |  | 0 | Yes | 195 | 4 | 4 |  | 1560 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-19 | [8 empty] | unk | unk | unk | unk
School: | Gilbert Spruance Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | [8 empty] | unk | unk | unk | unk
School: | Gilbert Spruance Little School House | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | Chadwick | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Spruance Main Building | [9 empty] | unk | unk | unk | unk
100 | Room | 108 | 7 |  | 728 | 16 | 7 | Unit Ventilator | 5824 | 1.1126 | 1 | 1.1126 | 1
101 & 101B | Room | 208 | 13 |  | 1180 | 26 | 13 | Unit Ventilator | 9440 | 1.322 | 1 | 1.322 | 1
102 | Room | 112 | 7 |  | 756 | 17 | 7 | Unit Ventilator | 6048 | 1.1111 | 1 | 1.1111 | 1
Outside 102 | Hallway | 0 | 0 |  | 370 | 8 | 0 | Unit Ventilator | 2960 | 0 | 0 | 0 | 0
103 | Room | 188 | 12 |  | 756 | 17 | 12 | Unit Ventilator | 6048 | 1.8651 | 1 | 1.8651 | 1
104 | Room | 101 | 6 |  | 756 | 17 | 6 | Unit Ventilator | 6048 | 1.002 | 1 | 1.002 | 1
105 | Room | 83 | 5 |  | 756 | 17 | 5 | Unit Ventilator | 6048 | 0.82341 | 0 | 0.82341 | 0
106 | Room | 106 | 7 |  | 756 | 17 | 7 | Unit Ventilator | 6048 | 1.0516 | 1 | 1.0516 | 1
107 | Room | 119 | 7 | Yes | 756 | 17 | 17 | Unit Ventilator | 6048 | 1.1806 | 1 | 21.1806 | 3
108 | Room | 115 | 7 |  | 756 | 17 | 7 | Unit Ventilator | 6048 | 1.1409 | 1 | 1.1409 | 1
109 | Room | 160 | 10 |  | 756 | 17 | 10 | Unit Ventilator | 6048 | 1.5873 | 1 | 1.5873 | 1
110 | Room | 97 | 6 |  | 756 | 17 | 6 | Unit Ventilator | 6048 | 0.9623 | 0 | 0.9623 | 0
111 | Room | 145 | 9 |  | 996 | 22 | 9 | Unit Ventilator | 7968 | 1.0919 | 1 | 1.0919 | 1
112 | Room | 208 | 13 |  | 996 | 22 | 13 | Unit Ventilator | 7968 | 1.5663 | 1 | 1.5663 | 1
113 | Room | 110 | 7 |  | 996 | 22 | 7 | Unit Ventilator | 7968 | 0.82831 | 0 | 0.82831 | 0
Outside of 113 | Hallway | 0 | 0 |  | 3700 | 84 | 0 | Unit Ventilator | 29600 | 0 | 0 | 0 | 0
114 | Room | 240 | 16 |  | 996 | 22 | 16 | Unit Ventilator | 7968 | 1.8072 | 1 | 1.8072 | 1
115 | Room | 150 | 10 |  | 996 | 22 | 10 | Unit Ventilator | 7968 | 1.1295 | 1 | 1.1295 | 1
116 | Room | 334 | 22 |  | 719 | 16 | 16 | Unit Ventilator | 5752 | 3.484 | 1 | 3.484 | 1
117 | Room | 240 | 16 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 2.4457 | 1 | 2.4457 | 1
118 | Room | 145 | 9 |  | 1075 | 24 | 9 | Unit Ventilator | 8600 | 1.0116 | 1 | 1.0116 | 1
118A | Room | 183 | 12 |  | 486 | 11 | 11 | Unit Ventilator | 3888 | 2.8241 | 1 | 2.8241 | 1
119 | Room | 241 | 16 |  | 736 | 16 | 16 | Unit Ventilator | 5888 | 2.4558 | 1 | 2.4558 | 1
120 | Room | 225 | 15 |  | 1062 | 24 | 15 | Unit Ventilator | 8496 | 1.589 | 1 | 1.589 | 1
122 | Room | 248 | 16 |  | 851 | 19 | 16 | Unit Ventilator | 6808 | 2.1857 | 1 | 2.1857 | 1
124 | Room | 58 | 3 | Yes | 756 | 17 | 17 | Unit Ventilator | 6048 | 0.5754 | 0 | 20.5754 | 3
- | Auditorium/Gym | 0 | 0 |  | 4620 | 105 | 0 | Unit Ventilator | 36960 | 0 | 0 | 0 | 0
- | Adjustment Room | 73 | 4 |  | 435 | 9 | 4 | Unit Ventilator | 3480 | 1.2586 | 1 | 1.2586 | 1
200 | Room | 148 | 9 |  | 756 | 17 | 9 | Unit Ventilator | 6048 | 1.4683 | 1 | 1.4683 | 1
201 | Room | 136 | 9 |  | 756 | 17 | 9 | Unit Ventilator | 6048 | 1.3492 | 1 | 1.3492 | 1
202 | Room | 179 | 11 |  | 690 | 15 | 11 | Unit Ventilator | 5520 | 1.9457 | 1 | 1.9457 | 1
Outside of 202 | Hallway | 0 | 0 |  | 3700 | 84 | 0 | Unit Ventilator | 29600 | 0 | 0 | 0 | 0
203 | Room | 134 | 8 |  | 756 | 17 | 8 | Unit Ventilator | 6048 | 1.3294 | 1 | 1.3294 | 1
204 | Room | 114 | 7 |  | 756 | 17 | 7 | Unit Ventilator | 6048 | 1.131 | 1 | 1.131 | 1
205 | Room | 97 | 6 |  | 756 | 17 | 6 | Unit Ventilator | 6048 | 0.9623 | 0 | 0.9623 | 0
206 | Room | 83 | 5 |  | 756 | 17 | 5 | Unit Ventilator | 6048 | 0.82341 | 0 | 0.82341 | 0
207 | Room | 102 | 6 |  | 756 | 17 | 6 | Unit Ventilator | 6048 | 1.0119 | 1 | 1.0119 | 1
208 | Room | 139 | 9 |  | 756 | 17 | 9 | Unit Ventilator | 6048 | 1.379 | 1 | 1.379 | 1
209 | Room | 121 | 8 |  | 756 | 17 | 8 | Unit Ventilator | 6048 | 1.2004 | 1 | 1.2004 | 1
210 | Room | 90 | 6 |  | 756 | 17 | 6 | Unit Ventilator | 6048 | 0.89286 | 0 | 0.89286 | 0
211 | Room | 199 | 13 |  | 756 | 17 | 13 | Unit Ventilator | 6048 | 1.9742 | 1 | 1.9742 | 1
212 | Room | 134 | 8 |  | 756 | 17 | 8 | Unit Ventilator | 6048 | 1.3294 | 1 | 1.3294 | 1
213A | Room | 103 | 6 |  | 420 | 9 | 6 | Unit Ventilator | 3360 | 1.8393 | 1 | 1.8393 | 1
Outside of Room 213A | Hallway | 0 | 0 |  | 756 | 17 | 0 | Unit Ventilator | 6048 | 0 | 0 | 0 | 0
213B | Room | 267 | 17 |  | 548 | 12 | 12 | Unit Ventilator | 4384 | 3.6542 | 1 | 3.6542 | 1
214 | Room | 114 | 7 |  | 755 | 17 | 7 | Unit Ventilator | 6040 | 1.1325 | 1 | 1.1325 | 1
214A | Room | 0 | 0 |  | 756 | 17 | 0 | Unit Ventilator | 6048 | 0 | 0 | 0 | 0
215 | Room | 53 | 3 |  | 756 | 17 | 3 | Unit Ventilator | 6048 | 0.52579 | 0 | 0.52579 | 0
216 | Room | 122 | 8 |  | 756 | 17 | 8 | Unit Ventilator | 6048 | 1.2103 | 1 | 1.2103 | 1
217 | Room | 83 | 5 |  | 756 | 17 | 5 | Unit Ventilator | 6048 | 0.82341 | 0 | 0.82341 | 0
Outside of Room 217 | Hallway | 0 | 0 |  | 1850 | 42 | 0 | Unit Ventilator | 14800 | 0 | 0 | 0 | 0
218 | Room | 139 | 9 |  | 718 | 16 | 9 | Unit Ventilator | 5744 | 1.4519 | 1 | 1.4519 | 1
220 | Room | 131 | 8 |  | 724 | 16 | 8 | Unit Ventilator | 5792 | 1.357 | 1 | 1.357 | 1
- | Cafeteria | 263 | 17 | Yes | 4550 | 103 | 103 | Unit Ventilator | 36400 | 0.43352 | 0 | 20.4335 | 3
- | Main Office | 315 | 21 |  | 456 | 10 | 10 |  | 3648 | 5.1809 | 2 | 5.1809 | 2
- | Principal | 240 | 16 |  | 241 | 5 | 5 |  | 1928 | 7.4689 | 2 | 7.4689 | 2
- | Nurse | 374 | 24 |  | 374 | 8 | 8 |  | 2992 | 7.5 | 2 | 7.5 | 2
- | Main Entrance Lobby | 1498 | 99 |  | 1498 | 34 | 34 | Unit Ventilator | 11984 | 7.5 | 2 | 7.5 | 2
Little School House | [9 empty] | unk | unk | unk | unk
1 | Room | 1072 | 71 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 7.6136 | 2 | 7.6136 | 2
2 | Room | 938 | 62 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 6.6619 | 2 | 6.6619 | 2
3 | Room | 741 | 49 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 5.2628 | 2 | 5.2628 | 2
4 | Room | 1188 | 79 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 8.4375 | 2 | 8.4375 | 2
5 | Room | 682 | 45 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 4.8438 | 2 | 4.8438 | 2
6 | Room | 713 | 47 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 5.0639 | 2 | 5.0639 | 2
7 | Room | 554 | 36 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 3.9347 | 1 | 3.9347 | 1
8 | Room | 690 | 46 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 4.9006 | 2 | 4.9006 | 2
9 | Room | 1558 | 103 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 11.0653 | 3 | 11.0653 | 3
10 | Room | 853 | 56 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 6.0582 | 2 | 6.0582 | 2
11 | Room | 1512 | 100 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 10.7386 | 3 | 10.7386 | 3
12 | Room | 946 | 63 |  | 1056 | 24 | 24 | Air Handling Unit | 8448 | 6.7188 | 2 | 6.7188 | 2
- | CLI Office | 159 | 10 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 9.9375 | 2 | 9.9375 | 2
- | Entrance/Lobby | 0 | 0 |  | 210 | 4 | 0 | Air Handling Unit | 1680 | 0 | 0 | 0 | 0
- | Hallway | 0 | 0 |  | 1950 | 44 | 0 | Air Handling Unit | 15600 | 0 | 0 | 0 | 0
- | Main Office | 165 | 11 |  | 315 | 7 | 7 | Air Handling Unit | 2520 | 3.9286 | 1 | 3.9286 | 1
- | Office | 158 | 10 |  | 126 | 2 | 2 | Air Handling Unit | 1008 | 9.4048 | 2 | 9.4048 | 2
- | Storage | 0 | 0 |  | 215 | 4 | 0 | Air Handling Unit | 1720 | 0 | 0 | 0 | 0
- | Teachers Lounge | 331 | 22 |  | 72 | 1 | 1 | Air Handling Unit | 576 | 34.4792 | 4 | 34.4792 | 4
- | Therapy Room | 0 | 0 |  | 72 | 1 | 0 | Air Handling Unit | 576 | 0 | 0 | 0 | 0
- | Girl's RR | 0 | 0 |  | 272 | 6 | 0 | Air Handling Unit | 2176 | 0 | 0 | 0 | 0
- | Boy's RR | 0 | 0 |  | 272 | 6 | 0 | Air Handling Unit | 2176 | 0 | 0 | 0 | 0
- | Men's RR | 0 | 0 |  | 77 | 1 | 0 | Air Handling Unit | 616 | 0 | 0 | 0 | 0
- | Women's RR | 0 | 0 |  | 131 | 2 | 0 | Air Handling Unit | 1048 | 0 | 0 | 0 | 0
- | Multi-purpose Room | 2808 | 187 |  | 1998 | 45 | 45 | Fan Coil Unit | 15984 | 10.5405 | 3 | 10.5405 | 3
Sheet Last Modified: | 2021-04-29 | [8 empty] | unk | unk | unk | unk
School: | Edwin M. Stanton Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Meehan | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Main Office | 0 | 0 | Yes | 375 | 8 | 8 | House Fan | 3000 | 0 | 0 | 20 | 3
101 | Classroom | 829 | 55 |  | 870 | 19 | 19 | House Fan | 6960 | 7.1466 | 2 | 7.1466 | 2
102 | Classroom | 598 | 39 |  | 870 | 19 | 19 | House Fan | 6960 | 5.1552 | 2 | 5.1552 | 2
103 | Classroom | 630 | 42 |  | 899 | 20 | 20 | House Fan | 7192 | 5.2558 | 2 | 5.2558 | 2
104 | Classroom | 635 | 42 |  | 864 | 19 | 19 | House Fan | 6912 | 5.5122 | 2 | 5.5122 | 2
105 | Classroom | 639 | 42 |  | 870 | 19 | 19 | House Fan | 6960 | 5.5086 | 2 | 5.5086 | 2
106 | Classroom | 764 | 50 |  | 870 | 19 | 19 | House Fan | 6960 | 6.5862 | 2 | 6.5862 | 2
107 | Classroom | 836 | 55 |  | 1450 | 32 | 32 | House Fan | 11600 | 4.3241 | 2 | 4.3241 | 2
201 | Classroom | 697 | 46 |  | 870 | 19 | 19 | House Fan | 6960 | 6.0086 | 2 | 6.0086 | 2
202 | Classroom | 500 | 33 |  | 870 | 19 | 19 | House Fan | 6960 | 4.3103 | 2 | 4.3103 | 2
203 | Classroom | 526 | 35 |  | 870 | 19 | 19 | House Fan | 6960 | 4.5345 | 2 | 4.5345 | 2
204 | Classroom | 527 | 35 |  | 870 | 19 | 19 | House Fan | 6960 | 4.5431 | 2 | 4.5431 | 2
205 | Library | 907 | 60 |  | 1363 | 30 | 30 | House Fan | 10904 | 4.9908 | 2 | 4.9908 | 2
206 | Classroom | 531 | 35 |  | 870 | 19 | 19 | House Fan | 6960 | 4.5776 | 2 | 4.5776 | 2
207 | Classroom | 706 | 47 |  | 870 | 19 | 19 | House Fan | 6960 | 6.0862 | 2 | 6.0862 | 2
208 | Classroom | 806 | 53 |  | 870 | 19 | 19 | House Fan | 6960 | 6.9483 | 2 | 6.9483 | 2
301 | Gym | 61 | 4 |  | 870 | 19 | 4 | House Fan | 6960 | 0.52586 | 0 | 0.52586 | 0
302 | Gym | 432 | 28 |  | 870 | 19 | 19 | House Fan | 6960 | 3.7241 | 1 | 3.7241 | 1
302 | Classroom | 560 | 37 |  | 870 | 19 | 19 | House Fan | 6960 | 4.8276 | 2 | 4.8276 | 2
304 | Classroom | 715 | 47 |  | 870 | 19 | 19 | House Fan | 6960 | 6.1638 | 2 | 6.1638 | 2
305 | Classroom | 833 | 55 |  | 1316 | 29 | 29 | House Fan | 10528 | 4.7473 | 2 | 4.7473 | 2
306 | Classroom | 525 | 35 |  | 870 | 19 | 19 | House Fan | 6960 | 4.5259 | 2 | 4.5259 | 2
307 | Classroom | 988 | 65 |  | 870 | 19 | 19 | House Fan | 6960 | 8.5172 | 2 | 8.5172 | 2
308 | Classroom | 230 | 15 |  | 870 | 19 | 15 | House Fan | 6960 | 1.9828 | 1 | 1.9828 | 1
Counselor | Office |  | 0 | Yes | 240 | 5 | 5 | House Fan | 1920 | unk | unk | 20 | 3
- | Cafeteria | 0 | 0 | Yes | 2400 | 54 | 54 | House Fan | 19200 | 0 | 0 | 20 | 3
- | Nurse Office | 0 | 0 | Yes | 200 | 4 | 4 | House Fan | 1600 | 0 | 0 | 20 | 3
- | Principal Office | 0 | 0 | Yes | 256 | 5 | 5 | House Fan | 2048 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-15 | [8 empty] | unk | unk | unk | unk
School: | Allen M. Stearne Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | EMCOR Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | classroom | 529 | 35 |  | 730 | 16 | 16 | Perimeter Heater | 5840 | 5.4349 | 2 | 5.4349 | 2
100A | First Floor | 30 | 2 |  | 222 | 5 | 2 | Perimeter Heater | 1776 | 1.0135 | 1 | 1.0135 | 1
101 | classroom | 316 | 21 |  | 1197 | 27 | 21 | Perimeter Heater | 9576 | 1.9799 | 1 | 1.9799 | 1
102 | classroom | 452 | 30 |  | 753 | 17 | 17 | Perimeter Heater | 6024 | 4.502 | 2 | 4.502 | 2
102A | First Floor | 284 | 18 |  | 401 | 9 | 9 | Perimeter Heater | 3208 | 5.3117 | 2 | 5.3117 | 2
103 | classroom | 569 | 37 |  | 1175 | 26 | 26 | Perimeter Heater | 9400 | 3.6319 | 1 | 3.6319 | 1
104 | classroom | 224 | 14 |  | 716 | 16 | 14 | Perimeter Heater | 5728 | 2.3464 | 1 | 2.3464 | 1
105 | Classroom |  | 0 |  | 319 | 7 | 0 | Perimeter Heater | 2552 | unk | unk | unk | unk
106 | classroom | 189 | 12 |  | 730 | 16 | 12 | Perimeter Heater | 5840 | 1.9418 | 1 | 1.9418 | 1
108A | First Floor | 276 | 18 |  | 810 | 18 | 18 | Perimeter Heater | 6480 | 2.5556 | 1 | 2.5556 | 1
108B | First Floor | 59 | 3 |  | 129 | 2 | 2 | Perimeter Heater | 1032 | 3.4302 | 1 | 3.4302 | 1
108C | First Floor | 109 | 7 |  | 146 | 3 | 3 | Perimeter Heater | 1168 | 5.5993 | 2 | 5.5993 | 2
108D | First Floor | 54 | 3 |  | 86 | 1 | 1 | Perimeter Heater | 688 | 4.7093 | 2 | 4.7093 | 2
108E | First Floor | 87 | 5 |  | 75 | 1 | 1 | Perimeter Heater | 600 | 8.7 | 2 | 8.7 | 2
108F | First Floor | 62 | 4 |  | 94 | 2 | 2 | Perimeter Heater | 752 | 4.9468 | 2 | 4.9468 | 2
200 | classroom | 274 | 18 |  | 740 | 16 | 16 | Perimeter Heater | 5920 | 2.777 | 1 | 2.777 | 1
201 | classroom | 322 | 21 |  | 717 | 16 | 16 | Perimeter Heater | 5736 | 3.3682 | 1 | 3.3682 | 1
202 | classroom | 313 | 20 |  | 705 | 16 | 16 | Perimeter Heater | 5640 | 3.3298 | 1 | 3.3298 | 1
203 | classroom | 337 | 22 |  | 739 | 16 | 16 | Perimeter Heater | 5912 | 3.4202 | 1 | 3.4202 | 1
204 | classroom | 329 | 21 |  | 737 | 16 | 16 | Perimeter Heater | 5896 | 3.348 | 1 | 3.348 | 1
205 | classroom | 325 | 21 |  | 756 | 17 | 17 | Perimeter Heater | 6048 | 3.2242 | 1 | 3.2242 | 1
206 | classroom | 334 | 22 |  | 745 | 16 | 16 | Perimeter Heater | 5960 | 3.3624 | 1 | 3.3624 | 1
207 | classroom | 0 | 0 | Yes | 386 | 8 | 8 | Perimeter Heater | 3088 | 0 | 0 | 20 | 3
208 | classroom | 328 | 21 |  | 882 | 20 | 20 | Perimeter Heater | 7056 | 2.7891 | 1 | 2.7891 | 1
209 | classroom | 109 | 7 | Yes | 639 | 14 | 14 | Perimeter Heater | 5112 | 1.2793 | 1 | 21.2793 | 3
209A | classroom | 80 | 5 |  | 152 | 3 | 3 | Perimeter Heater | 1216 | 3.9474 | 1 | 3.9474 | 1
209B | classroom | 0 | 0 |  | 125 | 2 | 0 | Perimeter Heater | 1000 | 0 | 0 | 0 | 0
210 | classroom | 549 | 36 |  | 1185 | 26 | 26 | Perimeter Heater | 9480 | 3.4747 | 1 | 3.4747 | 1
211 | classroom | 845 | 56 |  | 728 | 16 | 16 | Perimeter Heater | 5824 | 8.7054 | 2 | 8.7054 | 2
212 | classroom | 116 | 7 |  | 434 | 9 | 7 | Perimeter Heater | 3472 | 2.0046 | 1 | 2.0046 | 1
213 | classroom | 131 | 8 |  | 224 | 5 | 5 | Perimeter Heater | 1792 | 4.3862 | 2 | 4.3862 | 2
300 | classroom | 532 | 35 |  | 763 | 17 | 17 | Perimeter Heater | 6104 | 5.2294 | 2 | 5.2294 | 2
300A | classroom | 395 | 26 |  | 224 | 5 | 5 | Perimeter Heater | 1792 | 13.2254 | 3 | 13.2254 | 3
301 | classroom | 350 | 23 |  | 755 | 17 | 17 | Perimeter Heater | 6040 | 3.4768 | 1 | 3.4768 | 1
302 | classroom | 289 | 19 |  | 746 | 16 | 16 | Perimeter Heater | 5968 | 2.9055 | 1 | 2.9055 | 1
303 | classroom | 447 | 29 |  | 722 | 16 | 16 | Perimeter Heater | 5776 | 4.6434 | 2 | 4.6434 | 2
304 | classroom | 434 | 28 |  | 745 | 16 | 16 | Perimeter Heater | 5960 | 4.3691 | 2 | 4.3691 | 2
305 | classroom | 360 | 24 |  | 747 | 16 | 16 | Perimeter Heater | 5976 | 3.6145 | 1 | 3.6145 | 1
306 | classroom | 534 | 35 |  | 715 | 16 | 16 | Perimeter Heater | 5720 | 5.6014 | 2 | 5.6014 | 2
307 | Classroom |  | 0 |  | 790 | 17 | 0 | Perimeter Heater | 6320 | unk | unk | unk | unk
308 | classroom | 278 | 18 |  | 717 | 16 | 16 | Perimeter Heater | 5736 | 2.9079 | 1 | 2.9079 | 1
- | Auditorium | 0 | 0 |  | 2919 | 66 | 0 | AHU | 23352 | 0 | 0 | 0 | 0
- | Cafeteria/Gym | 0 | 0 | Yes | 3719 | 84 | 84 | AHU | 29752 | 0 | 0 | 20 | 3
- | Dean's Office (Temple) | 72 | 4 |  | 106 | 2 | 2 | Perimter Heater | 848 | 5.0943 | 2 | 5.0943 | 2
- | Health Office | 274 | 18 |  | 294 | 6 | 6 | Perimter Heater | 2352 | 6.9898 | 2 | 6.9898 | 2
- | Office | 300 | 20 |  | 984 | 22 | 20 | Perimter Heater | 7872 | 2.2866 | 1 | 2.2866 | 1
- | Principal | 187 | 12 |  | 321 | 7 | 7 | Perimter Heater | 2568 | 4.3692 | 2 | 4.3692 | 2
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | Edward Steel Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCORE Fluidics | Exhaust Report | [7 empty] | unk | unk | unk | unk
| 2-15-2021 Retest | 2-22-21 Retest | 4-12-21 Retest | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Storeroom | 0 | 0 | Yes | 323 | 7 | 7 | Air Coil Unit | 2584 | 0 | 0 | 20 | 3
101A - C | Office | 0 | 0 | Yes | 356 | 8 | 8 | Air Coil Unit | 2848 | 0 | 0 | 20 | 3
102 | Main Office- open office | 0 | 0 | Yes | 512 | 11 | 11 | Air Coil Unit | 4096 | 0 | 0 | 20 | 3
102 | Main Office- admin ofc | 0 | 0 |  | 121 | 2 | 0 | Air Coil Unit | 968 | 0 | 0 | 0 | 0
102 | Main Office- asst principals ofc | 0 | 0 | Yes | 121 | 2 | 2 | Air Coil Unit | 968 | 0 | 0 | 20 | 3
102 | Main Office- principals ofc | 0 | 0 | Yes | 143 | 3 | 3 | Air Coil Unit | 1144 | 0 | 0 | 20 | 3
102 | Main Office- conf rm | 0 | 0 | Yes | 204 | 4 | 4 | Air Coil Unit | 1632 | 0 | 0 | 20 | 3
103 | Lounge | 0 | 0 | Yes | 676 | 15 | 15 | Air Coil Unit | 5408 | 0 | 0 | 20 | 3
104 | counselors ofc | 0 | 0 | Yes | 385 | 8 | 8 | Air Coil Unit | 3080 | 0 | 0 | 20 | 3
105 | Classroom | 46 | 3 | Yes | 660 | 15 | 15 | Air Handling Unit | 5280 | 0.52273 | 0 | 20.5227 | 3
106 | data room | 0 | 0 | Yes | 1364 | 31 | 31 | Air Coil Unit | 10912 | 0 | 0 | 20 | 3
107 | Classroom | 363 | 24 | Yes | 1364 | 31 | 31 | Air Handling Unit | 10912 | 1.996 | 1 | 21.996 | 3
109 | Classroom | 257 | 17 | Yes | 1364 | 31 | 31 | Air Handling Unit | 10912 | 1.4131 | 1 | 21.4131 | 3
110 | nurse str | 0 | 0 | Yes | 886 | 20 | 20 | Air Coil Unit | 7088 | 0 | 0 | 20 | 3
- | Nurse Waiting Area |  | 0 | Yes | 208 | 4 | 4 |  | 1664 | unk | unk | 20 | 3
111 | Classroom | 450 | 30 | Yes | 1364 | 31 | 31 | Air Handling Unit | 10912 | 2.4743 | 1 | 22.4743 | 3
113 | Classroom | 338 | 22 | Yes | 1364 | 31 | 31 | Air Handling Unit | 10912 | 1.8585 | 1 | 21.8585 | 3
- | AUDITORIUM | 475 | 31 | Yes | 2482 | 56 | 56 | Air Coil Unit | 19856 | 1.4353 | 1 | 21.4353 | 3
- | CAFETERIA | 0 | 0 | Yes | 3478 | 79 | 79 | Air Coil Unit | 27824 | 0 | 0 | 20 | 3
- | Cafeteria Office |  | 0 | Yes | 300 | 6 | 6 |  | 2400 | unk | unk | 20 | 3
- | IMC | 2021 | 134 |  | 3283 | 74 | 74 | Air Coil Unit | 26264 | 4.617 | 2 | 4.617 | 2
201 | Classroom | 163 | 10 | Yes | 1330 | 30 | 30 | Air Handling Unit | 10640 | 0.91917 | 0 | 20.9192 | 3
202 | Classroom | 250 | 16 | Yes | 1330 | 30 | 30 | Air Handling Unit | 10640 | 1.4098 | 1 | 21.4098 | 3
203 | Classroom | 188 | 12 | Yes | 1147 | 26 | 26 | Air Handling Unit | 9176 | 1.2293 | 1 | 21.2293 | 3
204 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0 | 20 | 3
205 | Classroom | 194 | 12 | Yes | 1147 | 26 | 26 | Air Handling Unit | 9176 | 1.2685 | 1 | 21.2685 | 3
206 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0 | 20 | 3
207 | Classroom | 144 | 9 | Yes | 1147 | 26 | 26 | Air Handling Unit | 9176 | 0.94159 | 0 | 20.9416 | 3
208 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0 | 20 | 3
209 | Classroom | 186 | 12 | Yes | 1147 | 26 | 26 | Air Handling Unit | 9176 | 1.2162 | 1 | 21.2162 | 3
210 | Classroom | 196 | 13 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 1.2816 | 1 | 21.2816 | 3
211 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0 | 20 | 3
212 | Classroom | 287 | 19 | Yes | 1130 | 25 | 25 | Air Coil Unit | 9040 | 1.9049 | 1 | 21.9049 | 3
213 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | Air Coil Unit | 6960 | 0 | 0 | 20 | 3
214 | Classroom |  | 0 | Yes | 870 | 19 | 19 | Air Coil Unit | 6960 | unk | unk | 20 | 3
215 | Office | 0 | 0 | Yes | 345 | 7 | 7 | Air Coil Unit | 2760 | 0 | 0 | 20 | 3
216 | Classroom | 0 | 0 | Yes | 588 | 13 | 13 | Air Coil Unit | 4704 | 0 | 0 | 20 | 3
219 | Classroom |  | 0 | Yes | 462 | 10 | 10 | Air Coil Unit | 3696 | unk | unk | 20 | 3
220 | team office | 0 | 0 | Yes | 462 | 10 | 10 | Air Coil Unit | 3696 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 | Yes | 1330 | 30 | 30 | Air Coil Unit | 10640 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 1330 | 30 | 30 | Air Coil Unit | 10640 | 0 | 0 | 20 | 3
303 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0 | 20 | 3
304 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0 | 20 | 3
305 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0 | 20 | 3
308 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 | Yes | 1155 | 26 | 26 | Air Coil Unit | 9240 | 0 | 0 | 20 | 3
310 | Classroom | 0 | 0 | Yes | 1147 | 26 | 26 | Air Coil Unit | 9176 | 0 | 0 | 20 | 3
311 | Classroom | 0 | 0 | Yes | 1330 | 30 | 30 | Air Coil Unit | 10640 | 0 | 0 | 20 | 3
312 | Classroom | 482 | 32 |  | 1330 | 30 | 30 | Air Coil Unit | 10640 | 2.718 | 1 | 2.718 | 1
313 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | Air Coil Unit | 6960 | 0 | 0 | 20 | 3
314 | Classroom | 0 | 0 | Yes | 870 | 19 | 19 | Air Coil Unit | 6960 | 0 | 0 | 20 | 3
315 | Staff Lounge |  | 0 | Yes | 330 | 7 | 7 | Air Coil Unit | 2640 | unk | unk | 20 | 3
319 | Classroom |  | 0 | Yes | 462 | 10 | 10 | Air Coil Unit | 3696 | unk | unk | 20 | 3
320 | team office |  | 0 | Yes | 462 | 10 | 10 | Air Coil Unit | 3696 | unk | unk | 20 | 3
- | imc office | 105 | 7 | Yes | 3283 | 74 | 74 | Air Coil Unit | 26264 | 0.23987 | 0 | 20.2399 | 3
- | imc storage | 70 | 4 |  | 255 | 5 | 4 | Air Coil Unit | 2040 | 2.0588 | 1 | 2.0588 | 1
- | material production | 210 | 14 | Yes | 625 | 14 | 14 | Air Coil Unit | 5000 | 2.52 | 1 | 22.52 | 3
- | open library | 1180 | 78 |  | 3360 | 76 | 76 | Air Coil Unit | 26880 | 2.6339 | 1 | 2.6339 | 1
- | Gym Office |  | 0 | Yes | 168 | 3 | 3 |  | 1344 | unk | unk | 20 | 3
- | Gym | 7824 | 521 |  | 4860 | 110 | 110 |  | 38880 | 12.0741 | 3 | 12.0741 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | Parkway Center City Middle College @ Stoddart Fleisher | [8 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | kitchen |  | 0 |  | 837 | 19 | 0 |  | 6696 | unk | unk | unk | unk
- | lunchroom |  | 0 |  | 3822 | 86 | 0 |  | 30576 | unk | unk | unk | unk
- | art room |  | 0 |  | 782 | 17 | 0 |  | 6256 | unk | unk | unk | unk
506 | art room |  | 0 |  | 851 | 19 | 0 |  | 6808 | unk | unk | unk | unk
505B | office |  | 0 |  | 528 | 12 | 0 |  | 4224 | unk | unk | unk | unk
505 | classroom |  | 0 |  | 1078 | 24 | 0 |  | 8624 | unk | unk | unk | unk
504 | classroom |  | 0 |  | 1144 | 26 | 0 |  | 9152 | unk | unk | unk | unk
503A | office |  | 0 |  | 96 | 2 | 0 |  | 768 | unk | unk | unk | unk
503B | shop |  | 0 |  | 252 | 5 | 0 |  | 2016 | unk | unk | unk | unk
- | teacher's lounge |  | 0 |  | 621 | 14 | 0 |  | 4968 | unk | unk | unk | unk
502 | classroom |  | 0 |  | 552 | 12 | 0 |  | 4416 | unk | unk | unk | unk
501 | classroom |  | 0 |  | 640 | 14 | 0 |  | 5120 | unk | unk | unk | unk
411 | classroom |  | 0 |  | 770 | 17 | 0 |  | 6160 | unk | unk | unk | unk
410 | classroom |  | 0 |  | 805 | 18 | 0 |  | 6440 | unk | unk | unk | unk
409 | classroom |  | 0 |  | 713 | 16 | 0 |  | 5704 | unk | unk | unk | unk
408 | classroom |  | 0 |  | 716 | 16 | 0 |  | 5728 | unk | unk | unk | unk
407 | classroom |  | 0 |  | 748 | 17 | 0 |  | 5984 | unk | unk | unk | unk
406 | classroom |  | 0 |  | 704 | 16 | 0 |  | 5632 | unk | unk | unk | unk
405B | counselor |  | 0 |  | 135 | 3 | 0 |  | 1080 | unk | unk | unk | unk
405A | VP office |  | 0 |  | 506 | 11 | 0 |  | 4048 | unk | unk | unk | unk
404 | classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | unk | unk | unk | unk
403 | classroom |  | 0 |  | 621 | 14 | 0 |  | 4968 | unk | unk | unk | unk
402 | classroom |  | 0 |  | 598 | 13 | 0 |  | 4784 | unk | unk | unk | unk
401 | classroom |  | 0 |  | 640 | 14 | 0 |  | 5120 | unk | unk | unk | unk
310 | classroom |  | 0 |  | 704 | 16 | 0 |  | 5632 | unk | unk | unk | unk
309 | weight room |  | 0 |  | 920 | 20 | 0 |  | 7360 | unk | unk | unk | unk
308 | classroom |  | 0 |  | 897 | 20 | 0 |  | 7176 | unk | unk | unk | unk
307 | classroom |  | 0 |  | 858 | 19 | 0 |  | 6864 | unk | unk | unk | unk
306 | storage room |  | 0 |  | 682 | 15 | 0 |  | 5456 | unk | unk | unk | unk
305 | classroom |  | 0 |  | 660 | 15 | 0 |  | 5280 | unk | unk | unk | unk
304 | classroom |  | 0 |  | 726 | 16 | 0 |  | 5808 | unk | unk | unk | unk
303A | office |  | 0 |  | 161 | 3 | 0 |  | 1288 | unk | unk | unk | unk
303 | classroom |  | 0 |  | 713 | 16 | 0 |  | 5704 | unk | unk | unk | unk
302 | classroom |  | 0 |  | 682 | 15 | 0 |  | 5456 | unk | unk | unk | unk
301A | computer office |  | 0 |  | 184 | 4 | 0 |  | 1472 | unk | unk | unk | unk
301 | classroom |  | 0 |  | 640 | 14 | 0 |  | 5120 | unk | unk | unk | unk
- | Boys locker room |  | 0 |  | 360 | 8 | 0 |  | 2880 | unk | unk | unk | unk
- | Gym |  | 0 |  | 3300 | 75 | 0 |  | 26400 | unk | unk | unk | unk
- | Girls Locker room |  | 0 |  | 324 | 7 | 0 |  | 2592 | unk | unk | unk | unk
- | Nurses office |  | 0 |  | 240 | 5 | 0 |  | 1920 | unk | unk | unk | unk
- | Exam Room |  | 0 |  | 150 | 3 | 0 |  | 1200 | unk | unk | unk | unk
208 | classroom |  | 0 |  | 598 | 13 | 0 |  | 4784 | unk | unk | unk | unk
207 | classroom |  | 0 |  | 598 | 13 | 0 |  | 4784 | unk | unk | unk | unk
206 | classroom |  | 0 |  | 644 | 14 | 0 |  | 5152 | unk | unk | unk | unk
205 | Library |  | 0 |  | 1081 | 24 | 0 |  | 8648 | unk | unk | unk | unk
- | Main Office Area |  | 0 |  | 285 | 6 | 0 |  | 2280 | unk | unk | unk | unk
- | Main Office Waiting area |  | 0 |  | 150 | 3 | 0 |  | 1200 | unk | unk | unk | unk
- | Principal's office |  | 0 |  | 280 | 6 | 0 |  | 2240 | unk | unk | unk | unk
204 | classroom |  | 0 |  | 616 | 14 | 0 |  | 4928 | unk | unk | unk | unk
203 | classroom |  | 0 |  | 621 | 14 | 0 |  | 4968 | unk | unk | unk | unk
202 | classroom |  | 0 |  | 598 | 13 | 0 |  | 4784 | unk | unk | unk | unk
201 | counselor's Sitting area |  | 0 |  | 200 | 4 | 0 |  | 1600 | unk | unk | unk | unk
201A | counselor's A |  | 0 |  | 96 | 2 | 0 |  | 768 | unk | unk | unk | unk
201B | counselor's B |  | 0 |  | 132 | 3 | 0 |  | 1056 | unk | unk | unk | unk
201C | counselor's C |  | 0 |  | 121 | 2 | 0 |  | 968 | unk | unk | unk | unk
201D | counsel's D |  | 0 |  | 121 | 2 | 0 |  | 968 | unk | unk | unk | unk
105 | conferance room |  | 0 |  | 598 | 13 | 0 |  | 4784 | unk | unk | unk | unk
104A | classroom |  | 0 |  | 247 | 5 | 0 |  | 1976 | unk | unk | unk | unk
104B | office |  | 0 |  | 117 | 2 | 0 |  | 936 | unk | unk | unk | unk
104C | office |  | 0 |  | 112 | 2 | 0 |  | 896 | unk | unk | unk | unk
104D | office |  | 0 |  | 90 | 2 | 0 |  | 720 | unk | unk | unk | unk
104E | office |  | 0 |  | 99 | 2 | 0 |  | 792 | unk | unk | unk | unk
- | Regional office |  | 0 |  | No Access | 0 | 0 |  |  | unk | unk | unk | unk
- | Data room |  | 0 |  | 484 | 11 | 0 |  | 3872 | unk | unk | unk | unk
102A | classroom |  | 0 |  | 693 | 15 | 0 |  | 5544 | unk | unk | unk | unk
102C | office |  | 0 |  | 195 | 4 | 0 |  | 1560 | unk | unk | unk | unk
102E | classroom |  | 0 |  | 513 | 11 | 0 |  | 4104 | unk | unk | unk | unk
102D | office |  | 0 |  | 635 | 14 | 0 |  | 5080 | unk | unk | unk | unk
102B | office |  | 0 |  | 195 | 4 | 0 |  | 1560 | unk | unk | unk | unk
101 | counselor |  | 0 |  | 306 | 6 | 0 |  | 2448 | unk | unk | unk | unk
- | Auditorium |  | 0 |  | 4539 | 103 | 0 |  | 36312 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | Strawberry Mansion High School | [8 empty] | unk | unk | unk | unk
School: | Leslie P. Hill Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Strawberry Mansion | [9 empty] | unk | unk | unk | unk
101 | Music Rm. | 0 | 0 |  | 1288 | 29 | 0 | Heating Unit Ventilator | 10304 | 0 | 0 | 0 | 0
102 | Classroom | 542 | 36 |  | 768 | 17 | 17 | Univent | 6144 | 5.293 | 2 | 5.293 | 2
103 | Music Rm. | 78 | 5 |  | 1288 | 29 | 5 | Heating Unit Ventilator | 10304 | 0.45419 | 0 | 0.45419 | 0
104 | Classroom | 427 | 28 |  | 888 | 20 | 20 | Univent | 7104 | 3.6064 | 1 | 3.6064 | 1
108 | Classroom | 0 | 0 |  | 888 | 20 | 0 | Univent | 7104 | 0 | 0 | 0 | 0
109A & 109B | Classroom | 620 | 41 |  | 1288 | 29 | 29 | Heating Unit Ventilator | 10304 | 3.6102 | 1 | 3.6102 | 1
110 | Classroom | 695 | 46 |  | 888 | 20 | 20 | Univent | 7104 | 5.8699 | 2 | 5.8699 | 2
111 | Classroom | 444 | 29 |  | 288 | 6 | 6 | Univent | 2304 | 11.5625 | 3 | 11.5625 | 3
112 | Classroom | 0 | 0 |  | 888 | 20 | 0 | Univent | 7104 | 0 | 0 | 0 | 0
200 | Classroom | 0 | 0 |  | 1056 | 24 | 0 | Univent | 8448 | 0 | 0 | 0 | 0
201 | Classroom | 416 | 27 |  | 805 | 18 | 18 | Univent | 6440 | 3.8758 | 1 | 3.8758 | 1
202 | Classroom | 357 | 23 |  | 1152 | 26 | 23 | Univent | 9216 | 2.3242 | 1 | 2.3242 | 1
203 | Classroom | 607 | 40 |  | 782 | 17 | 17 | Univent | 6256 | 5.8216 | 2 | 5.8216 | 2
206 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0 | 0 | 0
207 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
208 | Classroom | 512 | 34 |  | 1104 | 25 | 25 | Univent | 8832 | 3.4783 | 1 | 3.4783 | 1
209 | Computer Lab | 859 | 57 |  | 1012 | 23 | 23 | Air Handling Unit | 8096 | 6.3661 | 2 | 6.3661 | 2
212 | Classroom | 382 | 25 |  | 851 | 19 | 19 | Univent | 6808 | 3.3666 | 1 | 3.3666 | 1
214 | Classroom | 301 | 20 |  | 851 | 19 | 19 | Univent | 6808 | 2.6528 | 1 | 2.6528 | 1
216 | Classroom | 350 | 23 |  | 851 | 19 | 19 | Univent | 6808 | 3.0846 | 1 | 3.0846 | 1
217 | Classroom | 516 | 34 |  | 1012 | 23 | 23 | Univent | 8096 | 3.8241 | 1 | 3.8241 | 1
219 | Classroom | 0 | 0 |  | 960 | 21 | 0 | Univent | 7680 | 0 | 0 | 0 | 0
220 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
222 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
224 | Classroom | 0 | 0 |  | 782 | 17 | 0 | Univent | 6256 | 0 | 0 | 0 | 0
300 | Classroom | 464 | 30 |  | 782 | 17 | 17 | Univent | 6256 | 4.4501 | 2 | 4.4501 | 2
301 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0 | 0 | 0
302 | Classroom | 401 | 26 |  | 782 | 17 | 17 | Univent | 6256 | 3.8459 | 1 | 3.8459 | 1
303 | Classroom | 0 | 0 |  | 805 | 18 | 0 | Univent | 6440 | 0 | 0 | 0 | 0
304 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
306 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
307 | Classroom | 442 | 29 |  | 851 | 19 | 19 | Univent | 6808 | 3.8954 | 1 | 3.8954 | 1
308 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
309 | Classroom | 335 | 22 |  | 851 | 19 | 19 | Univent | 6808 | 2.9524 | 1 | 2.9524 | 1
310 | Classroom | 430 | 28 |  | 851 | 19 | 19 | Univent | 6808 | 3.7897 | 1 | 3.7897 | 1
311 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
312 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
314 | Classroom | 446 | 29 |  | 851 | 19 | 19 | Univent | 6808 | 3.9307 | 1 | 3.9307 | 1
315 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
316 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
317 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
319 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
320 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
322 | Classroom | 459 | 30 |  | 851 | 19 | 19 | Univent | 6808 | 4.0452 | 2 | 4.0452 | 2
323 | Classroom | 601 | 40 |  | 851 | 19 | 19 | Univent | 6808 | 5.2967 | 2 | 5.2967 | 2
324 | Classroom | 466 | 31 |  | 782 | 17 | 17 | Univent | 6256 | 4.4693 | 2 | 4.4693 | 2
325 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
400A&B | Classroom | 0 | 0 |  | 598 | 13 | 0 | Univent | 4784 | 0 | 0 | 0 | 0
401A | Classroom | 488 | 32 |  | 345 | 7 | 7 | Univent | 2760 | 10.6087 | 3 | 10.6087 | 3
402 | Classroom | 465 | 31 |  | 1288 | 29 | 29 | Univent | 10304 | 2.7077 | 1 | 2.7077 | 1
403 | Classroom | 250 | 16 |  | 299 | 6 | 6 | Univent | 2392 | 6.2709 | 2 | 6.2709 | 2
404 | Classroom | 434 | 28 |  | 1196 | 27 | 27 | Univent | 9568 | 2.7216 | 1 | 2.7216 | 1
405 | Classroom | 503 | 33 |  | 987 | 22 | 22 | Univent | 7896 | 3.8222 | 1 | 3.8222 | 1
406 | Classroom | 239 | 15 |  | 666 | 15 | 15 | Univent | 5328 | 2.6914 | 1 | 2.6914 | 1
407 | Classroom | 236 | 15 |  | 375 | 8 | 8 | Univent | 3000 | 4.72 | 2 | 4.72 | 2
408 | Classroom | 456 | 30 |  | 851 | 19 | 19 | Univent | 6808 | 4.0188 | 2 | 4.0188 | 2
409 | Classroom | 0 | 0 |  | 1288 | 29 | 0 | Univent | 10304 | 0 | 0 | 0 | 0
410 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
412 | Classroom | 431 | 28 |  | 851 | 19 | 19 | Univent | 6808 | 3.7985 | 1 | 3.7985 | 1
413 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
414 | Classroom | 467 | 31 |  | 851 | 19 | 19 | Univent | 6808 | 4.1157 | 2 | 4.1157 | 2
415 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
417 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
418 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
420 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
421 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
422 | Classroom | 0 | 0 |  | 782 | 17 | 0 | Univent | 6256 | 0 | 0 | 0 | 0
423 | Classroom | 0 | 0 |  | 851 | 19 | 0 | Univent | 6808 | 0 | 0 | 0 | 0
500 | Classroom | 280 | 18 |  | 800 | 18 | 18 | Univent | 6400 | 2.625 | 1 | 2.625 | 1
500B | Classroom | 264 | 17 |  | 375 | 8 | 8 | Univent | 3000 | 5.28 | 2 | 5.28 | 2
502 | Classroom | 442 | 29 |  | 300 | 6 | 6 | Univent | 2400 | 11.05 | 3 | 11.05 | 3
505 | Classroom | 0 | 0 |  | 1300 | 29 | 0 | Univent | 10400 | 0 | 0 | 0 | 0
506 | Classroom | 0 | 0 |  | 925 | 21 | 0 | Univent | 7400 | 0 | 0 | 0 | 0
507 | Classroom | 0 | 0 |  | 425 | 9 | 0 | Univent | 3400 | 0 | 0 | 0 | 0
508 | Classroom | 487 | 32 |  | 1250 | 28 | 28 | Univent | 10000 | 2.922 | 1 | 2.922 | 1
509 | Classroom | 0 | 0 |  | 1100 | 25 | 0 | Univent | 8800 | 0 | 0 | 0 | 0
513 | Classroom | 489 | 32 |  | 325 | 7 | 7 | Univent | 2600 | 11.2846 | 3 | 11.2846 | 3
516 | Classroom | 0 | 0 |  | 1327 | 30 | 0 | Univent | 10616 | 0 | 0 | 0 | 0
517 | Classroom | 0 | 0 |  | 1162 | 26 | 0 | Univent | 9296 | 0 | 0 | 0 | 0
518 | Classroom | 0 | 0 |  | 1375 | 31 | 0 | Univent | 11000 | 0 | 0 | 0 | 0
519 | Classroom | 292 | 19 |  | 570 | 12 | 12 | Univent | 4560 | 3.8421 | 1 | 3.8421 | 1
520 | Classroom | 683 | 45 |  | 1447 | 32 | 32 | Univent | 11576 | 3.5401 | 1 | 3.5401 | 1
522 | Classroom | 0 | 0 |  | 1471 | 33 | 0 | Univent | 11768 | 0 | 0 | 0 | 0
- | Library | 1247 | 83 |  | 1863 | 42 | 42 | Air Handling Unit | 14904 | 5.0201 | 2 | 5.0201 | 2
- | Culinary Arts area | 1077 | 71 |  | 6536 | 148 | 71 | Air Handling Unit | 52288 | 1.2358 | 1 | 1.2358 | 1
- | Book Strg. Rm. Security office | 0 | 0 |  | 1733 | 39 | 0 | Air Handling Unit | 13864 | 0 | 0 | 0 | 0
- | DOS office | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
- | EST office | 513 | 34 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
| Serves unknown | 0 | 0 |  |  | 0 | 0 | Heating Unit Ventilator |  | unk | unk | unk | unk
- | Auditorium | 7054 | 470 |  | 9936 | 225 | 225 | Heating Unit Ventilator | 79488 | 5.3246 | 2 | 5.3246 | 2
- | Cafeteria | 1912 | 127 |  | 10725 | 243 | 127 | Heating Unit Ventilator | 85800 | 1.3371 | 1 | 1.3371 | 1
- | Aud. Stage | 2999 | 199 |  | 2668 | 60 | 60 | Heating Unit Ventilator | 21344 | 8.4305 | 2 | 8.4305 | 2
- | Unknown location and what it serves |  | 0 |  |  | 0 | 0 | Heating Unit Ventilator |  | unk | unk | unk | unk
- | Maintenance office, Lobby | 317 | 21 |  |  | 0 | 0 | Heating Unit Ventilator |  | unk | unk | unk | unk
- | Girls Locker Room | 1759 | 117 |  |  | 0 | 0 | Heating Unit Ventilator |  | unk | unk | unk | unk
- | Girls Gym | 885 | 59 |  | 5808 | 132 | 59 | Heating Unit Ventilator | 46464 | 1.1428 | 1 | 1.1428 | 1
- | Boys Locker Room | 126 | 8 |  |  | 0 | 0 | Heating Unit Ventilator |  | unk | unk | unk | unk
- | Boys Gym | 6081 | 405 |  | 5808 | 132 | 132 | Heating Unit Ventilator | 46464 | 7.8525 | 2 | 7.8525 | 2
- | Unknown location and what it serves |  | 0 |  |  | 0 | 0 | Heating Unit Ventilator |  | unk | unk | unk | unk
- | Music Prac. Rms. & Office | 607 | 40 |  |  | 0 | 0 | Heating Unit Ventilator |  | unk | unk | unk | unk
- | Nurses area, Admin areas | 796 | 53 |  |  | 0 | 0 | Heating Unit Ventilator |  | unk | unk | unk | unk
- | Unknown |  | 0 |  |  | 0 | 0 | Heating Unit Ventilator |  | unk | unk | unk | unk
- | Unknown |  | 0 |  |  | 0 | 0 | Heating Unit Ventilator |  | unk | unk | unk | unk
LP Hill Building | [9 empty] | unk | unk | unk | unk
1 | Office | 0 | 0 |  | 870.365 | 19 | 0 | Vertical ACU | 6962.92 | 0 | 0 | 0 | 0
4 | Office | 0 | 0 |  | 409.462 | 9 | 0 | Vertical Air Coil Unit and Univent | 3275.696 | 0 | 0 | 0 | 0
5 | Classroom | 0 | 0 |  |  | 0 | 0 | Vertical Air Coil Unit and Univent |  | unk | unk | unk | unk
7 | Classroom | 0 | 0 |  |  | 0 | 0 | Vertical Air Coil Unit and Univent |  | unk | unk | unk | unk
7 | Conference Rm. | 0 | 0 |  | 1111.66 | 25 | 0 | Vertical Air Coil Unit and Univent | 8893.28 | 0 | 0 | 0 | 0
10 | Storage Room | 0 | 0 |  | 454.88 | 10 | 0 | Vertical Air Coil Unit | 3639.04 | 0 | 0 | 0 | 0
12 | Truency Court | 0 | 0 |  | 988.792 | 22 | 0 | Vertical Air Coil Unit | 7910.336 | 0 | 0 | 0 | 0
14 | Truency Court | 0 | 0 |  | 715.596 | 16 | 0 | Univent | 5724.768 | 0 | 0 | 0 | 0
15 | General Room | 0 | 0 |  | 734.479 | 16 | 0 | Vertical Air Coil Unit and Univent | 5875.832 | 0 | 0 | 0 | 0
100 | Classroom | 0 | 0 |  | 982.127 | 22 | 0 | Vertical Air Coil Unit and Univent | 7857.016 | 0 | 0 | 0 | 0
101 | Classroom | 0 | 0 |  | 1041.52 | 23 | 0 | Vertical Air Coil Unit and Univent | 8332.16 | 0 | 0 | 0 | 0
102 | Classroom | 0 | 0 |  | 973.903 | 22 | 0 | Univent | 7791.224 | 0 | 0 | 0 | 0
103 | Classroom | 0 | 0 |  | 1054.8 | 23 | 0 | Vertical Air Coil Unit and Univent | 8438.4 | 0 | 0 | 0 | 0
104 | Classroom | 0 | 0 |  | 1022.271 | 23 | 0 | Univent | 8178.168 | 0 | 0 | 0 | 0
105 | Classroom | 0 | 0 |  | 875 | 19 | 0 | Univent | 7000 | 0 | 0 | 0 | 0
106 | Classroom | 160 | 10 |  | 933.66 | 21 | 10 | Univent | 7469.28 | 1.2853 | 1 | 1.2853 | 1
107 | Classroom | 15 | 1 |  | 1492.29 | 33 | 1 | Univent | 11938.32 | 0.075387 | 0 | 0.075387 | 0
108 | Classroom | 224 | 14 |  | 1492.29 | 33 | 14 | Univent | 11938.32 | 1.1258 | 1 | 1.1258 | 1
200 | Office | 0 | 0 |  | 917.724 | 20 | 0 | Univent | 7341.792 | 0 | 0 | 0 | 0
202 | Office | 294 | 19 |  | 1034 | 23 | 19 | Univent | 8272 | 2.1325 | 1 | 2.1325 | 1
203 | Office | 0 | 0 |  | 833.94 | 18 | 0 | Univent | 6671.52 | 0 | 0 | 0 | 0
204 | Office | 50 | 3 |  | 1034 | 23 | 3 | Univent | 8272 | 0.36267 | 0 | 0.36267 | 0
205 | Office | 0 | 0 |  | 1033.59 | 23 | 0 | Univent | 8268.72 | 0 | 0 | 0 | 0
206 | Office | 0 | 0 |  | 951.5 | 21 | 0 | Univent | 7612 | 0 | 0 | 0 | 0
207 | Office | 31 | 2 |  | 1033.59 | 23 | 2 | Univent | 8268.72 | 0.22494 | 0 | 0.22494 | 0
209 | Office | 119 | 7 |  | 1031.06 | 23 | 7 | Univent | 8248.48 | 0.86561 | 0 | 0.86561 | 0
210 | Office | 0 | 0 |  | 1009.73 | 22 | 0 | Univent | 8077.84 | 0 | 0 | 0 | 0
212 | Office | 169 | 11 |  | 882.972 | 20 | 11 | Univent | 7063.776 | 1.4355 | 1 | 1.4355 | 1
213 | Office | 0 | 0 |  | 940.62 | 21 | 0 | Univent | 7524.96 | 0 | 0 | 0 | 0
214 | Waiting area | 0 | 0 |  | 912.502 | 20 | 0 | Univent | 7300.016 | 0 | 0 | 0 | 0
215 | Waiting area | 0 | 0 |  | 1025.81 | 23 | 0 | Univent | 8206.48 | 0 | 0 | 0 | 0
300 | Classroom | 216 | 14 |  | 922.898 | 20 | 14 | Univent | 7383.184 | 1.7553 | 1 | 1.7553 | 1
301 | Classroom | 0 | 0 |  | 921.33 | 20 | 0 | Univent | 7370.64 | 0 | 0 | 0 | 0
302 | Classroom | 0 | 0 |  | 1010.47 | 22 | 0 | Univent | 8083.76 | 0 | 0 | 0 | 0
303 | Classroom | 0 | 0 |  | 912.38 | 20 | 0 | Univent | 7299.04 | 0 | 0 | 0 | 0
304 | Classroom | 0 | 0 |  | 986.631 | 22 | 0 | Univent | 7893.048 | 0 | 0 | 0 | 0
305 | Classroom | 25 | 1 |  | 618.57 | 14 | 1 | Univent | 4948.56 | 0.30312 | 0 | 0.30312 | 0
306 | Classroom | 0 | 0 |  | 932.119 | 21 | 0 | Univent | 7456.952 | 0 | 0 | 0 | 0
307 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
309 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
310 | Classroom | 280 | 18 |  | 1009.5 | 22 | 18 | Univent | 8076 | 2.0802 | 1 | 2.0802 | 1
312 | Classroom | 0 | 0 |  | 992.166 | 22 | 0 | Univent | 7937.328 | 0 | 0 | 0 | 0
313 | Classroom | 0 | 0 |  | 978.97 | 22 | 0 | Univent | 7831.76 | 0 | 0 | 0 | 0
314 | Classroom | 0 | 0 |  | 911.255 | 20 | 0 | Univent | 7290.04 | 0 | 0 | 0 | 0
315 | Classroom |  | 0 |  | 863.91 | 19 | 0 | Univent | 6911.28 | unk | unk | unk | unk
400 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
401 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
402 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
403 | Classroom | 194 | 12 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
404 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
405 | Classroom | 92 | 6 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
406 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
407 | Classroom | 131 | 8 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
409 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
410 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
411/413 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
412 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
414 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
415 | Classroom | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
- | Faculty Rm. | 0 | 0 |  |  | 0 | 0 | Univent |  | unk | unk | unk | unk
- | Main office | 0 | 0 |  | 1107.41 | 25 | 0 | Univent | 8859.28 | 0 | 0 | 0 | 0
- | Princ. Office | 682 | 45 |  | 355.756 | 8 | 8 | Univent | 2846.048 | 14.3778 | 3 | 14.3778 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | James J. Sullivan Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B7 | Classroom |  | 0 | Yes | 610 | 13 | 13 | House Fan | 4880 | unk | unk | 20 | 3
B2 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
- | Library |  | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | unk | unk | 20 | 3
B9 | Classroom |  | 0 |  | 506 | 11 | 0 | House Fan | 4048 | unk | unk | unk | unk
- | Kitchen |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | unk | unk | unk | unk
101 | Classroom |  | 0 | Yes | 920 | 20 | 20 | House Fan | 7360 | unk | unk | 20 | 3
102 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
103 | Classroom |  | 0 |  | 736 | 16 | 0 | House Fan | 5888 | unk | unk | unk | unk
104 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
105 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
106 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
107 | Classroom |  | 0 | Yes | 275 | 6 | 6 |  | 2200 | unk | unk | 20 | 3
107a | office |  | 0 | Yes | 115 | 2 | 2 | House Fan | 920 | unk | unk | 20 | 3
107b | office |  | 0 | Yes | 115 | 2 | 2 | House Fan | 920 | unk | unk | 20 | 3
107c | office |  | 0 | Yes | 115 | 2 | 2 | House Fan | 920 | unk | unk | 20 | 3
108 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
109 | Classroom |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
110 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
- | Main Office |  | 0 | Yes | 336 | 7 | 7 | House Fan | 2688 | unk | unk | 20 | 3
- | Principal's Office |  | 0 | Yes | 210 | 4 | 4 | House Fan | 1680 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
204 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
205 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
206 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
207 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
208 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
209 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
210 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
211 | Classroom |  | 0 | Yes | 192 | 4 | 4 | House Fan | 1536 | unk | unk | 20 | 3
214 | Classroom |  | 0 | Yes | 384 | 8 | 8 | House Fan | 3072 | unk | unk | 20 | 3
215 | Office |  | 0 | Yes | 195 | 4 | 4 | House Fan | 1560 | unk | unk | 20 | 3
- | Nurses Office |  | 0 | Yes | 264 | 6 | 6 | House Fan | 2112 | unk | unk | 20 | 3
300 | Classroom |  | 0 | Yes | 720 | 16 | 16 | House Fan | 5760 | unk | unk | 20 | 3
301 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
302 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
303 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
304 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
305 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
306 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
307 | Classroom |  | 0 | Yes | 690 | 15 | 15 | House Fan | 5520 | unk | unk | 20 | 3
307B | Classroom |  | 0 | Yes | 119 | 2 | 2 |  | 952 | unk | unk | 20 | 3
308 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
309 | Computer Room |  | 0 |  | 690 | 15 | 0 | House Fan | 5520 | unk | unk | unk | unk
310 | Classroom |  | 0 | Yes | 736 | 16 | 16 | House Fan | 5888 | unk | unk | 20 | 3
311 | Office |  | 0 | Yes | 192 | 4 | 4 | House Fan | 1536 | unk | unk | 20 | 3
- | Cafe/Gym |  | 0 | Yes | 3432 | 78 | 78 | Hydroxyl Unit | 27456 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-27 | [8 empty] | unk | unk | unk | unk
School: | Parkway West High School @ Sulzberger | [8 empty] | unk | unk | unk | unk
Vendor: | [9 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | - |  | 0 |  | 483 | 10 | 0 |  | 3864 | unk | unk | unk | unk
101 | - |  | 0 |  | 575 | 13 | 0 |  | 4600 | unk | unk | unk | unk
102 | - |  | 0 |  | 851 | 19 | 0 |  | 6808 | unk | unk | unk | unk
106 | - |  | 0 |  | 920 | 20 | 0 |  | 7360 | unk | unk | unk | unk
107 | - |  | 0 | Yes | 943 | 21 | 21 |  | 7544 | unk | unk | 20 | 3
108 | - |  | 0 | Yes | 874 | 19 | 19 |  | 6992 | unk | unk | 20 | 3
109 | - |  | 0 |  | 920 | 20 | 0 |  | 7360 | unk | unk | unk | unk
201 | - |  | 0 |  | 682 | 15 | 0 |  | 5456 | unk | unk | unk | unk
202 | - |  | 0 |  | 660 | 15 | 0 |  | 5280 | unk | unk | unk | unk
203 | - |  | 0 | Yes | 528 | 12 | 12 |  | 4224 | unk | unk | 20 | 3
203A | - |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | unk | unk | 20 | 3
204 | Nurses Office |  | 0 | Yes | 460 | 10 | 10 |  | 3680 | unk | unk | 20 | 3
205 | - |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | unk | unk | 20 | 3
206 | Counselors Office |  | 0 | Yes | 690 | 15 | 15 |  | 5520 | unk | unk | 20 | 3
Principal | Office |  | 0 | Yes | 322 | 7 | 7 |  | 2576 | unk | unk | 20 | 3
208 | Main Office |  | 0 | Yes | 825 | 18 | 18 |  | 6600 | unk | unk | 20 | 3
210 | - |  | 0 |  | 836 | 19 | 0 |  | 6688 | unk | unk | unk | unk
211 | - |  | 0 | Yes | 864 | 19 | 19 |  | 6912 | unk | unk | 20 | 3
212 | - |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | unk | unk | 20 | 3
212A | - |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | unk | unk | 20 | 3
213 | - |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | unk | unk | 20 | 3
215 | - |  | 0 |  | 816 | 18 | 0 |  | 6528 | unk | unk | unk | unk
216 | - |  | 0 | Yes | 748 | 17 | 17 |  | 5984 | unk | unk | 20 | 3
217 | - |  | 0 | Yes | 736 | 16 | 16 |  | 5888 | unk | unk | 20 | 3
218 | - |  | 0 | Yes | 704 | 16 | 16 |  | 5632 | unk | unk | 20 | 3
219 | - |  | 0 | Yes | 704 | 16 | 16 |  | 5632 | unk | unk | 20 | 3
220 | - |  | 0 | Yes | 704 | 16 | 16 |  | 5632 | unk | unk | 20 | 3
221 | - |  | 0 |  | 805 | 18 | 0 |  | 6440 | unk | unk | unk | unk
222 | - |  | 0 |  | 690 | 15 | 0 |  | 5520 | unk | unk | unk | unk
301-302 | - |  | 0 | Yes | 1012 | 23 | 23 |  | 8096 | unk | unk | 20 | 3
303 | - |  | 0 | Yes | 1176 | 26 | 26 |  | 9408 | unk | unk | 20 | 3
304 | - |  | 0 | Yes | 966 | 21 | 21 |  | 7728 | unk | unk | 20 | 3
305 | - |  | 0 |  | 858 | 19 | 0 |  | 6864 | unk | unk | unk | unk
306 | - |  | 0 | Yes | 770 | 17 | 17 |  | 6160 | unk | unk | 20 | 3
307 | - |  | 0 |  | 770 | 17 | 0 |  | 6160 | unk | unk | unk | unk
308 | - |  | 0 | Yes | 900 | 20 | 20 |  | 7200 | unk | unk | 20 | 3
309 | - |  | 0 |  | 880 | 20 | 0 |  | 7040 | unk | unk | unk | unk
310 | - |  | 0 |  | 880 | 20 | 0 |  | 7040 | unk | unk | unk | unk
311 | - |  | 0 |  | 924 | 21 | 0 |  | 7392 | unk | unk | unk | unk
312 | - |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | unk | unk | 20 | 3
313 | - |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | unk | unk | 20 | 3
314 | - |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | unk | unk | 20 | 3
315 | - |  | 0 |  | 330 | 7 | 0 |  | 2640 | unk | unk | unk | unk
316 | - |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | unk | unk | 20 | 3
317 | - |  | 0 |  | 748 | 17 | 0 |  | 5984 | unk | unk | unk | unk
318 | - |  | 0 | Yes | 736 | 16 | 16 |  | 5888 | unk | unk | 20 | 3
319 | - |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | unk | unk | 20 | 3
320 | - |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | unk | unk | 20 | 3
321 | - |  | 0 |  | 704 | 16 | 0 |  | 5632 | unk | unk | unk | unk
322 | - |  | 0 | Yes | 748 | 17 | 17 |  | 5984 | unk | unk | 20 | 3
323 | - |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
- | 3rd Flr. Computer Lab |  | 0 |  | 1035 | 23 | 0 |  | 8280 | unk | unk | unk | unk
- | Auditorium |  | 0 |  | 3390 | 77 | 0 |  | 27120 | unk | unk | unk | unk
- | North Caf. |  | 0 |  | 2680 | 60 | 0 |  | 21440 | unk | unk | unk | unk
- | South Caf. |  | 0 | Yes | 2720 | 61 | 61 |  | 21760 | unk | unk | 20 | 3
- | South Gym |  | 0 |  | 4186 | 95 | 0 |  | 33488 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | Swenson Arts & Technology High School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
49 | Classroom |  | 0 | Yes | 308 | 7 | 7 |  | 2464 | unk | unk | 20 | 3
50 | Classroom |  | 0 |  | 308 | 7 | 0 |  | 2464 | unk | unk | unk | unk
51 | Classroom |  | 0 | Yes | 308 | 7 | 7 |  | 2464 | unk | unk | 20 | 3
53 | Classroom |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | unk | unk | 20 | 3
4 | Classroom |  | 0 | Yes | 532 | 12 | 12 |  | 4256 | unk | unk | 20 | 3
5 | Classroom |  | 0 | Yes | 528 | 12 | 12 |  | 4224 | unk | unk | 20 | 3
6 | Classroom |  | 0 |  | 132 | 3 | 0 |  | 1056 | unk | unk | unk | unk
100 | Classroom | 242 | 16 |  | 1278 | 29 | 16 | Rooftop Unit | 10224 | 1.4202 | 1 | 1.4202 | 1
101 | Classroom | 143 | 9 |  | 228 | 5 | 5 | Rooftop Unit | 1824 | 4.7039 | 2 | 4.7039 | 2
102 | Classroom | 76 | 5 |  | 149 | 3 | 3 | Rooftop Unit | 1192 | 3.8255 | 1 | 3.8255 | 1
103 | Classroom | 82 | 5 |  | 151 | 3 | 3 | Rooftop Unit | 1208 | 4.0728 | 2 | 4.0728 | 2
104 | Classroom | 116 | 7 |  | 144 | 3 | 3 | Rooftop Unit | 1152 | 6.0417 | 2 | 6.0417 | 2
105 | Classroom | 40 | 2 |  | 110 | 2 | 2 | Rooftop Unit | 880 | 2.7273 | 1 | 2.7273 | 1
105 | Classroom | 55 | 3 |  | 200 | 4 | 3 | Rooftop Unit | 1600 | 2.0625 | 1 | 2.0625 | 1
106 | Classroom | 75 | 5 |  | 178 | 4 | 4 | Rooftop Unit | 1424 | 3.1601 | 1 | 3.1601 | 1
109 | Classroom | 93 | 6 |  | 306 | 6 | 6 | Rooftop Unit | 2448 | 2.2794 | 1 | 2.2794 | 1
110 | Classroom | 70 | 4 |  | 159 | 3 | 3 | Rooftop Unit | 1272 | 3.3019 | 1 | 3.3019 | 1
111 | Classroom | 42 | 2 |  | 146 | 3 | 2 | Rooftop Unit | 1168 | 2.1575 | 1 | 2.1575 | 1
112 | Classroom | 24 | 1 |  | 100 | 2 | 1 | Rooftop Unit | 800 | 1.8 | 1 | 1.8 | 1
113 | Classroom | 21 | 1 | Yes | 105 | 2 | 2 | Rooftop Unit | 840 | 1.5 | 1 | 21.5 | 3
114 | Classroom | 135 | 9 |  | 602 | 13 | 9 | Rooftop Unit | 4816 | 1.6819 | 1 | 1.6819 | 1
128 | Classroom | 612 | 40 |  | 1275 | 28 | 28 | Rooftop Unit | 10200 | 3.6 | 1 | 3.6 | 1
129 | Classroom | 39 | 2 |  | 144 | 3 | 2 | Rooftop Unit | 1152 | 2.0312 | 1 | 2.0312 | 1
130 | Classroom | 536 | 35 |  | 960 | 21 | 21 | Rooftop Unit | 7680 | 4.1875 | 2 | 4.1875 | 2
138 | Classroom | 305 | 20 | Yes | 1125 | 25 | 25 | Rooftop Unit | 9000 | 2.0333 | 1 | 22.0333 | 3
140 | Classroom | 675 | 45 |  | 1085 | 24 | 24 | Rooftop Unit | 8680 | 4.6659 | 2 | 4.6659 | 2
144 | Classroom | 1497 | 99 |  | 1734 | 39 | 39 | Rooftop Unit | 13872 | 6.4749 | 2 | 6.4749 | 2
146 | Classroom | 650 | 43 |  | 700 | 15 | 15 | Rooftop Unit | 5600 | 6.9643 | 2 | 6.9643 | 2
150 | Classroom | 618 | 41 |  | 308 | 7 | 7 | Rooftop Unit | 2464 | 15.0487 | 3 | 15.0487 | 3
164 | Classroom | 305 | 20 |  | 899 | 20 | 20 | Rooftop Unit | 7192 | 2.5445 | 1 | 2.5445 | 1
170 | Classroom | 188 | 12 |  | 351 | 7 | 7 | Rooftop Unit | 2808 | 4.0171 | 2 | 4.0171 | 2
171 | Classroom | 526 | 35 |  | 1461 | 33 | 33 | Rooftop Unit | 11688 | 2.7002 | 1 | 2.7002 | 1
172 | Classroom |  | 0 | Yes | 126 | 2 | 2 |  | 1008 | unk | unk | 20 | 3
176 | Classroom |  | 0 | Yes | 452 | 10 | 10 |  | 3616 | unk | unk | 20 | 3
180 | Classroom | 93 | 6 |  | 209 | 4 | 4 | Rooftop Unit | 1672 | 3.3373 | 1 | 3.3373 | 1
182 | Classroom | 251 | 16 | Yes | 1059 | 24 | 24 | Rooftop Unit | 8472 | 1.7776 | 1 | 21.7776 | 3
184 | Classroom | 228 | 15 | Yes | 1628 | 37 | 37 | Rooftop Unit | 13024 | 1.0504 | 1 | 21.0504 | 3
195 | Classroom | 439 | 29 |  | 1566 | 35 | 29 | Rooftop Unit | 12528 | 2.1025 | 1 | 2.1025 | 1
196 | Classroom | 68 | 4 |  | 272 | 6 | 4 | Rooftop Unit | 2176 | 1.875 | 1 | 1.875 | 1
200 | Classroom | 344 | 22 |  | 1624 | 36 | 22 | Rooftop Unit | 12992 | 1.5887 | 1 | 1.5887 | 1
201 & 201A | Classroom | 211 | 14 | Yes | 660 | 15 | 15 | Rooftop Unit | 5280 | 2.3977 | 1 | 22.3977 | 3
202 | Classroom | 181 | 12 | Yes | 836 | 19 | 19 | Rooftop Unit | 6688 | 1.6238 | 1 | 21.6238 | 3
203 | Classroom | 190 | 12 |  | 760 | 17 | 12 | Rooftop Unit | 6080 | 1.875 | 1 | 1.875 | 1
204 | Classroom |  | 0 | Yes | 1584 | 36 | 36 | Rooftop Unit | 12672 | unk | unk | 20 | 3
205 | Classroom | 328 | 21 | Yes | 1925 | 43 | 43 | Rooftop Unit | 15400 | 1.2779 | 1 | 21.2779 | 3
207 | Classroom | 994 | 66 |  | 2300 | 52 | 52 | Rooftop Unit | 18400 | 3.2413 | 1 | 3.2413 | 1
210 | Classroom | 1278 | 85 |  | 1020 | 23 | 23 | Rooftop Unit | 8160 | 9.3971 | 2 | 9.3971 | 2
213 | Classroom |  | 0 | Yes | 748 | 17 | 17 | Rooftop Unit | 5984 | unk | unk | 20 | 3
214 | Classroom |  | 0 | Yes | 126 | 2 | 2 |  | 1008 | unk | unk | 20 | 3
216 | Classroom | 410 | 27 |  | 1597 | 36 | 27 | Rooftop Unit | 12776 | 1.9255 | 1 | 1.9255 | 1
216 | Classroom | 1578 | 105 |  | 1597 | 36 | 36 | Rooftop Unit | 12776 | 7.4108 | 2 | 7.4108 | 2
227 | Classroom | 225 | 15 | Yes | 840 | 19 | 19 | Rooftop Unit | 6720 | 2.0089 | 1 | 22.0089 | 3
228 | Classroom | 135 | 9 | Yes | 930 | 21 | 21 | Rooftop Unit | 7440 | 1.0887 | 1 | 21.0887 | 3
229 | Classroom | 174 | 11 | Yes | 1008 | 22 | 22 | Rooftop Unit | 8064 | 1.2946 | 1 | 21.2946 | 3
230/231 | Classroom | 87 | 5 | Yes | 522 | 11 | 11 | Rooftop Unit | 4176 | 1.25 | 1 | 21.25 | 3
231 | Classroom | 43 | 2 |  | 100 | 2 | 2 | Rooftop Unit | 800 | 3.225 | 1 | 3.225 | 1
232 | Classroom |  | 0 | Yes | 968 | 22 | 22 |  | 7744 | unk | unk | 20 | 3
232B | Classroom | 46 | 3 | Yes | 348 | 7 | 7 | Rooftop Unit | 2784 | 0.99138 | 0 | 20.9914 | 3
234 | Classroom | 192 | 12 | Yes | 900 | 20 | 20 | Rooftop Unit | 7200 | 1.6 | 1 | 21.6 | 3
236 | Classroom | 293 | 19 |  | 1240 | 28 | 19 | Rooftop Unit | 9920 | 1.7722 | 1 | 1.7722 | 1
237 | Classroom | 186 | 12 | Yes | 969 | 22 | 22 | Rooftop Unit | 7752 | 1.4396 | 1 | 21.4396 | 3
238 | Classroom | 442 | 29 |  | 888 | 20 | 20 | Rooftop Unit | 7104 | 3.7331 | 1 | 3.7331 | 1
245 | Classroom | 281 | 18 |  | 675 | 15 | 15 | Rooftop Unit | 5400 | 3.1222 | 1 | 3.1222 | 1
247 | Classroom | 140 | 9 |  | 448 | 10 | 9 | Rooftop Unit | 3584 | 2.3438 | 1 | 2.3438 | 1
249 & 249 A-B | Classroom | 520 | 34 |  | 414 | 9 | 9 | Rooftop Unit | 3312 | 9.4203 | 2 | 9.4203 | 2
250 | Classroom | 303 | 20 |  | 900 | 20 | 20 | Rooftop Unit | 7200 | 2.525 | 1 | 2.525 | 1
253 | Classroom | 655 | 43 |  | 186 | 4 | 4 | Rooftop Unit | 1488 | 26.4113 | 4 | 26.4113 | 4
257 | Classroom | 341 | 22 |  | 756 | 17 | 17 | Rooftop Unit | 6048 | 3.3829 | 1 | 3.3829 | 1
258 | Classroom | 357 | 23 |  | 1050 | 23 | 23 | Rooftop Unit | 8400 | 2.55 | 1 | 2.55 | 1
259 | Classroom | 242 | 16 |  | 1225 | 27 | 16 | Rooftop Unit | 9800 | 1.4816 | 1 | 1.4816 | 1
260 and 260 A-C | Classroom | 579 | 38 |  | 561 | 12 | 12 | Rooftop Unit | 4488 | 7.7406 | 2 | 7.7406 | 2
261 | Classroom | 375 | 25 |  | 1050 | 23 | 23 | Rooftop Unit | 8400 | 2.6786 | 1 | 2.6786 | 1
262 | Classroom | 678 | 45 |  | 2373 | 53 | 45 | Rooftop Unit | 18984 | 2.1429 | 1 | 2.1429 | 1
263 | Classroom |  | 0 | Yes | 2373 | 53 | 53 |  | 18984 | unk | unk | 20 | 3
264 | Classroom | 333 | 22 |  | 870 | 19 | 19 | Rooftop Unit | 6960 | 2.8707 | 1 | 2.8707 | 1
265 | Classroom | 307 | 20 |  | 928 | 21 | 20 | Rooftop Unit | 7424 | 2.4811 | 1 | 2.4811 | 1
1750b | Room | 108 | 7 |  | 374 | 8 | 7 | Rooftop Unit | 2992 | 2.1658 | 1 | 2.1658 | 1
1775A | - |  | 0 | Yes | 528 | 12 | 12 |  | 4224 | unk | unk | 20 | 3
- | Baking Room | 525 | 34 |  | 1981 | 45 | 34 | Rooftop Unit | 15848 | 1.9876 | 1 | 1.9876 | 1
- | Dark Room | 59 | 3 |  | 104 | 2 | 2 | Rooftop Unit | 832 | 4.2548 | 2 | 4.2548 | 2
- | Corridor | 109 | 7 |  | 355 | 8 | 7 | Rooftop Unit | 2840 | 2.3028 | 1 | 2.3028 | 1
- | Hallway | 640 | 42 |  | 730 | 16 | 16 | Rooftop Unit | 5840 | 6.5753 | 2 | 6.5753 | 2
- | Corridor | 54 | 3 |  | 162 | 3 | 3 | Rooftop Unit | 1296 | 2.5 | 1 | 2.5 | 1
- | Corridor | 53 | 3 |  | 152 | 3 | 3 | Rooftop Unit | 1216 | 2.6151 | 1 | 2.6151 | 1
- | Corridor | 167 | 11 |  | 286 | 6 | 6 | Rooftop Unit | 2288 | 4.3794 | 2 | 4.3794 | 2
- | Corridor | 70 | 4 |  | 344 | 7 | 4 | Rooftop Unit | 2752 | 1.5262 | 1 | 1.5262 | 1
- | Hallway Diffuser s31 | 25 | 1 |  | 258 | 5 | 1 | Rooftop Unit | 2064 | 0.72674 | 0 | 0.72674 | 0
- | Kitchen | 1391 | 92 |  | 205 | 4 | 4 | Rooftop Unit | 1640 | 50.8902 | 5 | 50.8902 | 5
- | Nurse's Office/Medical | 165 | 11 |  | 591 | 13 | 11 | Rooftop Unit | 4728 | 2.0939 | 1 | 2.0939 | 1
- | Office | 35 | 2 |  | 287 | 6 | 2 | Rooftop Unit | 2296 | 0.91463 | 0 | 0.91463 | 0
- | Office | 77 | 5 |  | 1435 | 32 | 5 | Rooftop Unit | 11480 | 0.40244 | 0 | 0.40244 | 0
- | Office | 54 | 3 |  | 157 | 3 | 3 | Rooftop Unit | 1256 | 2.5796 | 1 | 2.5796 | 1
- | Office | 598 | 39 |  | 94 | 2 | 2 | Rooftop Unit | 752 | 47.7128 | 4 | 47.7128 | 4
- | Classroom | 313 | 20 |  | 1769 | 40 | 20 | Rooftop Unit | 14152 | 1.327 | 1 | 1.327 | 1
S1 | Classroom | 309 | 20 |  | 336 | 7 | 7 | Rooftop Unit | 2688 | 6.8973 | 2 | 6.8973 | 2
S2 | Classroom | 318 | 21 |  | 336 | 7 | 7 | Rooftop Unit | 2688 | 7.0982 | 2 | 7.0982 | 2
S3 | Classroom | 52 | 3 |  | 336 | 7 | 3 | Rooftop Unit | 2688 | 1.1607 | 1 | 1.1607 | 1
S3 | Office | 232 | 15 |  | 306 | 6 | 6 | Rooftop Unit | 2448 | 5.6863 | 2 | 5.6863 | 2
S4 | Office | 14 | 0 |  | 20 | 0 | 0 | Rooftop Unit | 160 | 5.25 | 2 | 5.25 | 2
S5 | Storage | 33 | 2 |  | 270 | 6 | 2 | Rooftop Unit | 2160 | 0.91667 | 0 | 0.91667 | 0
S6 | School Police | 207 | 13 |  | 515 | 11 | 11 | Rooftop Unit | 4120 | 3.0146 | 1 | 3.0146 | 1
S8 | Classroom | 104 | 6 |  | 560 | 12 | 6 | Rooftop Unit | 4480 | 1.3929 | 1 | 1.3929 | 1
- | School Store | 386 | 25 |  | 455 | 10 | 10 | Rooftop Unit | 3640 | 6.3626 | 2 | 6.3626 | 2
- | Second Floor Hallway | 95 | 6 |  | 1846 | 41 | 6 | Rooftop Unit | 14768 | 0.38597 | 0 | 0.38597 | 0
- | Storage | 33 | 2 |  | 590 | 13 | 2 | Rooftop Unit | 4720 | 0.41949 | 0 | 0.41949 | 0
- | Storage | 107 | 7 |  | 35 | 0 | 0 | Rooftop Unit | 280 | 22.9286 | 3 | 22.9286 | 3
- | Storage | 73 | 4 |  | 134 | 3 | 3 | Rooftop Unit | 1072 | 4.0858 | 2 | 4.0858 | 2
- | Storage | 44 | 2 |  | 94 | 2 | 2 | Rooftop Unit | 752 | 3.5106 | 1 | 3.5106 | 1
- | Storage | 45 | 3 |  | 91 | 2 | 2 | Rooftop Unit | 728 | 3.7088 | 1 | 3.7088 | 1
- | Storage/Closet | 237 | 15 |  | 50 | 1 | 1 | Rooftop Unit | 400 | 35.55 | 4 | 35.55 | 4
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | John H. Taggart Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | [9 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
102-A | Classroom |  | 0 |  | 372 | 8 | 0 |  | 2976 | unk | unk | unk | unk
102-B | Classroom |  | 0 |  | 230 | 5 | 0 |  | 1840 | unk | unk | unk | unk
103 | Classroom |  | 0 |  | 506 | 11 | 0 |  | 4048 | unk | unk | unk | unk
104 | Classroom |  | 0 | Yes | 594 | 13 | 13 |  | 4752 | unk | unk | 20 | 3
107 | Classroom |  | 0 | Yes | 682 | 15 | 15 |  | 5456 | unk | unk | 20 | 3
108 | Nurse's Office |  | 0 | Yes | 176 | 4 | 4 |  | 1408 | unk | unk | 20 | 3
- | 2nd Floor Dean of Student's Office |  | 0 |  | 144 | 3 | 0 |  | 1152 | unk | unk | unk | unk
200 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
201 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
203 | Classroom |  | 0 |  | 136 | 3 | 0 |  | 1088 | unk | unk | unk | unk
204 | Computer Lab |  | 0 | Yes | 924 | 21 | 21 |  | 7392 | unk | unk | 20 | 3
205 | Classroom |  | 0 |  | 414 | 9 | 0 |  | 3312 | unk | unk | unk | unk
206 | Classroom |  | 0 | Yes | 736 | 16 | 16 |  | 5888 | unk | unk | 20 | 3
207 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
208 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | unk | unk | 20 | 3
209 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | unk | unk | 20 | 3
- | 3rd Floor Men's Room |  | 0 |  | 56 | 1 | 0 |  | 448 | unk | unk | unk | unk
300 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | unk | unk | 20 | 3
301 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
302 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
303 | Classroom |  | 0 | Yes | 616 | 14 | 14 |  | 4928 | unk | unk | 20 | 3
304 | Classroom |  | 0 | Yes | 594 | 13 | 13 |  | 4752 | unk | unk | 20 | 3
305-306 | Library |  | 0 | Yes | 1320 | 30 | 30 |  | 10560 | unk | unk | 20 | 3
307 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | unk | unk | 20 | 3
308 | Classroom |  | 0 | Yes | 660 | 15 | 15 |  | 5280 | unk | unk | 20 | 3
309 | Classroom |  | 0 |  | 638 | 14 | 0 |  | 5104 | unk | unk | unk | unk
400 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
401 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
402 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
403 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | unk | unk | 20 | 3
404 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
405 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
406 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
407 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
408 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | unk | unk | 20 | 3
409 | Classroom |  | 0 | Yes | 667 | 15 | 15 |  | 5336 | unk | unk | 20 | 3
410 | Classroom |  | 0 | Yes | 638 | 14 | 14 |  | 5104 | unk | unk | 20 | 3
500 | Classroom |  | 0 | Yes | 132 | 3 | 3 |  | 1056 | unk | unk | 20 | 3
- | Gym |  | 0 | Yes | 3555 | 80 | 80 | Hydroxyl Unit | 28440 | unk | unk | 20 | 3
- | Building Engineer's Office |  | 0 |  | 286 | 6 | 0 |  | 2288 | unk | unk | unk | unk
- | Main Office |  | 0 | Yes | 286 | 6 | 6 |  | 2288 | unk | unk | 20 | 3
- | Principal's Office |  | 0 | Yes | 154 | 3 | 3 |  | 1232 | unk | unk | 20 | 3
- | Teacher's Lounge |  | 0 |  | 322 | 7 | 0 |  | 2576 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | Bayard Taylor Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Main Building Test 10-29-20 | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Main Building Retest 2-7-21 | [8 empty] | unk | unk | unk | unk
School: | Bayard Taylor Annex (Our Lady of Pompeii) | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | EMCOR Retest 2-18-21 | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Taylor Main Building | [9 empty] | unk | unk | unk | unk
B1 | Classroom | 210 | 14 |  | 780 | 17 | 14 | Univent | 6240 | 2.0192 | 1 | 2.0192 | 1
B1B and B1B North & South. | B1 and B1 North & South. | 325 | 21 |  | 760 | 17 | 17 | Univent | 6080 | 3.2072 | 1 | 3.2072 | 1
B2A & B2B | Classroom | 0 | 0 |  | 600 | 13 | 0 | Univent | 4800 | 0 | 0 | 0 | 0
B4 | Classroom | 299 | 19 |  | 1444 | 32 | 19 | Univent | 11552 | 1.553 | 1 | 1.553 | 1
B5 | Classroom | 316 | 21 |  | 1410 | 32 | 21 | Univent | 11280 | 1.6809 | 1 | 1.6809 | 1
101 | Classroom | 362 | 24 |  | 1159 | 26 | 24 | Univent | 9272 | 2.3425 | 1 | 2.3425 | 1
102 | Classroom |  | 0 | Yes | 1148 | 26 | 26 | Univent | 9184 | unk | unk | 20 | 3
103 | Classroom | 328 | 21 |  | 1149 | 26 | 21 | Univent | 9192 | 2.141 | 1 | 2.141 | 1
104 | Classroom | 387 | 25 |  | 1107 | 25 | 25 | Univent | 8856 | 2.622 | 1 | 2.622 | 1
105 | Classroom | 387 | 25 |  | 1394 | 31 | 25 | Univent | 11152 | 2.0821 | 1 | 2.0821 | 1
201 | Classroom | 342 | 22 |  | 1101 | 25 | 22 | Univent | 8808 | 2.3297 | 1 | 2.3297 | 1
202 | Classroom | 423 | 28 |  | 1097 | 24 | 24 | Univent | 8776 | 2.892 | 1 | 2.892 | 1
203 | Classroom |  | 0 | Yes | 1163 | 26 | 26 | Univent | 9304 | unk | unk | 20 | 3
204 | Classroom | 444 | 29 |  | 1099 | 24 | 24 | Univent | 8792 | 3.03 | 1 | 3.03 | 1
205 | Classroom | 470 | 31 |  | 1098 | 24 | 24 | Univent | 8784 | 3.2104 | 1 | 3.2104 | 1
206 | Classroom | 408 | 27 |  | 1052 | 23 | 23 | Univent | 8416 | 2.9087 | 1 | 2.9087 | 1
301 | Classroom |  | 0 | Yes | 1066 | 24 | 24 | Univent | 8528 | unk | unk | 20 | 3
302 | Classroom | 299 | 19 |  | 1065 | 24 | 19 | Univent | 8520 | 2.1056 | 1 | 2.1056 | 1
303 | Classroom | 317 | 21 |  | 1127 | 25 | 21 | Univent | 9016 | 2.1096 | 1 | 2.1096 | 1
304 | Classroom | 344 | 22 |  | 1133 | 25 | 22 | Univent | 9064 | 2.2771 | 1 | 2.2771 | 1
305 | Classroom | 73 | 4 | Yes | 1109 | 25 | 25 | Univent | 8872 | 0.49369 | 0 | 20.4937 | 3
306 | Classroom | 483 | 32 |  | 1107 | 25 | 25 | Univent | 8856 | 3.2724 | 1 | 3.2724 | 1
- | IMC Library | 353 | 23 |  | 1641 | 37 | 23 | Univent | 13128 | 1.6133 | 1 | 1.6133 | 1
- | Music Classroom | 162 | 10 |  | 780 | 17 | 10 | Univent | 6240 | 1.5577 | 1 | 1.5577 | 1
- | Main Office | 303 | 20 |  | 889 | 20 | 20 | Univent | 7112 | 2.5562 | 1 | 2.5562 | 1
- | Principal | 359 | 23 |  | 479 | 10 | 10 | Univent | 3832 | 5.6211 | 2 | 5.6211 | 2
- | Lounge | 232 | 15 |  | 300 | 6 | 6 | Univent | 2400 | 5.8 | 2 | 5.8 | 2
- | Nurse | 148 | 9 |  | 300 | 6 | 6 | Univent | 2400 | 3.7 | 1 | 3.7 | 1
- | Art Classroom | 123 | 8 |  | 1107 | 25 | 8 | Univent | 8856 | 0.83333 | 0 | 0.83333 | 0
Taylor Annex | [9 empty] | unk | unk | unk | unk
222 | Classroom |  | 0 |  | 750 | 17 | 0 | N/A | 6000 | unk | unk | unk | unk
223 | Classroom |  | 0 |  | 625 | 14 | 0 | N/A | 5000 | unk | unk | unk | unk
224 | Classroom |  | 0 |  | 675 | 15 | 0 | N/A | 5400 | unk | unk | unk | unk
231 | Classroom |  | 0 |  | 700 | 15 | 0 | N/A | 5600 | unk | unk | unk | unk
331 | Classroom |  | 0 |  | 700 | 15 | 0 | N/A | 5600 | unk | unk | unk | unk
332 | Classroom |  | 0 |  | 750 | 17 | 0 | N/A | 6000 | unk | unk | unk | unk
333 | Classroom |  | 0 |  | 675 | 15 | 0 | N/A | 5400 | unk | unk | unk | unk
334 | Classroom |  | 0 |  | 625 | 14 | 0 | N/A | 5000 | unk | unk | unk | unk
- | Auditorium/Gym/Ca |  | 0 |  | 2516 | 57 | 0 | N/A | 20128 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | Tilden Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | [9 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom |  | 0 |  | 576 | 13 | 0 | House Fan | 4608 | unk | unk | unk | unk
101 | Classroom |  | 0 |  | 624 | 14 | 0 | House Fan | 4992 | unk | unk | unk | unk
103 | Classroom |  | 0 | Yes | 960 | 21 | 21 | House Fan | 7680 | unk | unk | 20 | 3
104 | Classroom |  | 0 |  | 1248 | 28 | 0 | House Fan | 9984 | unk | unk | unk | unk
105 | Classroom |  | 0 | Yes | 1248 | 28 | 28 | House Fan | 9984 | unk | unk | 20 | 3
106 | Classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan | 6912 | unk | unk | 20 | 3
107 | Classroom |  | 0 | Yes | 792 | 18 | 18 | House Fan | 6336 | unk | unk | 20 | 3
109 | Classroom |  | 0 | Yes | 792 | 18 | 18 | House Fan | 6336 | unk | unk | 20 | 3
109A | Classroom |  | 0 |  | 704 | 16 | 0 | House Fan | 5632 | unk | unk | unk | unk
110 | Classroom |  | 0 | Yes | 616 | 14 | 14 | House Fan | 4928 | unk | unk | 20 | 3
202 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | unk | unk | 20 | 3
203 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | unk | unk | 20 | 3
203A | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan | 8448 | unk | unk | 20 | 3
204 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | unk | unk | 20 | 3
205 | Nurse's office |  | 0 | Yes | 384 | 8 | 8 | House Fan | 3072 | unk | unk | 20 | 3
207A | Principal's Office |  | 0 | Yes | 560 | 12 | 12 | House Fan | 4480 | unk | unk | 20 | 3
207C | Counselor's Suite |  | 0 |  | 120 | 2 | 0 | House Fan | 960 | unk | unk | unk | unk
207D | Counselor's Suite |  | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | unk | unk | 20 | 3
207F | Counselor's Suite |  | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | unk | unk | 20 | 3
207G | Counselor's Suite |  | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | unk | unk | 20 | 3
207H | Counselor's Suite |  | 0 |  | 120 | 2 | 0 | House Fan | 960 | unk | unk | unk | unk
208 | Main Office |  | 0 | Yes | 560 | 12 | 12 | House Fan | 4480 | unk | unk | 20 | 3
209 | IMC |  | 0 | Yes | 1728 | 39 | 39 | House Fan | 13824 | unk | unk | 20 | 3
211 | Classroom |  | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | unk | unk | 20 | 3
212 | Classroom |  | 0 | Yes | 1152 | 26 | 26 | House Fan | 9216 | unk | unk | 20 | 3
213 | Classroom |  | 0 |  | 616 | 14 | 0 | House Fan | 4928 | unk | unk | unk | unk
214 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | unk | unk | 20 | 3
214A | Classroom |  | 0 | Yes | 864 | 19 | 19 | House Fan | 6912 | unk | unk | 20 | 3
215 | Classroom |  | 0 | Yes | 576 | 13 | 13 | House Fan | 4608 | unk | unk | 20 | 3
301 | Classroom |  | 0 |  | 576 | 13 | 0 | House Fan | 4608 | unk | unk | unk | unk
302 | Carson Valley |  | 0 |  | 288 | 6 | 0 | House Fan | 2304 | unk | unk | unk | unk
303 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | unk | unk | 20 | 3
303A | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | unk | unk | 20 | 3
304 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | unk | unk | 20 | 3
305 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | unk | unk | unk | unk
306 | Classroom |  | 0 |  | 616 | 14 | 0 | House Fan | 4928 | unk | unk | unk | unk
307 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | unk | unk | unk | unk
308 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | unk | unk | unk | unk
310 | Classroom |  | 0 |  | 480 | 10 | 0 | House Fan | 3840 | unk | unk | unk | unk
311 | Classroom |  | 0 |  | 768 | 17 | 0 | House Fan | 6144 | unk | unk | unk | unk
312 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | unk | unk | unk | unk
313 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | unk | unk | unk | unk
314 | Classroom |  | 0 |  | 672 | 15 | 0 | House Fan | 5376 | unk | unk | unk | unk
315 | Dean of Students |  | 0 | Yes | 216 | 4 | 4 | House Fan | 1728 | unk | unk | 20 | 3
316 | Classroom |  | 0 | Yes | 768 | 17 | 17 | House Fan | 6144 | unk | unk | 20 | 3
318 | Classroom |  | 0 |  | 792 | 18 | 0 | House Fan | 6336 | unk | unk | unk | unk
319 | Classroom |  | 0 |  | 832 | 18 | 0 | House Fan | 6656 | unk | unk | unk | unk
401 | Classroom |  | 0 | Yes | 625 | 14 | 14 | House Fan | 5000 | unk | unk | 20 | 3
403A | Faculty Lounge |  | 0 | Yes | 792 | 18 | 18 | House Fan | 6336 | unk | unk | 20 | 3
404 | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan | 8448 | unk | unk | 20 | 3
404A | Classroom |  | 0 | Yes | 120 | 2 | 2 | House Fan | 960 | unk | unk | 20 | 3
405 | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan | 8448 | unk | unk | 20 | 3
406 | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan | 8448 | unk | unk | 20 | 3
407 | Classroom |  | 0 | Yes | 1056 | 24 | 24 | House Fan | 8448 | unk | unk | 20 | 3
408 | Classroom |  | 0 | Yes | 792 | 18 | 18 | House Fan | 6336 | unk | unk | 20 | 3
410B | Staff Conference |  | 0 | Yes | 1232 | 28 | 28 | House Fan | 9856 | unk | unk | 20 | 3
411 | Classroom |  | 0 | Yes | 769 | 17 | 17 | House Fan | 6152 | unk | unk | 20 | 3
412 | Classroom |  | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | unk | unk | 20 | 3
414 | Classroom |  | 0 | Yes | 968 | 22 | 22 | House Fan | 7744 | unk | unk | 20 | 3
415 | Classroom |  | 0 | Yes | 672 | 15 | 15 | House Fan | 5376 | unk | unk | 20 | 3
416 | Classroom |  | 0 | Yes | 392 | 8 | 8 | House Fan | 3136 | unk | unk | 20 | 3
- | Cafeteria |  | 0 | Yes | 5150 | 117 | 117 | House Fan | 41200 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-30 | [8 empty] | unk | unk | unk | unk
School: | Trinidad Center | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
- | Adult Restroom | 13 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Assistant Director's Office | 16 | 1 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Boy's Restroom | 16 | 1 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Computer Room | 31 | 2 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Corridor |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Front Entrance | 34 | 2 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Girl's Restroom | 18 | 1 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Gym |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Hallway |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Head Receptionist's Office | 21 | 1 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Kitchen | 50 | 3 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Library |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Main Corridor (Hallway) | 0 | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Maintenance Office | 22 | 1 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Rear Entrance | 19 | 1 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
1 | Classroom | 101 | 6 | Yes | 610 | 13 | 13 | Air Handling Unit | 4880 | 1.2418 | 1 | 21.2418 | 3
2 | Classroom | 95 | 6 | Yes | 610 | 13 | 13 | Air Handling Unit | 4880 | 1.168 | 1 | 21.168 | 3
3 | Classroom | 100 | 6 | Yes | 575 | 13 | 13 | Air Handling Unit | 4600 | 1.3043 | 1 | 21.3043 | 3
4 | Classroom | 112 | 7 | Yes | 575 | 13 | 13 | Air Handling Unit | 4600 | 1.4609 | 1 | 21.4609 | 3
5 | Classroom | 132 | 8 |  | 590 | 13 | 8 | Air Handling Unit | 4720 | 1.678 | 1 | 1.678 | 1
6 | Classroom |  | 0 | Yes | 629 | 14 | 14 | Air Handling Unit | 5032 | unk | unk | 20 | 3
7 | Storage |  | 0 | Yes | 609 | 13 | 13 | Air Handling Unit | 4872 | unk | unk | 20 | 3
8 | Storage |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
9 | Storage |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
10 | Roof Access |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Stairway |  | 0 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-18 | [8 empty] | unk | unk | unk | unk
School: | The U School at Ferguson | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
B10 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0 | 0 | 0
B11 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0 | 0 | 0
B12 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0 | 0 | 0
110 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0 | 0 | 0
111 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0 | 0 | 0
112 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0 | 0 | 0
113 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0 | 0 | 0
114 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0 | 0 | 0
115 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0 | 0 | 0
210 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0 | 0 | 0
211 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0 | 0 | 0
212 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0 | 0 | 0
213 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0 | 0 | 0
214 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0 | 0 | 0
215 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0 | 0 | 0
310 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0 | 0 | 0
311 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0 | 0 | 0
312 | Classroom | 0 | 0 |  | 886 | 20 | 0 | Unit Ventilator | 7088 | 0 | 0 | 0 | 0
313 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0 | 0 | 0
314 | Classroom | 0 | 0 |  | 442 | 10 | 0 | Unit Ventilator | 3536 | 0 | 0 | 0 | 0
315 | Classroom | 0 | 0 |  | 884 | 20 | 0 | Unit Ventilator | 7072 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-06 | [8 empty] | unk | unk | unk | unk
School: | Vare-Washington Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | EMCOR Retest | Devine Retest | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | classroom | 478 | 31 |  | 1040 | 23 | 23 | Unit Ventilator | 8320 | 3.4471 | 1 | 3.4471 | 1
102 | classroom | 251 | 16 | Yes | 936 | 21 | 21 | Unit Ventilator | 7488 | 2.0112 | 1 | 22.0112 | 3
103 | classroom | 267 | 17 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.5673 | 1 | 2.5673 | 1
104 | classroom | 331 | 22 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 3.1827 | 1 | 3.1827 | 1
105 | classroom | 297 | 19 |  | 936 | 21 | 19 | Unit Ventilator | 7488 | 2.3798 | 1 | 2.3798 | 1
106 | classroom | 390 | 26 |  | 1040 | 23 | 23 | Unit Ventilator | 8320 | 2.8125 | 1 | 2.8125 | 1
107 | classroom | 210 | 14 | Yes | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.0192 | 1 | 22.0192 | 3
108 | classroom | 319 | 21 |  | 767 | 17 | 17 | Unit Ventilator | 6136 | 3.1193 | 1 | 3.1193 | 1
109 | classroom | 313 | 20 |  | 767 | 17 | 17 | Unit Ventilator | 6136 | 3.0606 | 1 | 3.0606 | 1
110 | classroom | 594 | 39 |  | 1482 | 33 | 33 | Unit Ventilator | 11856 | 3.0061 | 1 | 3.0061 | 1
201 | Counselor | 380 | 25 |  | 684 | 15 | 15 | Unit Ventilator | 5472 | 4.1667 | 2 | 4.1667 | 2
202 | classroom | 326 | 21 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.9387 | 1 | 2.9387 | 1
203 | 4-6 Autistic Supp. | 316 | 21 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.8486 | 1 | 2.8486 | 1
204 | classroom | 310 | 20 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.7945 | 1 | 2.7945 | 1
205 | K-2 Autistic Supp. | 210 | 14 | Yes | 832 | 18 | 18 | Unit Ventilator | 6656 | 1.893 | 1 | 21.893 | 3
206 | classroom | 417 | 27 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 3.759 | 1 | 3.759 | 1
207 | classroom | 227 | 15 |  | 832 | 18 | 15 | Unit Ventilator | 6656 | 2.0463 | 1 | 2.0463 | 1
208A | 3-4 Autistic Supp. | 293 | 19 |  | 832 | 18 | 18 | Unit Ventilator | 6656 | 2.6412 | 1 | 2.6412 | 1
208B | K-2 Emotional Support | 297 | 19 |  | 725 | 16 | 16 | Unit Ventilator | 5800 | 3.0724 | 1 | 3.0724 | 1
210 | ESOL | 234 | 15 |  | 575 | 13 | 13 | Unit Ventilator | 4600 | 3.0522 | 1 | 3.0522 | 1
211 | ESOL/SBTL | 251 | 16 |  | 628 | 14 | 14 | Unit Ventilator | 5024 | 2.9976 | 1 | 2.9976 | 1
213 | classroom | 405 | 27 |  | 1092 | 24 | 24 | Unit Ventilator | 8736 | 2.7816 | 1 | 2.7816 | 1
214 | classroom | 322 | 21 |  | 468 | 10 | 10 | Unit Ventilator | 3744 | 5.1603 | 2 | 5.1603 | 2
301 | classroom | 258 | 17 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.4808 | 1 | 2.4808 | 1
302 | classroom | 291 | 19 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.7981 | 1 | 2.7981 | 1
303 | classroom | 217 | 14 | Yes | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.0865 | 1 | 22.0865 | 3
304 | classroom | 234 | 15 |  | 780 | 17 | 15 | Unit Ventilator | 6240 | 2.25 | 1 | 2.25 | 1
305 | classroom | 287 | 19 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.7596 | 1 | 2.7596 | 1
306 | classroom | 323 | 21 |  | 690 | 15 | 15 | Unit Ventilator | 5520 | 3.5109 | 1 | 3.5109 | 1
307 | classroom | 217 | 14 | Yes | 780 | 17 | 17 | Unit Ventilator | 6240 | 2.0865 | 1 | 22.0865 | 3
308 | classroom | 269 | 17 |  | 988 | 22 | 17 | Unit Ventilator | 7904 | 2.042 | 1 | 2.042 | 1
309 | Psychologist / Climate Liaison | 185 | 12 |  | 598 | 13 | 12 | Unit Ventilator | 4784 | 2.3202 | 1 | 2.3202 | 1
310 | Math Interventionist | 211 | 14 |  | 624 | 14 | 14 | Unit Ventilator | 4992 | 2.5361 | 1 | 2.5361 | 1
311 | classroom | 189 | 12 | Yes | 624 | 14 | 14 | Unit Ventilator | 4992 | 2.2716 | 1 | 22.2716 | 3
312A | classroom | 295 | 19 |  | 1014 | 23 | 19 | Unit Ventilator | 8112 | 2.182 | 1 | 2.182 | 1
313 | classroom | 166 | 11 |  | 494 | 11 | 11 | Unit Ventilator | 3952 | 2.5202 | 1 | 2.5202 | 1
- | Gym | 305 | 20 |  | 4352 | 98 | 20 | Unit Ventilator | 34816 | 0.52562 | 0 | 0.52562 | 0
- | Library | 208 | 13 |  | 578 | 13 | 13 | Unit Ventilator | 4624 | 2.699 | 1 | 2.699 | 1
- | Lunch Room | 146 | 9 | Yes | 1292 | 29 | 29 | Unit Ventilator | 10336 | 0.84752 | 0 | 20.8475 | 3
- | Music | 748 | 49 |  | 1098 | 24 | 24 | Unit Ventilator | 8784 | 5.1093 | 2 | 5.1093 | 2
- | Main Office |  | 0 | Yes | 396 | 9 | 9 | Active Pure Unit | 3168 | unk | unk | 20 | 3
- | Princpal's Office |  | 0 | Yes | 350 | 7 | 7 | Active Pure Unit | 2800 | unk | unk | 20 | 3
- | Nurse's Office |  | 0 | Yes | 264 | 6 | 6 | Active Pure Unit | 2112 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-12 | [8 empty] | unk | unk | unk | unk
School: | EH Vare | [8 empty] | unk | unk | unk | unk
Vendor: | [9 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
109 | - |  | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
110 | - |  | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-21 | [8 empty] | unk | unk | unk | unk
School: | General Louis Wagner Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | Exhaust Report | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101A | classroom | 312 | 20 |  | 552 | 12 | 12 | Air Handling Unit | 4416 | 4.2391 | 2 | 4.2391 | 2
101B | classroom | 376 | 25 |  | 506 | 11 | 11 | Air Handling Unit | 4048 | 5.5731 | 2 | 5.5731 | 2
102 | classroom | 644 | 42 |  | 888 | 20 | 20 | Air Handling Unit | 7104 | 5.4392 | 2 | 5.4392 | 2
103A | classroom | 1312 | 87 |  | 1344 | 30 | 30 | Air Handling Unit | 10752 | 7.3214 | 2 | 7.3214 | 2
105 | classroom | 527 | 35 |  | 878 | 19 | 19 | Air Handling Unit | 7024 | 4.5017 | 2 | 4.5017 | 2
106 | classroom | 713 | 47 |  | 883 | 20 | 20 | Air Handling Unit | 7064 | 6.0561 | 2 | 6.0561 | 2
107 | classroom | 635 | 42 |  | 705 | 16 | 16 | Air Handling Unit | 5640 | 6.7553 | 2 | 6.7553 | 2
108 | classroom | 586 | 39 |  | 916 | 20 | 20 | Air Handling Unit | 7328 | 4.798 | 2 | 4.798 | 2
111 | classroom | 536 | 35 |  | 360 | 8 | 8 | Air Handling Unit | 2880 | 11.1667 | 3 | 11.1667 | 3
112 | classroom | 585 | 39 |  | 720 | 16 | 16 | Air Handling Unit | 5760 | 6.0938 | 2 | 6.0938 | 2
201 | classroom | 973 | 64 |  | 711 | 16 | 16 | Air Handling Unit | 5688 | 10.2637 | 3 | 10.2637 | 3
202 | classroom | 907 | 60 |  | 677 | 15 | 15 | Air Handling Unit | 5416 | 10.048 | 3 | 10.048 | 3
203 | classroom | 306 | 20 |  | 697 | 15 | 15 | Air Handling Unit | 5576 | 3.2927 | 1 | 3.2927 | 1
204 | classroom | 600 | 40 |  | 657 | 14 | 14 | Air Handling Unit | 5256 | 6.8493 | 2 | 6.8493 | 2
205A | Counselor Office | 597 | 39 |  | 306 | 6 | 6 | Air Handling Unit | 2448 | 14.6324 | 3 | 14.6324 | 3
205B | Counselor Office | 690 | 46 |  | 306 | 6 | 6 | Air Handling Unit | 2448 | 16.9118 | 3 | 16.9118 | 3
209A | classroom | 496 | 33 |  | 2064 | 46 | 33 | Air Handling Unit | 16512 | 1.8023 | 1 | 1.8023 | 1
209B | classroom | 763 | 50 |  | 336 | 7 | 7 | Air Handling Unit | 2688 | 17.0312 | 3 | 17.0312 | 3
209C | classroom | 995 | 66 |  | 336 | 7 | 7 | Air Handling Unit | 2688 | 22.2098 | 3 | 22.2098 | 3
212 | classroom | 1030 | 68 |  | 859 | 19 | 19 | Air Handling Unit | 6872 | 8.993 | 2 | 8.993 | 2
213 | classroom | 870 | 58 |  | 656 | 14 | 14 | Air Handling Unit | 5248 | 9.9466 | 2 | 9.9466 | 2
214 | classroom | 446 | 29 |  | 714 | 16 | 16 | Air Handling Unit | 5712 | 4.6849 | 2 | 4.6849 | 2
215 | classroom | 240 | 16 |  | 659 | 14 | 14 | Air Handling Unit | 5272 | 2.7314 | 1 | 2.7314 | 1
216 | classroom | 2170 | 144 |  | 777 | 17 | 17 | Air Handling Unit | 6216 | 20.9459 | 3 | 20.9459 | 3
217 | classroom | 1626 | 108 |  | 743 | 16 | 16 | Air Handling Unit | 5944 | 16.4132 | 3 | 16.4132 | 3
218 | classroom | 197 | 13 |  | 645 | 14 | 13 | Air Handling Unit | 5160 | 2.2907 | 1 | 2.2907 | 1
219 | classroom | 1463 | 97 |  | 643 | 14 | 14 | Air Handling Unit | 5144 | 17.0645 | 3 | 17.0645 | 3
220 | classroom | 731 | 48 |  | 563 | 12 | 12 | Air Handling Unit | 4504 | 9.738 | 2 | 9.738 | 2
221 | classroom | 1653 | 110 |  | 779 | 17 | 17 | Air Handling Unit | 6232 | 15.9146 | 3 | 15.9146 | 3
222 | classroom | 667 | 44 |  | 670 | 15 | 15 | Air Handling Unit | 5360 | 7.4664 | 2 | 7.4664 | 2
225 | Dean | 272 | 18 |  | 348 | 7 | 7 | Air Handling Unit | 2784 | 5.8621 | 2 | 5.8621 | 2
226 | classroom | 671 | 44 |  | 654 | 14 | 14 | Air Handling Unit | 5232 | 7.695 | 2 | 7.695 | 2
301 | classroom | 1282 | 85 |  | 714 | 16 | 16 | Air Handling Unit | 5712 | 13.4664 | 3 | 13.4664 | 3
302 | classroom | 2224 | 148 |  | 670 | 15 | 15 | Air Handling Unit | 5360 | 24.8955 | 4 | 24.8955 | 4
303 | classroom | 2929 | 195 |  | 671 | 15 | 15 | Air Handling Unit | 5368 | 32.7385 | 4 | 32.7385 | 4
304A | classroom | 1335 | 89 |  | 984 | 22 | 22 | Air Handling Unit | 7872 | 10.1753 | 3 | 10.1753 | 3
305 | classroom | 3981 | 265 |  | 956 | 21 | 21 | Air Handling Unit | 7648 | 31.2317 | 4 | 31.2317 | 4
306 | classroom | 3461 | 230 |  | 783 | 17 | 17 | Air Handling Unit | 6264 | 33.1513 | 4 | 33.1513 | 4
307 | classroom | 996 | 66 |  | 912 | 20 | 20 | Air Handling Unit | 7296 | 8.1908 | 2 | 8.1908 | 2
308 | classroom | 1202 | 80 |  | 928 | 21 | 21 | Air Handling Unit | 7424 | 9.7144 | 2 | 9.7144 | 2
309 | classroom | 2171 | 144 |  | 847 | 19 | 19 | Air Handling Unit | 6776 | 19.2237 | 3 | 19.2237 | 3
310 | classroom | 2047 | 136 |  | 881 | 20 | 20 | Air Handling Unit | 7048 | 17.4262 | 3 | 17.4262 | 3
311A | classroom | 990 | 66 |  | 929 | 21 | 21 | Air Handling Unit | 7432 | 7.9925 | 2 | 7.9925 | 2
312 | classroom | 211 | 14 |  | 716 | 16 | 14 | Air Handling Unit | 5728 | 2.2102 | 1 | 2.2102 | 1
313 | classroom | 868 | 57 |  | 672 | 15 | 15 | Air Handling Unit | 5376 | 9.6875 | 2 | 9.6875 | 2
314 | classroom | 350 | 23 |  | 719 | 16 | 16 | Air Handling Unit | 5752 | 3.6509 | 1 | 3.6509 | 1
315 | classroom | 83 | 5 |  | 662 | 15 | 5 | Air Handling Unit | 5296 | 0.94033 | 0 | 0.94033 | 0
316 | classroom | 1078 | 71 |  | 778 | 17 | 17 | Air Handling Unit | 6224 | 10.392 | 3 | 10.392 | 3
317 | classroom | 1382 | 92 |  | 604 | 13 | 13 | Air Handling Unit | 4832 | 17.1606 | 3 | 17.1606 | 3
318 | classroom | 1811 | 120 |  | 610 | 13 | 13 | Air Handling Unit | 4880 | 22.2664 | 3 | 22.2664 | 3
319 | classroom | 3185 | 212 |  | 644 | 14 | 14 | Air Handling Unit | 5152 | 37.0924 | 4 | 37.0924 | 4
320 | classroom | 4504 | 300 |  | 738 | 16 | 16 | Air Handling Unit | 5904 | 45.7724 | 4 | 45.7724 | 4
321 | classroom | 3538 | 235 |  | 786 | 17 | 17 | Air Handling Unit | 6288 | 33.7595 | 4 | 33.7595 | 4
322 | classroom | 82 | 5 |  | 660 | 15 | 5 | Air Handling Unit | 5280 | 0.93182 | 0 | 0.93182 | 0
323 | classroom | 1074 | 71 |  | 324 | 7 | 7 | Air Handling Unit | 2592 | 24.8611 | 4 | 24.8611 | 4
324 | classroom | 909 | 60 |  | 659 | 14 | 14 | Air Handling Unit | 5272 | 10.3452 | 3 | 10.3452 | 3
325 | classroom | 1021 | 68 |  | 346 | 7 | 7 | Air Handling Unit | 2768 | 22.1315 | 3 | 22.1315 | 3
326 | classroom | 481 | 32 |  | 659 | 14 | 14 | Air Handling Unit | 5272 | 5.4742 | 2 | 5.4742 | 2
326 | Counselor Office | 513 | 34 |  | 306 | 6 | 6 | Air Handling Unit | 2448 | 12.5735 | 3 | 12.5735 | 3
- | Auditorium | 0 | 0 |  | 5460 | 124 | 0 | Air Handling Unit | 43680 | 0 | 0 | 0 | 0
- | Boy's Gym | 14624 | 974 |  | 4350 | 98 | 98 | Air Handling Unit | 34800 | 25.2138 | 4 | 25.2138 | 4
- | Cafeteria | 498 | 33 |  | 408 | 9 | 9 | Air Handling Unit | 3264 | 9.1544 | 2 | 9.1544 | 2
- | Computer Lab | 446 | 29 |  | 657 | 14 | 14 | Air Handling Unit | 5256 | 5.0913 | 2 | 5.0913 | 2
- | Conf. Room | 884 | 58 |  | 336 | 7 | 7 | Air Handling Unit | 2688 | 19.7321 | 3 | 19.7321 | 3
- | Kitchen | 5749 | 383 |  | 816 | 18 | 18 | Air Handling Unit | 6528 | 52.8401 | 5 | 52.8401 | 5
- | Kitchen- Freezer/Cooler Condenser Fan | 0 | 0 |  | 144 | 3 | 0 | Air Handling Unit | 1152 | 0 | 0 | 0 | 0
- | Lunch Room | 175 | 11 |  | 2040 | 46 | 11 | Air Handling Unit | 16320 | 0.64338 | 0 | 0.64338 | 0
- | Main Office | 632 | 42 |  | 531 | 12 | 12 | Air Handling Unit | 4248 | 8.9266 | 2 | 8.9266 | 2
Principal | Office |  | 0 | Yes | 259 | 5 | 5 |  | 2072 | unk | unk | 20 | 3
Nurse | Office |  | 0 | Yes | 249 | 5 | 5 |  | 1992 | unk | unk | 20 | 3
- | MEDIA LAB A | 304 | 20 |  | 60 | 1 | 1 | Air Handling Unit | 480 | 38 | 4 | 38 | 4
- | MEDIA LAB B | 564 | 37 |  | 60 | 1 | 1 | Air Handling Unit | 480 | 70.5 | 5 | 70.5 | 5
- | Staff Lounge | 421 | 28 |  | 657 | 14 | 14 | Air Handling Unit | 5256 | 4.8059 | 2 | 4.8059 | 2
- | VP Office | 1325 | 88 |  | 232 | 5 | 5 | Air Handling Unit | 1856 | 42.8341 | 4 | 42.8341 | 4
- | Gym- Weight Room A | 1230 | 82 |  | 181 | 4 | 4 | Air Handling Unit | 1448 | 50.9669 | 5 | 50.9669 | 5
- | Gym- Weight Room B | 1164 | 77 |  | 181 | 4 | 4 | Air Handling Unit | 1448 | 48.232 | 4 | 48.232 | 4
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-26 | [8 empty] | unk | unk | unk | unk
School: | Laura W. Waring Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | EMCOR Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 188 | 12 | Yes | 430 | 9 | 9 | Nesbitt Unit Ventilator | 3440 | 3.2791 | 1 | 23.2791 | 3
102 | Classroom | 118 | 7 | Yes | 872 | 19 | 19 | Nesbitt Unit Ventilator | 6976 | 1.0149 | 1 | 21.0149 | 3
103 | Classroom | 150 | 10 | Yes | 872 | 19 | 19 | Nesbitt Unit Ventilator | 6976 | 1.2901 | 1 | 21.2901 | 3
105 | Classroom | 180 | 12 | Yes | 789 | 17 | 17 | Nesbitt Unit Ventilator | 6312 | 1.711 | 1 | 21.711 | 3
106 | Classroom | 171 | 11 | Yes | 850 | 19 | 19 | Nesbitt Unit Ventilator | 6800 | 1.5088 | 1 | 21.5088 | 3
107 | Classroom | 226 | 15 |  | 850 | 19 | 15 | Nesbitt Unit Ventilator | 6800 | 1.9941 | 1 | 1.9941 | 1
108 | Classroom | 165 | 11 | Yes | 750 | 17 | 17 | Nesbitt Unit Ventilator | 6000 | 1.65 | 1 | 21.65 | 3
200 | Counselor's Room | 0 | 0 |  | 300 | 6 | 0 | Nesbitt Unit Ventilator | 2400 | 0 | 0 | 0 | 0
201 | Computer Room | 0 | 0 | Yes | 925 | 21 | 21 | Nesbitt Unit Ventilator | 7400 | 0 | 0 | 20 | 3
202 | Classroom | 87 | 5 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator | 7104 | 0.7348 | 0 | 20.7348 | 3
203 | Classroom | 274 | 18 |  | 888 | 20 | 18 | Nesbitt Unit Ventilator | 7104 | 2.3142 | 1 | 2.3142 | 1
204 | Classroom | 276 | 18 |  | 888 | 20 | 18 | Nesbitt Unit Ventilator | 7104 | 2.3311 | 1 | 2.3311 | 1
205 | Classroom | 311 | 20 |  | 850 | 19 | 19 | Nesbitt Unit Ventilator | 6800 | 2.7441 | 1 | 2.7441 | 1
206 | Classroom | 193 | 12 | Yes | 850 | 19 | 19 | Nesbitt Unit Ventilator | 6800 | 1.7029 | 1 | 21.7029 | 3
207 | Classroom | 152 | 10 | Yes | 850 | 19 | 19 | Nesbitt Unit Ventilator | 6800 | 1.3412 | 1 | 21.3412 | 3
208 | Classroom | 209 | 13 | Yes | 750 | 17 | 17 | Nesbitt Unit Ventilator | 6000 | 2.09 | 1 | 22.09 | 3
300 | Classroom | 0 | 0 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator | 7104 | 0 | 0 | 20 | 3
301 | Classroom | 212 | 14 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator | 7104 | 1.7905 | 1 | 21.7905 | 3
302 | Classroom | 105 | 7 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator | 7104 | 0.88682 | 0 | 20.8868 | 3
303 | Classroom | 133 | 8 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator | 7104 | 1.1233 | 1 | 21.1233 | 3
304 | Classroom | 255 | 17 |  | 888 | 20 | 17 | Nesbitt Unit Ventilator | 7104 | 2.1537 | 1 | 2.1537 | 1
305 | Classroom | 93 | 6 | Yes | 888 | 20 | 20 | Nesbitt Unit Ventilator | 7104 | 0.78547 | 0 | 20.7855 | 3
306/307 | Classroom | 266 | 17 |  | 1850 | 42 | 17 | Nesbitt Unit Ventilator | 14800 | 1.0784 | 1 | 1.0784 | 1
308 | Classroom | 220 | 14 | Yes | 896 | 20 | 20 | Nesbitt Unit Ventilator | 7168 | 1.8415 | 1 | 21.8415 | 3
311 | Dining Room | 120 | 8 |  | 242 | 5 | 5 | Nesbitt Unit Ventilator | 1936 | 3.719 | 1 | 3.719 | 1
- | Cafeteria | 0 | 0 |  | 3477 | 79 | 0 | Nesbitt Unit Ventilator | 27816 | 0 | 0 | 0 | 0
- | Vestibule left of office | 0 | 0 |  | 96 | 2 | 0 | Nesbitt Unit Ventilator | 768 | 0 | 0 | 0 | 0
- | Nurse |  | 0 |  | 231 | 5 | 0 | Nesbitt Unit Ventilator | 1848 | unk | unk | unk | unk
- | Faculty Lounge | 57 | 3 |  | 228 | 5 | 3 | Nesbitt Unit Ventilator | 1824 | 1.875 | 1 | 1.875 | 1
- | Health Office | 0 | 0 | Yes | 231 | 5 | 5 | Nesbitt Unit Ventilator | 1848 | 0 | 0 | 20 | 3
- | Multi-Purpose Room | 457 | 30 |  | 1820 | 41 | 30 | Nesbitt Unit Ventilator | 14560 | 1.8832 | 1 | 1.8832 | 1
- | Main Office | 0 | 0 | Yes | 378 | 8 | 8 | Nesbitt Unit Ventilator | 3024 | 0 | 0 | 20 | 3
- | Principal's Office | 69 | 4 | Yes | 381 | 8 | 8 | Nesbitt Unit Ventilator | 3048 | 1.3583 | 1 | 21.3583 | 3
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | George Washington High School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | Meehan (Auditorium) | [7 empty] | unk | unk | unk | unk
School: | George Washington High School Annex | [8 empty] | unk | unk | unk | unk
Vendor: | [9 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Main Building | [9 empty] | unk | unk | unk | unk
1 | - | 370 | 24 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.6133 | 1 | 3.6133 | 1
2 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
3 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0 | 0 | 0
4 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
5 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0 | 0 | 0
6 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
7 | - | 348 | 23 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.3984 | 1 | 3.3984 | 1
8 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
9 | - | 412 | 27 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.0234 | 2 | 4.0234 | 2
10 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
11 | - | 451 | 30 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.4043 | 2 | 4.4043 | 2
12 | - | 0 | 0 |  | 775 | 17 | 0 | Carrier / Perimeter Heater | 6200 | 0 | 0 | 0 | 0
13 | - | 414 | 27 |  | 1209 | 27 | 27 | Carrier / Perimeter Heater | 9672 | 2.5682 | 1 | 2.5682 | 1
14 | - | 374 | 24 |  | 1209 | 27 | 24 | Carrier / Perimeter Heater | 9672 | 2.3201 | 1 | 2.3201 | 1
15 | - | 403 | 26 |  | 1209 | 27 | 26 | Carrier / Perimeter Heater | 9672 | 2.5 | 1 | 2.5 | 1
16 | - | 849 | 56 |  | 1911 | 43 | 43 | Carrier / Perimeter Heater | 15288 | 3.332 | 1 | 3.332 | 1
17 | - | 0 | 0 |  | 1240 | 28 | 0 | Carrier / Perimeter Heater | 9920 | 0 | 0 | 0 | 0
18 | - | 763 | 50 |  | 1911 | 43 | 43 | Carrier / Perimeter Heater | 15288 | 2.9945 | 1 | 2.9945 | 1
19 | - | 0 | 0 |  | 1302 | 29 | 0 | Carrier / Perimeter Heater | 10416 | 0 | 0 | 0 | 0
20 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
21 | - | 451 | 30 |  | 1240 | 28 | 28 | Carrier / Perimeter Heater | 9920 | 2.7278 | 1 | 2.7278 | 1
22 | - | 421 | 28 |  | 1209 | 27 | 27 | Carrier / Perimeter Heater | 9672 | 2.6117 | 1 | 2.6117 | 1
23 | - | 0 | 0 |  | 1240 | 28 | 0 | Carrier / Perimeter Heater | 9920 | 0 | 0 | 0 | 0
24 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
25 | - | 419 | 27 |  | 912 | 20 | 20 | Carrier / Perimeter Heater | 7296 | 3.4457 | 1 | 3.4457 | 1
26 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
27 | - | 0 | 0 |  | 912 | 20 | 0 | Carrier / Perimeter Heater | 7296 | 0 | 0 | 0 | 0
28 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
29 | - | 355 | 23 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.4668 | 1 | 3.4668 | 1
30 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
31 | - | 413 | 27 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.0332 | 2 | 4.0332 | 2
32 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
33 | - | 338 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.3008 | 1 | 3.3008 | 1
34 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
35 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0 | 0 | 0
36 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
37 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0 | 0 | 0
38 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
39 | - | 403 | 26 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.9355 | 1 | 3.9355 | 1
100 | - | 334 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.2617 | 1 | 3.2617 | 1
102 | - | 335 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.2715 | 1 | 3.2715 | 1
104 | Health Room |  | 0 |  | 1488 | 33 | 0 |  | 11904 | unk | unk | unk | unk
107 | - | 495 | 33 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
108 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
109 | - | 357 | 23 |  | 744 | 16 | 16 | Carrier / Perimeter Heater | 5952 | 3.5988 | 1 | 3.5988 | 1
110 | - | 413 | 27 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
111 | - | 370 | 24 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.6133 | 1 | 3.6133 | 1
112 | - | 398 | 26 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.8867 | 1 | 3.8867 | 1
113 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
114 | - | 427 | 28 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.1699 | 2 | 4.1699 | 2
115 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
116 | - | 368 | 24 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.5938 | 1 | 3.5938 | 1
117 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
118 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0 | 0 | 0
119 | - | 368 | 24 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
120 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0 | 0 | 0
121 | - | 381 | 25 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.7207 | 1 | 3.7207 | 1
122 | - | 408 | 27 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 3.8636 | 1 | 3.8636 | 1
123 | - | 465 | 31 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.541 | 2 | 4.541 | 2
124 | - | 436 | 29 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.2578 | 2 | 4.2578 | 2
125 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
126 | - | 336 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.2812 | 1 | 3.2812 | 1
127 | - | 416 | 27 |  | 1102 | 25 | 25 | Carrier / Perimeter Heater | 8816 | 2.8312 | 1 | 2.8312 | 1
128 | - | 0 | 0 |  | 1280 | 29 | 0 | Carrier / Perimeter Heater | 10240 | 0 | 0 | 0 | 0
129 | - | 366 | 24 |  | 1073 | 24 | 24 | Carrier / Perimeter Heater | 8584 | 2.5582 | 1 | 2.5582 | 1
130 | - | 0 | 0 |  | 1280 | 29 | 0 | Carrier / Perimeter Heater | 10240 | 0 | 0 | 0 | 0
131 | - | 388 | 25 |  | 1160 | 26 | 25 | Carrier / Perimeter Heater | 9280 | 2.5086 | 1 | 2.5086 | 1
132 | - | 610 | 40 |  | 1092 | 24 | 24 | Carrier / Perimeter Heater | 8736 | 4.1896 | 2 | 4.1896 | 2
133 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
134 | - | 732 | 48 |  | 1092 | 24 | 24 | Carrier / Perimeter Heater | 8736 | 5.0275 | 2 | 5.0275 | 2
135 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
136 | - | 325 | 21 |  | 1092 | 24 | 21 | Carrier / Perimeter Heater | 8736 | 2.2321 | 1 | 2.2321 | 1
137 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
138 | - | 408 | 27 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
139 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
140 | - | 424 | 28 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
141 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
142 | - | 865 | 57 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
143 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
144 | - | 308 | 20 |  | 832 | 18 | 18 | Carrier / Perimeter Heater | 6656 | 2.7764 | 1 | 2.7764 | 1
145 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
146 | - | 0 | 0 |  | 775 | 17 | 0 | Carrier / Perimeter Heater | 6200 | 0 | 0 | 0 | 0
147 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
148 | - | 242 | 16 |  | 775 | 17 | 16 | Carrier / Perimeter Heater | 6200 | 2.3419 | 1 | 2.3419 | 1
149 -155 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
156 | - | 926 | 61 |  | 814 | 18 | 18 | Carrier / Perimeter Heater | 6512 | 8.5319 | 2 | 8.5319 | 2
157 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
158 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
159 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
160 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
161 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
162 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
164 | - | 695 | 46 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
200 | - | 485 | 32 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.7363 | 2 | 4.7363 | 2
201 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
202 | - | 417 | 27 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.0723 | 2 | 4.0723 | 2
203 | - | 397 | 26 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.877 | 1 | 3.877 | 1
204 | - | 337 | 22 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 3.291 | 1 | 3.291 | 1
205 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0 | 0 | 0
206 | - | 424 | 28 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
207 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0 | 0 | 0
208 | - | 536 | 35 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.2344 | 2 | 5.2344 | 2
209 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
210 | - | 575 | 38 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.6152 | 2 | 5.6152 | 2
211 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
212 | - | 514 | 34 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.0195 | 2 | 5.0195 | 2
213 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
214 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0 | 0 | 0
215 | - | 547 | 36 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.3418 | 2 | 5.3418 | 2
216 | - | 519 | 34 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.0684 | 2 | 5.0684 | 2
217 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
218 | - | 521 | 34 |  | 1536 | 34 | 34 | Carrier / Perimeter Heater | 12288 | 2.5439 | 1 | 2.5439 | 1
219 | - | 0 | 0 |  | 1536 | 34 | 0 | Carrier / Perimeter Heater | 12288 | 0 | 0 | 0 | 0
220 | - | 0 | 0 |  | 1536 | 34 | 0 | Carrier / Perimeter Heater | 12288 | 0 | 0 | 0 | 0
221 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0 | 0 | 0
222 | - | 569 | 37 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.5566 | 2 | 5.5566 | 2
223 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
224 | - | 533 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.0473 | 2 | 5.0473 | 2
225 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
226 | - | 536 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.0758 | 2 | 5.0758 | 2
227 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
228 | - | 543 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.142 | 2 | 5.142 | 2
229 | - | 508 | 33 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 4.8106 | 2 | 4.8106 | 2
230 | - | 563 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.3314 | 2 | 5.3314 | 2
231 | - | 492 | 32 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 4.6591 | 2 | 4.6591 | 2
232 | - | 563 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.3314 | 2 | 5.3314 | 2
233 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
234 | - | 539 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.1042 | 2 | 5.1042 | 2
235 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
236 | - | 544 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.1515 | 2 | 5.1515 | 2
237 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
238 | - | 399 | 26 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 3.7784 | 1 | 3.7784 | 1
239 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
240 | - | 0 | 0 |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 6144 | 0 | 0 | 0 | 0
241 | - | 344 | 22 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 3.2576 | 1 | 3.2576 | 1
242 | - | 450 | 30 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 4.3945 | 2 | 4.3945 | 2
243 | - | 455 | 30 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 4.3087 | 2 | 4.3087 | 2
244 | - | 428 | 28 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 4.053 | 2 | 4.053 | 2
245 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
246 | - | 423 | 28 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 4.0057 | 2 | 4.0057 | 2
300 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
301 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
302 | - | 542 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.1326 | 2 | 5.1326 | 2
303 | - | 539 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.1042 | 2 | 5.1042 | 2
304 | - | 591 | 39 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.5966 | 2 | 5.5966 | 2
305 | - | 556 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.2652 | 2 | 5.2652 | 2
306 | - | 561 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.3125 | 2 | 5.3125 | 2
307 | - | 592 | 39 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.6061 | 2 | 5.6061 | 2
308 | - | 263 | 17 |  | 792 | 18 | 17 | Carrier / Perimeter Heater | 6336 | 2.4905 | 1 | 2.4905 | 1
309 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
310 | - | 602 | 40 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.7008 | 2 | 5.7008 | 2
311 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
312 | - | 599 | 39 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.6723 | 2 | 5.6723 | 2
313 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
314 | - | 539 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.1042 | 2 | 5.1042 | 2
315 | - | 530 | 35 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.0189 | 2 | 5.0189 | 2
316 | - | 557 | 37 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.2746 | 2 | 5.2746 | 2
317 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
318 | - | 580 | 38 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.6641 | 2 | 5.6641 | 2
319 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
320 | - | 610 | 40 |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 6144 | 5.957 | 2 | 5.957 | 2
321 | - | 551 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.2178 | 2 | 5.2178 | 2
322 | - | 554 | 36 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.2462 | 2 | 5.2462 | 2
323 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
324 | - | 591 | 39 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 4.6172 | 2 | 4.6172 | 2
325 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
326 | - | 533 | 35 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 4.1641 | 2 | 4.1641 | 2
327 | - | 554 | 36 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 4.3281 | 2 | 4.3281 | 2
328 | - | 561 | 37 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 4.3828 | 2 | 4.3828 | 2
329 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
330 | - | 572 | 38 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 4.4688 | 2 | 4.4688 | 2
331 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
332 | - | 576 | 38 |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 6336 | 5.4545 | 2 | 5.4545 | 2
333 | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
334 | - | 506 | 33 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 3.9531 | 1 | 3.9531 | 1
335 | - | 605 | 40 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
336 | - | 559 | 37 |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 7680 | 4.3672 | 2 | 4.3672 | 2
337 | - | 0 | 0 |  | 792 | 18 | 0 | Carrier / Perimeter Heater | 6336 | 0 | 0 | 0 | 0
338 | - | 0 | 0 |  | 792 | 18 | 0 | Carrier / Perimeter Heater | 6336 | 0 | 0 | 0 | 0
339 | - | 0 | 0 |  | 792 | 18 | 0 | Carrier / Perimeter Heater | 6336 | 0 | 0 | 0 | 0
Gymnasium | Gymnasium |  | 0 |  |  | 0 | 0 |  |  | unk | unk | unk | unk
Auditorium | Auditorium | 17891 | 1192 |  | 10800 | 245 | 245 | Air Handling Unit | 86400 | 12.4243 | 3 | 12.4243 | 3
- | Beacon Left | 311 | 20 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
- | Beacon Right | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
- | Cafeteria | 17015 | 1134 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
Center | - | 438 | 29 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
Dean's Office | - | 437 | 29 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
Library Left | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
Main Office | - | 394 | 26 |  | 2332 | 53 | 26 | Carrier / Perimeter Heater | 18656 | 1.2672 | 1 | 1.2672 | 1
Principle | - | 0 | 0 |  | 615 | 13 | 0 | Carrier / Perimeter Heater | 4920 | 0 | 0 | 0 | 0
Right | - | 0 | 0 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
- | Roster | 426 | 28 |  |  | 0 | 0 | Carrier / Perimeter Heater |  | unk | unk | unk | unk
- | Staff Cafeteria | 1328 | 88 |  |  | 0 | 0 | Make-up Air Unit |  | unk | unk | unk | unk
- | Student Cafeteria | 8507 | 567 |  | 12000 | 272 | 272 | Make-up Air Unit | 96000 | 5.3169 | 2 | 5.3169 | 2
Annex | [9 empty] | unk | unk | unk | unk
408 Annex | Classroom |  | 0 | Yes | 858 | 19 | 19 | Air Handling Unit | 6864 | unk | unk | 20 | 3
409 Annex | Classroom |  | 0 | Yes | 858 | 19 | 19 | Air Handling Unit | 6864 | unk | unk | 20 | 3
410 Annex | Classroom |  | 0 | Yes | 858 | 19 | 19 | Air Handling Unit | 6864 | unk | unk | 20 | 3
412 Annex | Classroom |  | 0 | Yes |  | 0 | 0 | Air Handling Unit |  | unk | unk | 20 | 3
Kitchen Annex | Kitchen |  | 0 | Yes |  | 0 | 0 | Air Handling Unit |  | unk | unk | 20 | 3
Recceration room | - |  | 0 |  | 3780 | 85 | 85 |  | 30240 | unk | unk | unk | unk
Health Suite/ 11 rms | - |  | 0 |  | 77 | 1 | 1 |  | 616 | unk | unk | unk | unk
Health Suite/ 2 rms | - |  | 0 |  | 80 | 1 | 1 |  | 640 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-14 | [8 empty] | unk | unk | unk | unk
School: | Grover Washington Jr. Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | CLASSROOM | 288 | 19 |  | 700 | 15 | 15 | Fan Coil Unit | 5600 | 3.0857 | 1 | 3.0857 | 1
101 | CLASSROOM | 207 | 13 | Yes | 700 | 15 | 15 | Fan Coil Unit | 5600 | 2.2179 | 1 | 22.2179 | 3
102 | CLASSROOM | 164 | 10 | Yes | 698 | 15 | 15 | Fan Coil Unit | 5584 | 1.7622 | 1 | 21.7622 | 3
102A | CLASSROOM | 185 | 12 |  | 160 | 3 | 3 | Fan Coil Unit | 1280 | 8.6719 | 2 | 8.6719 | 2
103 | CLASSROOM | 476 | 31 |  | 858 | 19 | 19 | Univent | 6864 | 4.1608 | 2 | 4.1608 | 2
104 | CLASSROOM | 595 | 39 |  | 783 | 17 | 17 | Univent | 6264 | 5.6992 | 2 | 5.6992 | 2
105 | CLASSROOM | 935 | 62 |  | 726 | 16 | 16 | Univent | 5808 | 9.6591 | 2 | 9.6591 | 2
106 | CLASSROOM | 421 | 28 |  | 726 | 16 | 16 | Univent | 5808 | 4.3492 | 2 | 4.3492 | 2
107 | CLASSROOM | 274 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.3951 | 1 | 2.3951 | 1
108 | CLASSROOM | 395 | 26 |  | 858 | 19 | 19 | Univent | 6864 | 3.4528 | 1 | 3.4528 | 1
109 | CLASSROOM | 573 | 38 |  | 858 | 19 | 19 | Univent | 6864 | 5.0087 | 2 | 5.0087 | 2
110 | CLASSROOM | 310 | 20 |  | 858 | 19 | 19 | Univent | 6864 | 2.7098 | 1 | 2.7098 | 1
112 | CLASSROOM | 377 | 25 |  | 858 | 19 | 19 | Univent | 6864 | 3.2955 | 1 | 3.2955 | 1
113 | CLASSROOM | 392 | 26 |  | 312 | 7 | 7 | Univent | 2496 | 9.4231 | 2 | 9.4231 | 2
114 | CLASSROOM | 361 | 24 |  | 858 | 19 | 19 | Univent | 6864 | 3.1556 | 1 | 3.1556 | 1
115 | CLASSROOM | 292 | 19 |  | 726 | 16 | 16 | Univent | 5808 | 3.0165 | 1 | 3.0165 | 1
116 | CLASSROOM | 749 | 49 |  | 726 | 16 | 16 | Univent | 5808 | 7.7376 | 2 | 7.7376 | 2
117 | CLASSROOM | 763 | 50 |  | 726 | 16 | 16 | Univent | 5808 | 7.8822 | 2 | 7.8822 | 2
118 | CLASSROOM | 757 | 50 |  | 726 | 16 | 16 | Univent | 5808 | 7.8202 | 2 | 7.8202 | 2
119 | CLASSROOM | 396 | 26 |  | 858 | 19 | 19 | Univent | 6864 | 3.4615 | 1 | 3.4615 | 1
120 | CLASSROOM | 304 | 20 |  | 858 | 19 | 19 | Univent | 6864 | 2.6573 | 1 | 2.6573 | 1
121 | CLASSROOM | 370 | 24 |  | 858 | 19 | 19 | Univent | 6864 | 3.2343 | 1 | 3.2343 | 1
122 | CLASSROOM | 314 | 20 |  | 858 | 19 | 19 | Univent | 6864 | 2.7448 | 1 | 2.7448 | 1
201 | 2ND FLOOR C WING OFFICE | 211 | 14 |  | 312 | 7 | 7 | Univent | 2496 | 5.0721 | 2 | 5.0721 | 2
202 | CLASSROOM | 601 | 40 |  | 858 | 19 | 19 | Univent | 6864 | 5.2535 | 2 | 5.2535 | 2
203 | CLASSROOM | 580 | 38 |  | 858 | 19 | 19 | Univent | 6864 | 5.0699 | 2 | 5.0699 | 2
204 | CLASSROOM | 304 | 20 |  | 858 | 19 | 19 | Univent | 6864 | 2.6573 | 1 | 2.6573 | 1
205 | CLASSROOM | 285 | 19 |  | 858 | 19 | 19 | Univent | 6864 | 2.4913 | 1 | 2.4913 | 1
206 | CLASSROOM | 406 | 27 |  | 783 | 17 | 17 | Univent | 6264 | 3.8889 | 1 | 3.8889 | 1
207 | CLASSROOM | 456 | 30 |  | 726 | 16 | 16 | Univent | 5808 | 4.7107 | 2 | 4.7107 | 2
208 | CLASSROOM | 561 | 37 |  | 1584 | 36 | 36 | Univent | 12672 | 2.6562 | 1 | 2.6562 | 1
209 | CLASSROOM | 320 | 21 |  | 858 | 19 | 19 | Univent | 6864 | 2.7972 | 1 | 2.7972 | 1
210 | CLASSROOM | 388 | 25 |  | 858 | 19 | 19 | Univent | 6864 | 3.3916 | 1 | 3.3916 | 1
211 | CLASSROOM | 348 | 23 |  | 858 | 19 | 19 | Univent | 6864 | 3.042 | 1 | 3.042 | 1
212 | CLASSROOM | 318 | 21 |  | 858 | 19 | 19 | Univent | 6864 | 2.7797 | 1 | 2.7797 | 1
213 | CLASSROOM | 307 | 20 |  | 1248 | 28 | 20 | Univent | 9984 | 1.845 | 1 | 1.845 | 1
214 | CLASSROOM | 286 | 19 | Yes | 1144 | 26 | 26 | Univent | 9152 | 1.875 | 1 | 21.875 | 3
215 | CLASSROOM | 693 | 46 |  | 1170 | 26 | 26 | Univent | 9360 | 4.4423 | 2 | 4.4423 | 2
216 | CLASSROOM | 370 | 24 |  | 783 | 17 | 17 | Univent | 6264 | 3.5441 | 1 | 3.5441 | 1
217 | CLASSROOM | 306 | 20 |  | 726 | 16 | 16 | Univent | 5808 | 3.1612 | 1 | 3.1612 | 1
218 | CLASSROOM | 314 | 20 |  | 783 | 17 | 17 | Univent | 6264 | 3.0077 | 1 | 3.0077 | 1
219 | CLASSROOM | 332 | 22 |  | 858 | 19 | 19 | Univent | 6864 | 2.9021 | 1 | 2.9021 | 1
220 | CLASSROOM | 407 | 27 |  | 858 | 19 | 19 | Univent | 6864 | 3.5577 | 1 | 3.5577 | 1
221 | 2ND FLOOR D WING OFFICE | 181 | 12 |  | 312 | 7 | 7 | Univent | 2496 | 4.351 | 2 | 4.351 | 2
301 | CLASSROOM | 112 | 7 | Yes | 858 | 19 | 19 | Fan Coil Unit | 6864 | 0.97902 | 0 | 20.979 | 3
302 | CLASSROOM | 339 | 22 |  | 858 | 19 | 19 | Univent | 6864 | 2.9633 | 1 | 2.9633 | 1
303 | CLASSROOM | 0 | 0 | Yes | 858 | 19 | 19 | Univent | 6864 | 0 | 0 | 20 | 3
304 | CLASSROOM | 231 | 15 |  | 858 | 19 | 15 | Univent | 6864 | 2.0192 | 1 | 2.0192 | 1
305 | CLASSROOM | 385 | 25 |  | 858 | 19 | 19 | Univent | 6864 | 3.3654 | 1 | 3.3654 | 1
306 | CLASSROOM | 353 | 23 |  | 783 | 17 | 17 | Univent | 6264 | 3.3812 | 1 | 3.3812 | 1
307 | CLASSROOM | 316 | 21 |  | 726 | 16 | 16 | Univent | 5808 | 3.2645 | 1 | 3.2645 | 1
308 | CLASSROOM | 306 | 20 |  | 1584 | 36 | 20 | Univent | 12672 | 1.4489 | 1 | 1.4489 | 1
309 | CLASSROOM | 486 | 32 |  | 858 | 19 | 19 | Univent | 6864 | 4.2483 | 2 | 4.2483 | 2
310 | CLASSROOM | 283 | 18 |  | 858 | 19 | 18 | Univent | 6864 | 2.4738 | 1 | 2.4738 | 1
311 | CLASSROOM | 265 | 17 |  | 858 | 19 | 17 | Univent | 6864 | 2.3164 | 1 | 2.3164 | 1
312 | CLASSROOM | 389 | 25 |  | 858 | 19 | 19 | Univent | 6864 | 3.4003 | 1 | 3.4003 | 1
313 | CLASSROOM | 355 | 23 |  | 858 | 19 | 19 | Univent | 6864 | 3.1031 | 1 | 3.1031 | 1
314 | CLASSROOM | 305 | 20 | Yes | 1144 | 26 | 26 | Univent | 9152 | 1.9996 | 1 | 21.9996 | 3
315 | CLASSROOM | 1003 | 66 |  | 1170 | 26 | 26 | Univent | 9360 | 6.4295 | 2 | 6.4295 | 2
316 | CLASSROOM | 363 | 24 |  | 783 | 17 | 17 | Univent | 6264 | 3.477 | 1 | 3.477 | 1
317 | CLASSROOM | 81 | 5 | Yes | 858 | 19 | 19 | Univent | 6864 | 0.70804 | 0 | 20.708 | 3
318 | CLASSROOM | 510 | 34 | Yes | 858 | 19 | 19 | Univent | 6864 | 4.458 | 2 | 24.458 | 4
319 | CLASSROOM | 463 | 30 |  | 858 | 19 | 19 | Univent | 6864 | 4.0472 | 2 | 4.0472 | 2
320 | CLASSROOM | 0 | 0 | Yes | 858 | 19 | 19 | Univent | 6864 | 0 | 0 | 20 | 3
- | GYMNASIUM | 900 | 60 |  | 6370 | 144 | 60 | Rooftop Unit | 50960 | 1.0597 | 1 | 1.0597 | 1
- | CAFETERIA | 3339 | 222 |  | 5160 | 117 | 117 | Rooftop Unit | 41280 | 4.8532 | 2 | 4.8532 | 2
- | AUDITORIUM | 2146 | 143 |  | 7008 | 159 | 143 | Rooftop Unit | 56064 | 2.2967 | 1 | 2.2967 | 1
- | KITCHEN HOOD | 8665 | 577 |  | 1584 | 36 | 36 | Rooftop Unit | 12672 | 41.0275 | 4 | 41.0275 | 4
- | 1ST FLOOR BACK CORR. | 255 | 17 |  | 800 | 18 | 17 | Fan Coil Unit | 6400 | 2.3906 | 1 | 2.3906 | 1
- | 1ST FLOOR CIRCLE HALL | 220 | 14 |  | 1246 | 28 | 14 | Fan Coil Unit | 9968 | 1.3242 | 1 | 1.3242 | 1
- | 1ST FLOOR CORR INFRONT OF CAFÉ | 209 | 13 |  | 1008 | 22 | 13 | Fan Coil Unit | 8064 | 1.5551 | 1 | 1.5551 | 1
- | 1ST FLOOR D WING OFFICE | 149 | 9 |  | 312 | 7 | 7 | Fan Coil Unit | 2496 | 3.5817 | 1 | 3.5817 | 1
- | 1ST FLOOR ENTRANCE CORR. | 360 | 24 |  | 1053 | 23 | 23 | Fan Coil Unit | 8424 | 2.5641 | 1 | 2.5641 | 1
- | 1ST FLOOR FRONT CORR. | 1074 | 71 |  | 1008 | 22 | 22 | Fan Coil Unit | 8064 | 7.9911 | 2 | 7.9911 | 2
- | 1ST FLOOR FRONT HALL | 562 | 37 |  | 1540 | 35 | 35 | Fan Coil Unit | 12320 | 2.737 | 1 | 2.737 | 1
- | 1ST FLOOR OFFICES | 493 | 32 |  | 1888 | 42 | 32 | Fan Coil Unit | 15104 | 1.9584 | 1 | 1.9584 | 1
- | 2ND / 1ST FLOOR D WING CORR | 380 | 25 |  | 1616 | 36 | 25 | Fan Coil Unit | 12928 | 1.7636 | 1 | 1.7636 | 1
- | 2ND FLOOR C WING CLUSTER OFFICE | 1861 | 124 |  | 888 | 20 | 20 | Fan Coil Unit | 7104 | 15.7179 | 3 | 15.7179 | 3
- | 2ND FLOOR C WING CONF. ROOM | 107 | 7 |  | 810 | 18 | 7 | Fan Coil Unit | 6480 | 0.99074 | 0 | 0.99074 | 0
- | 2ND FLOOR CIRCLE HALL | 136 | 9 |  | 1246 | 28 | 9 | Fan Coil Unit | 9968 | 0.81862 | 0 | 0.81862 | 0
- | 2ND FLOOR D WING SHOP | 97 | 6 |  | 408 | 9 | 6 | Fan Coil Unit | 3264 | 1.7831 | 1 | 1.7831 | 1
- | 3RD FLOOR C WING CORR. | 660 | 44 |  | 1616 | 36 | 36 | Fan Coil Unit | 12928 | 3.0631 | 1 | 3.0631 | 1
- | 3RD FLOOR CIRCLE HALL | 137 | 9 |  | 1246 | 28 | 9 | Fan Coil Unit | 9968 | 0.82464 | 0 | 0.82464 | 0
- | 3RD FLOOR D WING CORR. | 501 | 33 |  | 1616 | 36 | 33 | Fan Coil Unit | 12928 | 2.3252 | 1 | 2.3252 | 1
- | 3RD FLOOR D WING OFFICE | 167 | 11 |  | 312 | 7 | 7 | Fan Coil Unit | 2496 | 4.0144 | 2 | 4.0144 | 2
- | 3RD FLOOR SHOP | 81 | 5 |  | 408 | 9 | 5 | Fan Coil Unit | 3264 | 1.489 | 1 | 1.489 | 1
- | BUILDING ENGINEER | 79 | 5 |  | 156 | 3 | 3 | Fan Coil Unit | 1248 | 3.7981 | 1 | 3.7981 | 1
- | FACULTY BREAK ROOM | 188 | 12 |  | 648 | 14 | 12 | Fan Coil Unit | 5184 | 2.1759 | 1 | 2.1759 | 1
- | GYM LOCKER ROOMS | 254 | 16 |  | 532 | 12 | 12 | Fan Coil Unit | 4256 | 3.5808 | 1 | 3.5808 | 1
- | GYM TEACHER | 144 | 9 |  | 280 | 6 | 6 | Fan Coil Unit | 2240 | 3.8571 | 1 | 3.8571 | 1
- | INSTRUMENT MUSIC | 0 | 0 | Yes | 1147 | 26 | 26 | Fan Coil Unit | 9176 | 0 | 0 | 20 | 3
- | IT Room | 268 | 17 |  | 396 | 9 | 9 | Fan Coil Unit | 3168 | 5.0758 | 2 | 5.0758 | 2
- | KITCHEN OFFICE | 164 | 10 |  | 156 | 3 | 3 | Fan Coil Unit | 1248 | 7.8846 | 2 | 7.8846 | 2
- | LIBRARY | 769 | 51 |  | 3864 | 87 | 51 | Fan Coil Unit | 30912 | 1.4926 | 1 | 1.4926 | 1
- | LIBRARY STORAGE | 184 | 12 |  | 396 | 9 | 9 | Fan Coil Unit | 3168 | 3.4848 | 1 | 3.4848 | 1
- | MUSIC PRACTICE B | 174 | 11 |  | 135 | 3 | 3 | Fan Coil Unit | 1080 | 9.6667 | 2 | 9.6667 | 2
- | MUSIC PRACTICE C | 272 | 18 |  | 135 | 3 | 3 | Fan Coil Unit | 1080 | 15.1111 | 3 | 15.1111 | 3
- | MUSIC PRATICE A | 126 | 8 |  | 135 | 3 | 3 | Fan Coil Unit | 1080 | 7 | 2 | 7 | 2
- | VOCAL MUSIC | 0 | 0 | Yes | 1221 | 27 | 27 | Fan Coil Unit | 9768 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-22 | [8 empty] | unk | unk | unk | unk
School: | Martha Washington Elementary-Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Meehan | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 808 | 53 |  | 782 | 17 | 17 | House Fan | 6256 | 7.7494 | 2 | 7.7494 | 2
102 | Classroom | 1564 | 104 |  | 920 | 20 | 20 | House Fan | 7360 | 12.75 | 3 | 12.75 | 3
103 | Classroom | 540 | 36 |  | 667 | 15 | 15 | House Fan | 5336 | 6.072 | 2 | 6.072 | 2
104 | Classroom | 250 | 16 |  | 667 | 15 | 15 | House Fan | 5336 | 2.8111 | 1 | 2.8111 | 1
106 | Classroom | 529 | 35 |  | 667 | 15 | 15 | House Fan | 5336 | 5.9483 | 2 | 5.9483 | 2
107 | Classroom | 370 | 24 |  | 690 | 15 | 15 | House Fan | 5520 | 4.0217 | 2 | 4.0217 | 2
108 | Classroom | 279 | 18 |  | 667 | 15 | 15 | House Fan | 5336 | 3.1372 | 1 | 3.1372 | 1
109 | Classroom | 525 | 35 |  | 667 | 15 | 15 | House Fan | 5336 | 5.9033 | 2 | 5.9033 | 2
110 | - |  | 0 |  | 667 | 15 | 0 | Univent | 5336 | unk | unk | unk | unk
111 | - |  | 0 | Yes | 667 | 15 | 15 | Univent | 5336 | unk | unk | 20 | 3
112 | - |  | 0 | Yes | 667 | 15 | 15 | Univent | 5336 | unk | unk | 20 | 3
113 | Classroom |  | 0 | Yes | 667 | 15 | 15 | Univent | 5336 | unk | unk | 20 | 3
201 | Classroom | 1290 | 86 |  | 667 | 15 | 15 | House Fan | 5336 | 14.5052 | 3 | 14.5052 | 3
202 | Classroom | 990 | 66 |  | 667 | 15 | 15 | House Fan | 5336 | 11.1319 | 3 | 11.1319 | 3
203 | Classroom | 425 | 28 |  | 759 | 17 | 17 | House Fan | 6072 | 4.1996 | 2 | 4.1996 | 2
204 | Classroom | 442 | 29 |  | 713 | 16 | 16 | House Fan | 5704 | 4.6494 | 2 | 4.6494 | 2
205 | Classroom | 345 | 23 |  | 621 | 14 | 14 | House Fan | 4968 | 4.1667 | 2 | 4.1667 | 2
206 | Classroom | 829 | 55 |  | 667 | 15 | 15 | House Fan | 5336 | 9.3216 | 2 | 9.3216 | 2
207 | Classroom | 479 | 31 |  | 660 | 15 | 15 | House Fan | 5280 | 5.4432 | 2 | 5.4432 | 2
208 | Classroom | 489 | 32 |  | 667 | 15 | 15 | House Fan | 5336 | 5.4985 | 2 | 5.4985 | 2
209 | Classroom | 394 | 26 |  | 667 | 15 | 15 | House Fan | 5336 | 4.4303 | 2 | 4.4303 | 2
211 | - |  | 0 | Yes | 667 | 15 | 15 | Univent | 5336 | unk | unk | 20 | 3
212 | - |  | 0 | Yes | 667 | 15 | 15 | Univent | 5336 | unk | unk | 20 | 3
301 | Classroom | 551 | 36 |  | 667 | 15 | 15 | House Fan | 5336 | 6.1957 | 2 | 6.1957 | 2
302 | Classroom | 850 | 56 |  | 667 | 15 | 15 | House Fan | 5336 | 9.5577 | 2 | 9.5577 | 2
303 | Classroom | 453 | 30 |  | 667 | 15 | 15 | House Fan | 5336 | 5.0937 | 2 | 5.0937 | 2
304 | Classroom | 236 | 15 |  | 1215 | 27 | 15 | House Fan | 9720 | 1.4568 | 1 | 1.4568 | 1
305 | Classroom | 62 | 4 |  | 644 | 14 | 4 | House Fan | 5152 | 0.72205 | 0 | 0.72205 | 0
306 | Classroom | 807 | 53 |  | 667 | 15 | 15 | House Fan | 5336 | 9.0742 | 2 | 9.0742 | 2
307 | Classroom | 649 | 43 |  | 667 | 15 | 15 | House Fan | 5336 | 7.2976 | 2 | 7.2976 | 2
308 | Classroom | 506 | 33 |  | 667 | 15 | 15 | House Fan | 5336 | 5.6897 | 2 | 5.6897 | 2
309 | Classroom | 826 | 55 |  | 667 | 15 | 15 | House Fan | 5336 | 9.2879 | 2 | 9.2879 | 2
310 | Classroom | 139 | 9 |  | 667 | 15 | 9 | House Fan | 5336 | 1.563 | 1 | 1.563 | 1
- | Main Office |  | 0 | Yes | 420 | 9 | 9 | Radiator | 3360 | unk | unk | 20 | 3
- | Principal's Office |  | 0 | Yes | 234 | 5 | 5 | Radiator | 1872 | unk | unk | 20 | 3
- | Nurse's Office |  | 0 | Yes | 180 | 4 | 4 | Radiator | 1440 | unk | unk | 20 | 3
- | BE's Office | 543 | 36 |  | 782 | 17 | 17 | House Fan | 6256 | 5.2078 | 2 | 5.2078 | 2
- | Lunch Room A | 1542 | 102 |  | 792 | 18 | 18 | House Fan | 6336 | 14.6023 | 3 | 14.6023 | 3
- | Lunch Room B | 1570 | 104 |  | 1540 | 35 | 35 | House Fan | 12320 | 7.6461 | 2 | 7.6461 | 2
G2 | - |  | 0 | Yes | 667 | 15 | 15 | Univent | 5336 | unk | unk | 20 | 3
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-23 | [8 empty] | unk | unk | unk | unk
School: | John H. Webster Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Devine Retest | [7 empty] | unk | unk | unk | unk
School: | John H. Webster Elementary School- Little School House | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Webster Main Building | [9 empty] | unk | unk | unk | unk
100 | Classroom | 1169 | 77 |  | 656 | 14 | 14 | Univent | 5248 | 13.3651 | 3 | 13.3651 | 3
101 | Classroom | 593 | 39 |  | 1263 | 28 | 28 | Univent | 10104 | 3.5214 | 1 | 3.5214 | 1
102 | Classroom | 435 | 29 |  | 721 | 16 | 16 | Univent | 5768 | 4.525 | 2 | 4.525 | 2
103 | Classroom | 1197 | 79 |  | 1062 | 24 | 24 | Univent | 8496 | 8.4534 | 2 | 8.4534 | 2
104 | Classroom | 251 | 16 |  | 897 | 20 | 16 | Univent | 7176 | 2.0987 | 1 | 2.0987 | 1
105 | Classroom | 310 | 20 |  | 531 | 12 | 12 | Univent | 4248 | 4.3785 | 2 | 4.3785 | 2
106 | Classroom | 477 | 31 |  | 949 | 21 | 21 | Univent | 7592 | 3.7698 | 1 | 3.7698 | 1
108 | Office | 49 | 3 |  | 226 | 5 | 3 | Air Handling Unit | 1808 | 1.6261 | 1 | 1.6261 | 1
110 | Classroom | 358 | 23 |  | 1365 | 31 | 23 | Air Handling Unit | 10920 | 1.967 | 1 | 1.967 | 1
111 | Classroom | 312 | 20 |  | 1160 | 26 | 20 | Air Handling Unit | 9280 | 2.0172 | 1 | 2.0172 | 1
112 | STS Classroom | 449 | 29 |  | 141 | 3 | 3 | Air Handling Unit | 1128 | 23.883 | 3 | 23.883 | 3
113 | Classroom | 280 | 18 |  | 1157 | 26 | 18 | Air Handling Unit | 9256 | 1.815 | 1 | 1.815 | 1
114 | Classroom | 290 | 19 |  | 1418 | 32 | 19 | Air Handling Unit | 11344 | 1.5339 | 1 | 1.5339 | 1
200 | Classroom | 503 | 33 |  | 761 | 17 | 17 | Univent | 6088 | 4.9573 | 2 | 4.9573 | 2
201 | Classroom | 369 | 24 |  | 597 | 13 | 13 | Univent | 4776 | 4.6357 | 2 | 4.6357 | 2
202 | Classroom | 403 | 26 |  | 475 | 10 | 10 | Univent | 3800 | 6.3632 | 2 | 6.3632 | 2
203 | Classroom | 444 | 29 |  | 772 | 17 | 17 | Univent | 6176 | 4.3135 | 2 | 4.3135 | 2
204 | Classroom | 285 | 19 |  | 532 | 12 | 12 | Univent | 4256 | 4.0179 | 2 | 4.0179 | 2
205 | Classroom | 329 | 21 |  | 823 | 18 | 18 | Univent | 6584 | 2.9982 | 1 | 2.9982 | 1
206 | Classroom | 438 | 29 |  | 480 | 10 | 10 | Univent | 3840 | 6.8438 | 2 | 6.8438 | 2
207 | Classroom | 108 | 7 | Yes | 648 | 14 | 14 | Univent | 5184 | 1.25 | 1 | 21.25 | 3
208 | Classroom | 352 | 23 |  | 540 | 12 | 12 | Univent | 4320 | 4.8889 | 2 | 4.8889 | 2
209 | Classroom | 387 | 25 |  | 537 | 12 | 12 | Univent | 4296 | 5.405 | 2 | 5.405 | 2
300 | Classroom | 161 | 10 |  | 789 | 17 | 10 | Univent | 6312 | 1.5304 | 1 | 1.5304 | 1
301 | Classroom | 313 | 20 |  | 729 | 16 | 16 | Univent | 5832 | 3.2202 | 1 | 3.2202 | 1
302 | Classroom | 447 | 29 |  | 473 | 10 | 10 | Univent | 3784 | 7.0877 | 2 | 7.0877 | 2
303 | Classroom | 137 | 9 | Yes | 690 | 15 | 15 | Univent | 5520 | 1.4891 | 1 | 21.4891 | 3
304 | Classroom | 324 | 21 |  | 667 | 15 | 15 | Univent | 5336 | 3.6432 | 1 | 3.6432 | 1
305 | Classroom | 321 | 21 |  | 794 | 18 | 18 | Univent | 6352 | 3.0321 | 1 | 3.0321 | 1
306 | Classroom | 223 | 14 |  | 559 | 12 | 12 | Univent | 4472 | 2.9919 | 1 | 2.9919 | 1
307 | Classroom | 171 | 11 |  | 790 | 17 | 11 | Univent | 6320 | 1.6234 | 1 | 1.6234 | 1
308 | Classroom | 265 | 17 |  | 662 | 15 | 15 | Univent | 5296 | 3.0023 | 1 | 3.0023 | 1
309 | Classroom | 360 | 24 |  | 567 | 12 | 12 | Univent | 4536 | 4.7619 | 2 | 4.7619 | 2
311 | Classroom | 0 | 0 | Yes | 775 | 17 | 17 | Univent | 6200 | 0 | 0 | 20 | 3
312 | Classroom | 397 | 26 |  | 573 | 13 | 13 | Univent | 4584 | 5.1963 | 2 | 5.1963 | 2
- | 2nd & 3rd corridors | 251 | 16 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Administration | 637 | 42 |  | 244 | 5 | 5 | Air Handling Unit | 1952 | 19.5799 | 3 | 19.5799 | 3
- | Auditorium | 2708 | 180 |  | 3216 | 73 | 73 | Air Handling Unit | 25728 | 6.3153 | 2 | 6.3153 | 2
- | Cafeteria | 2800 | 186 |  | 3216 | 73 | 73 | Air Handling Unit | 25728 | 6.5299 | 2 | 6.5299 | 2
- | Child Care | 1704 | 113 |  | 1115 | 25 | 25 | Air Handling Unit | 8920 | 11.4619 | 3 | 11.4619 | 3
- | Conference Office | 98 | 6 |  | 236 | 5 | 5 | Air Handling Unit | 1888 | 3.1144 | 1 | 3.1144 | 1
- | Copy Room Office | 44 | 2 |  | 178 | 4 | 2 | Air Handling Unit | 1424 | 1.8539 | 1 | 1.8539 | 1
- | Gym | 0 | 0 |  | 4403 | 100 | 0 | Air Handling Unit | 35224 | 0 | 0 | 0 | 0
- | IMC |  | 0 | Yes | 1363 | 30 | 30 | Univent | 10904 | unk | unk | 20 | 3
- | Kitchen Make Up | 1547 | 103 |  | 352 | 8 | 8 | Air Handling Unit | 2816 | 32.9616 | 4 | 32.9616 | 4
- | Main Office | 201 | 13 |  | 244 | 5 | 5 | Air Handling Unit | 1952 | 6.1783 | 2 | 6.1783 | 2
- | Mrs. Freeland's Office | 30 | 2 |  | 123 | 2 | 2 | Air Handling Unit | 984 | 1.8293 | 1 | 1.8293 | 1
- | Music Room | 1406 | 93 |  | 696 | 15 | 15 | Air Handling Unit | 5568 | 15.1509 | 3 | 15.1509 | 3
- | Nurse's Office | 87 | 5 |  | 412 | 9 | 5 | Air Handling Unit | 3296 | 1.5837 | 1 | 1.5837 | 1
- | Principal's Office | 65 | 4 |  | 270 | 6 | 4 | Air Handling Unit | 2160 | 1.8056 | 1 | 1.8056 | 1
- | Vice Principal's Office | 54 | 3 |  | 130 | 2 | 2 | Air Handling Unit | 1040 | 3.1154 | 1 | 3.1154 | 1
Webster LSH | [9 empty] | unk | unk | unk | unk
1 | Classroom | 441 | 29 |  | 971 | 22 | 22 | Blower Coil Unit | 7768 | 3.4063 | 1 | 3.4063 | 1
2 | Classroom | 189 | 12 | Yes | 1012 | 23 | 23 | Blower Coil Unit | 8096 | 1.4007 | 1 | 21.4007 | 3
3 | Classroom | 449 | 29 |  | 1016 | 23 | 23 | Blower Coil Unit | 8128 | 3.3145 | 1 | 3.3145 | 1
4 | Classroom | 195 | 13 | Yes | 1017 | 23 | 23 | Blower Coil Unit | 8136 | 1.4381 | 1 | 21.4381 | 3
5 | Classroom |  | 0 | Yes | 914 | 20 | 20 | Blower Coil Unit | 7312 | unk | unk | 20 | 3
6 | Classroom |  | 0 | Yes | 1040 | 23 | 23 | Blower Coil Unit | 8320 | unk | unk | 20 | 3
7 | Classroom |  | 0 | Yes | 1003 | 22 | 22 | Blower Coil Unit | 8024 | unk | unk | 20 | 3
8 | Classroom |  | 0 | Yes | 1024 | 23 | 23 | Blower Coil Unit | 8192 | unk | unk | 20 | 3
9 | Classroom | 162 | 10 | Yes | 975 | 22 | 22 | Blower Coil Unit | 7800 | 1.2462 | 1 | 21.2462 | 3
10 | Classroom | 164 | 10 | Yes | 982 | 22 | 22 | Blower Coil Unit | 7856 | 1.2525 | 1 | 21.2525 | 3
11 | Classroom | 188 | 12 | Yes | 1012 | 23 | 23 | Blower Coil Unit | 8096 | 1.3933 | 1 | 21.3933 | 3
- | Student Toilets | 171 | 11 |  | 292 | 6 | 6 | Blower Coil Unit | 2336 | 4.3921 | 2 | 4.3921 | 2
- | Custodial Closet |  | 0 |  | 58 | 1 | 0 | Fan Coil Unit | 464 | unk | unk | unk | unk
- | Faculty Room |  | 0 |  | 156 | 3 | 0 | Fan Coil Unit | 1248 | unk | unk | unk | unk
- | Multi Purpose Room | 2361 | 157 |  | 1714 | 38 | 38 | Blower Coil Unit | 13712 | 10.3311 | 3 | 10.3311 | 3
- | Office Area | 409 | 27 |  | 274 | 6 | 6 | Blower Coil Unit | 2192 | 11.1953 | 3 | 11.1953 | 3
- | Staff Toilets |  | 0 |  | 58 | 1 | 0 | Blower Coil Unit | 464 | unk | unk | unk | unk
- | Storage & Closet |  | 0 |  | 200 | 4 | 0 | Blower Coil Unit | 1600 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-13 | [8 empty] | unk | unk | unk | unk
School: | John Welsh Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine Brothers | Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 573 | 38 |  | 1122 | 25 | 25 | Univent | 8976 | 3.8302 | 1 | 3.8302 | 1
102 | Classroom | 641 | 42 |  | 1030 | 23 | 23 | Univent | 8240 | 4.6675 | 2 | 4.6675 | 2
103 | Classroom | 311 | 20 |  | 650 | 14 | 14 | Univent | 5200 | 3.5885 | 1 | 3.5885 | 1
104 | Faculty Lounge | 774 | 51 |  | 750 | 17 | 17 | Univent | 6000 | 7.74 | 2 | 7.74 | 2
105 | Classroom | 307 | 20 |  | 586 | 13 | 13 | Univent | 4688 | 3.9292 | 1 | 3.9292 | 1
106 | Classroom | 674 | 44 |  | 760 | 17 | 17 | Univent | 6080 | 6.6513 | 2 | 6.6513 | 2
200 | Classroom | 301 | 20 |  | 825 | 18 | 18 | Univent | 6600 | 2.7364 | 1 | 2.7364 | 1
201 | Classroom | 336 | 22 |  | 825 | 18 | 18 | Univent | 6600 | 3.0545 | 1 | 3.0545 | 1
202 | Classroom | 333 | 22 |  | 825 | 18 | 18 | Univent | 6600 | 3.0273 | 1 | 3.0273 | 1
203 | Classroom | 574 | 38 |  | 825 | 18 | 18 | Univent | 6600 | 5.2182 | 2 | 5.2182 | 2
204 | Classroom | 356 | 23 |  | 825 | 18 | 18 | Univent | 6600 | 3.2364 | 1 | 3.2364 | 1
205 | Classroom | 380 | 25 |  | 825 | 18 | 18 | Univent | 6600 | 3.4545 | 1 | 3.4545 | 1
206 | Classroom | 405 | 27 |  | 825 | 18 | 18 | Univent | 6600 | 3.6818 | 1 | 3.6818 | 1
209 | Classroom | 330 | 22 |  | 825 | 18 | 18 | Univent | 6600 | 3 | 1 | 3 | 1
210 | Library | 642 | 42 |  | 1218 | 27 | 27 | Univent | 9744 | 3.9532 | 1 | 3.9532 | 1
211 | Classroom | 320 | 21 |  | 825 | 18 | 18 | Univent | 6600 | 2.9091 | 1 | 2.9091 | 1
212 | Classroom | 610 | 40 |  | 825 | 18 | 18 | Univent | 6600 | 5.5455 | 2 | 5.5455 | 2
300 | Classroom | 858 | 57 |  | 830 | 18 | 18 | Univent | 6640 | 7.753 | 2 | 7.753 | 2
301A | Classroom | 341 | 22 |  | 393 | 8 | 8 | Univent | 3144 | 6.5076 | 2 | 6.5076 | 2
301B | Classroom |  | 0 | Yes | 393 | 8 | 8 | Univent | 3144 | unk | unk | 20 | 3
302 | Classroom | 887 | 59 |  | 830 | 18 | 18 | Univent | 6640 | 8.0151 | 2 | 8.0151 | 2
303 | Classroom | 341 | 22 |  | 830 | 18 | 18 | Univent | 6640 | 3.0813 | 1 | 3.0813 | 1
304 | Classroom | 790 | 52 |  | 830 | 18 | 18 | Univent | 6640 | 7.1386 | 2 | 7.1386 | 2
305 | Classroom | 885 | 59 |  | 830 | 18 | 18 | Univent | 6640 | 7.997 | 2 | 7.997 | 2
306 | Classroom | 590 | 39 |  | 423 | 9 | 9 | Univent | 3384 | 10.461 | 3 | 10.461 | 3
308 | Classroom | 420 | 28 |  | 411 | 9 | 9 | Univent | 3288 | 7.6642 | 2 | 7.6642 | 2
309 | Classroom | 454 | 30 |  | 830 | 18 | 18 | Univent | 6640 | 4.1024 | 2 | 4.1024 | 2
310 | Classroom | 705 | 47 |  | 830 | 18 | 18 | Univent | 6640 | 6.3705 | 2 | 6.3705 | 2
311 | Classroom | 890 | 59 |  | 830 | 18 | 18 | Univent | 6640 | 8.0422 | 2 | 8.0422 | 2
312 | Classroom | 798 | 53 |  | 830 | 18 | 18 | Univent | 6640 | 7.2108 | 2 | 7.2108 | 2
400 | Classroom | 346 | 23 |  | 825 | 18 | 18 | Univent | 6600 | 3.1455 | 1 | 3.1455 | 1
401 | Classroom | 874 | 58 |  | 825 | 18 | 18 | Univent | 6600 | 7.9455 | 2 | 7.9455 | 2
402 | Classroom | 801 | 53 |  | 825 | 18 | 18 | Univent | 6600 | 7.2818 | 2 | 7.2818 | 2
403 | Classroom | 852 | 56 |  | 825 | 18 | 18 | Univent | 6600 | 7.7455 | 2 | 7.7455 | 2
404 | Classroom | 368 | 24 |  | 825 | 18 | 18 | Univent | 6600 | 3.3455 | 1 | 3.3455 | 1
405 | Classroom | 820 | 54 |  | 825 | 18 | 18 | Univent | 6600 | 7.4545 | 2 | 7.4545 | 2
406 | Classroom | 328 | 21 |  | 425 | 9 | 9 | Univent | 3400 | 5.7882 | 2 | 5.7882 | 2
408 | Classroom | 426 | 28 |  | 410 | 9 | 9 | Univent | 3280 | 7.7927 | 2 | 7.7927 | 2
409 | Classroom | 417 | 27 |  | 825 | 18 | 18 | Univent | 6600 | 3.7909 | 1 | 3.7909 | 1
410 | Classroom | 558 | 37 |  | 825 | 18 | 18 | Univent | 6600 | 5.0727 | 2 | 5.0727 | 2
411 | Classroom | 897 | 59 |  | 825 | 18 | 18 | Univent | 6600 | 8.1545 | 2 | 8.1545 | 2
412 | Classroom | 0 | 0 |  | 403 | 9 | 0 | Univent | 3224 | 0 | 0 | 0 | 0
412A | Classroom | 820 | 54 |  | 403 | 9 | 9 | Univent | 3224 | 15.2605 | 3 | 15.2605 | 3
- | Main Office | 438 | 29 |  | 1038 | 23 | 23 | Univent | 8304 | 3.1647 | 1 | 3.1647 | 1
- | Auditorium | 0 | 0 |  | 3868 | 87 | 0 | Air Handling Unit | 30944 | 0 | 0 | 0 | 0
- | Gym | 4931 | 328 |  | 3509 | 79 | 79 | Air Handling Unit | 28072 | 10.5393 | 3 | 10.5393 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | New West Philadelphia High School | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
107 | Nurse Office |  | 0 |  | 264 | 6 | 0 | Air Handing Unit | 2112 | unk | unk | unk | unk
107A | Nurse Exam Room |  | 0 |  | 149 | 3 | 0 | Air Handing Unit | 1192 | unk | unk | unk | unk
107B | Nurse Suite |  | 0 |  | 100 | 2 | 0 | Air Handing Unit | 800 | unk | unk | unk | unk
107C | Nurse Suite |  | 0 |  | 110 | 2 | 0 | Air Handing Unit | 880 | unk | unk | unk | unk
101C | Maker Room |  | 0 | Yes | 1268 | 28 | 28 | Air Handing Unit | 10144 | unk | unk | 20 | 3
200 | - | 145 | 9 |  | 875 | 19 | 9 | Univent | 7000 | 1.2429 | 1 | 1.2429 | 1
201 | Classroom | 190 | 12 |  | 539 | 12 | 12 | Univent | 4312 | 2.6438 | 1 | 2.6438 | 1
202 | - | 308 | 20 |  | 895 | 20 | 20 | Univent | 7160 | 2.581 | 1 | 2.581 | 1
203 | - | 165 | 11 |  | 899 | 20 | 11 | Univent | 7192 | 1.3765 | 1 | 1.3765 | 1
204 | - | 398 | 26 |  | 900 | 20 | 20 | Univent | 7200 | 3.3167 | 1 | 3.3167 | 1
205 | - | 105 | 7 |  | 877 | 19 | 7 | Univent | 7016 | 0.89795 | 0 | 0.89795 | 0
206 | - | 344 | 22 |  | 898 | 20 | 20 | Univent | 7184 | 2.8731 | 1 | 2.8731 | 1
207 | - | 315 | 21 |  | 877 | 19 | 19 | Univent | 7016 | 2.6938 | 1 | 2.6938 | 1
208 | - | 281 | 18 |  | 937 | 21 | 18 | Univent | 7496 | 2.2492 | 1 | 2.2492 | 1
216 | - | 176 | 11 |  | 1330 | 30 | 11 | Univent | 10640 | 0.99248 | 0 | 0.99248 | 0
300 | - | 210 | 14 |  | 878 | 19 | 14 | Univent | 7024 | 1.7938 | 1 | 1.7938 | 1
301 | - | 0 | 0 |  | 544 | 12 | 0 | Univent | 4352 | 0 | 0 | 0 | 0
302 | - | 470 | 31 |  | 898 | 20 | 20 | Univent | 7184 | 3.9254 | 1 | 3.9254 | 1
303 | - | 205 | 13 |  | 900 | 20 | 13 | Univent | 7200 | 1.7083 | 1 | 1.7083 | 1
304 | - | 235 | 15 |  | 900 | 20 | 15 | Univent | 7200 | 1.9583 | 1 | 1.9583 | 1
305 | - |  | 0 |  | 874 | 19 | 0 | Univent | 6992 | unk | unk | unk | unk
306 | - | 190 | 12 |  | 896 | 20 | 12 | Univent | 7168 | 1.5904 | 1 | 1.5904 | 1
307 | Classroom |  | 0 | Yes | 1387 | 31 | 31 | Univent | 11096 | unk | unk | 20 | 3
308 | - | 230 | 15 |  | 897 | 20 | 15 | Univent | 7176 | 1.9231 | 1 | 1.9231 | 1
309 | Classroom |  | 0 | Yes | 1357 | 30 | 30 | Univent | 10856 | unk | unk | 20 | 3
310 | - | 115 | 7 |  | 898 | 20 | 7 | Univent | 7184 | 0.96047 | 0 | 0.96047 | 0
311 | - |  | 0 |  | 900 | 20 | 0 | Univent | 7200 | unk | unk | unk | unk
312 | - | 625 | 41 |  | 872 | 19 | 19 | Univent | 6976 | 5.3756 | 2 | 5.3756 | 2
313 | - |  | 0 |  | 877 | 19 | 0 | Univent | 7016 | unk | unk | unk | unk
315 | - | 425 | 28 |  | 876 | 19 | 19 | Univent | 7008 | 3.6387 | 1 | 3.6387 | 1
316 | - | 190 | 12 |  | 399 | 9 | 9 | Univent | 3192 | 3.5714 | 1 | 3.5714 | 1
317 | - | 205 | 13 |  | 902 | 20 | 13 | Univent | 7216 | 1.7045 | 1 | 1.7045 | 1
318 | - | 365 | 24 |  | 1274 | 28 | 24 | Univent | 10192 | 2.1487 | 1 | 2.1487 | 1
319 | - | 195 | 13 |  | 899 | 20 | 13 | Univent | 7192 | 1.6268 | 1 | 1.6268 | 1
320 | - |  | 0 |  | 876 | 19 | 0 | Univent | 7008 | unk | unk | unk | unk
321 | - | 425 | 28 |  | 894 | 20 | 20 | Univent | 7152 | 3.5654 | 1 | 3.5654 | 1
Gymnasium | Gymnasium | 0 | 0 |  | 6370 | 144 | 0 | Univent | 50960 | 0 | 0 | 0 | 0
Gymnasium | Gymnasium | 0 | 0 | Yes | 10648 | 242 | 242 | Univent | 85184 | 0 | 0 | 20 | 3
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-13 | [8 empty] | unk | unk | unk | unk
School: | Widener Memorial Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
2 | - | 1283 | 85 |  | 2800 | 63 | 63 | Carrier / Perimeter Heater | 22400 | 3.4366 | 1 | 3.4366 | 1
3 | - | 500 | 33 |  | 1344 | 30 | 30 | Carrier / Perimeter Heater | 10752 | 2.7902 | 1 | 2.7902 | 1
4 | - | 70 | 4 |  | 1332 | 30 | 4 | Carrier / Perimeter Heater | 10656 | 0.39414 | 0 | 0.39414 | 0
5 | - | 146 | 9 |  | 527 | 11 | 9 | Carrier / Perimeter Heater | 4216 | 2.0778 | 1 | 2.0778 | 1
6 | - | 38 | 2 |  | 744 | 16 | 2 | Carrier / Perimeter Heater | 5952 | 0.38306 | 0 | 0.38306 | 0
7 | - | 70 | 4 |  | 912 | 20 | 4 | Carrier / Perimeter Heater | 7296 | 0.57566 | 0 | 0.57566 | 0
8 | - | 317 | 21 |  | 460 | 10 | 10 | Carrier / Perimeter Heater | 3680 | 5.1685 | 2 | 5.1685 | 2
9 | - | 311 | 20 |  | 480 | 10 | 10 | Carrier / Perimeter Heater | 3840 | 4.8594 | 2 | 4.8594 | 2
10 | - | 291 | 19 |  | 504 | 11 | 11 | Carrier / Perimeter Heater | 4032 | 4.3304 | 2 | 4.3304 | 2
11 | - | 290 | 19 |  | 504 | 11 | 11 | Carrier / Perimeter Heater | 4032 | 4.3155 | 2 | 4.3155 | 2
12 | - | 292 | 19 |  | 744 | 16 | 16 | Carrier / Perimeter Heater | 5952 | 2.9435 | 1 | 2.9435 | 1
13 | - | 210 | 14 |  | 759.5 | 17 | 14 | Carrier / Perimeter Heater | 6076 | 2.0737 | 1 | 2.0737 | 1
14 | - | 244 | 16 |  | 759.5 | 17 | 16 | Carrier / Perimeter Heater | 6076 | 2.4095 | 1 | 2.4095 | 1
15 | - | 224 | 14 |  | 759.5 | 17 | 14 | Carrier / Perimeter Heater | 6076 | 2.212 | 1 | 2.212 | 1
16 | - | 225 | 15 |  | 759.5 | 17 | 15 | Carrier / Perimeter Heater | 6076 | 2.2219 | 1 | 2.2219 | 1
17 | - | 260 | 17 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 2.5675 | 1 | 2.5675 | 1
18 | - | 304 | 20 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 3.002 | 1 | 3.002 | 1
19 | - | 0 | 0 | Yes | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 0 | 0 | 20 | 3
20 | - | 356 | 23 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 3.5155 | 1 | 3.5155 | 1
21 | - | 271 | 18 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 2.6761 | 1 | 2.6761 | 1
22 | - | 282 | 18 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 2.7847 | 1 | 2.7847 | 1
23 | - | 275 | 18 |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 2.7156 | 1 | 2.7156 | 1
24 | - | 0 | 0 | Yes | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 6076 | 0 | 0 | 20 | 3
25 | - | 192 | 12 |  | 1014 | 23 | 12 | Carrier / Perimeter Heater | 8112 | 1.4201 | 1 | 1.4201 | 1
26 | - | 2008 | 133 |  | 891 | 20 | 20 | Air Handling Unit | 7128 | 16.9024 | 3 | 16.9024 | 3
27 | - | 416 | 27 |  | 619.5 | 14 | 14 | Air Handling Unit | 4956 | 5.0363 | 2 | 5.0363 | 2
28 | - | 416 | 27 |  | 925 | 21 | 21 | Air Handling Unit | 7400 | 3.373 | 1 | 3.373 | 1
31A | - | 0 | 0 | Yes | 190 | 4 | 4 | Carrier / Perimeter Heater | 1520 | 0 | 0 | 20 | 3
31B | Nurse's Office | 0 | 0 | Yes | 196 | 4 | 4 | Carrier / Perimeter Heater | 1568 | 0 | 0 | 20 | 3
32 | - | 0 | 0 |  | 272 | 6 | 0 | Carrier / Perimeter Heater | 2176 | 0 | 0 | 0 | 0
33 | - | 396 | 26 |  | 1271 | 28 | 26 | Carrier / Perimeter Heater | 10168 | 2.3367 | 1 | 2.3367 | 1
34 | - | 622 | 41 |  | 1470 | 33 | 33 | Carrier / Perimeter Heater | 11760 | 3.1735 | 1 | 3.1735 | 1
35A | - | 265 | 17 |  | 720 | 16 | 16 | Carrier / Perimeter Heater | 5760 | 2.7604 | 1 | 2.7604 | 1
35B | - | 222 | 14 |  | 1107 | 25 | 14 | Carrier / Perimeter Heater | 8856 | 1.5041 | 1 | 1.5041 | 1
35C | - | 0 | 0 | Yes | 364 | 8 | 8 | Carrier / Perimeter Heater | 2912 | 0 | 0 | 20 | 3
36 | - | 0 | 0 |  | 1288 | 29 | 0 | Carrier / Perimeter Heater | 10304 | 0 | 0 | 0 | 0
37 | - | 235 | 15 |  | 600 | 13 | 13 | Carrier / Perimeter Heater | 4800 | 2.9375 | 1 | 2.9375 | 1
38 | - | 257 | 17 |  | 600 | 13 | 13 | Carrier / Perimeter Heater | 4800 | 3.2125 | 1 | 3.2125 | 1
39 | - | 88 | 5 |  | 462 | 10 | 5 | Carrier / Perimeter Heater | 3696 | 1.4286 | 1 | 1.4286 | 1
40 | - | 115 | 7 |  | 472 | 10 | 7 | Carrier / Perimeter Heater | 3776 | 1.8273 | 1 | 1.8273 | 1
41 | - | 235 | 15 |  | 702 | 15 | 15 | Carrier / Perimeter Heater | 5616 | 2.5107 | 1 | 2.5107 | 1
46 | Small Cafeteria | 182 | 12 |  | 1347 | 30 | 12 | Carrier / Perimeter Heater | 10776 | 1.0134 | 1 | 1.0134 | 1
47 | - | 75 | 5 | Yes | 315 | 7 | 7 | Carrier / Perimeter Heater | 2520 | 1.7857 | 1 | 21.7857 | 3
48 | - | 90 | 6 |  | 817 | 18 | 6 | Carrier / Perimeter Heater | 6536 | 0.82619 | 0 | 0.82619 | 0
103 | - | 290 | 19 |  | 840 | 19 | 19 | Carrier / Perimeter Heater | 6720 | 2.5893 | 1 | 2.5893 | 1
104 | - | 310 | 20 |  | 840 | 19 | 19 | Carrier / Perimeter Heater | 6720 | 2.7679 | 1 | 2.7679 | 1
105 | - | 410 | 27 |  | 810 | 18 | 18 | Carrier / Perimeter Heater | 6480 | 3.7963 | 1 | 3.7963 | 1
106 | - | 300 | 20 |  | 868 | 19 | 19 | Carrier / Perimeter Heater | 6944 | 2.5922 | 1 | 2.5922 | 1
107 | - | 530 | 35 |  | 850 | 19 | 19 | Carrier / Perimeter Heater | 6800 | 4.6765 | 2 | 4.6765 | 2
108 | - | 489 | 32 |  | 840 | 19 | 19 | Carrier / Perimeter Heater | 6720 | 4.3661 | 2 | 4.3661 | 2
109 | - | 40 | 2 | Yes | 840 | 19 | 19 | Carrier / Perimeter Heater | 6720 | 0.35714 | 0 | 20.3571 | 3
110 | - | 550 | 36 |  | 840 | 19 | 19 | Carrier / Perimeter Heater | 6720 | 4.9107 | 2 | 4.9107 | 2
101 | - | 430 | 28 |  | 1271 | 28 | 28 | Carrier / Perimeter Heater | 10168 | 2.5374 | 1 | 2.5374 | 1
102A | - | 124 | 8 |  | 140 | 3 | 3 | Carrier / Perimeter Heater | 1120 | 6.6429 | 2 | 6.6429 | 2
102B | - | 165 | 11 |  | 140 | 3 | 3 | Carrier / Perimeter Heater | 1120 | 8.8393 | 2 | 8.8393 | 2
111A | - | 98 | 6 |  | 140 | 3 | 3 | Carrier / Perimeter Heater | 1120 | 5.25 | 2 | 5.25 | 2
111B | - | 110 | 7 |  | 140 | 3 | 3 | Carrier / Perimeter Heater | 1120 | 5.8929 | 2 | 5.8929 | 2
112 | - | 905 | 60 |  | 1271 | 28 | 28 | Carrier / Perimeter Heater | 10168 | 5.3403 | 2 | 5.3403 | 2
- | Auditorium | 1042 | 69 |  | 4087 | 92 | 69 | Air Handling Unit | 32696 | 1.9122 | 1 | 1.9122 | 1
- | Cafeteria | 918 | 61 |  | 2720 | 61 | 61 | Carrier / Perimeter Heater | 21760 | 2.5312 | 1 | 2.5312 | 1
- | Computer Lab | 320 | 21 | Yes | 943 | 21 | 21 | Air Handling Unit | 7544 | 2.5451 | 1 | 22.5451 | 3
- | Food Service "A & B" | 0 | 0 |  | 1320 | 30 | 0 | Carrier / Perimeter Heater | 10560 | 0 | 0 | 0 | 0
- | Game Room | 577 | 38 |  | 675 | 15 | 15 | Carrier / Perimeter Heater | 5400 | 6.4111 | 2 | 6.4111 | 2
- | GYM | 174 | 11 |  | 3721 | 84 | 11 | Air Handling Unit | 29768 | 0.35071 | 0 | 0.35071 | 0
- | Kitchen | 3011 | 200 |  | 1191 | 27 | 27 | Make-Up Air Unit | 9528 | 18.961 | 3 | 18.961 | 3
- | Music Room | 2765 | 184 |  | 2040 | 46 | 46 | Air Handling Unit | 16320 | 10.1654 | 3 | 10.1654 | 3
- | Pool | 0 | 0 |  | 7467 | 169 | 0 | Air Handling Unit | 59736 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | Frances E. Willard Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Devine | Main Building Retest | [7 empty] | unk | unk | unk | unk
School: | Willard Annex | [8 empty] | unk | unk | unk | unk
Vendor: | EMCOR Fluidics | EMCOR Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
Willard Main Building | [9 empty] | unk | unk | unk | unk
100A | OFFICE | 39 | 2 |  | 181 | 4 | 2 | Air Handling Unit | 1448 | 1.616 | 1 | 1.616 | 1
100B | OFFICE | 31 | 2 |  | 121 | 2 | 2 | Air Handling Unit | 968 | 1.9215 | 1 | 1.9215 | 1
100C | OFFICE | 39 | 2 |  | 43 | 0 | 0 | Air Handling Unit | 344 | 6.8023 | 2 | 6.8023 | 2
100D | OFFICE | 37 | 2 |  | 121 | 2 | 2 | Air Handling Unit | 968 | 2.2934 | 1 | 2.2934 | 1
100E | OFFICE | 35 | 2 |  | 120 | 2 | 2 | Air Handling Unit | 960 | 2.1875 | 1 | 2.1875 | 1
100F | OFFICE | 51 | 3 |  | 345 | 7 | 3 | Air Handling Unit | 2760 | 1.1087 | 1 | 1.1087 | 1
100G | Conference | 85 | 5 |  | 279 | 6 | 5 | Air Handling Unit | 2232 | 2.2849 | 1 | 2.2849 | 1
100H | BREAK ROOM | 70 | 4 |  | 145 | 3 | 3 | Air Handling Unit | 1160 | 3.6207 | 1 | 3.6207 | 1
100I | OFFICE | 76 | 5 |  | 210 | 4 | 4 | Air Handling Unit | 1680 | 2.7143 | 1 | 2.7143 | 1
101 | Classroom | 310 | 20 |  | 984 | 22 | 20 | Univent and Air Handling Unit | 7872 | 2.3628 | 1 | 2.3628 | 1
102 | Classroom | 304 | 20 |  | 1059 | 24 | 20 | Univent and Air Handling Unit | 8472 | 2.153 | 1 | 2.153 | 1
103 | Classroom | 321 | 21 |  | 889 | 20 | 20 | Univent and Air Handling Unit | 7112 | 2.7081 | 1 | 2.7081 | 1
104 | Classroom | 282 | 18 |  | 1086 | 24 | 18 | Univent and Air Handling Unit | 8688 | 1.9475 | 1 | 1.9475 | 1
105 | Classroom | 295 | 19 |  | 677 | 15 | 15 | Univent and Air Handling Unit | 5416 | 3.2681 | 1 | 3.2681 | 1
106 | Classroom | 331 | 22 |  | 800 | 18 | 18 | Univent and Air Handling Unit | 6400 | 3.1031 | 1 | 3.1031 | 1
107 | Nurse OFFICE | 35 | 2 |  | 277 | 6 | 2 | Fan Coil | 2216 | 0.94765 | 0 | 0.94765 | 0
107A | OFFICE | 45 | 3 |  | 161 | 3 | 3 | Fan Coil | 1288 | 2.0963 | 1 | 2.0963 | 1
107C | OFFICE | 14 | 0 |  | 150 | 3 | 0 | Air Handling Unit | 1200 | 0.7 | 0 | 0.7 | 0
107D | OFFICE | 26 | 1 |  | 103 | 2 | 1 | Air Handling Unit | 824 | 1.8932 | 1 | 1.8932 | 1
107G | COMPUTER LAB | 298 | 19 |  | 1033 | 23 | 19 | Univent | 8264 | 2.1636 | 1 | 2.1636 | 1
109 | Classroom | 282 | 18 |  | 802 | 18 | 18 | Univent and Air Handling Unit | 6416 | 2.6372 | 1 | 2.6372 | 1
110 | Classroom | 282 | 18 |  | 818 | 18 | 18 | Univent and Air Handling Unit | 6544 | 2.5856 | 1 | 2.5856 | 1
111 | Classroom | 295 | 19 |  | 818 | 18 | 18 | Univent and Air Handling Unit | 6544 | 2.7048 | 1 | 2.7048 | 1
112 | Classroom | 306 | 20 |  | 813 | 18 | 18 | Univent and Air Handling Unit | 6504 | 2.8229 | 1 | 2.8229 | 1
113 | Classroom | 305 | 20 |  | 813 | 18 | 18 | Univent and Air Handling Unit | 6504 | 2.8137 | 1 | 2.8137 | 1
114 | Classroom | 280 | 18 |  | 815 | 18 | 18 | Univent and Air Handling Unit | 6520 | 2.5767 | 1 | 2.5767 | 1
115 | Classroom | 293 | 19 |  | 815 | 18 | 18 | Univent and Air Handling Unit | 6520 | 2.6963 | 1 | 2.6963 | 1
116 | Classroom | 302 | 20 |  | 813 | 18 | 18 | Univent and Air Handling Unit | 6504 | 2.786 | 1 | 2.786 | 1
117 | Classroom | 295 | 19 |  | 813 | 18 | 18 | Univent and Air Handling Unit | 6504 | 2.7214 | 1 | 2.7214 | 1
121 | Classroom | 381 | 25 |  | 1059 | 24 | 24 | Univent and Air Handling Unit | 8472 | 2.6983 | 1 | 2.6983 | 1
122 | Music Room | 328 | 21 |  | 1189 | 27 | 21 | Univent | 9512 | 2.069 | 1 | 2.069 | 1
123 | Classroom | 392 | 26 |  | 1061 | 24 | 24 | Univent and Air Handling Unit | 8488 | 2.771 | 1 | 2.771 | 1
126 | Staff Lounge | 397 | 26 |  | 419 | 9 | 9 | Univent and Air Handling Unit | 3352 | 7.1062 | 2 | 7.1062 | 2
128 | Workroom | 154 | 10 |  | 285 | 6 | 6 | Air Handling Unit | 2280 | 4.0526 | 2 | 4.0526 | 2
132 | BE Office | 78 | 5 |  | 135 | 3 | 3 | Air Handling Unit | 1080 | 4.3333 | 2 | 4.3333 | 2
200E | IMC | 60 | 4 |  | 80 | 1 | 1 | Air Handling Unit | 640 | 5.625 | 2 | 5.625 | 2
200F | CONF ROOM | 325 | 21 |  | 352 | 8 | 8 | Univent | 2816 | 6.9247 | 2 | 6.9247 | 2
201 | Classsroom | 425 | 28 |  | 814 | 18 | 18 | Univent and Air Handling Unit | 6512 | 3.9158 | 1 | 3.9158 | 1
202 | Classsroom | 530 | 35 |  | 814 | 18 | 18 | Univent and Air Handling Unit | 6512 | 4.8833 | 2 | 4.8833 | 2
203 | Classsroom | 394 | 26 |  | 814 | 18 | 18 | Univent and Air Handling Unit | 6512 | 3.6302 | 1 | 3.6302 | 1
204 | Classsroom | 517 | 34 |  | 814 | 18 | 18 | Univent and Air Handling Unit | 6512 | 4.7635 | 2 | 4.7635 | 2
205 | Classsroom | 432 | 28 |  | 810 | 18 | 18 | Univent and Air Handling Unit | 6480 | 4 | 1 | 4 | 1
206 | Classsroom | 407 | 27 |  | 812 | 18 | 18 | Univent and Air Handling Unit | 6496 | 3.7592 | 1 | 3.7592 | 1
207 | Classsroom | 368 | 24 |  | 685 | 15 | 15 | Univent and Air Handling Unit | 5480 | 4.0292 | 2 | 4.0292 | 2
208 | ART | 479 | 31 |  | 1059 | 24 | 24 | Univent | 8472 | 3.3924 | 1 | 3.3924 | 1
209 | Classsroom | 379 | 25 |  | 807 | 18 | 18 | Univent and Air Handling Unit | 6456 | 3.5223 | 1 | 3.5223 | 1
210 | Classsroom | 382 | 25 |  | 820 | 18 | 18 | Univent and Air Handling Unit | 6560 | 3.4939 | 1 | 3.4939 | 1
211 | Classsroom | 389 | 25 |  | 821 | 18 | 18 | Univent and Air Handling Unit | 6568 | 3.5536 | 1 | 3.5536 | 1
212 | Classsroom | 375 | 25 |  | 814 | 18 | 18 | Univent and Air Handling Unit | 6512 | 3.4552 | 1 | 3.4552 | 1
213 | Classsroom | 392 | 26 |  | 814 | 18 | 18 | Univent and Air Handling Unit | 6512 | 3.6118 | 1 | 3.6118 | 1
214 | Classsroom | 382 | 25 |  | 811 | 18 | 18 | Univent and Air Handling Unit | 6488 | 3.5327 | 1 | 3.5327 | 1
215 | Classsroom | 420 | 28 |  | 811 | 18 | 18 | Univent and Air Handling Unit | 6488 | 3.8841 | 1 | 3.8841 | 1
216 | Classsroom | 301 | 20 |  | 811 | 18 | 18 | Univent and Air Handling Unit | 6488 | 2.7836 | 1 | 2.7836 | 1
217 | Classsroom | 411 | 27 |  | 811 | 18 | 18 | Univent and Air Handling Unit | 6488 | 3.8009 | 1 | 3.8009 | 1
221 | Classroom | 301 | 20 |  | 658 | 14 | 14 | Univent | 5264 | 3.4309 | 1 | 3.4309 | 1
223 | Classroom | 357 | 23 |  | 887 | 20 | 20 | Univent and Air Handling Unit | 7096 | 3.0186 | 1 | 3.0186 | 1
224 | Classroom | 585 | 39 |  | 1410 | 32 | 32 | Univent and Air Handling Unit | 11280 | 3.1117 | 1 | 3.1117 | 1
225 | Classroom | 175 | 11 |  | 1267 | 28 | 11 | Univent and Air Handling Unit | 10136 | 1.0359 | 1 | 1.0359 | 1
- | Auditorium | 3411 | 227 |  | 2755 | 62 | 62 | Air Handling Unit | 22040 | 9.2858 | 2 | 9.2858 | 2
- | Cafeteria | 2559 | 170 |  | 5041 | 114 | 114 | Air Handling Unit | 40328 | 3.8073 | 1 | 3.8073 | 1
- | Gym | 2627 | 175 |  | 5960 | 135 | 135 | Air Handling Unit | 47680 | 3.3058 | 1 | 3.3058 | 1
- | LIBRARY | 514 | 34 |  | 2639 | 59 | 34 | Air Handling Unit | 21112 | 1.4608 | 1 | 1.4608 | 1
- | Lobby | 1166 | 77 |  | 3402 | 77 | 77 | Air Handling Unit | 27216 | 2.5705 | 1 | 2.5705 | 1
- | Main Office | 236 | 15 |  | 1165 | 26 | 15 | Air Handling Unit | 9320 | 1.5193 | 1 | 1.5193 | 1
Willard Annex | [9 empty] | unk | unk | unk | unk
#1 | Classroom | 334 | 22 |  | 828 | 18 | 18 | Rooftop Unit | 6624 | 3.0254 | 1 | 3.0254 | 1
#2 | Classroom | 534 | 35 |  | 828 | 18 | 18 | Rooftop Unit | 6624 | 4.837 | 2 | 4.837 | 2
#3 | Classroom | 667 | 44 |  | 828 | 18 | 18 | Rooftop Unit | 6624 | 6.0417 | 2 | 6.0417 | 2
#4 | Classroom | 595 | 39 |  | 828 | 18 | 18 | Rooftop Unit | 6624 | 5.3895 | 2 | 5.3895 | 2
#5 | Classroom | 453 | 30 |  | 828 | 18 | 18 | Rooftop Unit | 6624 | 4.1033 | 2 | 4.1033 | 2
#6 | Classroom | 1118 | 74 |  | 828 | 18 | 18 | Rooftop Unit | 6624 | 10.1268 | 3 | 10.1268 | 3
- | Admin Desk/Office | 402 | 26 |  | 180 | 4 | 4 | Rooftop Unit | 1440 | 16.75 | 3 | 16.75 | 3
- | Entrance Hallway | 93 | 6 |  | N/A | 0 | 0 | Rooftop Unit |  | unk | unk | unk | unk
- | Kitchen | 123 | 8 |  | 180 | 4 | 4 | Rooftop Unit | 1440 | 5.125 | 2 | 5.125 | 2
- | Office Space | 29 | 1 |  | 200 | 4 | 1 | Rooftop Unit | 1600 | 1.0875 | 1 | 1.0875 | 1
- | Play Area | 2452 | 163 |  | 1228 | 27 | 27 | Rooftop Unit | 9824 | 14.9756 | 3 | 14.9756 | 3
- | Principals Office | 257 | 17 |  | 120 | 2 | 2 | Rooftop Unit | 960 | 16.0625 | 3 | 16.0625 | 3
- | BE Office | 362 | 24 |  | 195 | 4 | 4 | Rooftop Unit | 1560 | 13.9231 | 3 | 13.9231 | 3
- | Health/Teachers Lounge | 0 | 0 |  | 240 | 5 | 0 | Univent | 1920 | 0 | 0 | 0 | 0
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | Woodrow Wilson Middle School | [8 empty] | unk | unk | unk | unk
Vendor: | Capital | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Classroom | 693 | 46 |  | 1080 | 24 | 24 | Air Handling Unit | 8640 | 4.8125 | 2 | 4.8125 | 2
102 | Classroom | 429 | 28 |  | 853 | 19 | 19 | Air Handling Unit | 6824 | 3.772 | 1 | 3.772 | 1
103 | Classroom | 962 | 64 |  | 672 | 15 | 15 | Air Handling Unit | 5376 | 10.7366 | 3 | 10.7366 | 3
104 | Room |  | 0 |  | 616 | 14 | 0 | Air Handling Unit | 4928 | unk | unk | unk | unk
105 | Classroom | 540 | 36 |  | 1038 | 23 | 23 | Air Handling Unit | 8304 | 3.9017 | 1 | 3.9017 | 1
107 | Classroom | 882 | 58 |  | 968 | 22 | 22 | Air Handling Unit | 7744 | 6.8337 | 2 | 6.8337 | 2
108 | Room |  | 0 |  | 352 | 8 | 0 | Air Handling Unit | 2816 | unk | unk | unk | unk
109 | Classroom | 506 | 33 |  | 374 | 8 | 8 | Air Handling Unit | 2992 | 10.1471 | 3 | 10.1471 | 3
110 | Room |  | 0 |  | 660 | 15 | 0 | Air Handling Unit | 5280 | unk | unk | unk | unk
111 | Classroom | 277 | 18 |  | 812 | 18 | 18 | Air Handling Unit | 6496 | 2.5585 | 1 | 2.5585 | 1
112 | Classroom | 271 | 18 |  | 954 | 21 | 18 | Air Handling Unit | 7632 | 2.1305 | 1 | 2.1305 | 1
116 | Classroom | 143 | 9 |  | 697 | 15 | 9 | Air Handling Unit | 5576 | 1.5387 | 1 | 1.5387 | 1
117 | Classroom | 191 | 12 |  | 697 | 15 | 12 | Air Handling Unit | 5576 | 2.0552 | 1 | 2.0552 | 1
118 | Classroom | 146 | 9 |  | 697 | 15 | 9 | Air Handling Unit | 5576 | 1.571 | 1 | 1.571 | 1
119 | Classroom | 98 | 6 |  | 349 | 7 | 6 | Air Handling Unit | 2792 | 2.106 | 1 | 2.106 | 1
201 | Classroom | 0 | 0 | Yes | 727 | 16 | 16 | Air Handling Unit | 5816 | 0 | 0 | 20 | 3
202 | Classroom | 338 | 22 |  | 687 | 15 | 15 | Air Handling Unit | 5496 | 3.69 | 1 | 3.69 | 1
203 | Classroom | 451 | 30 |  | 726 | 16 | 16 | Air Handling Unit | 5808 | 4.6591 | 2 | 4.6591 | 2
204 | Office |  | 0 | Yes | 160 | 3 | 3 | Air Handling Unit | 1280 | unk | unk | 20 | 3
205 | Classroom | 311 | 20 |  | 348 | 7 | 7 | Air Handling Unit | 2784 | 6.7026 | 2 | 6.7026 | 2
206 | Classroom | 452 | 30 |  | 324 | 7 | 7 | Air Handling Unit | 2592 | 10.463 | 3 | 10.463 | 3
207 | Room |  | 0 |  | 308 | 7 | 0 | Air Handling Unit | 2464 | unk | unk | unk | unk
208-C | Main Office |  | 0 |  | 572 | 13 | 0 | Air Handling Unit | 4576 | unk | unk | unk | unk
209 | Classroom | 765 | 51 |  | 901 | 20 | 20 | Air Handling Unit | 7208 | 6.3679 | 2 | 6.3679 | 2
210 | Classroom | 394 | 26 |  | 1034 | 23 | 23 | Air Handling Unit | 8272 | 2.8578 | 1 | 2.8578 | 1
211 | Classroom | 356 | 23 |  | 849 | 19 | 19 | Air Handling Unit | 6792 | 3.1449 | 1 | 3.1449 | 1
212 | Classroom | 318 | 21 |  | 867 | 19 | 19 | Air Handling Unit | 6936 | 2.7509 | 1 | 2.7509 | 1
213 | Classroom | 213 | 14 |  | 687 | 15 | 14 | Air Handling Unit | 5496 | 2.3253 | 1 | 2.3253 | 1
214 | Classroom | 596 | 39 |  | 727 | 16 | 16 | Air Handling Unit | 5816 | 6.1486 | 2 | 6.1486 | 2
215 | Classroom | 1059 | 70 |  | 668 | 15 | 15 | Air Handling Unit | 5344 | 11.89 | 3 | 11.89 | 3
216 | Classroom | 1311 | 87 |  | 791 | 17 | 17 | Air Handling Unit | 6328 | 12.4305 | 3 | 12.4305 | 3
217 | Classroom | 1097 | 73 |  | 682 | 15 | 15 | Air Handling Unit | 5456 | 12.0638 | 3 | 12.0638 | 3
218 | Classroom | 810 | 54 |  | 702 | 15 | 15 | Air Handling Unit | 5616 | 8.6538 | 2 | 8.6538 | 2
219 | Classroom | 1352 | 90 |  | 700 | 15 | 15 | Air Handling Unit | 5600 | 14.4857 | 3 | 14.4857 | 3
220 | Classroom | 1207 | 80 |  | 682 | 15 | 15 | Air Handling Unit | 5456 | 13.2735 | 3 | 13.2735 | 3
221 | Classroom | 897 | 59 |  | 791 | 17 | 17 | Air Handling Unit | 6328 | 8.5051 | 2 | 8.5051 | 2
222 | Classroom | 608 | 40 |  | 668 | 15 | 15 | Air Handling Unit | 5344 | 6.8263 | 2 | 6.8263 | 2
223 | Classroom | 305 | 20 |  | 347 | 7 | 7 | Air Handling Unit | 2776 | 6.5922 | 2 | 6.5922 | 2
224 | Room |  | 0 |  | 308 | 7 | 0 | Air Handling Unit | 2464 | unk | unk | unk | unk
226 | Classroom | 86 | 5 |  | 216 | 4 | 4 | Air Handling Unit | 1728 | 2.9861 | 1 | 2.9861 | 1
227 | Classroom | 163 | 10 |  | 347 | 7 | 7 | Air Handling Unit | 2776 | 3.5231 | 1 | 3.5231 | 1
228 | Classroom | 208 | 13 |  | 694 | 15 | 13 | Air Handling Unit | 5552 | 2.2478 | 1 | 2.2478 | 1
245 | Room |  | 0 | Yes | 87 | 1 | 1 | Air Handling Unit | 696 | unk | unk | 20 | 3
246 | Room |  | 0 | Yes | 82 | 1 | 1 | Air Handling Unit | 656 | unk | unk | 20 | 3
247 | Room |  | 0 | Yes | 110 | 2 | 2 | Air Handling Unit | 880 | unk | unk | 20 | 3
301 | Classroom | 813 | 54 |  | 727 | 16 | 16 | Air Handling Unit | 5816 | 8.3872 | 2 | 8.3872 | 2
302 | Classroom | 439 | 29 |  | 684 | 15 | 15 | Air Handling Unit | 5472 | 4.8136 | 2 | 4.8136 | 2
303 | Classroom | 605 | 40 |  | 697 | 15 | 15 | Air Handling Unit | 5576 | 6.51 | 2 | 6.51 | 2
304 | Classroom | 552 | 36 |  | 972 | 22 | 22 | Air Handling Unit | 7776 | 4.2593 | 2 | 4.2593 | 2
305 | Classroom | 518 | 34 |  | 914 | 20 | 20 | Air Handling Unit | 7312 | 4.2505 | 2 | 4.2505 | 2
306 | Classroom | 497 | 33 |  | 898 | 20 | 20 | Air Handling Unit | 7184 | 4.1509 | 2 | 4.1509 | 2
307 | Classroom | 781 | 52 |  | 965 | 21 | 21 | Air Handling Unit | 7720 | 6.0699 | 2 | 6.0699 | 2
308 | Classroom | 466 | 31 |  | 833 | 18 | 18 | Air Handling Unit | 6664 | 4.1957 | 2 | 4.1957 | 2
309 | Classroom | 735 | 49 |  | 894 | 20 | 20 | Air Handling Unit | 7152 | 6.1661 | 2 | 6.1661 | 2
309-A | Room |  | 0 |  | 220 | 5 | 0 | Air Handling Unit | 1760 | unk | unk | unk | unk
310 | Classroom | 765 | 51 |  | 924 | 21 | 21 | Air Handling Unit | 7392 | 6.2094 | 2 | 6.2094 | 2
311 | Classroom | 1322 | 88 |  | 958 | 21 | 21 | Air Handling Unit | 7664 | 10.3497 | 3 | 10.3497 | 3
312 | Classroom | 660 | 44 |  | 728 | 16 | 16 | Air Handling Unit | 5824 | 6.7995 | 2 | 6.7995 | 2
313 | Classroom | 403 | 26 |  | 313 | 7 | 7 | Air Handling Unit | 2504 | 9.6565 | 2 | 9.6565 | 2
2021-11-09 | Classroom | 1020 | 68 |  | 314 | 7 | 7 | Air Handling Unit | 2512 | 24.3631 | 4 | 24.3631 | 4
315 | Classroom | 1082 | 72 |  | 668 | 15 | 15 | Air Handling Unit | 5344 | 12.1482 | 3 | 12.1482 | 3
316 | Classroom | 1750 | 116 |  | 791 | 17 | 17 | Air Handling Unit | 6328 | 16.5929 | 3 | 16.5929 | 3
317 | Classroom | 2057 | 137 |  | 685 | 15 | 15 | Air Handling Unit | 5480 | 22.5219 | 3 | 22.5219 | 3
318 | Classroom | 1824 | 121 |  | 699 | 15 | 15 | Air Handling Unit | 5592 | 19.5708 | 3 | 19.5708 | 3
319 | Classroom | 1263 | 84 |  | 699 | 15 | 15 | Air Handling Unit | 5592 | 13.5515 | 3 | 13.5515 | 3
320 | Classroom | 642 | 42 |  | 684 | 15 | 15 | Air Handling Unit | 5472 | 7.0395 | 2 | 7.0395 | 2
321 | Classroom | 658 | 43 |  | 791 | 17 | 17 | Air Handling Unit | 6328 | 6.2389 | 2 | 6.2389 | 2
322 | Classroom | 508 | 33 |  | 668 | 15 | 15 | Air Handling Unit | 5344 | 5.7036 | 2 | 5.7036 | 2
323 | Classroom | 282 | 18 |  | 347 | 7 | 7 | Air Handling Unit | 2776 | 6.0951 | 2 | 6.0951 | 2
324 | Classroom | 127 | 8 |  | 694 | 15 | 8 | Air Handling Unit | 5552 | 1.3725 | 1 | 1.3725 | 1
327 | Room |  | 0 |  | 264 | 6 | 0 | Air Handling Unit | 2112 | unk | unk | unk | unk
328 | Classroom | 107 | 7 |  | 694 | 15 | 7 | Air Handling Unit | 5552 | 1.1563 | 1 | 1.1563 | 1
401 | Room |  | 0 |  | 264 | 6 | 0 | Rooftop Unit | 2112 | unk | unk | unk | unk
401A | Room |  | 0 |  | 572 | 13 | 0 | Rooftop Unit | 4576 | unk | unk | unk | unk
402 | Room |  | 0 |  | 836 | 19 | 0 | Rooftop Unit | 6688 | unk | unk | unk | unk
403 | Room |  | 0 |  | 1056 | 24 | 0 | Rooftop Unit | 8448 | unk | unk | unk | unk
404 | Room |  | 0 |  | 1188 | 27 | 0 | Rooftop Unit | 9504 | unk | unk | unk | unk
406 | Room |  | 0 |  | 44 | 1 | 0 | Rooftop Unit | 352 | unk | unk | unk | unk
407 | Room |  | 0 |  | 44 | 1 | 0 | Rooftop Unit | 352 | unk | unk | unk | unk
408 | Room |  | 0 |  | 44 | 1 | 0 | Rooftop Unit | 352 | unk | unk | unk | unk
409 | Room |  | 0 |  | 132 | 3 | 0 | Rooftop Unit | 1056 | unk | unk | unk | unk
410 | Counselor's Office |  | 0 | Yes | 165 | 3 | 3 | Rooftop Unit | 1320 | unk | unk | 20 | 3
- | Auditorium |  | 0 |  | 3740 | 85 | 0 | Air Handling Unit | 29920 | unk | unk | unk | unk
- | Gym 1 |  | 0 |  | 2816 | 64 | 0 | Air Handling Unit | 22528 | unk | unk | unk | unk
- | Gym 2 |  | 0 |  | 2816 | 64 | 0 | Air Handling Unit | 22528 | unk | unk | unk | unk
- | Lunchroom 1 |  | 0 |  | 2640 | 60 | 0 | Air Handling Unit | 21120 | unk | unk | unk | unk
- | Lunchroom 2 |  | 0 |  | 2596 | 59 | 0 | Air Handling Unit | 20768 | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-29 | [8 empty] | unk | unk | unk | unk
School: | Wister Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Mastery Charter Property Management | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Classroom | 307 | 20 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
101 | Classroom | 319 | 21 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
103 | Classroom | 148 | 9 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
106 | Lounge | 202 | 13 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
107A | Main Office | 0 | 0 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
108 | Classroom | 316 | 21 |  | 1134 | 25 | 21 | Unit Ventilator | 9072 | 2.0899 | 1 | 2.0899 | 1
109 | Classroom | 313 | 20 |  | 1094 | 24 | 20 | Unit Ventilator | 8752 | 2.1458 | 1 | 2.1458 | 1
110 | Storage | 215 | 14 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
111 | Classroom | 339 | 22 |  | 1414 | 32 | 22 | Unit Ventilator | 11312 | 1.7981 | 1 | 1.7981 | 1
200 | Classroom | 309 | 20 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
201 | Office | 162 | 10 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
202 | Classroom | 138 | 9 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
203 | Classroom | 311 | 20 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
204 | Classroom | 271 | 18 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
205 | Classroom | 144 | 9 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
206 | Classroom | 304 | 20 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
207 | Classroom | 304 | 20 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
208 | Classroom | 308 | 20 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
209C | Classroom | 337 | 22 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
210 | Classroom | 319 | 21 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
211 | Classroom | 302 | 20 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
212 | Classroom | 313 | 20 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
213 | Classroom | 331 | 22 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
214 | Classroom | 349 | 23 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
300 | Classroom | 299 | 19 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
301 | Office | 129 | 8 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
302 | Classroom | 153 | 10 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
303 | Classroom | 308 | 20 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
304 | Classroom | 330 | 22 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
305 | Classroom | 332 | 22 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
306 | Classroom | 311 | 20 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
307 | Classroom | 312 | 20 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
- | Auditorium | 2036 | 135 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
- | Gym | 1544 | 102 |  |  | 0 | 0 | AHU |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-03-17 | [8 empty] | unk | unk | unk | unk
School: | Sustainability Workshop School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | [8 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
101 | Corridor | 7 | 0 |  | 533 | 12 | 0 | VAV | 4264 | 0.098499 | 0 | 0.098499 | 0
102 | Closet | 6 | 0 |  | 45 | 1 | 0 | VAV | 360 | 1 | 0 | 1 | 0
105 | Nurses Office / Classroom |  | 0 |  | 150 | 3 | 0 | HU | 1200 | unk | unk | unk | unk
106 | Woodshop | 43 | 2 |  | 1003 | 22 | 2 | HU | 8024 | 0.32154 | 0 | 0.32154 | 0
110 | Classroom | 23 | 1 |  | 884 | 20 | 1 | VAV | 7072 | 0.19514 | 0 | 0.19514 | 0
111 | Auto Service | 0 | 0 |  | 1761 | 40 | 0 | HU and Univent | 14088 | 0 | 0 | 0 | 0
111 | Classroom |  | 0 |  | 756 | 17 | 0 | Univent | 6048 | unk | unk | unk | unk
112 | Training Classroom | 0 | 0 |  | 459 | 10 | 0 | HU and Univent | 3672 | 0 | 0 | 0 | 0
114 | Tool Storage | 0 | 0 |  | 450 | 10 | 0 | HU and Univent | 3600 | 0 | 0 | 0 | 0
117 | Body Shop | 0 | 0 |  | 2944 | 66 | 0 | HU | 23552 | 0 | 0 | 0 | 0
121 | Classroom |  | 0 |  | 729 | 16 | 0 | Univent | 5832 | unk | unk | unk | unk
200 | Corridor | 33 | 2 |  | 1868 | 42 | 2 | VAV | 14944 | 0.13249 | 0 | 0.13249 | 0
201 | Classroom | 42 | 2 |  | 740 | 16 | 2 | VAV | 5920 | 0.42568 | 0 | 0.42568 | 0
206 | Main Office | 7 | 0 |  | 234 | 5 | 0 | VAV | 1872 | 0.22436 | 0 | 0.22436 | 0
207 | Office | 6 | 0 |  | 192 | 4 | 0 | VAV | 1536 | 0.23438 | 0 | 0.23438 | 0
208 | Principle Office | 5 | 0 |  | 80 | 1 | 0 | VAV | 640 | 0.46875 | 0 | 0.46875 | 0
209 | Copy Room | 12 | 0 |  | 132 | 3 | 0 | VAV | 1056 | 0.68182 | 0 | 0.68182 | 0
210 | Classroom | 25 | 1 |  | 748 | 17 | 1 | VAV | 5984 | 0.25067 | 0 | 0.25067 | 0
210-C | Counselors office in front of classroom 210 | 2 | 0 |  | NA | 0 | 0 | VAV |  | unk | unk | unk | unk
212 | Mechanical room |  | 0 |  | 620 | 14 | 0 | AHU | 4960 | unk | unk | unk | unk
212 | Classroom | 366 | 24 |  | 720 | 16 | 16 | VAV | 5760 | 3.8125 | 1 | 3.8125 | 1
213 | Classroom | 1829 | 121 |  | 691 | 15 | 15 | VAV | 5528 | 19.8517 | 3 | 19.8517 | 3
214 | Classroom | 837 | 55 |  | 761 | 17 | 17 | VAV | 6088 | 8.249 | 2 | 8.249 | 2
215 | Classroom | 839 | 55 |  | 961 | 21 | 21 | VAV | 7688 | 6.5479 | 2 | 6.5479 | 2
215A | Classroom | 96 | 6 |  | NA | 0 | 0 | VAV |  | unk | unk | unk | unk
216 | Classroom | 655 | 43 |  | 1012 | 23 | 23 | VAV | 8096 | 4.8542 | 2 | 4.8542 | 2
219 | Corridor Bathroom | 40 | 2 |  | 48 | 1 | 1 | VAV | 384 | 6.25 | 2 | 6.25 | 2
- | Automotive Classroom | 0 | 0 |  | NA | 0 | 0 | HU and Univent |  | unk | unk | unk | unk
- | Body Shop Classroom | 0 | 0 |  | NA | 0 | 0 | Univent |  | unk | unk | unk | unk
- | Cafeteria Bathroom | 41 | 2 |  | 49 | 1 | 1 | VAV | 392 | 6.2755 | 2 | 6.2755 | 2
- | Cafeteria | 402 | 26 |  | 2550 | 57 | 26 | RTU | 20400 | 1.1824 | 1 | 1.1824 | 1
- | Computer Lab | 60 | 4 |  | 312 | 7 | 4 | HU | 2496 | 1.4423 | 1 | 1.4423 | 1
- | Kitchen | 0 | 0 |  | 504 | 11 | 0 | MUA | 4032 | 0 | 0 | 0 | 0
- | Mr. Boyd Office | 185 | 12 |  | 152 | 3 | 3 | VAV and RETURN DUCT | 1216 | 9.1283 | 2 | 9.1283 | 2
- | Mr. Tobias Office | 185 | 12 |  | 80 | 1 | 1 | VAV | 640 | 17.3438 | 3 | 17.3438 | 3
- | Mrs. Walker Office | 138 | 9 |  | 80 | 1 | 1 | VAV | 640 | 12.9375 | 3 | 12.9375 | 3
- | Ms. Phoebe Office | 188 | 12 |  | 91 | 2 | 2 | VAV | 728 | 15.4945 | 3 | 15.4945 | 3
- | Nurse Room | 0 | 0 |  | NA | 0 | 0 | HU and Univent |  | unk | unk | unk | unk
- | Storage / Office | 15 | 1 |  | 120 | 2 | 1 | RTU | 960 | 0.9375 | 0 | 0.9375 | 0
- | Woodshop Office | 43 | 2 |  | NA | 0 | 0 | HU |  | unk | unk | unk | unk
- | Woodshop Saw | 24 | 1 |  | NA | 0 | 0 | HU |  | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-04-30 | [8 empty] | unk | unk | unk | unk
School: | Richard R. Wright Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Goldner | Goldner Retest | [7 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
100 | Art Room | 280 | 18 | Yes | 1400 | 31 | 31 | Unit Ventilator | 11200 | 1.5 | 1 | 21.5 | 3
108-A | 1st Floor Gymnasium Office | 5 | 0 |  | 100 | 2 | 0 | Air Handling Unit | 800 | 0.375 | 0 | 0.375 | 0
112-A | 1st Floor Music Practice | 10 | 0 |  | 100 | 2 | 0 | Air Handling Unit | 800 | 0.75 | 0 | 0.75 | 0
112-B | 1st Floor Music Practice | 19 | 1 |  | 100 | 2 | 1 | Air Handling Unit | 800 | 1.425 | 1 | 1.425 | 1
114 | Classroom | 334 | 22 | Yes | 1360 | 30 | 30 | Unit Ventilator | 10880 | 1.8419 | 1 | 21.8419 | 3
115 | Classroom | 358 | 23 | Yes | 1360 | 30 | 30 | Unit Ventilator | 10880 | 1.9743 | 1 | 21.9743 | 3
118 | Nurse area | 0 | 0 | Yes | 378 | 8 | 8 | Unit Ventilator | 3024 | 0 | 0 | 20 | 3
119 | Nurse area | 0 | 0 | Yes | 216 | 4 | 4 | Unit Ventilator | 1728 | 0 | 0 | 20 | 3
120 | Classroom | 273 | 18 | Yes | 1360 | 30 | 30 | Unit Ventilator | 10880 | 1.5055 | 1 | 21.5055 | 3
121 | Classroom | 435 | 29 |  | 1360 | 30 | 29 | Unit Ventilator | 10880 | 2.3989 | 1 | 2.3989 | 1
122 | Classroom | 273 | 18 | Yes | 1360 | 30 | 30 | Unit Ventilator | 10880 | 1.5055 | 1 | 21.5055 | 3
201 | Classroom | 342 | 22 | Yes | 1610 | 36 | 36 | Unit Ventilator | 12880 | 1.5932 | 1 | 21.5932 | 3
202 | Classroom | 634 | 42 |  | 1702 | 38 | 38 | Unit Ventilator | 13616 | 2.7938 | 1 | 2.7938 | 1
203 | Classroom | 349 | 23 | Yes | 1120 | 25 | 25 | Unit Ventilator | 8960 | 2.3371 | 1 | 22.3371 | 3
204 | Classroom | 358 | 23 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
205 | Classroom | 482 | 32 |  | 870 | 19 | 19 | Unit Ventilator | 6960 | 4.1552 | 2 | 4.1552 | 2
206 | Classroom | 499 | 33 |  | 812 | 18 | 18 | Unit Ventilator | 6496 | 4.609 | 2 | 4.609 | 2
207 | Classroom | 460 | 30 |  | 870 | 19 | 19 | Unit Ventilator | 6960 | 3.9655 | 1 | 3.9655 | 1
208 | Classroom | 232 | 15 | Yes | 841 | 19 | 19 | Unit Ventilator | 6728 | 2.069 | 1 | 22.069 | 3
209 | Classroom | 341 | 22 |  |  | 0 | 0 | Unit Ventilator |  | unk | unk | unk | unk
210 | Classroom | 413 | 27 |  | 899 | 20 | 20 | Unit Ventilator | 7192 | 3.4455 | 1 | 3.4455 | 1
211 | Classroom | 270 | 18 | Yes | 1715 | 38 | 38 | Unit Ventilator | 13720 | 1.1808 | 1 | 21.1808 | 3
212 | Classroom | 434 | 28 | Yes | 1911 | 43 | 43 | Unit Ventilator | 15288 | 1.7033 | 1 | 21.7033 | 3
213 | Classroom | 310 | 20 | Yes | 1715 | 38 | 38 | Unit Ventilator | 13720 | 1.3557 | 1 | 21.3557 | 3
214 | Classroom | 799 | 53 |  | 1786 | 40 | 40 | Unit Ventilator | 14288 | 3.3553 | 1 | 3.3553 | 1
215 | Classroom | 325 | 21 |  | 870 | 19 | 19 | Unit Ventilator | 6960 | 2.8017 | 1 | 2.8017 | 1
216 | Classroom | 296 | 19 | Yes | 930 | 21 | 21 | Unit Ventilator | 7440 | 2.3871 | 1 | 22.3871 | 3
217 | Classroom | 568 | 37 |  | 870 | 19 | 19 | Unit Ventilator | 6960 | 4.8966 | 2 | 4.8966 | 2
218 | Classroom | 415 | 27 |  | 870 | 19 | 19 | Unit Ventilator | 6960 | 3.5776 | 1 | 3.5776 | 1
219 | Classroom | 289 | 19 |  | 870 | 19 | 19 | Unit Ventilator | 6960 | 2.4914 | 1 | 2.4914 | 1
220 | Classroom | 278 | 18 |  | 870 | 19 | 18 | Unit Ventilator | 6960 | 2.3966 | 1 | 2.3966 | 1
221 | Classroom | 339 | 22 |  | 899 | 20 | 20 | Unit Ventilator | 7192 | 2.8281 | 1 | 2.8281 | 1
222 | Classroom | 372 | 24 |  | 784 | 17 | 17 | Unit Ventilator | 6272 | 3.5587 | 1 | 3.5587 | 1
223 | Classroom | 369 | 24 | Yes | 1739 | 39 | 39 | Unit Ventilator | 13912 | 1.5914 | 1 | 21.5914 | 3
224 | Classroom | 284 | 18 | Yes | 1739 | 39 | 39 | Unit Ventilator | 13912 | 1.2248 | 1 | 21.2248 | 3
225 | Room | 211 | 14 |  | 196 | 4 | 4 | Air Handling Unit | 1568 | 8.074 | 2 | 8.074 | 2
227 | Room | 119 | 7 |  | 196 | 4 | 4 | Air Handling Unit | 1568 | 4.5536 | 2 | 4.5536 | 2
- | 1st Floor Conference Room | 89 | 5 |  | 108 | 2 |  | Air Handling Unit | 864 | 6.1806 | 2 | 6.1806 | 2
- | 1st Floor Counselor's Office | 17 | 1 |  | 100 | 2 |  | Air Handling Unit | 800 | 1.275 | 1 | 1.275 | 1
- | 1st Floor Engineer's Office | 30 | 2 |  | 36 | 0 |  | Air Handling Unit | 288 | 6.25 | 2 | 6.25 | 2
- | 1st Floor Entry Hallway | 79 | 5 |  | 140 | 3 |  | Air Handling Unit | 1120 | 4.2321 | 2 | 4.2321 | 2
- | 1st Floor CSC Office | 4 | 0 |  | 100 | 2 |  | Air Handling Unit | 800 | 0.3 | 0 | 0.3 | 0
- | 1st Floor IT Room | 10 | 0 |  | 100 | 2 |  | Air Handling Unit | 800 | 0.75 | 0 | 0.75 | 0
- | 1st Floor Main Office | 98 | 6 |  | 144 | 3 |  | Air Handling Unit | 1152 | 5.1042 | 2 | 5.1042 | 2
- | 1st Floor Office Storage | 0 | 0 |  | 160 | 3 |  | Air Handling Unit | 1280 | 0 | 0 | 0 | 0
- | 1st Floor Prinicpal's Office | 23 | 1 |  | 140 | 3 |  | Air Handling Unit | 1120 | 1.2321 | 1 | 1.2321 | 1
- | 1st Floor Psychologist's Office | 14 | 0 |  | 140 | 3 |  | Air Handling Unit | 1120 | 0.75 | 0 | 0.75 | 0
- | 1st Floor Small Kitchen | 56 | 3 |  | 84 | 1 |  | Air Handling Unit | 672 | 5 | 2 | 5 | 2
- | 1st Floor Staff Lounge | 447 | 29 |  | 1556 | 35 | 29 | Unit Ventilator | 12448 | 2.1546 | 1 | 2.1546 | 1
- | 2nd Floor Computer Storage | 44 | 2 |  | 196 | 4 | 2 | Air Handling Unit | 1568 | 1.6837 | 1 | 1.6837 | 1
- | 2nd Floor Library | 2489 | 165 |  | 556 | 12 | 12 | Air Handling Unit | 4448 | 33.5746 | 4 | 33.5746 | 4
- | 2nd Floor Library Lounge | 131 | 8 |  | 192 | 4 | 4 | Air Handling Unit | 1536 | 5.1172 | 2 | 5.1172 | 2
- | 2nd Floor Library Storage | 109 | 7 |  | 336 | 7 | 7 | Air Handling Unit | 2688 | 2.433 | 1 | 2.433 | 1
- | 2nd Floor Office space | 250 | 16 |  | 216 | 4 | 4 | Unit Ventilator | 1728 | 8.6806 | 2 | 8.6806 | 2
- | 2nd Floor Storage space | 358 | 23 |  | 432 | 9 | 9 | Unit Ventilator | 3456 | 6.2153 | 2 | 6.2153 | 2
- | Cafetorium | 4622 | 308 |  | 4730 | 107 | 107 | Air Handling Unit | 37840 | 7.3288 | 2 | 7.3288 | 2
- | Gym | 890 | 59 |  | 5644 | 128 | 59 | Air Handling Unit | 45152 | 1.1827 | 1 | 1.1827 | 1
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
[10 empty] | unk | unk | unk | unk
Sheet Last Modified: | 2021-05-03 | [8 empty] | unk | unk | unk | unk
School: | William H. Ziegler Elementary School | [8 empty] | unk | unk | unk | unk
Vendor: | Chadwick | Chadwick Part 2 | Chadwick Part 3 | [6 empty] | unk | unk | unk | unk
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [9 empty] | unk | unk | unk | unk
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit |  | unk | unk | unk | unk
102 | Classroom | 147 | 9 |  | 140 | 3 | 3 | Unit Ventilator | 1120 | 7.875 | 2 | 7.875 | 2
103 | Classroom | 309 | 20 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.7721 | 1 | 2.7721 | 1
104 | Classroom | 346 | 23 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 3.1041 | 1 | 3.1041 | 1
105 | Classroom | 296 | 19 |  | 836 | 19 | 19 | Unit Ventilator | 6688 | 2.6555 | 1 | 2.6555 | 1
106 | Office/Classroom |  | 0 | Yes | 322 | 7 | 7 | Unit Ventilator | 2576 | unk | unk | 20 | 3
107 | Classroom | 161 | 10 | Yes | 638 | 14 | 14 | Unit Ventilator | 5104 | 1.8926 | 1 | 21.8926 | 3
108 | Nurse |  | 0 | Yes | 171 | 3 | 3 | Unit Ventilator | 1368 | unk | unk | 20 | 3
109 | Classroom |  | 0 | Yes | 696 | 15 | 15 | Unit Ventilator | 5568 | unk | unk | 20 | 3
111 | Classroom | 331 | 22 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.64 | 1 | 3.64 | 1
112 | Classroom | 300 | 20 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.2991 | 1 | 3.2991 | 1
113 | Classroom | 338 | 22 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.717 | 1 | 3.717 | 1
114 | Classroom | 301 | 20 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.3101 | 1 | 3.3101 | 1
115 | Classroom | 312 | 20 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.4311 | 1 | 3.4311 | 1
116 | Classroom | 318 | 21 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.4971 | 1 | 3.4971 | 1
117 | Classroom | 318 | 21 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.4971 | 1 | 3.4971 | 1
125 | Classroom | 294 | 19 |  | 600 | 13 | 13 | Energy Recovery Unit | 4800 | 3.675 | 1 | 3.675 | 1
201 | Classroom | 398 | 26 |  | 598 | 13 | 13 | Unit Ventilator | 4784 | 4.9916 | 2 | 4.9916 | 2
202 | Classroom | 511 | 34 |  | 644 | 14 | 14 | Unit Ventilator | 5152 | 5.9511 | 2 | 5.9511 | 2
203 | Classroom |  | 0 | Yes | 390 | 8 | 8 | Unit Ventilator | 3120 | unk | unk | 20 | 3
204 | Classroom | 417 | 27 |  | 780 | 17 | 17 | Unit Ventilator | 6240 | 4.0096 | 2 | 4.0096 | 2
205 | Classroom | 315 | 21 |  | 962 | 21 | 21 | Unit Ventilator | 7696 | 2.4558 | 1 | 2.4558 | 1
206 | Classroom | 110 | 7 | Yes | 644 | 14 | 14 | Unit Ventilator | 5152 | 1.2811 | 1 | 21.2811 | 3
207 | Classroom |  | 0 | Yes | 243 | 5 | 5 | Unit Ventilator | 1944 | unk | unk | 20 | 3
208 | Teacher's Lounge |  | 0 | Yes | 280 | 6 | 6 | Unit Ventilator | 2240 | unk | unk | 20 | 3
210 | Classroom | 147 | 9 | Yes | 644 | 14 | 14 | Unit Ventilator | 5152 | 1.712 | 1 | 21.712 | 3
212 | Classroom | 534 | 35 |  | 667 | 15 | 15 | Unit Ventilator | 5336 | 6.0045 | 2 | 6.0045 | 2
213 | Classroom | 332 | 22 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.651 | 1 | 3.651 | 1
214 | Classroom | 166 | 11 | Yes | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 1.8255 | 1 | 21.8255 | 3
215 | Classroom | 281 | 18 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.0902 | 1 | 3.0902 | 1
216 | Classroom | 265 | 17 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 2.9142 | 1 | 2.9142 | 1
217 | Classroom | 261 | 17 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 2.8702 | 1 | 2.8702 | 1
218 | Classroom | 275 | 18 |  | 682 | 15 | 15 | Energy Recovery Unit | 5456 | 3.0242 | 1 | 3.0242 | 1
220 | Classroom | 269 | 17 |  | 748 | 17 | 17 | Energy Recovery Unit | 5984 | 2.6972 | 1 | 2.6972 | 1
- | Cafeteria | 2750 | 183 |  | 2736 | 62 | 62 | Air Handling Unit | 21888 | 7.5384 | 2 | 7.5384 | 2
- | Gymasium | 1073 | 71 |  | 3498 | 79 | 71 | Air Handling Unit | 27984 | 2.3006 | 1 | 2.3006 | 1
- | Hallway | 105 | 7 |  |  | 0 | 0 | Air Handling Unit |  | unk | unk | unk | unk
- | Library/IMC | 983 | 65 |  | 1953 | 44 | 44 | Air Handling Unit | 15624 | 3.775 | 1 | 3.775 | 1
- | Main Office |  | 0 | Yes | 456 | 10 | 10 | Unit Ventilator | 3648 | unk | unk | 20 | 3
- | Principal's Office |  | 0 | Yes | 198 | 4 | 4 | Unit Ventilator | 1584 | unk | unk | 20 | 3
- | Science Lab | 228 | 15 |  | 968 | 22 | 15 | Energy Recovery Unit | 7744 | 1.7665 | 1 | 1.7665 | 1