## Coversheet
Contagion Mitigation System Certification of Buildings
By Walter Sobkiw
2021-05-06
05/01/2020 origination
This research is not associated with any institution.
It is ongoing and part of a broader set of COVID-19 systems oriented research areas.
www.cassbeth.com/covid-19
Copyright 2021. This spreadsheet may be freely distributed and referenced as long as the author is clearly identified. When using this information product for critical review or significant public meetings the author must be contacted and made aware of the events. Any commercial publication or other works that will collect money from part or all of this content must contact the author to arrange for release.

## Philadelphia Schools
[15 empty] | AUC Range | Cert Level | # of Rooms | Mitigation Number of Rooms
[8 empty] | 22 | Auto | 8 | Space cu-ft | LS Factors |  |  | 120+ | 6 | 1 | 1
[8 empty] | 9 | All other | 8 | 400000 | 7.7491 |  |  | 50-100 | 5 | 25 | 25
[8 empty] | 40 | Indoor Pool | 8 | 300000 | 5.9427 |  |  | 24 | 4 | 75 | 103
Sheet Last Modified: | 2021-03-22 | [6 empty] | 22 | Gymnasium | 8 | 200000 | 4.14 |  |  | 10 to 24 | 3 | 467 | 2921 | 0 | 0 | 0 | 0 | Min
School: | Alexander Adaire Elementary School | House Fan Abated/Final Report | [5 empty] | 18 | Cafetorium | 8 | 100000 | 2.3523 |  |  | 4 to 10 | 2 | 2564 | 2537 | 0.67277 | 0.67277 | 0 | 0 | Min > 0
Vendor: | Chadwick | Devine | Devine Retest |  |  |  |  | 12 | Cafeteria | 8 | 50000 | 1.4912 |  |  | 1 to 4 | 1 | 4528 | 4140 | 327.3333 | 6 | 327.3333 | 6 | Max
Please visit https://bit.ly/3mA7rMY for more information on how to read this report. | [7 empty] | 9 | Classroom | 8 | 20000 | 1.062 |  |  | 0 - 1 | 0 | 5116 | 3049 | 3.0024 | 1 | 6.8947 | 2 | Average
[17 empty] | 12776 | 12776
[10 empty] | Rooms | 12842 | 2.9843 |  | 2.9991 |  | 6.8914 | Macro What If
|  | 4337033 |  | 2503 |  | 11608960.158 |  |  |  |  | 92871681.264 | 38484.77 |  | 38675.5575 |  | 88499.7976
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed | pAUC | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit | Ceiling Height Assumption ft | cu-ft | Total AUC | Large Room Factor | Final AUC | Cert Level | Mitigation AUC | Mitigation Cert Level
- | Auditorium | 2417 | 161 |  |  | 3234 | 73 | 73 | Air Handling Unit | 8 | 25872 | 5.6053 | 1.062 | 5.953 | 2 | 5.953 | 2
- | Gym/Cafeteria | 322 | 21 |  |  | 3432 | 78 | 21 | Air Handling Unit | 8 | 27456 | 0.70367 | 1.062 | 0.74732 | 0 | 0.74732 | 0
- | Main Ofiice | 161 | 10 |  |  | 468 | 10 | 10 | Unit Ventilator | 8 | 3744 | 2.5801 | 1 | 2.5801 | 1 | 2.5801 | 1
100 | Classroom | 452 | 30 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 3.5312 | 1 | 3.5312 | 1 | 3.5312 | 1
101 | Classroom | 480 | 32 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 3.75 | 1 | 3.75 | 1 | 3.75 | 1
102 | Classroom | 509 | 33 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 3.9766 | 1 | 3.9766 | 1 | 3.9766 | 1
103 | Classroom | 409 | 27 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 3.1953 | 1 | 3.1953 | 1 | 3.1953 | 1
104 | Classroom | 514 | 34 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 4.0156 | 1 | 4.0156 | 2 | 4.0156 | 2
105 | Classroom | 523 | 34 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 4.0859 | 1 | 4.0859 | 2 | 4.0859 | 2
106 | Classroom | 125 | 8 | Yes | 20 | 782 | 17 | 17 | Unit Ventilator | 8 | 6256 | 1.1988 | 1 | 1.1988 | 1 | 21.1988 | 3
107 | Classroom | 272 | 18 |  |  | 380 | 8 | 8 | Unit Ventilator | 8 | 3040 | 5.3684 | 1 | 5.3684 | 2 | 5.3684 | 2
108 | Faculty Room | 0 | 0 |  |  | 104 | 2 | 0 | Unit Ventilator | 8 | 832 | 0 | 1 | 0 | 0 | 0 | 0
109 | Classroom | 485 | 32 |  |  | 1470 | 33 | 32 | Unit Ventilator | 8 | 11760 | 2.4745 | 1 | 2.4745 | 1 | 2.4745 | 1
200 | Classroom | 546 | 36 |  |  | 912 | 20 | 20 | Unit Ventilator | 8 | 7296 | 4.4901 | 1 | 4.4901 | 2 | 4.4901 | 2
201 | Classroom | 607 | 40 |  |  | 912 | 20 | 20 | Unit Ventilator | 8 | 7296 | 4.9918 | 1 | 4.9918 | 2 | 4.9918 | 2
202 | Classroom | 613 | 40 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 4.9119 | 1 | 4.9119 | 2 | 4.9119 | 2
203 | Library | 593 | 39 |  |  | 1080 | 24 | 24 | Unit Ventilator | 8 | 8640 | 4.1181 | 1 | 4.1181 | 2 | 4.1181 | 2
204 | Classroom | 480 | 32 |  |  | 912 | 20 | 20 | Unit Ventilator | 8 | 7296 | 3.9474 | 1 | 3.9474 | 1 | 3.9474 | 1
205 | Classroom | 182 | 12 | Yes | 20 | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 1.4219 | 1 | 1.4219 | 1 | 21.4219 | 3
206 | Classroom | 317 | 21 |  |  | 984 | 22 | 21 | Unit Ventilator | 8 | 7872 | 2.4162 | 1 | 2.4162 | 1 | 2.4162 | 1
207 | Classroom | 798 | 53 |  |  | 456 | 10 | 10 | Unit Ventilator | 8 | 3648 | 13.125 | 1 | 13.125 | 3 | 13.125 | 3
208 | Classroom | 577 | 38 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 4.5078 | 1 | 4.5078 | 2 | 4.5078 | 2
209 | Classroom | 458 | 30 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 3.5781 | 1 | 3.5781 | 1 | 3.5781 | 1
210 | Classroom | 519 | 34 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 4.0547 | 1 | 4.0547 | 2 | 4.0547 | 2
211 | Classroom | 534 | 35 |  |  | 1008 | 22 | 22 | Unit Ventilator | 8 | 8064 | 3.9732 | 1 | 3.9732 | 1 | 3.9732 | 1
212 | Classroom | 1568 | 104 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 12.25 | 1 | 12.25 | 3 | 12.25 | 3
214 | Classroom | 340 | 22 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 2.6562 | 1 | 2.6562 | 1 | 2.6562 | 1
216 | Classroom | 617 | 41 |  |  | 456 | 10 | 10 | Unit Ventilator | 8 | 3648 | 10.148 | 1 | 10.148 | 3 | 10.148 | 3
218 | Classroom | 424 | 28 |  |  | 782 | 17 | 17 | Unit Ventilator | 8 | 6256 | 4.0665 | 1 | 4.0665 | 2 | 4.0665 | 2
Sheet Last Modified: | 2021-03-24
School: | Ethan Allen Elementary-Middle School
Vendor: | Devine | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B1 | Classroom | 545 | 36 |  |  | 736 | 16 | 16 | House Fan | 8 | 5888 | 5.5537 | 1 | 5.5537 | 2 | 5.5537 | 2
B2 | Classroom | 708 | 47 |  |  | 352 | 8 | 8 | House Fan | 8 | 2816 | 15.0852 | 1 | 15.0852 | 3 | 15.0852 | 3
B3 | Classroom | 421 | 28 |  |  | 506 | 11 | 11 | House Fan | 8 | 4048 | 6.2401 | 1 | 6.2401 | 2 | 6.2401 | 2
B4 | Classroom | 453 | 30 |  |  | 452 | 10 | 10 | House Fan | 8 | 3616 | 7.5166 | 1 | 7.5166 | 2 | 7.5166 | 2
- | Auditorium | 2183 | 145 |  |  | 3432 | 78 | 78 | House Fan | 8 | 27456 | 4.7705 | 1.062 | 5.0665 | 2 | 5.0665 | 2
- | Boys Basement Restroom | 130 | 8 |  |  | 383 | 8 | 8 | AC Bathroom | 8 | 3064 | 2.5457 | 1 | 2.5457 | 1 | 2.5457 | 1
- | Girls Basement Restroom | 787 | 52 |  |  | 524 | 11 | 11 | AC Bathroom | 8 | 4192 | 11.2643 | 1 | 11.2643 | 3 | 11.2643 | 3
101 | Classroom | 600 | 40 |  |  | 920 | 20 | 20 | House Fan | 8 | 7360 | 4.8913 | 1 | 4.8913 | 2 | 4.8913 | 2
102 | Classroom | 405 | 27 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 4.4022 | 1 | 4.4022 | 2 | 4.4022 | 2
103 | Classroom | 190 | 12 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 1.9361 | 1 | 1.9361 | 1 | 21.9361 | 3
104 | Classroom | 505 | 33 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 5.4891 | 1 | 5.4891 | 2 | 5.4891 | 2
105 | Classroom | 1216 | 81 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 13.2174 | 1 | 13.2174 | 3 | 13.2174 | 3
106 | Classroom | 1055 | 70 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 11.4674 | 1 | 11.4674 | 3 | 11.4674 | 3
107 | Classroom | 1312 | 87 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 14.2609 | 1 | 14.2609 | 3 | 14.2609 | 3
108 | Classroom | 1307 | 87 |  |  | 736 | 16 | 16 | House Fan | 8 | 5888 | 13.3186 | 1 | 13.3186 | 3 | 13.3186 | 3
109 | Classroom | 874 | 58 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 9.5 | 1 | 9.5 | 2 | 9.5 | 2
110 | Classroom | 1349 | 89 |  |  | 736 | 16 | 16 | House Fan | 8 | 5888 | 13.7466 | 1 | 13.7466 | 3 | 13.7466 | 3
210 | Classroom | 1375 | 91 |  |  | 736 | 16 | 16 | House Fan | 8 | 5888 | 14.0115 | 1 | 14.0115 | 3 | 14.0115 | 3
202 | Classroom | 298 | 19 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 3.2391 | 1 | 3.2391 | 1 | 3.2391 | 1
203 | Classroom | 209 | 13 |  |  | 736 | 16 | 13 | House Fan | 8 | 5888 | 2.1298 | 1 | 2.1298 | 1 | 2.1298 | 1
204 | Classroom | 373 | 24 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 4.0543 | 1 | 4.0543 | 2 | 4.0543 | 2
205 | Classroom | 574 | 38 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 6.2391 | 1 | 6.2391 | 2 | 6.2391 | 2
206 | Classroom | 580 | 38 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 6.3043 | 1 | 6.3043 | 2 | 6.3043 | 2
207 | Classroom | 919 | 61 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 9.9891 | 1 | 9.9891 | 2 | 9.9891 | 2
208 | Classroom | 1175 | 78 |  |  | 736 | 16 | 16 | House Fan | 8 | 5888 | 11.9735 | 1 | 11.9735 | 3 | 11.9735 | 3
209 | Classroom | 753 | 50 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 8.1848 | 1 | 8.1848 | 2 | 8.1848 | 2
210 | Classroom | 1638 | 109 |  |  | 736 | 16 | 16 | House Fan | 8 | 5888 | 16.6916 | 1 | 16.6916 | 3 | 16.6916 | 3
214 | Classroom |  | 0 | Yes | 20 | 341 | 7 | 7 | House Fan | 8 | 2728 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 880 | 58 |  |  | 736 | 16 | 16 | House Fan | 8 | 5888 | 8.9674 | 1 | 8.9674 | 2 | 8.9674 | 2
302 | Classroom | 319 | 21 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 3.4674 | 1 | 3.4674 | 1 | 3.4674 | 1
303 | Classroom | 74 | 4 |  |  | 736 | 16 | 4 | House Fan | 8 | 5888 | 0.75408 | 1 | 0.75408 | 0 | 0.75408 | 0
304 | Classroom | 141 | 9 |  |  | 690 | 15 | 9 | House Fan | 8 | 5520 | 1.5326 | 1 | 1.5326 | 1 | 1.5326 | 1
305 | Classroom | 151 | 10 |  |  | 690 | 15 | 10 | House Fan | 8 | 5520 | 1.6413 | 1 | 1.6413 | 1 | 1.6413 | 1
306 | Classroom | 268 | 17 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 2.913 | 1 | 2.913 | 1 | 2.913 | 1
307 | Classroom | 921 | 61 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 10.0109 | 1 | 10.0109 | 3 | 10.0109 | 3
308 | Classroom | 520 | 34 |  |  | 736 | 16 | 16 | House Fan | 8 | 5888 | 5.2989 | 1 | 5.2989 | 2 | 5.2989 | 2
309 | Classroom | 121 | 8 |  |  | 690 | 15 | 8 | House Fan | 8 | 5520 | 1.3152 | 1 | 1.3152 | 1 | 1.3152 | 1
310 | Classroom | 290 | 19 |  |  | 736 | 16 | 16 | House Fan | 8 | 5888 | 2.9552 | 1 | 2.9552 | 1 | 2.9552 | 1
314 | Classroom | 421 | 28 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 4.3854 | 1 | 4.3854 | 2 | 4.3854 | 2
- | Main Office |  | 0 | Yes | 20 | 309 | 7 | 7 | House Fan | 8 | 2472 | 0 | 1 | 0 | 0 | 20 | 3
- | Prinicipal Office |  | 0 | Yes | 20 | 177 | 4 | 4 | House Fan | 8 | 1416 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 186 | 4 | 4 | House Fan | 8 | 1488 | 0 | 1 | 0 | 0 | 20 | 3
- | Conselor Office |  | 0 | Yes | 20 | 177 | 4 | 4 | House Fan | 8 | 1416 | 0 | 1 | 0 | 0 | 20 | 3
- | Pyschologist Office |  | 0 | Yes | 20 | 108 | 2 | 2 | House Fan | 8 | 864 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 | Yes | 20 | 3422 | 77 | 77 | Hydroxyl Unit | 8 | 27376 | 0 | 1.062 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-16
School: | Dr. Ethel Allen Elementary School
Vendor: | Chadwick | Chadwick Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101-A | Classroom | 528 | 35 |  |  | 896 | 20 | 20 | Unit Ventilator | 8 | 7168 | 4.4196 | 1 | 4.4196 | 2 | 4.4196 | 2
101-B | Classroom | 100 | 6 |  |  | 1036 | 23 | 6 | Unit Ventilator | 8 | 8288 | 0.72394 | 1 | 0.72394 | 0 | 0.72394 | 0
102-A | Classroom | 70 | 4 |  |  | 1110 | 25 | 4 | Unit Ventilator | 8 | 8880 | 0.47297 | 1 | 0.47297 | 0 | 0.47297 | 0
102-B | Classroom | 485 | 32 |  |  | 1110 | 25 | 25 | Unit Ventilator | 8 | 8880 | 3.277 | 1 | 3.277 | 1 | 3.277 | 1
102-C | Classroom | 0 | 0 |  |  | 1110 | 25 | 0 | Unit Ventilator | 8 | 8880 | 0 | 1 | 0 | 0 | 0 | 0
102-D | Classroom |  | 0 |  |  | 1110 | 25 | 0 | Unit Ventilator | 8 | 8880 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom | 1233 | 82 | Yes | 20 | 2277 | 51 | 51 | Unit Ventilator | 8 | 18216 | 4.0613 | 1 | 4.0613 | 2 | 24.0613 | 4
103-A | Classroom | 76 | 5 |  |  |  | 0 | 0 | Unit Ventilator
104 | Classroom | 419 | 27 |  |  | 1260 | 28 | 27 | Unit Ventilator | 8 | 10080 | 2.494 | 1 | 2.494 | 1 | 2.494 | 1
105 | Classroom | 472 | 31 |  |  | 1260 | 28 | 28 | Unit Ventilator | 8 | 10080 | 2.8095 | 1 | 2.8095 | 1 | 2.8095 | 1
106 | Classroom | 152 | 10 |  |  | 1184 | 26 | 10 | Unit Ventilator | 8 | 9472 | 0.96284 | 1 | 0.96284 | 0 | 0.96284 | 0
107 | Classroom |  | 0 |  |  | 1260 | 28 | 0 | Unit Ventilator | 8 | 10080 | 0 | 1 | 0 | 0 | 0 | 0
109 | Classroom | 172 | 11 | Yes | 20 | 1260 | 28 | 28 | Unit Ventilator | 8 | 10080 | 1.0238 | 1 | 1.0238 | 1 | 21.0238 | 3
110 | Classroom |  | 0 |  |  | 1036 | 23 | 0 | Unit Ventilator | 8 | 8288 | 0 | 1 | 0 | 0 | 0 | 0
112 | Classroom | 29 | 1 |  |  | 1056 | 24 | 1 | Unit Ventilator | 8 | 8448 | 0.20597 | 1 | 0.20597 | 0 | 0.20597 | 0
113 | Classroom | 26 | 1 |  |  | 1056 | 24 | 1 | Unit Ventilator | 8 | 8448 | 0.18466 | 1 | 0.18466 | 0 | 0.18466 | 0
114 | Classroom | 380 | 25 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 2.6989 | 1 | 2.6989 | 1 | 2.6989 | 1
200 | Classroom | 511 | 34 |  |  | 1500 | 34 | 34 | Unit Ventilator | 8 | 12000 | 2.555 | 1 | 2.555 | 1 | 2.555 | 1
200C | Classroom | 0 | 0 | Yes | 20 | 784 | 17 | 17 | Unit Ventilator | 8 | 6272 | 0 | 1 | 0 | 0 | 20 | 3
201B | Classroom |  | 0 |  |  | 840 | 19 | 0 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
202 | Classroom | 367 | 24 |  |  | 983 | 22 | 22 | Unit Ventilator | 8 | 7864 | 2.8001 | 1 | 2.8001 | 1 | 2.8001 | 1
202 | Classroom |  | 0 |  |  |  | 0 | 0 | Unit Ventilator
203A | Classroom |  | 0 |  |  | 1036 | 23 | 0 | Unit Ventilator | 8 | 8288 | 0 | 1 | 0 | 0 | 0 | 0
203B | Classroom |  | 0 |  |  | 1036 | 23 | 0 | Unit Ventilator | 8 | 8288 | 0 | 1 | 0 | 0 | 0 | 0
203C | Classroom |  | 0 |  |  | 1036 | 23 | 0 | Unit Ventilator | 8 | 8288 | 0 | 1 | 0 | 0 | 0 | 0
203D | Classroom |  | 0 |  |  | 1036 | 23 | 0 | Unit Ventilator | 8 | 8288 | 0 | 1 | 0 | 0 | 0 | 0
204 | Classroom | 525 | 35 |  |  | 980 | 22 | 22 | Unit Ventilator | 8 | 7840 | 4.0179 | 1 | 4.0179 | 2 | 4.0179 | 2
206 | Classroom | 194 | 12 |  |  | 1200 | 27 | 12 | Unit Ventilator | 8 | 9600 | 1.2125 | 1 | 1.2125 | 1 | 1.2125 | 1
206 | Classroom | 170 | 11 |  |  |  | 0 | 0 | Unit Ventilator
207A | Classroom |  | 0 |  |  | 1260 | 28 | 0 | Unit Ventilator | 8 | 10080 | 0 | 1 | 0 | 0 | 0 | 0
207B | Classroom |  | 0 |  |  | 1260 | 28 | 0 | Unit Ventilator | 8 | 10080 | 0 | 1 | 0 | 0 | 0 | 0
208A | Classroom | 108 | 7 |  |  | 1260 | 28 | 7 | Unit Ventilator | 8 | 10080 | 0.64286 | 1 | 0.64286 | 0 | 0.64286 | 0
208B | Classroom |  | 0 |  |  | 1260 | 28 | 0 | Unit Ventilator | 8 | 10080 | 0 | 1 | 0 | 0 | 0 | 0
208C | Classroom |  | 0 |  |  | 1260 | 28 | 0 | Unit Ventilator | 8 | 10080 | 0 | 1 | 0 | 0 | 0 | 0
209 | Classroom | 907 | 60 |  |  |  | 0 | 0 | Unit Ventilator
Sheet Last Modified: | 2021-04-29
School: | Add B. Anderson Elementary School
Vendor: | Devine Brothers | Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Auditorium | 5840 | 389 |  |  | 2589 | 58 | 58 | Air Handling Unit | 8 | 20712 | 16.9177 | 1.062 | 17.9672 | 3 | 17.9672 | 3
- | Gym | 2392 | 159 |  |  | 2200 | 50 | 50 | Air Handling Unit | 8 | 17600 | 8.1545 | 1 | 8.1545 | 2 | 8.1545 | 2
- | Main Office | 84 | 5 | Yes | 20 | 451 | 10 | 10 | Unit Ventilator | 8 | 3608 | 1.3969 | 1 | 1.3969 | 1 | 21.3969 | 3
- | Principal's Office |  | 0 | Yes | 20 | 350 | 7 | 7 | Convector | 8 | 2800 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse's Office |  | 0 | Yes | 20 | 350 | 7 | 7 | Convector | 8 | 2800 | 0 | 1 | 0 | 0 | 20 | 3
- | Stage | 2534 | 168 |  |  | 1008 | 22 | 22 | Air Handling Unit | 8 | 8064 | 18.8542 | 1 | 18.8542 | 3 | 18.8542 | 3
100 | Classroom | 281 | 18 |  |  | 467 | 10 | 10 | Unit Ventilator | 8 | 3736 | 4.5128 | 1 | 4.5128 | 2 | 4.5128 | 2
101 | Classroom | 32 | 2 |  |  | 355 | 8 | 2 | Unit Ventilator | 8 | 2840 | 0.67606 | 1 | 0.67606 | 0 | 0.67606 | 0
102 | Classroom | 102 | 6 | Yes | 20 | 540 | 12 | 12 | Unit Ventilator | 8 | 4320 | 1.4167 | 1 | 1.4167 | 1 | 21.4167 | 3
103 | Classroom | 40 | 2 | Yes | 20 | 628 | 14 | 14 | Unit Ventilator | 8 | 5024 | 0.47771 | 1 | 0.47771 | 0 | 20.4777 | 3
104 | Classroom | 287 | 19 |  |  | 395 | 8 | 8 | Unit Ventilator | 8 | 3160 | 5.4494 | 1 | 5.4494 | 2 | 5.4494 | 2
105 | Classroom | 295 | 19 |  |  | 521 | 11 | 11 | Unit Ventilator | 8 | 4168 | 4.2466 | 1 | 4.2466 | 2 | 4.2466 | 2
106 | Classroom | 290 | 19 |  |  | 446 | 10 | 10 | Unit Ventilator | 8 | 3568 | 4.8767 | 1 | 4.8767 | 2 | 4.8767 | 2
108 | Classroom | 283 | 18 |  |  | 405 | 9 | 9 | Unit Ventilator | 8 | 3240 | 5.2407 | 1 | 5.2407 | 2 | 5.2407 | 2
200 | Classroom | 82 | 5 | Yes | 20 | 476 | 10 | 10 | Unit Ventilator | 8 | 3808 | 1.292 | 1 | 1.292 | 1 | 21.292 | 3
201 | Classroom | 128 | 8 | Yes | 20 | 627 | 14 | 14 | Unit Ventilator | 8 | 5016 | 1.5311 | 1 | 1.5311 | 1 | 21.5311 | 3
202 | Classroom | 408 | 27 |  |  | 576 | 13 | 13 | Unit Ventilator | 8 | 4608 | 5.3125 | 1 | 5.3125 | 2 | 5.3125 | 2
204 | Classroom | 323 | 21 |  |  | 683 | 15 | 15 | Unit Ventilator | 8 | 5464 | 3.5469 | 1 | 3.5469 | 1 | 3.5469 | 1
205 | Classroom | 80 | 5 | Yes | 20 | 658 | 14 | 14 | Unit Ventilator | 8 | 5264 | 0.91185 | 1 | 0.91185 | 0 | 20.9119 | 3
206 | Classroom | 329 | 21 |  |  | 637 | 14 | 14 | Unit Ventilator | 8 | 5096 | 3.8736 | 1 | 3.8736 | 1 | 3.8736 | 1
207 | Classroom | 82 | 5 | Yes | 20 | 587 | 13 | 13 | Unit Ventilator | 8 | 4696 | 1.0477 | 1 | 1.0477 | 1 | 21.0477 | 3
208 | Classroom | 129 | 8 | Yes | 20 | 720 | 16 | 16 | Unit Ventilator | 8 | 5760 | 1.3438 | 1 | 1.3438 | 1 | 21.3438 | 3
209 | Classroom | 305 | 20 |  |  | 629 | 14 | 14 | Unit Ventilator | 8 | 5032 | 3.6367 | 1 | 3.6367 | 1 | 3.6367 | 1
210 | Classroom | 41 | 2 |  |  | 241 | 5 | 2 | Unit Ventilator | 8 | 1928 | 1.2759 | 1 | 1.2759 | 1 | 1.2759 | 1
211 | Classroom | 56 | 3 |  |  | 385 | 8 | 3 | Unit Ventilator | 8 | 3080 | 1.0909 | 1 | 1.0909 | 1 | 1.0909 | 1
212 | Classroom | 319 | 21 |  |  | 603 | 13 | 13 | Unit Ventilator | 8 | 4824 | 3.9677 | 1 | 3.9677 | 1 | 3.9677 | 1
213 | Classroom | 49 | 3 | Yes | 20 | 290 | 6 | 6 | Unit Ventilator | 8 | 2320 | 1.2672 | 1 | 1.2672 | 1 | 21.2672 | 3
214 | Classroom | 112 | 7 | Yes | 20 | 741 | 16 | 16 | Unit Ventilator | 8 | 5928 | 1.1336 | 1 | 1.1336 | 1 | 21.1336 | 3
300 | Classroom | 35 | 2 | Yes | 20 | 947 | 21 | 21 | Unit Ventilator | 8 | 7576 | 0.27719 | 1 | 0.27719 | 0 | 20.2772 | 3
301 | Classroom | 63 | 4 | Yes | 20 | 900 | 20 | 20 | Unit Ventilator | 8 | 7200 | 0.525 | 1 | 0.525 | 0 | 20.525 | 3
302 | Classroom | 87 | 5 | Yes | 20 | 588 | 13 | 13 | Unit Ventilator | 8 | 4704 | 1.1097 | 1 | 1.1097 | 1 | 21.1097 | 3
303 | Classroom | 85 | 5 | Yes | 20 | 571 | 12 | 12 | Unit Ventilator | 8 | 4568 | 1.1165 | 1 | 1.1165 | 1 | 21.1165 | 3
304 | Classroom | 293 | 19 |  |  | 431 | 9 | 9 | Unit Ventilator | 8 | 3448 | 5.0986 | 1 | 5.0986 | 2 | 5.0986 | 2
305 | Classroom | 58 | 3 | Yes | 20 | 504 | 11 | 11 | Unit Ventilator | 8 | 4032 | 0.8631 | 1 | 0.8631 | 0 | 20.8631 | 3
306 | Classroom | 286 | 19 |  |  | 415 | 9 | 9 | Unit Ventilator | 8 | 3320 | 5.1687 | 1 | 5.1687 | 2 | 5.1687 | 2
307 | Classroom | 97 | 6 | Yes | 20 | 501 | 11 | 11 | Unit Ventilator | 8 | 4008 | 1.4521 | 1 | 1.4521 | 1 | 21.4521 | 3
308 | Classroom | 79 | 5 | Yes | 20 | 686 | 15 | 15 | Unit Ventilator | 8 | 5488 | 0.8637 | 1 | 0.8637 | 0 | 20.8637 | 3
310 | Classroom | 106 | 7 | Yes | 20 | 592 | 13 | 13 | Unit Ventilator | 8 | 4736 | 1.3429 | 1 | 1.3429 | 1 | 21.3429 | 3
311 | Classroom | 53 | 3 | Yes | 20 | 441 | 10 | 10 | Unit Ventilator | 8 | 3528 | 0.90136 | 1 | 0.90136 | 0 | 20.9014 | 3
312 | Classroom | 18 | 1 | Yes | 20 | 465 | 10 | 10 | Unit Ventilator | 8 | 3720 | 0.29032 | 1 | 0.29032 | 0 | 20.2903 | 3
313 | Classroom | 72 | 4 | Yes | 20 | 463 | 10 | 10 | Unit Ventilator | 8 | 3704 | 1.1663 | 1 | 1.1663 | 1 | 21.1663 | 3
314 | Classroom | 61 | 4 | Yes | 20 | 533 | 12 | 12 | Unit Ventilator | 8 | 4264 | 0.85835 | 1 | 0.85835 | 0 | 20.8583 | 3
Sheet Last Modified: | 2021-04-30
School: | Chester A. Arthur Elementary School
Vendor: | Devine Retest | Devine 3rd Retest
| Devine 4th Retest | Devine 5th Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B001 | Classroom | 380 | 25 |  |  | 551 | 12 | 12 | Unit Ventilator | 8 | 4408 | 5.1724 | 1 | 5.1724 | 2 | 5.1724 | 2
B002 | Classroom | 0 | 0 |  |  | 100 | 2 | 0 | N/A | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
100 | Classroom | 309 | 20 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 2.9261 | 1 | 2.9261 | 1 | 2.9261 | 1
102 | Classroom | 335 | 22 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 3.1723 | 1 | 3.1723 | 1 | 3.1723 | 1
104 | Classroom | 295 | 19 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 2.7936 | 1 | 2.7936 | 1 | 2.7936 | 1
106 | Classroom | 346 | 23 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 3.2765 | 1 | 3.2765 | 1 | 3.2765 | 1
107A | Teacher's Lounge |  | 0 | Yes | 20 | 448 | 10 | 10 | Unit Ventilator | 8 | 3584 | 0 | 1 | 0 | 0 | 20 | 3
200 | Classroom | 335 | 22 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 3.1723 | 1 | 3.1723 | 1 | 3.1723 | 1
201 | Classroom | 304 | 20 |  |  | 364 | 8 | 8 | Unit Ventilator | 8 | 2912 | 6.2637 | 1 | 6.2637 | 2 | 6.2637 | 2
202 | Classroom | 320 | 21 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 3.0303 | 1 | 3.0303 | 1 | 3.0303 | 1
203 | Classroom | 299 | 19 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.5955 | 1 | 2.5955 | 1 | 2.5955 | 1
204 | Classroom | 333 | 22 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 3.1534 | 1 | 3.1534 | 1 | 3.1534 | 1
205 | Classroom | 374 | 24 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 3.2465 | 1 | 3.2465 | 1 | 3.2465 | 1
206 | Classroom | 280 | 18 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 2.6515 | 1 | 2.6515 | 1 | 2.6515 | 1
207 | Classroom | 341 | 22 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.9601 | 1 | 2.9601 | 1 | 2.9601 | 1
207A | Classroom |  | 0 | Yes | 20 | 425 | 9 | 9 | Unit Ventilator | 8 | 3400 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom | 311 | 20 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 2.9451 | 1 | 2.9451 | 1 | 2.9451 | 1
300 | Classroom | 293 | 19 |  |  | 857 | 19 | 19 | Unit Ventilator | 8 | 6856 | 2.5642 | 1 | 2.5642 | 1 | 2.5642 | 1
301 | Classroom | 273 | 18 |  |  | 364 | 8 | 8 | Unit Ventilator | 8 | 2912 | 5.625 | 1 | 5.625 | 2 | 5.625 | 2
302 | Classroom | 355 | 23 |  |  | 857 | 19 | 19 | Unit Ventilator | 8 | 6856 | 3.1068 | 1 | 3.1068 | 1 | 3.1068 | 1
303 | Classroom | 328 | 21 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.8472 | 1 | 2.8472 | 1 | 2.8472 | 1
304 | Classroom | 350 | 23 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 3.3144 | 1 | 3.3144 | 1 | 3.3144 | 1
305 | Classroom | 274 | 18 |  |  | 900 | 20 | 18 | Unit Ventilator | 8 | 7200 | 2.2833 | 1 | 2.2833 | 1 | 2.2833 | 1
306 | Classroom | 304 | 20 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 2.8788 | 1 | 2.8788 | 1 | 2.8788 | 1
307 | Classroom | 350 | 23 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 3.0382 | 1 | 3.0382 | 1 | 3.0382 | 1
307A | Classroom |  | 0 | Yes | 20 | 425 | 9 | 9 | Unit Ventilator | 8 | 3400 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom | 331 | 22 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 3.1345 | 1 | 3.1345 | 1 | 3.1345 | 1
- | Auditorium | 753 | 50 |  |  | 4335 | 98 | 50 | HV Unit | 8 | 34680 | 1.3028 | 1.062 | 1.3836 | 1 | 1.3836 | 1
- | Gym | 2466 | 164 |  |  | 3055 | 69 | 69 | HV Unit | 8 | 24440 | 6.054 | 1.062 | 6.4296 | 2 | 6.4296 | 2
- | IMC | 383 | 25 |  |  | 1472 | 33 | 25 | Unit Ventilator | 8 | 11776 | 1.9514 | 1 | 1.9514 | 1 | 1.9514 | 1
- | Resource Room/Storage | 0 | 0 | Yes | 20 | 300 | 6 | 6 | Unit Ventilator | 8 | 2400 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office | 401 | 26 |  |  | 1104 | 25 | 25 | Unit Ventilator | 8 | 8832 | 2.7242 | 1 | 2.7242 | 1 | 2.7242 | 1
- | BE Office | 63 | 4 |  |  | 240 | 5 | 4 | Unit Ventilator | 8 | 1920 | 1.9688 | 1 | 1.9688 | 1 | 1.9688 | 1
- | Nurse Office | 0 | 0 | Yes | 20 | 276 | 6 | 6 |  | 8 | 2208 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 20 | 240 | 5 | 5 |  | 8 | 1920 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-26
School: | Alexander D. Bache Elementary School | Bache Part 2
School: | W.E. Martin Building | Martin Part 2
Vendor: | EMCOR Fluidics
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Bache Building
1 | Classroom | 274 | 18 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 2.6758 | 1 | 2.6758 | 1 | 2.6758 | 1
2 | Classroom | 295 | 19 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 2.8809 | 1 | 2.8809 | 1 | 2.8809 | 1
3 | Classroom | 305 | 20 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 2.9785 | 1 | 2.9785 | 1 | 2.9785 | 1
4 | Classroom | 289 | 19 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 2.8223 | 1 | 2.8223 | 1 | 2.8223 | 1
5 | Classroom | 330 | 22 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 3.2227 | 1 | 3.2227 | 1 | 3.2227 | 1
6 | Classroom | 273 | 18 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 2.666 | 1 | 2.666 | 1 | 2.666 | 1
7 | Classroom | 312 | 20 |  |  | 528 | 12 | 12 | Unit Ventilator | 8 | 4224 | 4.4318 | 1 | 4.4318 | 2 | 4.4318 | 2
8 | Classroom | 406 | 27 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 3.9648 | 1 | 3.9648 | 1 | 3.9648 | 1
9 | Classroom | 455 | 30 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 4.4434 | 1 | 4.4434 | 2 | 4.4434 | 2
10 | Classroom | 400 | 26 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 3.9062 | 1 | 3.9062 | 1 | 3.9062 | 1
11 | Classroom | 346 | 23 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 3.3789 | 1 | 3.3789 | 1 | 3.3789 | 1
12 | Classroom | 388 | 25 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 3.7891 | 1 | 3.7891 | 1 | 3.7891 | 1
13 | Teacher's Lounge | 339 | 22 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 3.3105 | 1 | 3.3105 | 1 | 3.3105 | 1
14 | Classroom | 288 | 19 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 2.8125 | 1 | 2.8125 | 1 | 2.8125 | 1
15 | Classroom | 424 | 28 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 4.1406 | 1 | 4.1406 | 2 | 4.1406 | 2
16 | Library | 296 | 19 |  |  | 720 | 16 | 16 | Unit Ventilator | 8 | 5760 | 3.0833 | 1 | 3.0833 | 1 | 3.0833 | 1
17 | Library | 294 | 19 |  |  | 720 | 16 | 16 | Unit Ventilator | 8 | 5760 | 3.0625 | 1 | 3.0625 | 1 | 3.0625 | 1
18 | Classroom | 338 | 22 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 3.3008 | 1 | 3.3008 | 1 | 3.3008 | 1
19 | Classroom | 114 | 7 | Yes | 20 | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 1.1133 | 1 | 1.1133 | 1 | 21.1133 | 3
20 | Classroom | 302 | 20 |  |  | 720 | 16 | 16 | Unit Ventilator | 8 | 5760 | 3.1458 | 1 | 3.1458 | 1 | 3.1458 | 1
21 | Classroom | 278 | 18 |  |  | 704 | 16 | 16 | Unit Ventilator | 8 | 5632 | 2.9616 | 1 | 2.9616 | 1 | 2.9616 | 1
22 | Classroom | 328 | 21 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 3.7273 | 1 | 3.7273 | 1 | 3.7273 | 1
23 | Classroom | 360 | 24 |  |  | 704 | 16 | 16 | Unit Ventilator | 8 | 5632 | 3.8352 | 1 | 3.8352 | 1 | 3.8352 | 1
24 | Classroom | 347 | 23 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 3.9432 | 1 | 3.9432 | 1 | 3.9432 | 1
25 | Classroom | 377 | 25 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 3.6816 | 1 | 3.6816 | 1 | 3.6816 | 1
26 | Classroom | 381 | 25 |  |  | 720 | 16 | 16 | Unit Ventilator | 8 | 5760 | 3.9688 | 1 | 3.9688 | 1 | 3.9688 | 1
27 | Classroom | 436 | 29 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 4.2578 | 1 | 4.2578 | 2 | 4.2578 | 2
- | Cafeteria | 0 | 0 | Yes | 20 | 1891 | 42 | 42 | Unit Ventilator | 8 | 15128 | 0 | 1 | 0 | 0 | 20 | 3
Martin Building | 0
101 | Classroom | 405 | 27 |  |  | 713 | 16 | 16 | Unit Ventilator | 8 | 5704 | 4.2602 | 1 | 4.2602 | 2 | 4.2602 | 2
102 | Classroom | 415 | 27 |  |  | 713 | 16 | 16 | Unit Ventilator | 8 | 5704 | 4.3654 | 1 | 4.3654 | 2 | 4.3654 | 2
103 | Classroom | 308 | 20 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 3.5 | 1 | 3.5 | 1 | 3.5 | 1
104 | Classroom | 289 | 19 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 2.8223 | 1 | 2.8223 | 1 | 2.8223 | 1
105 | Classroom | 355 | 23 |  |  | 570 | 12 | 12 | Unit Ventilator | 8 | 4560 | 4.6711 | 1 | 4.6711 | 2 | 4.6711 | 2
106 | Classroom | 339 | 22 |  |  | 638 | 14 | 14 | Unit Ventilator | 8 | 5104 | 3.9851 | 1 | 3.9851 | 1 | 3.9851 | 1
107A | Classroom | 317 | 21 |  |  | 900 | 20 | 20 | Unit Ventilator | 8 | 7200 | 2.6417 | 1 | 2.6417 | 1 | 2.6417 | 1
107B | Classroom | 0 | 0 | Yes | 20 | 736 | 16 | 16 | Unit Ventilator | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom |  | 0 | Yes | 20 | 420 | 9 | 9 |  | 8 | 3360 | 0 | 1 | 0 | 0 | 20 | 3
110 | Classroom | 518 | 34 |  |  | 782 | 17 | 17 | Unit Ventilator | 8 | 6256 | 4.968 | 1 | 4.968 | 2 | 4.968 | 2
111 | Classroom | 354 | 23 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 3.9805 | 1 | 3.9805 | 1 | 3.9805 | 1
112 | Classroom | 328 | 21 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.5652 | 1 | 3.5652 | 1 | 3.5652 | 1
113 | Classroom | 389 | 25 |  |  | 1092 | 24 | 24 | Unit Ventilator | 8 | 8736 | 2.6717 | 1 | 2.6717 | 1 | 2.6717 | 1
114 | Classroom | 663 | 44 |  |  | 1036 | 23 | 23 | Unit Ventilator | 8 | 8288 | 4.7997 | 1 | 4.7997 | 2 | 4.7997 | 2
115 | Classroom | 422 | 28 |  |  | 814 | 18 | 18 | Unit Ventilator | 8 | 6512 | 3.8882 | 1 | 3.8882 | 1 | 3.8882 | 1
117 | Classroom | 536 | 35 |  |  | 782 | 17 | 17 | Unit Ventilator | 8 | 6256 | 5.1407 | 1 | 5.1407 | 2 | 5.1407 | 2
119 | Classroom | 480 | 32 |  |  | 713 | 16 | 16 | Unit Ventilator | 8 | 5704 | 5.0491 | 1 | 5.0491 | 2 | 5.0491 | 2
120 | Classroom | 277 | 18 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.0109 | 1 | 3.0109 | 1 | 3.0109 | 1
121 | Classroom | 0 | 0 | Yes | 20 | 720 | 16 | 16 | Unit Ventilator | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
122 | Classroom | 0 | 0 |  |  | 744 | 16 | 0 | Unit Ventilator | 8 | 5952 | 0 | 1 | 0 | 0 | 0 | 0
124 | Classroom | 273 | 18 |  |  | 759 | 17 | 17 | Unit Ventilator | 8 | 6072 | 2.6976 | 1 | 2.6976 | 1 | 2.6976 | 1
127 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | N/A | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
128 | Homemaking | 288 | 19 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 2.8125 | 1 | 2.8125 | 1 | 2.8125 | 1
129 | Classroom | 280 | 18 |  |  | 500 | 11 | 11 | Unit Ventilator | 8 | 4000 | 4.2 | 1 | 4.2 | 2 | 4.2 | 2
130 | Classroom | 321 | 21 |  |  | 644 | 14 | 14 | Unit Ventilator | 8 | 5152 | 3.7384 | 1 | 3.7384 | 1 | 3.7384 | 1
131 | Classroom | 283 | 18 |  |  | 638 | 14 | 14 | Unit Ventilator | 8 | 5104 | 3.3268 | 1 | 3.3268 | 1 | 3.3268 | 1
133 | Classroom | 337 | 22 |  |  | 403 | 9 | 9 | Unit Ventilator | 8 | 3224 | 6.2717 | 1 | 6.2717 | 2 | 6.2717 | 2
134 | Counselor office | 279 | 18 |  |  | 512 | 11 | 11 | Unit Ventilator | 8 | 4096 | 4.0869 | 1 | 4.0869 | 2 | 4.0869 | 2
135 | Custodial supply room | 0 | 0 |  |  | 512 | 11 | 0 | Unit Ventilator | 8 | 4096 | 0 | 1 | 0 | 0 | 0 | 0
136 | Classroom | 276 | 18 |  |  | 403 | 9 | 9 | Unit Ventilator | 8 | 3224 | 5.1365 | 1 | 5.1365 | 2 | 5.1365 | 2
- | Main Office |  | 0 | Yes | 20 | 529 | 12 | 12 |  | 8 | 4232 | 0 | 1 | 0 | 0 | 20 | 3
- | Principals Office |  | 0 | Yes | 20 | 221 | 5 | 5 |  | 8 | 1768 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses Office |  | 0 | Yes | 20 | 308 | 7 | 7 |  | 8 | 2464 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 109 | 7 |  |  | 1702 | 38 | 7 | Unit Ventilator | 8 | 13616 | 0.48032 | 1 | 0.48032 | 0 | 0.48032 | 0
- | Cafe | 642 | 42 |  |  | 2451 | 55 | 42 | Unit Ventilator | 8 | 19608 | 1.9645 | 1 | 1.9645 | 1 | 1.9645 | 1
- | Gym | 364 | 24 |  |  | 1914 | 43 | 24 | Unit Ventilator | 8 | 15312 | 1.4263 | 1 | 1.4263 | 1 | 1.4263 | 1
- | Hallway | 157 | 10 |  |  |  | 0 | 0 | Unit Ventilator
- | Staff Lounge |  | 0 |  |  | 525 | 11 | 0 |  | 8 | 4200 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-28
School: | Charles Carmine Antonio Baldi Middle School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
22 | Classroom | 903 | 60 |  |  | 799 | 18 | 18 | Air Handling Unit | 8 | 6392 | 8.4762 | 1 | 8.4762 | 2 | 8.4762 | 2
23 | Classroom | 552 | 36 |  |  | 844 | 19 | 19 | Unit Ventilator | 8 | 6752 | 4.9052 | 1 | 4.9052 | 2 | 4.9052 | 2
24 | Classroom | 670 | 44 |  |  | 853 | 19 | 19 | Unit Ventilator | 8 | 6824 | 5.891 | 1 | 5.891 | 2 | 5.891 | 2
26B | Classroom | 383 | 25 |  |  | 818 | 18 | 18 | Unit Ventilator | 8 | 6544 | 3.5116 | 1 | 3.5116 | 1 | 3.5116 | 1
27A | Classroom | 444 | 29 |  |  | 818 | 18 | 18 | Unit Ventilator | 8 | 6544 | 4.0709 | 1 | 4.0709 | 2 | 4.0709 | 2
28 | Science Lab | 1347 | 89 |  |  | 1213 | 27 | 27 | Unit Ventilator | 8 | 9704 | 8.3285 | 1 | 8.3285 | 2 | 8.3285 | 2
29 | Room | 733 | 48 |  |  | 1280 | 29 | 29 | Unit Ventilator | 8 | 10240 | 4.2949 | 1 | 4.2949 | 2 | 4.2949 | 2
30 | Science Lab | 1295 | 86 |  |  | 1213 | 27 | 27 | Unit Ventilator | 8 | 9704 | 8.007 | 1 | 8.007 | 2 | 8.007 | 2
31A | Classroom | 696 | 46 |  |  | 831 | 18 | 18 | Unit Ventilator | 8 | 6648 | 6.2816 | 1 | 6.2816 | 2 | 6.2816 | 2
31B | Classroom | 772 | 51 |  |  | 818 | 18 | 18 | Unit Ventilator | 8 | 6544 | 7.0782 | 1 | 7.0782 | 2 | 7.0782 | 2
32A | Classroom | 1064 | 70 |  |  | 852 | 19 | 19 | Unit Ventilator | 8 | 6816 | 9.3662 | 1 | 9.3662 | 2 | 9.3662 | 2
32B | Classroom | 395 | 26 |  |  | 818 | 18 | 18 | Unit Ventilator | 8 | 6544 | 3.6216 | 1 | 3.6216 | 1 | 3.6216 | 1
33A | Classroom | 1195 | 79 |  |  | 853 | 19 | 19 | Unit Ventilator | 8 | 6824 | 10.507 | 1 | 10.507 | 3 | 10.507 | 3
34a | Classroom | 310 | 20 |  |  | 844 | 19 | 19 | Unit Ventilator | 8 | 6752 | 2.7547 | 1 | 2.7547 | 1 | 2.7547 | 1
34b | Classroom | 232 | 15 |  |  | 799 | 18 | 15 | Unit Ventilator | 8 | 6392 | 2.1777 | 1 | 2.1777 | 1 | 2.1777 | 1
35 | Science Lab | 433 | 28 |  |  | 1227 | 27 | 27 | Unit Ventilator | 8 | 9816 | 2.6467 | 1 | 2.6467 | 1 | 2.6467 | 1
35 | Lounge | 133 | 8 |  |  | 435 | 9 | 8 | Unit Ventilator | 8 | 3480 | 2.2931 | 1 | 2.2931 | 1 | 2.2931 | 1
38 | Lounge | 0 | 0 |  |  | 435 | 9 | 0 | Unit Ventilator | 8 | 3480 | 0 | 1 | 0 | 0 | 0 | 0
39 | Lounge | 0 | 0 |  |  | 435 | 9 | 0 | Unit Ventilator | 8 | 3480 | 0 | 1 | 0 | 0 | 0 | 0
40 | Seminar Room | 1766 | 117 |  |  | 411 | 9 | 9 | Unit Ventilator | 8 | 3288 | 32.2263 | 1 | 32.2263 | 4 | 32.2263 | 4
40 | Classroom | 353 | 23 |  |  | 411 | 9 | 9 | Unit Ventilator | 8 | 3288 | 6.4416 | 1 | 6.4416 | 2 | 6.4416 | 2
42 | SGI Room | 205 | 13 |  |  | 435 | 9 | 9 | Unit Ventilator | 8 | 3480 | 3.5345 | 1 | 3.5345 | 1 | 3.5345 | 1
43 | SGI Room | 226 | 15 |  |  | 485 | 11 | 11 | Unit Ventilator | 8 | 3880 | 3.4948 | 1 | 3.4948 | 1 | 3.4948 | 1
44A | Classroom | 243 | 16 |  |  | 854 | 19 | 16 | Unit Ventilator | 8 | 6832 | 2.1341 | 1 | 2.1341 | 1 | 2.1341 | 1
44B | Classroom | 194 | 12 |  |  | 847 | 19 | 12 | Unit Ventilator | 8 | 6776 | 1.7178 | 1 | 1.7178 | 1 | 1.7178 | 1
45 | Teachers IPO Room | 0 | 0 |  |  | 980 | 22 | 0 | Unit Ventilator | 8 | 7840 | 0 | 1 | 0 | 0 | 0 | 0
46 | Conf. Room | 56 | 3 |  |  | 980 | 22 | 3 | Unit Ventilator | 8 | 7840 | 0.42857 | 1 | 0.42857 | 0 | 0.42857 | 0
46 | IPO Materials Room | 76 | 5 |  |  | 980 | 22 | 5 | Unit Ventilator | 8 | 7840 | 0.58163 | 1 | 0.58163 | 0 | 0.58163 | 0
47 | Faculty Lounge Room | 0 | 0 |  |  | 435 | 9 | 0 | Unit Ventilator | 8 | 3480 | 0 | 1 | 0 | 0 | 0 | 0
47a | Classroom | 195 | 13 |  |  | 841 | 19 | 13 | Air Handling Unit | 8 | 6728 | 1.739 | 1 | 1.739 | 1 | 1.739 | 1
47b | Classroom | 191 | 12 |  |  | 844 | 19 | 12 | Air Handling Unit | 8 | 6752 | 1.6973 | 1 | 1.6973 | 1 | 1.6973 | 1
48 | Science Lab | 858 | 57 |  |  | 1227 | 27 | 27 | Unit Ventilator | 8 | 9816 | 5.2445 | 1 | 5.2445 | 2 | 5.2445 | 2
B4 | Room |  | 0 |  |  | 853 | 19 | 0 |  | 8 | 6824 | 0 | 1 | 0 | 0 | 0 | 0
G5 | Room |  | 0 |  |  | 853 | 19 | 0 |  | 8 | 6824 | 0 | 1 | 0 | 0 | 0 | 0
G100 | Classroom |  | 0 | Yes | 20 | 565 | 12 | 12 |  | 8 | 4520 | 0 | 1 | 0 | 0 | 20 | 3
G101 | Classroom |  | 0 |  |  | 1227 | 27 | 0 |  | 8 | 9816 | 0 | 1 | 0 | 0 | 0 | 0
G102 | Classroom |  | 0 |  |  | 799 | 18 | 0 |  | 8 | 6392 | 0 | 1 | 0 | 0 | 0 | 0
G103 | Classroom |  | 0 |  |  | 844 | 19 | 0 |  | 8 | 6752 | 0 | 1 | 0 | 0 | 0 | 0
G104 | Classroom |  | 0 |  |  | 853 | 19 | 0 |  | 8 | 6824 | 0 | 1 | 0 | 0 | 0 | 0
G105 | Classroom |  | 0 |  |  | 853 | 19 | 0 |  | 8 | 6824 | 0 | 1 | 0 | 0 | 0 | 0
Y3 | Room |  | 0 |  |  | 818 | 18 | 0 |  | 8 | 6544 | 0 | 1 | 0 | 0 | 0 | 0
Y5 | Room |  | 0 |  |  | 852 | 19 | 0 |  | 8 | 6816 | 0 | 1 | 0 | 0 | 0 | 0
Y104 | Room |  | 0 |  |  | 818 | 18 | 0 |  | 8 | 6544 | 0 | 1 | 0 | 0 | 0 | 0
Y105 | Room |  | 0 |  |  | 852 | 19 | 0 |  | 8 | 6816 | 0 | 1 | 0 | 0 | 0 | 0
100 | Common Area | 0 | 0 |  |  | 3443 | 78 | 0 | Unit Ventilator | 8 | 27544 | 0 | 1.062 | 0 | 0 | 0 | 0
127 | Art Lab | 0 | 0 | Yes | 20 | 2279 | 51 | 51 | Unit Ventilator | 8 | 18232 | 0 | 1 | 0 | 0 | 20 | 3
128 | Art Lab | 0 | 0 | Yes | 20 | 2184 | 49 | 49 | Unit Ventilator | 8 | 17472 | 0 | 1 | 0 | 0 | 20 | 3
129 | Faculty Dining Room | 0 | 0 |  |  | 435 | 9 | 0 | Unit Ventilator | 8 | 3480 | 0 | 1 | 0 | 0 | 0 | 0
137 | Classroom | 1440 | 96 |  |  | 818 | 18 | 18 | Unit Ventilator | 8 | 6544 | 13.2029 | 1 | 13.2029 | 3 | 13.2029 | 3
138 | Classroom | 1218 | 81 |  |  | 831 | 18 | 18 | Unit Ventilator | 8 | 6648 | 10.9928 | 1 | 10.9928 | 3 | 10.9928 | 3
139 | Lab | 2473 | 164 |  |  | 1213 | 27 | 27 | Unit Ventilator | 8 | 9704 | 15.2906 | 1 | 15.2906 | 3 | 15.2906 | 3
140 | Large Group Room | 1508 | 100 |  |  | 1280 | 29 | 29 | Unit Ventilator | 8 | 10240 | 8.8359 | 1 | 8.8359 | 2 | 8.8359 | 2
141 | Science Lab | 1291 | 86 |  |  | 1213 | 27 | 27 | Unit Ventilator | 8 | 9704 | 7.9823 | 1 | 7.9823 | 2 | 7.9823 | 2
142 | Classroom | 1844 | 122 |  |  | 831 | 18 | 18 | Unit Ventilator | 8 | 6648 | 16.6426 | 1 | 16.6426 | 3 | 16.6426 | 3
143 | Classroom | 1560 | 104 |  |  | 818 | 18 | 18 | Unit Ventilator | 8 | 6544 | 14.3032 | 1 | 14.3032 | 3 | 14.3032 | 3
144 | Classroom | 391 | 26 |  |  | 818 | 18 | 18 | Unit Ventilator | 8 | 6544 | 3.585 | 1 | 3.585 | 1 | 3.585 | 1
145 | Classroom | 619 | 41 |  |  | 852 | 19 | 19 | Unit Ventilator | 8 | 6816 | 5.4489 | 1 | 5.4489 | 2 | 5.4489 | 2
146 | Classroom | 265 | 17 |  |  | 853 | 19 | 17 | Unit Ventilator | 8 | 6824 | 2.33 | 1 | 2.33 | 1 | 2.33 | 1
147 | Classroom | 562 | 37 |  |  | 853 | 19 | 19 | Unit Ventilator | 8 | 6824 | 4.9414 | 1 | 4.9414 | 2 | 4.9414 | 2
148 | Classroom | 592 | 39 |  |  | 844 | 19 | 19 | Unit Ventilator | 8 | 6752 | 5.2607 | 1 | 5.2607 | 2 | 5.2607 | 2
149 | Classroom | 385 | 25 |  |  | 799 | 18 | 18 | Unit Ventilator | 8 | 6392 | 3.6139 | 1 | 3.6139 | 1 | 3.6139 | 1
150 | Science Lab | 611 | 40 |  |  | 1233 | 28 | 28 | Unit Ventilator | 8 | 9864 | 3.7165 | 1 | 3.7165 | 1 | 3.7165 | 1
200 | Classroom |  | 0 | Yes | 20 | 566 | 12 | 12 |  | 8 | 4528 | 0 | 1 | 0 | 0 | 20 | 3
200 Office | Office |  | 0 | Yes | 20 | 374 | 8 | 8 |  | 8 | 2992 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 1085 | 24 | 24 |  | 8 | 8680 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 893 | 20 | 20 |  | 8 | 7144 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 |  |  | 1029 | 23 | 0 |  | 8 | 8232 | 0 | 1 | 0 | 0 | 0 | 0
205 | Classroom |  | 0 | Yes | 20 | 1575 | 35 | 35 |  | 8 | 12600 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom |  | 0 | Yes | 20 | 930 | 21 | 21 |  | 8 | 7440 | 0 | 1 | 0 | 0 | 20 | 3
212 | Classroom |  | 0 | Yes | 20 | 600 | 13 | 13 |  | 8 | 4800 | 0 | 1 | 0 | 0 | 20 | 3
213 | Classroom |  | 0 | Yes | 20 | 870 | 19 | 19 |  | 8 | 6960 | 0 | 1 | 0 | 0 | 20 | 3
214 | Classroom |  | 0 | Yes | 20 | 1326 | 30 | 30 |  | 8 | 10608 | 0 | 1 | 0 | 0 | 20 | 3
215 | Classroom |  | 0 |  |  | 980 | 22 | 0 |  | 8 | 7840 | 0 | 1 | 0 | 0 | 0 | 0
225 | Library | 0 | 0 |  |  | 1230 | 27 | 0 | Unit Ventilator | 8 | 9840 | 0 | 1 | 0 | 0 | 0 | 0
226 | Study Area | 0 | 0 |  |  | 3510 | 79 | 0 | Unit Ventilator | 8 | 28080 | 0 | 1.062 | 0 | 0 | 0 | 0
227 | Computer Lab | 0 | 0 |  |  | 980 | 22 | 0 | Unit Ventilator | 8 | 7840 | 0 | 1 | 0 | 0 | 0 | 0
228 | Mech. Room | 0 | 0 |  |  | 411 | 9 | 0 | Unit Ventilator | 8 | 3288 | 0 | 1 | 0 | 0 | 0 | 0
155A | Teachers Office | 0 | 0 |  |  | 948 | 21 | 0 | Unit Ventilator | 8 | 7584 | 0 | 1 | 0 | 0 | 0 | 0
156A | Teachers Office | 0 | 0 |  |  | 948 | 21 | 0 | Unit Ventilator | 8 | 7584 | 0 | 1 | 0 | 0 | 0 | 0
225A | Office | 0 | 0 |  |  | 948 | 21 | 0 | Unit Ventilator | 8 | 7584 | 0 | 1 | 0 | 0 | 0 | 0
225B | Office | 0 | 0 |  |  | 1029 | 23 | 0 | Unit Ventilator | 8 | 8232 | 0 | 1 | 0 | 0 | 0 | 0
225C | Storage | 0 | 0 |  |  | 1000 | 22 | 0 | Unit Ventilator | 8 | 8000 | 0 | 1 | 0 | 0 | 0 | 0
225D | Office | 0 | 0 |  |  | 299 | 6 | 0 | Unit Ventilator | 8 | 2392 | 0 | 1 | 0 | 0 | 0 | 0
Computer Lab A | Lab |  | 0 |  |  | 2640 | 60 | 0 |  | 8 | 21120 | 0 | 1.062 | 0 | 0 | 0 | 0
Computer Lab B | Lab |  | 0 |  |  | 2067 | 46 | 0 |  | 8 | 16536 | 0 | 1 | 0 | 0 | 0 | 0
Computer Lab C | Lab |  | 0 |  |  | 2262 | 51 | 0 |  | 8 | 18096 | 0 | 1 | 0 | 0 | 0 | 0
Main Office | Office |  | 0 | Yes | 20 | 875 | 19 | 19 |  | 8 | 7000 | 0 | 1 | 0 | 0 | 20 | 3
Principal | Office |  | 0 | Yes | 20 | 270 | 6 | 6 | Mobile Mini | 8 | 2160 | 0 | 1 | 0 | 0 | 20 | 3
Vice Principal | Office |  | 0 | Yes | 20 | 144 | 3 | 3 | Mobile Mini | 8 | 1152 | 0 | 1 | 0 | 0 | 20 | 3
Vice Principal | Office |  | 0 | Yes | 20 | 144 | 3 | 3 | Mobile Mini | 8 | 1152 | 0 | 1 | 0 | 0 | 20 | 3
Vice Principal | Office |  | 0 | Yes | 20 | 153 | 3 | 3 | Mobile Mini | 8 | 1224 | 0 | 1 | 0 | 0 | 20 | 3
- | Boys Gym | 0 | 0 |  |  | 5418 | 123 | 0 | Unit Ventilator | 8 | 43344 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Boys Locker Room | 0 | 0 |  |  | 1824 | 41 | 0 | Unit Ventilator | 8 | 14592 | 0 | 1 | 0 | 0 | 0 | 0
- | Corridor/Hall | 1107 | 73 |  |  | 435 | 9 | 9 | Unit Ventilator | 8 | 3480 | 19.0862 | 1 | 19.0862 | 3 | 19.0862 | 3
Cafeteria 1 | Dining | 0 | 0 |  |  | 2179 | 49 | 0 | Unit Ventilator | 8 | 17432 | 0 | 1 | 0 | 0 | 0 | 0
Cafeteria 2 | Dining |  | 0 |  |  | 2179 | 49 | 0 |  | 8 | 17432 | 0 | 1 | 0 | 0 | 0 | 0
Cafeteria 3 | Dining |  | 0 |  |  | 2179 | 49 | 0 |  | 8 | 17432 | 0 | 1 | 0 | 0 | 0 | 0
Cafeteria 4 | Dining |  | 0 |  |  | 2179 | 49 | 0 |  | 8 | 17432 | 0 | 1 | 0 | 0 | 0 | 0
- | Girls Gym | 4087 | 272 | Yes | 20 | 5418 | 123 | 123 | Air Handling Unit | 8 | 43344 | 5.6575 | 1.062 | 6.0085 | 2 | 26.0085 | 4
- | IPO Bathrooms | 129 | 8 |  |  | 411 | 9 | 8 | Unit Ventilator | 8 | 3288 | 2.354 | 1 | 2.354 | 1 | 2.354 | 1
- | IPO Office 1 |  | 0 |  |  | 435 | 9 | 0 | Unit Ventilator | 8 | 3480 | 0 | 1 | 0 | 0 | 0 | 0
- | IPO Office 1 | 40 | 2 |  |  | 435 | 9 | 2 | Unit Ventilator | 8 | 3480 | 0.68966 | 1 | 0.68966 | 0 | 0.68966 | 0
- | IPO Office 3 | 46 | 3 |  |  | 435 | 9 | 3 | Unit Ventilator | 8 | 3480 | 0.7931 | 1 | 0.7931 | 0 | 0.7931 | 0
- | Lounge | 104 | 6 |  |  | 485 | 11 | 6 | Unit Ventilator | 8 | 3880 | 1.6082 | 1 | 1.6082 | 1 | 1.6082 | 1
Sheet Last Modified: | 2021-03-12
School: | New Commodore John Barry Elementary School
Vendor: | EMCOR | Exhaust
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Room |  | 0 | Yes | 20 | 425 | 9 | 9 | Rooftop Unit | 8 | 3400 | 0 | 1 | 0 | 0 | 20 | 3
104 | Room | 116 | 7 | Yes | 20 | 1008 | 22 | 22 | Rooftop Unit | 8 | 8064 | 0.8631 | 1 | 0.8631 | 0 | 20.8631 | 3
105 | Room | 133 | 8 | Yes | 20 | 1134 | 25 | 25 | Rooftop Unit | 8 | 9072 | 0.87963 | 1 | 0.87963 | 0 | 20.8796 | 3
106 | Room |  | 0 | Yes | 20 | 1140 | 25 | 25 | Rooftop Unit | 8 | 9120 | 0 | 1 | 0 | 0 | 20 | 3
107 | Room | 308 | 20 |  |  | 1118 | 25 | 20 | Rooftop Unit | 8 | 8944 | 2.0662 | 1 | 2.0662 | 1 | 2.0662 | 1
108 | Room | 303 | 20 |  |  | 1140 | 25 | 20 | Rooftop Unit | 8 | 9120 | 1.9934 | 1 | 1.9934 | 1 | 1.9934 | 1
109 | Room | 1254 | 83 |  |  | 2100 | 47 | 47 | Rooftop Unit | 8 | 16800 | 4.4786 | 1 | 4.4786 | 2 | 4.4786 | 2
116 | Room | 125 | 8 |  |  |  | 0 | 0 | Rooftop Unit
202 | Room | 147 | 9 | Yes | 20 | 551 | 12 | 12 | Rooftop Unit | 8 | 4408 | 2.0009 | 1 | 2.0009 | 1 | 22.0009 | 3
203 | Room | 148 | 9 | Yes | 20 | 551 | 12 | 12 | Rooftop Unit | 8 | 4408 | 2.0145 | 1 | 2.0145 | 1 | 22.0145 | 3
204 | Room | 139 | 9 | Yes | 20 | 418 | 9 | 9 | Rooftop Unit | 8 | 3344 | 2.494 | 1 | 2.494 | 1 | 22.494 | 3
205 | Room | 202 | 13 | Yes | 20 | 551 | 12 | 12 | Rooftop Unit | 8 | 4408 | 2.7495 | 1 | 2.7495 | 1 | 22.7495 | 3
206 | Room | 145 | 9 | Yes | 20 | 728 | 16 | 16 | Rooftop Unit | 8 | 5824 | 1.4938 | 1 | 1.4938 | 1 | 21.4938 | 3
207 | Room | 185 | 12 | Yes | 20 | 728 | 16 | 16 | Rooftop Unit | 8 | 5824 | 1.9059 | 1 | 1.9059 | 1 | 21.9059 | 3
208 | Room | 139 | 9 | Yes | 20 | 728 | 16 | 16 | Rooftop Unit | 8 | 5824 | 1.432 | 1 | 1.432 | 1 | 21.432 | 3
209 | Room | 313 | 20 |  |  | 728 | 16 | 16 | Rooftop Unit | 8 | 5824 | 3.2246 | 1 | 3.2246 | 1 | 3.2246 | 1
210 | Room | 272 | 18 |  |  | 630 | 14 | 14 | Rooftop Unit | 8 | 5040 | 3.2381 | 1 | 3.2381 | 1 | 3.2381 | 1
211 | Room | 192 | 12 |  |  | 756 | 17 | 12 | Rooftop Unit | 8 | 6048 | 1.9048 | 1 | 1.9048 | 1 | 1.9048 | 1
212 | Room | 154 | 10 | Yes | 20 | 900 | 20 | 20 | Rooftop Unit | 8 | 7200 | 1.2833 | 1 | 1.2833 | 1 | 21.2833 | 3
213 | Room | 130 | 8 | Yes | 20 | 900 | 20 | 20 | Rooftop Unit | 8 | 7200 | 1.0833 | 1 | 1.0833 | 1 | 21.0833 | 3
214 | Room | 268 | 17 |  |  | 812 | 18 | 17 | Rooftop Unit | 8 | 6496 | 2.4754 | 1 | 2.4754 | 1 | 2.4754 | 1
215 | Room | 219 | 14 | Yes | 20 | 756 | 17 | 17 | Rooftop Unit | 8 | 6048 | 2.1726 | 1 | 2.1726 | 1 | 22.1726 | 3
216 | Room | 223 | 14 | Yes | 20 | 756 | 17 | 17 | Rooftop Unit | 8 | 6048 | 2.2123 | 1 | 2.2123 | 1 | 22.2123 | 3
301 | Room | 210 | 14 |  |  | 630 | 14 | 14 | Rooftop Unit | 8 | 5040 | 2.5 | 1 | 2.5 | 1 | 2.5 | 1
302A | Room |  | 0 |  |  | 104 | 2 | 0 | Rooftop Unit | 8 | 832 | 0 | 1 | 0 | 0 | 0 | 0
302B | Room |  | 0 |  |  | 117 | 2 | 0 | Rooftop Unit | 8 | 936 | 0 | 1 | 0 | 0 | 0 | 0
302C | Room |  | 0 |  |  | 104 | 2 | 0 | Rooftop Unit | 8 | 832 | 0 | 1 | 0 | 0 | 0 | 0
303 | Room | 99 | 6 |  |  | 651 | 14 | 6 | Rooftop Unit | 8 | 5208 | 1.1406 | 1 | 1.1406 | 1 | 1.1406 | 1
304 | Room |  | 0 |  |  | 110 | 2 | 0 | Rooftop Unit | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
305 | Room | 237 | 15 |  |  | 756 | 17 | 15 | Rooftop Unit | 8 | 6048 | 2.3512 | 1 | 2.3512 | 1 | 2.3512 | 1
306 | Room | 156 | 10 |  |  | 756 | 17 | 10 | Rooftop Unit | 8 | 6048 | 1.5476 | 1 | 1.5476 | 1 | 1.5476 | 1
307 | Room | 265 | 17 |  |  | 784 | 17 | 17 | Rooftop Unit | 8 | 6272 | 2.5351 | 1 | 2.5351 | 1 | 2.5351 | 1
308 | Room | 192 | 12 | Yes | 20 | 864 | 19 | 19 | Rooftop Unit | 8 | 6912 | 1.6667 | 1 | 1.6667 | 1 | 21.6667 | 3
309 | Room | 208 | 13 |  |  | 810 | 18 | 13 | Rooftop Unit | 8 | 6480 | 1.9259 | 1 | 1.9259 | 1 | 1.9259 | 1
310 | Room | 296 | 19 |  |  | 810 | 18 | 18 | Rooftop Unit | 8 | 6480 | 2.7407 | 1 | 2.7407 | 1 | 2.7407 | 1
311 | Room | 249 | 16 |  |  | 812 | 18 | 16 | Rooftop Unit | 8 | 6496 | 2.2999 | 1 | 2.2999 | 1 | 2.2999 | 1
312 | Room | 210 | 14 |  |  | 840 | 19 | 14 | Rooftop Unit | 8 | 6720 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
313 | Room | 96 | 6 |  |  | 810 | 18 | 6 | Rooftop Unit | 8 | 6480 | 0.88889 | 1 | 0.88889 | 0 | 0.88889 | 0
314 | Room | 219 | 14 |  |  | 810 | 18 | 14 | Rooftop Unit | 8 | 6480 | 2.0278 | 1 | 2.0278 | 1 | 2.0278 | 1
315 | Room | 105 | 7 |  |  | 812 | 18 | 7 | Rooftop Unit | 8 | 6496 | 0.96983 | 1 | 0.96983 | 0 | 0.96983 | 0
316 | Room | 143 | 9 |  |  | 812 | 18 | 9 | Rooftop Unit | 8 | 6496 | 1.3208 | 1 | 1.3208 | 1 | 1.3208 | 1
320 | Room | 212 | 14 |  |  | 620 | 14 | 14 | Rooftop Unit | 8 | 4960 | 2.5645 | 1 | 2.5645 | 1 | 2.5645 | 1
323 | Room | 230 | 15 |  |  | 620 | 14 | 14 | Rooftop Unit | 8 | 4960 | 2.7823 | 1 | 2.7823 | 1 | 2.7823 | 1
401 | Room | 215 | 14 | Yes | 20 | 1260 | 28 | 28 | Rooftop Unit | 8 | 10080 | 1.2798 | 1 | 1.2798 | 1 | 21.2798 | 3
403A | Room |  | 0 |  |  | 240 | 5 | 0 | Rooftop Unit | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
403B | Room |  | 0 |  |  | 210 | 4 | 0 | Rooftop Unit | 8 | 1680 | 0 | 1 | 0 | 0 | 0 | 0
403C | Room |  | 0 |  |  | 240 | 5 | 0 | Rooftop Unit | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
404 | Room |  | 0 | Yes | 20 | 1024 | 23 | 23 | Rooftop Unit | 8 | 8192 | 0 | 1 | 0 | 0 | 20 | 3
405 | Room | 382 | 25 |  |  | 1476 | 33 | 25 | Rooftop Unit | 8 | 11808 | 1.9411 | 1 | 1.9411 | 1 | 1.9411 | 1
406 | Room |  | 0 |  |  | 1462 | 33 | 0 | Rooftop Unit | 8 | 11696 | 0 | 1 | 0 | 0 | 0 | 0
407 | Room |  | 0 |  |  | 1054 | 23 | 0 | Rooftop Unit | 8 | 8432 | 0 | 1 | 0 | 0 | 0 | 0
408 | Room | 561 | 37 |  |  | 1280 | 29 | 29 | Rooftop Unit | 8 | 10240 | 3.2871 | 1 | 3.2871 | 1 | 3.2871 | 1
409 | Room | 213 | 14 |  |  | 1160 | 26 | 14 | Rooftop Unit | 8 | 9280 | 1.3772 | 1 | 1.3772 | 1 | 1.3772 | 1
- | Café | 593 | 39 |  |  | 4800 | 109 | 39 | Rooftop Unit | 8 | 38400 | 0.92656 | 1.062 | 0.98404 | 0 | 0.98404 | 0
- | Gym |  | 0 | Yes | 20 | 6240 | 141 | 141 | Rooftop Unit | 8 | 49920 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Library |  | 0 | Yes | 20 | 1961 | 44 | 44 | Rooftop Unit | 8 | 15688 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 |  |  | 924 | 21 | 0 | Rooftop Unit | 8 | 7392 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurse's Office |  | 0 |  |  | 143 | 3 | 0 | Rooftop Unit | 8 | 1144 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-16
School: | Clara Barton
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B7 | Classroom | 0 | 0 | Yes | 20 | 601 | 13 | 13 | House Fan | 8 | 4808 | 0 | 1 | 0 | 0 | 20 | 3
B8 | Classroom | 0 | 0 | Yes | 20 | 848 | 19 | 19 | House Fan | 8 | 6784 | 0 | 1 | 0 | 0 | 20 | 3
B10 | Classroom | 0 | 0 |  |  | 686 | 15 | 0 | House Fan | 8 | 5488 | 0 | 1 | 0 | 0 | 0 | 0
B11 | Classroom | 0 | 0 |  |  | 806 | 18 | 0 | House Fan | 8 | 6448 | 0 | 1 | 0 | 0 | 0 | 0
100 | Classroom | 0 | 0 | Yes | 20 | 742 | 16 | 16 | House Fan | 8 | 5936 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom | 0 | 0 | Yes | 20 | 650 | 14 | 14 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
102 | Office | 0 | 0 | Yes | 20 | 452 | 10 | 10 | House Fan | 8 | 3616 | 0 | 1 | 0 | 0 | 20 | 3
102 A | Classroom | 0 | 0 |  |  | 70 | 1 | 0 | House Fan | 8 | 560 | 0 | 1 | 0 | 0 | 0 | 0
102 B | Office | 0 | 0 |  |  | 122 | 2 | 0 | House Fan | 8 | 976 | 0 | 1 | 0 | 0 | 0 | 0
103 C | Office | 0 | 0 |  |  | 90 | 2 | 0 | House Fan | 8 | 720 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom | 0 | 0 | Yes | 20 | 627 | 14 | 14 | House Fan | 8 | 5016 | 0 | 1 | 0 | 0 | 20 | 3
104 | Library | 0 | 0 | Yes | 20 | 645 | 14 | 14 | House Fan | 8 | 5160 | 0 | 1 | 0 | 0 | 20 | 3
105 | Library | 0 | 0 | Yes | 20 | 658 | 14 | 14 | House Fan | 8 | 5264 | 0 | 1 | 0 | 0 | 20 | 3
106 | Library | 0 | 0 | Yes | 20 | 653 | 14 | 14 | House Fan | 8 | 5224 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom | 0 | 0 | Yes | 20 | 632 | 14 | 14 | House Fan | 8 | 5056 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 20 | 640 | 14 | 14 | House Fan | 8 | 5120 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 0 | 0 | Yes | 20 | 694 | 15 | 15 | House Fan | 8 | 5552 | 0 | 1 | 0 | 0 | 20 | 3
110 | Classroom | 0 | 0 | Yes | 20 | 683 | 15 | 15 | House Fan | 8 | 5464 | 0 | 1 | 0 | 0 | 20 | 3
111 | Classroom | 0 | 0 | Yes | 20 | 650 | 14 | 14 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
112 | Nurse's Office | 0 | 0 | Yes | 20 | 118 | 2 | 2 | House Fan | 8 | 944 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office | 0 | 0 | Yes | 20 | 297 | 6 | 6 | House Fan | 8 | 2376 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office | 0 | 0 | Yes | 20 | 159 | 3 | 3 | House Fan | 8 | 1272 | 0 | 1 | 0 | 0 | 20 | 3
200 | Classroom | 0 | 0 | Yes | 20 | 663 | 15 | 15 | House Fan | 8 | 5304 | 0 | 1 | 0 | 0 | 20 | 3
200 A | Office | 0 | 0 | Yes | 20 | 226 | 5 | 5 | House Fan | 8 | 1808 | 0 | 1 | 0 | 0 | 20 | 3
200 B | Classroom | 0 | 0 | Yes | 20 | 158 | 3 | 3 | House Fan | 8 | 1264 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 20 | 635 | 14 | 14 | House Fan | 8 | 5080 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 | Yes | 20 | 713 | 16 | 16 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom | 0 | 0 | Yes | 20 | 645 | 14 | 14 | House Fan | 8 | 5160 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom | 0 | 0 | Yes | 20 | 624 | 14 | 14 | House Fan | 8 | 4992 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom | 0 | 0 | Yes | 20 | 624 | 14 | 14 | House Fan | 8 | 4992 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom | 0 | 0 | Yes | 20 | 653 | 14 | 14 | House Fan | 8 | 5224 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 20 | 664 | 15 | 15 | House Fan | 8 | 5312 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 20 | 638 | 14 | 14 | House Fan | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 | Yes | 20 | 662 | 15 | 15 | House Fan | 8 | 5296 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom | 0 | 0 | Yes | 20 | 694 | 15 | 15 | House Fan | 8 | 5552 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom | 0 | 0 | Yes | 20 | 616 | 14 | 14 | House Fan | 8 | 4928 | 0 | 1 | 0 | 0 | 20 | 3
211 A | Office | 0 | 0 |  |  | 115 | 2 | 0 | House Fan | 8 | 920 | 0 | 1 | 0 | 0 | 0 | 0
- | Teacher Lounge | 0 | 0 | Yes | 20 | 340 | 7 | 7 | House Fan | 8 | 2720 | 0 | 1 | 0 | 0 | 20 | 3
215 | Classroom |  | 0 | Yes | 20 | 345 | 7 | 7 | house Fan | 8 | 2760 | 0 | 1 | 0 | 0 | 20 | 3
300 | Classroom | 0 | 0 | Yes | 20 | 640 | 14 | 14 | House Fan | 8 | 5120 | 0 | 1 | 0 | 0 | 20 | 3
300A | Office |  | 0 | Yes | 20 | 264 | 6 | 6 | House Fan | 8 | 2112 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 | Yes | 20 | 668 | 15 | 15 | House Fan | 8 | 5344 | 0 | 1 | 0 | 0 | 20 | 3
301 A | Office | 0 | 0 |  |  | 203 | 4 | 0 | House Fan | 8 | 1624 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom | 0 | 0 | Yes | 20 | 639 | 14 | 14 | House Fan | 8 | 5112 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom | 0 | 0 | Yes | 20 | 692 | 15 | 15 | House Fan | 8 | 5536 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom | 0 | 0 | Yes | 20 | 627 | 14 | 14 | House Fan | 8 | 5016 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom | 0 | 0 | Yes | 20 | 655 | 14 | 14 | House Fan | 8 | 5240 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 20 | 664 | 15 | 15 | House Fan | 8 | 5312 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 | Yes | 20 | 642 | 14 | 14 | House Fan | 8 | 5136 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom | 0 | 0 | Yes | 20 | 663 | 15 | 15 | House Fan | 8 | 5304 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 | Yes | 20 | 605 | 13 | 13 | House Fan | 8 | 4840 | 0 | 1 | 0 | 0 | 20 | 3
310 | Classroom | 0 | 0 | Yes | 20 | 673 | 15 | 15 | House Fan | 8 | 5384 | 0 | 1 | 0 | 0 | 20 | 3
311 | Classroom | 0 | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
312 | Classroom | 0 | 0 |  |  | 634 | 14 | 0 | House Fan | 8 | 5072 | 0 | 1 | 0 | 0 | 0 | 0
312 A | Office | 0 | 0 |  |  | 112 | 2 | 0 | House Fan | 8 | 896 | 0 | 1 | 0 | 0 | 0 | 0
- | Counselor Office |  | 0 | Yes | 20 | 152 | 3 | 3 | House Fan | 8 | 1216 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym | 0 | 0 | Yes | 20 | 3436 | 78 | 78 | N/A | 8 | 27488 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Kitchen | 0 | 0 | Yes | 20 | 1140 | 25 | 25 | House Fan | 8 | 9120 | 0 | 1 | 0 | 0 | 20 | 3
- | Cafeteria | 0 | 0 | Yes | 20 | 1478 | 33 | 33 | House Fan | 8 | 11824 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-26
School: | John Bartram High School
Vendor: | Devine Brothers | Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 590 | 39 |  |  | 1196 | 27 | 27 | Unit Ventilator | 8 | 9568 | 3.6998 | 1 | 3.6998 | 1 | 3.6998 | 1
102 | Classroom | 359 | 23 |  |  | 851 | 19 | 19 | Unit Ventilator | 8 | 6808 | 3.1639 | 1 | 3.1639 | 1 | 3.1639 | 1
103 | Classroom | 759 | 50 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 6.875 | 1 | 6.875 | 2 | 6.875 | 2
104 | Classroom | 646 | 43 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 5.2663 | 1 | 5.2663 | 2 | 5.2663 | 2
105 | Classroom | 582 | 38 |  |  | 851 | 19 | 19 | Unit Ventilator | 8 | 6808 | 5.1293 | 1 | 5.1293 | 2 | 5.1293 | 2
106 | Classroom | 696 | 46 |  |  | 989 | 22 | 22 | Unit Ventilator | 8 | 7912 | 5.2781 | 1 | 5.2781 | 2 | 5.2781 | 2
107 | Classroom | 980 | 65 |  |  | 946 | 21 | 21 | Unit Ventilator | 8 | 7568 | 7.7696 | 1 | 7.7696 | 2 | 7.7696 | 2
108 | Classroom | 575 | 38 |  |  | 1012 | 23 | 23 | Unit Ventilator | 8 | 8096 | 4.2614 | 1 | 4.2614 | 2 | 4.2614 | 2
110 | Office | 0 | 0 |  |  | 238 | 5 | 0 | Unit Ventilator | 8 | 1904 | 0 | 1 | 0 | 0 | 0 | 0
111 | Classroom | 418 | 27 |  |  | 805 | 18 | 18 | Unit Ventilator | 8 | 6440 | 3.8944 | 1 | 3.8944 | 1 | 3.8944 | 1
112 | Room | 416 | 27 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 3.3913 | 1 | 3.3913 | 1 | 3.3913 | 1
113 | Classroom | 416 | 27 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.5217 | 1 | 4.5217 | 2 | 4.5217 | 2
115 | Classroom | 343 | 22 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.7283 | 1 | 3.7283 | 1 | 3.7283 | 1
116 | Classroom | 467 | 31 |  |  | 1357 | 30 | 30 | Unit Ventilator | 8 | 10856 | 2.5811 | 1 | 2.5811 | 1 | 2.5811 | 1
117 | Classroom | 352 | 23 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.8261 | 1 | 3.8261 | 1 | 3.8261 | 1
118 | Classroom | 325 | 21 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.5326 | 1 | 3.5326 | 1 | 3.5326 | 1
119 | Classroom | 346 | 23 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.7609 | 1 | 3.7609 | 1 | 3.7609 | 1
120 | Classroom | 0 | 0 |  |  | 690 | 15 | 0 | Unit Ventilator | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
121 | Office | 0 | 0 | Yes | 20 | 227 | 5 | 5 | Unit Ventilator | 8 | 1816 | 0 | 1 | 0 | 0 | 20 | 3
123 | Room | 498 | 33 |  |  | 1242 | 28 | 28 | Unit Ventilator | 8 | 9936 | 3.0072 | 1 | 3.0072 | 1 | 3.0072 | 1
124 | Office | 0 | 0 | Yes | 20 | 309 | 7 | 7 | Unit Ventilator | 8 | 2472 | 0 | 1 | 0 | 0 | 20 | 3
124A | Office | 0 | 0 | Yes | 20 | 218 | 4 | 4 | Unit Ventilator | 8 | 1744 | 0 | 1 | 0 | 0 | 20 | 3
125 | Room | 356 | 23 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.8696 | 1 | 3.8696 | 1 | 3.8696 | 1
126 | Room | 339 | 22 |  |  | 276 | 6 | 6 | Unit Ventilator | 8 | 2208 | 9.212 | 1 | 9.212 | 2 | 9.212 | 2
127 | Room | 349 | 23 |  |  | 644 | 14 | 14 | Unit Ventilator | 8 | 5152 | 4.0644 | 1 | 4.0644 | 2 | 4.0644 | 2
127a | Room | 331 | 22 |  |  | 345 | 7 | 7 | Unit Ventilator | 8 | 2760 | 7.1957 | 1 | 7.1957 | 2 | 7.1957 | 2
128 | Office | 0 | 0 |  |  | 230 | 5 | 0 | Unit Ventilator | 8 | 1840 | 0 | 1 | 0 | 0 | 0 | 0
130 | Room | 288 | 19 |  |  | 375 | 8 | 8 | Unit Ventilator | 8 | 3000 | 5.76 | 1 | 5.76 | 2 | 5.76 | 2
130A | Office | 0 | 0 |  |  | 236 | 5 | 0 | Unit Ventilator | 8 | 1888 | 0 | 1 | 0 | 0 | 0 | 0
131 | Office | 0 | 0 | Yes | 20 | 237 | 5 | 5 | Unit Ventilator | 8 | 1896 | 0 | 1 | 0 | 0 | 20 | 3
133 | Office | 0 | 0 | Yes | 20 | 333 | 7 | 7 | Unit Ventilator | 8 | 2664 | 0 | 1 | 0 | 0 | 20 | 3
134 | Main Office | 593 | 39 |  |  | 1656 | 37 | 37 | Unit Ventilator | 8 | 13248 | 2.6857 | 1 | 2.6857 | 1 | 2.6857 | 1
201 | Classroom | 617 | 41 |  |  | 989 | 22 | 22 | Unit Ventilator | 8 | 7912 | 4.679 | 1 | 4.679 | 2 | 4.679 | 2
202 | Classroom | 282 | 18 |  |  | 805 | 18 | 18 | Unit Ventilator | 8 | 6440 | 2.6273 | 1 | 2.6273 | 1 | 2.6273 | 1
203 | Classroom | 632 | 42 |  |  | 989 | 22 | 22 | Unit Ventilator | 8 | 7912 | 4.7927 | 1 | 4.7927 | 2 | 4.7927 | 2
204 | Classroom | 309 | 20 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.3587 | 1 | 3.3587 | 1 | 3.3587 | 1
205 | Classroom | 516 | 34 |  |  | 989 | 22 | 22 | Unit Ventilator | 8 | 7912 | 3.913 | 1 | 3.913 | 1 | 3.913 | 1
206 | Classroom | 324 | 21 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.5217 | 1 | 3.5217 | 1 | 3.5217 | 1
207 | Classroom | 363 | 24 |  |  | 989 | 22 | 22 | Unit Ventilator | 8 | 7912 | 2.7528 | 1 | 2.7528 | 1 | 2.7528 | 1
208 | Classroom | 291 | 19 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.163 | 1 | 3.163 | 1 | 3.163 | 1
209 | Classroom | 0 | 0 | Yes | 20 | 309 | 7 | 7 | Unit Ventilator | 8 | 2472 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom | 297 | 19 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.2283 | 1 | 3.2283 | 1 | 3.2283 | 1
211 | Room | 0 | 0 | Yes | 20 | 321 | 7 | 7 | Unit Ventilator | 8 | 2568 | 0 | 1 | 0 | 0 | 20 | 3
211A | copy Room | 0 | 0 |  |  | 227 | 5 | 0 | Unit Ventilator | 8 | 1816 | 0 | 1 | 0 | 0 | 0 | 0
214 | Classroom | 370 | 24 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.0217 | 1 | 4.0217 | 2 | 4.0217 | 2
215 | Classroom | 337 | 22 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.663 | 1 | 3.663 | 1 | 3.663 | 1
216 | Classroom | 327 | 21 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.5543 | 1 | 3.5543 | 1 | 3.5543 | 1
217 | Classroom | 282 | 18 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.0652 | 1 | 3.0652 | 1 | 3.0652 | 1
218 | Classroom | 563 | 37 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 6.1196 | 1 | 6.1196 | 2 | 6.1196 | 2
219 | Office | 0 | 0 | Yes | 20 | 272 | 6 | 6 | Unit Ventilator | 8 | 2176 | 0 | 1 | 0 | 0 | 20 | 3
220A | Office | 0 | 0 | Yes | 20 | 169 | 3 | 3 | Unit Ventilator | 8 | 1352 | 0 | 1 | 0 | 0 | 20 | 3
221 | Classroom | 97 | 6 | Yes | 20 | 851 | 19 | 19 | Unit Ventilator | 8 | 6808 | 0.85488 | 1 | 0.85488 | 0 | 20.8549 | 3
222 | Classroom | 320 | 21 |  |  | 851 | 19 | 19 | Unit Ventilator | 8 | 6808 | 2.8202 | 1 | 2.8202 | 1 | 2.8202 | 1
223 | Classroom | 329 | 21 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.5761 | 1 | 3.5761 | 1 | 3.5761 | 1
224 | Classroom | 302 | 20 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.2826 | 1 | 3.2826 | 1 | 3.2826 | 1
225 | Classroom | 437 | 29 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.75 | 1 | 4.75 | 2 | 4.75 | 2
226 | Classroom | 315 | 21 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.4239 | 1 | 3.4239 | 1 | 3.4239 | 1
227 | Classroom | 299 | 19 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.25 | 1 | 3.25 | 1 | 3.25 | 1
228 | Classroom | 302 | 20 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.2826 | 1 | 3.2826 | 1 | 3.2826 | 1
229 | Classroom | 407 | 27 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.4239 | 1 | 4.4239 | 2 | 4.4239 | 2
230 | Classroom | 290 | 19 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.1522 | 1 | 3.1522 | 1 | 3.1522 | 1
231 | Classroom | 331 | 22 |  |  | 322 | 7 | 7 | Unit Ventilator | 8 | 2576 | 7.7096 | 1 | 7.7096 | 2 | 7.7096 | 2
232 | Classroom | 0 | 0 | Yes | 20 | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
234 | Office | 0 | 0 | Yes | 20 | 298 | 6 | 6 | Unit Ventilator | 8 | 2384 | 0 | 1 | 0 | 0 | 20 | 3
236 | Office | 0 | 0 | Yes | 20 | 299 | 6 | 6 | Unit Ventilator | 8 | 2392 | 0 | 1 | 0 | 0 | 20 | 3
236A | Copy room | 0 | 0 |  |  | 203 | 4 | 0 | Unit Ventilator | 8 | 1624 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom |  | 0 |  |  | 816 | 18 | 0 | Air Handling Unit | 8 | 6528 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom |  | 0 |  |  | 816 | 18 | 0 | Air Handling Unit | 8 | 6528 | 0 | 1 | 0 | 0 | 0 | 0
305 | Classroom |  | 0 |  |  | 1000 | 22 | 0 | Air Handling Unit | 8 | 8000 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom |  | 0 |  |  | 136 | 3 | 0 | Air Handling Unit | 8 | 1088 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom |  | 0 |  |  | 696 | 15 | 0 | Air Handling Unit | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
309 | Classroom |  | 0 |  |  | 225 | 5 | 0 | Air Handling Unit | 8 | 1800 | 0 | 1 | 0 | 0 | 0 | 0
313 | Faculty | 309 | 20 |  |  | 832 | 18 | 18 | Unit Ventilator | 8 | 6656 | 2.7855 | 1 | 2.7855 | 1 | 2.7855 | 1
320 | Classroom | 618 | 41 |  |  | 1080 | 24 | 24 | Unit Ventilator | 8 | 8640 | 4.2917 | 1 | 4.2917 | 2 | 4.2917 | 2
321 | Classroom | 574 | 38 |  |  | 1100 | 25 | 25 | Unit Ventilator | 8 | 8800 | 3.9136 | 1 | 3.9136 | 1 | 3.9136 | 1
324 | Classroom | 553 | 36 |  |  | 945 | 21 | 21 | Unit Ventilator | 8 | 7560 | 4.3889 | 1 | 4.3889 | 2 | 4.3889 | 2
325 | Classroom | 394 | 26 |  |  | 1080 | 24 | 24 | Unit Ventilator | 8 | 8640 | 2.7361 | 1 | 2.7361 | 1 | 2.7361 | 1
328 | Room | 0 | 0 | Yes | 20 | 169 | 3 | 3 | Unit Ventilator | 8 | 1352 | 0 | 1 | 0 | 0 | 20 | 3
331 | Classroom | 351 | 23 |  |  | 805 | 18 | 18 | Unit Ventilator | 8 | 6440 | 3.2702 | 1 | 3.2702 | 1 | 3.2702 | 1
332 | Classroom | 361 | 24 |  |  | 1081 | 24 | 24 | Unit Ventilator | 8 | 8648 | 2.5046 | 1 | 2.5046 | 1 | 2.5046 | 1
333 | Classroom | 321 | 21 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.4891 | 1 | 3.4891 | 1 | 3.4891 | 1
334 | Classroom | 284 | 18 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.087 | 1 | 3.087 | 1 | 3.087 | 1
335 | Classroom | 286 | 19 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 3.2159 | 1 | 3.2159 | 1 | 3.2159 | 1
336 | Classroom | 295 | 19 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.2065 | 1 | 3.2065 | 1 | 3.2065 | 1
337 | Classroom | 86 | 5 | Yes | 20 | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 0.93478 | 1 | 0.93478 | 0 | 20.9348 | 3
338 | Classroom | 280 | 18 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 3.1484 | 1 | 3.1484 | 1 | 3.1484 | 1
339 | Classroom | 366 | 24 |  |  | 506 | 11 | 11 | Unit Ventilator | 8 | 4048 | 5.4249 | 1 | 5.4249 | 2 | 5.4249 | 2
340 | Classroom | 274 | 18 |  |  | 484 | 11 | 11 | Unit Ventilator | 8 | 3872 | 4.2459 | 1 | 4.2459 | 2 | 4.2459 | 2
341 | Classroom | 356 | 23 |  |  | 484 | 11 | 11 | Unit Ventilator | 8 | 3872 | 5.5165 | 1 | 5.5165 | 2 | 5.5165 | 2
342 | Classroom | 289 | 19 |  |  | 529 | 12 | 12 | Unit Ventilator | 8 | 4232 | 4.0974 | 1 | 4.0974 | 2 | 4.0974 | 2
344 | Room | 0 | 0 | Yes | 20 | 233 | 5 | 5 | Unit Ventilator | 8 | 1864 | 0 | 1 | 0 | 0 | 20 | 3
346 | Classroom | 291 | 19 |  |  | 675 | 15 | 15 | Unit Ventilator | 8 | 5400 | 3.2333 | 1 | 3.2333 | 1 | 3.2333 | 1
B12 | Room | 0 | 0 |  |  | 383 | 8 | 0 | Unit Ventilator | 8 | 3064 | 0 | 1 | 0 | 0 | 0 | 0
B13 | BE Office | 0 | 0 |  |  | 238 | 5 | 0 | Unit Ventilator | 8 | 1904 | 0 | 1 | 0 | 0 | 0 | 0
B17 | Room | 0 | 0 |  |  | 209 | 4 | 0 | Unit Ventilator | 8 | 1672 | 0 | 1 | 0 | 0 | 0 | 0
Bc | Room | 0 | 0 | Yes | 20 | 244 | 5 | 5 | Unit Ventilator | 8 | 1952 | 0 | 1 | 0 | 0 | 20 | 3
C1 | Classroom | 398 | 26 |  |  | 1000 | 22 | 22 | Unit Ventilator | 8 | 8000 | 2.985 | 1 | 2.985 | 1 | 2.985 | 1
C2 | Classroom | 0 | 0 |  |  | 1000 | 22 | 0 | Unit Ventilator | 8 | 8000 | 0 | 1 | 0 | 0 | 0 | 0
C3 | Classroom | 1212 | 80 |  |  | 1000 | 22 | 22 | Unit Ventilator | 8 | 8000 | 9.09 | 1 | 9.09 | 2 | 9.09 | 2
C4 | Classroom | 0 | 0 |  |  | 1000 | 22 | 0 | Unit Ventilator | 8 | 8000 | 0 | 1 | 0 | 0 | 0 | 0
C5 | Classroom | 0 | 0 |  |  | 1000 | 22 | 0 | Unit Ventilator | 8 | 8000 | 0 | 1 | 0 | 0 | 0 | 0
C7 | Classroom | 881 | 58 |  |  | 968 | 22 | 22 | Unit Ventilator | 8 | 7744 | 6.8259 | 1 | 6.8259 | 2 | 6.8259 | 2
C7A | Classroom | 0 | 0 |  |  | 909 | 20 | 0 | Unit Ventilator | 8 | 7272 | 0 | 1 | 0 | 0 | 0 | 0
- | School police | 0 | 0 | Yes | 20 | 192 | 4 | 4 | Unit Ventilator | 8 | 1536 | 0 | 1 | 0 | 0 | 20 | 3
- | 3rd Floor C Wing | 0 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Auditorium | 0 | 0 |  |  | 11625 | 264 | 0 | Air Handling Unit | 8 | 93000 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | Boys Gym | 5931 | 395 |  |  | 5280 | 120 | 120 | Air Handling Unit | 8 | 42240 | 8.4247 | 1.062 | 8.9473 | 2 | 8.9473 | 2
- | Library | 866 | 57 |  |  | 4526 | 102 | 57 | Unit Ventilator | 8 | 36208 | 1.435 | 1.062 | 1.5241 | 1 | 1.5241 | 1
- | Corridor | 0 | 0 |  |  |  | 0 | 0 | Unit Ventilator
- | Girls Gym | 6806 | 453 |  |  | 5280 | 120 | 120 | Air Handling Unit | 8 | 42240 | 9.6676 | 1.062 | 10.2673 | 3 | 10.2673 | 3
- | Nurse Area | 255 | 17 |  |  | 936 | 21 | 17 | Unit Ventilator | 8 | 7488 | 2.0433 | 1 | 2.0433 | 1 | 2.0433 | 1
- | Cafeteria | 0 | 0 | Yes | 20 | 6262 | 142 | 142 | Unit Ventilator | 8 | 50096 | 0 | 1.4912 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-05
School: | Mary McLeod Bethune School
Vendor: | Capital | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 300 | 20 |  |  | 1350 | 30 | 20 | Unit Ventilator | 8 | 10800 | 1.6667 | 1 | 1.6667 | 1 | 1.6667 | 1
2 | Classroom | 278 | 18 |  |  | 1350 | 30 | 18 | Unit Ventilator | 8 | 10800 | 1.5444 | 1 | 1.5444 | 1 | 1.5444 | 1
3 | Classroom | 395 | 26 |  |  | 1350 | 30 | 26 | Unit Ventilator | 8 | 10800 | 2.1944 | 1 | 2.1944 | 1 | 2.1944 | 1
4 | Classroom | 425 | 28 |  |  | 1296 | 29 | 28 | Unit Ventilator | 8 | 10368 | 2.4595 | 1 | 2.4595 | 1 | 2.4595 | 1
5 | Classroom | 314 | 20 |  |  | 1296 | 29 | 20 | Unit Ventilator | 8 | 10368 | 1.8171 | 1 | 1.8171 | 1 | 1.8171 | 1
100 | Classroom | 614 | 40 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 4.7969 | 1 | 4.7969 | 2 | 4.7969 | 2
101 | Classroom | 597 | 39 |  |  | 1024 | 23 | 23 | Unit Ventilator | 8 | 8192 | 4.3726 | 1 | 4.3726 | 2 | 4.3726 | 2
101A | Instructional Storage | 0 | 0 |  |  |  | 0 | 0 | HUV
102 | Classroom | 560 | 37 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 6.087 | 1 | 6.087 | 2 | 6.087 | 2
103 | Classroom | 555 | 37 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 6.0326 | 1 | 6.0326 | 2 | 6.0326 | 2
104 | Classroom | 575 | 38 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 6.25 | 1 | 6.25 | 2 | 6.25 | 2
105 | Classroom | 618 | 41 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 6.7174 | 1 | 6.7174 | 2 | 6.7174 | 2
106 | Class Area | 163 | 10 |  |  | 625 | 14 | 10 | Unit Ventilator | 8 | 5000 | 1.956 | 1 | 1.956 | 1 | 1.956 | 1
106A | IT room | 280 | 18 |  |  | 304 | 6 | 6 | Unit Ventilator | 8 | 2432 | 6.9079 | 1 | 6.9079 | 2 | 6.9079 | 2
107 | Class Area | 155 | 10 |  |  | 1050 | 23 | 10 | Unit Ventilator | 8 | 8400 | 1.1071 | 1 | 1.1071 | 1 | 1.1071 | 1
108 | Class Area | 141 | 9 |  |  | 1050 | 23 | 9 | Unit Ventilator | 8 | 8400 | 1.0071 | 1 | 1.0071 | 1 | 1.0071 | 1
109 | Class Area | 143 | 9 |  |  | 625 | 14 | 9 | Unit Ventilator | 8 | 5000 | 1.716 | 1 | 1.716 | 1 | 1.716 | 1
110 | Class Area | 159 | 10 |  |  | 690 | 15 | 10 | Unit Ventilator | 8 | 5520 | 1.7283 | 1 | 1.7283 | 1 | 1.7283 | 1
111 | Class Area | 164 | 10 |  |  | 690 | 15 | 10 | Unit Ventilator | 8 | 5520 | 1.7826 | 1 | 1.7826 | 1 | 1.7826 | 1
112 | Class Area | 142 | 9 |  |  | 690 | 15 | 9 | Unit Ventilator | 8 | 5520 | 1.5435 | 1 | 1.5435 | 1 | 1.5435 | 1
113 | Class Area | 149 | 9 |  |  | 690 | 15 | 9 | Unit Ventilator | 8 | 5520 | 1.6196 | 1 | 1.6196 | 1 | 1.6196 | 1
114 | Class Area | 137 | 9 |  |  | 690 | 15 | 9 | Unit Ventilator | 8 | 5520 | 1.4891 | 1 | 1.4891 | 1 | 1.4891 | 1
114A | Team Planning | 0 | 0 |  |  | 360 | 8 | 0 | HUV | 8 | 2880 | 0 | 1 | 0 | 0 | 0 | 0
115 | Class | 141 | 9 |  |  | 690 | 15 | 9 | Unit Ventilator | 8 | 5520 | 1.5326 | 1 | 1.5326 | 1 | 1.5326 | 1
118D | Main Office | 0 | 0 |  |  | 150 | 3 | 0 | Unit Ventilator | 8 | 1200 | 0 | 1 | 0 | 0 | 0 | 0
119A | Instructional Storage | 0 | 0 |  |  |  | 0 | 0 | HUV
119B | Building Engineer's Office | 305 | 20 |  |  | 450 | 10 | 10 | Unit Ventilator | 8 | 3600 | 5.0833 | 1 | 5.0833 | 2 | 5.0833 | 2
120 | Instructional Materials Center | 303 | 20 |  |  | 2520 | 57 | 20 | Unit Ventilator | 8 | 20160 | 0.90179 | 1.062 | 0.95773 | 0 | 0.95773 | 0
122 | Main Office | 394 | 26 |  |  | 600 | 13 | 13 | Unit Ventilator | 8 | 4800 | 4.925 | 1 | 4.925 | 2 | 4.925 | 2
122C | Main Office | 301 | 20 |  |  | 130 | 2 | 2 | Unit Ventilator | 8 | 1040 | 17.3654 | 1 | 17.3654 | 3 | 17.3654 | 3
122D | Principal's Office | 383 | 25 |  |  | 216 | 4 | 4 | Unit Ventilator | 8 | 1728 | 13.2986 | 1 | 13.2986 | 3 | 13.2986 | 3
123 | Teacher's Dining | 355 | 23 |  |  | 594 | 13 | 13 | Unit Ventilator | 8 | 4752 | 4.4823 | 1 | 4.4823 | 2 | 4.4823 | 2
123A | Teacher's Lounge | 298 | 19 |  |  | 270 | 6 | 6 | Unit Ventilator | 8 | 2160 | 8.2778 | 1 | 8.2778 | 2 | 8.2778 | 2
127 | Corridor | 0 | 0 |  |  |  | 0 | 0 | HUV
150 | Storage | 163 | 10 |  |  | 360 | 8 | 8 | Unit Ventilator | 8 | 2880 | 3.3958 | 1 | 3.3958 | 1 | 3.3958 | 1
153 | Corridor | 0 | 0 |  |  |  | 0 | 0 | HUV
165 | Gym Office | 152 | 10 |  |  | 130 | 2 | 2 | Unit Ventilator | 8 | 1040 | 8.7692 | 1 | 8.7692 | 2 | 8.7692 | 2
184 | Examination | 153 | 10 |  |  | 130 | 2 | 2 | Unit Ventilator | 8 | 1040 | 8.8269 | 1 | 8.8269 | 2 | 8.8269 | 2
200 | Classroom | 622 | 41 |  |  | 1350 | 30 | 30 | Unit Ventilator | 8 | 10800 | 3.4556 | 1 | 3.4556 | 1 | 3.4556 | 1
201 | Classroom | 530 | 35 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 5.7609 | 1 | 5.7609 | 2 | 5.7609 | 2
201A | Instructional Storage | 0 | 0 |  |  |  | 0 | 0 | HUV
202 | Classroom | 519 | 34 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 5.6413 | 1 | 5.6413 | 2 | 5.6413 | 2
203 | Classroom | 434 | 28 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.7174 | 1 | 4.7174 | 2 | 4.7174 | 2
204 | Classroom | 550 | 36 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 5.9783 | 1 | 5.9783 | 2 | 5.9783 | 2
205 | Classroom | 436 | 29 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.7391 | 1 | 4.7391 | 2 | 4.7391 | 2
206 | Classroom | 500 | 33 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 5.4348 | 1 | 5.4348 | 2 | 5.4348 | 2
206A | Team Planning | 149 | 9 |  |  | 270 | 6 | 6 | Unit Ventilator | 8 | 2160 | 4.1389 | 1 | 4.1389 | 2 | 4.1389 | 2
207 | Classroom | 327 | 21 |  |  | 945 | 21 | 21 | Unit Ventilator | 8 | 7560 | 2.5952 | 1 | 2.5952 | 1 | 2.5952 | 1
208 | Corridor | 0 | 0 |  |  |  | 0 | 0 | HUV
208 | Classroom | 509 | 33 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 5.5326 | 1 | 5.5326 | 2 | 5.5326 | 2
209 | Classroom | 552 | 36 |  |  | 625 | 14 | 14 | Unit Ventilator | 8 | 5000 | 6.624 | 1 | 6.624 | 2 | 6.624 | 2
210 | Classroom | 694 | 46 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 7.5435 | 1 | 7.5435 | 2 | 7.5435 | 2
211 | Classroom | 531 | 35 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 5.7717 | 1 | 5.7717 | 2 | 5.7717 | 2
212 | Classroom | 379 | 25 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.1196 | 1 | 4.1196 | 2 | 4.1196 | 2
213 | Classroom | 688 | 45 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 7.4783 | 1 | 7.4783 | 2 | 7.4783 | 2
214 | Classroom | 382 | 25 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.1522 | 1 | 4.1522 | 2 | 4.1522 | 2
214A | Instructional Storage | 0 | 0 |  |  |  | 0 | 0 | HUV
215 | Classroom | 370 | 24 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 3.3036 | 1 | 3.3036 | 1 | 3.3036 | 1
216 | Classroom | 388 | 25 |  |  | 805 | 18 | 18 | Unit Ventilator | 8 | 6440 | 3.6149 | 1 | 3.6149 | 1 | 3.6149 | 1
217 | Classroom | 413 | 27 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 3.911 | 1 | 3.911 | 1 | 3.911 | 1
218 | Classroom | 328 | 21 |  |  | 625 | 14 | 14 | Unit Ventilator | 8 | 5000 | 3.936 | 1 | 3.936 | 1 | 3.936 | 1
218C | Classroom | 286 | 19 |  |  | 960 | 21 | 19 | Unit Ventilator | 8 | 7680 | 2.2344 | 1 | 2.2344 | 1 | 2.2344 | 1
219 | Classroom | 862 | 57 |  |  | 1800 | 40 | 40 | Unit Ventilator | 8 | 14400 | 3.5917 | 1 | 3.5917 | 1 | 3.5917 | 1
220 | Classroom | 980 | 65 |  |  | 1350 | 30 | 30 | Unit Ventilator | 8 | 10800 | 5.4444 | 1 | 5.4444 | 2 | 5.4444 | 2
221 | Classroom | 342 | 22 |  |  | 625 | 14 | 14 | Unit Ventilator | 8 | 5000 | 4.104 | 1 | 4.104 | 2 | 4.104 | 2
234 | Corridor | 0 | 0 |  |  |  | 0 | 0 | HUV
244 | Counselor | 0 | 0 |  |  |  | 0 | 0 | HUV
- | Nurse's Office | 279 | 18 |  |  | 150 | 3 | 3 | Unit Ventilator | 8 | 1200 | 13.95 | 1 | 13.95 | 3 | 13.95 | 3
Sheet Last Modified: | 2021-03-18
School: | James G. Blaine Elementary School
Vendor: | Devine Brothers Retest | 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Gym / Cafe. | 1104 | 73 |  |  | 3749 | 85 | 73 | Air Handling Unit | 8 | 29992 | 2.2086 | 1.062 | 2.3456 | 1 | 2.3456 | 1
- | Auditorium | 577 | 38 |  |  | 3161 | 71 | 38 | Air Handling Unit | 8 | 25288 | 1.369 | 1.062 | 1.454 | 1 | 1.454 | 1
100 | Classroom | 437 | 29 |  |  | 1415 | 32 | 29 | Unit Ventilator | 8 | 11320 | 2.3163 | 1 | 2.3163 | 1 | 2.3163 | 1
101 | Classroom | 684 | 45 |  |  | 1476 | 33 | 33 | Unit Ventilator | 8 | 11808 | 3.4756 | 1 | 3.4756 | 1 | 3.4756 | 1
102 | Classroom | 625 | 41 |  |  | 1460 | 33 | 33 | Unit Ventilator | 8 | 11680 | 3.2106 | 1 | 3.2106 | 1 | 3.2106 | 1
103 | Classroom | 461 | 30 |  |  | 1465 | 33 | 30 | Unit Ventilator | 8 | 11720 | 2.3601 | 1 | 2.3601 | 1 | 2.3601 | 1
104 | Classroom | 319 | 21 |  |  | 856 | 19 | 19 | Unit Ventilator | 8 | 6848 | 2.795 | 1 | 2.795 | 1 | 2.795 | 1
105 | Classroom | 306 | 20 |  |  | 655 | 14 | 14 | Unit Ventilator | 8 | 5240 | 3.5038 | 1 | 3.5038 | 1 | 3.5038 | 1
106 | Classroom | 452 | 30 |  |  | 921 | 20 | 20 | Unit Ventilator | 8 | 7368 | 3.6808 | 1 | 3.6808 | 1 | 3.6808 | 1
107 | Classroom | 274 | 18 |  |  | 970 | 22 | 18 | Unit Ventilator | 8 | 7760 | 2.1186 | 1 | 2.1186 | 1 | 2.1186 | 1
108 | Custodial | 251 | 16 |  |  | 835 | 18 | 16 | Unit Ventilator | 8 | 6680 | 2.2545 | 1 | 2.2545 | 1 | 2.2545 | 1
110 | Nurse |  | 0 | Yes | 20 | 452 | 10 | 10 | Unit Ventilator | 8 | 3616 | 0 | 1 | 0 | 0 | 20 | 3
200 | Classroom | 297 | 19 |  |  | 947 | 21 | 19 | Unit Ventilator | 8 | 7576 | 2.3522 | 1 | 2.3522 | 1 | 2.3522 | 1
201 | Classroom | 246 | 16 |  |  | 649 | 14 | 14 | Unit Ventilator | 8 | 5192 | 2.8428 | 1 | 2.8428 | 1 | 2.8428 | 1
202 | Classroom | 414 | 27 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 3.3173 | 1 | 3.3173 | 1 | 3.3173 | 1
203 | Classroom | 230 | 15 |  |  | 937 | 21 | 15 | Unit Ventilator | 8 | 7496 | 1.841 | 1 | 1.841 | 1 | 1.841 | 1
204 | Classroom | 359 | 23 |  |  | 958 | 21 | 21 | Unit Ventilator | 8 | 7664 | 2.8105 | 1 | 2.8105 | 1 | 2.8105 | 1
205 | Classroom | 286 | 19 |  |  | 937 | 21 | 19 | Unit Ventilator | 8 | 7496 | 2.2892 | 1 | 2.2892 | 1 | 2.2892 | 1
206 | Classroom | 447 | 29 |  |  | 952 | 21 | 21 | Unit Ventilator | 8 | 7616 | 3.5215 | 1 | 3.5215 | 1 | 3.5215 | 1
207 | Classroom | 291 | 19 |  |  | 956 | 21 | 19 | Unit Ventilator | 8 | 7648 | 2.2829 | 1 | 2.2829 | 1 | 2.2829 | 1
208 | Classroom | 314 | 20 |  |  | 968 | 22 | 20 | Unit Ventilator | 8 | 7744 | 2.4329 | 1 | 2.4329 | 1 | 2.4329 | 1
209 | Classroom | 349 | 23 |  |  | 975 | 22 | 22 | Unit Ventilator | 8 | 7800 | 2.6846 | 1 | 2.6846 | 1 | 2.6846 | 1
210 | Classroom | 236 | 15 |  |  | 931 | 21 | 15 | Unit Ventilator | 8 | 7448 | 1.9012 | 1 | 1.9012 | 1 | 1.9012 | 1
211 | Classroom | 287 | 19 |  |  | 982 | 22 | 19 | Unit Ventilator | 8 | 7856 | 2.192 | 1 | 2.192 | 1 | 2.192 | 1
212 | Classroom | 362 | 24 |  |  | 953 | 21 | 21 | Unit Ventilator | 8 | 7624 | 2.8489 | 1 | 2.8489 | 1 | 2.8489 | 1
213 | Classroom | 296 | 19 |  |  | 957 | 21 | 19 | Unit Ventilator | 8 | 7656 | 2.3197 | 1 | 2.3197 | 1 | 2.3197 | 1
214 | Classroom | 378 | 25 |  |  | 956 | 21 | 21 | Unit Ventilator | 8 | 7648 | 2.9655 | 1 | 2.9655 | 1 | 2.9655 | 1
215 | Classroom | 288 | 19 |  |  | 603 | 13 | 13 | Unit Ventilator | 8 | 4824 | 3.5821 | 1 | 3.5821 | 1 | 3.5821 | 1
216 | Classroom | 406 | 27 |  |  | 942 | 21 | 21 | Unit Ventilator | 8 | 7536 | 3.2325 | 1 | 3.2325 | 1 | 3.2325 | 1
217 | Classroom | 407 | 27 |  |  | 656 | 14 | 14 | Unit Ventilator | 8 | 5248 | 4.6532 | 1 | 4.6532 | 2 | 4.6532 | 2
300 | Classroom | 332 | 22 |  |  | 956 | 21 | 21 | Unit Ventilator | 8 | 7648 | 2.6046 | 1 | 2.6046 | 1 | 2.6046 | 1
301 | Classroom | 333 | 22 |  |  | 601 | 13 | 13 | Unit Ventilator | 8 | 4808 | 4.1556 | 1 | 4.1556 | 2 | 4.1556 | 2
302 | Classroom | 249 | 16 |  |  | 864 | 19 | 16 | Unit Ventilator | 8 | 6912 | 2.1615 | 1 | 2.1615 | 1 | 2.1615 | 1
303 | Classroom | 341 | 22 |  |  | 859 | 19 | 19 | Unit Ventilator | 8 | 6872 | 2.9773 | 1 | 2.9773 | 1 | 2.9773 | 1
304 | Classroom | 270 | 18 |  |  | 863 | 19 | 18 | Unit Ventilator | 8 | 6904 | 2.3465 | 1 | 2.3465 | 1 | 2.3465 | 1
305 | Classroom | 286 | 19 |  |  | 862 | 19 | 19 | Unit Ventilator | 8 | 6896 | 2.4884 | 1 | 2.4884 | 1 | 2.4884 | 1
306 | Classroom | 254 | 16 |  |  | 861 | 19 | 16 | Unit Ventilator | 8 | 6888 | 2.2125 | 1 | 2.2125 | 1 | 2.2125 | 1
307 | Classroom | 348 | 23 |  |  | 865 | 19 | 19 | Unit Ventilator | 8 | 6920 | 3.0173 | 1 | 3.0173 | 1 | 3.0173 | 1
308 | Classroom | 334 | 22 |  |  | 859 | 19 | 19 | Unit Ventilator | 8 | 6872 | 2.9162 | 1 | 2.9162 | 1 | 2.9162 | 1
309 | Classroom | 287 | 19 |  |  | 972 | 22 | 19 | Unit Ventilator | 8 | 7776 | 2.2145 | 1 | 2.2145 | 1 | 2.2145 | 1
310 | Classroom | 324 | 21 |  |  | 852 | 19 | 19 | Unit Ventilator | 8 | 6816 | 2.8521 | 1 | 2.8521 | 1 | 2.8521 | 1
311 | Classroom | 306 | 20 |  |  | 958 | 21 | 20 | Unit Ventilator | 8 | 7664 | 2.3956 | 1 | 2.3956 | 1 | 2.3956 | 1
312 | Classroom | 483 | 32 |  |  | 950 | 21 | 21 | Unit Ventilator | 8 | 7600 | 3.8132 | 1 | 3.8132 | 1 | 3.8132 | 1
313 | Classroom | 460 | 30 |  |  | 944 | 21 | 21 | Unit Ventilator | 8 | 7552 | 3.6547 | 1 | 3.6547 | 1 | 3.6547 | 1
314 | Classroom | 238 | 15 |  |  | 951 | 21 | 15 | Unit Ventilator | 8 | 7608 | 1.877 | 1 | 1.877 | 1 | 1.877 | 1
315 | Classroom | 359 | 23 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 4.0367 | 1 | 4.0367 | 2 | 4.0367 | 2
316 | Classroom | 315 | 21 |  |  | 952 | 21 | 21 | Unit Ventilator | 8 | 7616 | 2.4816 | 1 | 2.4816 | 1 | 2.4816 | 1
317 | Classroom | 288 | 19 |  |  | 651 | 14 | 14 | Unit Ventilator | 8 | 5208 | 3.318 | 1 | 3.318 | 1 | 3.318 | 1
- | Main Office |  | 0 | Yes | 20 | 1235 | 28 | 28 | Unit Ventilator | 8 | 9880 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal |  | 0 | Yes | 20 | 361 | 8 | 8 | Unit Ventilator | 8 | 2888 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-20
School: | Randolph Blankenburg Elementary-Middle School | House fan Abated
Vendor: | Devine | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
K-1 | Classroom | 906 | 60 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 9.652 | 1 | 9.652 | 2 | 9.652 | 2
K-4 | Classroom | 828 | 55 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 8.821 | 1 | 8.821 | 2 | 8.821 | 2
B27 | Classroom | 517 | 34 |  |  | 1047 | 23 | 23 | House Fan | 8 | 8376 | 3.7034 | 1 | 3.7034 | 1 | 3.7034 | 1
10A | Vice Principal | 0 | 0 | Yes | 20 | 176 | 4 | 4 | N/A | 8 | 1408 | 0 | 1 | 0 | 0 | 20 | 3
29 | Classroom | 594 | 39 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.3281 | 1 | 6.3281 | 2 | 6.3281 | 2
30 | Classroom | 930 | 62 |  |  | 836 | 19 | 19 | House Fan | 8 | 6688 | 8.3433 | 1 | 8.3433 | 2 | 8.3433 | 2
101 | Classroom | 890 | 59 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 9.4815 | 1 | 9.4815 | 2 | 9.4815 | 2
102 | Classroom | 63 | 4 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0.67116 | 1 | 0.67116 | 0 | 20.6712 | 3
103 | Classroom | 954 | 63 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 10.1634 | 1 | 10.1634 | 3 | 10.1634 | 3
105 | Classroom | 907 | 60 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 9.6626 | 1 | 9.6626 | 2 | 9.6626 | 2
106 | Classroom | 988 | 65 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 10.5256 | 1 | 10.5256 | 3 | 10.5256 | 3
107 | Classroom | 959 | 63 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 10.2166 | 1 | 10.2166 | 3 | 10.2166 | 3
208 | Classroom | 620 | 41 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.6051 | 1 | 6.6051 | 2 | 6.6051 | 2
208A | Nurse's Office | 0 | 0 |  |  | 176 | 4 | 0 | N/A | 8 | 1408 | 0 | 1 | 0 | 0 | 0 | 0
209 | Classroom | 695 | 46 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.4041 | 1 | 7.4041 | 2 | 7.4041 | 2
210 | Classroom | 930 | 62 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 9.9077 | 1 | 9.9077 | 2 | 9.9077 | 2
211 | Classroom | 887 | 59 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 9.4496 | 1 | 9.4496 | 2 | 9.4496 | 2
212 | Classroom | 751 | 50 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 8.0007 | 1 | 8.0007 | 2 | 8.0007 | 2
213 | Classroom | 955 | 63 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 10.174 | 1 | 10.174 | 3 | 10.174 | 3
214 | Classroom | 950 | 63 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 10.1207 | 1 | 10.1207 | 3 | 10.1207 | 3
316 | Classroom | 0 | 0 | Yes | 20 | 880 | 20 | 20 | House Fan | 8 | 7040 | 0 | 1 | 0 | 0 | 20 | 3
317 | Classroom | 361 | 24 |  |  | 484 | 11 | 11 | House Fan | 8 | 3872 | 5.594 | 1 | 5.594 | 2 | 5.594 | 2
318 | Classroom | 588 | 39 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.2642 | 1 | 6.2642 | 2 | 6.2642 | 2
319 | Classroom | 341 | 22 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 3.6328 | 1 | 3.6328 | 1 | 3.6328 | 1
320 | Classroom | 483 | 32 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 5.1456 | 1 | 5.1456 | 2 | 5.1456 | 2
321 | Classroom | 743 | 49 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.9155 | 1 | 7.9155 | 2 | 7.9155 | 2
322 | Classroom | 877 | 58 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 9.343 | 1 | 9.343 | 2 | 9.343 | 2
323 | Classroom | 642 | 42 |  |  | 748 | 17 | 17 | House Fan | 8 | 5984 | 6.4372 | 1 | 6.4372 | 2 | 6.4372 | 2
324 | Classroom | 818 | 54 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 8.7145 | 1 | 8.7145 | 2 | 8.7145 | 2
325 | Classroom | 809 | 53 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 8.6186 | 1 | 8.6186 | 2 | 8.6186 | 2
326 | Classroom | 565 | 37 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.0192 | 1 | 6.0192 | 2 | 6.0192 | 2
327 | Classroom | 698 | 46 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.4361 | 1 | 7.4361 | 2 | 7.4361 | 2
328 | Classroom | 151 | 10 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 1.6087 | 1 | 1.6087 | 1 | 21.6087 | 3
329 | Classroom | 0 | 0 | Yes | 20 | 264 | 6 | 6 | House Fan | 8 | 2112 | 0 | 1 | 0 | 0 | 20 | 3
2121 | Storage | 0 | 0 | Yes | 20 | 399 | 9 | 9 | House Fan | 8 | 3192 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 2451 | 163 |  |  | 3520 | 80 | 80 | House Fan | 8 | 28160 | 5.2223 | 1.062 | 5.5463 | 2 | 5.5463 | 2
- | Counselor Office | 0 | 0 | Yes | 20 | 220 | 5 | 5 | N/A | 8 | 1760 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym | 0 | 0 | Yes | 20 | 3872 | 88 | 88 | N/A | 8 | 30976 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Kitchen | 634 | 42 |  |  | 880 | 20 | 20 | House Fan | 8 | 7040 | 5.4034 | 1 | 5.4034 | 2 | 5.4034 | 2
- | Library | 865 | 57 |  |  | 1675 | 38 | 38 | House Fan | 8 | 13400 | 3.8731 | 1 | 3.8731 | 1 | 3.8731 | 1
- | Main Office | 0 | 0 | Yes | 20 | 308 | 7 | 7 | N/A | 8 | 2464 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office | 0 | 0 | Yes | 20 | 160 | 3 | 3 | N/A | 8 | 1280 | 0 | 1 | 0 | 0 | 20 | 3
- | SEL Classroom | 970 | 64 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 10.3338 | 1 | 10.3338 | 3 | 10.3338 | 3
- | Staff Lounge | 0 | 0 | Yes | 20 | 399 | 9 | 9 | N/A | 8 | 3192 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-17
School: | Bodine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
401 | Classroom |  | 0 |  |  | 660 | 15 | 0 |  | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
402 | classroom |  | 0 |  |  | 616 | 14 | 0 |  | 8 | 4928 | 0 | 1 | 0 | 0 | 0 | 0
403 | Classroom |  | 0 |  |  | 598 | 13 | 0 |  | 8 | 4784 | 0 | 1 | 0 | 0 | 0 | 0
404 | Classroom |  | 0 |  |  | 644 | 14 | 0 |  | 8 | 5152 | 0 | 1 | 0 | 0 | 0 | 0
405 A | Dept Head |  | 0 |  |  | 98 | 2 | 0 |  | 8 | 784 | 0 | 1 | 0 | 0 | 0 | 0
405 B | Counselor |  | 0 |  |  | 133 | 3 | 0 |  | 8 | 1064 | 0 | 1 | 0 | 0 | 0 | 0
406 | Classroom |  | 0 |  |  | 672 | 15 | 0 |  | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
407 | Classroom |  | 0 |  |  | 644 | 14 | 0 |  | 8 | 5152 | 0 | 1 | 0 | 0 | 0 | 0
408 | Computer |  | 0 |  |  | 726 | 16 | 0 |  | 8 | 5808 | 0 | 1 | 0 | 0 | 0 | 0
409 | Classroom |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom |  | 0 |  |  | 667 | 15 | 0 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
303 | Classroom |  | 0 |  |  | 644 | 14 | 0 |  | 8 | 5152 | 0 | 1 | 0 | 0 | 0 | 0
304 | Classroom |  | 0 |  |  | 621 | 14 | 0 |  | 8 | 4968 | 0 | 1 | 0 | 0 | 0 | 0
305 | Faculty Area |  | 0 |  |  | 450 | 10 | 0 |  | 8 | 3600 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom |  | 0 |  |  | 644 | 14 | 0 |  | 8 | 5152 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom |  | 0 |  |  | 644 | 14 | 0 |  | 8 | 5152 | 0 | 1 | 0 | 0 | 0 | 0
308 | Classrrom |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
309 | Classroom |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
202 | Classroom |  | 0 |  |  | 660 | 15 | 0 |  | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
203 | Library |  | 0 |  |  | 1058 | 24 | 0 |  | 8 | 8464 | 0 | 1 | 0 | 0 | 0 | 0
203 | Library office |  | 0 |  |  | 140 | 3 | 0 |  | 8 | 1120 | 0 | 1 | 0 | 0 | 0 | 0
205 | Classroom |  | 0 |  |  | 644 | 14 | 0 |  | 8 | 5152 | 0 | 1 | 0 | 0 | 0 | 0
206 | Classroom |  | 0 |  |  | 621 | 14 | 0 |  | 8 | 4968 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
208 | Classroom |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
102 | Classroom |  | 0 |  |  | 880 | 20 | 0 |  | 8 | 7040 | 0 | 1 | 0 | 0 | 0 | 0
103 | Counselor |  | 0 |  |  | 110 | 2 | 0 |  | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
104 | Teacher Lounge |  | 0 |  |  | 345 | 7 | 0 |  | 8 | 2760 | 0 | 1 | 0 | 0 | 0 | 0
105 A | Office |  | 0 |  |  | 63 | 1 | 0 |  | 8 | 504 | 0 | 1 | 0 | 0 | 0 | 0
105 B | Office |  | 0 |  |  | 108 | 2 | 0 |  | 8 | 864 | 0 | 1 | 0 | 0 | 0 | 0
105 C | Office |  | 0 |  |  | 81 | 1 | 0 |  | 8 | 648 | 0 | 1 | 0 | 0 | 0 | 0
108 | Room |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
109 | Room |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
2 | Art Room |  | 0 |  |  | 484 | 11 | 0 |  | 8 | 3872 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office |  | 0 |  |  | 322 | 7 | 0 |  | 8 | 2576 | 0 | 1 | 0 | 0 | 0 | 0
- | Principal Office |  | 0 |  |  | 96 | 2 | 0 |  | 8 | 768 | 0 | 1 | 0 | 0 | 0 | 0
- | Conferance Room |  | 0 |  |  | 220 | 5 | 0 |  | 8 | 1760 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym / Lunchroom |  | 0 |  |  | 2760 | 62 | 0 |  | 8 | 22080 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Kitchen |  | 0 |  |  | 648 | 14 | 0 |  | 8 | 5184 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-28
School: | Amedee F. Bregy Elementary-Middle School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Auditorium | 6957 | 463 |  |  | 4017 | 91 | 91 | House Fan | 8 | 32136 | 12.9892 | 1.062 | 13.795 | 3 | 13.795 | 3
- | Cafeteria | 934 | 62 |  |  | 1584 | 36 | 36 | House Fan | 8 | 12672 | 4.4223 | 1 | 4.4223 | 2 | 4.4223 | 2
- | Gym | 0 | 0 | Yes | 20 | 3872 | 88 | 88 | House Fan | 8 | 30976 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Library | 991 | 66 |  |  | 1739 | 39 | 39 | House Fan | 8 | 13912 | 4.274 | 1 | 4.274 | 2 | 4.274 | 2
- | Basement Science Classroom | 557 | 37 |  |  | 1064 | 24 | 24 | House Fan | 8 | 8512 | 3.9262 | 1 | 3.9262 | 1 | 3.9262 | 1
- | Basement Storage | 143 | 9 |  |  | 396 | 9 | 9 | House Fan | 8 | 3168 | 2.7083 | 1 | 2.7083 | 1 | 2.7083 | 1
- | Basement Boy's Bathroom | 471 | 31 |  |  | 528 | 12 | 12 | House Fan | 8 | 4224 | 6.6903 | 1 | 6.6903 | 2 | 6.6903 | 2
- | Basement Girl's Bathroom | 434 | 28 |  |  | 528 | 12 | 12 | House Fan | 8 | 4224 | 6.1648 | 1 | 6.1648 | 2 | 6.1648 | 2
101 | Classroom | 271 | 18 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 3.0795 | 1 | 3.0795 | 1 | 3.0795 | 1
102 | Classroom | 312 | 20 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 3.5455 | 1 | 3.5455 | 1 | 3.5455 | 1
1K1 | Classroom | 823 | 54 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 9.3523 | 1 | 9.3523 | 2 | 9.3523 | 2
103 | Classroom | 51 | 3 |  |  | 650 | 14 | 3 | House Fan | 8 | 5200 | 0.58846 | 1 | 0.58846 | 0 | 0.58846 | 0
104 | Classroom | 564 | 37 |  |  | 650 | 14 | 14 | House Fan | 8 | 5200 | 6.5077 | 1 | 6.5077 | 2 | 6.5077 | 2
105 | Classroom | 255 | 17 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 3.1047 | 1 | 3.1047 | 1 | 3.1047 | 1
106 | Classroom | 723 | 48 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 8.8028 | 1 | 8.8028 | 2 | 8.8028 | 2
107 | Classroom | 664 | 44 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 8.0844 | 1 | 8.0844 | 2 | 8.0844 | 2
208 | Classroom | 866 | 57 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 9.8409 | 1 | 9.8409 | 2 | 9.8409 | 2
209 | Classroom | 751 | 50 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 8.5341 | 1 | 8.5341 | 2 | 8.5341 | 2
210 | Classroom | 128 | 8 | Yes | 20 | 652 | 14 | 14 | House Fan | 8 | 5216 | 1.4724 | 1 | 1.4724 | 1 | 21.4724 | 3
211 | Classroom | 663 | 44 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 8.0722 | 1 | 8.0722 | 2 | 8.0722 | 2
212 | Classroom | 669 | 44 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 7.6023 | 1 | 7.6023 | 2 | 7.6023 | 2
213 | Classroom | 694 | 46 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 7.8864 | 1 | 7.8864 | 2 | 7.8864 | 2
214 | Classroom | 629 | 41 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 7.1477 | 1 | 7.1477 | 2 | 7.1477 | 2
215 | Classroom | 279 | 18 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 3.1705 | 1 | 3.1705 | 1 | 3.1705 | 1
316 | Classroom | 404 | 26 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 4.5909 | 1 | 4.5909 | 2 | 4.5909 | 2
317 | Classroom | 0 | 0 | Yes | 20 | 656 | 14 | 14 | House Fan | 8 | 5248 | 0 | 1 | 0 | 0 | 20 | 3
318 | Classroom | 577 | 38 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 6.5568 | 1 | 6.5568 | 2 | 6.5568 | 2
319 | Classroom | 231 | 15 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 2.625 | 1 | 2.625 | 1 | 2.625 | 1
320 | Classroom | 726 | 48 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.7344 | 1 | 7.7344 | 2 | 7.7344 | 2
321 | Classroom | 298 | 19 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 3.1747 | 1 | 3.1747 | 1 | 3.1747 | 1
322 | Classroom | 511 | 34 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 5.4439 | 1 | 5.4439 | 2 | 5.4439 | 2
323 | Classroom | 702 | 46 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 7.9773 | 1 | 7.9773 | 2 | 7.9773 | 2
324 | Classroom | 375 | 25 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 4.2614 | 1 | 4.2614 | 2 | 4.2614 | 2
325 | Classroom | 623 | 41 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 7.5852 | 1 | 7.5852 | 2 | 7.5852 | 2
326 | Classroom | 557 | 37 |  |  | 654 | 14 | 14 | House Fan | 8 | 5232 | 6.3876 | 1 | 6.3876 | 2 | 6.3876 | 2
327 | Classroom | 525 | 35 |  |  | 654 | 14 | 14 | House Fan | 8 | 5232 | 6.0206 | 1 | 6.0206 | 2 | 6.0206 | 2
328 | Classroom | 664 | 44 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 7.5455 | 1 | 7.5455 | 2 | 7.5455 | 2
- | Principal Office |  | 0 | Yes | 20 | 108 | 2 | 2 | House Fan | 8 | 864 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 220 | 5 | 5 | House Fan | 8 | 1760 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-07
School: | Bridesburg Elementary School
Vendor: | Goldner | Goldner Part 2
Devine Annex Retest
School: | Bridesburg Elementary School Annex
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
102 | Classroom | 422 | 28 |  |  | 846 | 19 | 19 | Unit Ventilator | 8 | 6768 | 3.7411 | 1 | 3.7411 | 1 | 3.7411 | 1
103 | Classroom | 377 | 25 |  |  | 686 | 15 | 15 | Unit Ventilator | 8 | 5488 | 4.1217 | 1 | 4.1217 | 2 | 4.1217 | 2
104 | Classroom | 476 | 31 |  |  | 993 | 22 | 22 | Unit Ventilator | 8 | 7944 | 3.5952 | 1 | 3.5952 | 1 | 3.5952 | 1
105 | Classroom | 300 | 20 |  |  | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 3.3482 | 1 | 3.3482 | 1 | 3.3482 | 1
106 | Classroom | 536 | 35 |  |  | 972 | 22 | 22 | Unit Ventilator | 8 | 7776 | 4.1358 | 1 | 4.1358 | 2 | 4.1358 | 2
107 | Classroom | 334 | 22 |  |  | 737 | 16 | 16 | Unit Ventilator | 8 | 5896 | 3.3989 | 1 | 3.3989 | 1 | 3.3989 | 1
108 | Classroom | 322 | 21 |  |  | 1030 | 23 | 21 | Unit Ventilator | 8 | 8240 | 2.3447 | 1 | 2.3447 | 1 | 2.3447 | 1
109 | Classroom | 294 | 19 |  |  | 684 | 15 | 15 | Unit Ventilator | 8 | 5472 | 3.2237 | 1 | 3.2237 | 1 | 3.2237 | 1
110A | Counselor's Office | 198 | 13 |  |  | 130 | 2 | 2 | Unit Ventilator | 8 | 1040 | 11.4231 | 1 | 11.4231 | 3 | 11.4231 | 3
111 | Classroom | 372 | 24 |  |  | 253 | 5 | 5 | Unit Ventilator | 8 | 2024 | 11.0277 | 1 | 11.0277 | 3 | 11.0277 | 3
112 | Nurse's Office | 272 | 18 |  |  | 369 | 8 | 8 | Unit Ventilator | 8 | 2952 | 5.5285 | 1 | 5.5285 | 2 | 5.5285 | 2
112A | Classroom | 0 | 0 |  |  | 218 | 4 | 0 | Unit Ventilator | 8 | 1744 | 0 | 1 | 0 | 0 | 0 | 0
112B | Classroom | 0 | 0 |  |  | 218 | 4 | 0 | Unit Ventilator | 8 | 1744 | 0 | 1 | 0 | 0 | 0 | 0
113 | Classroom | 137 | 9 |  |  | 117 | 2 | 2 | Unit Ventilator | 8 | 936 | 8.7821 | 1 | 8.7821 | 2 | 8.7821 | 2
114 | Classroom | 327 | 21 |  |  | 930 | 21 | 21 | Unit Ventilator | 8 | 7440 | 2.6371 | 1 | 2.6371 | 1 | 2.6371 | 1
115 | Classroom | 281 | 18 |  |  | 659 | 14 | 14 | Unit Ventilator | 8 | 5272 | 3.198 | 1 | 3.198 | 1 | 3.198 | 1
116 | Library | 1510 | 100 |  |  | 1700 | 38 | 38 | Unit Ventilator | 8 | 13600 | 6.6618 | 1 | 6.6618 | 2 | 6.6618 | 2
200 | Classroom | 0 | 0 | Yes | 20 | 754 | 17 | 17 | Unit Ventilator | 8 | 6032 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 136 | 9 |  |  | 609 | 13 | 9 | Unit Ventilator | 8 | 4872 | 1.6749 | 1 | 1.6749 | 1 | 1.6749 | 1
202 | Classroom | 312 | 20 |  |  | 539 | 12 | 12 | Unit Ventilator | 8 | 4312 | 4.3414 | 1 | 4.3414 | 2 | 4.3414 | 2
203 | Classroom | 377 | 25 |  |  | 714 | 16 | 16 | Unit Ventilator | 8 | 5712 | 3.9601 | 1 | 3.9601 | 1 | 3.9601 | 1
204 | Classroom | 152 | 10 |  |  | 695 | 15 | 10 | Unit Ventilator | 8 | 5560 | 1.6403 | 1 | 1.6403 | 1 | 1.6403 | 1
205 | Classroom | 1577 | 105 |  |  | 1129 | 25 | 25 | Unit Ventilator | 8 | 9032 | 10.4761 | 1 | 10.4761 | 3 | 10.4761 | 3
206 | Classroom | 157 | 10 |  |  | 715 | 16 | 10 | Unit Ventilator | 8 | 5720 | 1.6469 | 1 | 1.6469 | 1 | 1.6469 | 1
207 | Classroom | 247 | 16 |  |  | 725 | 16 | 16 | Unit Ventilator | 8 | 5800 | 2.5552 | 1 | 2.5552 | 1 | 2.5552 | 1
208 | Classroom | 351 | 23 |  |  | 650 | 14 | 14 | Unit Ventilator | 8 | 5200 | 4.05 | 1 | 4.05 | 2 | 4.05 | 2
209 | Classroom | 0 | 0 | Yes | 20 | 709 | 16 | 16 | Unit Ventilator | 8 | 5672 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom | 147 | 9 |  |  | 759 | 17 | 9 | Unit Ventilator | 8 | 6072 | 1.4526 | 1 | 1.4526 | 1 | 1.4526 | 1
211 | Classroom | 147 | 9 |  |  | 735 | 16 | 9 | Unit Ventilator | 8 | 5880 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1
212 | Classroom | 180 | 12 |  |  | 787 | 17 | 12 | Unit Ventilator | 8 | 6296 | 1.7154 | 1 | 1.7154 | 1 | 1.7154 | 1
213 | Classroom | 283 | 18 |  |  | 665 | 15 | 15 | Unit Ventilator | 8 | 5320 | 3.1917 | 1 | 3.1917 | 1 | 3.1917 | 1
214 | Classroom | 1248 | 83 |  |  | 845 | 19 | 19 | Unit Ventilator | 8 | 6760 | 11.0769 | 1 | 11.0769 | 3 | 11.0769 | 3
215 | Classroom | 457 | 30 |  |  | 677 | 15 | 15 | Unit Ventilator | 8 | 5416 | 5.0628 | 1 | 5.0628 | 2 | 5.0628 | 2
217 | Classroom | 282 | 18 |  |  | 735 | 16 | 16 | Unit Ventilator | 8 | 5880 | 2.8776 | 1 | 2.8776 | 1 | 2.8776 | 1
218 | Classroom | 292 | 19 |  |  | 601 | 13 | 13 | Unit Ventilator | 8 | 4808 | 3.6439 | 1 | 3.6439 | 1 | 3.6439 | 1
220 | Classroom | 287 | 19 |  |  | 706 | 16 | 16 | Unit Ventilator | 8 | 5648 | 3.0489 | 1 | 3.0489 | 1 | 3.0489 | 1
- | Hallway |  | 0 |  |  |  | 0 | 0 | HRU
- | Hallway 2 |  | 0 |  |  |  | 0 | 0 | HRU
- | Hallway Right |  | 0 |  |  |  | 0 | 0 | HRU
- | Hallways 2 Center |  | 0 |  |  |  | 0 | 0 | HRU
- | Gym | 0 | 0 |  |  | 3925 | 89 | 0 | N/A | 8 | 31400 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 |  |  | 3080 | 70 | 0 | N/A | 8 | 24640 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Kitchen | 0 | 0 |  |  | 697 | 15 | 0 | N/A | 8 | 5576 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office | 1167 | 77 |  |  | 752 | 17 | 17 | HRU | 8 | 6016 | 11.639 | 1 | 11.639 | 3 | 11.639 | 3
Bridesburg Elementary School Annex
1 | Classroom |  | 0 | Yes | 20 | 710 | 16 | 16 | N/A | 8 | 5680 | 0 | 1 | 0 | 0 | 20 | 3
2 | Staff Lounge |  | 0 | Yes | 20 | 504 | 11 | 11 | N/A | 8 | 4032 | 0 | 1 | 0 | 0 | 20 | 3
3 | Classroom |  | 0 | Yes | 20 | 575 | 13 | 13 | N/A | 8 | 4600 | 0 | 1 | 0 | 0 | 20 | 3
4 | Vice Principal |  | 0 | Yes | 20 | 245 | 5 | 5 | N/A | 8 | 1960 | 0 | 1 | 0 | 0 | 20 | 3
5 | Classroom |  | 0 | Yes | 20 | 693 | 15 | 15 | N/A | 8 | 5544 | 0 | 1 | 0 | 0 | 20 | 3
6 | Classroom |  | 0 | Yes | 20 | 732 | 16 | 16 | N/A | 8 | 5856 | 0 | 1 | 0 | 0 | 20 | 3
7 | Classroom |  | 0 | Yes | 20 | 773 | 17 | 17 | N/A | 8 | 6184 | 0 | 1 | 0 | 0 | 20 | 3
8 | Classroom |  | 0 | Yes | 20 | 589 | 13 | 13 | N/A | 8 | 4712 | 0 | 1 | 0 | 0 | 20 | 3
9 | Classroom |  | 0 | Yes | 20 | 610 | 13 | 13 | N/A | 8 | 4880 | 0 | 1 | 0 | 0 | 20 | 3
10 | Classroom |  | 0 | Yes | 20 | 623 | 14 | 14 | N/A | 8 | 4984 | 0 | 1 | 0 | 0 | 20 | 3
11 | Classroom |  | 0 | Yes | 20 | 581 | 13 | 13 | N/A | 8 | 4648 | 0 | 1 | 0 | 0 | 20 | 3
12 | Classroom |  | 0 | Yes | 20 | 569 | 12 | 12 | N/A | 8 | 4552 | 0 | 1 | 0 | 0 | 20 | 3
13 | Classroom |  | 0 | Yes | 20 | 625 | 14 | 14 | N/A | 8 | 5000 | 0 | 1 | 0 | 0 | 20 | 3
14 | Classroom |  | 0 | Yes | 20 | 576 | 13 | 13 | N/A | 8 | 4608 | 0 | 1 | 0 | 0 | 20 | 3
15 | Classroom |  | 0 | Yes | 20 | 547 | 12 | 12 | N/A | 8 | 4376 | 0 | 1 | 0 | 0 | 20 | 3
- | Support Room |  | 0 | Yes | 20 | 140 | 3 | 3 | N/A | 8 | 1120 | 0 | 1 | 0 | 0 | 20 | 3
- | Speech Room |  | 0 | Yes | 20 | 152 | 3 | 3 | N/A | 8 | 1216 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 144 | 3 | 3 | N/A | 8 | 1152 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 334 | 7 | 7 | N/A | 8 | 2672 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-23
School: | Henry A. Brown Elementary School
Vendor: | Devine | Retest Report
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Admin | 418 | 27 |  |  | 1058 | 24 | 24 | FCU | 8 | 8464 | 2.9631 | 1 | 2.9631 | 1 | 2.9631 | 1
- | Cafeteria | 2904 | 193 |  |  | 1994 | 45 | 45 | AHU | 8 | 15952 | 10.9228 | 1 | 10.9228 | 3 | 10.9228 | 3
- | Gym | 1581 | 105 |  |  | 3360 | 76 | 76 | AHU | 8 | 26880 | 3.529 | 1.062 | 3.7479 | 1 | 3.7479 | 1
- | Library | 488 | 32 |  |  | 1486 | 33 | 32 | FCU | 8 | 11888 | 2.463 | 1 | 2.463 | 1 | 2.463 | 1
- | Nurses Room | 133 | 8 |  |  | 290 | 6 | 6 | FCU | 8 | 2320 | 3.4397 | 1 | 3.4397 | 1 | 3.4397 | 1
- | Outside Library | 366 | 24 |  |  | 900 | 20 | 20 | FCU | 8 | 7200 | 3.05 | 1 | 3.05 | 1 | 3.05 | 1
100 | Classroom | 328 | 21 |  |  | 705 | 16 | 16 | Unit Ventilator | 8 | 5640 | 3.4894 | 1 | 3.4894 | 1 | 3.4894 | 1
101 | Classroom | 395 | 26 |  |  | 730 | 16 | 16 | Unit Ventilator | 8 | 5840 | 4.0582 | 1 | 4.0582 | 2 | 4.0582 | 2
113 | Classroom | 296 | 19 |  |  | 745 | 16 | 16 | Unit Ventilator | 8 | 5960 | 2.9799 | 1 | 2.9799 | 1 | 2.9799 | 1
114 | Classroom | 309 | 20 |  |  | 700 | 15 | 15 | Unit Ventilator | 8 | 5600 | 3.3107 | 1 | 3.3107 | 1 | 3.3107 | 1
151 | Classroom | 779 | 51 |  |  | 784 | 17 | 17 | FCU | 8 | 6272 | 7.4522 | 1 | 7.4522 | 2 | 7.4522 | 2
153 | Classroom | 689 | 45 |  |  | 895 | 20 | 20 | FCU | 8 | 7160 | 5.7737 | 1 | 5.7737 | 2 | 5.7737 | 2
154 | Classroom | 590 | 39 |  |  | 780 | 17 | 17 | FCU | 8 | 6240 | 5.6731 | 1 | 5.6731 | 2 | 5.6731 | 2
156 | Classroom | 647 | 43 |  |  | 835 | 18 | 18 | FCU | 8 | 6680 | 5.8114 | 1 | 5.8114 | 2 | 5.8114 | 2
200 | Classroom | 608 | 40 |  |  | 905 | 20 | 20 | Unit Ventilator | 8 | 7240 | 5.0387 | 1 | 5.0387 | 2 | 5.0387 | 2
201 | Classroom | 633 | 42 |  |  | 900 | 20 | 20 | Unit Ventilator | 8 | 7200 | 5.275 | 1 | 5.275 | 2 | 5.275 | 2
202 | Classroom |  | 0 | Yes | 20 | 655 | 14 | 14 |  | 8 | 5240 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 | Yes | 20 | 795 | 18 | 18 |  | 8 | 6360 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom |  | 0 | Yes | 20 | 655 | 14 | 14 |  | 8 | 5240 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom | 470 | 31 |  |  | 895 | 20 | 20 | Unit Ventilator | 8 | 7160 | 3.9385 | 1 | 3.9385 | 1 | 3.9385 | 1
212 | Classroom | 307 | 20 |  |  | 905 | 20 | 20 | Unit Ventilator | 8 | 7240 | 2.5442 | 1 | 2.5442 | 1 | 2.5442 | 1
213 | Classroom | 782 | 52 |  |  | 875 | 19 | 19 | Unit Ventilator | 8 | 7000 | 6.7029 | 1 | 6.7029 | 2 | 6.7029 | 2
214 | Classroom | 616 | 41 |  |  | 875 | 19 | 19 | Unit Ventilator | 8 | 7000 | 5.28 | 1 | 5.28 | 2 | 5.28 | 2
217 | Classroom | 250 | 16 |  |  | 665 | 15 | 15 | Unit Ventilator | 8 | 5320 | 2.8195 | 1 | 2.8195 | 1 | 2.8195 | 1
226 South | Classroom | 405 | 27 |  |  | 777 | 17 | 17 | Unit Ventilator | 8 | 6216 | 3.9093 | 1 | 3.9093 | 1 | 3.9093 | 1
226 West | Classroom | 458 | 30 |  |  | 777 | 17 | 17 | Unit Ventilator | 8 | 6216 | 4.4208 | 1 | 4.4208 | 2 | 4.4208 | 2
227 | Classroom | 487 | 32 |  |  | 740 | 16 | 16 | Unit Ventilator | 8 | 5920 | 4.9358 | 1 | 4.9358 | 2 | 4.9358 | 2
228 | Classroom | 685 | 45 |  |  | 775 | 17 | 17 | Unit Ventilator | 8 | 6200 | 6.629 | 1 | 6.629 | 2 | 6.629 | 2
229 | Computer Lab | 103 | 6 | Yes | 20 | 990 | 22 | 22 | FCU | 8 | 7920 | 0.7803 | 1 | 0.7803 | 0 | 20.7803 | 3
300 | Classroom | 582 | 38 |  |  | 905 | 20 | 20 | Unit Ventilator | 8 | 7240 | 4.8232 | 1 | 4.8232 | 2 | 4.8232 | 2
301 | Classroom | 535 | 35 |  |  | 890 | 20 | 20 | Unit Ventilator | 8 | 7120 | 4.5084 | 1 | 4.5084 | 2 | 4.5084 | 2
302 | Classroom | 151 | 10 |  |  | 695 | 15 | 10 | Unit Ventilator | 8 | 5560 | 1.6295 | 1 | 1.6295 | 1 | 1.6295 | 1
304 | Classroom | 445 | 29 |  |  | 825 | 18 | 18 | Unit Ventilator | 8 | 6600 | 4.0455 | 1 | 4.0455 | 2 | 4.0455 | 2
310 | Classroom | 657 | 43 |  |  | 715 | 16 | 16 | Unit Ventilator | 8 | 5720 | 6.8916 | 1 | 6.8916 | 2 | 6.8916 | 2
311 | Classroom | 241 | 16 |  |  | 935 | 21 | 16 | Unit Ventilator | 8 | 7480 | 1.9332 | 1 | 1.9332 | 1 | 1.9332 | 1
312 | Classroom | 426 | 28 |  |  | 935 | 21 | 21 | Unit Ventilator | 8 | 7480 | 3.4171 | 1 | 3.4171 | 1 | 3.4171 | 1
313 | Classroom | 327 | 21 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 2.6658 | 1 | 2.6658 | 1 | 2.6658 | 1
314 | Classroom | 512 | 34 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 4.1739 | 1 | 4.1739 | 2 | 4.1739 | 2
317 | Classroom | 165 | 11 |  |  | 660 | 15 | 11 | Unit Ventilator | 8 | 5280 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
318 | Classroom | 473 | 31 |  |  | 1090 | 24 | 24 | FCU | 8 | 8720 | 3.2546 | 1 | 3.2546 | 1 | 3.2546 | 1
319 | Classroom | 284 | 18 |  |  | 1125 | 25 | 18 | FCU | 8 | 9000 | 1.8933 | 1 | 1.8933 | 1 | 1.8933 | 1
322 South | Classroom | 174 | 11 |  |  | 745 | 16 | 11 | Unit Ventilator | 8 | 5960 | 1.7517 | 1 | 1.7517 | 1 | 1.7517 | 1
322 West | Classroom | 107 | 7 |  |  | 745 | 16 | 7 | Unit Ventilator | 8 | 5960 | 1.0772 | 1 | 1.0772 | 1 | 1.0772 | 1
323 | Classroom | 472 | 31 |  |  | 730 | 16 | 16 | Unit Ventilator | 8 | 5840 | 4.8493 | 1 | 4.8493 | 2 | 4.8493 | 2
324 | Classroom | 784 | 52 |  |  | 765 | 17 | 17 | Unit Ventilator | 8 | 6120 | 7.6863 | 1 | 7.6863 | 2 | 7.6863 | 2
325 West | Classroom | 533 | 35 |  |  | 890 | 20 | 20 | Unit Ventilator | 8 | 7120 | 4.4916 | 1 | 4.4916 | 2 | 4.4916 | 2
325 North | Classroom | 581 | 38 |  |  | 890 | 20 | 20 | Unit Ventilator | 8 | 7120 | 4.8961 | 1 | 4.8961 | 2 | 4.8961 | 2
Sheet Last Modified: | 2021-04-27
School: | Joseph H. Brown Elementary School
Vendor: | Emcor Mechanical Retest | Emcor Exhaust Report
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | GYM | 921 | 61 |  |  | 3510 | 79 | 61 | Unit Ventilator | 8 | 28080 | 1.9679 | 1.062 | 2.09 | 1 | 2.09 | 1
- | CAFE | 921 | 61 |  |  | 1440 | 32 | 32 | Unit Ventilator | 8 | 11520 | 4.7969 | 1 | 4.7969 | 2 | 4.7969 | 2
101 | classroom | 519 | 34 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 5.8358 | 1 | 5.8358 | 2 | 5.8358 | 2
102 | classroom | 562 | 37 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 6.3193 | 1 | 6.3193 | 2 | 6.3193 | 2
103 | classroom | 358 | 23 |  |  | 713 | 16 | 16 | Unit Ventilator | 8 | 5704 | 3.7658 | 1 | 3.7658 | 1 | 3.7658 | 1
104 | classroom | 932 | 62 |  |  | 851 | 19 | 19 | Unit Ventilator | 8 | 6808 | 8.2139 | 1 | 8.2139 | 2 | 8.2139 | 2
105 | classroom | 844 | 56 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 6.8804 | 1 | 6.8804 | 2 | 6.8804 | 2
106 | classroom | 786 | 52 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 6.4076 | 1 | 6.4076 | 2 | 6.4076 | 2
107 | classroom | 985 | 65 |  |  | 1104 | 25 | 25 | Unit Ventilator | 8 | 8832 | 6.6916 | 1 | 6.6916 | 2 | 6.6916 | 2
108 | classroom | 836 | 55 |  |  | 851 | 19 | 19 | Unit Ventilator | 8 | 6808 | 7.3678 | 1 | 7.3678 | 2 | 7.3678 | 2
109 | Counselor Office |  | 0 | Yes | 20 | 112 | 2 | 2 |  | 8 | 896 | 0 | 1 | 0 | 0 | 20 | 3
110 | Nurse Room |  | 0 |  |  | 224 | 5 | 0 | N/A | 8 | 1792 | 0 | 1 | 0 | 0 | 0 | 0
111 | Medical Waiting |  | 0 | Yes | 20 | 120 | 2 | 2 |  | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
200 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
201 | classroom | 394 | 26 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.2826 | 1 | 4.2826 | 2 | 4.2826 | 2
202 | classroom | 0 | 0 | Yes | 20 | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
203 | classroom | 417 | 27 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 4.6889 | 1 | 4.6889 | 2 | 4.6889 | 2
204 | classroom | 408 | 27 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.4348 | 1 | 4.4348 | 2 | 4.4348 | 2
205 | classroom | 550 | 36 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 5.9783 | 1 | 5.9783 | 2 | 5.9783 | 2
206 | classroom | 750 | 50 |  |  | 950 | 21 | 21 | Unit Ventilator | 8 | 7600 | 5.9211 | 1 | 5.9211 | 2 | 5.9211 | 2
206A | Room |  | 0 | Yes | 20 | 288 | 6 | 6 |  | 8 | 2304 | 0 | 1 | 0 | 0 | 20 | 3
207 | classroom | 484 | 32 |  |  | 506 | 11 | 11 | Unit Ventilator | 8 | 4048 | 7.1739 | 1 | 7.1739 | 2 | 7.1739 | 2
207A | Office |  | 0 | Yes | 20 | 168 | 3 | 3 |  | 8 | 1344 | 0 | 1 | 0 | 0 | 20 | 3
208 | classroom | 513 | 34 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 5.5761 | 1 | 5.5761 | 2 | 5.5761 | 2
209 | classroom | 723 | 48 |  |  | 713 | 16 | 16 | Unit Ventilator | 8 | 5704 | 7.6052 | 1 | 7.6052 | 2 | 7.6052 | 2
210 | classroom | 495 | 33 |  |  | 713 | 16 | 16 | Unit Ventilator | 8 | 5704 | 5.2069 | 1 | 5.2069 | 2 | 5.2069 | 2
211 | classroom | 376 | 25 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 4.2279 | 1 | 4.2279 | 2 | 4.2279 | 2
300 | classroom |  | 0 | Yes | 20 | 150 | 3 | 3 |  | 8 | 1200 | 0 | 1 | 0 | 0 | 20 | 3
301 | classroom | 605 | 40 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 6.8028 | 1 | 6.8028 | 2 | 6.8028 | 2
302 | classroom | 457 | 30 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.9674 | 1 | 4.9674 | 2 | 4.9674 | 2
303 | classroom | 389 | 25 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.2283 | 1 | 4.2283 | 2 | 4.2283 | 2
304 | classroom | 469 | 31 |  |  | 713 | 16 | 16 | Unit Ventilator | 8 | 5704 | 4.9334 | 1 | 4.9334 | 2 | 4.9334 | 2
305 | classroom | 0 | 0 | Yes | 20 | 713 | 16 | 16 | Unit Ventilator | 8 | 5704 | 0 | 1 | 0 | 0 | 20 | 3
306 | classroom | 0 | 0 | Yes | 20 | 874 | 19 | 19 | Unit Ventilator | 8 | 6992 | 0 | 1 | 0 | 0 | 20 | 3
307 | classroom | 419 | 27 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.5543 | 1 | 4.5543 | 2 | 4.5543 | 2
308 | classroom |  | 0 | Yes | 20 | 713 | 16 | 16 |  | 8 | 5704 | 0 | 1 | 0 | 0 | 20 | 3
Principal | Office |  | 0 | Yes | 20 | 160 | 3 | 3 |  | 8 | 1280 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 368 | 8 | 8 | N/A | 8 | 2944 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-29
School: | William C Bryant Elementary School | House fan Abated
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Gym | 1521 | 101 |  |  | 2765 | 62 | 62 | House Fan | 8 | 22120 | 4.1257 | 1.062 | 4.3816 | 2 | 4.3816 | 2
- | Shop Classroom | 795 | 53 |  |  | 740 | 16 | 16 | House Fan | 8 | 5920 | 8.0574 | 1 | 8.0574 | 2 | 8.0574 | 2
- | Art Room | 0 | 0 |  |  | 740 | 16 | 0 | House Fan | 8 | 5920 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria/Auditorium | 1853 | 123 |  |  | 2479 | 56 | 56 | AHU | 8 | 19832 | 5.6061 | 1 | 5.6061 | 2 | 5.6061 | 2
- | Principal's Office | 0 | 0 | Yes | 20 | 204 | 4 | 4 | House Fan | 8 | 1632 | 0 | 1 | 0 | 0 | 20 | 3
- | Office | 0 | 0 |  |  | 135 | 3 | 0 | House Fan | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom | 1717 | 114 |  |  | 1013 | 23 | 23 | House Fan | 8 | 8104 | 12.7122 | 1 | 12.7122 | 3 | 12.7122 | 3
102 | Classroom | 888 | 59 |  |  | 696 | 15 | 15 | House Fan | 8 | 5568 | 9.569 | 1 | 9.569 | 2 | 9.569 | 2
103 | Classroom | 853 | 56 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 9.2717 | 1 | 9.2717 | 2 | 9.2717 | 2
104 | Classroom | 653 | 43 |  |  | 740 | 16 | 16 | House Fan | 8 | 5920 | 6.6182 | 1 | 6.6182 | 2 | 6.6182 | 2
105 | Classroom | 0 | 0 | Yes | 20 | 700 | 15 | 15 | House Fan | 8 | 5600 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom | 0 | 0 | Yes | 20 | 740 | 16 | 16 | House Fan | 8 | 5920 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom | 0 | 0 | Yes | 20 | 718 | 16 | 16 | House Fan | 8 | 5744 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 20 | 795 | 18 | 18 | House Fan | 8 | 6360 | 0 | 1 | 0 | 0 | 20 | 3
110 | Nurse Office | 0 | 0 | Yes | 20 | 219 | 4 | 4 | House Fan | 8 | 1752 | 0 | 1 | 0 | 0 | 20 | 3
111 | - |  | 0 |  |  | 731 | 16 | 0 | House Fan | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
112 | Main Office |  | 0 | Yes | 20 | 707 | 16 | 16 | House Fan | 8 | 5656 | 0 | 1 | 0 | 0 | 20 | 3
113 | Classroom | 0 | 0 | Yes | 20 | 674 | 15 | 15 | House Fan | 8 | 5392 | 0 | 1 | 0 | 0 | 20 | 3
114 | Classroom | 0 | 0 | Yes | 20 | 713 | 16 | 16 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 1845 | 123 |  |  | 1013 | 23 | 23 | House Fan | 8 | 8104 | 13.6599 | 1 | 13.6599 | 3 | 13.6599 | 3
202 | Classroom | 843 | 56 |  |  | 686 | 15 | 15 | House Fan | 8 | 5488 | 9.2165 | 1 | 9.2165 | 2 | 9.2165 | 2
203 | Classroom | 108 | 7 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 1.1739 | 1 | 1.1739 | 1 | 21.1739 | 3
204 | Classroom | 893 | 59 |  |  | 740 | 16 | 16 | House Fan | 8 | 5920 | 9.0507 | 1 | 9.0507 | 2 | 9.0507 | 2
205 | Classroom | 0 | 0 | Yes | 20 | 700 | 15 | 15 | House Fan | 8 | 5600 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom | 0 | 0 | Yes | 20 | 740 | 16 | 16 | House Fan | 8 | 5920 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 20 | 718 | 16 | 16 | House Fan | 8 | 5744 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 20 | 795 | 18 | 18 | House Fan | 8 | 6360 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 |  |  | 753 | 17 | 0 | House Fan | 8 | 6024 | 0 | 1 | 0 | 0 | 0 | 0
210 | Classroom | 0 | 0 | Yes | 20 | 715 | 16 | 16 | House Fan | 8 | 5720 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom | 0 | 0 |  |  | 731 | 16 | 0 | House Fan | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
212 | Classroom | 0 | 0 | Yes | 20 | 707 | 16 | 16 | House Fan | 8 | 5656 | 0 | 1 | 0 | 0 | 20 | 3
213 | Classroom | 0 | 0 | Yes | 20 | 674 | 15 | 15 | House Fan | 8 | 5392 | 0 | 1 | 0 | 0 | 20 | 3
214 | Classroom | 0 | 0 |  |  | 713 | 16 | 0 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 0 | 0
- | IMC - Library | 0 | 0 |  |  | 2788 | 63 | 0 | Roof Top Unit | 8 | 22304 | 0 | 1.062 | 0 | 0 | 0 | 0
- | 2nd Flr Teacher's Lounge | 0 | 0 |  |  | 349 | 7 | 0 | House Fan | 8 | 2792 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom | 387 | 25 |  |  | 1013 | 23 | 23 | House Fan | 8 | 8104 | 2.8653 | 1 | 2.8653 | 1 | 2.8653 | 1
302 | Classroom | 748 | 49 |  |  | 686 | 15 | 15 | House Fan | 8 | 5488 | 8.1778 | 1 | 8.1778 | 2 | 8.1778 | 2
303 | Classroom | 68 | 4 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0.73913 | 1 | 0.73913 | 0 | 20.7391 | 3
304 | Classroom | 156 | 10 | Yes | 20 | 740 | 16 | 16 | House Fan | 8 | 5920 | 1.5811 | 1 | 1.5811 | 1 | 21.5811 | 3
305 | Classroom | 0 | 0 | Yes | 20 | 700 | 15 | 15 | House Fan | 8 | 5600 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 20 | 740 | 16 | 16 | House Fan | 8 | 5920 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 |  |  | 718 | 16 | 0 | House Fan | 8 | 5744 | 0 | 1 | 0 | 0 | 0 | 0
308 | Classroom | 0 | 0 |  |  | 795 | 18 | 0 | House Fan | 8 | 6360 | 0 | 1 | 0 | 0 | 0 | 0
309 | Classroom | 0 | 0 |  |  | 753 | 17 | 0 | House Fan | 8 | 6024 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom | 0 | 0 | Yes | 20 | 715 | 16 | 16 | House Fan | 8 | 5720 | 0 | 1 | 0 | 0 | 20 | 3
311 | Classroom | 0 | 0 | Yes | 20 | 731 | 16 | 16 | House Fan | 8 | 5848 | 0 | 1 | 0 | 0 | 20 | 3
312 | Classroom | 0 | 0 | Yes | 20 | 707 | 16 | 16 | House Fan | 8 | 5656 | 0 | 1 | 0 | 0 | 20 | 3
313 | Classroom | 0 | 0 | Yes | 20 | 674 | 15 | 15 | House Fan | 8 | 5392 | 0 | 1 | 0 | 0 | 20 | 3
314 | Classroom | 0 | 0 | Yes | 20 | 713 | 16 | 16 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 20 | 3
- | 3rd Flr Teacher's Lounge | 0 | 0 |  |  | 349 | 7 | 0 | House Fan | 8 | 2792 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-17
School: | Building 21 (Kinsey)
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
600 | Classroom |  | 0 |  |  | 810 | 18 | 0 |  | 8 | 6480 | 0 | 1 | 0 | 0 | 0 | 0
2 | Classroom |  | 0 |  |  | 1104 | 25 | 0 |  | 8 | 8832 | 0 | 1 | 0 | 0 | 0 | 0
4 | Classroom |  | 0 |  |  | 884 | 20 | 0 |  | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
5 | Kitchen |  | 0 |  |  | 910 | 20 | 0 |  | 8 | 7280 | 0 | 1 | 0 | 0 | 0 | 0
112 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
112A | Nurse |  | 0 |  |  | 99 | 2 | 0 |  | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
111 | Office |  | 0 |  |  | 319 | 7 | 0 |  | 8 | 2552 | 0 | 1 | 0 | 0 | 0 | 0
111A | Office |  | 0 |  |  | 140 | 3 | 0 |  | 8 | 1120 | 0 | 1 | 0 | 0 | 0 | 0
111B | Office |  | 0 |  |  | 168 | 3 | 0 |  | 8 | 1344 | 0 | 1 | 0 | 0 | 0 | 0
113 | Office |  | 0 |  |  | 475 | 10 | 0 |  | 8 | 3800 | 0 | 1 | 0 | 0 | 0 | 0
113A | Office |  | 0 |  |  | 81 | 1 | 0 |  | 8 | 648 | 0 | 1 | 0 | 0 | 0 | 0
113B | Office |  | 0 |  |  | 81 | 1 | 0 |  | 8 | 648 | 0 | 1 | 0 | 0 | 0 | 0
110 | Main Office |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
115 | Classroom |  | 0 |  |  | 140 | 3 | 0 |  | 8 | 1120 | 0 | 1 | 0 | 0 | 0 | 0
114 | Classroom |  | 0 |  |  | 81 | 1 | 0 |  | 8 | 648 | 0 | 1 | 0 | 0 | 0 | 0
109 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
108 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
107 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
106 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
104 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
102 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
116 | Aud |  | 0 |  |  | 5244 | 119 | 0 |  | 8 | 41952 | 0 | 1.062 | 0 | 0 | 0 | 0
201 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
202 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
203 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
204 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
205 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
206 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
208 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
210 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
211 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
212 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
213 | Nurse |  | 0 |  |  | 295 | 6 | 0 |  | 8 | 2360 | 0 | 1 | 0 | 0 | 0 | 0
214 | Office |  | 0 |  |  | 140 | 3 | 0 |  | 8 | 1120 | 0 | 1 | 0 | 0 | 0 | 0
209 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
215 | Office |  | 0 |  |  | 140 | 3 | 0 |  | 8 | 1120 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
303 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
304 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
305 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
308 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
309 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
311 | Classroom |  | 0 |  |  | 710 | 16 | 0 |  | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21
School: | Camelot Academy @ Boone
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
300 | Office | 292 | 19 |  |  | 370 | 8 | 8 | Univent | 8 | 2960 | 5.9189 | 1 | 5.9189 | 2 | 5.9189 | 2
301 | Classroom | 335 | 22 |  |  | 803 | 18 | 18 | Univent | 8 | 6424 | 3.1289 | 1 | 3.1289 | 1 | 3.1289 | 1
302 | Classroom | 281 | 18 |  |  | 816 | 18 | 18 | Univent | 8 | 6528 | 2.5827 | 1 | 2.5827 | 1 | 2.5827 | 1
304 | Classroom | 292 | 19 |  |  | 1808 | 41 | 19 | Univent | 8 | 14464 | 1.2113 | 1 | 1.2113 | 1 | 1.2113 | 1
305 (309) | Classroom | 330 | 22 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 2.9083 | 1 | 2.9083 | 1 | 2.9083 | 1
306 | Classroom | 364 | 24 |  |  | 966 | 21 | 21 | Univent | 8 | 7728 | 2.8261 | 1 | 2.8261 | 1 | 2.8261 | 1
307 | Classroom | 348 | 23 |  |  | 1647 | 37 | 23 | Univent | 8 | 13176 | 1.5847 | 1 | 1.5847 | 1 | 1.5847 | 1
308 | Office | 266 | 17 |  |  | 494 | 11 | 11 | Univent | 8 | 3952 | 4.0385 | 1 | 4.0385 | 2 | 4.0385 | 2
310 | Office | 135 | 9 |  |  | 399 | 9 | 9 | Univent | 8 | 3192 | 2.5376 | 1 | 2.5376 | 1 | 2.5376 | 1
312 | Classroom | 293 | 19 |  |  | 663 | 15 | 15 | Univent | 8 | 5304 | 3.3145 | 1 | 3.3145 | 1 | 3.3145 | 1
314 | Classroom | 218 | 14 |  |  | 458 | 10 | 10 | Univent | 8 | 3664 | 3.5699 | 1 | 3.5699 | 1 | 3.5699 | 1
316 | Classroom | 367 | 24 |  |  | 877 | 19 | 19 | Univent | 8 | 7016 | 3.1385 | 1 | 3.1385 | 1 | 3.1385 | 1
- | Principal Office | 424 | 28 |  |  | 312 | 7 | 7 | ERU | 8 | 2496 | 10.1923 | 1 | 10.1923 | 3 | 10.1923 | 3
200 | Classroom | 332 | 22 |  |  | 807 | 18 | 18 | Univent | 8 | 6456 | 3.0855 | 1 | 3.0855 | 1 | 3.0855 | 1
201 | Classroom | 305 | 20 |  |  | 593 | 13 | 13 | Univent | 8 | 4744 | 3.8575 | 1 | 3.8575 | 1 | 3.8575 | 1
202 | Classroom | 287 | 19 |  |  | 589 | 13 | 13 | Univent | 8 | 4712 | 3.6545 | 1 | 3.6545 | 1 | 3.6545 | 1
204 | Classroom | 300 | 20 |  |  | 1084 | 24 | 20 | Univent | 8 | 8672 | 2.0756 | 1 | 2.0756 | 1 | 2.0756 | 1
206 | Classroom | 434 | 28 |  |  | 962 | 21 | 21 | Univent | 8 | 7696 | 3.3836 | 1 | 3.3836 | 1 | 3.3836 | 1
207 | Classroom | 326 | 21 |  |  | 880 | 20 | 20 | Univent | 8 | 7040 | 2.7784 | 1 | 2.7784 | 1 | 2.7784 | 1
208 | Office | 239 | 15 |  |  | 494 | 11 | 11 | Univent | 8 | 3952 | 3.6285 | 1 | 3.6285 | 1 | 3.6285 | 1
209 | Classroom | 349 | 23 |  |  | 879 | 19 | 19 | Univent | 8 | 7032 | 2.9778 | 1 | 2.9778 | 1 | 2.9778 | 1
- | Academic Office | 308 | 20 |  |  | 311 | 7 | 7 | Univent | 8 | 2488 | 7.4277 | 1 | 7.4277 | 2 | 7.4277 | 2
- | Operations Office | 348 | 23 |  |  | 395 | 8 | 8 | ERU | 8 | 3160 | 6.6076 | 1 | 6.6076 | 2 | 6.6076 | 2
212 | Classroom | 380 | 25 |  |  | 567 | 12 | 12 | Univent | 8 | 4536 | 5.0265 | 1 | 5.0265 | 2 | 5.0265 | 2
214 | Classroom | 397 | 26 |  |  | 652 | 14 | 14 | Univent | 8 | 5216 | 4.5667 | 1 | 4.5667 | 2 | 4.5667 | 2
216 | Classroom | 408 | 27 |  |  | 651 | 14 | 14 | Univent | 8 | 5208 | 4.7005 | 1 | 4.7005 | 2 | 4.7005 | 2
104 | Conference Room | 424 | 28 |  |  | 497 | 11 | 11 | Univent | 8 | 3976 | 6.3984 | 1 | 6.3984 | 2 | 6.3984 | 2
- | Main Office | 372 | 24 |  |  | 1055 | 23 | 23 | Univent | 8 | 8440 | 2.6445 | 1 | 2.6445 | 1 | 2.6445 | 1
102 | Computer Lab | 304 | 20 | Yes | 20 | 1019 | 23 | 23 | Univent | 8 | 8152 | 2.2375 | 1 | 2.2375 | 1 | 22.2375 | 3
B5 | Classroom | 310 | 20 |  |  | 1248 | 28 | 20 | Univent | 8 | 9984 | 1.863 | 1 | 1.863 | 1 | 1.863 | 1
B6 | Cosmo Room 1 | 290 | 19 |  |  | 535 | 12 | 12 | Univent | 8 | 4280 | 4.0654 | 1 | 4.0654 | 2 | 4.0654 | 2
B7 | Hair Salon | 443 | 29 |  |  | 693 | 15 | 15 | Univent | 8 | 5544 | 4.7944 | 1 | 4.7944 | 2 | 4.7944 | 2
B8 | Barbershop | 275 | 18 |  |  | 539 | 12 | 12 | Univent | 8 | 4312 | 3.8265 | 1 | 3.8265 | 1 | 3.8265 | 1
Sheet Last Modified: | 2021-04-14
School: | Philadelphia High School for the Creative & Performing Arts
Vendor: | Chadwick | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
109 | Room | 714 | 47 |  |  | 1215.8 | 27 | 27 |  | 8 | 9726.4 | 4.4045 | 1 | 4.4045 | 2 | 4.4045 | 2
108 | Room | 0 | 0 |  |  | 872.49 | 19 | 0 |  | 8 | 6979.92 | 0 | 1 | 0 | 0 | 0 | 0
107 | Room | 468 | 31 |  |  | 1182.7 | 26 | 26 |  | 8 | 9461.6 | 2.9678 | 1 | 2.9678 | 1 | 2.9678 | 1
105 | Room | 0 | 0 |  |  | 1171.6 | 26 | 0 |  | 8 | 9372.8 | 0 | 1 | 0 | 0 | 0 | 0
110 | Office | 45 | 3 |  |  | 171.71 | 3 | 3 |  | 8 | 1373.68 | 1.9655 | 1 | 1.9655 | 1 | 1.9655 | 1
- | First Floor North Corridor | 290 | 19 |  |  | 3004.3 | 68 | 19 |  | 8 | 24034.4 | 0.72396 | 1.062 | 0.76887 | 0 | 0.76887 | 0
- | First Floor South Corridor | 118 | 7 |  |  | 1139.3 | 25 | 7 |  | 8 | 9114.4 | 0.77679 | 1 | 0.77679 | 0 | 0.77679 | 0
116 | Room | -100 | -6 |  |  | 216.61 | 4 | -6 |  | 8 | 1732.88 | 3.4624 | 1 | 3.4624 | 1 | 3.4624 | 1
106 | Editing Suite | 15 | 1 |  |  | 112.47 | 2 | 1 |  | 8 | 899.76 | 1.0003 | 1 | 1.0003 | 1 | 1.0003 | 1
106 | Room |  | 0 |  |  | 1119.1 | 25 | 0 |  | 8 | 8952.8 | 0 | 1 | 0 | 0 | 0 | 0
114 | Room | -61 | -4 |  |  | 845.65 | 19 | -4 |  | 8 | 6765.2 | 0.541 | 1 | 0.541 | 0 | 0.541 | 0
116 | Control Room | 219 | 14 |  |  | 327.76 | 7 | 7 |  | 8 | 2622.08 | 5.0113 | 1 | 5.0113 | 2 | 5.0113 | 2
- | Second Floor South Corridor Outside Stair 4 | 45 | 3 |  |  | 2223.7 | 50 | 3 |  | 8 | 17789.6 | 0.15177 | 1 | 0.15177 | 0 | 0.15177 | 0
- | Second Floor South Corridor | 0 | 0 |  |  | 1642.3 | 37 | 0 |  | 8 | 13138.4 | 0 | 1 | 0 | 0 | 0 | 0
- | Second Floor North Corridor | 301 | 20 |  |  | 1642.3 | 37 | 20 |  | 8 | 13138.4 | 1.3746 | 1 | 1.3746 | 1 | 1.3746 | 1
202 | Room | 78 | 5 |  |  | 275.81 | 6 | 5 |  | 8 | 2206.48 | 2.121 | 1 | 2.121 | 1 | 2.121 | 1
203 | Room | 142 | 9 |  |  | 1209.4 | 27 | 9 |  | 8 | 9675.2 | 0.8806 | 1 | 0.8806 | 0 | 0.8806 | 0
204 | Room | 616 | 41 |  |  | 1059.9 | 24 | 24 |  | 8 | 8479.2 | 4.3589 | 1 | 4.3589 | 2 | 4.3589 | 2
205 | Room | 607 | 40 |  |  | 874.01 | 19 | 19 |  | 8 | 6992.08 | 5.2088 | 1 | 5.2088 | 2 | 5.2088 | 2
206 | Room | 0 | 0 |  |  | 1206.6 | 27 | 0 |  | 8 | 9652.8 | 0 | 1 | 0 | 0 | 0 | 0
207 | Room | 613 | 40 |  |  | 891.99 | 20 | 20 |  | 8 | 7135.92 | 5.1542 | 1 | 5.1542 | 2 | 5.1542 | 2
208 | Room | 809 | 53 |  |  | 870.75 | 19 | 19 |  | 8 | 6966 | 6.9681 | 1 | 6.9681 | 2 | 6.9681 | 2
209 | Room | 584 | 38 |  |  | 871.76 | 19 | 19 |  | 8 | 6974.08 | 5.0243 | 1 | 5.0243 | 2 | 5.0243 | 2
210 | Room | 304 | 20 |  |  | 791.75 | 17 | 17 |  | 8 | 6334 | 2.8797 | 1 | 2.8797 | 1 | 2.8797 | 1
211 | Room | 420 | 28 |  |  | 1119.8 | 25 | 25 |  | 8 | 8958.4 | 2.813 | 1 | 2.813 | 1 | 2.813 | 1
213 | Room | -85 | -5 |  |  | 815.15 | 18 | -5 |  | 8 | 6521.2 | 0.78206 | 1 | 0.78206 | 0 | 0.78206 | 0
214 | Room | 567 | 37 |  |  | 1351.8 | 30 | 30 |  | 8 | 10814.4 | 3.1458 | 1 | 3.1458 | 1 | 3.1458 | 1
304 | Room | 15 | 1 |  |  | 1059.9 | 24 | 1 |  | 8 | 8479.2 | 0.10614 | 1 | 0.10614 | 0 | 0.10614 | 0
305 | Room | 70 | 4 |  |  | 192.7 | 4 | 4 |  | 8 | 1541.6 | 2.7244 | 1 | 2.7244 | 1 | 2.7244 | 1
306 | Room | 122 | 8 |  |  | 888.58 | 20 | 8 |  | 8 | 7108.64 | 1.0297 | 1 | 1.0297 | 1 | 1.0297 | 1
307 | Room | 0 | 0 |  |  | 251.97 | 5 | 0 |  | 8 | 2015.76 | 0 | 1 | 0 | 0 | 0 | 0
308 | Room | 533 | 35 |  |  | 1094.9 | 24 | 24 |  | 8 | 8759.2 | 3.651 | 1 | 3.651 | 1 | 3.651 | 1
310 | Room | 527 | 35 |  |  | 877.6 | 19 | 19 |  | 8 | 7020.8 | 4.5038 | 1 | 4.5038 | 2 | 4.5038 | 2
311 | Room | 824 | 54 |  |  | 1209 | 27 | 27 |  | 8 | 9672 | 5.1117 | 1 | 5.1117 | 2 | 5.1117 | 2
312 | Room | 101 | 6 |  |  | 892.16 | 20 | 6 |  | 8 | 7137.28 | 0.84906 | 1 | 0.84906 | 0 | 0.84906 | 0
313 | Room | -121 | -8 |  |  | 870.18 | 19 | -8 |  | 8 | 6961.44 | 1.0429 | 1 | 1.0429 | 1 | 1.0429 | 1
314 | Room | 342 | 22 |  |  | 771.96 | 17 | 17 |  | 8 | 6175.68 | 3.3227 | 1 | 3.3227 | 1 | 3.3227 | 1
315 | Room | -455 | -30 |  |  | 888.8 | 20 | -30 |  | 8 | 7110.4 | 3.8394 | 1 | 3.8394 | 1 | 3.8394 | 1
316 | Room | 1080 | 72 |  |  | 1532.3 | 34 | 34 |  | 8 | 12258.4 | 5.2862 | 1 | 5.2862 | 2 | 5.2862 | 2
317 | Room | 754 | 50 |  |  | 850.53 | 19 | 19 |  | 8 | 6804.24 | 6.6488 | 1 | 6.6488 | 2 | 6.6488 | 2
318 | Room | 849 | 56 |  |  | 1015 | 23 | 23 |  | 8 | 8120 | 6.2734 | 1 | 6.2734 | 2 | 6.2734 | 2
320 | Room | -20 | -1 |  |  | 94.85 | 2 | -1 |  | 8 | 758.8 | 1.5814 | 1 | 1.5814 | 1 | 1.5814 | 1
321 | Room | -15 | -1 |  |  | 77.87 | 1 | -1 |  | 8 | 622.96 | 1.4447 | 1 | 1.4447 | 1 | 1.4447 | 1
322 | Room | -17 | -1 |  |  | 58.45 | 1 | -1 |  | 8 | 467.6 | 2.1814 | 1 | 2.1814 | 1 | 2.1814 | 1
323 | Room | 35 | 2 |  |  | 1013.7 | 23 | 2 |  | 8 | 8109.6 | 0.25895 | 1 | 0.25895 | 0 | 0.25895 | 0
324 | Room | 30 | 2 |  |  | 257.05 | 5 | 2 |  | 8 | 2056.4 | 0.87532 | 1 | 0.87532 | 0 | 0.87532 | 0
326 | Room | -297 | -19 |  |  |  | 0 | -19
- | Third Floor North Corridor | 303 | 20 |  |  | 1655.3 | 37 | 20 |  | 8 | 13242.4 | 1.3729 | 1 | 1.3729 | 1 | 1.3729 | 1
- | Third Floor South Corridor | 0 | 0 |  |  | 1655.3 | 37 | 0 |  | 8 | 13242.4 | 0 | 1 | 0 | 0 | 0 | 0
400 | Room | 932 | 62 |  |  | 1893.6 | 43 | 43 |  | 8 | 15148.8 | 3.6914 | 1 | 3.6914 | 1 | 3.6914 | 1
401 | Room | 302 | 20 |  |  | 1794.2 | 40 | 20 |  | 8 | 14353.6 | 1.2624 | 1 | 1.2624 | 1 | 1.2624 | 1
402 | Room | 615 | 41 |  |  | 2176.1 | 49 | 41 |  | 8 | 17408.8 | 2.1196 | 1 | 2.1196 | 1 | 2.1196 | 1
403 | Room | -67 | -4 |  |  | 216.87 | 4 | -4 |  | 8 | 1734.96 | 2.3171 | 1 | 2.3171 | 1 | 2.3171 | 1
403 | Print Room | 130 | 8 |  |  | 275.87 | 6 | 6 |  | 8 | 2206.96 | 3.5343 | 1 | 3.5343 | 1 | 3.5343 | 1
403 | Room | 52 | 3 |  |  | 2280.1 | 51 | 3 |  | 8 | 18240.8 | 0.17105 | 1 | 0.17105 | 0 | 0.17105 | 0
404 | Room | 226 | 15 |  |  | 1882.5 | 42 | 15 |  | 8 | 15060 | 0.9004 | 1 | 0.9004 | 0 | 0.9004 | 0
405 | Room | 390 | 26 |  |  | 1656.39 | 37 | 26 |  | 8 | 13251.12 | 1.7659 | 1 | 1.7659 | 1 | 1.7659 | 1
405 | Prep Room | 45 | 3 |  |  |  | 0 | 0
406 | Room | 710 | 47 |  |  |  | 0 | 0
407 | Room | 113 | 7 |  |  |  | 0 | 0
408 | Room | 0 | 0 |  |  | 217.94 | 4 | 0 |  | 8 | 1743.52 | 0 | 1 | 0 | 0 | 0 | 0
- | 4th Floor Corridor South | 0 | 0 |  |  | 1677.4 | 38 | 0 |  | 8 | 13419.2 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23
School: | Laura H. Carnell Elementary School
| Laura H. Carnell Little School House | House Fan Abated
Vendor: | Devine Brothers | LSH Retest
| EMCOR | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
- | Basement Corridor | 0 | 0 |  |  | 450 | 10 | 0 | Unit Ventilator | 8 | 3600 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym Office | 0 | 0 |  |  | 144 | 3 | 0 | N/A | 8 | 1152 | 0 | 1 | 0 | 0 | 0 | 0
B-3 | Art | 0 | 0 |  |  | 920 | 20 | 0 | House Fan | 8 | 7360 | 0 | 1 | 0 | 0 | 0 | 0
B-4 | Music | 0 | 0 |  |  | 660 | 15 | 0 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
B1 | Counselors | 0 | 0 |  |  | 630 | 14 | 0 | House Fan | 8 | 5040 | 0 | 1 | 0 | 0 | 0 | 0
B2 | Family Resource | 0 | 0 |  |  | 1023 | 23 | 0 | House Fan | 8 | 8184 | 0 | 1 | 0 | 0 | 0 | 0
B5 | Classroom | 519 | 34 |  |  | 800 | 18 | 18 | Unit Ventilator | 8 | 6400 | 4.8656 | 1 | 4.8656 | 2 | 4.8656 | 2
B6 | Classroom | 110 | 7 |  |  | 800 | 18 | 7 | Unit Ventilator | 8 | 6400 | 1.0312 | 1 | 1.0312 | 1 | 1.0312 | 1
B7 | Classroom | 421 | 28 |  |  | 800 | 18 | 18 | Unit Ventilator | 8 | 6400 | 3.9469 | 1 | 3.9469 | 1 | 3.9469 | 1
- | 1st flr Corridor |  | 0 |  |  | 828 | 18 | 0 | Unit Ventilator | 8 | 6624 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office | 0 | 0 |  |  | 483 | 10 | 0 | N/A | 8 | 3864 | 0 | 1 | 0 | 0 | 0 | 0
- | Principal's Office | 0 | 0 |  |  | 304 | 6 | 0 | N/A | 8 | 2432 | 0 | 1 | 0 | 0 | 0 | 0
- | 1st Flr Security | 0 | 0 |  |  | 81 | 1 | 0 | N/A | 8 | 648 | 0 | 1 | 0 | 0 | 0 | 0
- | 1st Flr Counselors | 0 | 0 |  |  | 126 | 2 | 0 | N/A | 8 | 1008 | 0 | 1 | 0 | 0 | 0 | 0
- | 1st Flr Office |  | 0 |  |  | 216 | 4 | 0 | N/A | 8 | 1728 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom | 0 | 0 | Yes | 20 | 957 | 21 | 21 | House Fan | 8 | 7656 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom | 0 | 0 |  |  | 870 | 19 | 0 | House Fan | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom | 0 | 0 |  |  | 899 | 20 | 0 | House Fan | 8 | 7192 | 0 | 1 | 0 | 0 | 0 | 0
104 | Classroom | 0 | 0 | Yes | 20 | 870 | 19 | 19 | House Fan | 8 | 6960 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom | 0 | 0 |  |  | 900 | 20 | 0 | House Fan | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
106 | Classroom | 0 | 0 |  |  | 870 | 19 | 0 | House Fan | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 20 | 900 | 20 | 20 | House Fan | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 20 | 930 | 21 | 21 | House Fan | 8 | 7440 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 0 | 0 | Yes | 20 | 900 | 20 | 20 | House Fan | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
110 | Classroom | 0 | 0 |  |  | 960 | 21 | 0 | House Fan | 8 | 7680 | 0 | 1 | 0 | 0 | 0 | 0
111 | Classroom | 0 | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
112 | Classroom | 0 | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
113 | Classroom | 0 | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
- | 2nd flr Corridor |  | 0 |  |  | 828 | 18 | 0 | Unit Ventilator | 8 | 6624 | 0 | 1 | 0 | 0 | 0 | 0
- | 2nd Flr Nurse's | 0 | 0 |  |  | 216 | 4 | 0 | N/A | 8 | 1728 | 0 | 1 | 0 | 0 | 0 | 0
- | 2nd Flr. Office | 0 | 0 |  |  | 126 | 2 | 0 | N/A | 8 | 1008 | 0 | 1 | 0 | 0 | 0 | 0
- | Asst. Principal | 0 | 0 |  |  | 312 | 7 | 0 | N/A | 8 | 2496 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 20 | 928 | 21 | 21 | House Fan | 8 | 7424 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 |  |  | 870 | 19 | 0 | House Fan | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
203 | Classroom | 0 | 0 |  |  | 899 | 20 | 0 | House Fan | 8 | 7192 | 0 | 1 | 0 | 0 | 0 | 0
206 | Classroom | 0 | 0 |  |  | 870 | 19 | 0 | House Fan | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom | 0 | 0 |  |  | 900 | 20 | 0 | House Fan | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
208 | Classroom | 0 | 0 | Yes | 20 | 930 | 21 | 21 | House Fan | 8 | 7440 | 0 | 1 | 0 | 0 | 20 | 3
209 | Computer Lab | 0 | 0 |  |  | 900 | 20 | 0 | House Fan | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
210 | Computer Lab | 0 | 0 |  |  | 960 | 21 | 0 | House Fan | 8 | 7680 | 0 | 1 | 0 | 0 | 0 | 0
211 | Classroom | 0 | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
212 | Classroom | 0 | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
213 | Classroom | 0 | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
217 | Teachers Lounge | 0 | 0 |  |  | 552 | 12 | 0 | N/A | 8 | 4416 | 0 | 1 | 0 | 0 | 0 | 0
- | 3rd flr Corridor |  | 0 |  |  | 828 | 18 | 0 | Unit Ventilator | 8 | 6624 | 0 | 1 | 0 | 0 | 0 | 0
- | 3rd Flr. Office | 0 | 0 |  |  | 126 | 2 | 0 | N/A | 8 | 1008 | 0 | 1 | 0 | 0 | 0 | 0
300 East | Classroom | 0 | 0 |  |  | 720 | 16 | 0 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
300 West | Office | 0 | 0 |  |  | 99 | 2 | 0 | N/A | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom | 0 | 0 | Yes | 20 | 928 | 21 | 21 | House Fan | 8 | 7424 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 20 | 870 | 19 | 19 | House Fan | 8 | 6960 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom | 0 | 0 |  |  | 899 | 20 | 0 | House Fan | 8 | 7192 | 0 | 1 | 0 | 0 | 0 | 0
304 | Classroom | 0 | 0 | Yes | 20 | 870 | 19 | 19 | House Fan | 8 | 6960 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom | 0 | 0 | Yes | 20 | 900 | 20 | 20 | House Fan | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 |  |  | 870 | 19 | 0 | House Fan | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom | 0 | 0 | Yes | 20 | 900 | 20 | 20 | House Fan | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom | 0 | 0 | Yes | 20 | 930 | 21 | 21 | House Fan | 8 | 7440 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 |  |  | 900 | 20 | 0 | House Fan | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom | 0 | 0 |  |  | 960 | 21 | 0 | House Fan | 8 | 7680 | 0 | 1 | 0 | 0 | 0 | 0
312 | Classroom | 544 | 36 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 5.3125 | 1 | 5.3125 | 2 | 5.3125 | 2
313 | Classroom | 479 | 31 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 4.6777 | 1 | 4.6777 | 2 | 4.6777 | 2
314 | Classroom | 65 | 4 |  |  | 768 | 17 | 4 | Unit Ventilator | 8 | 6144 | 0.63477 | 1 | 0.63477 | 0 | 0.63477 | 0
317 | Speech | 0 | 0 |  |  | 117 | 2 | 0 | N/A | 8 | 936 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 |  |  | 3456 | 78 | 0 | House Fan | 8 | 27648 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 |  |  | 986 | 22 | 0 | N/A | 8 | 7888 | 0 | 1 | 0 | 0 | 0 | 0
- | Dean's Office | 0 | 0 |  |  | 108 | 2 | 0 | N/A | 8 | 864 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym | 0 | 0 |  |  | 3306 | 75 | 0 | N/A | 8 | 26448 | 0 | 1.062 | 0 | 0 | 0 | 0
- | IMC Classroom | 0 | 0 |  |  | 1363 | 30 | 0 | House Fan | 8 | 10904 | 0 | 1 | 0 | 0 | 0 | 0
- | IMC Office | 0 | 0 |  |  | 95 | 2 | 0 | House Fan | 8 | 760 | 0 | 1 | 0 | 0 | 0 | 0
Little School House
A-1 | Classroom | 293 | 19 |  |  | 1056 | 24 | 19 | AHU | 8 | 8448 | 2.081 | 1 | 2.081 | 1 | 2.081 | 1
A-3 | Classroom | 296 | 19 |  |  | 1056 | 24 | 19 | AHU | 8 | 8448 | 2.1023 | 1 | 2.1023 | 1 | 2.1023 | 1
A-2 | Classroom | 331 | 22 |  |  | 1056 | 24 | 22 | AHU | 8 | 8448 | 2.3509 | 1 | 2.3509 | 1 | 2.3509 | 1
A-4 | Classroom | 343 | 22 |  |  | 1056 | 24 | 22 | AHU | 8 | 8448 | 2.4361 | 1 | 2.4361 | 1 | 2.4361 | 1
A-5 | Classroom |  | 0 |  |  | 1056 | 24 | 0 | BCU | 8 | 8448 | 0 | 1 | 0 | 0 | 0 | 0
A-5 | Storage |  | 0 |  |  | 52 | 1 | 0 | BCU | 8 | 416 | 0 | 1 | 0 | 0 | 0 | 0
A-7 | Classroom |  | 0 |  |  | 1056 | 24 | 0 | BCU | 8 | 8448 | 0 | 1 | 0 | 0 | 0 | 0
A-6 | Classroom | 321 | 21 |  |  | 1056 | 24 | 21 | AHU | 8 | 8448 | 2.2798 | 1 | 2.2798 | 1 | 2.2798 | 1
A-8 | Classroom | 355 | 23 |  |  | 1056 | 24 | 23 | AHU | 8 | 8448 | 2.5213 | 1 | 2.5213 | 1 | 2.5213 | 1
A-9 | Classroom | 364 | 24 |  |  | 1056 | 24 | 24 | AHU | 8 | 8448 | 2.5852 | 1 | 2.5852 | 1 | 2.5852 | 1
A-11 | Classroom | 396 | 26 |  |  | 1056 | 24 | 24 | AHU | 8 | 8448 | 2.8125 | 1 | 2.8125 | 1 | 2.8125 | 1
A-10 | Classroom | 292 | 19 |  |  | 1056 | 24 | 19 | AHU | 8 | 8448 | 2.0739 | 1 | 2.0739 | 1 | 2.0739 | 1
A-12 | Classroom | 285 | 19 |  |  | 1056 | 24 | 19 | AHU | 8 | 8448 | 2.0241 | 1 | 2.0241 | 1 | 2.0241 | 1
- | Corridor | 0 | 0 |  |  | 1056 | 24 | 0 | AHU | 8 | 8448 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria | 2789 | 185 |  |  | 1850 | 42 | 42 | AHU | 8 | 14800 | 11.3068 | 1 | 11.3068 | 3 | 11.3068 | 3
- | BE Office | 76 | 5 |  |  | 88 | 2 | 2 | AHU | 8 | 704 | 6.4773 | 1 | 6.4773 | 2 | 6.4773 | 2
- | Main Office | 215 | 14 |  |  | 168 | 3 | 3 | AHU | 8 | 1344 | 9.5982 | 1 | 9.5982 | 2 | 9.5982 | 2
- | Vice Principal | 93 | 6 |  |  | 100 | 2 | 2 | AHU | 8 | 800 | 6.975 | 1 | 6.975 | 2 | 6.975 | 2
- | Counselor | 105 | 7 |  |  | 100 | 2 | 2 | AHU | 8 | 800 | 7.875 | 1 | 7.875 | 2 | 7.875 | 2
- | Comm Closet | 54 | 3 |  |  | 50 | 1 | 1 | AHU | 8 | 400 | 8.1 | 1 | 8.1 | 2 | 8.1 | 2
- | Storage | 73 | 4 |  |  | 250 | 5 | 4 | AHU | 8 | 2000 | 2.19 | 1 | 2.19 | 1 | 2.19 | 1
- | Lobby | 66 | 4 |  |  | 216 | 4 | 4 | AHU | 8 | 1728 | 2.2917 | 1 | 2.2917 | 1 | 2.2917 | 1
- | Store Room 1 Ceiling | 43 | 2 |  |  | 250 | 5 | 2 | BCU | 8 | 2000 | 1.29 | 1 | 1.29 | 1 | 1.29 | 1
- | Store Room 2 | 26 | 1 |  |  | 70 | 1 | 1 | BCU | 8 | 560 | 2.7857 | 1 | 2.7857 | 1 | 2.7857 | 1
- | Store Room 3 | 27 | 1 |  |  | 70 | 1 | 1 | BCU | 8 | 560 | 2.8929 | 1 | 2.8929 | 1 | 2.8929 | 1
- | Janitors Closet | 20 | 1 |  |  | 32 | 0 | 0 | BCU | 8 | 256 | 4.6875 | 1 | 4.6875 | 2 | 4.6875 | 2
- | Storage next to B.E. | 22 | 1 |  |  | 99 | 2 | 1 | BCU | 8 | 792 | 1.6667 | 1 | 1.6667 | 1 | 1.6667 | 1
Sheet Last Modified: | 2021-04-30
School: | George Washington Carver High School for Engineering and Science
Vendor: | Devine Brothers | Devine Retest | Devine 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Carver Commons- in IMC Room 147 | 0 | 0 |  |  | 96 | 2 | 0 |  | 8 | 768 | 0 | 1 | 0 | 0 | 0 | 0
2 | Carver Commons- in IMC Room 147 | 0 | 0 |  |  | 147 | 3 | 0 |  | 8 | 1176 | 0 | 1 | 0 | 0 | 0 | 0
3 | Carver Commons- in IMC Room 147 | 0 | 0 |  |  | 143 | 3 | 0 |  | 8 | 1144 | 0 | 1 | 0 | 0 | 0 | 0
4 | Carver Commons- in IMC Room 147 | 0 | 0 |  |  | 99 | 2 | 0 |  | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
104 | Room | 783 | 52 |  |  | 625 | 14 | 14 |  | 8 | 5000 | 9.396 | 1 | 9.396 | 2 | 9.396 | 2
107 | Room | 158 | 10 |  |  | 704 | 16 | 10 |  | 8 | 5632 | 1.6832 | 1 | 1.6832 | 1 | 1.6832 | 1
114 | Room | 0 | 0 |  |  | 840 | 19 | 0 |  | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
115 | Room | 305 | 20 |  |  | 840 | 19 | 19 |  | 8 | 6720 | 2.7232 | 1 | 2.7232 | 1 | 2.7232 | 1
123 | Room | 181 | 12 |  |  | 920 | 20 | 12 |  | 8 | 7360 | 1.4755 | 1 | 1.4755 | 1 | 1.4755 | 1
124 | Room | 85 | 5 |  |  | 480 | 10 | 5 |  | 8 | 3840 | 1.3281 | 1 | 1.3281 | 1 | 1.3281 | 1
125 | Room | 643 | 42 |  |  | 1753 | 39 | 39 |  | 8 | 14024 | 2.751 | 1 | 2.751 | 1 | 2.751 | 1
126 | Room | 399 | 26 |  |  | 750 | 17 | 17 |  | 8 | 6000 | 3.99 | 1 | 3.99 | 1 | 3.99 | 1
134 | Room | 221 | 14 |  |  | 566 | 12 | 12 |  | 8 | 4528 | 2.9284 | 1 | 2.9284 | 1 | 2.9284 | 1
135 | Room | 0 | 0 |  |  | 400 | 9 | 0 |  | 8 | 3200 | 0 | 1 | 0 | 0 | 0 | 0
136 | Room | 86 | 5 |  |  | 200 | 4 | 4 |  | 8 | 1600 | 3.225 | 1 | 3.225 | 1 | 3.225 | 1
137 | Womens Room | 0 | 0 |  |  | 280 | 6 | 0 |  | 8 | 2240 | 0 | 1 | 0 | 0 | 0 | 0
138 | Weight Room | 417 | 27 |  |  | 1500 | 34 | 27 |  | 8 | 12000 | 2.085 | 1 | 2.085 | 1 | 2.085 | 1
139 | PE Office | 0 | 0 |  |  | 176 | 4 | 0 |  | 8 | 1408 | 0 | 1 | 0 | 0 | 0 | 0
139 | Training Room | 0 | 0 |  |  | 139 | 3 | 0 |  | 8 | 1112 | 0 | 1 | 0 | 0 | 0 | 0
139A | Lavatory | 0 | 0 |  |  | 96 | 2 | 0 |  | 8 | 768 | 0 | 1 | 0 | 0 | 0 | 0
144 | Room | 235 | 15 |  |  | 1311 | 29 | 15 |  | 8 | 10488 | 1.3444 | 1 | 1.3444 | 1 | 1.3444 | 1
145 | Env. Science Lab | 373 | 24 |  |  | 2349 | 53 | 24 |  | 8 | 18792 | 1.1909 | 1 | 1.1909 | 1 | 1.1909 | 1
147 | IMC | 1282 | 85 |  |  | 4087 | 92 | 85 |  | 8 | 32696 | 2.3526 | 1.062 | 2.4985 | 1 | 2.4985 | 1
201 | Room | 0 | 0 |  |  | 1200 | 27 | 0 |  | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
202 | Room | 371 | 24 |  |  | 864 | 19 | 19 |  | 8 | 6912 | 3.2205 | 1 | 3.2205 | 1 | 3.2205 | 1
203 | Room | 294 | 19 |  |  | 864 | 19 | 19 |  | 8 | 6912 | 2.5521 | 1 | 2.5521 | 1 | 2.5521 | 1
209 | Room | 401 | 26 |  |  | 952 | 21 | 21 |  | 8 | 7616 | 3.1591 | 1 | 3.1591 | 1 | 3.1591 | 1
211 | Room | 367 | 24 |  |  | 960 | 21 | 21 |  | 8 | 7680 | 2.8672 | 1 | 2.8672 | 1 | 2.8672 | 1
212 | Room | 292 | 19 |  |  | 960 | 21 | 19 |  | 8 | 7680 | 2.2812 | 1 | 2.2812 | 1 | 2.2812 | 1
213 | Room | 295 | 19 |  |  | 960 | 21 | 19 |  | 8 | 7680 | 2.3047 | 1 | 2.3047 | 1 | 2.3047 | 1
214 | Room | 0 | 0 |  |  | 960 | 21 | 0 |  | 8 | 7680 | 0 | 1 | 0 | 0 | 0 | 0
217 | Room | 271 | 18 |  |  | 1250 | 28 | 18 |  | 8 | 10000 | 1.626 | 1 | 1.626 | 1 | 1.626 | 1
220 | Room | 0 | 0 |  |  | 1408 | 32 | 0 |  | 8 | 11264 | 0 | 1 | 0 | 0 | 0 | 0
221 | Room | 95 | 6 |  |  | 1680 | 38 | 6 |  | 8 | 13440 | 0.42411 | 1 | 0.42411 | 0 | 0.42411 | 0
222 | Room | 201 | 13 |  |  | 1200 | 27 | 13 |  | 8 | 9600 | 1.2563 | 1 | 1.2563 | 1 | 1.2563 | 1
224 | Room | 392 | 26 |  |  | 1680 | 38 | 26 |  | 8 | 13440 | 1.75 | 1 | 1.75 | 1 | 1.75 | 1
226 | Room | 309 | 20 |  |  | 1680 | 38 | 20 |  | 8 | 13440 | 1.3795 | 1 | 1.3795 | 1 | 1.3795 | 1
229 | Room | 0 | 0 |  |  | 1600 | 36 | 0 |  | 8 | 12800 | 0 | 1 | 0 | 0 | 0 | 0
230 | Room | 162 | 10 |  |  | 1680 | 38 | 10 |  | 8 | 13440 | 0.72321 | 1 | 0.72321 | 0 | 0.72321 | 0
301 | Room | 0 | 0 |  |  | 1157 | 26 | 0 |  | 8 | 9256 | 0 | 1 | 0 | 0 | 0 | 0
302 | Room | 834 | 55 |  |  | 864 | 19 | 19 |  | 8 | 6912 | 7.2396 | 1 | 7.2396 | 2 | 7.2396 | 2
303 | Room | 281 | 18 |  |  | 864 | 19 | 18 |  | 8 | 6912 | 2.4392 | 1 | 2.4392 | 1 | 2.4392 | 1
309 | Room | 462 | 30 |  |  | 864 | 19 | 19 |  | 8 | 6912 | 4.0104 | 1 | 4.0104 | 2 | 4.0104 | 2
311 | Room | 533 | 35 |  |  | 1041 | 23 | 23 |  | 8 | 8328 | 3.8401 | 1 | 3.8401 | 1 | 3.8401 | 1
312 | Room | 201 | 13 |  |  | 1118 | 25 | 13 |  | 8 | 8944 | 1.3484 | 1 | 1.3484 | 1 | 1.3484 | 1
313 | Room | 243 | 16 |  |  | 816 | 18 | 16 |  | 8 | 6528 | 2.2335 | 1 | 2.2335 | 1 | 2.2335 | 1
314 | Room | 389 | 25 |  |  | 816 | 18 | 18 |  | 8 | 6528 | 3.5754 | 1 | 3.5754 | 1 | 3.5754 | 1
317 | Room | 0 | 0 |  |  | 816 | 18 | 0 |  | 8 | 6528 | 0 | 1 | 0 | 0 | 0 | 0
318 | Room | 170 | 11 |  |  | 768 | 17 | 11 |  | 8 | 6144 | 1.6602 | 1 | 1.6602 | 1 | 1.6602 | 1
320 | Room | 142 | 9 |  |  | 1056 | 24 | 9 |  | 8 | 8448 | 1.0085 | 1 | 1.0085 | 1 | 1.0085 | 1
321 | Room | 487 | 32 |  |  | 1200 | 27 | 27 |  | 8 | 9600 | 3.0438 | 1 | 3.0438 | 1 | 3.0438 | 1
322 | Room | 460 | 30 |  |  | 1200 | 27 | 27 |  | 8 | 9600 | 2.875 | 1 | 2.875 | 1 | 2.875 | 1
324 | Room | 75 | 5 |  |  | 1200 | 27 | 5 |  | 8 | 9600 | 0.46875 | 1 | 0.46875 | 0 | 0.46875 | 0
327 | Room | 226 | 15 |  |  | 1519 | 34 | 15 |  | 8 | 12152 | 1.1159 | 1 | 1.1159 | 1 | 1.1159 | 1
329 | Room | 400 | 26 |  |  | 1440 | 32 | 26 |  | 8 | 11520 | 2.0833 | 1 | 2.0833 | 1 | 2.0833 | 1
- | Art Room | 756 | 50 |  |  | 2500 | 56 | 50 |  | 8 | 20000 | 2.268 | 1 | 2.268 | 1 | 2.268 | 1
- | Auditorium | 4245 | 283 |  |  | 5612 | 127 | 127 |  | 8 | 44896 | 5.6731 | 1.062 | 6.025 | 2 | 6.025 | 2
- | Cafeteria | 6739 | 449 |  |  | 3826 | 86 | 86 |  | 8 | 30608 | 13.2103 | 1.062 | 14.0298 | 3 | 14.0298 | 3
- | Dance Area | 104 | 6 |  |  | 1920 | 43 | 6 |  | 8 | 15360 | 0.40625 | 1 | 0.40625 | 0 | 0.40625 | 0
- | Dance Studio | 1644 | 109 |  |  | 336 | 7 | 7 |  | 8 | 2688 | 36.6964 | 1 | 36.6964 | 4 | 36.6964 | 4
- | Gymnasium | 13040 | 869 |  |  | 8949 | 203 | 203 |  | 8 | 71592 | 10.9286 | 1.4912 | 16.2963 | 3 | 16.2963 | 3
- | Female Student Locker Room | 579 | 38 |  |  | 1200 | 27 | 27 |  | 8 | 9600 | 3.6187 | 1 | 3.6187 | 1 | 3.6187 | 1
- | Male Student Locker Room | 176 | 11 |  |  | 1200 | 27 | 11 |  | 8 | 9600 | 1.1 | 1 | 1.1 | 1 | 1.1 | 1
- | Female Staff Locker Room | 52 | 3 |  |  | 117 | 2 | 2 |  | 8 | 936 | 3.3333 | 1 | 3.3333 | 1 | 3.3333 | 1
- | Male Staff Locker Room | 446 | 29 |  |  | 112 | 2 | 2 |  | 8 | 896 | 29.8661 | 1 | 29.8661 | 4 | 29.8661 | 4
- | Male Staff Locker Room | 446 | 29 |  |  | 112 | 2 | 2 |  | 8 | 896 | 29.8661 | 1 | 29.8661 | 4 | 29.8661 | 4
Sheet Last Modified: | 2021-04-06
School: | Lewis C. Cassidy Elementary School
Vendor: | Devine | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Boy's Gang Bathroom | 560 | 37 |  |  | 575 | 13 | 13 | House Fan | 8 | 4600 | 7.3043 | 1 | 7.3043 | 2 | 7.3043 | 2
- | Girl's Gang Bathroom | 326 | 21 |  |  | 396 | 9 | 9 | House Fan | 8 | 3168 | 6.1742 | 1 | 6.1742 | 2 | 6.1742 | 2
B | Teachers Lounge | 384 | 25 |  |  | 308 | 7 | 7 | House Fan | 8 | 2464 | 9.3506 | 1 | 9.3506 | 2 | 9.3506 | 2
B2 | Office | 0 | 0 | Yes | 20 | 748 | 17 | 17 |  | 8 | 5984 | 0 | 1 | 0 | 0 | 20 | 3
B3 | Classroom | 741 | 49 |  |  | 742 | 16 | 16 | House Fan | 8 | 5936 | 7.4899 | 1 | 7.4899 | 2 | 7.4899 | 2
B7 | Gym | 0 | 0 | Yes | 20 | 3872 | 88 | 88 | N/A | 8 | 30976 | 0 | 1.062 | 0 | 0 | 20 | 3
B8 | Classroom | 527 | 35 |  |  | 968 | 22 | 22 | House Fan | 8 | 7744 | 4.0832 | 1 | 4.0832 | 2 | 4.0832 | 2
101 | Classroom | 542 | 36 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 6.1591 | 1 | 6.1591 | 2 | 6.1591 | 2
102 | Classroom | 478 | 31 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 5.4318 | 1 | 5.4318 | 2 | 5.4318 | 2
103 | Classroom | 538 | 35 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 6.1136 | 1 | 6.1136 | 2 | 6.1136 | 2
104 | Classroom | 473 | 31 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 5.7589 | 1 | 5.7589 | 2 | 5.7589 | 2
105 | Office | 0 | 0 |  |  | 132 | 3 | 0 | N/A | 8 | 1056 | 0 | 1 | 0 | 0 | 0 | 0
106 | Classroom | 682 | 45 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.2656 | 1 | 7.2656 | 2 | 7.2656 | 2
107 | Classroom | 741 | 49 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 9.0219 | 1 | 9.0219 | 2 | 9.0219 | 2
108 | Classroom | 812 | 54 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 9.2273 | 1 | 9.2273 | 2 | 9.2273 | 2
109 | Classroom | 734 | 48 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 8.3409 | 1 | 8.3409 | 2 | 8.3409 | 2
201 | Nurses Office | 0 | 0 | Yes | 20 | 176 | 4 | 4 | N/A | 8 | 1408 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 551 | 36 |  |  | 792 | 18 | 18 | House Fan | 8 | 6336 | 5.2178 | 1 | 5.2178 | 2 | 5.2178 | 2
203 | Classroom | 389 | 25 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 4.4205 | 1 | 4.4205 | 2 | 4.4205 | 2
204 | Classroom | 471 | 31 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 5.3523 | 1 | 5.3523 | 2 | 5.3523 | 2
205 | Teachers Lounge | 0 | 0 | Yes | 20 | 308 | 7 | 7 | N/A | 8 | 2464 | 0 | 1 | 0 | 0 | 20 | 3
206 | Asst Principal | 0 | 0 | Yes | 20 | 207 | 4 | 4 | N/A | 8 | 1656 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom | 525 | 35 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 5.9659 | 1 | 5.9659 | 2 | 5.9659 | 2
208 | Small Classroom | 0 | 0 | Yes | 20 | 220 | 5 | 5 | House Fan | 8 | 1760 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom | 675 | 45 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 7.6705 | 1 | 7.6705 | 2 | 7.6705 | 2
210 | Classroom | 551 | 36 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 6.7086 | 1 | 6.7086 | 2 | 6.7086 | 2
211 | Classroom | 565 | 37 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 6.4205 | 1 | 6.4205 | 2 | 6.4205 | 2
212 | Classroom | 611 | 40 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 6.9432 | 1 | 6.9432 | 2 | 6.9432 | 2
213 | Office | 0 | 0 | Yes | 20 | 264 | 6 | 6 | N/A | 8 | 2112 | 0 | 1 | 0 | 0 | 20 | 3
301 | Office | 0 | 0 | Yes | 20 | 264 | 6 | 6 | N/A | 8 | 2112 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom | 562 | 37 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 5.9872 | 1 | 5.9872 | 2 | 5.9872 | 2
303 | Classroom | 430 | 28 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 4.581 | 1 | 4.581 | 2 | 4.581 | 2
304 | Classroom | 392 | 26 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 4.7727 | 1 | 4.7727 | 2 | 4.7727 | 2
305 | Classroom | 507 | 33 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 6.1729 | 1 | 6.1729 | 2 | 6.1729 | 2
306 | Classroom | 112 | 7 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 1.1932 | 1 | 1.1932 | 1 | 21.1932 | 3
307 | Classroom | 465 | 31 |  |  | 748 | 17 | 17 | House Fan | 8 | 5984 | 4.6624 | 1 | 4.6624 | 2 | 4.6624 | 2
308 | Classroom | 378 | 25 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 3.1535 | 1 | 3.1535 | 1 | 3.1535 | 1
309 | Classroom | 378 | 25 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 4.027 | 1 | 4.027 | 2 | 4.027 | 2
310 | Classroom | 154 | 10 |  |  | 660 | 15 | 10 | House Fan | 8 | 5280 | 1.75 | 1 | 1.75 | 1 | 1.75 | 1
311 | Classroom | 518 | 34 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 6.3068 | 1 | 6.3068 | 2 | 6.3068 | 2
312 | Classroom | 718 | 47 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 8.7419 | 1 | 8.7419 | 2 | 8.7419 | 2
313 | Classroom | 550 | 36 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 6.25 | 1 | 6.25 | 2 | 6.25 | 2
314 | Classroom | 561 | 37 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 6.375 | 1 | 6.375 | 2 | 6.375 | 2
315 | Storage | 0 | 0 |  |  | 264 | 6 | 0 | N/A | 8 | 2112 | 0 | 1 | 0 | 0 | 0 | 0
- | Attwood Lunch Rm | 940 | 62 |  |  | 836 | 19 | 19 | House Fan | 8 | 6688 | 8.433 | 1 | 8.433 | 2 | 8.433 | 2
- | Auditorium | 1895 | 126 |  |  | 3608 | 82 | 82 | House Fan | 8 | 28864 | 3.9392 | 1.062 | 4.1835 | 2 | 4.1835 | 2
- | Backstage Office | 0 | 0 |  |  | 132 | 3 | 0 | N/A | 8 | 1056 | 0 | 1 | 0 | 0 | 0 | 0
- | Lunch Room | 660 | 44 |  |  | 880 | 20 | 20 | House Fan | 8 | 7040 | 5.625 | 1 | 5.625 | 2 | 5.625 | 2
- | Library | 732 | 48 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.7983 | 1 | 7.7983 | 2 | 7.7983 | 2
- | Main Office | 0 | 0 | Yes | 20 | 308 | 7 | 7 | N/A | 8 | 2464 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office | 0 | 0 | Yes | 20 | 132 | 3 | 3 | N/A | 8 | 1056 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-19
School: | Joseph W. Catharine Elementary School
Vendor: | EMCOR | Main Building Part 2
School: | Joseph W. Catharine Elementary School Annex
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
- | Lunch | 503 | 33 |  |  | 1247 | 28 | 28 | Unit Ventilator | 8 | 9976 | 3.0253 | 1 | 3.0253 | 1 | 3.0253 | 1
- | Gym | 976 | 65 |  |  | 4544 | 103 | 65 | Unit Ventilator | 8 | 36352 | 1.6109 | 1.062 | 1.7108 | 1 | 1.7108 | 1
102 | Classroom | 270 | 18 |  |  | 681 | 15 | 15 | Unit Ventilator | 8 | 5448 | 2.9736 | 1 | 2.9736 | 1 | 2.9736 | 1
103 | Classroom | 313 | 20 |  |  | 550 | 12 | 12 | Unit Ventilator | 8 | 4400 | 4.2682 | 1 | 4.2682 | 2 | 4.2682 | 2
104 | Classroom | 670 | 44 |  |  | 953 | 21 | 21 | Unit Ventilator | 8 | 7624 | 5.2728 | 1 | 5.2728 | 2 | 5.2728 | 2
105 | Classroom | 0 | 0 | Yes | 20 | 953 | 21 | 21 | Unit Ventilator | 8 | 7624 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom | 0 | 0 | Yes | 20 | 842 | 19 | 19 | Unit Ventilator | 8 | 6736 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom | 627 | 41 |  |  | 1062 | 24 | 24 | Unit Ventilator | 8 | 8496 | 4.428 | 1 | 4.428 | 2 | 4.428 | 2
108 | Classroom | 307 | 20 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 2.7542 | 1 | 2.7542 | 1 | 2.7542 | 1
- | Office | 212 | 14 |  |  | 367 | 8 | 8 | Unit Ventilator | 8 | 2936 | 4.3324 | 1 | 4.3324 | 2 | 4.3324 | 2
201 | Classroom | 407 | 27 |  |  | 676 | 15 | 15 | Unit Ventilator | 8 | 5408 | 4.5155 | 1 | 4.5155 | 2 | 4.5155 | 2
202 | Classroom | 331 | 22 |  |  | 683 | 15 | 15 | Unit Ventilator | 8 | 5464 | 3.6347 | 1 | 3.6347 | 1 | 3.6347 | 1
203 | Classroom | 306 | 20 |  |  | 673 | 15 | 15 | Unit Ventilator | 8 | 5384 | 3.4101 | 1 | 3.4101 | 1 | 3.4101 | 1
204 | Classroom | 144 | 9 | Yes | 20 | 708 | 16 | 16 | Unit Ventilator | 8 | 5664 | 1.5254 | 1 | 1.5254 | 1 | 21.5254 | 3
205 | Classroom | 300 | 20 |  |  | 678 | 15 | 15 | Unit Ventilator | 8 | 5424 | 3.3186 | 1 | 3.3186 | 1 | 3.3186 | 1
206 | Classroom | 0 | 0 | Yes | 20 | 855 | 19 | 19 | Unit Ventilator | 8 | 6840 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 20 | 504 | 11 | 11 | Unit Ventilator | 8 | 4032 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 20 | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 | Yes | 20 | 709 | 16 | 16 | Unit Ventilator | 8 | 5672 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom | 0 | 0 | Yes | 20 | 705 | 16 | 16 | Unit Ventilator | 8 | 5640 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom | 0 | 0 | Yes | 20 | 673 | 15 | 15 | Unit Ventilator | 8 | 5384 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 | Yes | 20 | 684 | 15 | 15 | Unit Ventilator | 8 | 5472 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 20 | 684 | 15 | 15 | Unit Ventilator | 8 | 5472 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom | 0 | 0 | Yes | 20 | 679 | 15 | 15 | Unit Ventilator | 8 | 5432 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom | 173 | 11 | Yes | 20 | 708 | 16 | 16 | Unit Ventilator | 8 | 5664 | 1.8326 | 1 | 1.8326 | 1 | 21.8326 | 3
305 | Classroom | 209 | 13 | Yes | 20 | 698 | 15 | 15 | Unit Ventilator | 8 | 5584 | 2.2457 | 1 | 2.2457 | 1 | 22.2457 | 3
306 | Classroom | 0 | 0 | Yes | 20 | 872 | 19 | 19 | Unit Ventilator | 8 | 6976 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 | Yes | 20 | 675 | 15 | 15 | Unit Ventilator | 8 | 5400 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom | 198 | 13 | Yes | 20 | 674 | 15 | 15 | Unit Ventilator | 8 | 5392 | 2.2033 | 1 | 2.2033 | 1 | 22.2033 | 3
309 | Classroom | 284 | 18 |  |  | 705 | 16 | 16 | Unit Ventilator | 8 | 5640 | 3.0213 | 1 | 3.0213 | 1 | 3.0213 | 1
310 | Classroom | 297 | 19 |  |  | 707 | 16 | 16 | Unit Ventilator | 8 | 5656 | 3.1506 | 1 | 3.1506 | 1 | 3.1506 | 1
311 | Classroom | 0 | 0 | Yes | 20 | 674 | 15 | 15 | Unit Ventilator | 8 | 5392 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's office | 0 | 0 | Yes | 20 | 359 | 8 | 8 |  | 8 | 2872 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse office | 0 | 0 | Yes | 20 | 324 | 7 | 7 |  | 8 | 2592 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office | 0 | 0 | Yes | 20 | 109 | 2 | 2 |  | 8 | 872 | 0 | 1 | 0 | 0 | 20 | 3
Joseph W. Catherine Elementary School Annex
100 | Office |  | 0 | Yes | 20 | 273 | 6 | 6 | N/A | 8 | 2184 | 0 | 1 | 0 | 0 | 20 | 3
102 | K-1 Room |  | 0 | Yes | 20 | 680 | 15 | 15 | N/A | 8 | 5440 | 0 | 1 | 0 | 0 | 20 | 3
104 | K-2 Room |  | 0 | Yes | 20 | 714 | 16 | 16 | N/A | 8 | 5712 | 0 | 1 | 0 | 0 | 20 | 3
213 | K-3 |  | 0 | Yes | 20 | 1056 | 24 | 24 | N/A | 8 | 8448 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-28
School: | Cayuga Elementary School (former St. Henry’s)
Vendor: | Chadwick | Devine Brothers Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | classroom | 355 | 23 |  |  | 830 | 18 | 18 | Unit Ventilator | 8 | 6640 | 3.2078 | 1 | 3.2078 | 1 | 3.2078 | 1
102 | classroom | 375 | 25 |  |  | 740 | 16 | 16 | Unit Ventilator | 8 | 5920 | 3.8007 | 1 | 3.8007 | 1 | 3.8007 | 1
103 | classroom | 315 | 21 |  |  | 795 | 18 | 18 | Unit Ventilator | 8 | 6360 | 2.9717 | 1 | 2.9717 | 1 | 2.9717 | 1
104 | classroom | 280 | 18 |  |  | 796 | 18 | 18 | Unit Ventilator | 8 | 6368 | 2.6382 | 1 | 2.6382 | 1 | 2.6382 | 1
105 | Nurse's Office |  | 0 | Yes | 20 | 330 | 7 | 7 | N/A | 8 | 2640 | 0 | 1 | 0 | 0 | 20 | 3
106 | classroom | 275 | 18 |  |  | 403 | 9 | 9 | Unit Ventilator | 8 | 3224 | 5.1179 | 1 | 5.1179 | 2 | 5.1179 | 2
117 | classroom | 736 | 49 |  |  | 806 | 18 | 18 | Unit Ventilator | 8 | 6448 | 6.8486 | 1 | 6.8486 | 2 | 6.8486 | 2
118 | classroom | 625 | 41 |  |  | 688 | 15 | 15 | Unit Ventilator | 8 | 5504 | 6.8132 | 1 | 6.8132 | 2 | 6.8132 | 2
119 | classroom | 586 | 39 |  |  | 845 | 19 | 19 | Unit Ventilator | 8 | 6760 | 5.2012 | 1 | 5.2012 | 2 | 5.2012 | 2
120 | classroom | 335 | 22 |  |  | 670 | 15 | 15 | Unit Ventilator | 8 | 5360 | 3.75 | 1 | 3.75 | 1 | 3.75 | 1
201 | classroom | 325 | 21 |  |  | 830 | 18 | 18 | Unit Ventilator | 8 | 6640 | 2.9367 | 1 | 2.9367 | 1 | 2.9367 | 1
202 | classroom | 305 | 20 |  |  | 740 | 16 | 16 | Unit Ventilator | 8 | 5920 | 3.0912 | 1 | 3.0912 | 1 | 3.0912 | 1
203 | classroom | 380 | 25 |  |  | 795 | 18 | 18 | Unit Ventilator | 8 | 6360 | 3.5849 | 1 | 3.5849 | 1 | 3.5849 | 1
204 | classroom | 360 | 24 |  |  | 796 | 18 | 18 | Unit Ventilator | 8 | 6368 | 3.392 | 1 | 3.392 | 1 | 3.392 | 1
205 | classroom | 355 | 23 |  |  | 765 | 17 | 17 | Unit Ventilator | 8 | 6120 | 3.4804 | 1 | 3.4804 | 1 | 3.4804 | 1
206 | classroom | 310 | 20 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.9808 | 1 | 2.9808 | 1 | 2.9808 | 1
214 | classroom | 375 | 25 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 3.8633 | 1 | 3.8633 | 1 | 3.8633 | 1
215 | classroom | 365 | 24 |  |  | 693 | 15 | 15 | Unit Ventilator | 8 | 5544 | 3.9502 | 1 | 3.9502 | 1 | 3.9502 | 1
216 | classroom | 330 | 22 |  |  | 737 | 16 | 16 | Unit Ventilator | 8 | 5896 | 3.3582 | 1 | 3.3582 | 1 | 3.3582 | 1
217 | classroom | 1606 | 107 |  |  | 822 | 18 | 18 | Unit Ventilator | 8 | 6576 | 14.6533 | 1 | 14.6533 | 3 | 14.6533 | 3
301 | classroom | 345 | 23 |  |  | 830 | 18 | 18 | Unit Ventilator | 8 | 6640 | 3.1175 | 1 | 3.1175 | 1 | 3.1175 | 1
302 | classroom | 275 | 18 |  |  | 740 | 16 | 16 | Unit Ventilator | 8 | 5920 | 2.7872 | 1 | 2.7872 | 1 | 2.7872 | 1
303 | classroom | 380 | 25 |  |  | 795 | 18 | 18 | Unit Ventilator | 8 | 6360 | 3.5849 | 1 | 3.5849 | 1 | 3.5849 | 1
304 | classroom | 380 | 25 |  |  | 796 | 18 | 18 | Unit Ventilator | 8 | 6368 | 3.5804 | 1 | 3.5804 | 1 | 3.5804 | 1
305 | classroom | 553 | 36 |  |  | 765 | 17 | 17 | Unit Ventilator | 8 | 6120 | 5.4216 | 1 | 5.4216 | 2 | 5.4216 | 2
306 | classroom | 315 | 21 |  |  | 790 | 17 | 17 | Unit Ventilator | 8 | 6320 | 2.9905 | 1 | 2.9905 | 1 | 2.9905 | 1
- | Gym | 1213 | 80 |  |  | 2754 | 62 | 62 | AHU | 8 | 22032 | 3.3034 | 1.062 | 3.5083 | 1 | 3.5083 | 1
- | Basement Corridor | 90 | 6 |  |  |  | 0 | 0 | AHU
- | Main Entrance Corridor | 46 | 3 |  |  |  | 0 | 0 | AHU
- | 1st Floor Corridor | 31 | 2 |  |  |  | 0 | 0 | AHU
- | Cafeteria | 936 | 62 |  |  | 3432 | 78 | 62 | AHU | 8 | 27456 | 2.0455 | 1.062 | 2.1723 | 1 | 2.1723 | 1
Sheet Last Modified: | 2091-04-29
School: | Central High School
Vendor: | Devine Brothers | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Ceramic | 253 | 16 |  |  | 723 | 16 | 16 |  | 8 | 5784 | 2.6245 | 1 | 2.6245 | 1 | 2.6245 | 1
2 | Kiln | 58 | 3 |  |  | 128 | 2 | 2 |  | 8 | 1024 | 3.3984 | 1 | 3.3984 | 1 | 3.3984 | 1
3 | Drafting Studio | 403 | 26 |  |  | 1366 | 31 | 26 |  | 8 | 10928 | 2.2127 | 1 | 2.2127 | 1 | 2.2127 | 1
4 | Fashion | 40 | 2 |  |  | 290 | 6 | 2 |  | 8 | 2320 | 1.0345 | 1 | 1.0345 | 1 | 1.0345 | 1
5 | Office | 64 | 4 |  |  | 349 | 7 | 4 |  | 8 | 2792 | 1.3754 | 1 | 1.3754 | 1 | 1.3754 | 1
6 | Photography | 32 | 2 |  |  | 171 | 3 | 2 |  | 8 | 1368 | 1.4035 | 1 | 1.4035 | 1 | 1.4035 | 1
7 | Computer Lab | 31 | 2 |  |  | 148 | 3 | 2 |  | 8 | 1184 | 1.5709 | 1 | 1.5709 | 1 | 1.5709 | 1
8 | Art Studio | 356 | 23 |  |  | 1452 | 33 | 23 |  | 8 | 11616 | 1.8388 | 1 | 1.8388 | 1 | 1.8388 | 1
9 | Printing Studio | 70 | 4 |  |  | 390 | 8 | 4 |  | 8 | 3120 | 1.3462 | 1 | 1.3462 | 1 | 1.3462 | 1
12 | Classroom | 333 | 22 |  |  | 840 | 19 | 19 |  | 8 | 6720 | 2.9732 | 1 | 2.9732 | 1 | 2.9732 | 1
13 | Classroom | 388 | 25 |  |  | 709 | 16 | 16 |  | 8 | 5672 | 4.1044 | 1 | 4.1044 | 2 | 4.1044 | 2
82 | Classroom | 301 | 20 |  |  | 1714 | 38 | 20 |  | 8 | 13712 | 1.3171 | 1 | 1.3171 | 1 | 1.3171 | 1
84 | Classroom | 300 | 20 |  |  | 1531 | 34 | 20 |  | 8 | 12248 | 1.4696 | 1 | 1.4696 | 1 | 1.4696 | 1
85 | Classroom | 300 | 20 |  |  | 1594 | 36 | 20 |  | 8 | 12752 | 1.4115 | 1 | 1.4115 | 1 | 1.4115 | 1
89 | Classroom | 389 | 25 |  |  | 1327 | 30 | 25 |  | 8 | 10616 | 2.1986 | 1 | 2.1986 | 1 | 2.1986 | 1
95 | Classroom | 604 | 40 |  |  | 1307 | 29 | 29 |  | 8 | 10456 | 3.466 | 1 | 3.466 | 1 | 3.466 | 1
97 | Classroom | 605 | 40 |  |  | 1216 | 27 | 27 |  | 8 | 9728 | 3.7315 | 1 | 3.7315 | 1 | 3.7315 | 1
98 | Classroom | 428 | 28 |  |  | 1374 | 31 | 28 |  | 8 | 10992 | 2.3362 | 1 | 2.3362 | 1 | 2.3362 | 1
99 | Classroom | 432 | 28 |  |  | 1258 | 28 | 28 |  | 8 | 10064 | 2.5755 | 1 | 2.5755 | 1 | 2.5755 | 1
101 | Classroom | 376 | 25 |  |  | 876 | 19 | 19 |  | 8 | 7008 | 3.2192 | 1 | 3.2192 | 1 | 3.2192 | 1
102 | Classroom | 370 | 24 |  |  | 852 | 19 | 19 |  | 8 | 6816 | 3.257 | 1 | 3.257 | 1 | 3.257 | 1
103 | Classroom | 387 | 25 |  |  | 876 | 19 | 19 |  | 8 | 7008 | 3.3134 | 1 | 3.3134 | 1 | 3.3134 | 1
104 | Classroom | 316 | 21 |  |  | 700 | 15 | 15 |  | 8 | 5600 | 3.3857 | 1 | 3.3857 | 1 | 3.3857 | 1
105 | Classroom | 305 | 20 |  |  | 675 | 15 | 15 |  | 8 | 5400 | 3.3889 | 1 | 3.3889 | 1 | 3.3889 | 1
106 | Classroom | 283 | 18 |  |  | 687 | 15 | 15 |  | 8 | 5496 | 3.0895 | 1 | 3.0895 | 1 | 3.0895 | 1
107 | Classroom | 288 | 19 |  |  | 706 | 16 | 16 |  | 8 | 5648 | 3.0595 | 1 | 3.0595 | 1 | 3.0595 | 1
108 | Classroom | 329 | 21 |  |  | 700 | 15 | 15 |  | 8 | 5600 | 3.525 | 1 | 3.525 | 1 | 3.525 | 1
109 | Classroom | 0 | 0 |  |  | 675 | 15 | 0 |  | 8 | 5400 | 0 | 1 | 0 | 0 | 0 | 0
110 | Office | 248 | 16 |  |  | 339 | 7 | 7 |  | 8 | 2712 | 5.4867 | 1 | 5.4867 | 2 | 5.4867 | 2
111 | Classroom | 0 | 0 |  |  | 654 | 14 | 0 |  | 8 | 5232 | 0 | 1 | 0 | 0 | 0 | 0
119 | Classroom | 0 | 0 |  |  | 470 | 10 | 0 |  | 8 | 3760 | 0 | 1 | 0 | 0 | 0 | 0
120 | Classroom | 332 | 22 |  |  | 857 | 19 | 19 |  | 8 | 6856 | 2.9055 | 1 | 2.9055 | 1 | 2.9055 | 1
121 | Classroom | 366 | 24 |  |  | 694 | 15 | 15 |  | 8 | 5552 | 3.9553 | 1 | 3.9553 | 1 | 3.9553 | 1
122 | Classroom | 346 | 23 |  |  | 724 | 16 | 16 |  | 8 | 5792 | 3.5843 | 1 | 3.5843 | 1 | 3.5843 | 1
123 | Classroom | 297 | 19 |  |  | 694 | 15 | 15 |  | 8 | 5552 | 3.2097 | 1 | 3.2097 | 1 | 3.2097 | 1
124 | Classroom | 280 | 18 |  |  | 680 | 15 | 15 |  | 8 | 5440 | 3.0882 | 1 | 3.0882 | 1 | 3.0882 | 1
125 | Classroom | 427 | 28 |  |  | 683 | 15 | 15 |  | 8 | 5464 | 4.6889 | 1 | 4.6889 | 2 | 4.6889 | 2
126 | Classroom | 415 | 27 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 4.3229 | 1 | 4.3229 | 2 | 4.3229 | 2
127 | Classroom | 290 | 19 |  |  | 722 | 16 | 16 |  | 8 | 5776 | 3.0125 | 1 | 3.0125 | 1 | 3.0125 | 1
136 | Classroom | 281 | 18 |  |  | 297 | 6 | 6 |  | 8 | 2376 | 7.096 | 1 | 7.096 | 2 | 7.096 | 2
138 | Principal | 176 | 11 |  |  | 235 | 5 | 5 |  | 8 | 1880 | 5.617 | 1 | 5.617 | 2 | 5.617 | 2
141 | Classroom | 293 | 19 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 3.1848 | 1 | 3.1848 | 1 | 3.1848 | 1
142 | Office | 377 | 25 |  |  | 982 | 22 | 22 |  | 8 | 7856 | 2.8793 | 1 | 2.8793 | 1 | 2.8793 | 1
143 | Classroom | 405 | 27 |  |  | 700 | 15 | 15 |  | 8 | 5600 | 4.3393 | 1 | 4.3393 | 2 | 4.3393 | 2
144 | Roster Office | 179 | 11 |  |  | 652 | 14 | 11 |  | 8 | 5216 | 2.059 | 1 | 2.059 | 1 | 2.059 | 1
201 | Classroom | 0 | 0 |  |  | 530 | 12 | 0 |  | 8 | 4240 | 0 | 1 | 0 | 0 | 0 | 0
202 | Classroom | 288 | 19 |  |  | 834 | 18 | 18 |  | 8 | 6672 | 2.5899 | 1 | 2.5899 | 1 | 2.5899 | 1
203 | Classroom | 293 | 19 |  |  | 681 | 15 | 15 |  | 8 | 5448 | 3.2269 | 1 | 3.2269 | 1 | 3.2269 | 1
204 | Classroom | 288 | 19 |  |  | 692 | 15 | 15 |  | 8 | 5536 | 3.1214 | 1 | 3.1214 | 1 | 3.1214 | 1
205 | Classroom | 283 | 18 |  |  | 676 | 15 | 15 |  | 8 | 5408 | 3.1398 | 1 | 3.1398 | 1 | 3.1398 | 1
206 | Classroom | 344 | 22 |  |  | 681 | 15 | 15 |  | 8 | 5448 | 3.7885 | 1 | 3.7885 | 1 | 3.7885 | 1
207 | Classroom | 344 | 22 |  |  | 705 | 16 | 16 |  | 8 | 5640 | 3.6596 | 1 | 3.6596 | 1 | 3.6596 | 1
208 | Classroom | 286 | 19 |  |  | 682 | 15 | 15 |  | 8 | 5456 | 3.1452 | 1 | 3.1452 | 1 | 3.1452 | 1
209 | Classroom | 306 | 20 |  |  | 694 | 15 | 15 |  | 8 | 5552 | 3.3069 | 1 | 3.3069 | 1 | 3.3069 | 1
210 | Office | 226 | 15 |  |  | 336 | 7 | 7 |  | 8 | 2688 | 5.0446 | 1 | 5.0446 | 2 | 5.0446 | 2
211 | Classroom | 0 | 0 |  |  | 650 | 14 | 0 |  | 8 | 5200 | 0 | 1 | 0 | 0 | 0 | 0
224 | Classroom | 646 | 43 |  |  | 831 | 18 | 18 |  | 8 | 6648 | 5.8303 | 1 | 5.8303 | 2 | 5.8303 | 2
225 | Classroom | 289 | 19 |  |  | 800 | 18 | 18 |  | 8 | 6400 | 2.7094 | 1 | 2.7094 | 1 | 2.7094 | 1
226 | Classroom | 286 | 19 |  |  | 700 | 15 | 15 |  | 8 | 5600 | 3.0643 | 1 | 3.0643 | 1 | 3.0643 | 1
227 | Classroom | 0 | 0 |  |  | 693 | 15 | 0 |  | 8 | 5544 | 0 | 1 | 0 | 0 | 0 | 0
229 | Classroom | 377 | 25 |  |  | 676 | 15 | 15 |  | 8 | 5408 | 4.1827 | 1 | 4.1827 | 2 | 4.1827 | 2
230 | Classroom | 358 | 23 |  |  | 680 | 15 | 15 |  | 8 | 5440 | 3.9485 | 1 | 3.9485 | 1 | 3.9485 | 1
231 | Classroom | 0 | 0 |  |  | 680 | 15 | 0 |  | 8 | 5440 | 0 | 1 | 0 | 0 | 0 | 0
232 | Classroom | 315 | 21 |  |  | 638 | 14 | 14 |  | 8 | 5104 | 3.703 | 1 | 3.703 | 1 | 3.703 | 1
233 | Classroom | 246 | 16 |  |  | 597 | 13 | 13 |  | 8 | 4776 | 3.0905 | 1 | 3.0905 | 1 | 3.0905 | 1
244 | Classroom | 357 | 23 |  |  | 840 | 19 | 19 |  | 8 | 6720 | 3.1875 | 1 | 3.1875 | 1 | 3.1875 | 1
245 | Classroom | 316 | 21 |  |  | 840 | 19 | 19 |  | 8 | 6720 | 2.8214 | 1 | 2.8214 | 1 | 2.8214 | 1
246 | Classroom | 315 | 21 |  |  | 683 | 15 | 15 |  | 8 | 5464 | 3.459 | 1 | 3.459 | 1 | 3.459 | 1
247 | Classroom | 368 | 24 |  |  | 686 | 15 | 15 |  | 8 | 5488 | 4.0233 | 1 | 4.0233 | 2 | 4.0233 | 2
248 | Classroom | 401 | 26 |  |  | 705 | 16 | 16 |  | 8 | 5640 | 4.266 | 1 | 4.266 | 2 | 4.266 | 2
249 | Classroom | 379 | 25 |  |  | 694 | 15 | 15 |  | 8 | 5552 | 4.0958 | 1 | 4.0958 | 2 | 4.0958 | 2
250 | Classroom | 314 | 20 |  |  | 687 | 15 | 15 |  | 8 | 5496 | 3.4279 | 1 | 3.4279 | 1 | 3.4279 | 1
251 | Classroom | 458 | 30 |  |  | 705 | 16 | 16 |  | 8 | 5640 | 4.8723 | 1 | 4.8723 | 2 | 4.8723 | 2
252 | Classroom | 364 | 24 |  |  | 670 | 15 | 15 |  | 8 | 5360 | 4.0746 | 1 | 4.0746 | 2 | 4.0746 | 2
253 | Classroom | 314 | 20 |  |  | 330 | 7 | 7 |  | 8 | 2640 | 7.1364 | 1 | 7.1364 | 2 | 7.1364 | 2
302 | classroom | 483 | 32 |  |  | 1260 | 28 | 28 |  | 8 | 10080 | 2.875 | 1 | 2.875 | 1 | 2.875 | 1
303 | Classroom | 331 | 22 |  |  | 1145 | 26 | 22 |  | 8 | 9160 | 2.1681 | 1 | 2.1681 | 1 | 2.1681 | 1
304 | Classroom | 291 | 19 |  |  | 670 | 15 | 15 |  | 8 | 5360 | 3.2575 | 1 | 3.2575 | 1 | 3.2575 | 1
305 | Theater | 250 | 16 |  |  | 480 | 10 | 10 |  | 8 | 3840 | 3.9062 | 1 | 3.9062 | 1 | 3.9062 | 1
306 | Classroom | 430 | 28 |  |  | 661 | 15 | 15 |  | 8 | 5288 | 4.879 | 1 | 4.879 | 2 | 4.879 | 2
307 | Classroom | 478 | 31 |  |  | 657 | 14 | 14 |  | 8 | 5256 | 5.4566 | 1 | 5.4566 | 2 | 5.4566 | 2
308 | Classroom | 209 | 13 |  |  | 624 | 14 | 13 |  | 8 | 4992 | 2.512 | 1 | 2.512 | 1 | 2.512 | 1
309 | Classroom | 200 | 13 |  |  | 700 | 15 | 13 |  | 8 | 5600 | 2.1429 | 1 | 2.1429 | 1 | 2.1429 | 1
311 | Computer Lab | 64 | 4 |  |  | 827 | 18 | 4 |  | 8 | 6616 | 0.58041 | 1 | 0.58041 | 0 | 0.58041 | 0
321C | Storage | 210 | 14 |  |  | 157 | 3 | 3 |  | 8 | 1256 | 10.0318 | 1 | 10.0318 | 3 | 10.0318 | 3
323 | Classroom | 256 | 17 |  |  | 1082 | 24 | 17 |  | 8 | 8656 | 1.7745 | 1 | 1.7745 | 1 | 1.7745 | 1
325 | Computer Lab | 314 | 20 |  |  | 654 | 14 | 14 |  | 8 | 5232 | 3.6009 | 1 | 3.6009 | 1 | 3.6009 | 1
326 | Classroom | 294 | 19 |  |  | 654 | 14 | 14 |  | 8 | 5232 | 3.3716 | 1 | 3.3716 | 1 | 3.3716 | 1
327 | Computer Lab | 356 | 23 |  |  | 654 | 14 | 14 |  | 8 | 5232 | 4.0826 | 1 | 4.0826 | 2 | 4.0826 | 2
328 | Music Room | 289 | 19 |  |  | 647 | 14 | 14 |  | 8 | 5176 | 3.3501 | 1 | 3.3501 | 1 | 3.3501 | 1
329 | Computer Lab | 205 | 13 |  |  | 296 | 6 | 6 |  | 8 | 2368 | 5.1943 | 1 | 5.1943 | 2 | 5.1943 | 2
402 | Classroom | 625 | 41 |  |  | 941 | 21 | 21 |  | 8 | 7528 | 4.9814 | 1 | 4.9814 | 2 | 4.9814 | 2
403 | Classroom | 391 | 26 |  |  | 779 | 17 | 17 |  | 8 | 6232 | 3.7644 | 1 | 3.7644 | 1 | 3.7644 | 1
406 | Classroom | 531 | 35 |  |  | 1102 | 25 | 25 |  | 8 | 8816 | 3.6139 | 1 | 3.6139 | 1 | 3.6139 | 1
407 | Classroom | 510 | 34 |  |  | 1102 | 25 | 25 |  | 8 | 8816 | 3.471 | 1 | 3.471 | 1 | 3.471 | 1
Gym | Gym |  | 0 | Yes | 20 | 16550 | 376 | 376 |  | 8 | 132400 | 0 | 2.3523 | 0 | 0 | 20 | 3
- | Office Break Rm | 240 | 16 |  |  | 170 | 3 | 3 |  | 8 | 1360 | 10.5882 | 1 | 10.5882 | 3 | 10.5882 | 3
Sheet Last Modified: | 2021-05-03
School: | George W. Childs Elementary School @ Barratt
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom |  | 0 | Yes | 20 | 1575 | 35 | 35 |  | 8 | 12600 | 0 | 1 | 0 | 0 | 20 | 3
2 | Classroom |  | 0 | Yes | 20 | 1075 | 24 | 24 |  | 8 | 8600 | 0 | 1 | 0 | 0 | 20 | 3
3 | Head Start Kitchen |  | 0 | Yes | 20 | 696 | 15 | 15 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
4 | - |  | 0 |  |  | 1224 | 27 | 0 | House Fan | 8 | 9792 | 0 | 1 | 0 | 0 | 0 | 0
5 | - |  | 0 | Yes | 20 | 1035 | 23 | 23 | House Fan | 8 | 8280 | 0 | 1 | 0 | 0 | 20 | 3
8 | Classroom |  | 0 |  |  | 704 | 16 | 0 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
100B | VP's Office |  | 0 |  |  | 143 | 3 | 0 | House Fan | 8 | 1144 | 0 | 1 | 0 | 0 | 0 | 0
100C | Conference Room |  | 0 |  |  | 221 | 5 | 0 | House Fan | 8 | 1768 | 0 | 1 | 0 | 0 | 0 | 0
102 | Classroom |  | 0 | Yes | 20 | 1012 | 23 | 23 | House Fan | 8 | 8096 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 1012 | 23 | 23 | House Fan | 8 | 8096 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom |  | 0 | Yes | 20 | 851 | 19 | 19 | House Fan | 8 | 6808 | 0 | 1 | 0 | 0 | 20 | 3
105a | - |  | 0 | Yes | 20 | 575 | 13 | 13 | House Fan | 8 | 4600 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom |  | 0 | Yes | 20 | 800 | 18 | 18 | House Fan | 8 | 6400 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
109A | Counsleor |  | 0 |  |  | 240 | 5 | 0 | House Fan | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
109C | Dicipline Room |  | 0 |  |  | 240 | 5 | 0 |  | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
118 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
119 | Nurse |  | 0 | Yes | 20 | 420 | 9 | 9 | House Fan | 8 | 3360 | 0 | 1 | 0 | 0 | 20 | 3
121 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 460 | 10 | 10 | House Fan | 8 | 3680 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom |  | 0 | Yes | 20 | 504 | 11 | 11 | House Fan | 8 | 4032 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom |  | 0 | Yes | 20 | 912 | 20 | 20 | House Fan | 8 | 7296 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom |  | 0 | Yes | 20 | 828 | 18 | 18 | House Fan | 8 | 6624 | 0 | 1 | 0 | 0 | 20 | 3
210 | - |  | 0 | Yes | 20 | 912 | 20 | 20 | House Fan | 8 | 7296 | 0 | 1 | 0 | 0 | 20 | 3
212 | Classroom |  | 0 | Yes | 20 | 902 | 20 | 20 | House Fan | 8 | 7216 | 0 | 1 | 0 | 0 | 20 | 3
214 | Classroom |  | 0 | Yes | 20 | 966 | 21 | 21 | House Fan | 8 | 7728 | 0 | 1 | 0 | 0 | 20 | 3
215 | Classroom |  | 0 | Yes | 20 | 748 | 17 | 17 | House Fan | 8 | 5984 | 0 | 1 | 0 | 0 | 20 | 3
216 | Classroom |  | 0 | Yes | 20 | 1012 | 23 | 23 | House Fan | 8 | 8096 | 0 | 1 | 0 | 0 | 20 | 3
217 | - |  | 0 | Yes | 20 | 1450 | 32 | 32 | House Fan | 8 | 11600 | 0 | 1 | 0 | 0 | 20 | 3
219 | Classroom |  | 0 |  |  | 1450 | 32 | 0 | House Fan | 8 | 11600 | 0 | 1 | 0 | 0 | 0 | 0
220 | Classroom |  | 0 | Yes | 20 | 1058 | 24 | 24 | House Fan | 8 | 8464 | 0 | 1 | 0 | 0 | 20 | 3
222 | - |  | 0 | Yes | 20 | 1058 | 24 | 24 | House Fan | 8 | 8464 | 0 | 1 | 0 | 0 | 20 | 3
224 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
224B | - |  | 0 | Yes | 20 | 689 | 15 | 15 | House Fan | 8 | 5512 | 0 | 1 | 0 | 0 | 20 | 3
226 | Classroom |  | 0 |  |  | 704 | 16 | 0 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
2nd Floor | Special Needs Changing Room |  | 0 | Yes | 20 | 180 | 4 | 4 |  | 8 | 1440 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 | Yes | 20 | 989 | 22 | 22 | House Fan | 8 | 7912 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom |  | 0 | Yes | 20 | 989 | 22 | 22 | House Fan | 8 | 7912 | 0 | 1 | 0 | 0 | 20 | 3
304 | - |  | 0 |  |  | 704 | 16 | 0 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
305 | - |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
306 | - |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom |  | 0 | Yes | 20 | 552 | 12 | 12 | House Fan | 8 | 4416 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
310 | Classroom |  | 0 | Yes | 20 | 805 | 18 | 18 | House Fan | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
311 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
313 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
314 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
315 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
316 | Teacher's Lounge |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
401 | - |  | 0 |  |  | 989 | 22 | 0 | House Fan | 8 | 7912 | 0 | 1 | 0 | 0 | 0 | 0
402 | - |  | 0 | Yes | 20 | 989 | 22 | 22 | House Fan | 8 | 7912 | 0 | 1 | 0 | 0 | 20 | 3
404 | Classroom |  | 0 | Yes | 20 | 989 | 22 | 22 | House Fan | 8 | 7912 | 0 | 1 | 0 | 0 | 20 | 3
405 | Classroom |  | 0 |  |  | 460 | 10 | 0 | House Fan | 8 | 3680 | 0 | 1 | 0 | 0 | 0 | 0
406 | - |  | 0 | Yes | 20 | 989 | 22 | 22 | House Fan | 8 | 7912 | 0 | 1 | 0 | 0 | 20 | 3
407 | - |  | 0 | Yes | 20 | 828 | 18 | 18 | House Fan | 8 | 6624 | 0 | 1 | 0 | 0 | 20 | 3
408 | Classroom |  | 0 | Yes | 20 | 989 | 22 | 22 | House Fan | 8 | 7912 | 0 | 1 | 0 | 0 | 20 | 3
409 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
411 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
412 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
| Auditorium |  | 0 |  |  | 4128 | 93 | 0 |  | 8 | 33024 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria |  | 0 | Yes | 20 | 5512 | 125 | 125 | House Fan | 8 | 44096 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Special Needs Classroom |  | 0 | Yes | 20 | 345 | 7 | 7 | House Fan | 8 | 2760 | 0 | 1 | 0 | 0 | 20 | 3
- | IMC |  | 0 | Yes | 20 | 1725 | 39 | 39 | House Fan | 8 | 13800 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 726 | 16 | 16 | House Fan | 8 | 5808 | 0 | 1 | 0 | 0 | 20 | 3
- | Music Room |  | 0 |  |  | 726 | 16 | 0 | House Fan | 8 | 5808 | 0 | 1 | 0 | 0 | 0 | 0
- | Principal |  | 0 | Yes | 20 | 312 | 7 | 7 | House Fan | 8 | 2496 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-23
School: | Roberto Clemente Middle School and The LINC High School
Vendor: | Chadwick | Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 126 | 8 |  |  | 664 | 15 | 8 | 1 Univent & 1 AHU | 8 | 5312 | 1.4232 | 1 | 1.4232 | 1 | 1.4232 | 1
102 | Classroom | 54 | 3 |  |  | 664 | 15 | 3 | Univent | 8 | 5312 | 0.60994 | 1 | 0.60994 | 0 | 0.60994 | 0
103 | Classroom | 95 | 6 |  |  | 664 | 15 | 6 | 1 Univent & 1 AHU | 8 | 5312 | 1.073 | 1 | 1.073 | 1 | 1.073 | 1
104 | Classroom | 54 | 3 |  |  | 664 | 15 | 3 | Univent | 8 | 5312 | 0.60994 | 1 | 0.60994 | 0 | 0.60994 | 0
106 | Classroom | 24 | 1 |  |  | 312 | 7 | 1 |  | 8 | 2496 | 0.57692 | 1 | 0.57692 | 0 | 0.57692 | 0
107 | Classroom | 179 | 11 |  |  | 682 | 15 | 11 | 1 Unitvent & 2 AHU | 8 | 5456 | 1.9685 | 1 | 1.9685 | 1 | 1.9685 | 1
108 | Classroom | 108 | 7 |  |  | 682 | 15 | 7 | 1 Univent & 1 AHU | 8 | 5456 | 1.1877 | 1 | 1.1877 | 1 | 1.1877 | 1
109 | Classroom | 83 | 5 |  |  | 672 | 15 | 5 | 1 Univent & 1 AHU | 8 | 5376 | 0.92634 | 1 | 0.92634 | 0 | 0.92634 | 0
110 | Classroom | 54 | 3 |  |  | 530 | 12 | 3 | 1 Univent & 1 AHU | 8 | 4240 | 0.76415 | 1 | 0.76415 | 0 | 0.76415 | 0
111 | Classroom | 86 | 5 |  |  | 984 | 22 | 5 | 1 Univent & 1 AHU | 8 | 7872 | 0.65549 | 1 | 0.65549 | 0 | 0.65549 | 0
112 | Classroom | 113 | 7 |  |  | 984 | 22 | 7 | 1 Univent & 1 AHU | 8 | 7872 | 0.86128 | 1 | 0.86128 | 0 | 0.86128 | 0
113 | Classroom | 116 | 7 |  |  | 987 | 22 | 7 | 1 Univent & 1 AHU | 8 | 7896 | 0.88146 | 1 | 0.88146 | 0 | 0.88146 | 0
114 | Classroom | 87 | 5 |  |  | 987 | 22 | 5 | 1 Univent & 1 AHU | 8 | 7896 | 0.66109 | 1 | 0.66109 | 0 | 0.66109 | 0
115 | Classroom | 87 | 5 |  |  | 987 | 22 | 5 | 1 Univent & 1 AHU | 8 | 7896 | 0.66109 | 1 | 0.66109 | 0 | 0.66109 | 0
116 | Classroom | 82 | 5 |  |  | 987 | 22 | 5 | 1 Univent & 1 AHU | 8 | 7896 | 0.6231 | 1 | 0.6231 | 0 | 0.6231 | 0
121 | - | 24 | 1 |  |  | 264 | 6 | 1 |  | 8 | 2112 | 0.68182 | 1 | 0.68182 | 0 | 0.68182 | 0
125 | Classroom | 24 | 1 |  |  | 132 | 3 | 1 |  | 8 | 1056 | 1.3636 | 1 | 1.3636 | 1 | 1.3636 | 1
126 | Classroom | 24 | 1 |  |  | 132 | 3 | 1 |  | 8 | 1056 | 1.3636 | 1 | 1.3636 | 1 | 1.3636 | 1
128 | Classroom | 24 | 1 |  |  | 120 | 2 | 1 |  | 8 | 960 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1
129 | Classroom | 24 | 1 |  |  | 120 | 2 | 1 |  | 8 | 960 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1
131 | Classroom | 24 | 1 |  |  | 120 | 2 | 1 |  | 8 | 960 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1
132 | Classroom | 24 | 1 |  |  | 120 | 2 | 1 |  | 8 | 960 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1
144 | Classroom | 11 | 0 |  |  | 109 | 2 | 0 |  | 8 | 872 | 0.75688 | 1 | 0.75688 | 0 | 0.75688 | 0
145 | Classroom | 11 | 0 |  |  | 70 | 1 | 0 |  | 8 | 560 | 1.1786 | 1 | 1.1786 | 1 | 1.1786 | 1
146 | Classroom | 10 | 0 |  |  | 286 | 6 | 0 |  | 8 | 2288 | 0.26224 | 1 | 0.26224 | 0 | 0.26224 | 0
147 | Classroom | 10 | 0 |  |  | 160 | 3 | 0 |  | 8 | 1280 | 0.46875 | 1 | 0.46875 | 0 | 0.46875 | 0
148 | Classroom | 10 | 0 |  |  | 80 | 1 | 0 |  | 8 | 640 | 0.9375 | 1 | 0.9375 | 0 | 0.9375 | 0
149 | Classroom | 10 | 0 |  |  | 90 | 2 | 0 |  | 8 | 720 | 0.83333 | 1 | 0.83333 | 0 | 0.83333 | 0
150 | Classroom | 10 | 0 |  |  | 108 | 2 | 0 |  | 8 | 864 | 0.69444 | 1 | 0.69444 | 0 | 0.69444 | 0
151 | Classroom | 10 | 0 |  |  | 70 | 1 | 0 |  | 8 | 560 | 1.0714 | 1 | 1.0714 | 1 | 1.0714 | 1
152 | Classroom | 10 | 0 |  |  | 108 | 2 | 0 |  | 8 | 864 | 0.69444 | 1 | 0.69444 | 0 | 0.69444 | 0
153 | Classroom | 10 | 0 |  |  | 108 | 2 | 0 |  | 8 | 864 | 0.69444 | 1 | 0.69444 | 0 | 0.69444 | 0
201 | Classroom | 91 | 6 |  |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 8 | 6528 | 0.8364 | 1 | 0.8364 | 0 | 0.8364 | 0
202 | Classroom | 63 | 4 |  |  | 816 | 18 | 4 | 1 Univent & 1 AHU | 8 | 6528 | 0.57904 | 1 | 0.57904 | 0 | 0.57904 | 0
203 | Classroom | 86 | 5 |  |  | 816 | 18 | 5 | 1 Univent & 1 AHU | 8 | 6528 | 0.79044 | 1 | 0.79044 | 0 | 0.79044 | 0
204 | Classroom | 48 | 3 |  |  | 816 | 18 | 3 | 1 Univent & 1 AHU | 8 | 6528 | 0.44118 | 1 | 0.44118 | 0 | 0.44118 | 0
205 | Classroom | 96 | 6 |  |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 8 | 6528 | 0.88235 | 1 | 0.88235 | 0 | 0.88235 | 0
206 | Classroom | 198 | 13 |  |  | 816 | 18 | 13 | 1 Univent & 1 AHU | 8 | 6528 | 1.8199 | 1 | 1.8199 | 1 | 1.8199 | 1
207 | Classroom | 199 | 13 |  |  | 816 | 18 | 13 | 1 Univent & 1 AHU | 8 | 6528 | 1.829 | 1 | 1.829 | 1 | 1.829 | 1
208 | Classroom | 69 | 4 |  |  | 816 | 18 | 4 | 1 Univent & 1 AHU | 8 | 6528 | 0.63419 | 1 | 0.63419 | 0 | 0.63419 | 0
209 | Classroom | 186 | 12 |  |  | 816 | 18 | 12 | 1 Univent & 1 AHU | 8 | 6528 | 1.7096 | 1 | 1.7096 | 1 | 1.7096 | 1
210 | Classroom | 91 | 6 |  |  | 792 | 18 | 6 | 1 Univent & 1 AHU | 8 | 6336 | 0.86174 | 1 | 0.86174 | 0 | 0.86174 | 0
211 | Classroom | 191 | 12 |  |  | 675 | 15 | 12 | 1 Univent & 1 AHU | 8 | 5400 | 2.1222 | 1 | 2.1222 | 1 | 2.1222 | 1
212 | Classroom | 62 | 4 |  |  | 624 | 14 | 4 | 1 Univent & 1 AHU | 8 | 4992 | 0.74519 | 1 | 0.74519 | 0 | 0.74519 | 0
213 | Classroom | 150 | 10 |  |  | 675 | 15 | 10 | 1 Univent & 1 AHU | 8 | 5400 | 1.6667 | 1 | 1.6667 | 1 | 1.6667 | 1
214 | Classroom | 67 | 4 |  |  | 775 | 17 | 4 | 1 Univent & 1 AHU | 8 | 6200 | 0.64839 | 1 | 0.64839 | 0 | 0.64839 | 0
215 | Classroom | 90 | 6 |  |  | 675 | 15 | 6 | 1 Univent & 1 AHU | 8 | 5400 | 1 | 1 | 1 | 0 | 1 | 0
216 | Classroom | 44 | 2 |  |  | 689 | 15 | 2 | 1 Univent & 1 AHU | 8 | 5512 | 0.47896 | 1 | 0.47896 | 0 | 0.47896 | 0
217 | Classroom | 74 | 4 |  |  | 684 | 15 | 4 | 1 Univent & 1 AHU | 8 | 5472 | 0.8114 | 1 | 0.8114 | 0 | 0.8114 | 0
218 | Classroom | 64 | 4 |  |  | 684 | 15 | 4 | 1 Univent & 1 AHU | 8 | 5472 | 0.70175 | 1 | 0.70175 | 0 | 0.70175 | 0
219 | Classroom | 163 | 10 |  |  | 768 | 17 | 10 | 1 Univent & 1 AHU | 8 | 6144 | 1.5918 | 1 | 1.5918 | 1 | 1.5918 | 1
220 | Classroom | 42 | 2 |  |  | 768 | 17 | 2 | 1 Univent & 1 AHU | 8 | 6144 | 0.41016 | 1 | 0.41016 | 0 | 0.41016 | 0
221 | Classroom | 68 | 4 |  |  | 768 | 17 | 4 | 1 Univent & 1 AHU | 8 | 6144 | 0.66406 | 1 | 0.66406 | 0 | 0.66406 | 0
222 | Classroom | 37 | 2 |  |  | 768 | 17 | 2 | Univent | 8 | 6144 | 0.36133 | 1 | 0.36133 | 0 | 0.36133 | 0
223 | Classroom | 417 | 27 |  |  | 768 | 17 | 17 | 1 Univent & 1 AHU | 8 | 6144 | 4.0723 | 1 | 4.0723 | 2 | 4.0723 | 2
224 | Classroom | 69 | 4 |  |  | 768 | 17 | 4 | 1 Univent & 1 AHU | 8 | 6144 | 0.67383 | 1 | 0.67383 | 0 | 0.67383 | 0
225 | Classroom | 136 | 9 |  |  | 768 | 17 | 9 | 1 Univent & 1 AHU | 8 | 6144 | 1.3281 | 1 | 1.3281 | 1 | 1.3281 | 1
226 | Classroom | 63 | 4 |  |  | 816 | 18 | 4 | 1 Univent & 1 AHU | 8 | 6528 | 0.57904 | 1 | 0.57904 | 0 | 0.57904 | 0
227 | Classroom | 125 | 8 |  |  | 744 | 16 | 8 | 1 Univent & 1 AHU | 8 | 5952 | 1.2601 | 1 | 1.2601 | 1 | 1.2601 | 1
228 | Classroom | 58 | 3 |  |  | 744 | 16 | 3 | 1 Univent & 1 AHU | 8 | 5952 | 0.58468 | 1 | 0.58468 | 0 | 0.58468 | 0
301 | Classroom | 121 | 8 |  |  | 816 | 18 | 8 | 1 Univent & 1 AHU | 8 | 6528 | 1.1121 | 1 | 1.1121 | 1 | 1.1121 | 1
302 | Classroom | 98 | 6 |  |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 8 | 6528 | 0.90074 | 1 | 0.90074 | 0 | 0.90074 | 0
303 | Classroom | 69 | 4 |  |  | 816 | 18 | 4 | Univent | 8 | 6528 | 0.63419 | 1 | 0.63419 | 0 | 0.63419 | 0
304 | Classroom | 97 | 6 |  |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 8 | 6528 | 0.89154 | 1 | 0.89154 | 0 | 0.89154 | 0
305 | Classroom | 69 | 4 |  |  | 816 | 18 | 4 | Univent | 8 | 6528 | 0.63419 | 1 | 0.63419 | 0 | 0.63419 | 0
306 | Classroom | 132 | 8 |  |  | 816 | 18 | 8 | 1 Univent & 1 AHU | 8 | 6528 | 1.2132 | 1 | 1.2132 | 1 | 1.2132 | 1
307 | Classroom | 172 | 11 |  |  | 816 | 18 | 11 | 1 Univent & 1 AHU | 8 | 6528 | 1.5809 | 1 | 1.5809 | 1 | 1.5809 | 1
308 | Classroom | 95 | 6 |  |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 8 | 6528 | 0.87316 | 1 | 0.87316 | 0 | 0.87316 | 0
309 | Classroom | 238 | 15 |  |  | 816 | 18 | 15 | 1 Univent & 1 AHU | 8 | 6528 | 2.1875 | 1 | 2.1875 | 1 | 2.1875 | 1
310 | Classroom | 210 | 14 |  |  | 792 | 18 | 14 | 1 Univent & 1 AHU | 8 | 6336 | 1.9886 | 1 | 1.9886 | 1 | 1.9886 | 1
311 | Classroom | 153 | 10 |  |  | 675 | 15 | 10 | 1 Univent & 1 AHU | 8 | 5400 | 1.7 | 1 | 1.7 | 1 | 1.7 | 1
312 | Classroom | 103 | 6 |  |  | 624 | 14 | 6 | 1 Univent & 1 AHU | 8 | 4992 | 1.238 | 1 | 1.238 | 1 | 1.238 | 1
313 | Classroom | 69 | 4 |  |  | 675 | 15 | 4 | Univent | 8 | 5400 | 0.76667 | 1 | 0.76667 | 0 | 0.76667 | 0
314 | Classroom | 100 | 6 |  |  | 775 | 17 | 6 | 1 Univent & 1 AHU | 8 | 6200 | 0.96774 | 1 | 0.96774 | 0 | 0.96774 | 0
315 | Classroom | 198 | 13 |  |  | 675 | 15 | 13 | 1 Univent & 1 AHU | 8 | 5400 | 2.2 | 1 | 2.2 | 1 | 2.2 | 1
316 | Classroom | 97 | 6 |  |  | 689 | 15 | 6 | 1 Univent & 1 AHU | 8 | 5512 | 1.0559 | 1 | 1.0559 | 1 | 1.0559 | 1
317 | Classroom | 106 | 7 |  |  | 684 | 15 | 7 | 1 Univent & 1 AHU | 8 | 5472 | 1.1623 | 1 | 1.1623 | 1 | 1.1623 | 1
318 | Classroom | 96 | 6 |  |  | 684 | 15 | 6 | 1 Univent & 1 AHU | 8 | 5472 | 1.0526 | 1 | 1.0526 | 1 | 1.0526 | 1
319 | Classroom | 139 | 9 |  |  | 757 | 17 | 9 | 1 Univent & 1 AHU | 8 | 6056 | 1.3771 | 1 | 1.3771 | 1 | 1.3771 | 1
320 | Classroom | 106 | 7 |  |  | 768 | 17 | 7 | 1 Univent & 1 AHU | 8 | 6144 | 1.0352 | 1 | 1.0352 | 1 | 1.0352 | 1
321 | Classroom | 101 | 6 |  |  | 768 | 17 | 6 | 1 Univent & 1 AHU | 8 | 6144 | 0.98633 | 1 | 0.98633 | 0 | 0.98633 | 0
322 | Classroom | 160 | 10 |  |  | 768 | 17 | 10 | 1 Univent & 1 AHU | 8 | 6144 | 1.5625 | 1 | 1.5625 | 1 | 1.5625 | 1
323 | Classroom | 104 | 6 |  |  | 768 | 17 | 6 | 1 Univent & 1 AHU | 8 | 6144 | 1.0156 | 1 | 1.0156 | 1 | 1.0156 | 1
324 | Classroom | 99 | 6 |  |  | 768 | 17 | 6 | 1 Univent & 1 AHU | 8 | 6144 | 0.9668 | 1 | 0.9668 | 0 | 0.9668 | 0
325 | Classroom | 180 | 12 |  |  | 768 | 17 | 12 | 1 Univent & 1 AHU | 8 | 6144 | 1.7578 | 1 | 1.7578 | 1 | 1.7578 | 1
326 | Classroom | 94 | 6 |  |  | 816 | 18 | 6 | 1 Univent & 1 AHU | 8 | 6528 | 0.86397 | 1 | 0.86397 | 0 | 0.86397 | 0
327 | Classroom | 120 | 8 |  |  | 744 | 16 | 8 | 1 Univent & 1 AHU | 8 | 5952 | 1.2097 | 1 | 1.2097 | 1 | 1.2097 | 1
328 | Classroom | 252 | 16 |  |  | 744 | 16 | 16 | 1 Univent & 1 AHU | 8 | 5952 | 2.5403 | 1 | 2.5403 | 1 | 2.5403 | 1
503 | Classroom | 180 | 12 |  |  | 714 | 16 | 12 | 1 Univent & 1 AHU | 8 | 5712 | 1.8908 | 1 | 1.8908 | 1 | 1.8908 | 1
504 | Classroom | 252 | 16 |  |  | 849 | 19 | 16 | AHU | 8 | 6792 | 2.2261 | 1 | 2.2261 | 1 | 2.2261 | 1
505 | Classroom | 149 | 9 |  |  | 1456 | 33 | 9 | 1 Univent & 1 AHU | 8 | 11648 | 0.76751 | 1 | 0.76751 | 0 | 0.76751 | 0
507 | Classroom | 217 | 14 |  |  | 1458 | 33 | 14 | 1 Univent & 1 AHU | 8 | 11664 | 1.1163 | 1 | 1.1163 | 1 | 1.1163 | 1
508 | Classroom | 149 | 9 |  |  | 765 | 17 | 9 | Univent | 8 | 6120 | 1.4608 | 1 | 1.4608 | 1 | 1.4608 | 1
509 | Classroom | 204 | 13 |  |  | 738 | 16 | 13 | 1 Univent & 1 AHU | 8 | 5904 | 2.0732 | 1 | 2.0732 | 1 | 2.0732 | 1
510 | Classroom | 205 | 13 |  |  | 848 | 19 | 13 | 1 Univent & 1 AHU | 8 | 6784 | 1.8131 | 1 | 1.8131 | 1 | 1.8131 | 1
511 | Classroom | 226 | 15 |  |  | 740 | 16 | 15 | 1 Univent & 1 AHU | 8 | 5920 | 2.2905 | 1 | 2.2905 | 1 | 2.2905 | 1
512 | Classroom | 196 | 13 |  |  | 833 | 18 | 13 | 1 Univent & 1 AHU | 8 | 6664 | 1.7647 | 1 | 1.7647 | 1 | 1.7647 | 1
- | Auditorium | 1643 | 109 |  |  | 8015 | 182 | 109 |  | 8 | 64120 | 1.5374 | 1.4912 | 2.2926 | 1 | 2.2926 | 1
- | Basement / Cafe | 62 | 4 |  |  | 5900 | 134 | 4 |  | 8 | 47200 | 0.078814 | 1.062 | 0.083703 | 0 | 0.083703 | 0
- | cubicle-1 | 48 | 3 |  |  | 437 | 9 | 3 |  | 8 | 3496 | 0.8238 | 1 | 0.8238 | 0 | 0.8238 | 0
- | GYM | 2494 | 166 |  |  | 2633 | 59 | 59 |  | 8 | 21064 | 7.1041 | 1.062 | 7.5448 | 2 | 7.5448 | 2
- | library | 288 | 19 |  |  | 2675 | 60 | 19 |  | 8 | 21400 | 0.80748 | 1.062 | 0.85757 | 0 | 0.85757 | 0
- | mail room | 24 | 1 |  |  | 153 | 3 | 1 |  | 8 | 1224 | 1.1765 | 1 | 1.1765 | 1 | 1.1765 | 1
- | Link Main Office | 201 | 13 |  |  | 809 | 18 | 13 |  | 8 | 6472 | 1.8634 | 1 | 1.8634 | 1 | 1.8634 | 1
- | Clemente Main Office | 24 | 1 |  |  | 240 | 5 | 1 |  | 8 | 1920 | 0.75 | 1 | 0.75 | 0 | 0.75 | 0
Sheet Last Modified: | 2021-04-01
School: | Cleveland
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
109 | - |  | 0 | Yes | 20 | 850 | 19 | 19 |  | 8 | 6800 | 0 | 1 | 0 | 0 | 20 | 3
110 | - |  | 0 | Yes | 20 | 840 | 19 | 19 |  | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-19
School: | Benjamin B. Comegys Elementary School | House fan Abated
Vendor: | Devine | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
K-1 | Classroom | 418 | 27 |  |  | 2240 | 50 | 27 | Unit Ventilator | 8 | 17920 | 1.3996 | 1 | 1.3996 | 1 | 1.3996 | 1
K-2 | Classroom | 462 | 30 |  |  | 2240 | 50 | 30 | Unit Ventilator | 8 | 17920 | 1.5469 | 1 | 1.5469 | 1 | 1.5469 | 1
100 | Classroom | 366 | 24 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 3.1771 | 1 | 3.1771 | 1 | 3.1771 | 1
101 | Classroom | 369 | 24 |  |  | 832 | 18 | 18 | Unit Ventilator | 8 | 6656 | 3.3263 | 1 | 3.3263 | 1 | 3.3263 | 1
103 | Classroom | 273 | 18 |  |  | 864 | 19 | 18 | Unit Ventilator | 8 | 6912 | 2.3698 | 1 | 2.3698 | 1 | 2.3698 | 1
104 | Classroom | 0 | 0 | Yes | 20 | 576 | 13 | 13 | Unit Ventilator | 8 | 4608 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom | 231 | 15 |  |  | 864 | 19 | 15 | Unit Ventilator | 8 | 6912 | 2.0052 | 1 | 2.0052 | 1 | 2.0052 | 1
106 | Classroom | 710 | 47 |  |  | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 7.9241 | 1 | 7.9241 | 2 | 7.9241 | 2
200 | Classroom | 251 | 16 |  |  | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 2.8013 | 1 | 2.8013 | 1 | 2.8013 | 1
201 | Classroom | 0 | 0 | Yes | 20 | 365 | 8 | 8 | Radiator | 8 | 2920 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 371 | 24 |  |  | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 4.1406 | 1 | 4.1406 | 2 | 4.1406 | 2
203 | Classroom | 1226 | 81 |  |  | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 13.683 | 1 | 13.683 | 3 | 13.683 | 3
204 | Classroom | 426 | 28 |  |  | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 4.7545 | 1 | 4.7545 | 2 | 4.7545 | 2
205 | Classroom | 366 | 24 |  |  | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 4.0848 | 1 | 4.0848 | 2 | 4.0848 | 2
206 | Classroom | 320 | 21 |  |  | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 3.5714 | 1 | 3.5714 | 1 | 3.5714 | 1
207 | Classroom | 0 | 0 | Yes | 20 | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 283 | 18 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 2.9155 | 1 | 2.9155 | 1 | 2.9155 | 1
209 | Classroom | 288 | 19 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 2.967 | 1 | 2.967 | 1 | 2.967 | 1
210 | Classroom | 303 | 20 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 3.1216 | 1 | 3.1216 | 1 | 3.1216 | 1
211 | Classroom | 272 | 18 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 2.8022 | 1 | 2.8022 | 1 | 2.8022 | 1
212 | Classroom | 135 | 9 |  |  | 728 | 16 | 9 | Unit Ventilator | 8 | 5824 | 1.3908 | 1 | 1.3908 | 1 | 1.3908 | 1
213 | Classroom | 913 | 60 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 9.4059 | 1 | 9.4059 | 2 | 9.4059 | 2
214 | Classroom | 446 | 29 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 4.5948 | 1 | 4.5948 | 2 | 4.5948 | 2
300 | Classroom | 226 | 15 |  |  | 728 | 16 | 15 | Unit Ventilator | 8 | 5824 | 2.3283 | 1 | 2.3283 | 1 | 2.3283 | 1
301 | Classroom | 254 | 16 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 2.6168 | 1 | 2.6168 | 1 | 2.6168 | 1
302 | Classroom | 322 | 21 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 3.3173 | 1 | 3.3173 | 1 | 3.3173 | 1
303 | Classroom | 213 | 14 |  |  | 728 | 16 | 14 | Unit Ventilator | 8 | 5824 | 2.1944 | 1 | 2.1944 | 1 | 2.1944 | 1
304 | Classroom | 0 | 0 | Yes | 20 | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom | 858 | 57 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 8.8393 | 1 | 8.8393 | 2 | 8.8393 | 2
306 | Classroom | 883 | 58 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 9.0968 | 1 | 9.0968 | 2 | 9.0968 | 2
307 | Classroom | 209 | 13 |  |  | 728 | 16 | 13 | Unit Ventilator | 8 | 5824 | 2.1532 | 1 | 2.1532 | 1 | 2.1532 | 1
- | Art Classroom | 385 | 25 |  |  | 616 | 14 | 14 | Unit Ventilator | 8 | 4928 | 4.6875 | 1 | 4.6875 | 2 | 4.6875 | 2
- | Main Office |  | 0 | Yes | 20 | 936 | 21 | 21 | Radiator | 8 | 7488 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 360 | 8 | 8 | Radiator | 8 | 2880 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office |  | 0 | Yes | 20 | 391 | 8 | 8 | Radiator | 8 | 3128 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 280 | 6 | 6 | Radiator | 8 | 2240 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 271 | 18 |  |  | 4320 | 98 | 18 | AHU | 8 | 34560 | 0.47049 | 1.062 | 0.49967 | 0 | 0.49967 | 0
- | Gym / Cafe | 477 | 31 |  |  | 3672 | 83 | 31 | AHU | 8 | 29376 | 0.97426 | 1.062 | 1.0347 | 1 | 1.0347 | 1
Sheet Last Modified: | 2021-04-29
School: | Watson Comly Elementary School | House fan Abated
Vendor: | Emcor Fluidics | 2nd Retest | 3rd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
102A | Classroom |  | 0 |  |  | 155 | 3 | 0 | House Fan | 8 | 1240 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
103A | Classroom |  | 0 |  |  | 164 | 3 | 0 | House Fan | 8 | 1312 | 0 | 1 | 0 | 0 | 0 | 0
104 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom | 555 | 37 |  |  | 910 | 20 | 20 | Unit Ventilator | 8 | 7280 | 4.5742 | 1 | 4.5742 | 2 | 4.5742 | 2
106 | Classroom | 581 | 38 |  |  | 910 | 20 | 20 | Unit Ventilator | 8 | 7280 | 4.7885 | 1 | 4.7885 | 2 | 4.7885 | 2
107 | Classroom | 609 | 40 |  |  | 910 | 20 | 20 | Unit Ventilator | 8 | 7280 | 5.0192 | 1 | 5.0192 | 2 | 5.0192 | 2
108 | Classroom |  | 0 | Yes | 20 | 910 | 20 | 20 | Unit Ventilator | 8 | 7280 | 0 | 1 | 0 | 0 | 20 | 3
110 (ESOL) | Classroom |  | 0 | Yes | 20 | 439 | 9 | 9 |  | 8 | 3512 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 435 | 9 | 9 |  | 8 | 3480 | 0 | 1 | 0 | 0 | 20 | 3
201A | Classroom |  | 0 | Yes | 20 | 306 | 6 | 6 | House Fan | 8 | 2448 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 | Yes | 20 | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom |  | 0 | Yes | 20 | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom |  | 0 | Yes | 20 | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom |  | 0 | Yes | 20 | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom |  | 0 | Yes | 20 | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom | 147 | 9 |  |  | 812 | 18 | 9 | Unit Ventilator | 8 | 6496 | 1.3578 | 1 | 1.3578 | 1 | 1.3578 | 1
212 | Classroom | 199 | 13 | Yes | 20 | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 1.8381 | 1 | 1.8381 | 1 | 21.8381 | 3
213 | Classroom | 197 | 13 |  |  | 812 | 18 | 13 | Unit Ventilator | 8 | 6496 | 1.8196 | 1 | 1.8196 | 1 | 1.8196 | 1
214 | Classroom | 156 | 10 | Yes | 20 | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 1.4409 | 1 | 1.4409 | 1 | 21.4409 | 3
215 | Classroom | 510 | 34 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 4.7106 | 1 | 4.7106 | 2 | 4.7106 | 2
216 | Classroom | 385 | 25 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 3.556 | 1 | 3.556 | 1 | 3.556 | 1
Art | 1st Fl Art Room | 342 | 22 |  |  | 1672 | 38 | 22 | Unit Ventilator | 8 | 13376 | 1.5341 | 1 | 1.5341 | 1 | 1.5341 | 1
- | Art Teacher Office | 205 | 13 |  |  | 308 | 7 | 7 | MUA | 8 | 2464 | 4.9919 | 1 | 4.9919 | 2 | 4.9919 | 2
- | Special Needs Room | 335 | 22 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 3.0942 | 1 | 3.0942 | 1 | 3.0942 | 1
- | Music Room | 383 | 25 |  |  | 594 | 13 | 13 | Unit Ventilator | 8 | 4752 | 4.8359 | 1 | 4.8359 | 2 | 4.8359 | 2
- | Office - Main | 183 | 12 |  |  | 169 | 3 | 3 | Unit Ventilator | 8 | 1352 | 8.1213 | 1 | 8.1213 | 2 | 8.1213 | 2
- | Office-2 |  | 0 |  |  | 176 | 4 | 0 |  | 8 | 1408 | 0 | 1 | 0 | 0 | 0 | 0
- | 2nd Floor Counselors Office |  | 0 | Yes | 20 | 182 | 4 | 4 |  | 8 | 1456 | 0 | 1 | 0 | 0 | 20 | 3
- | Counslor waiting rm |  | 0 |  |  | 104 | 2 | 0 |  | 8 | 832 | 0 | 1 | 0 | 0 | 0 | 0
- | Conference room 1st floor |  | 0 |  |  | 338 | 7 | 0 |  | 8 | 2704 | 0 | 1 | 0 | 0 | 0 | 0
- | Amy's Room |  | 0 |  |  | 156 | 3 | 0 |  | 8 | 1248 | 0 | 1 | 0 | 0 | 0 | 0
- | Principals Office | 0 | 0 | Yes | 20 | 196 | 4 | 4 | N/A | 8 | 1568 | 0 | 1 | 0 | 0 | 20 | 3
- | Break Room | 0 | 0 |  |  | 390 | 8 | 0 | N/A | 8 | 3120 | 0 | 1 | 0 | 0 | 0 | 0
- | 2nd Floor Staff room |  | 0 |  |  | 170 | 3 | 0 |  | 8 | 1360 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurse 1st Floor | 90 | 6 |  |  | 150 | 3 | 3 | MUA | 8 | 1200 | 4.5 | 1 | 4.5 | 2 | 4.5 | 2
- | Nurse Office | 125 | 8 |  |  | 344 | 7 | 7 | MUA | 8 | 2752 | 2.7253 | 1 | 2.7253 | 1 | 2.7253 | 1
- | Nurse waiting |  | 0 | Yes | 20 | 202 | 4 | 4 |  | 8 | 1616 | 0 | 1 | 0 | 0 | 20 | 3
- | Cafeteria |  | 0 | Yes | 20 | 3321 | 75 | 75 |  | 8 | 26568 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Gym |  | 0 |  |  | 4838 | 109 | 0 |  | 8 | 38704 | 0 | 1.062 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-20
School: | Russell Conwell Middle School / Conwell Annex
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Conwell Main Building
B1 | - |  | 0 |  |  | 1575 | 35 | 0 |  | 8 | 12600 | 0 | 1 | 0 | 0 | 0 | 0
B2 | - |  | 0 |  |  | 782 | 17 | 0 |  | 8 | 6256 | 0 | 1 | 0 | 0 | 0 | 0
Main Office | Office |  | 0 | Yes | 20 | 396 | 9 | 9 |  | 8 | 3168 | 0 | 1 | 0 | 0 | 20 | 3
Nurse | Office |  | 0 | Yes | 20 | 473 | 10 | 10 |  | 8 | 3784 | 0 | 1 | 0 | 0 | 20 | 3
102 | - |  | 0 |  |  | 575 | 13 | 0 |  | 8 | 4600 | 0 | 1 | 0 | 0 | 0 | 0
107 | - |  | 0 |  |  | 120 | 2 | 0 |  | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
108 | - |  | 0 | Yes | 20 | 816 | 18 | 18 |  | 8 | 6528 | 0 | 1 | 0 | 0 | 20 | 3
109 | - |  | 0 | Yes | 20 | 850 | 19 | 19 |  | 8 | 6800 | 0 | 1 | 0 | 0 | 20 | 3
111 | - |  | 0 | Yes | 20 | 1200 | 27 | 27 |  | 8 | 9600 | 0 | 1 | 0 | 0 | 20 | 3
103/104/ IMC | - |  | 0 |  |  | 4300 | 97 | 0 |  | 8 | 34400 | 0 | 1.062 | 0 | 0 | 0 | 0
201 | - |  | 0 |  |  | 850 | 19 | 0 |  | 8 | 6800 | 0 | 1 | 0 | 0 | 0 | 0
202 | - |  | 0 |  |  | 840 | 19 | 0 |  | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
204 | - |  | 0 |  |  | 625 | 14 | 0 |  | 8 | 5000 | 0 | 1 | 0 | 0 | 0 | 0
205 | - |  | 0 |  |  | 550 | 12 | 0 |  | 8 | 4400 | 0 | 1 | 0 | 0 | 0 | 0
206 | - |  | 0 |  |  | 875 | 19 | 0 |  | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
207 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
208 | - |  | 0 |  |  | 805 | 18 | 0 |  | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
209 | - |  | 0 | Yes | 20 | 850 | 19 | 19 |  | 8 | 6800 | 0 | 1 | 0 | 0 | 20 | 3
301 | - |  | 0 | Yes | 20 | 720 | 16 | 16 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
302 | - |  | 0 |  |  | 805 | 18 | 0 |  | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
303 | - |  | 0 |  |  | 550 | 12 | 0 |  | 8 | 4400 | 0 | 1 | 0 | 0 | 0 | 0
304 | - |  | 0 |  |  | 625 | 14 | 0 |  | 8 | 5000 | 0 | 1 | 0 | 0 | 0 | 0
305 | - |  | 0 |  |  | 506 | 11 | 0 |  | 8 | 4048 | 0 | 1 | 0 | 0 | 0 | 0
306 | - |  | 0 |  |  | 875 | 19 | 0 |  | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
307 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
308 | - |  | 0 |  |  | 805 | 18 | 0 |  | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
309 | - |  | 0 | Yes | 20 | 575 | 13 | 13 |  | 8 | 4600 | 0 | 1 | 0 | 0 | 20 | 3
Conwell Annex
1 | - |  | 0 |  |  | 1276 | 29 | 0 |  | 8 | 10208 | 0 | 1 | 0 | 0 | 0 | 0
9 | - |  | 0 |  |  | 1200 | 27 | 0 |  | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
102 | - |  | 0 |  |  | 2318 | 52 | 0 |  | 8 | 18544 | 0 | 1 | 0 | 0 | 0 | 0
104 | - |  | 0 |  |  | 870 | 19 | 0 |  | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
203 | - |  | 0 |  |  | 4800 | 109 | 0 |  | 8 | 38400 | 0 | 1.062 | 0 | 0 | 0 | 0
200 | - |  | 0 |  |  | 512 | 11 | 0 |  | 8 | 4096 | 0 | 1 | 0 | 0 | 0 | 0
301 | - |  | 0 |  |  | 840 | 19 | 0 |  | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
305 | - |  | 0 |  |  | 630 | 14 | 0 |  | 8 | 5040 | 0 | 1 | 0 | 0 | 0 | 0
306 | - |  | 0 |  |  | 768 | 17 | 0 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29
School: | Cook-Wissahickon Elementary-Middle School
Vendor: | Devine | Devine Retest | Capital
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 310 | 20 |  |  | 695 | 15 | 15 | Unit Ventilator | 8 | 5560 | 3.3453 | 1 | 3.3453 | 1 | 3.3453 | 1
2 | Classroom | 280 | 18 |  |  | 950 | 21 | 18 | Unit Ventilator | 8 | 7600 | 2.2105 | 1 | 2.2105 | 1 | 2.2105 | 1
3 | Classroom | 443 | 29 |  |  | 513 | 11 | 11 | Unit Ventilator | 8 | 4104 | 6.4766 | 1 | 6.4766 | 2 | 6.4766 | 2
15 | - | 131 | 8 |  |  |  | 0 | 0 | Unit Ventilator
016A | - | 131 | 8 |  |  |  | 0 | 0 | Unit Ventilator
101 | Classroom | 341 | 22 |  |  | 717 | 16 | 16 | Unit Ventilator | 8 | 5736 | 3.5669 | 1 | 3.5669 | 1 | 3.5669 | 1
102 | Classroom | 694 | 46 |  |  | 700 | 15 | 15 | Unit Ventilator | 8 | 5600 | 7.4357 | 1 | 7.4357 | 2 | 7.4357 | 2
103 | Classroom | 0 | 0 |  |  | 1495 | 33 | 0 | Unit Ventilator | 8 | 11960 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom | 337 | 22 |  |  | 1005 | 22 | 22 | Unit Ventilator | 8 | 8040 | 2.5149 | 1 | 2.5149 | 1 | 2.5149 | 1
106 | Classroom | 342 | 22 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 2.776 | 1 | 2.776 | 1 | 2.776 | 1
107 | Classroom | 327 | 21 |  |  | 630 | 14 | 14 | Unit Ventilator | 8 | 5040 | 3.8929 | 1 | 3.8929 | 1 | 3.8929 | 1
108 | Classroom | 352 | 23 |  |  | 441 | 10 | 10 | Unit Ventilator | 8 | 3528 | 5.9864 | 1 | 5.9864 | 2 | 5.9864 | 2
109 | Classroom | 585 | 39 |  |  | 851 | 19 | 19 | Unit Ventilator | 8 | 6808 | 5.1557 | 1 | 5.1557 | 2 | 5.1557 | 2
110 | Classroom | 280 | 18 |  |  | 674 | 15 | 15 | Unit Ventilator | 8 | 5392 | 3.1157 | 1 | 3.1157 | 1 | 3.1157 | 1
111 | Classroom | 285 | 19 |  |  | 386 | 8 | 8 | Unit Ventilator | 8 | 3088 | 5.5376 | 1 | 5.5376 | 2 | 5.5376 | 2
200 | Classroom | 366 | 24 |  |  | 636 | 14 | 14 | Unit Ventilator | 8 | 5088 | 4.316 | 1 | 4.316 | 2 | 4.316 | 2
200A | Classroom | 324 | 21 |  |  | 485 | 11 | 11 | Unit Ventilator | 8 | 3880 | 5.0103 | 1 | 5.0103 | 2 | 5.0103 | 2
201 | Classroom | 310 | 20 |  |  | 447 | 10 | 10 | Unit Ventilator | 8 | 3576 | 5.2013 | 1 | 5.2013 | 2 | 5.2013 | 2
202 | Classroom | 418 | 27 |  |  | 730 | 16 | 16 | Unit Ventilator | 8 | 5840 | 4.2945 | 1 | 4.2945 | 2 | 4.2945 | 2
203 | Classroom | 0 | 0 |  |  | 813 | 18 | 0 | Unit Ventilator | 8 | 6504 | 0 | 1 | 0 | 0 | 0 | 0
204 | Classroom | 326 | 21 |  |  | 867 | 19 | 19 | Unit Ventilator | 8 | 6936 | 2.8201 | 1 | 2.8201 | 1 | 2.8201 | 1
205 | Classroom | 401 | 26 |  |  | 716 | 16 | 16 | Unit Ventilator | 8 | 5728 | 4.2004 | 1 | 4.2004 | 2 | 4.2004 | 2
206 | Classroom | 0 | 0 |  |  | 810 | 18 | 0 | Unit Ventilator | 8 | 6480 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom | 284 | 18 |  |  | 456 | 10 | 10 | Unit Ventilator | 8 | 3648 | 4.6711 | 1 | 4.6711 | 2 | 4.6711 | 2
208 | Classroom | 336 | 22 |  |  | 422 | 9 | 9 | Unit Ventilator | 8 | 3376 | 5.9716 | 1 | 5.9716 | 2 | 5.9716 | 2
209 | Classroom | 300 | 20 |  |  | 731 | 16 | 16 | Unit Ventilator | 8 | 5848 | 3.078 | 1 | 3.078 | 1 | 3.078 | 1
210 | Classroom | 315 | 21 |  |  | 731 | 16 | 16 | Unit Ventilator | 8 | 5848 | 3.2319 | 1 | 3.2319 | 1 | 3.2319 | 1
211 | Classroom | 0 | 0 |  |  | 872 | 19 | 0 | Unit Ventilator | 8 | 6976 | 0 | 1 | 0 | 0 | 0 | 0
212 | Classroom | 440 | 29 |  |  | 365 | 8 | 8 | Unit Ventilator | 8 | 2920 | 9.0411 | 1 | 9.0411 | 2 | 9.0411 | 2
213 | Room | 310 | 20 |  |  | 525 | 11 | 11 | Air Handling Unit | 8 | 4200 | 4.4286 | 1 | 4.4286 | 2 | 4.4286 | 2
- | Cafeteria | 2213 | 147 |  |  |  | 0 | 0 | Air Handling Unit
- | Copy Room | 340 | 22 |  |  | 199 | 4 | 4 | Air Handling Unit | 8 | 1592 | 12.8141 | 1 | 12.8141 | 3 | 12.8141 | 3
- | Gymnasium | 1486 | 99 |  |  | 4325 | 98 | 98 | Air Handling Unit | 8 | 34600 | 2.5769 | 1.062 | 2.7367 | 1 | 2.7367 | 1
- | Library | 1180 | 78 |  |  | 2998 | 68 | 68 | Air Handling Unit | 8 | 23984 | 2.952 | 1.062 | 3.1351 | 1 | 3.1351 | 1
- | Main Office | 789 | 52 |  |  | 396 | 9 | 9 | Air Handling Unit | 8 | 3168 | 14.9432 | 1 | 14.9432 | 3 | 14.9432 | 3
- | Pricipal's office | 498 | 33 |  |  | 358 | 8 | 8 | Air Handling Unit | 8 | 2864 | 10.433 | 1 | 10.433 | 3 | 10.433 | 3
- | Speech Room | 330 | 22 |  |  | 358 | 8 | 8 | Air Handling Unit | 8 | 2864 | 6.9134 | 1 | 6.9134 | 2 | 6.9134 | 2
- | Prep and lounge |  | 0 |  |  | 602 | 13 | 0 |  | 8 | 4816 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26
School: | Jay Cooke Elementary School | House Fan Abated
Vendor: | Devine | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100C | Classroom | 293 | 19 |  |  | 506 | 11 | 11 | House Fan | 8 | 4048 | 4.3429 | 1 | 4.3429 | 2 | 4.3429 | 2
101C | Classroom | 411 | 27 |  |  | 543 | 12 | 12 | House Fan | 8 | 4344 | 5.6768 | 1 | 5.6768 | 2 | 5.6768 | 2
102C | Classroom | 284 | 18 |  |  | 833 | 18 | 18 | House Fan | 8 | 6664 | 2.557 | 1 | 2.557 | 1 | 2.557 | 1
103 | Classroom | 531 | 35 |  |  | 1082 | 24 | 24 | House Fan | 8 | 8656 | 3.6807 | 1 | 3.6807 | 1 | 3.6807 | 1
104 | Classroom | 279 | 18 |  |  | 809 | 18 | 18 | House Fan | 8 | 6472 | 2.5865 | 1 | 2.5865 | 1 | 2.5865 | 1
105 | Classroom | 369 | 24 |  |  | 695 | 15 | 15 | House Fan | 8 | 5560 | 3.982 | 1 | 3.982 | 1 | 3.982 | 1
108 | Classroom | 328 | 21 |  |  | 858 | 19 | 19 | House Fan | 8 | 6864 | 2.8671 | 1 | 2.8671 | 1 | 2.8671 | 1
109 | Office | 313 | 20 |  |  | 548 | 12 | 12 | House Fan | 8 | 4384 | 4.2838 | 1 | 4.2838 | 2 | 4.2838 | 2
110 | Classroom | 422 | 28 |  |  | 665 | 15 | 15 | House Fan | 8 | 5320 | 4.7594 | 1 | 4.7594 | 2 | 4.7594 | 2
110A | Office | 335 | 22 |  |  | 333 | 7 | 7 | House Fan | 8 | 2664 | 7.545 | 1 | 7.545 | 2 | 7.545 | 2
201 | Classroom | 335 | 22 |  |  | 711 | 16 | 16 | House Fan | 8 | 5688 | 3.5338 | 1 | 3.5338 | 1 | 3.5338 | 1
202 | Classroom | 515 | 34 |  |  | 674 | 15 | 15 | House Fan | 8 | 5392 | 5.7307 | 1 | 5.7307 | 2 | 5.7307 | 2
202A | Classroom | 347 | 23 |  |  | 1015 | 23 | 23 | House Fan | 8 | 8120 | 2.564 | 1 | 2.564 | 1 | 2.564 | 1
203 | Classroom | 388 | 25 |  |  | 717 | 16 | 16 | House Fan | 8 | 5736 | 4.0586 | 1 | 4.0586 | 2 | 4.0586 | 2
205 | Office | 0 | 0 |  |  | 304 | 6 | 0 | House Fan(partial Duct) | 8 | 2432 | 0 | 1 | 0 | 0 | 0 | 0
206 | Office | 0 | 0 | Yes | 20 | 240 | 5 | 5 | House Fan(partial Duct) | 8 | 1920 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom | 435 | 29 |  |  | 726 | 16 | 16 | House Fan | 8 | 5808 | 4.4938 | 1 | 4.4938 | 2 | 4.4938 | 2
207A | Classroom | 330 | 22 |  |  | 334 | 7 | 7 | House Fan | 8 | 2672 | 7.4102 | 1 | 7.4102 | 2 | 7.4102 | 2
208 | Classroom | 433 | 28 |  |  | 673 | 15 | 15 | House Fan | 8 | 5384 | 4.8254 | 1 | 4.8254 | 2 | 4.8254 | 2
208A | Storage | 279 | 18 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 2.9062 | 1 | 2.9062 | 1 | 2.9062 | 1
209 | Classroom | 363 | 24 |  |  | 693 | 15 | 15 | House Fan | 8 | 5544 | 3.9286 | 1 | 3.9286 | 1 | 3.9286 | 1
210 | Classroom | 378 | 25 |  |  | 650 | 14 | 14 | House Fan | 8 | 5200 | 4.3615 | 1 | 4.3615 | 2 | 4.3615 | 2
211 | Classroom | 748 | 49 |  |  | 211 | 4 | 4 | House Fan | 8 | 1688 | 26.5877 | 1 | 26.5877 | 4 | 26.5877 | 4
212 | Classroom | 736 | 49 |  |  | 774 | 17 | 17 | House Fan | 8 | 6192 | 7.1318 | 1 | 7.1318 | 2 | 7.1318 | 2
213 | Classroom | 807 | 53 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 8.4062 | 1 | 8.4062 | 2 | 8.4062 | 2
214 | Classroom | 846 | 56 |  |  | 727 | 16 | 16 | House Fan | 8 | 5816 | 8.7276 | 1 | 8.7276 | 2 | 8.7276 | 2
215 | Classroom | 797 | 53 |  |  | 748 | 17 | 17 | House Fan | 8 | 5984 | 7.9913 | 1 | 7.9913 | 2 | 7.9913 | 2
216 | Classroom | 811 | 54 |  |  | 762 | 17 | 17 | House Fan | 8 | 6096 | 7.9823 | 1 | 7.9823 | 2 | 7.9823 | 2
217 | Classroom | 496 | 33 |  |  | 670 | 15 | 15 | House Fan | 8 | 5360 | 5.5522 | 1 | 5.5522 | 2 | 5.5522 | 2
301 | Classroom | 278 | 18 |  |  | 711 | 16 | 16 | House Fan | 8 | 5688 | 2.9325 | 1 | 2.9325 | 1 | 2.9325 | 1
302 | Classroom | 522 | 34 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 5.6739 | 1 | 5.6739 | 2 | 5.6739 | 2
302A | Classroom | 273 | 18 |  |  | 405 | 9 | 9 | House Fan | 8 | 3240 | 5.0556 | 1 | 5.0556 | 2 | 5.0556 | 2
303 | Classroom | 581 | 38 |  |  | 714 | 16 | 16 | House Fan | 8 | 5712 | 6.1029 | 1 | 6.1029 | 2 | 6.1029 | 2
303A | Classroom | 284 | 18 | Yes | 20 | 405 | 9 | 9 | House Fan | 8 | 3240 | 5.2593 | 1 | 5.2593 | 2 | 25.2593 | 4
303B | Classroom | 0 | 0 | Yes | 20 | 216 | 4 | 4 |  | 8 | 1728 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom | 633 | 42 |  |  | 882 | 20 | 20 | House Fan | 8 | 7056 | 5.3827 | 1 | 5.3827 | 2 | 5.3827 | 2
305 | Classroom | 437 | 29 |  |  | 907 | 20 | 20 | House Fan | 8 | 7256 | 3.6136 | 1 | 3.6136 | 1 | 3.6136 | 1
306 | Classroom | 456 | 30 |  |  | 815 | 18 | 18 | House Fan | 8 | 6520 | 4.1963 | 1 | 4.1963 | 2 | 4.1963 | 2
307 | Classroom | 541 | 36 |  |  | 798 | 18 | 18 | House Fan | 8 | 6384 | 5.0846 | 1 | 5.0846 | 2 | 5.0846 | 2
308 | Classroom | 469 | 31 |  |  | 1031 | 23 | 23 | House Fan | 8 | 8248 | 3.4117 | 1 | 3.4117 | 1 | 3.4117 | 1
309 | Classroom | 456 | 30 |  |  | 896 | 20 | 20 | House Fan | 8 | 7168 | 3.817 | 1 | 3.817 | 1 | 3.817 | 1
310 | Classroom | 441 | 29 |  |  | 769 | 17 | 17 | House Fan | 8 | 6152 | 4.301 | 1 | 4.301 | 2 | 4.301 | 2
311 | Classroom | 617 | 41 |  |  | 985 | 22 | 22 | House Fan | 8 | 7880 | 4.698 | 1 | 4.698 | 2 | 4.698 | 2
312 | Classroom | 333 | 22 |  |  | 713 | 16 | 16 | House Fan | 8 | 5704 | 3.5028 | 1 | 3.5028 | 1 | 3.5028 | 1
312A | Classroom | 325 | 21 |  |  | 332 | 7 | 7 | House Fan | 8 | 2656 | 7.3419 | 1 | 7.3419 | 2 | 7.3419 | 2
313 | Classroom | 393 | 26 |  |  | 666 | 15 | 15 | House Fan | 8 | 5328 | 4.4257 | 1 | 4.4257 | 2 | 4.4257 | 2
313A | Classroom | 307 | 20 |  |  | 703 | 15 | 15 | House Fan | 8 | 5624 | 3.2752 | 1 | 3.2752 | 1 | 3.2752 | 1
314 | Classroom | 365 | 24 |  |  | 709 | 16 | 16 | House Fan | 8 | 5672 | 3.8611 | 1 | 3.8611 | 1 | 3.8611 | 1
315 | Classroom | 271 | 18 |  |  | 650 | 14 | 14 | House Fan | 8 | 5200 | 3.1269 | 1 | 3.1269 | 1 | 3.1269 | 1
316 | Classroom | 673 | 44 |  |  | 765 | 17 | 17 | House Fan | 8 | 6120 | 6.598 | 1 | 6.598 | 2 | 6.598 | 2
317 | Classroom | 278 | 18 |  |  | 729 | 16 | 16 | House Fan | 8 | 5832 | 2.8601 | 1 | 2.8601 | 1 | 2.8601 | 1
318 | Classroom | 744 | 49 |  |  | 730 | 16 | 16 | House Fan | 8 | 5840 | 7.6438 | 1 | 7.6438 | 2 | 7.6438 | 2
319 | Classroom | 656 | 43 |  |  | 719 | 16 | 16 | House Fan | 8 | 5752 | 6.8428 | 1 | 6.8428 | 2 | 6.8428 | 2
320 | Classroom | 764 | 50 |  |  | 700 | 15 | 15 | House Fan | 8 | 5600 | 8.1857 | 1 | 8.1857 | 2 | 8.1857 | 2
321 | Classroom | 480 | 32 |  |  | 787 | 17 | 17 | House Fan | 8 | 6296 | 4.5743 | 1 | 4.5743 | 2 | 4.5743 | 2
322 | Classroom | 353 | 23 |  |  | 653 | 14 | 14 | House Fan | 8 | 5224 | 4.0544 | 1 | 4.0544 | 2 | 4.0544 | 2
- | Asst. Principal Waiting Room | 125 | 8 |  |  | 118 | 2 | 2 | House Fan | 8 | 944 | 7.9449 | 1 | 7.9449 | 2 | 7.9449 | 2
- | Asst. Principal Office |  | 0 | Yes | 20 | 110 | 2 | 2 |  | 8 | 880 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 3875 | 258 |  |  | 3793 | 86 | 86 | House Fan | 8 | 30344 | 7.6621 | 1.062 | 8.1375 | 2 | 8.1375 | 2
- | Boy's Cafeteria | 1403 | 93 |  |  | 2254 | 51 | 51 | House Fan | 8 | 18032 | 4.6684 | 1 | 4.6684 | 2 | 4.6684 | 2
- | Boy's Gym | 1455 | 97 |  |  | 2806 | 63 | 63 | House Fan | 8 | 22448 | 3.889 | 1.062 | 4.1302 | 2 | 4.1302 | 2
- | Counselor Waiting Room | 134 | 8 |  |  | 123 | 2 | 2 | House Fan | 8 | 984 | 8.1707 | 1 | 8.1707 | 2 | 8.1707 | 2
- | Counselor Office 1 | 0 | 0 | Yes | 20 | 92 | 2 | 2 | House Fan | 8 | 736 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office 2 | 0 | 0 |  |  | 101 | 2 | 0 | House Fan | 8 | 808 | 0 | 1 | 0 | 0 | 0 | 0
- | Counselor Office 3 | 0 | 0 |  |  | 156 | 3 | 0 |  | 8 | 1248 | 0 | 1 | 0 | 0 | 0 | 0
- | Girl's Cafeteria | 1178 | 78 |  |  | 1944 | 44 | 44 | House Fan | 8 | 15552 | 4.5448 | 1 | 4.5448 | 2 | 4.5448 | 2
- | Girl's Gym | 1461 | 97 |  |  | 2806 | 63 | 63 | House Fan | 8 | 22448 | 3.905 | 1.062 | 4.1473 | 2 | 4.1473 | 2
- | Kitchen | 321 | 21 |  |  | 409 | 9 | 9 | House Fan | 8 | 3272 | 5.8863 | 1 | 5.8863 | 2 | 5.8863 | 2
- | Library | 1042 | 69 |  |  | 2053 | 46 | 46 | House Fan | 8 | 16424 | 3.8066 | 1 | 3.8066 | 1 | 3.8066 | 1
- | Nurse Office | 53 | 3 | Yes | 20 | 186 | 4 | 4 | House Fan | 8 | 1488 | 2.1371 | 1 | 2.1371 | 1 | 22.1371 | 3
- | Principal Office | 141 | 9 |  |  | 336 | 7 | 7 | House Fan | 8 | 2688 | 3.1473 | 1 | 3.1473 | 1 | 3.1473 | 1
- | Weight Room | 842 | 56 |  |  | 1027 | 23 | 23 | House Fan | 8 | 8216 | 6.149 | 1 | 6.149 | 2 | 6.149 | 2
- | CASST Office | 0 | 0 | Yes | 20 | 264 | 6 | 6 |  | 8 | 2112 | 0 | 1 | 0 | 0 | 20 | 3
- | SPECM Speech Therapy Office | 0 | 0 |  |  | 112 | 2 | 0 |  | 8 | 896 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29
School: | William Cramp Elementary School
Vendor: | Devine Brothers | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
102 | Office | 27 | 1 |  |  | 133 | 3 | 1 |  | 8 | 1064 | 1.5226 | 1 | 1.5226 | 1 | 1.5226 | 1
102A | Office | 20 | 1 |  |  | 133 | 3 | 1 |  | 8 | 1064 | 1.1278 | 1 | 1.1278 | 1 | 1.1278 | 1
103 | Small Classroom | 103 | 6 |  |  | 533 | 12 | 6 |  | 8 | 4264 | 1.4493 | 1 | 1.4493 | 1 | 1.4493 | 1
106 | Classroom | 387 | 25 |  |  | 1033 | 23 | 23 | Unit Ventilator | 8 | 8264 | 2.8098 | 1 | 2.8098 | 1 | 2.8098 | 1
107 | Counselor | 137 | 9 |  |  | 385 | 8 | 8 |  | 8 | 3080 | 2.6688 | 1 | 2.6688 | 1 | 2.6688 | 1
108 | Classroom | 148 | 9 | Yes | 20 | 1220 | 27 | 27 | Unit Ventilator | 8 | 9760 | 0.90984 | 1 | 0.90984 | 0 | 20.9098 | 3
109 | Classroom | 405 | 27 |  |  | 1120 | 25 | 25 | Unit Ventilator | 8 | 8960 | 2.7121 | 1 | 2.7121 | 1 | 2.7121 | 1
110 | Classroom | 277 | 18 |  |  | 1543 | 35 | 18 | Unit Ventilator | 8 | 12344 | 1.3464 | 1 | 1.3464 | 1 | 1.3464 | 1
111 | Classroom | 318 | 21 |  |  | 1228 | 27 | 21 | Unit Ventilator | 8 | 9824 | 1.9422 | 1 | 1.9422 | 1 | 1.9422 | 1
112 | Classroom | 498 | 33 |  |  | 1170 | 26 | 26 |  | 8 | 9360 | 3.1923 | 1 | 3.1923 | 1 | 3.1923 | 1
112E | Office | 29 | 1 |  |  | 200 | 4 | 1 |  | 8 | 1600 | 1.0875 | 1 | 1.0875 | 1 | 1.0875 | 1
113 | Classroom | 338 | 22 |  |  | 1311 | 29 | 22 | Unit Ventilator | 8 | 10488 | 1.9336 | 1 | 1.9336 | 1 | 1.9336 | 1
13A | Classroom | 307 | 20 |  |  | 1073 | 24 | 20 |  | 8 | 8584 | 2.1459 | 1 | 2.1459 | 1 | 2.1459 | 1
13B | Classroom | 500 | 33 |  |  | 1294 | 29 | 29 | Unit Ventilator | 8 | 10352 | 2.898 | 1 | 2.898 | 1 | 2.898 | 1
114 | Art | 385 | 25 |  |  | 876 | 19 | 19 | AHU | 8 | 7008 | 3.2962 | 1 | 3.2962 | 1 | 3.2962 | 1
115 | Classroom | 283 | 18 |  |  | 1559 | 35 | 18 |  | 8 | 12472 | 1.3614 | 1 | 1.3614 | 1 | 1.3614 | 1
119 | Office | 0 | 0 |  |  | 459 | 10 | 0 |  | 8 | 3672 | 0 | 1 | 0 | 0 | 0 | 0
200 | Classroom | 763 | 50 |  |  | 967 | 21 | 21 | Unit Ventilator | 8 | 7736 | 5.9178 | 1 | 5.9178 | 2 | 5.9178 | 2
201 | Classroom | 605 | 40 |  |  | 825 | 18 | 18 | Unit Ventilator | 8 | 6600 | 5.5 | 1 | 5.5 | 2 | 5.5 | 2
202 | Counselor | 26 | 1 |  |  | 151 | 3 | 1 |  | 8 | 1208 | 1.2914 | 1 | 1.2914 | 1 | 1.2914 | 1
203/212 | Speech | 27 | 1 |  |  | 151 | 3 | 1 |  | 8 | 1208 | 1.3411 | 1 | 1.3411 | 1 | 1.3411 | 1
204 | Classroom | 527 | 35 |  |  | 1050 | 23 | 23 | Unit Ventilator | 8 | 8400 | 3.7643 | 1 | 3.7643 | 1 | 3.7643 | 1
205 | Classroom | 128 | 8 |  |  | 902 | 20 | 8 | Unit Ventilator | 8 | 7216 | 1.0643 | 1 | 1.0643 | 1 | 1.0643 | 1
206 | Classroom | 437 | 29 |  |  | 1030 | 23 | 23 | Unit Ventilator | 8 | 8240 | 3.182 | 1 | 3.182 | 1 | 3.182 | 1
207 | Classroom | 440 | 29 |  |  | 971 | 22 | 22 | Unit Ventilator | 8 | 7768 | 3.3986 | 1 | 3.3986 | 1 | 3.3986 | 1
208 | Classroom | 544 | 36 |  |  | 950 | 21 | 21 | Unit Ventilator | 8 | 7600 | 4.2947 | 1 | 4.2947 | 2 | 4.2947 | 2
209 | Classroom | 438 | 29 |  |  | 897 | 20 | 20 | Unit Ventilator | 8 | 7176 | 3.6622 | 1 | 3.6622 | 1 | 3.6622 | 1
210 | Classroom | 462 | 30 |  |  | 967 | 21 | 21 | Unit Ventilator | 8 | 7736 | 3.5832 | 1 | 3.5832 | 1 | 3.5832 | 1
211 | Classroom | 118 | 7 |  |  | 976 | 22 | 7 | Unit Ventilator | 8 | 7808 | 0.90676 | 1 | 0.90676 | 0 | 0.90676 | 0
300 | Classroom | 782 | 52 |  |  | 866 | 19 | 19 | Unit Ventilator | 8 | 6928 | 6.7725 | 1 | 6.7725 | 2 | 6.7725 | 2
301 | Classroom | 675 | 45 |  |  | 982 | 22 | 22 | Unit Ventilator | 8 | 7856 | 5.1553 | 1 | 5.1553 | 2 | 5.1553 | 2
302 | Counselor | 42 | 2 |  |  | 151 | 3 | 2 |  | 8 | 1208 | 2.0861 | 1 | 2.0861 | 1 | 2.0861 | 1
303/312 | Office | 48 | 3 |  |  | 151 | 3 | 3 |  | 8 | 1208 | 2.3841 | 1 | 2.3841 | 1 | 2.3841 | 1
304 | Classroom | 133 | 8 |  |  | 1050 | 23 | 8 | Unit Ventilator | 8 | 8400 | 0.95 | 1 | 0.95 | 0 | 0.95 | 0
304 | Classroom | 330 | 22 |  |  | 1050 | 23 | 22 |  | 8 | 8400 | 2.3571 | 1 | 2.3571 | 1 | 2.3571 | 1
305 | Classroom | 393 | 26 |  |  | 968 | 22 | 22 | Unit Ventilator | 8 | 7744 | 3.0449 | 1 | 3.0449 | 1 | 3.0449 | 1
306 | Classroom | 122 | 8 |  |  | 855 | 19 | 8 | Unit Ventilator | 8 | 6840 | 1.0702 | 1 | 1.0702 | 1 | 1.0702 | 1
306 | Classroom | 501 | 33 |  |  | 855 | 19 | 19 |  | 8 | 6840 | 4.3947 | 1 | 4.3947 | 2 | 4.3947 | 2
307 | Classroom | 713 | 47 |  |  | 965 | 21 | 21 | Unit Ventilator | 8 | 7720 | 5.5415 | 1 | 5.5415 | 2 | 5.5415 | 2
308 | Classroom | 320 | 21 |  |  | 772 | 17 | 17 | Unit Ventilator | 8 | 6176 | 3.1088 | 1 | 3.1088 | 1 | 3.1088 | 1
309 | Classroom | 471 | 31 |  |  | 941 | 21 | 21 | Unit Ventilator | 8 | 7528 | 3.754 | 1 | 3.754 | 1 | 3.754 | 1
310 | Classroom | 327 | 21 |  |  | 972 | 22 | 21 | Unit Ventilator | 8 | 7776 | 2.5231 | 1 | 2.5231 | 1 | 2.5231 | 1
311 | Classroom | 421 | 28 |  |  | 896 | 20 | 20 | Unit Ventilator | 8 | 7168 | 3.524 | 1 | 3.524 | 1 | 3.524 | 1
313 | Classroom | 329 | 21 |  |  | 368 | 8 | 8 | Unit Ventilator | 8 | 2944 | 6.7052 | 1 | 6.7052 | 2 | 6.7052 | 2
- | Gym | 42 | 2 |  |  | 4800 | 109 | 2 | AHU | 8 | 38400 | 0.065625 | 1.062 | 0.069696 | 0 | 0.069696 | 0
- | LGI | 736 | 49 |  |  | 697 | 15 | 15 | AHU | 8 | 5576 | 7.9197 | 1 | 7.9197 | 2 | 7.9197 | 2
- | Admin Office | 827 | 55 |  |  | 251 | 5 | 5 | AHU | 8 | 2008 | 24.7112 | 1 | 24.7112 | 4 | 24.7112 | 4
- | Cafeteria | 630 | 42 |  |  | 7287 | 165 | 42 | AHU | 8 | 58296 | 0.64841 | 1.4912 | 0.96689 | 0 | 0.96689 | 0
- | Computer Lab | 498 | 33 |  |  | 2840 | 64 | 33 | Unit Ventilator | 8 | 22720 | 1.3151 | 1.062 | 1.3967 | 1 | 1.3967 | 1
- | Computer Room | 1015 | 67 |  |  | 2437 | 55 | 55 | AHU | 8 | 19496 | 3.1237 | 1 | 3.1237 | 1 | 3.1237 | 1
- | Conference/Storage | 110 | 7 |  |  | 199 | 4 | 4 |  | 8 | 1592 | 4.1457 | 1 | 4.1457 | 2 | 4.1457 | 2
- | IMC Office | 40 | 2 |  |  | 141 | 3 | 2 |  | 8 | 1128 | 2.1277 | 1 | 2.1277 | 1 | 2.1277 | 1
- | IMC Library | 36 | 2 |  |  | 2456 | 55 | 2 |  | 8 | 19648 | 0.10993 | 1 | 0.10993 | 0 | 0.10993 | 0
- | Kitchen | 1510 | 100 |  |  | 972 | 22 | 22 |  | 8 | 7776 | 11.6512 | 1 | 11.6512 | 3 | 11.6512 | 3
- | Library North Classroom | 537 | 35 |  |  | 2635 | 59 | 35 | Unit Ventilator | 8 | 21080 | 1.5285 | 1.062 | 1.6233 | 1 | 1.6233 | 1
- | Library South Classroom | 443 | 29 |  |  | 362 | 8 | 8 | Unit Ventilator | 8 | 2896 | 9.1782 | 1 | 9.1782 | 2 | 9.1782 | 2
- | Mail Room | 47 | 3 |  |  | 133 | 3 | 3 |  | 8 | 1064 | 2.6504 | 1 | 2.6504 | 1 | 2.6504 | 1
- | Main Office | 113 | 7 |  |  | 571 | 12 | 7 |  | 8 | 4568 | 1.4842 | 1 | 1.4842 | 1 | 1.4842 | 1
- | Nurse Office | 109 | 7 |  |  | 374 | 8 | 7 |  | 8 | 2992 | 2.1858 | 1 | 2.1858 | 1 | 2.1858 | 1
- | Nurse Exam Room | 44 | 2 |  |  | 128 | 2 | 2 |  | 8 | 1024 | 2.5781 | 1 | 2.5781 | 1 | 2.5781 | 1
- | Principals Office | 60 | 4 |  |  | 258 | 5 | 4 |  | 8 | 2064 | 1.7442 | 1 | 1.7442 | 1 | 1.7442 | 1
- | Teachers Lounge | 354 | 23 |  |  | 775 | 17 | 17 |  | 8 | 6200 | 3.4258 | 1 | 3.4258 | 1 | 3.4258 | 1
- | Vice Principal's Office | 64 | 4 |  |  | 213 | 4 | 4 |  | 8 | 1704 | 2.2535 | 1 | 2.2535 | 1 | 2.2535 | 1
Sheet Last Modified: | 2021-04-05
School: | Kenneth C. Crossan Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Kindergarten Classroom | 580 | 38 |  |  | 1088 | 24 | 24 | House Fan | 8 | 8704 | 3.9982 | 1 | 3.9982 | 1 | 3.9982 | 1
2 | Classroom | 555 | 37 |  |  | 900 | 20 | 20 | House Fan | 8 | 7200 | 4.625 | 1 | 4.625 | 2 | 4.625 | 2
3 | Classroom | 522 | 34 |  |  | 930 | 21 | 21 | House Fan | 8 | 7440 | 4.2097 | 1 | 4.2097 | 2 | 4.2097 | 2
4 | Classroom | 299 | 19 |  |  | 840 | 19 | 19 | House Fan | 8 | 6720 | 2.6696 | 1 | 2.6696 | 1 | 2.6696 | 1
5 | Kindergarten Classroom |  | 0 | Yes | 20 | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
5 | Classroom | 505 | 33 |  |  | 600 | 13 | 13 | House Fan | 8 | 4800 | 6.3125 | 1 | 6.3125 | 2 | 6.3125 | 2
6 | Classroom | 820 | 54 |  |  | 805 | 18 | 18 | House Fan | 8 | 6440 | 7.6398 | 1 | 7.6398 | 2 | 7.6398 | 2
7 | Computer Classrm. | 437 | 29 |  |  | 900 | 20 | 20 | House Fan | 8 | 7200 | 3.6417 | 1 | 3.6417 | 1 | 3.6417 | 1
8 | Classroom | 580 | 38 |  |  | 1094 | 24 | 24 | House Fan | 8 | 8752 | 3.9762 | 1 | 3.9762 | 1 | 3.9762 | 1
9 | Classrom | 444 | 29 |  |  | 840 | 19 | 19 | House Fan | 8 | 6720 | 3.9643 | 1 | 3.9643 | 1 | 3.9643 | 1
9A | Teachers Rm. | 0 | 0 | Yes | 20 | 450 | 10 | 10 | N/A | 8 | 3600 | 0 | 1 | 0 | 0 | 20 | 3
10 | Classroom | 822 | 54 |  |  | 600 | 13 | 13 |  | 8 | 4800 | 10.275 | 1 | 10.275 | 3 | 10.275 | 3
11 | Classroom | 466 | 31 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 4.8542 | 1 | 4.8542 | 2 | 4.8542 | 2
12 | Classroom | 606 | 40 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 6.3125 | 1 | 6.3125 | 2 | 6.3125 | 2
13 | Classroom | 626 | 41 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 6.5208 | 1 | 6.5208 | 2 | 6.5208 | 2
- | Auditorium | 1107 | 73 |  |  | 2760 | 62 | 62 | House Fan | 8 | 22080 | 3.0082 | 1.062 | 3.1948 | 1 | 3.1948 | 1
- | Cafeteria/Gym | 0 | 0 |  |  | 2300 | 52 | 0 | N/A | 8 | 18400 | 0 | 1 | 0 | 0 | 0 | 0
- | Counselors Rm. | 0 | 0 | Yes | 20 | 450 | 10 | 10 | N/A | 8 | 3600 | 0 | 1 | 0 | 0 | 20 | 3
- | Grnd. Fl. Boys Bathrm. | 568 | 37 |  |  | 736 | 16 | 16 | House Fan | 8 | 5888 | 5.788 | 1 | 5.788 | 2 | 5.788 | 2
- | Grnd. Fl. Girls Bathrm. | 620 | 41 |  |  | 775 | 17 | 17 | House Fan | 8 | 6200 | 6 | 1 | 6 | 2 | 6 | 2
- | Ind. Arts Classroom | 0 | 0 |  |  | 600 | 13 | 0 | N/A | 8 | 4800 | 0 | 1 | 0 | 0 | 0 | 0
- | Library | 525 | 35 |  |  | 1152 | 26 | 26 | House Fan | 8 | 9216 | 3.418 | 1 | 3.418 | 1 | 3.418 | 1
- | Main Office | 0 | 0 | Yes | 20 | 460 | 10 | 10 | N/A | 8 | 3680 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 450 | 10 | 10 |  | 8 | 3600 | 0 | 1 | 0 | 0 | 20 | 3
- | Art Room |  | 0 | Yes | 20 | 600 | 13 | 13 |  | 8 | 4800 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Ofice | 0 | 0 |  |  | 450 | 10 | 0 | N/A | 8 | 3600 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29
School: | Anne Blakiston Day Elementary School
Vendor: | EMCOR / Chadwick
School: | Anne Blakiston Day Elementary School- Little School House
Vendor: | Chadwick | Part 2 and Exhaust | Exhaust
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Anna Blakiston Day Elementary School- Main Building
101 | classroom | 186 | 12 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 1.5852 | 1 | 1.5852 | 1 | 21.5852 | 3
102 | classroom | 194 | 12 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 1.6534 | 1 | 1.6534 | 1 | 21.6534 | 3
103 | classroom | 45 | 3 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 0.38352 | 1 | 0.38352 | 0 | 20.3835 | 3
104 | classroom | 75 | 5 | Yes | 20 | 1440 | 32 | 32 | Unit Ventilator | 8 | 11520 | 0.39062 | 1 | 0.39062 | 0 | 20.3906 | 3
105 | classroom | 126 | 8 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 1.0739 | 1 | 1.0739 | 1 | 21.0739 | 3
106 | classroom | 0 | 0 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 0 | 1 | 0 | 0 | 20 | 3
107 | classroom | 210 | 14 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 1.7898 | 1 | 1.7898 | 1 | 21.7898 | 3
108 | classroom | 0 | 0 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 0 | 1 | 0 | 0 | 20 | 3
109 | classroom |  | 0 | Yes | 20 | 880 | 20 | 20 |  | 8 | 7040 | 0 | 1 | 0 | 0 | 20 | 3
111 | Classroom |  | 0 | Yes | 20 | 880 | 20 | 20 |  | 8 | 7040 | 0 | 1 | 0 | 0 | 20 | 3
112 | Classroom |  | 0 | Yes | 20 | 260 | 5 | 5 |  | 8 | 2080 | 0 | 1 | 0 | 0 | 20 | 3
201 | classroom | 255 | 17 | Yes | 20 | 875 | 19 | 19 | Unit Ventilator | 8 | 7000 | 2.1857 | 1 | 2.1857 | 1 | 22.1857 | 3
202 | classroom | 257 | 17 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 2.1903 | 1 | 2.1903 | 1 | 22.1903 | 3
203 | classroom | 0 | 0 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 0 | 1 | 0 | 0 | 20 | 3
204 | classroom | 365 | 24 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 3.1108 | 1 | 3.1108 | 1 | 23.1108 | 3
205 | classroom | 0 | 0 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 0 | 1 | 0 | 0 | 20 | 3
206 | classroom | 84 | 5 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 0.71591 | 1 | 0.71591 | 0 | 20.7159 | 3
207 | classroom | 0 | 0 | Yes | 20 | 575 | 13 | 13 | Unit Ventilator | 8 | 4600 | 0 | 1 | 0 | 0 | 20 | 3
208 | classroom | 47 | 3 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 0.40057 | 1 | 0.40057 | 0 | 20.4006 | 3
209 | classroom | 235 | 15 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 2.0028 | 1 | 2.0028 | 1 | 22.0028 | 3
210 | classroom | 0 | 0 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 0 | 1 | 0 | 0 | 20 | 3
211 | classroom | 244 | 16 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 2.0795 | 1 | 2.0795 | 1 | 22.0795 | 3
214 | Classroom |  | 0 | Yes | 20 | 228 | 5 | 5 |  | 8 | 1824 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 0 | 0 |  |  | 3300 | 75 | 0 | AHU | 8 | 26400 | 0 | 1.062 | 0 | 0 | 0 | 0
- | GYM | 573 | 38 |  |  | 5000 | 113 | 38 | AHU | 8 | 40000 | 0.8595 | 1.062 | 0.91282 | 0 | 0.91282 | 0
- | Library | 0 | 0 |  |  | 2700 | 61 | 0 | RTU | 8 | 21600 | 0 | 1.062 | 0 | 0 | 0 | 0
Anna Blakiston Day Elementary School- Little School House
1 | classroom | 322 | 21 |  |  | 1056 | 24 | 21 | AHU | 8 | 8448 | 2.2869 | 1 | 2.2869 | 1 | 2.2869 | 1
2 | classroom | 274 | 18 |  |  | 1056 | 24 | 18 | AHU | 8 | 8448 | 1.946 | 1 | 1.946 | 1 | 1.946 | 1
3 | classroom | 322 | 21 |  |  | 1056 | 24 | 21 | AHU | 8 | 8448 | 2.2869 | 1 | 2.2869 | 1 | 2.2869 | 1
4 | classroom | 510 | 34 |  |  | 1056 | 24 | 24 | AHU | 8 | 8448 | 3.6222 | 1 | 3.6222 | 1 | 3.6222 | 1
5 | classroom | 302 | 20 |  |  | 1056 | 24 | 20 | AHU | 8 | 8448 | 2.1449 | 1 | 2.1449 | 1 | 2.1449 | 1
6 | classroom | 325 | 21 |  |  | 1056 | 24 | 21 | AHU | 8 | 8448 | 2.3082 | 1 | 2.3082 | 1 | 2.3082 | 1
7 | classroom | 302 | 20 |  |  | 1056 | 24 | 20 | AHU | 8 | 8448 | 2.1449 | 1 | 2.1449 | 1 | 2.1449 | 1
8 | classroom | 325 | 21 |  |  | 1056 | 24 | 21 | AHU | 8 | 8448 | 2.3082 | 1 | 2.3082 | 1 | 2.3082 | 1
9 | classroom | 302 | 20 |  |  | 1056 | 24 | 20 | AHU | 8 | 8448 | 2.1449 | 1 | 2.1449 | 1 | 2.1449 | 1
10 | classroom | 325 | 21 |  |  | 1056 | 24 | 21 | AHU | 8 | 8448 | 2.3082 | 1 | 2.3082 | 1 | 2.3082 | 1
11 | classroom | 302 | 20 |  |  | 1056 | 24 | 20 | AHU | 8 | 8448 | 2.1449 | 1 | 2.1449 | 1 | 2.1449 | 1
12 | classroom | 325 | 21 |  |  | 1056 | 24 | 21 | AHU | 8 | 8448 | 2.3082 | 1 | 2.3082 | 1 | 2.3082 | 1
- | Lunchroom | 1136 | 75 |  |  | 1750 | 39 | 39 | AHU | 8 | 14000 | 4.8686 | 1 | 4.8686 | 2 | 4.8686 | 2
- | Staff Bathroom Staff Toilet | 159 | 10 |  |  | 120 | 2 | 2 | N/A | 8 | 960 | 9.9375 | 1 | 9.9375 | 2 | 9.9375 | 2
- | Staff Bathroom Staff Toilet | 277 | 18 |  |  | 120 | 2 | 2 | N/A | 8 | 960 | 17.3125 | 1 | 17.3125 | 3 | 17.3125 | 3
- | Various Office | 392 | 26 |  |  |  | 0 | 0 | AHU
- | Corridor | 224 | 14 |  |  |  | 0 | 0 | FCU
- | Various Storage | 374 | 24 |  |  |  | 0 | 0 | AHU
Sheet Last Modified: | 2021-04-21
School: | Julia deBurgos Elementary School
Vendor: | Chadwick | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
108 | storage |  | 0 |  |  | 100 | 2 | 0 | AHU-1 | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
111 | work rm |  | 0 |  |  | 100 | 2 | 0 | AHU-1 | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
115 | office | 100 | 6 |  |  | 150 | 3 | 3 | AHU-1 | 8 | 1200 | 5 | 1 | 5 | 2 | 5 | 2
116 | classroom | 281 | 18 |  |  | 658 | 14 | 14 | Univent | 8 | 5264 | 3.2029 | 1 | 3.2029 | 1 | 3.2029 | 1
118 | classroom |  | 0 |  |  | 400 | 9 | 0 | AHU-1 | 8 | 3200 | 0 | 1 | 0 | 0 | 0 | 0
120 | classroom | 380 | 25 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.7549 | 1 | 3.7549 | 1 | 3.7549 | 1
121 | classroom | 288 | 19 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 2.8458 | 1 | 2.8458 | 1 | 2.8458 | 1
123 | classroom | 486 | 32 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 4.8024 | 1 | 4.8024 | 2 | 4.8024 | 2
125 | classroom | 307 | 20 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.0336 | 1 | 3.0336 | 1 | 3.0336 | 1
129 | classroom | 335 | 22 |  |  | 640 | 14 | 14 | Univent | 8 | 5120 | 3.9258 | 1 | 3.9258 | 1 | 3.9258 | 1
130 | classroom | 295 | 19 |  |  | 672 | 15 | 15 | Univent | 8 | 5376 | 3.2924 | 1 | 3.2924 | 1 | 3.2924 | 1
132 | classroom | 470 | 31 |  |  | 704 | 16 | 16 | Univent | 8 | 5632 | 5.0071 | 1 | 5.0071 | 2 | 5.0071 | 2
133 | classroom | 345 | 23 |  |  | 880 | 20 | 20 | Univent | 8 | 7040 | 2.9403 | 1 | 2.9403 | 1 | 2.9403 | 1
134 | classroom | 301 | 20 |  |  | 667 | 15 | 15 | AHU-5 | 8 | 5336 | 3.3846 | 1 | 3.3846 | 1 | 3.3846 | 1
135 | classroom | 552 | 36 |  |  | 750 | 17 | 17 | Univent | 8 | 6000 | 5.52 | 1 | 5.52 | 2 | 5.52 | 2
136 | classroom | 291 | 19 |  |  | 750 | 17 | 17 | Univent | 8 | 6000 | 2.91 | 1 | 2.91 | 1 | 2.91 | 1
138 | classroom | 734 | 48 |  |  | 748 | 17 | 17 | AHU-5 | 8 | 5984 | 7.3596 | 1 | 7.3596 | 2 | 7.3596 | 2
139 | classroom | 0 | 0 | Yes | 20 | 704 | 16 | 16 | AHU-5 | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
139B | PRACTICE RM | 0 | 0 |  |  | 100 | 2 | 0 | AHU-5 | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
139C | PRACTICE RM | 0 | 0 |  |  | 100 | 2 | 0 | AHU-5 | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
148 | office | 244 | 16 |  |  | 350 | 7 | 7 | AHU-5 | 8 | 2800 | 5.2286 | 1 | 5.2286 | 2 | 5.2286 | 2
148A | office | 130 | 8 |  |  | 100 | 2 | 2 | AHU-5 | 8 | 800 | 9.75 | 1 | 9.75 | 2 | 9.75 | 2
148B | office | 54 | 3 |  |  | 110 | 2 | 2 | AHU-5 | 8 | 880 | 3.6818 | 1 | 3.6818 | 1 | 3.6818 | 1
148C | office | 37 | 2 |  |  | 100 | 2 | 2 | AHU-5 | 8 | 800 | 2.775 | 1 | 2.775 | 1 | 2.775 | 1
148D | office | 51 | 3 |  |  | 100 | 2 | 2 | AHU-5 | 8 | 800 | 3.825 | 1 | 3.825 | 1 | 3.825 | 1
148E | office | 67 | 4 |  |  | 100 | 2 | 2 | AHU-5 | 8 | 800 | 5.025 | 1 | 5.025 | 2 | 5.025 | 2
148F | office | 89 | 5 |  |  | 100 | 2 | 2 | AHU-5 | 8 | 800 | 6.675 | 1 | 6.675 | 2 | 6.675 | 2
148G | office | 44 | 2 |  |  | 100 | 2 | 2 | AHU-5 | 8 | 800 | 3.3 | 1 | 3.3 | 1 | 3.3 | 1
148H | office | 26 | 1 |  |  | 100 | 2 | 1 | AHU-5 | 8 | 800 | 1.95 | 1 | 1.95 | 1 | 1.95 | 1
148I | office | 64 | 4 |  |  | 100 | 2 | 2 | AHU-5 | 8 | 800 | 4.8 | 1 | 4.8 | 2 | 4.8 | 2
148L | office | 126 | 8 |  |  | 242 | 5 | 5 | AHU-5 | 8 | 1936 | 3.905 | 1 | 3.905 | 1 | 3.905 | 1
149 | office | 59 | 3 |  |  | 100 | 2 | 2 | AHU-5 | 8 | 800 | 4.425 | 1 | 4.425 | 2 | 4.425 | 2
- | Nurse Office |  | 0 | Yes | 20 | 180 | 4 | 4 | AHU-5 | 8 | 1440 | 0 | 1 | 0 | 0 | 20 | 3
151 | WAITING RM | 22 | 1 | Yes | 20 | 180 | 4 | 4 | AHU-5 | 8 | 1440 | 0.91667 | 1 | 0.91667 | 0 | 20.9167 | 3
151A | OFFICE | 0 | 0 |  |  | 110 | 2 | 0 | AHU-5 | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
151B | OFFICE | 17 | 1 |  |  | 150 | 3 | 1 | AHU-5 | 8 | 1200 | 0.85 | 1 | 0.85 | 0 | 0.85 | 0
151C | OFFICE | 17 | 1 |  |  | 80 | 1 | 1 | AHU-5 | 8 | 640 | 1.5938 | 1 | 1.5938 | 1 | 1.5938 | 1
151E | OFFICE | 0 | 0 |  |  | 100 | 2 | 0 | AHU-5 | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
152f | office | 39 | 2 |  |  | 99 | 2 | 2 | AHU-5 | 8 | 792 | 2.9545 | 1 | 2.9545 | 1 | 2.9545 | 1
152g | office | 47 | 3 |  |  | 99 | 2 | 2 | AHU-5 | 8 | 792 | 3.5606 | 1 | 3.5606 | 1 | 3.5606 | 1
152h | office | 0 | 0 |  |  | 208 | 4 | 0 | AHU-5 | 8 | 1664 | 0 | 1 | 0 | 0 | 0 | 0
152j | office | 178 | 11 |  |  | 288 | 6 | 6 | AHU-5 | 8 | 2304 | 4.6354 | 1 | 4.6354 | 2 | 4.6354 | 2
152k | office | 160 | 10 |  |  | 368 | 8 | 8 | AHU-5 | 8 | 2944 | 3.2609 | 1 | 3.2609 | 1 | 3.2609 | 1
202 | classroom | 608 | 40 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 6.0079 | 1 | 6.0079 | 2 | 6.0079 | 2
203 | classroom | 481 | 32 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 4.753 | 1 | 4.753 | 2 | 4.753 | 2
207 | classroom | 310 | 20 |  |  | 1081 | 24 | 20 | Univent | 8 | 8648 | 2.1508 | 1 | 2.1508 | 1 | 2.1508 | 1
208 | classroom | 331 | 22 |  |  | 621 | 14 | 14 | Univent | 8 | 4968 | 3.9976 | 1 | 3.9976 | 1 | 3.9976 | 1
211 | classroom | 300 | 20 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 2.9644 | 1 | 2.9644 | 1 | 2.9644 | 1
212 | classroom | 405 | 27 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 4.002 | 1 | 4.002 | 2 | 4.002 | 2
213 | classroom | 345 | 23 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.4091 | 1 | 3.4091 | 1 | 3.4091 | 1
215 | office | 385 | 25 |  |  | 675 | 15 | 15 | AHU-1 | 8 | 5400 | 4.2778 | 1 | 4.2778 | 2 | 4.2778 | 2
218 | classroom | 720 | 48 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 7.1146 | 1 | 7.1146 | 2 | 7.1146 | 2
220 | classroom | 360 | 24 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.5573 | 1 | 3.5573 | 1 | 3.5573 | 1
221 | classroom | 310 | 20 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.0632 | 1 | 3.0632 | 1 | 3.0632 | 1
225 | classroom | 413 | 27 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 4.081 | 1 | 4.081 | 2 | 4.081 | 2
226 | classroom | 328 | 21 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.2411 | 1 | 3.2411 | 1 | 3.2411 | 1
228 | classroom | 345 | 23 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.4091 | 1 | 3.4091 | 1 | 3.4091 | 1
229 | classroom | 300 | 20 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 2.9644 | 1 | 2.9644 | 1 | 2.9644 | 1
230 | classroom | 345 | 23 |  |  | 1196 | 27 | 23 | Univent | 8 | 9568 | 2.1635 | 1 | 2.1635 | 1 | 2.1635 | 1
236 | classroom | 83 | 5 |  |  | 494 | 11 | 5 | AHU-5 | 8 | 3952 | 1.2601 | 1 | 1.2601 | 1 | 1.2601 | 1
236A | STORAGE | 150 | 10 |  |  | 171 | 3 | 3 | AHU-5 | 8 | 1368 | 6.5789 | 1 | 6.5789 | 2 | 6.5789 | 2
236B | OFFICE | 0 | 0 |  |  | 171 | 3 | 0 | AHU-5 | 8 | 1368 | 0 | 1 | 0 | 0 | 0 | 0
237B | STORAGE | 37 | 2 |  |  | 165 | 3 | 2 | AHU-5 | 8 | 1320 | 1.6818 | 1 | 1.6818 | 1 | 1.6818 | 1
237C | OFFICE | 63 | 4 |  |  | 165 | 3 | 3 | AHU-5 | 8 | 1320 | 2.8636 | 1 | 2.8636 | 1 | 2.8636 | 1
238 | classroom | 442 | 29 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 4.3676 | 1 | 4.3676 | 2 | 4.3676 | 2
239 | classroom | 284 | 18 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 2.8063 | 1 | 2.8063 | 1 | 2.8063 | 1
302 | classroom | 430 | 28 |  |  | 1081 | 24 | 24 | Univent | 8 | 8648 | 2.9833 | 1 | 2.9833 | 1 | 2.9833 | 1
306 | classroom | 289 | 19 |  |  | 526 | 11 | 11 | Univent | 8 | 4208 | 4.1207 | 1 | 4.1207 | 2 | 4.1207 | 2
307 | classroom | 299 | 19 |  |  | 621 | 14 | 14 | Univent | 8 | 4968 | 3.6111 | 1 | 3.6111 | 1 | 3.6111 | 1
308 | classroom | 285 | 19 |  |  | 504 | 11 | 11 | Univent | 8 | 4032 | 4.2411 | 1 | 4.2411 | 2 | 4.2411 | 2
310 | classroom | 320 | 21 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.1621 | 1 | 3.1621 | 1 | 3.1621 | 1
311 | classroom | 365 | 24 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.6067 | 1 | 3.6067 | 1 | 3.6067 | 1
312 | classroom | 325 | 21 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.2115 | 1 | 3.2115 | 1 | 3.2115 | 1
313 | office | 453 | 30 |  |  | 675 | 15 | 15 | AHU-1 | 8 | 5400 | 5.0333 | 1 | 5.0333 | 2 | 5.0333 | 2
316 | classroom | 345 | 23 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.4091 | 1 | 3.4091 | 1 | 3.4091 | 1
317 | classroom | 380 | 25 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.7549 | 1 | 3.7549 | 1 | 3.7549 | 1
319 | classroom | 307 | 20 |  |  | 989 | 22 | 20 | Unit Ventilator | 8 | 7912 | 2.3281 | 1 | 2.3281 | 1 | 2.3281 | 1
319A | storage | 233 | 15 |  |  | 367 | 8 | 8 | Unit Ventilator | 8 | 2936 | 4.7616 | 1 | 4.7616 | 2 | 4.7616 | 2
323 | classroom | 336 | 22 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.3202 | 1 | 3.3202 | 1 | 3.3202 | 1
324 | classroom | 384 | 25 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.7945 | 1 | 3.7945 | 1 | 3.7945 | 1
326 | classroom | 423 | 28 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 4.1798 | 1 | 4.1798 | 2 | 4.1798 | 2
327 | classroom | 453 | 30 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 4.4763 | 1 | 4.4763 | 2 | 4.4763 | 2
328 | classroom | 425 | 28 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 4.1996 | 1 | 4.1996 | 2 | 4.1996 | 2
335 | STUDIO | 389 | 25 |  |  | 798 | 18 | 18 | AHU-8 | 8 | 6384 | 3.656 | 1 | 3.656 | 1 | 3.656 | 1
336 | classroom | 366 | 24 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.6166 | 1 | 3.6166 | 1 | 3.6166 | 1
337 | classroom | 375 | 25 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.7055 | 1 | 3.7055 | 1 | 3.7055 | 1
- | BOYS LOCKER ROOM | 80 | 5 |  |  | 143 | 3 | 3 | AHU-5 | 8 | 1144 | 4.1958 | 1 | 4.1958 | 2 | 4.1958 | 2
- | FRONT IMC LIBRARY | 118 | 7 |  |  | 171 | 3 | 3 | AHU-5 | 8 | 1368 | 5.1754 | 1 | 5.1754 | 2 | 5.1754 | 2
- | GIRLS LOCKER ROOM | 84 | 5 |  |  | 143 | 3 | 3 | AHU-5 | 8 | 1144 | 4.4056 | 1 | 4.4056 | 2 | 4.4056 | 2
- | GYM OFFICE | 41 | 2 |  |  | 225 | 5 | 2 | AHU-5 | 8 | 1800 | 1.3667 | 1 | 1.3667 | 1 | 1.3667 | 1
- | LIBRARY | 892 | 59 |  |  | 3276 | 74 | 59 | AHU-8 | 8 | 26208 | 2.0421 | 1.062 | 2.1688 | 1 | 2.1688 | 1
- | Mail Room | 159 | 10 |  |  | 200 | 4 | 4 | AHU-5 | 8 | 1600 | 5.9625 | 1 | 5.9625 | 2 | 5.9625 | 2
- | Main Office | 618 | 41 |  |  | 924 | 21 | 21 | AHU-5 | 8 | 7392 | 5.0162 | 1 | 5.0162 | 2 | 5.0162 | 2
- | Principal Office | 208 | 13 |  |  | 324 | 7 | 7 | AHU-5 | 8 | 2592 | 4.8148 | 1 | 4.8148 | 2 | 4.8148 | 2
- | Staff Locker Room |  | 0 |  |  | 70 | 1 | 0 | AHU-1 | 8 | 560 | 0 | 1 | 0 | 0 | 0 | 0
- | Storage Office | 38 | 2 |  |  | 100 | 2 | 2 | AHU-5 | 8 | 800 | 2.85 | 1 | 2.85 | 1 | 2.85 | 1
- | Cafeteria | 4650 | 310 |  |  | 6020 | 136 | 136 | AHU-2 | 8 | 48160 | 5.7932 | 1.062 | 6.1526 | 2 | 6.1526 | 2
- | Gym | 3322 | 221 |  |  | 5904 | 134 | 134 | ahu-6 | 8 | 47232 | 4.22 | 1.062 | 4.4818 | 2 | 4.4818 | 2
- | Auditorium | 3405 | 227 |  |  | 2983 | 67 | 67 | AHU-7 | 8 | 23864 | 8.561 | 1.062 | 9.0921 | 2 | 9.0921 | 2
Sheet Last Modified: | 2021-04-27
School: | Stephen Decatur Elementary School
Stephen Decatur Elementary School Annex
Stephen Decatur Elementary School White Building
Vendor: | EMCOR | Devine Brothers | Devine Retest | Emcor Retest 2-15
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Decatur Main Building
K-1 | classroom | 283 | 18 |  |  | 1450 | 32 | 18 | Unit Ventilator | 8 | 11600 | 1.4638 | 1 | 1.4638 | 1 | 1.4638 | 1
K-2 | classroom | 375 | 25 |  |  | 1450 | 32 | 25 | Unit Ventilator | 8 | 11600 | 1.9397 | 1 | 1.9397 | 1 | 1.9397 | 1
100 | classroom | 329 | 21 |  |  | 897 | 20 | 20 | Unit Ventilator | 8 | 7176 | 2.7508 | 1 | 2.7508 | 1 | 2.7508 | 1
101 | classroom | 271 | 18 |  |  | 805 | 18 | 18 | Unit Ventilator | 8 | 6440 | 2.5248 | 1 | 2.5248 | 1 | 2.5248 | 1
102 | classroom | 228 | 15 |  |  | 897 | 20 | 15 | Unit Ventilator | 8 | 7176 | 1.9064 | 1 | 1.9064 | 1 | 1.9064 | 1
103 | classroom | 253 | 16 |  |  | 805 | 18 | 16 | Unit Ventilator | 8 | 6440 | 2.3571 | 1 | 2.3571 | 1 | 2.3571 | 1
104 | classroom | 240 | 16 |  |  | 897 | 20 | 16 | Unit Ventilator | 8 | 7176 | 2.0067 | 1 | 2.0067 | 1 | 2.0067 | 1
105 | classroom | 321 | 21 |  |  | 805 | 18 | 18 | Unit Ventilator | 8 | 6440 | 2.9907 | 1 | 2.9907 | 1 | 2.9907 | 1
106 | Nurse's Office |  | 0 | Yes | 20 | 357 | 8 | 8 | N/A | 8 | 2856 | 0 | 1 | 0 | 0 | 20 | 3
107 | classroom | 326 | 21 |  |  | 805 | 18 | 18 | Unit Ventilator | 8 | 6440 | 3.0373 | 1 | 3.0373 | 1 | 3.0373 | 1
108 | classroom | 322 | 21 |  |  | 897 | 20 | 20 | Unit Ventilator | 8 | 7176 | 2.6923 | 1 | 2.6923 | 1 | 2.6923 | 1
109 | classroom | 326 | 21 |  |  | 851 | 19 | 19 | Unit Ventilator | 8 | 6808 | 2.8731 | 1 | 2.8731 | 1 | 2.8731 | 1
110 | classroom | 301 | 20 |  |  | 702 | 15 | 15 | Unit Ventilator | 8 | 5616 | 3.2158 | 1 | 3.2158 | 1 | 3.2158 | 1
200 | Classroom | 352 | 23 |  |  | 805 | 18 | 18 | Unit Ventilator | 8 | 6440 | 3.2795 | 1 | 3.2795 | 1 | 3.2795 | 1
201 | Classroom |  | 0 | Yes | 20 | 805 | 18 | 18 |  | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 805 | 18 | 18 |  | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom | 234 | 15 |  |  | 854 | 19 | 15 | Unit Ventilator | 8 | 6832 | 2.055 | 1 | 2.055 | 1 | 2.055 | 1
204 | Classroom |  | 0 | Yes | 20 | 805 | 18 | 18 |  | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 805 | 18 | 18 |  | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 | Yes | 20 | 805 | 18 | 18 |  | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 301 | 20 |  |  | 805 | 18 | 18 | Unit Ventilator | 8 | 6440 | 2.8043 | 1 | 2.8043 | 1 | 2.8043 | 1
210 | Classroom | 242 | 16 |  |  | 805 | 18 | 16 | Unit Ventilator | 8 | 6440 | 2.2547 | 1 | 2.2547 | 1 | 2.2547 | 1
212 | Classroom |  | 0 | Yes | 20 | 805 | 18 | 18 |  | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
214 | Classroom | 247 | 16 |  |  | 391 | 8 | 8 | Unit Ventilator | 8 | 3128 | 4.7379 | 1 | 4.7379 | 2 | 4.7379 | 2
216/218 | Classroom | 599 | 39 |  |  | 1702 | 38 | 38 | Unit Ventilator | 8 | 13616 | 2.6395 | 1 | 2.6395 | 1 | 2.6395 | 1
217 | Classroom | 283 | 18 |  |  | 1352 | 30 | 18 | Unit Ventilator | 8 | 10816 | 1.5699 | 1 | 1.5699 | 1 | 1.5699 | 1
219 | Classroom | 274 | 18 |  |  | 798 | 18 | 18 | Unit Ventilator | 8 | 6384 | 2.5752 | 1 | 2.5752 | 1 | 2.5752 | 1
220 | Classroom | 184 | 12 | Yes | 20 | 865 | 19 | 19 | Unit Ventilator | 8 | 6920 | 1.5954 | 1 | 1.5954 | 1 | 21.5954 | 3
300 | Classroom |  | 0 | Yes | 20 | 910 | 20 | 20 |  | 8 | 7280 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 | Yes | 20 | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom |  | 0 | Yes | 20 | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom |  | 0 | Yes | 20 | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom |  | 0 | Yes | 20 | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom |  | 0 | Yes | 20 | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom |  | 0 | Yes | 20 | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom |  | 0 | Yes | 20 | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
310 | Classroom |  | 0 | Yes | 20 | 910 | 20 | 20 |  | 8 | 7280 | 0 | 1 | 0 | 0 | 20 | 3
312 | Classroom | 277 | 18 |  |  | 391 | 8 | 8 | Unit Ventilator | 8 | 3128 | 5.3133 | 1 | 5.3133 | 2 | 5.3133 | 2
314 | Classroom | 241 | 16 |  |  | 397 | 9 | 9 | Unit Ventilator | 8 | 3176 | 4.5529 | 1 | 4.5529 | 2 | 4.5529 | 2
316 | Classroom | 238 | 15 |  |  | 851 | 19 | 15 | Unit Ventilator | 8 | 6808 | 2.0975 | 1 | 2.0975 | 1 | 2.0975 | 1
317 | Classroom |  | 0 | Yes | 20 | 910 | 20 | 20 |  | 8 | 7280 | 0 | 1 | 0 | 0 | 20 | 3
318 | Classroom |  | 0 | Yes | 20 | 850 | 19 | 19 |  | 8 | 6800 | 0 | 1 | 0 | 0 | 20 | 3
319 | Classroom |  | 0 | Yes | 20 | 910 | 20 | 20 |  | 8 | 7280 | 0 | 1 | 0 | 0 | 20 | 3
320 | Classroom |  | 0 | Yes | 20 | 910 | 20 | 20 |  | 8 | 7280 | 0 | 1 | 0 | 0 | 20 | 3
- | AP | N/A | 0 |  |  | 126 | 2 | 0 | N/A | 8 | 1008 | #VALUE! | 1 | #VALUE! | #VALUE! | #VALUE!
- | Auditorium | 675 | 45 |  |  | 2800 | 63 | 45 | AHU | 8 | 22400 | 1.808 | 1.062 | 1.9202 | 1 | 1.9202 | 1
- | Basement | 0 | 0 |  |  | 456 | 10 | 0 | N/A | 8 | 3648 | 0 | 1 | 0 | 0 | 0 | 0
B-1 | - |  | 0 | Yes | 20 | 731 | 16 | 16 | Unit Ventilator | 8 | 5848 | 0 | 1 | 0 | 0 | 20 | 3
B-2 | Counselors | 356 | 23 |  |  | 875 | 19 | 19 | Unit Ventilator | 8 | 7000 | 3.0514 | 1 | 3.0514 | 1 | 3.0514 | 1
- | Dean | N/A | 0 |  |  | 126 | 2 | 0 | N/A | 8 | 1008 | #VALUE! | 1 | #VALUE! | #VALUE! | #VALUE!
- | ESOL | 275 | 18 |  |  | 750 | 17 | 17 | Unit Ventilator | 8 | 6000 | 2.75 | 1 | 2.75 | 1 | 2.75 | 1
- | GYM | 1543 | 102 |  |  | 4108 | 93 | 93 | AHU | 8 | 32864 | 2.8171 | 1.062 | 2.9918 | 1 | 2.9918 | 1
- | IMC | 301 | 20 |  |  | 1404 | 31 | 20 | RTU | 8 | 11232 | 1.6079 | 1 | 1.6079 | 1 | 1.6079 | 1
- | Main Office | 360 | 24 |  |  | 999 | 22 | 22 | Unit Ventilator | 8 | 7992 | 2.7027 | 1 | 2.7027 | 1 | 2.7027 | 1
- | Cafeteria | 0 | 0 | Yes | 20 | 6161 | 140 | 140 | Unit Ventilator | 8 | 49288 | 0 | 1.062 | 0 | 0 | 20 | 3
Decatur Annex
A-1 | classroom | 335 | 22 |  |  | 875 | 19 | 19 | Unit Ventilator | 8 | 7000 | 2.8714 | 1 | 2.8714 | 1 | 2.8714 | 1
A-2 | classroom | 294 | 19 |  |  | 899 | 20 | 19 | Unit Ventilator | 8 | 7192 | 2.4527 | 1 | 2.4527 | 1 | 2.4527 | 1
A-3 | classroom | 329 | 21 |  |  | 874 | 19 | 19 | Unit Ventilator | 8 | 6992 | 2.8232 | 1 | 2.8232 | 1 | 2.8232 | 1
A-4 | classroom | 285 | 19 |  |  | 852 | 19 | 19 | Unit Ventilator | 8 | 6816 | 2.5088 | 1 | 2.5088 | 1 | 2.5088 | 1
A-5 | classroom | 326 | 21 |  |  | 861 | 19 | 19 | Unit Ventilator | 8 | 6888 | 2.8397 | 1 | 2.8397 | 1 | 2.8397 | 1
A-6 | classroom | 322 | 21 |  |  | 789 | 17 | 17 | Unit Ventilator | 8 | 6312 | 3.0608 | 1 | 3.0608 | 1 | 3.0608 | 1
A-7 | classroom | 317 | 21 |  |  | 899 | 20 | 20 | Unit Ventilator | 8 | 7192 | 2.6446 | 1 | 2.6446 | 1 | 2.6446 | 1
A-8 | classroom | 332 | 22 |  |  | 832 | 18 | 18 | Unit Ventilator | 8 | 6656 | 2.9928 | 1 | 2.9928 | 1 | 2.9928 | 1
A-9 | classroom | 288 | 19 |  |  | 879 | 19 | 19 | Unit Ventilator | 8 | 7032 | 2.4573 | 1 | 2.4573 | 1 | 2.4573 | 1
A-10 | classroom | 281 | 18 |  |  | 888 | 20 | 18 | Unit Ventilator | 8 | 7104 | 2.3733 | 1 | 2.3733 | 1 | 2.3733 | 1
Decatur White Building
1 | classroom | 315 | 21 |  |  | 875 | 19 | 19 | Unit Ventilator | 8 | 7000 | 2.7 | 1 | 2.7 | 1 | 2.7 | 1
2 | classroom | 241 | 16 |  |  | 888 | 20 | 16 | Unit Ventilator | 8 | 7104 | 2.0355 | 1 | 2.0355 | 1 | 2.0355 | 1
3 | classroom | 340 | 22 |  |  | 878 | 19 | 19 | Unit Ventilator | 8 | 7024 | 2.9043 | 1 | 2.9043 | 1 | 2.9043 | 1
4 | classroom | 284 | 18 |  |  | 845 | 19 | 18 | Unit Ventilator | 8 | 6760 | 2.5207 | 1 | 2.5207 | 1 | 2.5207 | 1
Sheet Last Modified: | 2021-04-29
School: | William Dick Elementary School
Vendor: | EMCOR | Exhaust Report | Retest Report
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 355 | 23 |  |  | 963 | 21 | 21 | Unit Ventilator | 8 | 7704 | 2.7648 | 1 | 2.7648 | 1 | 2.7648 | 1
102 | Classroom | 319 | 21 |  |  | 963 | 21 | 21 | Unit Ventilator | 8 | 7704 | 2.4844 | 1 | 2.4844 | 1 | 2.4844 | 1
103 | Nurses Office |  | 0 | Yes | 20 | 825 | 18 | 18 |  | 8 | 6600 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom | 481 | 32 |  |  | 1036 | 23 | 23 | Unit Ventilator | 8 | 8288 | 3.4821 | 1 | 3.4821 | 1 | 3.4821 | 1
105 | Office | 0 | 0 | Yes | 20 | 4046 | 91 | 91 | Unit Ventilator | 8 | 32368 | 0 | 1.062 | 0 | 0 | 20 | 3
105-A | Principal's Office |  | 0 | Yes | 20 | 280 | 6 | 6 |  | 8 | 2240 | 0 | 1 | 0 | 0 | 20 | 3
106 | Small room |  | 0 | Yes | 20 | 303 | 6 | 6 |  | 8 | 2424 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom | 328 | 21 |  |  | 1050 | 23 | 21 | Unit Ventilator | 8 | 8400 | 2.3429 | 1 | 2.3429 | 1 | 2.3429 | 1
108 | Classroom | 167 | 11 |  |  | 1055 | 23 | 11 | Unit Ventilator | 8 | 8440 | 1.1872 | 1 | 1.1872 | 1 | 1.1872 | 1
109 | Classroom | 237 | 15 | Yes | 20 | 1048 | 23 | 23 | Unit Ventilator | 8 | 8384 | 1.6961 | 1 | 1.6961 | 1 | 21.6961 | 3
111 | Classroom | 176 | 11 | Yes | 20 | 1272 | 28 | 28 | Unit Ventilator | 8 | 10176 | 1.0377 | 1 | 1.0377 | 1 | 21.0377 | 3
112 | Classroom | 345 | 23 |  |  | 1275 | 28 | 23 | Unit Ventilator | 8 | 10200 | 2.0294 | 1 | 2.0294 | 1 | 2.0294 | 1
200 | Room |  | 0 | Yes | 20 | 133 | 3 | 3 |  | 8 | 1064 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 356 | 23 |  |  | 747 | 16 | 16 | Unit Ventilator | 8 | 5976 | 3.5743 | 1 | 3.5743 | 1 | 3.5743 | 1
202 | Classroom | 286 | 19 |  |  | 1051 | 23 | 19 | Unit Ventilator | 8 | 8408 | 2.0409 | 1 | 2.0409 | 1 | 2.0409 | 1
203 | Classroom | 158 | 10 | Yes | 20 | 1052 | 23 | 23 | Unit Ventilator | 8 | 8416 | 1.1264 | 1 | 1.1264 | 1 | 21.1264 | 3
204 | Classroom | 142 | 9 | Yes | 20 | 1035 | 23 | 23 | Unit Ventilator | 8 | 8280 | 1.029 | 1 | 1.029 | 1 | 21.029 | 3
205 | Classroom | 191 | 12 | Yes | 20 | 1057 | 24 | 24 | Unit Ventilator | 8 | 8456 | 1.3553 | 1 | 1.3553 | 1 | 21.3553 | 3
207 | Classroom | 199 | 13 | Yes | 20 | 1009 | 22 | 22 | Unit Ventilator | 8 | 8072 | 1.4792 | 1 | 1.4792 | 1 | 21.4792 | 3
208 | Classroom | 207 | 13 | Yes | 20 | 1049 | 23 | 23 | Unit Ventilator | 8 | 8392 | 1.48 | 1 | 1.48 | 1 | 21.48 | 3
209 | Classroom | 317 | 21 |  |  | 1055 | 23 | 21 | Unit Ventilator | 8 | 8440 | 2.2536 | 1 | 2.2536 | 1 | 2.2536 | 1
211 | Classroom | 286 | 19 |  |  | 1049 | 23 | 19 | Unit Ventilator | 8 | 8392 | 2.0448 | 1 | 2.0448 | 1 | 2.0448 | 1
212 | Classroom | 344 | 22 |  |  | 1048 | 23 | 22 | Unit Ventilator | 8 | 8384 | 2.4618 | 1 | 2.4618 | 1 | 2.4618 | 1
213 | Classroom | 235 | 15 | Yes | 20 | 1049 | 23 | 23 | Unit Ventilator | 8 | 8392 | 1.6802 | 1 | 1.6802 | 1 | 21.6802 | 3
214 | Classroom | 119 | 7 | Yes | 20 | 1029 | 23 | 23 | Unit Ventilator | 8 | 8232 | 0.86735 | 1 | 0.86735 | 0 | 20.8673 | 3
300 | Counselor's Office |  | 0 | Yes | 20 | 164 | 3 | 3 |  | 8 | 1312 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 136 | 9 | Yes | 20 | 741 | 16 | 16 | Unit Ventilator | 8 | 5928 | 1.3765 | 1 | 1.3765 | 1 | 21.3765 | 3
302 | Classroom | 398 | 26 |  |  | 1053 | 23 | 23 | Unit Ventilator | 8 | 8424 | 2.8348 | 1 | 2.8348 | 1 | 2.8348 | 1
303 | Library | 241 | 16 | Yes | 20 | 1032 | 23 | 23 | Unit Ventilator | 8 | 8256 | 1.7515 | 1 | 1.7515 | 1 | 21.7515 | 3
304 | Classroom | 169 | 11 | Yes | 20 | 1049 | 23 | 23 | Unit Ventilator | 8 | 8392 | 1.2083 | 1 | 1.2083 | 1 | 21.2083 | 3
305 | Classroom | 330 | 22 |  |  | 1213 | 27 | 22 | Unit Ventilator | 8 | 9704 | 2.0404 | 1 | 2.0404 | 1 | 2.0404 | 1
307 | Classroom | 101 | 6 | Yes | 20 | 1057 | 24 | 24 | Unit Ventilator | 8 | 8456 | 0.71665 | 1 | 0.71665 | 0 | 20.7167 | 3
308 | Classroom | 133 | 8 | Yes | 20 | 1028 | 23 | 23 | Unit Ventilator | 8 | 8224 | 0.97033 | 1 | 0.97033 | 0 | 20.9703 | 3
309 | Classroom | 369 | 24 |  |  | 1048 | 23 | 23 | Unit Ventilator | 8 | 8384 | 2.6407 | 1 | 2.6407 | 1 | 2.6407 | 1
311 | Classroom | 406 | 27 |  |  | 1050 | 23 | 23 | Unit Ventilator | 8 | 8400 | 2.9 | 1 | 2.9 | 1 | 2.9 | 1
312 | Classroom | 281 | 18 |  |  | 1046 | 23 | 18 | Unit Ventilator | 8 | 8368 | 2.0148 | 1 | 2.0148 | 1 | 2.0148 | 1
313 | Classroom | 53 | 3 | Yes | 20 | 1046 | 23 | 23 | Unit Ventilator | 8 | 8368 | 0.38002 | 1 | 0.38002 | 0 | 20.38 | 3
314 | Classroom | 0 | 0 | Yes | 20 | 1047 | 23 | 23 | Unit Ventilator | 8 | 8376 | 0 | 1 | 0 | 0 | 20 | 3
- | Gymnasium | 248 | 16 |  |  | 739 | 16 | 16 | Unit Ventilator | 8 | 5912 | 2.5169 | 1 | 2.5169 | 1 | 2.5169 | 1
- | Auditorium |  | 0 |  |  | 4436 | 100 | 0 | AHU | 8 | 35488 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Building Engineer's Office |  | 0 | Yes | 20 | 482 | 10 | 10 |  | 8 | 3856 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-03
School: | Hamilton Disston Elementary-Middle School
Vendor: | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Mechanical Rm. |  | 0 |  |  | 570 | 12 | 0 | House Fan | 8 | 4560 | 0 | 1 | 0 | 0 | 0 | 0
B1 | Cafeteria | 1021 | 68 |  |  | 1680 | 38 | 38 | House Fan | 8 | 13440 | 4.558 | 1 | 4.558 | 2 | 4.558 | 2
B2 | Food Service | 1059 | 70 |  |  | 816 | 18 | 18 | House Fan | 8 | 6528 | 9.7335 | 1 | 9.7335 | 2 | 9.7335 | 2
B3 | Gym | 0 | 0 | Yes | 20 | 3840 | 87 | 87 | House Fan | 8 | 30720 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Gym Office | 0 | 0 |  |  | 288 | 6 | 0 | House Fan | 8 | 2304 | 0 | 1 | 0 | 0 | 0 | 0
B4 | Classroom | 0 | 0 | Yes | 20 | 1008 | 22 | 22 | House Fan | 8 | 8064 | 0 | 1 | 0 | 0 | 20 | 3
B5 | Classroom | 1005 | 67 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 8.724 | 1 | 8.724 | 2 | 8.724 | 2
B6 | Classroom | 768 | 51 |  |  | 984 | 22 | 22 | House Fan | 8 | 7872 | 5.8537 | 1 | 5.8537 | 2 | 5.8537 | 2
017B | Basement Girls Bathroom | 464 | 30 |  |  | 504 | 11 | 11 | House Fan | 8 | 4032 | 6.9048 | 1 | 6.9048 | 2 | 6.9048 | 2
011B | Basement Boys Bathroom | 271 | 18 |  |  | 528 | 12 | 12 | House Fan | 8 | 4224 | 3.8494 | 1 | 3.8494 | 1 | 3.8494 | 1
101 | Classroom | 545 | 36 |  |  | 816 | 18 | 18 | House Fan | 8 | 6528 | 5.0092 | 1 | 5.0092 | 2 | 5.0092 | 2
102 | Classroom | 764 | 50 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 7.9583 | 1 | 7.9583 | 2 | 7.9583 | 2
103 | Classroom | 821 | 54 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 7.1267 | 1 | 7.1267 | 2 | 7.1267 | 2
104 | Classroom | 593 | 39 |  |  | 766 | 17 | 17 | House Fan | 8 | 6128 | 5.8061 | 1 | 5.8061 | 2 | 5.8061 | 2
104A | Office | 0 | 0 | Yes | 20 | 168 | 3 | 3 | House Fan | 8 | 1344 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 3956 | 263 |  |  | 2784 | 63 | 63 | House Fan | 8 | 22272 | 10.6573 | 1.062 | 11.3185 | 3 | 11.3185 | 3
105 | Classroom | 635 | 42 |  |  | 766 | 17 | 17 | House Fan | 8 | 6128 | 6.2174 | 1 | 6.2174 | 2 | 6.2174 | 2
106 | Classroom | 403 | 26 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 3.4983 | 1 | 3.4983 | 1 | 3.4983 | 1
107 | Classroom | 574 | 38 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 5.9792 | 1 | 5.9792 | 2 | 5.9792 | 2
108 | Classroom | 593 | 39 |  |  | 816 | 18 | 18 | House Fan | 8 | 6528 | 5.4504 | 1 | 5.4504 | 2 | 5.4504 | 2
- | Nurses Office | 0 | 0 | Yes | 20 | 200 | 4 | 4 | House Fan | 8 | 1600 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 447 | 29 |  |  | 816 | 18 | 18 | House Fan | 8 | 6528 | 4.1085 | 1 | 4.1085 | 2 | 4.1085 | 2
202 | Classroom | 668 | 44 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 6.9583 | 1 | 6.9583 | 2 | 6.9583 | 2
203 | Classroom | 601 | 40 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 5.217 | 1 | 5.217 | 2 | 5.217 | 2
203A | Climate Office | 0 | 0 | Yes | 20 | 280 | 6 | 6 | House Fan | 8 | 2240 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom | 548 | 36 |  |  | 816 | 18 | 18 | House Fan | 8 | 6528 | 5.0368 | 1 | 5.0368 | 2 | 5.0368 | 2
204A | AP Office | 0 | 0 |  |  | 180 | 4 | 0 | House Fan | 8 | 1440 | 0 | 1 | 0 | 0 | 0 | 0
205 | Classroom | 301 | 20 |  |  | 816 | 18 | 18 | House Fan | 8 | 6528 | 2.7665 | 1 | 2.7665 | 1 | 2.7665 | 1
- | Counselor's Office | 0 | 0 | Yes | 20 | 260 | 5 | 5 | House Fan | 8 | 2080 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom | 570 | 38 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 4.9479 | 1 | 4.9479 | 2 | 4.9479 | 2
207 | Classroom | 421 | 28 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 4.3854 | 1 | 4.3854 | 2 | 4.3854 | 2
208 | Classroom | 281 | 18 |  |  | 816 | 18 | 18 | House Fan | 8 | 6528 | 2.5827 | 1 | 2.5827 | 1 | 2.5827 | 1
- | Helping Hands Office | 0 | 0 | Yes | 20 | 120 | 2 | 2 | House Fan | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
301A | Office | 0 | 0 |  |  | 280 | 6 | 0 | House Fan | 8 | 2240 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom | 365 | 24 |  |  | 816 | 18 | 18 | House Fan | 8 | 6528 | 3.3548 | 1 | 3.3548 | 1 | 3.3548 | 1
302 | Classroom | 563 | 37 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 5.8646 | 1 | 5.8646 | 2 | 5.8646 | 2
303 | Classroom | 442 | 29 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 3.8368 | 1 | 3.8368 | 1 | 3.8368 | 1
304 | Classroom | 657 | 43 |  |  | 816 | 18 | 18 | House Fan | 8 | 6528 | 6.0386 | 1 | 6.0386 | 2 | 6.0386 | 2
305 | Classroom | 53 | 3 | Yes | 20 | 870 | 19 | 19 | House Fan | 8 | 6960 | 0.4569 | 1 | 0.4569 | 0 | 20.4569 | 3
306 | Classroom | 186 | 12 |  |  | 864 | 19 | 12 | House Fan | 8 | 6912 | 1.6146 | 1 | 1.6146 | 1 | 1.6146 | 1
307 | Classroom | 56 | 3 | Yes | 20 | 957 | 21 | 21 | House Fan | 8 | 7656 | 0.43887 | 1 | 0.43887 | 0 | 20.4389 | 3
308 | Classroom | 489 | 32 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 4.2448 | 1 | 4.2448 | 2 | 4.2448 | 2
309 | Classroom | 127 | 8 | Yes | 20 | 900 | 20 | 20 | House Fan | 8 | 7200 | 1.0583 | 1 | 1.0583 | 1 | 21.0583 | 3
310 | Classroom | 96 | 6 | Yes | 20 | 816 | 18 | 18 | House Fan | 8 | 6528 | 0.88235 | 1 | 0.88235 | 0 | 20.8824 | 3
311 | Classroom | 611 | 40 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 5.3038 | 1 | 5.3038 | 2 | 5.3038 | 2
312 | Classroom | 424 | 28 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 4.4167 | 1 | 4.4167 | 2 | 4.4167 | 2
313 | Classroom | 411 | 27 |  |  | 816 | 18 | 18 | House Fan | 8 | 6528 | 3.7776 | 1 | 3.7776 | 1 | 3.7776 | 1
313A | Office | 0 | 0 |  |  | 816 | 18 | 0 | House Fan | 8 | 6528 | 0 | 1 | 0 | 0 | 0 | 0
- | Library | 747 | 49 |  |  | 2156 | 49 | 49 | RTU-1 | 8 | 17248 | 2.5986 | 1 | 2.5986 | 1 | 2.5986 | 1
- | Office | 155 | 10 |  |  | 312 | 7 | 7 | RTU-1 | 8 | 2496 | 3.726 | 1 | 3.726 | 1 | 3.726 | 1
- | Office | 55 | 3 |  |  | 312 | 7 | 3 | RTU-1 | 8 | 2496 | 1.3221 | 1 | 1.3221 | 1 | 1.3221 | 1
- | Main Office | 0 | 0 | Yes | 20 | 308 | 7 | 7 | RTU-2 | 8 | 2464 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office | 0 | 0 |  |  | 160 | 3 | 0 | RTU-2 | 8 | 1280 | 0 | 1 | 0 | 0 | 0 | 0
- | Faculty Lounge | 0 | 0 |  |  | 312 | 7 | 0 | RTU-2 | 8 | 2496 | 0 | 1 | 0 | 0 | 0 | 0
- | Modular Classroom | 0 | 0 |  |  | 720 | 16 | 0 | AHU | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-19
School: | Murrell Dobbins Vocational High School
Vendor: | Capital | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
016 B-5 | Classroom | 1130 | 75 |  |  | 2511 | 57 | 57 |  | 8 | 20088 | 3.3751 | 1.062 | 3.5845 | 1 | 3.5845 | 1
016 B-6 | Classroom | 536 | 35 |  |  | 2511 | 57 | 35 |  | 8 | 20088 | 1.601 | 1.062 | 1.7003 | 1 | 1.7003 | 1
016 B-7 | Classroom | 718 | 47 |  |  | 2424 | 55 | 47 |  | 8 | 19392 | 2.2215 | 1 | 2.2215 | 1 | 2.2215 | 1
016 B-8 | Classroom | 494 | 32 |  |  | 2543 | 57 | 32 |  | 8 | 20344 | 1.4569 | 1.062 | 1.5473 | 1 | 1.5473 | 1
120 | Classroom | 249 | 16 |  |  | 597 | 13 | 13 |  | 8 | 4776 | 3.1281 | 1 | 3.1281 | 1 | 3.1281 | 1
122-A | Classroom | 325 | 21 |  |  | 1226 | 27 | 21 |  | 8 | 9808 | 1.9882 | 1 | 1.9882 | 1 | 1.9882 | 1
122-B | Classroom | 391 | 26 |  |  | 1226 | 27 | 26 |  | 8 | 9808 | 2.3919 | 1 | 2.3919 | 1 | 2.3919 | 1
123-A | Classroom | 287 | 19 |  |  | 1445 | 32 | 19 |  | 8 | 11560 | 1.4896 | 1 | 1.4896 | 1 | 1.4896 | 1
123-B | Classroom | 0 | 0 |  |  | 1445 | 32 | 0 |  | 8 | 11560 | 0 | 1 | 0 | 0 | 0 | 0
123C | Classroom | 0 | 0 |  |  | 136 | 3 | 0 |  | 8 | 1088 | 0 | 1 | 0 | 0 | 0 | 0
123J | Classroom | 428 | 28 |  |  | 322 | 7 | 7 |  | 8 | 2576 | 9.9689 | 1 | 9.9689 | 2 | 9.9689 | 2
130 | Classroom | 284 | 18 |  |  | 1017 | 23 | 18 |  | 8 | 8136 | 2.0944 | 1 | 2.0944 | 1 | 2.0944 | 1
131-A | Classroom | 0 | 0 |  |  | 2226 | 50 | 0 |  | 8 | 17808 | 0 | 1 | 0 | 0 | 0 | 0
131-B | Classroom | 458 | 30 |  |  | 2226 | 50 | 30 |  | 8 | 17808 | 1.5431 | 1 | 1.5431 | 1 | 1.5431 | 1
131-C | Classroom | 0 | 0 |  |  | 2226 | 50 | 0 |  | 8 | 17808 | 0 | 1 | 0 | 0 | 0 | 0
131-D | Classroom | 232 | 15 |  |  | 2226 | 50 | 15 |  | 8 | 17808 | 0.78167 | 1 | 0.78167 | 0 | 0.78167 | 0
134 | Classroom | 0 | 0 |  |  | 596 | 13 | 0 |  | 8 | 4768 | 0 | 1 | 0 | 0 | 0 | 0
201 | Library/IMC | 397 | 26 |  |  | 3115 | 70 | 26 |  | 8 | 24920 | 0.95586 | 1.062 | 1.0152 | 1 | 1.0152 | 1
220-A | Classroom | 760 | 50 |  |  | 435 | 9 | 9 |  | 8 | 3480 | 13.1034 | 1 | 13.1034 | 3 | 13.1034 | 3
220-B | Classroom | 452 | 30 |  |  | 210 | 4 | 4 |  | 8 | 1680 | 16.1429 | 1 | 16.1429 | 3 | 16.1429 | 3
220-C | Classroom | 398 | 26 |  |  | 210 | 4 | 4 |  | 8 | 1680 | 14.2143 | 1 | 14.2143 | 3 | 14.2143 | 3
220-D | Classroom | 411 | 27 |  |  | 308 | 7 | 7 |  | 8 | 2464 | 10.0081 | 1 | 10.0081 | 3 | 10.0081 | 3
222 | Classroom | 299 | 19 |  |  | 1228 | 27 | 19 |  | 8 | 9824 | 1.8261 | 1 | 1.8261 | 1 | 1.8261 | 1
223 | Classroom | 393 | 26 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 4.0938 | 1 | 4.0938 | 2 | 4.0938 | 2
225 | Classroom | 394 | 26 |  |  | 735 | 16 | 16 |  | 8 | 5880 | 4.0204 | 1 | 4.0204 | 2 | 4.0204 | 2
227-A | Classroom | 505 | 33 |  |  | 871 | 19 | 19 |  | 8 | 6968 | 4.3485 | 1 | 4.3485 | 2 | 4.3485 | 2
227-B | Classroom | 335 | 22 |  |  | 871 | 19 | 19 |  | 8 | 6968 | 2.8846 | 1 | 2.8846 | 1 | 2.8846 | 1
231-A | Classroom | 0 | 0 |  |  | 1125 | 25 | 0 |  | 8 | 9000 | 0 | 1 | 0 | 0 | 0 | 0
231-B | Classroom | 141 | 9 |  |  | 1125 | 25 | 9 |  | 8 | 9000 | 0.94 | 1 | 0.94 | 0 | 0.94 | 0
233-A | Classroom | 371 | 24 |  |  | 2122 | 48 | 24 |  | 8 | 16976 | 1.3113 | 1 | 1.3113 | 1 | 1.3113 | 1
233-B | Classroom | 347 | 23 |  |  | 2122 | 48 | 23 |  | 8 | 16976 | 1.2264 | 1 | 1.2264 | 1 | 1.2264 | 1
233-C | Classroom | 319 | 21 |  |  | 2122 | 48 | 21 |  | 8 | 16976 | 1.1275 | 1 | 1.1275 | 1 | 1.1275 | 1
234 | Classroom | 0 | 0 |  |  | 771 | 17 | 0 |  | 8 | 6168 | 0 | 1 | 0 | 0 | 0 | 0
236 | Classroom | 381 | 25 |  |  | 1030 | 23 | 23 |  | 8 | 8240 | 2.7743 | 1 | 2.7743 | 1 | 2.7743 | 1
236,234,233, | Classrooms | 6741 | 449 |  |  | 792 | 18 | 18 |  | 8 | 6336 | 63.8352 | 1 | 63.8352 | 5 | 63.8352 | 5
232, & 231
- | 2nd E/Center Corr | 375 | 25 |  |  | 2310 | 52 | 25 |  | 8 | 18480 | 1.2175 | 1 | 1.2175 | 1 | 1.2175 | 1
- | 2nd East Corr | 312 | 20 |  |  | 2310 | 52 | 20 |  | 8 | 18480 | 1.013 | 1 | 1.013 | 1 | 1.013 | 1
- | 2nd W/Center Corr | 292 | 19 |  |  | 2310 | 52 | 19 |  | 8 | 18480 | 0.94805 | 1 | 0.94805 | 0 | 0.94805 | 0
- | 2nd West Corr | 0 | 0 |  |  | 2310 | 52 | 0 |  | 8 | 18480 | 0 | 1 | 0 | 0 | 0 | 0
300 | Classroom | 451 | 30 |  |  | 975 | 22 | 22 |  | 8 | 7800 | 3.4692 | 1 | 3.4692 | 1 | 3.4692 | 1
305,330,331, | Classrooms | 7434 | 495 |  |  | 792 | 18 | 18 |  | 8 | 6336 | 70.3977 | 1 | 70.3977 | 5 | 70.3977 | 5
332, & 332A
315-A | Classroom | 300 | 20 |  |  | 1008 | 22 | 20 |  | 8 | 8064 | 2.2321 | 1 | 2.2321 | 1 | 2.2321 | 1
315-B | Classroom | 390 | 26 |  |  | 1008 | 22 | 22 |  | 8 | 8064 | 2.9018 | 1 | 2.9018 | 1 | 2.9018 | 1
317 | Classroom | 346 | 23 |  |  | 832 | 18 | 18 |  | 8 | 6656 | 3.119 | 1 | 3.119 | 1 | 3.119 | 1
321,323,322, | Classrooms | 5053 | 336 |  |  | 792 | 18 | 18 |  | 8 | 6336 | 47.8504 | 1 | 47.8504 | 4 | 47.8504 | 4
322A, &322B
322-A | Classroom | 0 | 0 |  |  | 3737 | 84 | 0 |  | 8 | 29896 | 0 | 1.062 | 0 | 0 | 0 | 0
322-B | Classroom | 171 | 11 |  |  | 3737 | 84 | 11 |  | 8 | 29896 | 0.34319 | 1.062 | 0.36448 | 0 | 0.36448 | 0
322-C | Classroom | 0 | 0 |  |  | 3737 | 84 | 0 |  | 8 | 29896 | 0 | 1.062 | 0 | 0 | 0 | 0
322-D | Classroom | 680 | 45 |  |  | 3737 | 84 | 45 |  | 8 | 29896 | 1.3647 | 1.062 | 1.4494 | 1 | 1.4494 | 1
322-E | Classroom | 756 | 50 |  |  | 3737 | 84 | 50 |  | 8 | 29896 | 1.5173 | 1.062 | 1.6114 | 1 | 1.6114 | 1
322B | Classroom | 89 | 5 |  |  | 187 | 4 | 4 |  | 8 | 1496 | 3.5695 | 1 | 3.5695 | 1 | 3.5695 | 1
323-A | Classroom | 682 | 45 |  |  | 1035 | 23 | 23 |  | 8 | 8280 | 4.942 | 1 | 4.942 | 2 | 4.942 | 2
331-A | Classroom | 538 | 35 |  |  | 1852 | 42 | 35 |  | 8 | 14816 | 2.1787 | 1 | 2.1787 | 1 | 2.1787 | 1
331-B | Classroom | 221 | 14 |  |  | 1852 | 42 | 14 |  | 8 | 14816 | 0.89498 | 1 | 0.89498 | 0 | 0.89498 | 0
332-A | Classroom | 352 | 23 |  |  | 963 | 21 | 21 |  | 8 | 7704 | 2.7414 | 1 | 2.7414 | 1 | 2.7414 | 1
332-B | Classroom | 371 | 24 |  |  | 963 | 21 | 21 |  | 8 | 7704 | 2.8894 | 1 | 2.8894 | 1 | 2.8894 | 1
333-A | Classroom | 478 | 31 |  |  | 1862 | 42 | 31 |  | 8 | 14896 | 1.9253 | 1 | 1.9253 | 1 | 1.9253 | 1
333-B | Classroom | 0 | 0 |  |  | 1862 | 42 | 0 |  | 8 | 14896 | 0 | 1 | 0 | 0 | 0 | 0
333-C | Classroom | 543 | 36 |  |  | 1862 | 42 | 36 |  | 8 | 14896 | 2.1872 | 1 | 2.1872 | 1 | 2.1872 | 1
335 | Classroom | 393 | 26 |  |  | 250 | 5 | 5 |  | 8 | 2000 | 11.79 | 1 | 11.79 | 3 | 11.79 | 3
- | 3rd E/Center Corr | 296 | 19 |  |  | 2310 | 52 | 19 |  | 8 | 18480 | 0.96104 | 1 | 0.96104 | 0 | 0.96104 | 0
- | 3rd East Corr | 310 | 20 |  |  | 2310 | 52 | 20 |  | 8 | 18480 | 1.0065 | 1 | 1.0065 | 1 | 1.0065 | 1
- | 3rd W/Center Corr | 437 | 29 |  |  | 2310 | 52 | 29 |  | 8 | 18480 | 1.4188 | 1 | 1.4188 | 1 | 1.4188 | 1
- | 3rd West Corr | 0 | 0 |  |  | 2310 | 52 | 0 |  | 8 | 18480 | 0 | 1 | 0 | 0 | 0 | 0
400-A | Classroom | 356 | 23 |  |  | 2045 | 46 | 23 |  | 8 | 16360 | 1.3056 | 1 | 1.3056 | 1 | 1.3056 | 1
400-B | Classroom | 333 | 22 |  |  | 2045 | 46 | 22 |  | 8 | 16360 | 1.2213 | 1 | 1.2213 | 1 | 1.2213 | 1
400, 402, 403, & 403A | Classroom | 21 | 1 |  |  | 2310 | 52 | 1 |  | 8 | 18480 | 0.068182 | 1 | 0.068182 | 0 | 0.068182 | 0
401-A | Classroom | 0 | 0 |  |  | 1080 | 24 | 0 |  | 8 | 8640 | 0 | 1 | 0 | 0 | 0 | 0
401-B | Classroom | 168 | 11 |  |  | 1080 | 24 | 11 |  | 8 | 8640 | 1.1667 | 1 | 1.1667 | 1 | 1.1667 | 1
401A | Storage | 264 | 17 |  |  | 222 | 5 | 5 |  | 8 | 1776 | 8.9189 | 1 | 8.9189 | 2 | 8.9189 | 2
402-A | Classroom | 0 | 0 |  |  | 951 | 21 | 0 |  | 8 | 7608 | 0 | 1 | 0 | 0 | 0 | 0
402-B | Classroom | 194 | 12 |  |  | 951 | 21 | 12 |  | 8 | 7608 | 1.53 | 1 | 1.53 | 1 | 1.53 | 1
403-A | Classroom | 257 | 17 |  |  | 2279 | 51 | 17 |  | 8 | 18232 | 0.84577 | 1 | 0.84577 | 0 | 0.84577 | 0
403-B | Classroom | 81 | 5 |  |  | 2279 | 51 | 5 |  | 8 | 18232 | 0.26656 | 1 | 0.26656 | 0 | 0.26656 | 0
403-C | Classroom | 190 | 12 |  |  | 2279 | 51 | 12 |  | 8 | 18232 | 0.62527 | 1 | 0.62527 | 0 | 0.62527 | 0
403-D | Classroom | 226 | 15 |  |  | 2279 | 51 | 15 |  | 8 | 18232 | 0.74375 | 1 | 0.74375 | 0 | 0.74375 | 0
410-A | Classroom | 273 | 18 |  |  | 1058 | 24 | 18 |  | 8 | 8464 | 1.9353 | 1 | 1.9353 | 1 | 1.9353 | 1
410-B | Classroom | 273 | 18 |  |  | 1058 | 24 | 18 |  | 8 | 8464 | 1.9353 | 1 | 1.9353 | 1 | 1.9353 | 1
411-A | Classroom | 0 | 0 |  |  | 1067 | 24 | 0 |  | 8 | 8536 | 0 | 1 | 0 | 0 | 0 | 0
411-B | Classroom | 0 | 0 |  |  | 1067 | 24 | 0 |  | 8 | 8536 | 0 | 1 | 0 | 0 | 0 | 0
412 | Classroom | 422 | 28 |  |  | 1066 | 24 | 24 |  | 8 | 8528 | 2.969 | 1 | 2.969 | 1 | 2.969 | 1
413 | Classroom | 0 | 0 |  |  | 952 | 21 | 0 |  | 8 | 7616 | 0 | 1 | 0 | 0 | 0 | 0
414 | Classroom | 364 | 24 |  |  | 921 | 20 | 20 |  | 8 | 7368 | 2.9642 | 1 | 2.9642 | 1 | 2.9642 | 1
420-A | Classroom | 766 | 51 |  |  | 745 | 16 | 16 |  | 8 | 5960 | 7.7114 | 1 | 7.7114 | 2 | 7.7114 | 2
420-B | Classroom | 326 | 21 |  |  | 745 | 16 | 16 |  | 8 | 5960 | 3.2819 | 1 | 3.2819 | 1 | 3.2819 | 1
422-A | Classroom | 514 | 34 |  |  | 2438 | 55 | 34 |  | 8 | 19504 | 1.5812 | 1 | 1.5812 | 1 | 1.5812 | 1
422-B | Classroom | 417 | 27 |  |  | 2438 | 55 | 27 |  | 8 | 19504 | 1.2828 | 1 | 1.2828 | 1 | 1.2828 | 1
422-C | Classroom | 407 | 27 |  |  | 2438 | 55 | 27 |  | 8 | 19504 | 1.2521 | 1 | 1.2521 | 1 | 1.2521 | 1
423 & 420 | Classrooms | 0 | 0 |  |  | 576 | 13 | 0 |  | 8 | 4608 | 0 | 1 | 0 | 0 | 0 | 0
423-A | Classroom | 0 | 0 |  |  | 1372 | 31 | 0 |  | 8 | 10976 | 0 | 1 | 0 | 0 | 0 | 0
423-B | Classroom | 0 | 0 |  |  | 1372 | 31 | 0 |  | 8 | 10976 | 0 | 1 | 0 | 0 | 0 | 0
430-A | Classroom | 300 | 20 |  |  | 1431 | 32 | 20 |  | 8 | 11448 | 1.5723 | 1 | 1.5723 | 1 | 1.5723 | 1
430-B | Classroom | 319 | 21 |  |  | 1431 | 32 | 21 |  | 8 | 11448 | 1.6719 | 1 | 1.6719 | 1 | 1.6719 | 1
430,431, & 432 | Classrooms | 8038 | 535 |  |  | 792 | 18 | 18 |  | 8 | 6336 | 76.1174 | 1 | 76.1174 | 5 | 76.1174 | 5
431-A | Classroom | 673 | 44 |  |  | 2491 | 56 | 44 |  | 8 | 19928 | 2.0263 | 1 | 2.0263 | 1 | 2.0263 | 1
431-B | Classroom | 221 | 14 |  |  | 2491 | 56 | 14 |  | 8 | 19928 | 0.6654 | 1 | 0.6654 | 0 | 0.6654 | 0
431-C | Classroom | 533 | 35 |  |  | 2491 | 56 | 35 |  | 8 | 19928 | 1.6048 | 1 | 1.6048 | 1 | 1.6048 | 1
431-D | Classroom | 347 | 23 |  |  | 2491 | 56 | 23 |  | 8 | 19928 | 1.0448 | 1 | 1.0448 | 1 | 1.0448 | 1
431-E | Classroom | 325 | 21 |  |  | 2491 | 56 | 21 |  | 8 | 19928 | 0.97852 | 1 | 0.97852 | 0 | 0.97852 | 0
- | 4th E/Center Corr | 0 | 0 |  |  | 2310 | 52 | 0 |  | 8 | 18480 | 0 | 1 | 0 | 0 | 0 | 0
- | 4th East Corr | 0 | 0 |  |  | 2310 | 52 | 0 |  | 8 | 18480 | 0 | 1 | 0 | 0 | 0 | 0
- | 4th W/ Center Corr | 199 | 13 |  |  | 2310 | 52 | 13 |  | 8 | 18480 | 0.6461 | 1 | 0.6461 | 0 | 0.6461 | 0
- | 4th West Corr | 267 | 17 |  |  | 2310 | 52 | 17 |  | 8 | 18480 | 0.86688 | 1 | 0.86688 | 0 | 0.86688 | 0
500 | Classroom | 299 | 19 |  |  | 1160 | 26 | 19 |  | 8 | 9280 | 1.9332 | 1 | 1.9332 | 1 | 1.9332 | 1
500-A | Classroom | 301 | 20 |  |  | 270 | 6 | 6 |  | 8 | 2160 | 8.3611 | 1 | 8.3611 | 2 | 8.3611 | 2
501 | Classroom | 388 | 25 |  |  | 956 | 21 | 21 |  | 8 | 7648 | 3.0439 | 1 | 3.0439 | 1 | 3.0439 | 1
502-A | Classroom | 206 | 13 |  |  | 956 | 21 | 13 |  | 8 | 7648 | 1.6161 | 1 | 1.6161 | 1 | 1.6161 | 1
502-B | Classroom | 258 | 17 |  |  | 956 | 21 | 17 |  | 8 | 7648 | 2.0241 | 1 | 2.0241 | 1 | 2.0241 | 1
503-A | Classroom | 208 | 13 |  |  | 956 | 21 | 13 |  | 8 | 7648 | 1.6318 | 1 | 1.6318 | 1 | 1.6318 | 1
503-B | Classroom | 144 | 9 |  |  | 956 | 21 | 9 |  | 8 | 7648 | 1.1297 | 1 | 1.1297 | 1 | 1.1297 | 1
504-A | Classroom | 224 | 14 |  |  | 957 | 21 | 14 |  | 8 | 7656 | 1.7555 | 1 | 1.7555 | 1 | 1.7555 | 1
504-B | Classroom | 108 | 7 |  |  | 957 | 21 | 7 |  | 8 | 7656 | 0.84639 | 1 | 0.84639 | 0 | 0.84639 | 0
505 | Classroom | 0 | 0 |  |  | 863 | 19 | 0 |  | 8 | 6904 | 0 | 1 | 0 | 0 | 0 | 0
506-A | Classroom | 0 | 0 |  |  | 833 | 18 | 0 |  | 8 | 6664 | 0 | 1 | 0 | 0 | 0 | 0
506-B | Classroom | 280 | 18 |  |  | 833 | 18 | 18 |  | 8 | 6664 | 2.521 | 1 | 2.521 | 1 | 2.521 | 1
507-A | Classroom | 221 | 14 |  |  | 1032 | 23 | 14 |  | 8 | 8256 | 1.6061 | 1 | 1.6061 | 1 | 1.6061 | 1
507-B | Classroom | 467 | 31 |  |  | 1032 | 23 | 23 |  | 8 | 8256 | 3.3939 | 1 | 3.3939 | 1 | 3.3939 | 1
510-A | Classroom | 313 | 20 |  |  | 1085 | 24 | 20 |  | 8 | 8680 | 2.1636 | 1 | 2.1636 | 1 | 2.1636 | 1
510-B | Classroom | 323 | 21 |  |  | 1085 | 24 | 21 |  | 8 | 8680 | 2.2327 | 1 | 2.2327 | 1 | 2.2327 | 1
511 | Classroom | 293 | 19 |  |  | 954 | 21 | 19 |  | 8 | 7632 | 2.3035 | 1 | 2.3035 | 1 | 2.3035 | 1
512 | Classroom | 344 | 22 |  |  | 712 | 16 | 16 |  | 8 | 5696 | 3.6236 | 1 | 3.6236 | 1 | 3.6236 | 1
513 | Classroom | 294 | 19 |  |  | 712 | 16 | 16 |  | 8 | 5696 | 3.0969 | 1 | 3.0969 | 1 | 3.0969 | 1
514 | Classroom | 311 | 20 |  |  | 665 | 15 | 15 |  | 8 | 5320 | 3.5075 | 1 | 3.5075 | 1 | 3.5075 | 1
515 | Classroom | 358 | 23 |  |  | 818 | 18 | 18 |  | 8 | 6544 | 3.2824 | 1 | 3.2824 | 1 | 3.2824 | 1
516 | Classroom | 394 | 26 |  |  | 819 | 18 | 18 |  | 8 | 6552 | 3.6081 | 1 | 3.6081 | 1 | 3.6081 | 1
520-B | Classroom | 0 | 0 |  |  | 221 | 5 | 0 |  | 8 | 1768 | 0 | 1 | 0 | 0 | 0 | 0
522 | Classroom | 0 | 0 |  |  | 316 | 7 | 0 |  | 8 | 2528 | 0 | 1 | 0 | 0 | 0 | 0
523 | Classroom | 0 | 0 |  |  | 795 | 18 | 0 |  | 8 | 6360 | 0 | 1 | 0 | 0 | 0 | 0
524 | Classroom | 0 | 0 |  |  | 800 | 18 | 0 |  | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
525 | Classroom | 378 | 25 |  |  | 851 | 19 | 19 |  | 8 | 6808 | 3.3314 | 1 | 3.3314 | 1 | 3.3314 | 1
526-A | Classroom | 57 | 3 |  |  | 961 | 21 | 3 |  | 8 | 7688 | 0.44485 | 1 | 0.44485 | 0 | 0.44485 | 0
526-B | Classroom | 377 | 25 |  |  | 961 | 21 | 21 |  | 8 | 7688 | 2.9422 | 1 | 2.9422 | 1 | 2.9422 | 1
530 | Classroom | 293 | 19 |  |  | 821 | 18 | 18 |  | 8 | 6568 | 2.6766 | 1 | 2.6766 | 1 | 2.6766 | 1
531-A | Classroom | 576 | 38 |  |  | 724 | 16 | 16 |  | 8 | 5792 | 5.9669 | 1 | 5.9669 | 2 | 5.9669 | 2
531-B | Classroom | 81 | 5 |  |  | 724 | 16 | 5 |  | 8 | 5792 | 0.83909 | 1 | 0.83909 | 0 | 0.83909 | 0
532 | Classroom | 292 | 19 |  |  | 879 | 19 | 19 |  | 8 | 7032 | 2.4915 | 1 | 2.4915 | 1 | 2.4915 | 1
533-A | Classroom | 225 | 15 |  |  | 800 | 18 | 15 |  | 8 | 6400 | 2.1094 | 1 | 2.1094 | 1 | 2.1094 | 1
533-B | Classroom | 0 | 0 |  |  | 800 | 18 | 0 |  | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
534-A | Classroom | 438 | 29 |  |  | 1036 | 23 | 23 |  | 8 | 8288 | 3.1708 | 1 | 3.1708 | 1 | 3.1708 | 1
534-B | Classroom | 0 | 0 |  |  | 1036 | 23 | 0 |  | 8 | 8288 | 0 | 1 | 0 | 0 | 0 | 0
535 | Classroom | 0 | 0 |  |  | 1006 | 22 | 0 |  | 8 | 8048 | 0 | 1 | 0 | 0 | 0 | 0
- | 5th E.Cent Corr | 201 | 13 |  |  | 2310 | 52 | 13 |  | 8 | 18480 | 0.6526 | 1 | 0.6526 | 0 | 0.6526 | 0
- | 5th East Corr. | 0 | 0 |  |  | 2310 | 52 | 0 |  | 8 | 18480 | 0 | 1 | 0 | 0 | 0 | 0
- | 5th W.Cent Corr | 276 | 18 |  |  | 2310 | 52 | 18 |  | 8 | 18480 | 0.8961 | 1 | 0.8961 | 0 | 0.8961 | 0
601-A | Classroom | 138 | 9 |  |  | 1553 | 35 | 9 |  | 8 | 12424 | 0.66645 | 1 | 0.66645 | 0 | 0.66645 | 0
601-B | Classroom | 0 | 0 |  |  | 1553 | 35 | 0 |  | 8 | 12424 | 0 | 1 | 0 | 0 | 0 | 0
601-C | Classroom | 0 | 0 |  |  | 1553 | 35 | 0 |  | 8 | 12424 | 0 | 1 | 0 | 0 | 0 | 0
603-A | Classroom | 0 | 0 |  |  | 962 | 21 | 0 |  | 8 | 7696 | 0 | 1 | 0 | 0 | 0 | 0
603-B | Classroom | 229 | 15 |  |  | 962 | 21 | 15 |  | 8 | 7696 | 1.7853 | 1 | 1.7853 | 1 | 1.7853 | 1
604 | Classroom | 0 | 0 |  |  | 400 | 9 | 0 |  | 8 | 3200 | 0 | 1 | 0 | 0 | 0 | 0
610 | Classroom | 331 | 22 |  |  | 738 | 16 | 16 |  | 8 | 5904 | 3.3638 | 1 | 3.3638 | 1 | 3.3638 | 1
611 | Classroom | 460 | 30 |  |  | 712 | 16 | 16 |  | 8 | 5696 | 4.8455 | 1 | 4.8455 | 2 | 4.8455 | 2
612 | Classroom | 298 | 19 |  |  | 704 | 16 | 16 |  | 8 | 5632 | 3.1747 | 1 | 3.1747 | 1 | 3.1747 | 1
613 | Classroom | 257 | 17 |  |  | 711 | 16 | 16 |  | 8 | 5688 | 2.711 | 1 | 2.711 | 1 | 2.711 | 1
614 | Classroom | 270 | 18 |  |  | 800 | 18 | 18 |  | 8 | 6400 | 2.5312 | 1 | 2.5312 | 1 | 2.5312 | 1
615 | Classroom | 382 | 25 |  |  | 814 | 18 | 18 |  | 8 | 6512 | 3.5197 | 1 | 3.5197 | 1 | 3.5197 | 1
622-A | Classroom | 0 | 0 |  |  | 801 | 18 | 0 |  | 8 | 6408 | 0 | 1 | 0 | 0 | 0 | 0
622-B | Classroom | 242 | 16 |  |  | 801 | 18 | 16 |  | 8 | 6408 | 2.2659 | 1 | 2.2659 | 1 | 2.2659 | 1
623 | Classroom | 682 | 45 |  |  | 679 | 15 | 15 |  | 8 | 5432 | 7.5331 | 1 | 7.5331 | 2 | 7.5331 | 2
624 | Classroom | 267 | 17 |  |  | 820 | 18 | 17 |  | 8 | 6560 | 2.4421 | 1 | 2.4421 | 1 | 2.4421 | 1
625 | Classroom | 174 | 11 |  |  | 680 | 15 | 11 |  | 8 | 5440 | 1.9191 | 1 | 1.9191 | 1 | 1.9191 | 1
627 | Classroom | 815 | 54 |  |  | 794 | 18 | 18 |  | 8 | 6352 | 7.6984 | 1 | 7.6984 | 2 | 7.6984 | 2
- | 6th Center Corr. | 0 | 0 |  |  | 792 | 18 | 0 |  | 8 | 6336 | 0 | 1 | 0 | 0 | 0 | 0
- | 6th East Corr. | 466 | 31 |  |  | 792 | 18 | 18 |  | 8 | 6336 | 4.4129 | 1 | 4.4129 | 2 | 4.4129 | 2
- | Admin | 4788 | 319 |  |  | 786 | 17 | 17 |  | 8 | 6288 | 45.687 | 1 | 45.687 | 4 | 45.687 | 4
- | Auditorium | 0 | 0 | Yes | 20 | 10676 | 242 | 242 |  | 8 | 85408 | 0 | 1.4912 | 0 | 0 | 20 | 3
- | Boy's Gym | 0 | 0 |  |  | 5940 | 135 | 0 |  | 8 | 47520 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Girl's Gym | 0 | 0 |  |  | 5696 | 129 | 0 |  | 8 | 45568 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Lunch Rm | 0 | 0 |  |  | 4563 | 103 | 0 |  | 8 | 36504 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Lunch Rm | 0 | 0 |  |  | 4563 | 103 | 0 |  | 8 | 36504 | 0 | 1.062 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27
School: | James Dobson Middle School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom |  | 0 | Yes | 20 | 108 | 2 | 2 | House Fan | 8 | 864 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom |  | 0 | Yes | 20 | 968 | 22 | 22 | House Fan | 8 | 7744 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
106 | Office |  | 0 | Yes | 20 | 638 | 14 | 14 | House Fan | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom |  | 0 | Yes | 20 | 120 | 2 | 2 | House Fan | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
205 | Office |  | 0 | Yes | 20 | 342 | 7 | 7 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
210 | Office |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
303/304 | Classroom |  | 0 | Yes | 20 | 1320 | 30 | 30 | House Fan | 8 | 10560 | 0 | 1 | 0 | 0 | 20 | 3
306/307 | Classroom |  | 0 | Yes | 20 | 1320 | 30 | 30 | House Fan | 8 | 10560 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
313 | Classroom |  | 0 | Yes | 20 | 858 | 19 | 19 | House Fan | 8 | 6864 | 0 | 1 | 0 | 0 | 20 | 3
- | Councelors office |  | 0 | Yes | 20 | 243 | 5 | 5 |  | 8 | 1944 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 510 | 11 | 11 | House Fan | 8 | 4080 | 0 | 1 | 0 | 0 | 20 | 3
- | Principals office |  | 0 | Yes | 20 | 236 | 5 | 5 | House Fan | 8 | 1888 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 | Yes | 20 | 3080 | 70 | 70 |  | 8 | 24640 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Cafeteria large |  | 0 |  |  | 944 | 21 | 0 |  | 8 | 7552 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium |  | 0 |  |  | 3124 | 71 | 0 |  | 8 | 24992 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Library |  | 0 | Yes | 20 | 1320 | 30 | 30 |  | 8 | 10560 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses office |  | 0 | Yes | 20 | 264 | 6 | 6 |  | 8 | 2112 | 0 | 1 | 0 | 0 | 20 | 3
| Cafeteria small |  | 0 |  |  | 919 | 20 |  |  | 8 | 7352 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21
School: | Tanner Duckrey Elementary School
Exhaust Report
Vendor: | Chadwick | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B19 | Art Room | 358 | 23 |  |  | 1032 | 23 | 23 | AHU | 8 | 8256 | 2.6017 | 1 | 2.6017 | 1 | 2.6017 | 1
B21 | Classroom | 0 | 0 | Yes | 20 | 1029 | 23 | 23 | Unit Ventilator | 8 | 8232 | 0 | 1 | 0 | 0 | 20 | 3
111 | Classroom | 718 | 47 |  |  | 1115 | 25 | 25 | Unit Ventilator | 8 | 8920 | 4.8296 | 1 | 4.8296 | 2 | 4.8296 | 2
114 | Classroom | 284 | 18 |  |  | 941 | 21 | 18 | Unit Ventilator | 8 | 7528 | 2.2635 | 1 | 2.2635 | 1 | 2.2635 | 1
117 | Classroom | 608 | 40 |  |  | 940 | 21 | 21 | Unit Ventilator | 8 | 7520 | 4.8511 | 1 | 4.8511 | 2 | 4.8511 | 2
118 | Classroom | 271 | 18 |  |  | 691 | 15 | 15 | Unit Ventilator | 8 | 5528 | 2.9414 | 1 | 2.9414 | 1 | 2.9414 | 1
119 | - | 276 | 18 | Yes | 20 | 1237 | 28 | 28 | Unit Ventilator | 8 | 9896 | 1.6734 | 1 | 1.6734 | 1 | 21.6734 | 3
120 | Classroom | 638 | 42 |  |  | 1024 | 23 | 23 | Unit Ventilator | 8 | 8192 | 4.6729 | 1 | 4.6729 | 2 | 4.6729 | 2
121A | Classroom | 367 | 24 |  |  | 715 | 16 | 16 | Unit Ventilator | 8 | 5720 | 3.8497 | 1 | 3.8497 | 1 | 3.8497 | 1
121B | Classroom | 315 | 21 |  |  | 795 | 18 | 18 | Unit Ventilator | 8 | 6360 | 2.9717 | 1 | 2.9717 | 1 | 2.9717 | 1
122 | Classroom | 413 | 27 |  |  | 1027 | 23 | 23 | Unit Ventilator | 8 | 8216 | 3.0161 | 1 | 3.0161 | 1 | 3.0161 | 1
124 | Classroom | 686 | 45 |  |  | 921 | 20 | 20 | Unit Ventilator | 8 | 7368 | 5.5863 | 1 | 5.5863 | 2 | 5.5863 | 2
126 | Classroom | 310 | 20 |  |  | 927 | 21 | 20 | Unit Ventilator | 8 | 7416 | 2.5081 | 1 | 2.5081 | 1 | 2.5081 | 1
128 | Classroom | 409 | 27 |  |  | 1012 | 23 | 23 | Unit Ventilator | 8 | 8096 | 3.0311 | 1 | 3.0311 | 1 | 3.0311 | 1
130 | Classroom | 429 | 28 |  |  | 1101 | 25 | 25 | Unit Ventilator | 8 | 8808 | 2.9223 | 1 | 2.9223 | 1 | 2.9223 | 1
200 | - | 639 | 42 |  |  | 1036 | 23 | 23 | Unit Ventilator | 8 | 8288 | 4.626 | 1 | 4.626 | 2 | 4.626 | 2
201 | - | 803 | 53 |  |  | 1050 | 23 | 23 | Unit Ventilator | 8 | 8400 | 5.7357 | 1 | 5.7357 | 2 | 5.7357 | 2
204 | - | 564 | 37 |  |  | 952 | 21 | 21 | Unit Ventilator | 8 | 7616 | 4.4433 | 1 | 4.4433 | 2 | 4.4433 | 2
207 | - | 0 | 0 | Yes | 20 | 951 | 21 | 21 | Unit Ventilator | 8 | 7608 | 0 | 1 | 0 | 0 | 20 | 3
208 | - | 786 | 52 |  |  | 917 | 20 | 20 | Unit Ventilator | 8 | 7336 | 6.4286 | 1 | 6.4286 | 2 | 6.4286 | 2
209 | - | 648 | 43 |  |  | 951 | 21 | 21 | Unit Ventilator | 8 | 7608 | 5.1104 | 1 | 5.1104 | 2 | 5.1104 | 2
210 | - | 638 | 42 |  |  | 953 | 21 | 21 | Unit Ventilator | 8 | 7624 | 5.021 | 1 | 5.021 | 2 | 5.021 | 2
211 | - | 617 | 41 |  |  | 919 | 20 | 20 | Unit Ventilator | 8 | 7352 | 5.0354 | 1 | 5.0354 | 2 | 5.0354 | 2
212 | - |  | 0 | Yes | 20 | 1023 | 23 | 23 |  | 8 | 8184 | 0 | 1 | 0 | 0 | 20 | 3
213 | - | 830 | 55 |  |  | 1088 | 24 | 24 | Unit Ventilator | 8 | 8704 | 5.7215 | 1 | 5.7215 | 2 | 5.7215 | 2
214 | - | 819 | 54 |  |  | 1037 | 23 | 23 | Unit Ventilator | 8 | 8296 | 5.9233 | 1 | 5.9233 | 2 | 5.9233 | 2
215 | - | 475 | 31 |  |  | 1035 | 23 | 23 | Unit Ventilator | 8 | 8280 | 3.442 | 1 | 3.442 | 1 | 3.442 | 1
216 | - | 838 | 55 |  |  | 1039 | 23 | 23 | Unit Ventilator | 8 | 8312 | 6.0491 | 1 | 6.0491 | 2 | 6.0491 | 2
216A | - | 384 | 25 |  |  | 926 | 21 | 21 | Unit Ventilator | 8 | 7408 | 3.1102 | 1 | 3.1102 | 1 | 3.1102 | 1
217 | - | 546 | 36 |  |  | 922 | 20 | 20 | Unit Ventilator | 8 | 7376 | 4.4414 | 1 | 4.4414 | 2 | 4.4414 | 2
218 | - | 307 | 20 |  |  | 922 | 20 | 20 | Unit Ventilator | 8 | 7376 | 2.4973 | 1 | 2.4973 | 1 | 2.4973 | 1
219 | - | 348 | 23 |  |  | 925 | 21 | 21 | Unit Ventilator | 8 | 7400 | 2.8216 | 1 | 2.8216 | 1 | 2.8216 | 1
220 | - | 459 | 30 |  |  | 411 | 9 | 9 | Unit Ventilator | 8 | 3288 | 8.3759 | 1 | 8.3759 | 2 | 8.3759 | 2
220A | - | 290 | 19 |  |  | 330 | 7 | 7 | Unit Ventilator | 8 | 2640 | 6.5909 | 1 | 6.5909 | 2 | 6.5909 | 2
221 | - | 556 | 37 |  |  | 873 | 19 | 19 | Unit Ventilator | 8 | 6984 | 4.7766 | 1 | 4.7766 | 2 | 4.7766 | 2
221A | - | 432 | 28 |  |  | 194 | 4 | 4 | Unit Ventilator | 8 | 1552 | 16.701 | 1 | 16.701 | 3 | 16.701 | 3
222 | - | 334 | 22 |  |  | 875 | 19 | 19 | Unit Ventilator | 8 | 7000 | 2.8629 | 1 | 2.8629 | 1 | 2.8629 | 1
223 | - | 538 | 35 |  |  | 872 | 19 | 19 | Unit Ventilator | 8 | 6976 | 4.6273 | 1 | 4.6273 | 2 | 4.6273 | 2
- | Auditorium/Cafe | 264 | 17 | Yes | 20 | 5376 | 122 | 122 | AHU | 8 | 43008 | 0.3683 | 1.062 | 0.39115 | 0 | 20.3912 | 3
- | Faculty Lounge | 1156 | 77 |  |  | 513 | 11 | 11 | Unit Ventilator | 8 | 4104 | 16.9006 | 1 | 16.9006 | 3 | 16.9006 | 3
- | Kitchen | 203 | 13 |  |  | 2070 | 47 | 13 | AHU | 8 | 16560 | 0.73551 | 1 | 0.73551 | 0 | 0.73551 | 0
- | Library | 336 | 22 |  |  | 1914 | 43 | 22 | AHU | 8 | 15312 | 1.3166 | 1 | 1.3166 | 1 | 1.3166 | 1
- | Main Office | 1063 | 70 |  |  | 903 | 20 | 20 | Unit Ventilator | 8 | 7224 | 8.8289 | 1 | 8.8289 | 2 | 8.8289 | 2
- | Nurse | 334 | 22 |  |  | 387 | 8 | 8 | Unit Ventilator | 8 | 3096 | 6.4729 | 1 | 6.4729 | 2 | 6.4729 | 2
- | Science Room | 1464 | 97 |  |  | 799 | 18 | 18 | Unit Ventilator | 8 | 6392 | 13.7422 | 1 | 13.7422 | 3 | 13.7422 | 3
- | Gym | 215 | 14 |  |  | 4808 | 109 | 14 | AHU | 8 | 38464 | 0.33538 | 1.062 | 0.35618 | 0 | 0.35618 | 0
Sheet Last Modified: | 2021-04-06
School: | Paul L. Dunbar High School
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
102 | Clasroom | 0 | 0 | Yes | 20 | 730 | 16 | 16 | House Fan | 8 | 5840 | 0 | 1 | 0 | 0 | 20 | 3
103 | office | 0 | 0 | Yes | 20 | 682 | 15 | 15 | House Fan | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
103 | bathroom | 0 | 0 |  |  | 49 | 1 | 0 | House Fan | 8 | 392 | 0 | 1 | 0 | 0 | 0 | 0
104 | Lunchroom | 0 | 0 | Yes | 20 | 1413 | 32 | 32 | House Fan | 8 | 11304 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom | 0 | 0 | Yes | 20 | 730 | 16 | 16 | House Fan | 8 | 5840 | 0 | 1 | 0 | 0 | 20 | 3
105 | Bathroom | 0 | 0 |  |  | 54 | 1 | 0 | House Fan | 8 | 432 | 0 | 1 | 0 | 0 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 20 | 914 | 20 | 20 | House Fan | 8 | 7312 | 0 | 1 | 0 | 0 | 20 | 3
107 | Bathroom | 0 | 0 |  |  | 41 | 0 | 0 | House Fan | 8 | 328 | 0 | 1 | 0 | 0 | 0 | 0
108 | Classroom | 0 | 0 | Yes | 20 | 682 | 15 | 15 | House Fan | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
108 | Bathroom | 0 | 0 |  |  | 45 | 1 | 0 | House Fan | 8 | 360 | 0 | 1 | 0 | 0 | 0 | 0
109 | Climate rm | 0 | 0 | Yes | 20 | 251 | 5 | 5 | House Fan | 8 | 2008 | 0 | 1 | 0 | 0 | 20 | 3
109 | Bathroom | 0 | 0 |  |  | 58 | 1 | 0 | House Fan | 8 | 464 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 20 | 682 | 15 | 15 | House Fan | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 | Yes | 20 | 698 | 15 | 15 | House Fan | 8 | 5584 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom | 0 | 0 | Yes | 20 | 682 | 15 | 15 | House Fan | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom | 0 | 0 | Yes | 20 | 666 | 15 | 15 | House Fan | 8 | 5328 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom | 0 | 0 | Yes | 20 | 682 | 15 | 15 | House Fan | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom | 0 | 0 | Yes | 20 | 716 | 16 | 16 | House Fan | 8 | 5728 | 0 | 1 | 0 | 0 | 20 | 3
207 | Art room | 0 | 0 | Yes | 20 | 838 | 19 | 19 | House Fan | 8 | 6704 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 20 | 679 | 15 | 15 | House Fan | 8 | 5432 | 0 | 1 | 0 | 0 | 20 | 3
209 | scc room | 0 | 0 | Yes | 20 | 457 | 10 | 10 | House Fan | 8 | 3656 | 0 | 1 | 0 | 0 | 20 | 3
300 | computer lab | 0 | 0 | Yes | 20 | 688 | 15 | 15 | House Fan | 8 | 5504 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 | Yes | 20 | 688 | 15 | 15 | House Fan | 8 | 5504 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 20 | 704 | 15 | 15 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom | 0 | 0 | Yes | 20 | 670 | 15 | 15 | House Fan | 8 | 5360 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom | 0 | 0 | Yes | 20 | 643 | 14 | 14 | House Fan | 8 | 5144 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom | 0 | 0 | Yes | 20 | 691 | 15 | 15 | House Fan | 8 | 5528 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 20 | 725 | 16 | 16 | House Fan | 8 | 5800 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 | Yes | 20 | 966 | 21 | 21 | House Fan | 8 | 7728 | 0 | 1 | 0 | 0 | 20 | 3
308 |  | 0 |  |  |  | 688 |  | 0 | House Fan | 8 | 5504 |  | 1 | #VALUE! | #VALUE! | 0
309 |  | 0 |  |  |  | 360 |  | 0 | House Fan | 8 | 2880 |  | 1 | #VALUE! | #VALUE! | 0
310 |  | 0 |  |  |  | 172 |  | 0 | House Fan | 8 | 1376 |  | 1 | #VALUE! | #VALUE! | 0
- | Auditorium | 0 | 0 |  |  | 3202 | 72 | 0 | House Fan | 8 | 25616 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Boys bathroom near rm 307 | 0 | 0 |  |  | 297 | 6 | 0 | N/A | 8 | 2376 | 0 | 1 | 0 | 0 | 0 | 0
- | Boys bathroom near Nurse's Office | 0 | 0 |  |  | 144 | 3 | 0 | N/A | 8 | 1152 | 0 | 1 | 0 | 0 | 0 | 0
- | Basement Boys Bathroom | 0 | 0 |  |  | 599 | 13 | 0 | N/A | 8 | 4792 | 0 | 1 | 0 | 0 | 0 | 0
- | Basement Boys Bathroom | 0 | 0 |  |  | 317 | 7 | 0 | N/A | 8 | 2536 | 0 | 1 | 0 | 0 | 0 | 0
- | Girls bathroom near rm 301 | 0 | 0 |  |  | 415 | 9 | 0 | N/A | 8 | 3320 | 0 | 1 | 0 | 0 | 0 | 0
- | Basement Girls Bathroom | 0 | 0 |  |  | 387 | 8 | 0 | N/A | 8 | 3096 | 0 | 1 | 0 | 0 | 0 | 0
- | Girls bathroom near rm 201 | 0 | 0 |  |  | 441 | 10 | 0 | N/A | 8 | 3528 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym | 0 | 0 |  |  | 2723 | 61 | 0 | House Fan | 8 | 21784 | 0 | 1.062 | 0 | 0 | 0 | 0
- | IMC | 0 | 0 | Yes | 20 | 1168 | 26 | 26 | House Fan | 8 | 9344 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office | 0 | 0 | Yes | 20 | 360 | 8 | 8 | House Fan | 8 | 2880 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office | 0 | 0 | Yes | 20 | 175 | 3 | 3 | House Fan | 8 | 1400 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office | 0 | 0 | Yes | 20 | 231 | 5 | 5 | House Fan | 8 | 1848 | 0 | 1 | 0 | 0 | 20 | 3
- | Asst Principal Office |  | 0 | Yes | 20 | 879 | 19 | 19 | House Fan | 8 | 7032 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office |  | 0 | Yes | 20 | 458 | 10 | 10 | House Fan | 8 | 3664 | 0 | 1 | 0 | 0 | 20 | 3
- | Teachers Lounge | 0 | 0 |  |  | 605 | 13 | 0 | House Fan | 8 | 4840 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-20
School: | Thomas Edison High School
Vendor: | Devine Brothers | Devine Retest
Devine 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Office | 85 | 5 |  |  | 568 | 12 | 5 | AHU | 8 | 4544 | 1.1224 | 1 | 1.1224 | 1 | 1.1224 | 1
102 | Nurse | 212 | 14 |  |  | 498 | 11 | 11 | AHU | 8 | 3984 | 3.1928 | 1 | 3.1928 | 1 | 3.1928 | 1
103A | Mail room | 261 | 17 |  |  | 414 | 9 | 9 | AHU | 8 | 3312 | 4.7283 | 1 | 4.7283 | 2 | 4.7283 | 2
104 | Office | 66 | 4 |  |  | 140 | 3 | 3 | AHU | 8 | 1120 | 3.5357 | 1 | 3.5357 | 1 | 3.5357 | 1
105 | Office | 171 | 11 |  |  | 284 | 6 | 6 | AHU | 8 | 2272 | 4.5158 | 1 | 4.5158 | 2 | 4.5158 | 2
105C | Conference | 79 | 5 |  |  | 242 | 5 | 5 | AHU | 8 | 1936 | 2.4483 | 1 | 2.4483 | 1 | 2.4483 | 1
106 | Office | 94 | 6 |  |  | 119 | 2 | 2 | AHU | 8 | 952 | 5.9244 | 1 | 5.9244 | 2 | 5.9244 | 2
107 | Office | 68 | 4 |  |  | 112 | 2 | 2 | AHU | 8 | 896 | 4.5536 | 1 | 4.5536 | 2 | 4.5536 | 2
108 | Office | 61 | 4 |  |  | 86 | 1 | 1 | AHU | 8 | 688 | 5.3198 | 1 | 5.3198 | 2 | 5.3198 | 2
109 | Office | 56 | 3 |  |  | 74 | 1 | 1 | AHU | 8 | 592 | 5.6757 | 1 | 5.6757 | 2 | 5.6757 | 2
110 | Office | 71 | 4 |  |  | 86 | 1 | 1 | AHU | 8 | 688 | 6.1919 | 1 | 6.1919 | 2 | 6.1919 | 2
111 | Office | 68 | 4 |  |  | 86 | 1 | 1 | AHU | 8 | 688 | 5.9302 | 1 | 5.9302 | 2 | 5.9302 | 2
112 | Office | 80 | 5 |  |  | 86 | 1 | 1 | AHU | 8 | 688 | 6.9767 | 1 | 6.9767 | 2 | 6.9767 | 2
113 | Office | 63 | 4 |  |  | 86 | 1 | 1 | AHU | 8 | 688 | 5.4942 | 1 | 5.4942 | 2 | 5.4942 | 2
114 | Office | 115 | 7 |  |  | 86 | 1 | 1 | AHU | 8 | 688 | 10.0291 | 1 | 10.0291 | 3 | 10.0291 | 3
115 | Office | 124 | 8 |  |  | 86 | 1 | 1 | AHU | 8 | 688 | 10.814 | 1 | 10.814 | 3 | 10.814 | 3
116 | Office | 160 | 10 |  |  | 242 | 5 | 5 | AHU | 8 | 1936 | 4.9587 | 1 | 4.9587 | 2 | 4.9587 | 2
117 | Office | 92 | 6 |  |  | 20 | 0 | 0 | AHU | 8 | 160 | 34.5 | 1 | 34.5 | 4 | 34.5 | 4
118 | Office | 55 | 3 |  |  | 83 | 1 | 1 | AHU | 8 | 664 | 4.9699 | 1 | 4.9699 | 2 | 4.9699 | 2
120 | Office | 70 | 4 |  |  | 90 | 2 | 2 | AHU | 8 | 720 | 5.8333 | 1 | 5.8333 | 2 | 5.8333 | 2
121 | Office | 56 | 3 |  |  | 90 | 2 | 2 | AHU | 8 | 720 | 4.6667 | 1 | 4.6667 | 2 | 4.6667 | 2
122 | Office | 69 | 4 |  |  | 90 | 2 | 2 | AHU | 8 | 720 | 5.75 | 1 | 5.75 | 2 | 5.75 | 2
123 | Office | 59 | 3 |  |  | 90 | 2 | 2 | AHU | 8 | 720 | 4.9167 | 1 | 4.9167 | 2 | 4.9167 | 2
124 | Office | 57 | 3 |  |  | 90 | 2 | 2 | AHU | 8 | 720 | 4.75 | 1 | 4.75 | 2 | 4.75 | 2
125 | Office | 68 | 4 |  |  | 90 | 2 | 2 | AHU | 8 | 720 | 5.6667 | 1 | 5.6667 | 2 | 5.6667 | 2
127B | Office | 136 | 9 |  |  | 174 | 3 | 3 | AHU | 8 | 1392 | 5.8621 | 1 | 5.8621 | 2 | 5.8621 | 2
128 | Conference | 658 | 43 |  |  | 676 | 15 | 15 | AHU | 8 | 5408 | 7.3003 | 1 | 7.3003 | 2 | 7.3003 | 2
129 | Office | 150 | 10 |  |  | 281 | 6 | 6 | AHU | 8 | 2248 | 4.0036 | 1 | 4.0036 | 2 | 4.0036 | 2
130 | Office | 262 | 17 |  |  | 345 | 7 | 7 | AHU | 8 | 2760 | 5.6957 | 1 | 5.6957 | 2 | 5.6957 | 2
131 | Break Room | 84 | 5 |  |  | 131 | 2 | 2 | AHU | 8 | 1048 | 4.8092 | 1 | 4.8092 | 2 | 4.8092 | 2
132 | Classroom | 292 | 19 |  |  | 713 | 16 | 16 | AHU | 8 | 5704 | 3.0715 | 1 | 3.0715 | 1 | 3.0715 | 1
133 | Classroom | 273 | 18 |  |  | 566 | 12 | 12 | AHU | 8 | 4528 | 3.6175 | 1 | 3.6175 | 1 | 3.6175 | 1
134 | Classroom | 575 | 38 |  |  | 2286 | 51 | 38 | AHU | 8 | 18288 | 1.8865 | 1 | 1.8865 | 1 | 1.8865 | 1
135 | Classroom | 460 | 30 |  |  | 1604 | 36 | 30 | AHU | 8 | 12832 | 2.1509 | 1 | 2.1509 | 1 | 2.1509 | 1
135A | Kitchen | 61 | 4 |  |  | 37 | 0 | 0 | AHU | 8 | 296 | 12.3649 | 1 | 12.3649 | 3 | 12.3649 | 3
135B | Office | 78 | 5 |  |  | 137 | 3 | 3 | AHU | 8 | 1096 | 4.2701 | 1 | 4.2701 | 2 | 4.2701 | 2
136 | Classroom | 310 | 20 |  |  | 1144 | 26 | 20 | AHU | 8 | 9152 | 2.0323 | 1 | 2.0323 | 1 | 2.0323 | 1
136B | Classroom | 483 | 32 |  |  | 1142 | 25 | 25 | AHU | 8 | 9136 | 3.1721 | 1 | 3.1721 | 1 | 3.1721 | 1
137 | Classroom | 297 | 19 |  |  | 2086 | 47 | 19 | AHU | 8 | 16688 | 1.0678 | 1 | 1.0678 | 1 | 1.0678 | 1
137A | Office | 77 | 5 |  |  | 228 | 5 | 5 | AHU | 8 | 1824 | 2.5329 | 1 | 2.5329 | 1 | 2.5329 | 1
138 | Womens Locker Room | 1166 | 77 |  |  | 4342 | 98 | 77 | AHU | 8 | 34736 | 2.014 | 1.062 | 2.139 | 1 | 2.139 | 1
138A | Office | 50 | 3 |  |  | 78 | 1 | 1 | AHU | 8 | 624 | 4.8077 | 1 | 4.8077 | 2 | 4.8077 | 2
138B | Office | 124 | 8 |  |  | 314 | 7 | 7 | AHU | 8 | 2512 | 2.9618 | 1 | 2.9618 | 1 | 2.9618 | 1
139 | Mens Locker Room | 1278 | 85 |  |  | 3031 | 68 | 68 | AHU | 8 | 24248 | 3.1623 | 1.062 | 3.3585 | 1 | 3.3585 | 1
139A | Office | 122 | 8 |  |  | 77 | 1 | 1 | AHU | 8 | 616 | 11.8831 | 1 | 11.8831 | 3 | 11.8831 | 3
139B | Storage | 66 | 4 |  |  | 178 | 4 | 4 | AHU | 8 | 1424 | 2.7809 | 1 | 2.7809 | 1 | 2.7809 | 1
141 | Physical Fitness | 603 | 40 |  |  | 1325 | 30 | 30 | AHU | 8 | 10600 | 3.4132 | 1 | 3.4132 | 1 | 3.4132 | 1
144A | Bathroom | 52 | 3 |  |  | 333 | 7 | 3 | AHU | 8 | 2664 | 1.1712 | 1 | 1.1712 | 1 | 1.1712 | 1
144B | Bathroom | 36 | 2 |  |  | 211 | 4 | 2 | AHU | 8 | 1688 | 1.2796 | 1 | 1.2796 | 1 | 1.2796 | 1
145 | Plumbing Shop | 6184 | 412 |  |  | 1635 | 37 | 37 | AHU | 8 | 13080 | 28.367 | 1 | 28.367 | 4 | 28.367 | 4
145 | Classroom | 358 | 23 |  |  | 2286 | 51 | 23 | AHU | 8 | 18288 | 1.1745 | 1 | 1.1745 | 1 | 1.1745 | 1
145B | Classroom | 161 | 10 |  |  | 498 | 11 | 10 | AHU | 8 | 3984 | 2.4247 | 1 | 2.4247 | 1 | 2.4247 | 1
146 | Office | 297 | 19 |  |  | 1280 | 29 | 19 | AHU | 8 | 10240 | 1.7402 | 1 | 1.7402 | 1 | 1.7402 | 1
146 | Office | 332 | 22 |  |  | 276 | 6 | 6 | AHU | 8 | 2208 | 9.0217 | 1 | 9.0217 | 2 | 9.0217 | 2
147 | Storage | 87 | 5 |  |  | 476 | 10 | 5 | AHU | 8 | 3808 | 1.3708 | 1 | 1.3708 | 1 | 1.3708 | 1
147 | Classroom | 553 | 36 |  |  | 1497 | 34 | 34 | AHU | 8 | 11976 | 2.7705 | 1 | 2.7705 | 1 | 2.7705 | 1
148 | Classroom |  | 0 | Yes | 20 | 3146 | 71 | 71 |  | 8 | 25168 | 0 | 1.062 | 0 | 0 | 20 | 3
149 | Camera Room | 88 | 5 |  |  | 208 | 4 | 4 | AHU | 8 | 1664 | 3.1731 | 1 | 3.1731 | 1 | 3.1731 | 1
150 | Classroom | 375 | 25 |  |  | 814 | 18 | 18 | AHU | 8 | 6512 | 3.4552 | 1 | 3.4552 | 1 | 3.4552 | 1
150A | Office | 0 | 0 |  |  | 165 | 3 | 0 | AHU | 8 | 1320 | 0 | 1 | 0 | 0 | 0 | 0
150B | Studio | 114 | 7 |  |  | 1182 | 26 | 7 | AHU | 8 | 9456 | 0.72335 | 1 | 0.72335 | 0 | 0.72335 | 0
151A | Classroom | 534 | 35 |  |  | 1233 | 28 | 28 | AHU | 8 | 9864 | 3.2482 | 1 | 3.2482 | 1 | 3.2482 | 1
151B | Classroom | 912 | 60 |  |  | 1441 | 32 | 32 | AHU | 8 | 11528 | 4.7467 | 1 | 4.7467 | 2 | 4.7467 | 2
152 | Classroom | 655 | 43 |  |  | 794 | 18 | 18 | AHU | 8 | 6352 | 6.187 | 1 | 6.187 | 2 | 6.187 | 2
152A | Classroom | 994 | 66 |  |  | 244 | 5 | 5 | AHU | 8 | 1952 | 30.5533 | 1 | 30.5533 | 4 | 30.5533 | 4
152B | Classroom | 901 | 60 |  |  | 1073 | 24 | 24 | AHU | 8 | 8584 | 6.2978 | 1 | 6.2978 | 2 | 6.2978 | 2
153A | Classroom | 321 | 21 |  |  | 533 | 12 | 12 | AHU | 8 | 4264 | 4.5169 | 1 | 4.5169 | 2 | 4.5169 | 2
153B | Classroom | 302 | 20 |  |  | 107 | 2 | 2 | AHU | 8 | 856 | 21.1682 | 1 | 21.1682 | 3 | 21.1682 | 3
154A | Office | 278 | 18 |  |  | 175 | 3 | 3 | AHU | 8 | 1400 | 11.9143 | 1 | 11.9143 | 3 | 11.9143 | 3
154E | Classroom | 0 | 0 |  |  | 516 | 11 | 0 | AHU | 8 | 4128 | 0 | 1 | 0 | 0 | 0 | 0
154H | Classroom | 304 | 20 |  |  | 407 | 9 | 9 | AHU | 8 | 3256 | 5.602 | 1 | 5.602 | 2 | 5.602 | 2
154D 154A | Theory | 240 | 16 |  |  | 514 | 11 | 11 | AHU | 8 | 4112 | 3.5019 | 1 | 3.5019 | 1 | 3.5019 | 1
156 | Classroom | 293 | 19 |  |  | 514 | 11 | 11 | AHU | 8 | 4112 | 4.2753 | 1 | 4.2753 | 2 | 4.2753 | 2
157 | Classroom | 961 | 64 |  |  | 1255 | 28 | 28 | AHU | 8 | 10040 | 5.743 | 1 | 5.743 | 2 | 5.743 | 2
158 | Classroom | 592 | 39 |  |  | 1234 | 28 | 28 | AHU | 8 | 9872 | 3.5981 | 1 | 3.5981 | 1 | 3.5981 | 1
160 | Classroom | 727 | 48 |  |  | 1267 | 28 | 28 | AHU | 8 | 10136 | 4.3035 | 1 | 4.3035 | 2 | 4.3035 | 2
160A | Office | 78 | 5 |  |  | 119 | 2 | 2 | AHU | 8 | 952 | 4.916 | 1 | 4.916 | 2 | 4.916 | 2
161 | Classroom | 551 | 36 |  |  | 1440 | 32 | 32 | AHU | 8 | 11520 | 2.8698 | 1 | 2.8698 | 1 | 2.8698 | 1
161A | Office | 88 | 5 |  |  | 120 | 2 | 2 | AHU | 8 | 960 | 5.5 | 1 | 5.5 | 2 | 5.5 | 2
161H | Classroom | 52 | 3 |  |  | 36 | 0 | 0 | AHU | 8 | 288 | 10.8333 | 1 | 10.8333 | 3 | 10.8333 | 3
161I | Practice room | 9 | 0 |  |  | 36 | 0 | 0 | AHU | 8 | 288 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
161J | Classroom | 73 | 4 |  |  | 90 | 2 | 2 | AHU | 8 | 720 | 6.0833 | 1 | 6.0833 | 2 | 6.0833 | 2
164 | Classroom | 1398 | 93 |  |  | 825 | 18 | 18 | AHU | 8 | 6600 | 12.7091 | 1 | 12.7091 | 3 | 12.7091 | 3
164B | Classroom | 402 | 26 |  |  | 159 | 3 | 3 | AHU | 8 | 1272 | 18.9623 | 1 | 18.9623 | 3 | 18.9623 | 3
171 | Classroom | 0 | 0 |  |  | 1392 | 31 | 0 | AHU | 8 | 11136 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom | 333 | 22 |  |  | 679 | 15 | 15 | AHU | 8 | 5432 | 3.6782 | 1 | 3.6782 | 1 | 3.6782 | 1
202 | Classroom | 334 | 22 |  |  | 677 | 15 | 15 | AHU | 8 | 5416 | 3.7001 | 1 | 3.7001 | 1 | 3.7001 | 1
203 | Classroom | 325 | 21 |  |  | 680 | 15 | 15 | AHU | 8 | 5440 | 3.5846 | 1 | 3.5846 | 1 | 3.5846 | 1
204 | Classroom | 436 | 29 |  |  | 770 | 17 | 17 | AHU | 8 | 6160 | 4.2468 | 1 | 4.2468 | 2 | 4.2468 | 2
205 | Classroom | 601 | 40 |  |  | 1444 | 32 | 32 | AHU | 8 | 11552 | 3.1215 | 1 | 3.1215 | 1 | 3.1215 | 1
205B | Storage | 153 | 10 |  |  | 375 | 8 | 8 | AHU | 8 | 3000 | 3.06 | 1 | 3.06 | 1 | 3.06 | 1
207 | Classroom | 845 | 56 |  |  | 2973 | 67 | 56 | AHU | 8 | 23784 | 2.1317 | 1.062 | 2.2639 | 1 | 2.2639 | 1
209 | Classroom | 472 | 31 |  |  | 1646 | 37 | 31 | AHU | 8 | 13168 | 2.1507 | 1 | 2.1507 | 1 | 2.1507 | 1
209B | Storage | 112 | 7 |  |  | 279 | 6 | 6 | AHU | 8 | 2232 | 3.0108 | 1 | 3.0108 | 1 | 3.0108 | 1
210 | Classroom | 466 | 31 |  |  | 1552 | 35 | 31 | AHU | 8 | 12416 | 2.2519 | 1 | 2.2519 | 1 | 2.2519 | 1
210B | Storage | 190 | 12 |  |  | 331 | 7 | 7 | AHU | 8 | 2648 | 4.3051 | 1 | 4.3051 | 2 | 4.3051 | 2
212 | Office | 134 | 8 |  |  | 174 | 3 | 3 | AHU | 8 | 1392 | 5.7759 | 1 | 5.7759 | 2 | 5.7759 | 2
213A | Classroom | 384 | 25 |  |  | 721 | 16 | 16 | AHU | 8 | 5768 | 3.9945 | 1 | 3.9945 | 1 | 3.9945 | 1
213B | Classroom | 312 | 20 |  |  | 872 | 19 | 19 | AHU | 8 | 6976 | 2.6835 | 1 | 2.6835 | 1 | 2.6835 | 1
214 | Classroom | 282 | 18 |  |  | 703 | 15 | 15 | AHU | 8 | 5624 | 3.0085 | 1 | 3.0085 | 1 | 3.0085 | 1
215 | Classroom | 286 | 19 |  |  | 828 | 18 | 18 | AHU | 8 | 6624 | 2.5906 | 1 | 2.5906 | 1 | 2.5906 | 1
216 | Office | 164 | 10 |  |  | 397 | 9 | 9 | AHU | 8 | 3176 | 3.0982 | 1 | 3.0982 | 1 | 3.0982 | 1
217 | Classroom | 356 | 23 |  |  | 601 | 13 | 13 | AHU | 8 | 4808 | 4.4426 | 1 | 4.4426 | 2 | 4.4426 | 2
218 | Classroom | 352 | 23 |  |  | 639 | 14 | 14 | AHU | 8 | 5112 | 4.1315 | 1 | 4.1315 | 2 | 4.1315 | 2
219 | Office | 129 | 8 |  |  | 265 | 6 | 6 | AHU | 8 | 2120 | 3.6509 | 1 | 3.6509 | 1 | 3.6509 | 1
220 | Classroom | 444 | 29 |  |  | 715 | 16 | 16 | AHU | 8 | 5720 | 4.6573 | 1 | 4.6573 | 2 | 4.6573 | 2
220 | Classroom | 456 | 30 |  |  | 715 | 16 | 16 | AHU | 8 | 5720 | 4.7832 | 1 | 4.7832 | 2 | 4.7832 | 2
221 | Classroom | 321 | 21 |  |  | 720 | 16 | 16 | AHU | 8 | 5760 | 3.3438 | 1 | 3.3438 | 1 | 3.3438 | 1
222 | Classroom | 328 | 21 |  |  | 680 | 15 | 15 | AHU | 8 | 5440 | 3.6176 | 1 | 3.6176 | 1 | 3.6176 | 1
223 | Classroom | 299 | 19 |  |  | 781 | 17 | 17 | AHU | 8 | 6248 | 2.8713 | 1 | 2.8713 | 1 | 2.8713 | 1
224 | Classroom | 292 | 19 |  |  | 790 | 17 | 17 | AHU | 8 | 6320 | 2.7722 | 1 | 2.7722 | 1 | 2.7722 | 1
225 | Classroom | 284 | 18 |  |  | 749 | 17 | 17 | AHU | 8 | 5992 | 2.8438 | 1 | 2.8438 | 1 | 2.8438 | 1
226 | Classroom | 293 | 19 |  |  | 721 | 16 | 16 | AHU | 8 | 5768 | 3.0479 | 1 | 3.0479 | 1 | 3.0479 | 1
229 | Library | 1039 | 69 |  |  | 6194 | 140 | 69 | AHU | 8 | 49552 | 1.2581 | 1.062 | 1.3361 | 1 | 1.3361 | 1
229A | Office | 79 | 5 |  |  | 117 | 2 | 2 | AHU | 8 | 936 | 5.0641 | 1 | 5.0641 | 2 | 5.0641 | 2
229B | Office | 148 | 9 |  |  | 229 | 5 | 5 | AHU | 8 | 1832 | 4.8472 | 1 | 4.8472 | 2 | 4.8472 | 2
229C | Computer Lab | 100 | 6 |  |  | 270 | 6 | 6 | AHU | 8 | 2160 | 2.7778 | 1 | 2.7778 | 1 | 2.7778 | 1
230 | Office | 79 | 5 |  |  | 218 | 4 | 4 | AHU | 8 | 1744 | 2.7179 | 1 | 2.7179 | 1 | 2.7179 | 1
231 | Classroom | 308 | 20 |  |  | 613 | 13 | 13 | AHU | 8 | 4904 | 3.7684 | 1 | 3.7684 | 1 | 3.7684 | 1
232 | Office | 144 | 9 |  |  | 931 | 21 | 9 | AHU | 8 | 7448 | 1.16 | 1 | 1.16 | 1 | 1.16 | 1
233 | Classroom | 325 | 21 |  |  | 613 | 13 | 13 | AHU | 8 | 4904 | 3.9763 | 1 | 3.9763 | 1 | 3.9763 | 1
234 | Classroom | 334 | 22 |  |  | 700 | 15 | 15 | AHU | 8 | 5600 | 3.5786 | 1 | 3.5786 | 1 | 3.5786 | 1
235 | Classroom | 457 | 30 |  |  | 592 | 13 | 13 | AHU | 8 | 4736 | 5.7897 | 1 | 5.7897 | 2 | 5.7897 | 2
236 | Classroom | 431 | 28 |  |  | 720 | 16 | 16 | AHU | 8 | 5760 | 4.4896 | 1 | 4.4896 | 2 | 4.4896 | 2
237 | Classroom | 220 | 14 |  |  | 931 | 21 | 14 | AHU | 8 | 7448 | 1.7723 | 1 | 1.7723 | 1 | 1.7723 | 1
238 | Classroom | 112 | 7 |  |  | 606 | 13 | 7 | AHU | 8 | 4848 | 1.3861 | 1 | 1.3861 | 1 | 1.3861 | 1
239 | Classroom | 494 | 32 |  |  | 627 | 14 | 14 | AHU | 8 | 5016 | 5.9091 | 1 | 5.9091 | 2 | 5.9091 | 2
240 | Classroom | 957 | 63 |  |  | 1407 | 31 | 31 | AHU | 8 | 11256 | 5.1013 | 1 | 5.1013 | 2 | 5.1013 | 2
241 | Classroom | 318 | 21 |  |  | 714 | 16 | 16 | AHU | 8 | 5712 | 3.3403 | 1 | 3.3403 | 1 | 3.3403 | 1
241A | Classroom | 156 | 10 |  |  | 700 | 15 | 10 | AHU | 8 | 5600 | 1.6714 | 1 | 1.6714 | 1 | 1.6714 | 1
242 | Classroom | 1072 | 71 |  |  | 1512 | 34 | 34 | AHU | 8 | 12096 | 5.3175 | 1 | 5.3175 | 2 | 5.3175 | 2
243 | Classroom | 605 | 40 |  |  | 2253 | 51 | 40 | AHU | 8 | 18024 | 2.014 | 1 | 2.014 | 1 | 2.014 | 1
245 | Classroom | 403 | 26 |  |  | 1908 | 43 | 26 | AHU | 8 | 15264 | 1.5841 | 1 | 1.5841 | 1 | 1.5841 | 1
245A | Office | 107 | 7 |  |  | 258 | 5 | 5 | AHU | 8 | 2064 | 3.1105 | 1 | 3.1105 | 1 | 3.1105 | 1
246 | Classroom | 380 | 25 |  |  | 2009 | 45 | 25 | AHU | 8 | 16072 | 1.4186 | 1 | 1.4186 | 1 | 1.4186 | 1
246B | Classroom | 308 | 20 |  |  | 510 | 11 | 11 | AHU | 8 | 4080 | 4.5294 | 1 | 4.5294 | 2 | 4.5294 | 2
247 | Classroom | 676 | 45 |  |  | 1992 | 45 | 45 | AHU | 8 | 15936 | 2.5452 | 1 | 2.5452 | 1 | 2.5452 | 1
247A | Classroom | 383 | 25 |  |  | 495 | 11 | 11 | AHU | 8 | 3960 | 5.803 | 1 | 5.803 | 2 | 5.803 | 2
249 | Classroom | 307 | 20 |  |  | 888 | 20 | 20 | AHU | 8 | 7104 | 2.5929 | 1 | 2.5929 | 1 | 2.5929 | 1
250 | Classroom | 121 | 8 |  |  | 142 | 3 | 3 | AHU | 8 | 1136 | 6.3908 | 1 | 6.3908 | 2 | 6.3908 | 2
251 | Classroom | 223 | 14 |  |  | 504 | 11 | 11 | AHU | 8 | 4032 | 3.3185 | 1 | 3.3185 | 1 | 3.3185 | 1
253 | Classroom | 0 | 0 |  |  | 939 | 21 | 0 | AHU | 8 | 7512 | 0 | 1 | 0 | 0 | 0 | 0
301 | Science Lab | 428 | 28 |  |  | 940 | 21 | 21 | AHU | 8 | 7520 | 3.4149 | 1 | 3.4149 | 1 | 3.4149 | 1
302 | science prep | 0 | 0 |  |  | 197 | 4 | 0 | AHU | 8 | 1576 | 0 | 1 | 0 | 0 | 0 | 0
304 | Classroom | 448 | 29 |  |  | 1086 | 24 | 24 | AHU | 8 | 8688 | 3.0939 | 1 | 3.0939 | 1 | 3.0939 | 1
305 | Classroom | 428 | 28 |  |  | 469 | 10 | 10 | AHU | 8 | 3752 | 6.8443 | 1 | 6.8443 | 2 | 6.8443 | 2
307 | Lab | 150 | 10 |  |  | 370 | 8 | 8 | AHU | 8 | 2960 | 3.0405 | 1 | 3.0405 | 1 | 3.0405 | 1
307B | Office | 205 | 13 |  |  | 161 | 3 | 3 | AHU | 8 | 1288 | 9.5497 | 1 | 9.5497 | 2 | 9.5497 | 2
307C | Office | 152 | 10 |  |  | 92 | 2 | 2 | AHU | 8 | 736 | 12.3913 | 1 | 12.3913 | 3 | 12.3913 | 3
308 | Science Lab | 360 | 24 |  |  | 1015 | 23 | 23 | AHU | 8 | 8120 | 2.6601 | 1 | 2.6601 | 1 | 2.6601 | 1
309 | Science Prep | 316 | 21 |  |  | 260 | 5 | 5 | AHU | 8 | 2080 | 9.1154 | 1 | 9.1154 | 2 | 9.1154 | 2
310 | Classroom | 331 | 22 |  |  | 990 | 22 | 22 | AHU | 8 | 7920 | 2.5076 | 1 | 2.5076 | 1 | 2.5076 | 1
311 | Classroom | 417 | 27 |  |  | 997 | 22 | 22 | AHU | 8 | 7976 | 3.1369 | 1 | 3.1369 | 1 | 3.1369 | 1
313 | Classroom | 389 | 25 |  |  | 716 | 16 | 16 | AHU | 8 | 5728 | 4.0747 | 1 | 4.0747 | 2 | 4.0747 | 2
314 | Classroom | 296 | 19 |  |  | 793 | 18 | 18 | AHU | 8 | 6344 | 2.7995 | 1 | 2.7995 | 1 | 2.7995 | 1
315 | Classroom | 410 | 27 |  |  | 804 | 18 | 18 | AHU | 8 | 6432 | 3.8246 | 1 | 3.8246 | 1 | 3.8246 | 1
316 | Classroom | 326 | 21 |  |  | 750 | 17 | 17 | AHU | 8 | 6000 | 3.26 | 1 | 3.26 | 1 | 3.26 | 1
317A | Office | 58 | 3 |  |  | 213 | 4 | 3 | AHU | 8 | 1704 | 2.0423 | 1 | 2.0423 | 1 | 2.0423 | 1
317B | Office | 42 | 2 |  |  | 220 | 5 | 2 | AHU | 8 | 1760 | 1.4318 | 1 | 1.4318 | 1 | 1.4318 | 1
318 | Classroom | 378 | 25 |  |  | 678 | 15 | 15 | AHU | 8 | 5424 | 4.1814 | 1 | 4.1814 | 2 | 4.1814 | 2
319 | Classroom | 329 | 21 |  |  | 678 | 15 | 15 | AHU | 8 | 5424 | 3.6394 | 1 | 3.6394 | 1 | 3.6394 | 1
320 | Classroom | 325 | 21 |  |  | 678 | 15 | 15 | AHU | 8 | 5424 | 3.5951 | 1 | 3.5951 | 1 | 3.5951 | 1
321 | Classroom | 367 | 24 |  |  | 678 | 15 | 15 | AHU | 8 | 5424 | 4.0597 | 1 | 4.0597 | 2 | 4.0597 | 2
322 | Faculty Lounge | 34 | 2 |  |  | 196 | 4 | 2 | AHU | 8 | 1568 | 1.301 | 1 | 1.301 | 1 | 1.301 | 1
324 | Classroom | 282 | 18 |  |  | 611 | 13 | 13 | AHU | 8 | 4888 | 3.4615 | 1 | 3.4615 | 1 | 3.4615 | 1
325 | Classroom | 326 | 21 |  |  | 703 | 15 | 15 | AHU | 8 | 5624 | 3.478 | 1 | 3.478 | 1 | 3.478 | 1
326 | Classroom | 280 | 18 |  |  | 681 | 15 | 15 | AHU | 8 | 5448 | 3.0837 | 1 | 3.0837 | 1 | 3.0837 | 1
327 | Classroom | 310 | 20 |  |  | 702 | 15 | 15 | AHU | 8 | 5616 | 3.312 | 1 | 3.312 | 1 | 3.312 | 1
328 | Office | 135 | 9 |  |  | 334 | 7 | 7 | AHU | 8 | 2672 | 3.0314 | 1 | 3.0314 | 1 | 3.0314 | 1
328A and B | Office | 229 | 15 |  |  | 391 | 8 | 8 | AHU | 8 | 3128 | 4.3926 | 1 | 4.3926 | 2 | 4.3926 | 2
329 | Classroom | 310 | 20 |  |  | 573 | 13 | 13 | AHU | 8 | 4584 | 4.0576 | 1 | 4.0576 | 2 | 4.0576 | 2
330 | Classroom | 330 | 22 |  |  | 573 | 13 | 13 | AHU | 8 | 4584 | 4.3194 | 1 | 4.3194 | 2 | 4.3194 | 2
331 | Classroom | 425 | 28 |  |  | 708 | 16 | 16 | AHU | 8 | 5664 | 4.5021 | 1 | 4.5021 | 2 | 4.5021 | 2
333 | Classroom | 304 | 20 |  |  | 697 | 15 | 15 | AHU | 8 | 5576 | 3.2712 | 1 | 3.2712 | 1 | 3.2712 | 1
334 | Classroom | 296 | 19 |  |  | 631 | 14 | 14 | AHU | 8 | 5048 | 3.5182 | 1 | 3.5182 | 1 | 3.5182 | 1
335 | Classroom | 280 | 18 |  |  | 614 | 13 | 13 | AHU | 8 | 4912 | 3.4202 | 1 | 3.4202 | 1 | 3.4202 | 1
336 | Classroom | 282 | 18 |  |  | 632 | 14 | 14 | AHU | 8 | 5056 | 3.3465 | 1 | 3.3465 | 1 | 3.3465 | 1
338 | Classroom | 283 | 18 |  |  | 678 | 15 | 15 | AHU | 8 | 5424 | 3.1305 | 1 | 3.1305 | 1 | 3.1305 | 1
339 | Office | 47 | 3 |  |  | 322 | 7 | 3 | AHU | 8 | 2576 | 1.0947 | 1 | 1.0947 | 1 | 1.0947 | 1
340 | Classroom | 281 | 18 |  |  | 931 | 21 | 18 | AHU | 8 | 7448 | 2.2637 | 1 | 2.2637 | 1 | 2.2637 | 1
341A | Classroom | 300 | 20 |  |  | 834 | 18 | 18 | AHU | 8 | 6672 | 2.6978 | 1 | 2.6978 | 1 | 2.6978 | 1
341B | Classroom | 122 | 8 |  |  | 262 | 5 | 5 | AHU | 8 | 2096 | 3.4924 | 1 | 3.4924 | 1 | 3.4924 | 1
342 | Classroom | 332 | 22 |  |  | 587 | 13 | 13 | AHU | 8 | 4696 | 4.2419 | 1 | 4.2419 | 2 | 4.2419 | 2
344 | Classroom | 311 | 20 |  |  | 820 | 18 | 18 | AHU | 8 | 6560 | 2.8445 | 1 | 2.8445 | 1 | 2.8445 | 1
345 | Classroom | 290 | 19 |  |  | 1154 | 26 | 19 | AHU | 8 | 9232 | 1.8847 | 1 | 1.8847 | 1 | 1.8847 | 1
- | Main office Rear reception desk | 79 | 5 |  |  | 429 | 9 | 5 | AHU | 8 | 3432 | 1.3811 | 1 | 1.3811 | 1 | 1.3811 | 1
- | Main office | 221 | 14 |  |  | 1109 | 25 | 14 | AHU | 8 | 8872 | 1.4946 | 1 | 1.4946 | 1 | 1.4946 | 1
- | Student Store | 236 | 15 |  |  | 339 | 7 | 7 | AHU | 8 | 2712 | 5.2212 | 1 | 5.2212 | 2 | 5.2212 | 2
- | Teaching Kitchen | 2167 | 144 |  |  | 2843 | 64 | 64 | AHU | 8 | 22744 | 5.7167 | 1.062 | 6.0713 | 2 | 6.0713 | 2
- | Cafeteria | 0 | 0 |  |  | 8970 | 203 | 0 | AHU | 8 | 71760 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | Teaching Kitchen | 2480 | 165 |  |  | 1316 | 29 | 29 | AHU | 8 | 10528 | 14.1337 | 1 | 14.1337 | 3 | 14.1337 | 3
- | Kitchen | 1030 | 68 |  |  | 1361 | 30 | 30 | AHU | 8 | 10888 | 5.676 | 1 | 5.676 | 2 | 5.676 | 2
- | Kitchen Hood | 3846 | 256 |  |  | N/A | 0 | 0 | AHU
- | Auditorium | 6454 | 430 |  |  | 5600 | 127 | 127 | AHU | 8 | 44800 | 8.6438 | 1.062 | 9.18 | 2 | 9.18 | 2
- | 1st Floor NE | 176 | 11 |  |  | 20126 | 457 | 11 | AHU | 8 | 161008 | 0.065587 | 2.3523 | 0.15428 | 0 | 0.15428 | 0
- | Heavy Equipment | 2723 | 181 |  |  | 3189 | 72 | 72 | AHU | 8 | 25512 | 6.404 | 1.062 | 6.8013 | 2 | 6.8013 | 2
- | Autobody | 4337 | 289 |  |  | 444 | 10 | 10 | AHU | 8 | 3552 | 73.2601 | 1 | 73.2601 | 5 | 73.2601 | 5
- | Welding | 1296 | 86 |  |  | 520 | 11 | 11 | AHU | 8 | 4160 | 18.6923 | 1 | 18.6923 | 3 | 18.6923 | 3
- | Sheet Metal | 3436 | 229 |  |  | 514 | 11 | 11 | AHU | 8 | 4112 | 50.1362 | 1 | 50.1362 | 5 | 50.1362 | 5
- | Warehouse Classroom | 8094 | 539 |  |  | 533 | 12 | 12 | AHU | 8 | 4264 | 113.8931 | 1 | 113.8931 | 5 | 113.8931 | 5
- | Gym | 7088 | 472 |  |  | 15450 | 351 | 351 | AHU | 8 | 123600 | 3.4408 | 2.3523 | 8.0939 | 2 | 8.0939 | 2
- | Factory Lab | 3833 | 255 |  |  | 417 | 9 | 9 | AHU | 8 | 3336 | 68.9388 | 1 | 68.9388 | 5 | 68.9388 | 5
- | 1st Floor | 210 | 14 |  |  | 2760 | 62 | 14 | AHU | 8 | 22080 | 0.57065 | 1.062 | 0.60605 | 0 | 0.60605 | 0
- | Vending Machine Repair | 317 | 21 |  |  | 3167 | 71 | 21 | AHU | 8 | 25336 | 0.75071 | 1.062 | 0.79728 | 0 | 0.79728 | 0
- | Boiler Room | 3303 | 220 |  |  | 4914 | 111 | 111 | AHU | 8 | 39312 | 5.0412 | 1.062 | 5.3539 | 2 | 5.3539 | 2
- | Maint. Break room | 153 | 10 |  |  | 461 | 10 | 10 | AHU | 8 | 3688 | 2.4892 | 1 | 2.4892 | 1 | 2.4892 | 1
- | Eng. Office | 128 | 8 |  |  | 187 | 4 | 4 | AHU | 8 | 1496 | 5.1337 | 1 | 5.1337 | 2 | 5.1337 | 2
- | Weight Room | 990 | 66 |  |  | 939 | 21 | 21 | AHU | 8 | 7512 | 7.9073 | 1 | 7.9073 | 2 | 7.9073 | 2
- | Offices | 3928 | 261 |  |  | 90 | 2 | 2 | AHU | 8 | 720 | 327.3333 | 1 | 327.3333 | 6 | 327.3333 | 6
Sheet Last Modified: | 2021-04-21
School: | Franklin S. Edmonds Elementary School
Vendor: | Devine | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B1 | Classroom | 0 | 0 | Yes | 20 | 400 | 9 | 9 | Unit Ventilator | 8 | 3200 | 0 | 1 | 0 | 0 | 20 | 3
B2 | Kitchen | 75 | 5 |  |  | 572 | 13 | 5 | Unit Ventilator | 8 | 4576 | 0.98339 | 1 | 0.98339 | 0 | 0.98339 | 0
B3 | Kitchen | 165 | 11 |  |  | 480 | 10 | 10 | Unit Ventilator | 8 | 3840 | 2.5781 | 1 | 2.5781 | 1 | 2.5781 | 1
H2 | Office |  | 0 | Yes | 20 | 178 | 4 | 4 |  | 8 | 1424 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom | 165 | 11 | Yes | 20 | 1128 | 25 | 25 | Unit Ventilator | 8 | 9024 | 1.0971 | 1 | 1.0971 | 1 | 21.0971 | 3
102 | Classroom | 441 | 29 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 3.1321 | 1 | 3.1321 | 1 | 3.1321 | 1
103 | Classroom | 397 | 26 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 3.4462 | 1 | 3.4462 | 1 | 3.4462 | 1
104 | Classroom | 455 | 30 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 3.2315 | 1 | 3.2315 | 1 | 3.2315 | 1
105 | Classroom | 412 | 27 |  |  | 1128 | 25 | 25 | Unit Ventilator | 8 | 9024 | 2.7394 | 1 | 2.7394 | 1 | 2.7394 | 1
106 | Classroom | 460 | 30 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 3.267 | 1 | 3.267 | 1 | 3.267 | 1
107 | Classroom | 256 | 17 |  |  | 720 | 16 | 16 | Unit Ventilator | 8 | 5760 | 2.6667 | 1 | 2.6667 | 1 | 2.6667 | 1
108 | Classroom | 567 | 37 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 4.027 | 1 | 4.027 | 2 | 4.027 | 2
109 | Classroom | 527 | 35 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 3.7429 | 1 | 3.7429 | 1 | 3.7429 | 1
110 | Classroom | 431 | 28 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 3.0611 | 1 | 3.0611 | 1 | 3.0611 | 1
111 | Classroom | 634 | 42 |  |  | 1008 | 22 | 22 | Unit Ventilator | 8 | 8064 | 4.7173 | 1 | 4.7173 | 2 | 4.7173 | 2
112A | Office |  | 0 | Yes | 20 | 364 | 8 | 8 | Not supplied | 8 | 2912 | 0 | 1 | 0 | 0 | 20 | 3
112B | Office |  | 0 | Yes | 20 | 210 | 4 | 4 |  | 8 | 1680 | 0 | 1 | 0 | 0 | 20 | 3
113 | Classroom | 662 | 44 |  |  | 1008 | 22 | 22 | Unit Ventilator | 8 | 8064 | 4.9256 | 1 | 4.9256 | 2 | 4.9256 | 2
114 | Office |  | 0 | Yes | 20 | 364 | 8 | 8 | Unit Ventilator | 8 | 2912 | 0 | 1 | 0 | 0 | 20 | 3
115 | Classroom | 551 | 36 |  |  | 1008 | 22 | 22 | Unit Ventilator | 8 | 8064 | 4.0997 | 1 | 4.0997 | 2 | 4.0997 | 2
115A | Office |  | 0 | Yes | 20 | 252 | 5 | 5 |  | 8 | 2016 | 0 | 1 | 0 | 0 | 20 | 3
116 | Classroom | 169 | 11 | Yes | 20 | 736 | 16 | 16 | Unit Ventilator | 8 | 5888 | 1.7221 | 1 | 1.7221 | 1 | 21.7221 | 3
117 | Classroom | 299 | 19 |  |  | 912 | 20 | 19 | Unit Ventilator | 8 | 7296 | 2.4589 | 1 | 2.4589 | 1 | 2.4589 | 1
118 | Classroom | 281 | 18 |  |  | 912 | 20 | 18 | Unit Ventilator | 8 | 7296 | 2.3109 | 1 | 2.3109 | 1 | 2.3109 | 1
118A | Office |  | 0 |  |  | 175 | 3 | 0 |  | 8 | 1400 | 0 | 1 | 0 | 0 | 0 | 0
119 | Classroom | 282 | 18 |  |  | 912 | 20 | 18 | Unit Ventilator | 8 | 7296 | 2.3191 | 1 | 2.3191 | 1 | 2.3191 | 1
120 | Classroom | 0 | 0 | Yes | 20 | 912 | 20 | 20 | Unit Ventilator | 8 | 7296 | 0 | 1 | 0 | 0 | 20 | 3
121 | Classroom | 0 | 0 | Yes | 20 | 912 | 20 | 20 | Unit Ventilator | 8 | 7296 | 0 | 1 | 0 | 0 | 20 | 3
122 | Classroom | 340 | 22 |  |  | 912 | 20 | 20 | Unit Ventilator | 8 | 7296 | 2.7961 | 1 | 2.7961 | 1 | 2.7961 | 1
201 | Classroom | 503 | 33 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 3.5724 | 1 | 3.5724 | 1 | 3.5724 | 1
202 | Classroom | 418 | 27 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 2.9688 | 1 | 2.9688 | 1 | 2.9688 | 1
203 | Classroom | 415 | 27 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 2.9474 | 1 | 2.9474 | 1 | 2.9474 | 1
204 | Classroom | 395 | 26 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 2.8054 | 1 | 2.8054 | 1 | 2.8054 | 1
205 | Classroom | 491 | 32 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 3.4872 | 1 | 3.4872 | 1 | 3.4872 | 1
206 | Classroom | 414 | 27 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 2.9403 | 1 | 2.9403 | 1 | 2.9403 | 1
207 | Classroom | 485 | 32 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 3.4446 | 1 | 3.4446 | 1 | 3.4446 | 1
208 | Classroom | 348 | 23 |  |  | 1056 | 24 | 23 | Unit Ventilator | 8 | 8448 | 2.4716 | 1 | 2.4716 | 1 | 2.4716 | 1
209 | Classroom | 431 | 28 |  |  | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 3.0611 | 1 | 3.0611 | 1 | 3.0611 | 1
210 | Classroom | 304 | 20 |  |  | 1056 | 24 | 20 | Unit Ventilator | 8 | 8448 | 2.1591 | 1 | 2.1591 | 1 | 2.1591 | 1
211 | Classroom | 322 | 21 |  |  | 1056 | 24 | 21 | Unit Ventilator | 8 | 8448 | 2.2869 | 1 | 2.2869 | 1 | 2.2869 | 1
212 | Classroom | 31 | 2 | Yes | 20 | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 0.22017 | 1 | 0.22017 | 0 | 20.2202 | 3
213 | Classroom | 186 | 12 |  |  | 1008 | 22 | 12 | Unit Ventilator | 8 | 8064 | 1.3839 | 1 | 1.3839 | 1 | 1.3839 | 1
215 | Classroom | 509 | 33 |  |  | 1008 | 22 | 22 | Unit Ventilator | 8 | 8064 | 3.7872 | 1 | 3.7872 | 1 | 3.7872 | 1
216 | Library | 969 | 64 |  |  | 1008 | 22 | 22 | Unit Ventilator | 8 | 8064 | 7.2098 | 1 | 7.2098 | 2 | 7.2098 | 2
217 | Classroom | 503 | 33 |  |  | 1008 | 22 | 22 | Unit Ventilator | 8 | 8064 | 3.7426 | 1 | 3.7426 | 1 | 3.7426 | 1
217-A | VP office |  | 0 | Yes | 20 | 252 | 5 | 5 | Convector | 8 | 2016 | 0 | 1 | 0 | 0 | 20 | 3
218 | Classroom | 0 | 0 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
219 | Classroom | 44 | 2 |  |  | 1008 | 22 | 2 | Unit Ventilator | 8 | 8064 | 0.32738 | 1 | 0.32738 | 0 | 0.32738 | 0
- | Auditorium | 1860 | 124 |  |  | 1849 | 42 | 42 | AHU | 8 | 14792 | 7.5446 | 1 | 7.5446 | 2 | 7.5446 | 2
- | Gym | 1195 | 79 |  |  | 2795 | 63 | 63 | AHU | 8 | 22360 | 3.2066 | 1.062 | 3.4055 | 1 | 3.4055 | 1
- | Lunch | 0 | 0 |  |  | 780 | 17 | 0 | Unit Ventilator | 8 | 6240 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria | 411 | 27 | Yes | 20 | 1560 | 35 | 35 | Unit Ventilator | 8 | 12480 | 1.976 | 1 | 1.976 | 1 | 21.976 | 3
- | Kitchen | 0 | 0 | Yes | 20 | 400 | 9 | 9 | Unit Ventilator | 8 | 3200 | 0 | 1 | 0 | 0 | 20 | 3
| Women Helper |  | 0 | Yes | 20 | 262 | 5 | 5 |  | 8 | 2096 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse | 0 | 0 | Yes | 20 | 280 | 6 | 6 | N/A | 8 | 2240 | 0 | 1 | 0 | 0 | 20 | 3
- | Prin. Office | 0 | 0 | Yes | 20 | 322 | 7 | 7 | Convector | 8 | 2576 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office | 0 | 0 | Yes | 20 | 650 | 14 | 14 | Convector | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-26
School: | Lewis Elkin Elementary School
Vendor: | Devine Part 1 | Devine Part 2 | Devine Part 3
School: | Elkin Little School House
Vendor: | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
101 | Classroom | 391 | 26 |  |  | 420 | 9 | 9 | Unit Ventilator | 8 | 3360 | 6.9821 | 1 | 6.9821 | 2 | 6.9821 | 2
102 | Classroom | 0 | 0 | Yes | 20 | 1136 | 25 | 25 | Unit Ventilator | 8 | 9088 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom | 299 | 19 | Yes | 20 | 1303 | 29 | 29 | Unit Ventilator | 8 | 10424 | 1.721 | 1 | 1.721 | 1 | 21.721 | 3
104 | Classroom | 293 | 19 |  |  | 1201 | 27 | 19 | Unit Ventilator | 8 | 9608 | 1.8297 | 1 | 1.8297 | 1 | 1.8297 | 1
105 | Classroom | 301 | 20 | Yes | 20 | 1269 | 28 | 28 | Unit Ventilator | 8 | 10152 | 1.779 | 1 | 1.779 | 1 | 21.779 | 3
106 | Classroom | 300 | 20 |  |  | 418 | 9 | 9 | Unit Ventilator | 8 | 3344 | 5.3828 | 1 | 5.3828 | 2 | 5.3828 | 2
107 | Classroom | 411 | 27 |  |  | 897 | 20 | 20 | Unit Ventilator | 8 | 7176 | 3.4365 | 1 | 3.4365 | 1 | 3.4365 | 1
108 | Classroom | 386 | 25 |  |  | 897 | 20 | 20 | Unit Ventilator | 8 | 7176 | 3.2274 | 1 | 3.2274 | 1 | 3.2274 | 1
109 | Classroom | 389 | 25 |  |  | 897 | 20 | 20 | Unit Ventilator | 8 | 7176 | 3.2525 | 1 | 3.2525 | 1 | 3.2525 | 1
110 | Classroom | 376 | 25 |  |  | 821 | 18 | 18 | Unit Ventilator | 8 | 6568 | 3.4348 | 1 | 3.4348 | 1 | 3.4348 | 1
111 | Classroom | 313 | 20 |  |  | 938 | 21 | 20 | Unit Ventilator | 8 | 7504 | 2.5027 | 1 | 2.5027 | 1 | 2.5027 | 1
112 | Classroom | 363 | 24 |  |  | 898 | 20 | 20 | Unit Ventilator | 8 | 7184 | 3.0317 | 1 | 3.0317 | 1 | 3.0317 | 1
113 | Classroom | 318 | 21 |  |  | 898 | 20 | 20 | Unit Ventilator | 8 | 7184 | 2.6559 | 1 | 2.6559 | 1 | 2.6559 | 1
114 | Classroom | 349 | 23 |  |  | 898 | 20 | 20 | Unit Ventilator | 8 | 7184 | 2.9148 | 1 | 2.9148 | 1 | 2.9148 | 1
115 | Classroom | 345 | 23 |  |  | 1024 | 23 | 23 | Unit Ventilator | 8 | 8192 | 2.5269 | 1 | 2.5269 | 1 | 2.5269 | 1
116 | Lounge | 133 | 8 |  |  | 309 | 7 | 7 | Unit Ventilator | 8 | 2472 | 3.2282 | 1 | 3.2282 | 1 | 3.2282 | 1
117 | Classroom | 129 | 8 |  |  | 215 | 4 | 4 | Unit Ventilator | 8 | 1720 | 4.5 | 1 | 4.5 | 2 | 4.5 | 2
117 | Office | 96 | 6 |  |  | 317 | 7 | 6 | Unit Ventilator | 8 | 2536 | 2.2713 | 1 | 2.2713 | 1 | 2.2713 | 1
117A | Classroom Vestibule | 171 | 11 |  |  | 102 | 2 | 2 | Unit Ventilator | 8 | 816 | 12.5735 | 1 | 12.5735 | 3 | 12.5735 | 3
118 | Office | 109 | 7 |  |  | 122 | 2 | 2 | Unit Ventilator | 8 | 976 | 6.7008 | 1 | 6.7008 | 2 | 6.7008 | 2
119 | Office | 105 | 7 |  |  | 117 | 2 | 2 | Unit Ventilator | 8 | 936 | 6.7308 | 1 | 6.7308 | 2 | 6.7308 | 2
120 | Security Office | 214 | 14 |  |  | 259 | 5 | 5 | Unit Ventilator | 8 | 2072 | 6.1969 | 1 | 6.1969 | 2 | 6.1969 | 2
121 | Office |  | 0 | Yes | 20 | 400 | 9 | 9 |  | 8 | 3200 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 496 | 33 |  |  | 772 | 17 | 17 | Unit Ventilator | 8 | 6176 | 4.8187 | 1 | 4.8187 | 2 | 4.8187 | 2
202 | Classroom | 325 | 21 |  |  | 933 | 21 | 21 | Unit Ventilator | 8 | 7464 | 2.6125 | 1 | 2.6125 | 1 | 2.6125 | 1
203 | Classroom | 385 | 25 |  |  | 838 | 19 | 19 | Unit Ventilator | 8 | 6704 | 3.4457 | 1 | 3.4457 | 1 | 3.4457 | 1
204 | Classroom | 360 | 24 |  |  | 756 | 17 | 17 | Unit Ventilator | 8 | 6048 | 3.5714 | 1 | 3.5714 | 1 | 3.5714 | 1
204A | Office | 178 | 11 |  |  | 201 | 4 | 4 | Unit Ventilator | 8 | 1608 | 6.6418 | 1 | 6.6418 | 2 | 6.6418 | 2
205 | Classroom | 334 | 22 |  |  | 815 | 18 | 18 | Unit Ventilator | 8 | 6520 | 3.0736 | 1 | 3.0736 | 1 | 3.0736 | 1
206 | Classroom | 402 | 26 |  |  | 815 | 18 | 18 | Unit Ventilator | 8 | 6520 | 3.6994 | 1 | 3.6994 | 1 | 3.6994 | 1
207 | Classroom | 357 | 23 |  |  | 815 | 18 | 18 | Unit Ventilator | 8 | 6520 | 3.2853 | 1 | 3.2853 | 1 | 3.2853 | 1
207A | Office | 74 | 4 |  |  | 201 | 4 | 4 | Unit Ventilator | 8 | 1608 | 2.7612 | 1 | 2.7612 | 1 | 2.7612 | 1
208 | Classroom | 388 | 25 |  |  | 762 | 17 | 17 | Unit Ventilator | 8 | 6096 | 3.8189 | 1 | 3.8189 | 1 | 3.8189 | 1
209 | Classroom | 365 | 24 |  |  | 811 | 18 | 18 | Unit Ventilator | 8 | 6488 | 3.3755 | 1 | 3.3755 | 1 | 3.3755 | 1
210 | Classroom | 285 | 19 |  |  | 814 | 18 | 18 | Unit Ventilator | 8 | 6512 | 2.6259 | 1 | 2.6259 | 1 | 2.6259 | 1
211 | Classroom | 430 | 28 |  |  | 746 | 16 | 16 | Unit Ventilator | 8 | 5968 | 4.3231 | 1 | 4.3231 | 2 | 4.3231 | 2
211A | Office | 161 | 10 |  |  | 201 | 4 | 4 | Unit Ventilator | 8 | 1608 | 6.0075 | 1 | 6.0075 | 2 | 6.0075 | 2
212 | Classroom | 312 | 20 |  |  | 810 | 18 | 18 | Unit Ventilator | 8 | 6480 | 2.8889 | 1 | 2.8889 | 1 | 2.8889 | 1
213 | Classroom | 358 | 23 |  |  | 815 | 18 | 18 | Unit Ventilator | 8 | 6520 | 3.2945 | 1 | 3.2945 | 1 | 3.2945 | 1
214 | Classroom | 376 | 25 |  |  | 786 | 17 | 17 | Unit Ventilator | 8 | 6288 | 3.5878 | 1 | 3.5878 | 1 | 3.5878 | 1
215 | Classroom | 0 | 0 | Yes | 20 | 863 | 19 | 19 | Unit Ventilator | 8 | 6904 | 0 | 1 | 0 | 0 | 20 | 3
215A | Classroom | 131 | 8 |  |  | 201 | 4 | 4 | Unit Ventilator | 8 | 1608 | 4.8881 | 1 | 4.8881 | 2 | 4.8881 | 2
216 | Classroom | 395 | 26 |  |  | 855 | 19 | 19 | Unit Ventilator | 8 | 6840 | 3.4649 | 1 | 3.4649 | 1 | 3.4649 | 1
217 | Classroom | 493 | 32 |  |  | 1259 | 28 | 28 | Unit Ventilator | 8 | 10072 | 2.9369 | 1 | 2.9369 | 1 | 2.9369 | 1
218 | Classroom | 437 | 29 |  |  | 788 | 17 | 17 | Unit Ventilator | 8 | 6304 | 4.1593 | 1 | 4.1593 | 2 | 4.1593 | 2
219 | Classroom | 76 | 5 |  |  | 117 | 2 | 2 | Unit Ventilator | 8 | 936 | 4.8718 | 1 | 4.8718 | 2 | 4.8718 | 2
220 | Library | 1770 | 118 |  |  | 2982 | 67 | 67 | Unit Ventilator | 8 | 23856 | 4.4517 | 1.062 | 4.7279 | 2 | 4.7279 | 2
220A | Office | 214 | 14 |  |  | 373 | 8 | 8 | Unit Ventilator | 8 | 2984 | 4.3029 | 1 | 4.3029 | 2 | 4.3029 | 2
220B | Office | 0 | 0 |  |  | 421 | 9 | 0 | N/A | 8 | 3368 | 0 | 1 | 0 | 0 | 0 | 0
220C | Office | 0 | 0 |  |  | 398 | 9 | 0 | N/A | 8 | 3184 | 0 | 1 | 0 | 0 | 0 | 0
221 | Room | 0 | 0 |  |  | 141 | 3 | 0 | Unit Ventilator | 8 | 1128 | 0 | 1 | 0 | 0 | 0 | 0
B01 | Classroom | 360 | 24 |  |  | 1859 | 42 | 24 | Unit Ventilator | 8 | 14872 | 1.4524 | 1 | 1.4524 | 1 | 1.4524 | 1
B02 | Classroom | 364 | 24 |  |  | 928 | 21 | 21 | Unit Ventilator | 8 | 7424 | 2.9418 | 1 | 2.9418 | 1 | 2.9418 | 1
B03 | Classroom | 183 | 12 |  |  | 525 | 11 | 11 | Unit Ventilator | 8 | 4200 | 2.6143 | 1 | 2.6143 | 1 | 2.6143 | 1
B04 | Classroom | 300 | 20 |  |  | 613 | 13 | 13 | Unit Ventilator | 8 | 4904 | 3.6705 | 1 | 3.6705 | 1 | 3.6705 | 1
- | Assistant Principal's Office | 40 | 2 |  |  | 98 | 2 | 2 | Unit Ventilator | 8 | 784 | 3.0612 | 1 | 3.0612 | 1 | 3.0612 | 1
- | Auditorium | 0 | 0 |  |  | 7138 | 162 | 0 | Unit Ventilator | 8 | 57104 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | Main Office Conference Room | 0 | 0 |  |  | 181 | 4 | 0 | Unit Ventilator | 8 | 1448 | 0 | 1 | 0 | 0 | 0 | 0
- | Copy room | 34 | 2 |  |  | 179 | 4 | 2 | Unit Ventilator | 8 | 1432 | 1.4246 | 1 | 1.4246 | 1 | 1.4246 | 1
- | Parent Resources Office | 0 | 0 |  |  | 84 | 1 | 0 | Unit Ventilator | 8 | 672 | 0 | 1 | 0 | 0 | 0 | 0
- | Education Office | 57 | 3 |  |  | 207 | 4 | 3 | Unit Ventilator | 8 | 1656 | 2.0652 | 1 | 2.0652 | 1 | 2.0652 | 1
- | Gymnasium | 3457 | 230 |  |  | 4778 | 108 | 108 | Unit Ventilator | 8 | 38224 | 5.4264 | 1.062 | 5.7631 | 2 | 5.7631 | 2
- | Ms. Potts' Office | 46 | 3 |  |  | 133 | 3 | 3 | Unit Ventilator | 8 | 1064 | 2.594 | 1 | 2.594 | 1 | 2.594 | 1
- | Health Office/Nurses Area/Nurse's Suite | 480 | 32 |  |  | 637 | 14 | 14 | Unit Ventilator | 8 | 5096 | 5.6515 | 1 | 5.6515 | 2 | 5.6515 | 2
- | Cafeteria/Lunchroom | 1731 | 115 |  |  | 2558 | 58 | 58 | Unit Ventilator | 8 | 20464 | 5.0753 | 1.062 | 5.3901 | 2 | 5.3901 | 2
- | Principal's Office | 34 | 2 |  |  | 167 | 3 | 2 | Unit Ventilator | 8 | 1336 | 1.5269 | 1 | 1.5269 | 1 | 1.5269 | 1
- | Main Office | 235 | 15 | Yes | 20 | 674 | 15 | 15 | Unit Ventilator | 8 | 5392 | 2.615 | 1 | 2.615 | 1 | 22.615 | 3
- | Teacher's Lounge | 0 | 0 |  |  | 623 | 14 | 0 | Unit Ventilator | 8 | 4984 | 0 | 1 | 0 | 0 | 0 | 0
- | Library (Wall mount unit, south area) | 33 | 2 |  |  | 2775 | 63 | 2 | Unit Ventilator | 8 | 22200 | 0.089189 | 1.062 | 0.094722 | 0 | 0.094722 | 0
LSH Building
1 | Classroom | 829 | 55 |  |  | 1018 | 23 | 23 | AHU | 8 | 8144 | 6.1076 | 1 | 6.1076 | 2 | 6.1076 | 2
2 | Classroom | 619 | 41 |  |  | 1018 | 23 | 23 | AHU | 8 | 8144 | 4.5604 | 1 | 4.5604 | 2 | 4.5604 | 2
3 | Classroom | 651 | 43 |  |  | 1018 | 23 | 23 | AHU | 8 | 8144 | 4.7962 | 1 | 4.7962 | 2 | 4.7962 | 2
4 | Classroom | 486 | 32 |  |  | 1018 | 23 | 23 | AHU | 8 | 8144 | 3.5806 | 1 | 3.5806 | 1 | 3.5806 | 1
5 | Classroom | 410 | 27 |  |  | 1018 | 23 | 23 | AHU | 8 | 8144 | 3.0206 | 1 | 3.0206 | 1 | 3.0206 | 1
6 | Classroom | 586 | 39 |  |  | 1018 | 23 | 23 | AHU | 8 | 8144 | 4.3173 | 1 | 4.3173 | 2 | 4.3173 | 2
7 | Classroom | 379 | 25 |  |  | 1018 | 23 | 23 | AHU | 8 | 8144 | 2.7922 | 1 | 2.7922 | 1 | 2.7922 | 1
8 | Classroom | 519 | 34 |  |  | 1018 | 23 | 23 | AHU | 8 | 8144 | 3.8237 | 1 | 3.8237 | 1 | 3.8237 | 1
- | Main Office | 0 | 0 |  |  | 295 | 6 | 0 | AHU | 8 | 2360 | 0 | 1 | 0 | 0 | 0 | 0
- | Multi Purpose Room | 1105 | 73 |  |  | 1995 | 45 | 45 | AHU | 8 | 15960 | 4.1541 | 1 | 4.1541 | 2 | 4.1541 | 2
- | Teacher's Lounge | 0 | 0 |  |  | 220 | 5 | 0 | AHU | 8 | 1760 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-12
School: | Ellwood Elementary School
Vendor: | EMCOR | Exhaust | Retest
Devine 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | 100 | 13 | 0 | Yes | 20 | 1465 | 33 | 33 | Unit Ventilator | 8 | 11720 | 0.066553 | 1 | 0.066553 | 0 | 20.0666 | 3
100 A | Counselor Office |  | 0 | Yes | 20 | 297 | 6 | 6 |  | 8 | 2376 | 0 | 1 | 0 | 0 | 20 | 3
100 B-C | Nurse |  | 0 | Yes | 20 | 342 | 7 | 7 |  | 8 | 2736 | 0 | 1 | 0 | 0 | 20 | 3
100 E | Main Office |  | 0 | Yes | 20 | 416 | 9 | 9 |  | 8 | 3328 | 0 | 1 | 0 | 0 | 20 | 3
102 | 102 | 414 | 27 |  |  | 574 | 13 | 13 | Unit Ventilator | 8 | 4592 | 5.4094 | 1 | 5.4094 | 2 | 5.4094 | 2
102 C | Principal |  | 0 | Yes | 20 | 400 | 9 | 9 |  | 8 | 3200 | 0 | 1 | 0 | 0 | 20 | 3
103 | 103 | 328 | 21 |  |  | 582 | 13 | 13 | Unit Ventilator | 8 | 4656 | 4.2268 | 1 | 4.2268 | 2 | 4.2268 | 2
104 | 104 | 392 | 26 |  |  | 701 | 15 | 15 | Unit Ventilator | 8 | 5608 | 4.194 | 1 | 4.194 | 2 | 4.194 | 2
105 | 105 | 457 | 30 |  |  | 1158 | 26 | 26 | Unit Ventilator | 8 | 9264 | 2.9598 | 1 | 2.9598 | 1 | 2.9598 | 1
107 | 107 | 420 | 28 |  |  | 905 | 20 | 20 | Unit Ventilator | 8 | 7240 | 3.4807 | 1 | 3.4807 | 1 | 3.4807 | 1
108 | 108 | 443 | 29 |  |  | 906 | 20 | 20 | Unit Ventilator | 8 | 7248 | 3.6672 | 1 | 3.6672 | 1 | 3.6672 | 1
109 | 109 | 468 | 31 |  |  | 904 | 20 | 20 | Unit Ventilator | 8 | 7232 | 3.8827 | 1 | 3.8827 | 1 | 3.8827 | 1
110 | 110 | 372 | 24 |  |  | 916 | 20 | 20 | Unit Ventilator | 8 | 7328 | 3.0459 | 1 | 3.0459 | 1 | 3.0459 | 1
111 | 111 | 260 | 17 |  |  | 448 | 10 | 10 | Unit Ventilator | 8 | 3584 | 4.3527 | 1 | 4.3527 | 2 | 4.3527 | 2
201 | 201 | 520 | 34 |  |  | 940 | 21 | 21 | Unit Ventilator | 8 | 7520 | 4.1489 | 1 | 4.1489 | 2 | 4.1489 | 2
202 | 202 | 195 | 13 |  |  | 912 | 20 | 13 | Unit Ventilator | 8 | 7296 | 1.6036 | 1 | 1.6036 | 1 | 1.6036 | 1
203 | 203 | 640 | 42 |  |  | 903 | 20 | 20 | Unit Ventilator | 8 | 7224 | 5.3156 | 1 | 5.3156 | 2 | 5.3156 | 2
204 | 204 | 430 | 28 |  |  | 914 | 20 | 20 | Unit Ventilator | 8 | 7312 | 3.5284 | 1 | 3.5284 | 1 | 3.5284 | 1
206 | 206 | 409 | 27 |  |  | 860 | 19 | 19 | Unit Ventilator | 8 | 6880 | 3.5669 | 1 | 3.5669 | 1 | 3.5669 | 1
207 | 207 | 423 | 28 |  |  | 912 | 20 | 20 | Unit Ventilator | 8 | 7296 | 3.4786 | 1 | 3.4786 | 1 | 3.4786 | 1
208 | 208 | 417 | 27 |  |  | 904 | 20 | 20 | Unit Ventilator | 8 | 7232 | 3.4596 | 1 | 3.4596 | 1 | 3.4596 | 1
210 | 210 | 154 | 10 |  |  | 903 | 20 | 10 | Unit Ventilator | 8 | 7224 | 1.2791 | 1 | 1.2791 | 1 | 1.2791 | 1
211 | 211 | 511 | 34 |  |  | 912 | 20 | 20 | Unit Ventilator | 8 | 7296 | 4.2023 | 1 | 4.2023 | 2 | 4.2023 | 2
212 | 212 | 534 | 35 |  |  | 975 | 22 | 22 | Unit Ventilator | 8 | 7800 | 4.1077 | 1 | 4.1077 | 2 | 4.1077 | 2
- | Auditorium | 0 | 0 |  |  | 2900 | 65 | 0 | AHU | 8 | 23200 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Gym | 2115 | 141 |  |  | 3922 | 89 | 89 | AHU | 8 | 31376 | 4.0445 | 1.062 | 4.2954 | 2 | 4.2954 | 2
- | Library | 0 | 0 | Yes | 20 | 2809 | 63 | 63 | AHU | 8 | 22472 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Floor 1 East Corridor | 0 | 0 |  |  |  | 0 | 0 | Unit Ventilator
- | Floor 1 East Corridor | 0 | 0 |  |  |  | 0 | 0 | Unit Ventilator
Sheet Last Modified: | 2021-03-17
School: | Philadelphia Military Academy At Elverson
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
103 | Conference room | 788 | 52 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 8.5652 | 1 | 8.5652 | 2 | 8.5652 | 2
104 | IMC | 973 | 64 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 10.5761 | 1 | 10.5761 | 3 | 10.5761 | 3
105 | Conference room | 354 | 23 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 3.8478 | 1 | 3.8478 | 1 | 3.8478 | 1
106 | Weight room | 871 | 58 |  |  | 943 | 21 | 21 |  | 8 | 7544 | 6.9274 | 1 | 6.9274 | 2 | 6.9274 | 2
107 | Classroom | 1423 | 94 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 15.4674 | 1 | 15.4674 | 3 | 15.4674 | 3
108 | Classroom | 787 | 52 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 8.5543 | 1 | 8.5543 | 2 | 8.5543 | 2
111 | Classroom | 625 | 41 |  |  | 736 | 16 | 16 |  | 8 | 5888 | 6.3689 | 1 | 6.3689 | 2 | 6.3689 | 2
112 | Classroom | 112 | 7 |  |  | 736 | 16 | 7 |  | 8 | 5888 | 1.1413 | 1 | 1.1413 | 1 | 1.1413 | 1
113 | Classroom | 728 | 48 |  |  | 736 | 16 | 16 |  | 8 | 5888 | 7.4185 | 1 | 7.4185 | 2 | 7.4185 | 2
114 | Classroom | 525 | 35 |  |  | 1180 | 26 | 26 |  | 8 | 9440 | 3.3369 | 1 | 3.3369 | 1 | 3.3369 | 1
201 | Classroom | 1325 | 88 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 14.4022 | 1 | 14.4022 | 3 | 14.4022 | 3
202 | Classroom | 180 | 12 |  |  | 690 | 15 | 12 |  | 8 | 5520 | 1.9565 | 1 | 1.9565 | 1 | 1.9565 | 1
203 | Classroom | 428 | 28 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 4.6522 | 1 | 4.6522 | 2 | 4.6522 | 2
204 | Classroom | 487 | 32 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 5.2935 | 1 | 5.2935 | 2 | 5.2935 | 2
205 | Classroom | 73 | 4 |  |  | 805 | 18 | 4 |  | 8 | 6440 | 0.68012 | 1 | 0.68012 | 0 | 0.68012 | 0
206 | Classroom | 796 | 53 |  |  | 943 | 21 | 21 |  | 8 | 7544 | 6.3309 | 1 | 6.3309 | 2 | 6.3309 | 2
207 | Classroom | 63 | 4 |  |  | 690 | 15 | 4 |  | 8 | 5520 | 0.68478 | 1 | 0.68478 | 0 | 0.68478 | 0
208 | Classroom | 445 | 29 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 4.837 | 1 | 4.837 | 2 | 4.837 | 2
211 | Classroom | 0 | 0 |  |  | 736 | 16 | 0 |  | 8 | 5888 | 0 | 1 | 0 | 0 | 0 | 0
212 | Classroom | 0 | 0 |  |  | 736 | 16 | 0 |  | 8 | 5888 | 0 | 1 | 0 | 0 | 0 | 0
213 | Classroom | 670 | 44 |  |  | 736 | 16 | 16 |  | 8 | 5888 | 6.8274 | 1 | 6.8274 | 2 | 6.8274 | 2
214 | Classroom | 0 | 0 |  |  | 736 | 16 | 0 |  | 8 | 5888 | 0 | 1 | 0 | 0 | 0 | 0
215 | Classroom | 745 | 49 |  |  | 736 | 16 | 16 |  | 8 | 5888 | 7.5917 | 1 | 7.5917 | 2 | 7.5917 | 2
301 | Classroom | 142 | 9 |  |  | 690 | 15 | 9 |  | 8 | 5520 | 1.5435 | 1 | 1.5435 | 1 | 1.5435 | 1
302 | Classroom | 447 | 29 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 4.8587 | 1 | 4.8587 | 2 | 4.8587 | 2
303 | Classroom | 117 | 7 |  |  | 690 | 15 | 7 |  | 8 | 5520 | 1.2717 | 1 | 1.2717 | 1 | 1.2717 | 1
304 | Classroom | 147 | 9 |  |  | 690 | 15 | 9 |  | 8 | 5520 | 1.5978 | 1 | 1.5978 | 1 | 1.5978 | 1
305 | Classroom | 120 | 8 |  |  | 805 | 18 | 8 |  | 8 | 6440 | 1.118 | 1 | 1.118 | 1 | 1.118 | 1
306 | Classroom | 796 | 53 |  |  | 1048 | 23 | 23 |  | 8 | 8384 | 5.6966 | 1 | 5.6966 | 2 | 5.6966 | 2
307 | Classroom | 370 | 24 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 4.0217 | 1 | 4.0217 | 2 | 4.0217 | 2
308 | Classroom | 477 | 31 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 5.1848 | 1 | 5.1848 | 2 | 5.1848 | 2
309 | Classroom | 115 | 7 |  |  | 690 | 15 | 7 |  | 8 | 5520 | 1.25 | 1 | 1.25 | 1 | 1.25 | 1
311 | Classroom | 572 | 38 |  |  | 736 | 16 | 16 |  | 8 | 5888 | 5.8288 | 1 | 5.8288 | 2 | 5.8288 | 2
312 | Classroom | 0 | 0 |  |  | 736 | 16 | 0 |  | 8 | 5888 | 0 | 1 | 0 | 0 | 0 | 0
313 | Classroom | 697 | 46 |  |  | 736 | 16 | 16 |  | 8 | 5888 | 7.1026 | 1 | 7.1026 | 2 | 7.1026 | 2
314 | Classroom | 0 | 0 |  |  | 736 | 16 | 0 |  | 8 | 5888 | 0 | 1 | 0 | 0 | 0 | 0
315 | Classroom | 0 | 0 |  |  | 736 | 16 | 0 |  | 8 | 5888 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria / Kitchen | 970 | 64 |  |  | 2595 | 58 | 58 |  | 8 | 20760 | 2.8035 | 1.062 | 2.9774 | 1 | 2.9774 | 1
- | Hallway | 462 | 30 |  |  | 1400 | 31 | 30 |  | 8 | 11200 | 2.475 | 1 | 2.475 | 1 | 2.475 | 1
- | Hallway | 0 | 0 |  |  | 1400 | 31 | 0 |  | 8 | 11200 | 0 | 1 | 0 | 0 | 0 | 0
- | Hallway | 432 | 28 |  |  | 1400 | 31 | 28 |  | 8 | 11200 | 2.3143 | 1 | 2.3143 | 1 | 2.3143 | 1
- | main office | 1050 | 70 |  |  | 744 | 16 | 16 |  | 8 | 5952 | 10.5847 | 1 | 10.5847 | 3 | 10.5847 | 3
- | Office / storage | 735 | 49 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 7.6562 | 1 | 7.6562 | 2 | 7.6562 | 2
Sheet Last Modified: | 2021-04-21
School: | Eleanor Emlen Elementary School | House fan Abated
Vendor: | Devine Brothers | Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B001 | Classroom | 736 | 49 |  |  | 736 | 16 | 16 | Unit Ventilator | 8 | 5888 | 7.5 | 1 | 7.5 | 2 | 7.5 | 2
B002 | Classroom | 0 | 0 | Yes | 20 | 1848 | 42 | 42 | Unit Ventilator | 8 | 14784 | 0 | 1 | 0 | 0 | 20 | 3
B003 | Classroom | 994 | 66 |  |  | 1032 | 23 | 23 | Unit Ventilator | 8 | 8256 | 7.2238 | 1 | 7.2238 | 2 | 7.2238 | 2
B004A | Classroom | 701 | 46 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 6.8457 | 1 | 6.8457 | 2 | 6.8457 | 2
B004B | Classroom | 360 | 24 |  |  | 816 | 18 | 18 | Unit Ventilator | 8 | 6528 | 3.3088 | 1 | 3.3088 | 1 | 3.3088 | 1
B005 | Classroom | 419 | 27 |  |  | 546 | 12 | 12 | Unit Ventilator | 8 | 4368 | 5.7555 | 1 | 5.7555 | 2 | 5.7555 | 2
101 | Classroom | 857 | 57 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 8.3691 | 1 | 8.3691 | 2 | 8.3691 | 2
102 | Classroom | 267 | 17 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 2.9022 | 1 | 2.9022 | 1 | 2.9022 | 1
103 | Classroom | 517 | 34 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 5.6196 | 1 | 5.6196 | 2 | 5.6196 | 2
104 | Office | 193 | 12 |  |  | 88 | 2 | 2 | House Fan | 8 | 704 | 16.4489 | 1 | 16.4489 | 3 | 16.4489 | 3
104D | Waiting Room | 255 | 17 |  |  | 90 | 2 | 2 | House Fan | 8 | 720 | 21.25 | 1 | 21.25 | 3 | 21.25 | 3
104D | Office | 199 | 13 |  |  | 396 | 9 | 9 | House Fan | 8 | 3168 | 3.7689 | 1 | 3.7689 | 1 | 3.7689 | 1
104D | Storage | 136 | 9 |  |  | 207 | 4 | 4 | House Fan | 8 | 1656 | 4.9275 | 1 | 4.9275 | 2 | 4.9275 | 2
104D | Nurse | 173 | 11 |  |  | 144 | 3 | 3 | House Fan | 8 | 1152 | 9.0104 | 1 | 9.0104 | 2 | 9.0104 | 2
105 | Waiting Room | 174 | 11 |  |  | 248 | 5 | 5 | House Fan | 8 | 1984 | 5.2621 | 1 | 5.2621 | 2 | 5.2621 | 2
105A | Office | 93 | 6 |  |  | 182 | 4 | 4 | House Fan | 8 | 1456 | 3.8324 | 1 | 3.8324 | 1 | 3.8324 | 1
105B | Office | 85 | 5 |  |  | 126 | 2 | 2 | House Fan | 8 | 1008 | 5.0595 | 1 | 5.0595 | 2 | 5.0595 | 2
105C | Office | 103 | 6 |  |  | 126 | 2 | 2 | House Fan | 8 | 1008 | 6.131 | 1 | 6.131 | 2 | 6.131 | 2
106 | Classroom | 378 | 25 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 4.1087 | 1 | 4.1087 | 2 | 4.1087 | 2
107 | Classroom | 289 | 19 |  |  | 792 | 18 | 18 | House Fan | 8 | 6336 | 2.7367 | 1 | 2.7367 | 1 | 2.7367 | 1
108 | Classroom | 643 | 42 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 6.9891 | 1 | 6.9891 | 2 | 6.9891 | 2
109 | Classroom | 782 | 52 |  |  | 1050 | 23 | 23 | House Fan | 8 | 8400 | 5.5857 | 1 | 5.5857 | 2 | 5.5857 | 2
110 | Classroom | 485 | 32 |  |  | 621 | 14 | 14 | House Fan | 8 | 4968 | 5.8575 | 1 | 5.8575 | 2 | 5.8575 | 2
200 | Classroom | 0 | 0 | Yes | 20 | 528 | 12 | 12 | House Fan | 8 | 4224 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 531 | 35 |  |  | 800 | 18 | 18 | House Fan | 8 | 6400 | 4.9781 | 1 | 4.9781 | 2 | 4.9781 | 2
202 | Classroom | 312 | 20 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 3.3913 | 1 | 3.3913 | 1 | 3.3913 | 1
203 | Classroom | 273 | 18 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 2.9674 | 1 | 2.9674 | 1 | 2.9674 | 1
204 | Classroom | 97 | 6 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 1.0543 | 1 | 1.0543 | 1 | 21.0543 | 3
205 | Classroom | 443 | 29 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 4.8152 | 1 | 4.8152 | 2 | 4.8152 | 2
206 | Classroom | 267 | 17 |  |  | 900 | 20 | 17 | House Fan | 8 | 7200 | 2.225 | 1 | 2.225 | 1 | 2.225 | 1
207 | Classroom | 372 | 24 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 4.0435 | 1 | 4.0435 | 2 | 4.0435 | 2
208 | Classroom | 437 | 29 |  |  | 805 | 18 | 18 | House Fan | 8 | 6440 | 4.0714 | 1 | 4.0714 | 2 | 4.0714 | 2
209 | Classroom | 504 | 33 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 5.4783 | 1 | 5.4783 | 2 | 5.4783 | 2
210 | Classroom | 361 | 24 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 3.9239 | 1 | 3.9239 | 1 | 3.9239 | 1
211 | Classroom | 416 | 27 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 4.5217 | 1 | 4.5217 | 2 | 4.5217 | 2
213 | Classroom | 0 | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
214 | Classroom | 0 | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
215 | Classroom | 0 | 0 | Yes | 20 | 744 | 16 | 16 | House Fan | 8 | 5952 | 0 | 1 | 0 | 0 | 20 | 3
216 | Classroom | 0 | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
217 | Classroom | 0 | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
218 | Classroom | 0 | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 | Yes | 20 | 1190 | 27 |  |  | 8 | 9520 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom | 695 | 46 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 7.8977 | 1 | 7.8977 | 2 | 7.8977 | 2
303 | Classroom | 99 | 6 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 1.125 | 1 | 1.125 | 1 | 21.125 | 3
304 | Classroom | 719 | 47 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 8.1705 | 1 | 8.1705 | 2 | 8.1705 | 2
305 | Classroom | 427 | 28 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 5.1989 | 1 | 5.1989 | 2 | 5.1989 | 2
306 | Classroom | 259 | 17 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 3.0447 | 1 | 3.0447 | 1 | 3.0447 | 1
307 | Classroom | 336 | 22 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 3.6522 | 1 | 3.6522 | 1 | 3.6522 | 1
308 | Classroom | 372 | 24 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 4.2273 | 1 | 4.2273 | 2 | 4.2273 | 2
308A | Classroom |  | 0 | Yes | 20 | 220 | 5 |  |  | 8 | 1760 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom | 105 | 7 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 1.1413 | 1 | 1.1413 | 1 | 21.1413 | 3
310 | Classroom | 346 | 23 |  |  | 540 | 12 | 12 | House Fan | 8 | 4320 | 4.8056 | 1 | 4.8056 | 2 | 4.8056 | 2
311 | Classroom | 178 | 11 |  |  | 690 | 15 | 11 | House Fan | 8 | 5520 | 1.9348 | 1 | 1.9348 | 1 | 1.9348 | 1
Portable Building | Cafeteria 1 |  | 0 |  |  | 1840 | 41 |  |  | 8 | 14720 | 0 | 1 | 0 | 0 | 0 | 0
Portable Building | Cafeteria 2 |  | 0 |  |  | 989 | 22 |  |  | 8 | 7912 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 | Yes | 20 | 5336 | 121 | 121 | House Fan | 8 | 42688 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Basement Office/Classroom | 617 | 41 |  |  | 1088 | 24 | 24 | House Fan | 8 | 8704 | 4.2532 | 1 | 4.2532 | 2 | 4.2532 | 2
- | Gym | 3331 | 222 |  |  | 5005 | 113 | 113 | AHU | 8 | 40040 | 4.9915 | 1.062 | 5.3012 | 2 | 5.3012 | 2
- | Prinicipal Office |  | 0 |  |  | 108 | 2 | 0 |  | 8 | 864 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office |  | 0 |  |  | 234 | 5 | 0 |  | 8 | 1872 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27
School: | Louis H. Farrell Elementary School
Vendor: | EMCOR | Retest
| Devine 2nd Retest | Devine 3rd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
A-2 | LS | 269 | 17 |  |  | 891 | 20 | 17 | Unit Ventilator | 8 | 7128 | 2.2643 | 1 | 2.2643 | 1 | 2.2643 | 1
A-3 | LS | 319 | 21 |  |  | 891 | 20 | 20 | Unit Ventilator | 8 | 7128 | 2.6852 | 1 | 2.6852 | 1 | 2.6852 | 1
A-4 | LS | 259 | 17 |  |  | 540 | 12 | 12 | Unit Ventilator | 8 | 4320 | 3.5972 | 1 | 3.5972 | 1 | 3.5972 | 1
A-6 | LS | 274 | 18 |  |  | 891 | 20 | 18 | Unit Ventilator | 8 | 7128 | 2.3064 | 1 | 2.3064 | 1 | 2.3064 | 1
A-10 | A-10 | 290 | 19 |  |  | 1130 | 25 | 19 | RTU | 8 | 9040 | 1.9248 | 1 | 1.9248 | 1 | 1.9248 | 1
A-11 | A-11 | 276 | 18 |  |  | 800 | 18 | 18 | RTU | 8 | 6400 | 2.5875 | 1 | 2.5875 | 1 | 2.5875 | 1
A-12 | A-12 | 296 | 19 |  |  | 800 | 18 | 18 | RTU | 8 | 6400 | 2.775 | 1 | 2.775 | 1 | 2.775 | 1
A-13 | A-13 | 306 | 20 |  |  | 800 | 18 | 18 | RTU | 8 | 6400 | 2.8687 | 1 | 2.8687 | 1 | 2.8687 | 1
A-14 | A-14 | 293 | 19 |  |  | 800 | 18 | 18 | RTU | 8 | 6400 | 2.7469 | 1 | 2.7469 | 1 | 2.7469 | 1
A-15 | A-15 | 331 | 22 |  |  | 800 | 18 | 18 | RTU | 8 | 6400 | 3.1031 | 1 | 3.1031 | 1 | 3.1031 | 1
A-16 | A-16 | 303 | 20 |  |  | 800 | 18 | 18 | RTU | 8 | 6400 | 2.8406 | 1 | 2.8406 | 1 | 2.8406 | 1
A-21 | A-21 | 314 | 20 |  |  | 800 | 18 | 18 | RTU | 8 | 6400 | 2.9438 | 1 | 2.9438 | 1 | 2.9438 | 1
A-22 | A-22 | 285 | 19 |  |  | 800 | 18 | 18 | RTU | 8 | 6400 | 2.6719 | 1 | 2.6719 | 1 | 2.6719 | 1
A-23 | A-23 | 293 | 19 |  |  | 800 | 18 | 18 | RTU | 8 | 6400 | 2.7469 | 1 | 2.7469 | 1 | 2.7469 | 1
A-24 | A-24 | 293 | 19 |  |  | 800 | 18 | 18 | RTU | 8 | 6400 | 2.7469 | 1 | 2.7469 | 1 | 2.7469 | 1
A-25 | A-25 | 333 | 22 |  |  | 800 | 18 | 18 | RTU | 8 | 6400 | 3.1219 | 1 | 3.1219 | 1 | 3.1219 | 1
A-26 | A-26 | 316 | 21 |  |  | 800 | 18 | 18 | RTU | 8 | 6400 | 2.9625 | 1 | 2.9625 | 1 | 2.9625 | 1
100 | LS | 328 | 21 |  |  | 1813 | 41 | 21 | Unit Ventilator | 8 | 14504 | 1.3569 | 1 | 1.3569 | 1 | 1.3569 | 1
101 | LS | 326 | 21 |  |  | 1813 | 41 | 21 | Unit Ventilator | 8 | 14504 | 1.3486 | 1 | 1.3486 | 1 | 1.3486 | 1
103 | LS | 406 | 27 |  |  | 925 | 21 | 21 | Unit Ventilator | 8 | 7400 | 3.2919 | 1 | 3.2919 | 1 | 3.2919 | 1
105 | AS | 318 | 21 |  |  | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 3.5491 | 1 | 3.5491 | 1 | 3.5491 | 1
108 |  |  |  | Yes | 20 | 350 |  |  | N/A | 8 | 2800 |  | 1 | #VALUE! | #VALUE! | 20
111 | AS | 241 | 16 |  |  | 950 | 21 | 16 | Unit Ventilator | 8 | 7600 | 1.9026 | 1 | 1.9026 | 1 | 1.9026 | 1
112 | ? | 282 | 18 |  |  | 950 | 21 | 18 | Unit Ventilator | 8 | 7600 | 2.2263 | 1 | 2.2263 | 1 | 2.2263 | 1
113 | ? | 222 | 14 |  |  | 950 | 21 | 14 | Unit Ventilator | 8 | 7600 | 1.7526 | 1 | 1.7526 | 1 | 1.7526 | 1
200 | LIT/SS | 318 | 21 |  |  | 950 | 21 | 21 | Unit Ventilator | 8 | 7600 | 2.5105 | 1 | 2.5105 | 1 | 2.5105 | 1
201 | M/SC | 278 | 18 |  |  | 950 | 21 | 18 | Unit Ventilator | 8 | 7600 | 2.1947 | 1 | 2.1947 | 1 | 2.1947 | 1
202 | LS | 297 | 19 |  |  | 950 | 21 | 19 | Unit Ventilator | 8 | 7600 | 2.3447 | 1 | 2.3447 | 1 | 2.3447 | 1
203 | RELA/LS/EL PI | 297 | 19 |  |  | 950 | 21 | 19 | Unit Ventilator | 8 | 7600 | 2.3447 | 1 | 2.3447 | 1 | 2.3447 | 1
204 | Classroom |  | 0 | Yes | 20 | 288 | 6 | 6 | Unit Ventilator | 8 | 2304 | 0 | 1 | 0 | 0 | 20 | 3
205 | M/SC/SS | 345 | 23 |  |  | 950 | 21 | 21 | Unit Ventilator | 8 | 7600 | 2.7237 | 1 | 2.7237 | 1 | 2.7237 | 1
206 | RELA | 327 | 21 |  |  | 950 | 21 | 21 | Unit Ventilator | 8 | 7600 | 2.5816 | 1 | 2.5816 | 1 | 2.5816 | 1
207 | ESOL | 372 | 24 |  |  | 950 | 21 | 21 | Unit Ventilator | 8 | 7600 | 2.9368 | 1 | 2.9368 | 1 | 2.9368 | 1
208 | MATH | 308 | 20 |  |  | 950 | 21 | 20 | Unit Ventilator | 8 | 7600 | 2.4316 | 1 | 2.4316 | 1 | 2.4316 | 1
209 | M/SC/SS | 294 | 19 |  |  | 950 | 21 | 19 | Unit Ventilator | 8 | 7600 | 2.3211 | 1 | 2.3211 | 1 | 2.3211 | 1
209A |  |  |  | Yes | 20 | 310 |  |  | N/A | 8 | 2480 |  | 1 | #VALUE! | #VALUE! | 20
210 | RELA/SS | 203 | 13 |  |  | 950 | 21 | 13 | Unit Ventilator | 8 | 7600 | 1.6026 | 1 | 1.6026 | 1 | 1.6026 | 1
211 | MATH/SC | 245 | 16 |  |  | 950 | 21 | 16 | Unit Ventilator | 8 | 7600 | 1.9342 | 1 | 1.9342 | 1 | 1.9342 | 1
212 | RELA | 293 | 19 |  |  | 950 | 21 | 19 | Unit Ventilator | 8 | 7600 | 2.3132 | 1 | 2.3132 | 1 | 2.3132 | 1
213 | SC/SS | 283 | 18 |  |  | 950 | 21 | 18 | Unit Ventilator | 8 | 7600 | 2.2342 | 1 | 2.2342 | 1 | 2.2342 | 1
300 | RELA / SS | 265 | 17 |  |  | 950 | 21 | 17 | Unit Ventilator | 8 | 7600 | 2.0921 | 1 | 2.0921 | 1 | 2.0921 | 1
301 | CSC | 277 | 18 |  |  | 950 | 21 | 18 | Unit Ventilator | 8 | 7600 | 2.1868 | 1 | 2.1868 | 1 | 2.1868 | 1
302 | MATH | 254 | 16 |  |  | 950 | 21 | 16 | Unit Ventilator | 8 | 7600 | 2.0053 | 1 | 2.0053 | 1 | 2.0053 | 1
303 | SC/SS | 224 | 14 |  |  | 950 | 21 | 14 | Unit Ventilator | 8 | 7600 | 1.7684 | 1 | 1.7684 | 1 | 1.7684 | 1
304 | Room |  | 0 | Yes | 20 | 192 | 4 | 4 |  | 8 | 1536 | 0 | 1 | 0 | 0 | 20 | 3
305 | SC/MATH | 287 | 19 |  |  | 950 | 21 | 19 | Unit Ventilator | 8 | 7600 | 2.2658 | 1 | 2.2658 | 1 | 2.2658 | 1
306 | MATH | 300 | 20 |  |  | 950 | 21 | 20 | Unit Ventilator | 8 | 7600 | 2.3684 | 1 | 2.3684 | 1 | 2.3684 | 1
307 | SS/RELA | 226 | 15 |  |  | 950 | 21 | 15 | Unit Ventilator | 8 | 7600 | 1.7842 | 1 | 1.7842 | 1 | 1.7842 | 1
308 | RELA/EL B | 277 | 18 |  |  | 950 | 21 | 18 | Unit Ventilator | 8 | 7600 | 2.1868 | 1 | 2.1868 | 1 | 2.1868 | 1
309 | SC/SS | 277 | 18 |  |  | 1175 | 26 | 18 | Unit Ventilator | 8 | 9400 | 1.7681 | 1 | 1.7681 | 1 | 1.7681 | 1
310 | MATH | 346 | 23 |  |  | 950 | 21 | 21 | Unit Ventilator | 8 | 7600 | 2.7316 | 1 | 2.7316 | 1 | 2.7316 | 1
311 | RELA EL PI | 232 | 15 |  |  | 950 | 21 | 15 | Unit Ventilator | 8 | 7600 | 1.8316 | 1 | 1.8316 | 1 | 1.8316 | 1
312 | SS/RELA ALG | 203 | 13 |  |  | 950 | 21 | 13 | Unit Ventilator | 8 | 7600 | 1.6026 | 1 | 1.6026 | 1 | 1.6026 | 1
313 | SC/MATH | 223 | 14 |  |  | 950 | 21 | 14 | Unit Ventilator | 8 | 7600 | 1.7605 | 1 | 1.7605 | 1 | 1.7605 | 1
- | Lunchroom | 815 | 54 |  |  | 2604 | 59 | 54 | Unit Ventilator | 8 | 20832 | 2.3474 | 1.062 | 2.493 | 1 | 2.493 | 1
Gymnasium | Gymnasium |  | 0 | Yes | 20 | 3940 | 89 | 89 |  | 8 | 31520 | 0 | 1.062 | 0 | 0 | 20 | 3
Gymnasium | Office |  | 0 | Yes | 20 | 247 | 5 | 5 |  | 8 | 1976 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 72 | 4 |  |  | 3808 | 86 | 4 | Unit Ventilator | 8 | 30464 | 0.14181 | 1.062 | 0.1506 | 0 | 0.1506 | 0
- | Main Office |  | 0 | Yes | 20 | 279 | 6 | 6 | N/A | 8 | 2232 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 |  |  | 288 | 6 | 0 | N/A | 8 | 2304 | 0 | 1 | 0 | 0 | 0 | 0
Vice Principal | Office |  | 0 | Yes | 20 | 96 | 2 | 2 |  | 8 | 768 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office |  | 0 | Yes | 20 | 288 | 6 | 6 | N/A | 8 | 2304 | 0 | 1 | 0 | 0 | 20 | 3
Building Engineer | Office |  | 0 | Yes | 20 | 275 | 6 | 6 |  | 8 | 2200 | 0 | 1 | 0 | 0 | 20 | 3
- | IMC |  | 0 | Yes | 20 | 1485 | 33 | 33 | N/A | 8 | 11880 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse |  | 0 | Yes | 20 | 234 | 5 | 5 | N/A | 8 | 1872 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-23
School: | D. Newlin Fell Elementary-Middle School | House fan Abated
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
2 | Music Room | 519 | 34 |  |  | 418 | 9 | 9 | House Fan | 8 | 3344 | 9.3122 | 1 | 9.3122 | 2 | 9.3122 | 2
100 | Classroom | 677 | 45 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.2124 | 1 | 7.2124 | 2 | 7.2124 | 2
101 | Classroom | 791 | 52 |  |  | 308 | 7 | 7 | House Fan | 8 | 2464 | 19.2614 | 1 | 19.2614 | 3 | 19.2614 | 3
102 | Classroom | 653 | 43 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.9567 | 1 | 6.9567 | 2 | 6.9567 | 2
103 | Classroom | 588 | 39 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 6.6818 | 1 | 6.6818 | 2 | 6.6818 | 2
104 | Classroom | 604 | 40 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 6.8636 | 1 | 6.8636 | 2 | 6.8636 | 2
105 | Classroom | 960 | 64 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 10.9091 | 1 | 10.9091 | 3 | 10.9091 | 3
106 | Classroom | 560 | 37 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 6.3636 | 1 | 6.3636 | 2 | 6.3636 | 2
107 | Classroom | 760 | 50 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 8.3578 | 1 | 8.3578 | 2 | 8.3578 | 2
108 | Classroom | 550 | 36 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 6.4655 | 1 | 6.4655 | 2 | 6.4655 | 2
109 | Classroom | 491 | 32 |  |  | 687 | 15 | 15 | House Fan | 8 | 5496 | 5.3603 | 1 | 5.3603 | 2 | 5.3603 | 2
200 | Classroom | 362 | 24 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 3.9809 | 1 | 3.9809 | 1 | 3.9809 | 1
201 | Classroom | 750 | 50 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 8.8166 | 1 | 8.8166 | 2 | 8.8166 | 2
202 | Classroom | 840 | 56 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 9.2375 | 1 | 9.2375 | 2 | 9.2375 | 2
203 | Classroom | 411 | 27 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 4.6705 | 1 | 4.6705 | 2 | 4.6705 | 2
204 | Classroom | 952 | 63 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 10.8182 | 1 | 10.8182 | 3 | 10.8182 | 3
205 | Library | 670 | 44 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 7.8762 | 1 | 7.8762 | 2 | 7.8762 | 2
206 | Library | 668 | 44 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 7.8527 | 1 | 7.8527 | 2 | 7.8527 | 2
207 | Classroom | 512 | 34 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 5.6305 | 1 | 5.6305 | 2 | 5.6305 | 2
208 | Classroom | 765 | 51 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 8.9929 | 1 | 8.9929 | 2 | 8.9929 | 2
209 | Classroom | 478 | 31 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 5.2566 | 1 | 5.2566 | 2 | 5.2566 | 2
300 | Classroom | 500 | 33 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 5.3267 | 1 | 5.3267 | 2 | 5.3267 | 2
301 | Classroom | 406 | 27 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 4.7727 | 1 | 4.7727 | 2 | 4.7727 | 2
302 | Classroom | 110 | 7 |  |  | 682 | 15 | 7 | House Fan | 8 | 5456 | 1.2097 | 1 | 1.2097 | 1 | 1.2097 | 1
303 | Classroom | 426 | 28 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 4.8409 | 1 | 4.8409 | 2 | 4.8409 | 2
304 | Classroom | 630 | 42 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 7.1591 | 1 | 7.1591 | 2 | 7.1591 | 2
305 | Classroom | 888 | 59 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 10.0909 | 1 | 10.0909 | 3 | 10.0909 | 3
306 | Classroom | 791 | 52 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 8.9886 | 1 | 8.9886 | 2 | 8.9886 | 2
307 | Classroom | 407 | 27 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 4.4758 | 1 | 4.4758 | 2 | 4.4758 | 2
308 | Classroom | 641 | 42 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 7.5353 | 1 | 7.5353 | 2 | 7.5353 | 2
309 | Classroom | 645 | 43 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.8714 | 1 | 6.8714 | 2 | 6.8714 | 2
309A | Classroom |  | 0 | Yes | 20 | 275 | 6 | 6 | N/A | 8 | 2200 | 0 | 1 | 0 | 0 | 20 | 3
310 | Classroom | 310 | 20 |  |  | 275 | 6 | 6 | House Fan | 8 | 2200 | 8.4545 | 1 | 8.4545 | 2 | 8.4545 | 2
- | Auditrium | 3031 | 202 |  |  | 3055 | 69 | 69 | House Fan | 8 | 24440 | 7.4411 | 1.062 | 7.9027 | 2 | 7.9027 | 2
- | Boys Bathroom | 300 | 20 |  |  | 114 | 2 | 2 | N/A | 8 | 912 | 19.7368 | 1 | 19.7368 | 3 | 19.7368 | 3
- | Cafeteria | 375 | 25 |  |  | 990 | 22 | 22 | House Fan | 8 | 7920 | 2.8409 | 1 | 2.8409 | 1 | 2.8409 | 1
- | Girls Bathroom | 421 | 28 |  |  | 96 | 2 | 2 | N/A | 8 | 768 | 32.8906 | 1 | 32.8906 | 4 | 32.8906 | 4
- | Gym | 0 | 0 | Yes | 20 | 3219 | 73 | 73 | N/A | 8 | 25752 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Main Office | 0 | 0 | Yes | 20 | 330 | 7 | 7 | House Fan | 8 | 2640 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 288 | 6 | 6 | N/A | 8 | 2304 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office | 0 | 0 | Yes | 20 | 220 | 5 | 5 | House Fan | 8 | 1760 | 0 | 1 | 0 | 0 | 20 | 3
- | PTA Room | 900 | 60 |  |  | 1540 | 35 | 35 | House Fan | 8 | 12320 | 4.3831 | 1 | 4.3831 | 2 | 4.3831 | 2
- | Speech Room | 438 | 29 |  |  | 506 | 11 | 11 | House Fan | 8 | 4048 | 6.4921 | 1 | 6.4921 | 2 | 6.4921 | 2
- | Teachers Lounge | 0 | 0 |  |  | 330 | 7 | 0 | House Fan | 8 | 2640 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30
School: | Samuel Fels High School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
A100 | Classroom | 69 | 4 |  |  | 290 | 6 | 4 |  | 8 | 2320 | 1.7845 | 1 | 1.7845 | 1 | 1.7845 | 1
A103 | Classroom | 125 | 8 |  |  | 870 | 19 | 8 |  | 8 | 6960 | 1.0776 | 1 | 1.0776 | 1 | 1.0776 | 1
A105 | Classroom | 148 | 9 |  |  | 870 | 19 | 9 |  | 8 | 6960 | 1.2759 | 1 | 1.2759 | 1 | 1.2759 | 1
A106 | Classroom | 147 | 9 |  |  | 870 | 19 | 9 |  | 8 | 6960 | 1.2672 | 1 | 1.2672 | 1 | 1.2672 | 1
A107 | Classroom | 135 | 9 |  |  | 870 | 19 | 9 |  | 8 | 6960 | 1.1638 | 1 | 1.1638 | 1 | 1.1638 | 1
A108 | Classroom | 39 | 2 |  |  | 870 | 19 | 2 |  | 8 | 6960 | 0.33621 | 1 | 0.33621 | 0 | 0.33621 | 0
A109 | Classroom | 162 | 10 |  |  | 870 | 19 | 10 |  | 8 | 6960 | 1.3966 | 1 | 1.3966 | 1 | 1.3966 | 1
A110 | Classroom | 162 | 10 |  |  | 870 | 19 | 10 |  | 8 | 6960 | 1.3966 | 1 | 1.3966 | 1 | 1.3966 | 1
A111 | Classroom | 167 | 11 |  |  | 870 | 19 | 11 |  | 8 | 6960 | 1.4397 | 1 | 1.4397 | 1 | 1.4397 | 1
A113 | Classroom | 161 | 10 |  |  | 870 | 19 | 10 |  | 8 | 6960 | 1.3879 | 1 | 1.3879 | 1 | 1.3879 | 1
A114 | Classroom | 0 | 0 |  |  | 930 | 21 | 0 |  | 8 | 7440 | 0 | 1 | 0 | 0 | 0 | 0
A120 | Office | 125 | 8 |  |  | 144 | 3 | 3 |  | 8 | 1152 | 6.5104 | 1 | 6.5104 | 2 | 6.5104 | 2
A123 | Classroom | 298 | 19 |  |  | 900 | 20 | 19 |  | 8 | 7200 | 2.4833 | 1 | 2.4833 | 1 | 2.4833 | 1
A124 | Classroom | 345 | 23 |  |  | 900 | 20 | 20 |  | 8 | 7200 | 2.875 | 1 | 2.875 | 1 | 2.875 | 1
A125 | Classroom | 376 | 25 |  |  | 900 | 20 | 20 |  | 8 | 7200 | 3.1333 | 1 | 3.1333 | 1 | 3.1333 | 1
A126 | Classroom | 266 | 17 |  |  | 900 | 20 | 17 |  | 8 | 7200 | 2.2167 | 1 | 2.2167 | 1 | 2.2167 | 1
A130 | Classroom | 697 | 46 |  |  | 900 | 20 | 20 |  | 8 | 7200 | 5.8083 | 1 | 5.8083 | 2 | 5.8083 | 2
A131 | Classroom | 155 | 10 |  |  | 900 | 20 | 10 |  | 8 | 7200 | 1.2917 | 1 | 1.2917 | 1 | 1.2917 | 1
A132 | Classroom | 291 | 19 |  |  | 960 | 21 | 19 |  | 8 | 7680 | 2.2734 | 1 | 2.2734 | 1 | 2.2734 | 1
A135 | Classroom | 645 | 43 |  |  | 960 | 21 | 21 |  | 8 | 7680 | 5.0391 | 1 | 5.0391 | 2 | 5.0391 | 2
A136 | Classroom | 162 | 10 |  |  | 960 | 21 | 10 |  | 8 | 7680 | 1.2656 | 1 | 1.2656 | 1 | 1.2656 | 1
A137 | Classroom | 229 | 15 |  |  | 1320 | 30 | 15 |  | 8 | 10560 | 1.3011 | 1 | 1.3011 | 1 | 1.3011 | 1
A138 | Classroom | 963 | 64 |  |  | 1376 | 31 | 31 |  | 8 | 11008 | 5.2489 | 1 | 5.2489 | 2 | 5.2489 | 2
A139 | Classroom | 161 | 10 |  |  | 1376 | 31 | 10 |  | 8 | 11008 | 0.87754 | 1 | 0.87754 | 0 | 0.87754 | 0
A140 | Classroom | 1027 | 68 |  |  | 1376 | 31 | 31 |  | 8 | 11008 | 5.5977 | 1 | 5.5977 | 2 | 5.5977 | 2
A142 | Classroom | 1338 | 89 |  |  | 1271 | 28 | 28 |  | 8 | 10168 | 7.8954 | 1 | 7.8954 | 2 | 7.8954 | 2
A143 | Classroom | 964 | 64 |  |  | 1505 | 34 | 34 |  | 8 | 12040 | 4.804 | 1 | 4.804 | 2 | 4.804 | 2
A144 | Classroom | 937 | 62 |  |  | 1394 | 31 | 31 |  | 8 | 11152 | 5.0412 | 1 | 5.0412 | 2 | 5.0412 | 2
A148 | Hallway | 193 | 12 |  |  |  | 0 | 0
A150 | Hallway | 255 | 17 |  |  |  | 0 | 0
A152 | Hallway | 180 | 12 |  |  |  | 0 | 0
A200 | Classroom | 451 | 30 |  |  | 290 | 6 | 6 |  | 8 | 2320 | 11.6638 | 1 | 11.6638 | 3 | 11.6638 | 3
A203 | Classroom | 252 | 16 |  |  | 870 | 19 | 16 |  | 8 | 6960 | 2.1724 | 1 | 2.1724 | 1 | 2.1724 | 1
A205 | Classroom | 332 | 22 |  |  | 870 | 19 | 19 |  | 8 | 6960 | 2.8621 | 1 | 2.8621 | 1 | 2.8621 | 1
A206 | Classroom | 911 | 60 |  |  | 870 | 19 | 19 |  | 8 | 6960 | 7.8534 | 1 | 7.8534 | 2 | 7.8534 | 2
A207 | Classroom | 536 | 35 |  |  | 870 | 19 | 19 |  | 8 | 6960 | 4.6207 | 1 | 4.6207 | 2 | 4.6207 | 2
A208 | Classroom | 1475 | 98 |  |  | 870 | 19 | 19 |  | 8 | 6960 | 12.7155 | 1 | 12.7155 | 3 | 12.7155 | 3
A209 | Classroom | 620 | 41 |  |  | 870 | 19 | 19 |  | 8 | 6960 | 5.3448 | 1 | 5.3448 | 2 | 5.3448 | 2
A210 | Classroom | 1060 | 70 |  |  | 870 | 19 | 19 |  | 8 | 6960 | 9.1379 | 1 | 9.1379 | 2 | 9.1379 | 2
A211 | Classroom | 1246 | 83 |  |  | 870 | 19 | 19 |  | 8 | 6960 | 10.7414 | 1 | 10.7414 | 3 | 10.7414 | 3
A212 | Classroom | 1262 | 84 |  |  | 1271 | 28 | 28 |  | 8 | 10168 | 7.4469 | 1 | 7.4469 | 2 | 7.4469 | 2
A213 | Classroom | 879 | 58 |  |  | 961 | 21 | 21 |  | 8 | 7688 | 6.86 | 1 | 6.86 | 2 | 6.86 | 2
A214 | Classroom | 667 | 44 |  |  | 961 | 21 | 21 |  | 8 | 7688 | 5.2055 | 1 | 5.2055 | 2 | 5.2055 | 2
A220 | Office | 7 | 0 |  |  | 144 | 3 | 0 |  | 8 | 1152 | 0.36458 | 1 | 0.36458 | 0 | 0.36458 | 0
A223 | Classroom | 486 | 32 |  |  | 1860 | 42 | 32 |  | 8 | 14880 | 1.9597 | 1 | 1.9597 | 1 | 1.9597 | 1
A225 | Classroom | 90 | 6 |  |  | 160 | 3 | 3 |  | 8 | 1280 | 4.2188 | 1 | 4.2188 | 2 | 4.2188 | 2
A226 | Classroom | 323 | 21 |  |  | 900 | 20 | 20 |  | 8 | 7200 | 2.6917 | 1 | 2.6917 | 1 | 2.6917 | 1
A227 | Classroom | 830 | 55 |  |  | 960 | 21 | 21 |  | 8 | 7680 | 6.4844 | 1 | 6.4844 | 2 | 6.4844 | 2
A231 | Classroom | 260 | 17 |  |  | 1320 | 30 | 17 |  | 8 | 10560 | 1.4773 | 1 | 1.4773 | 1 | 1.4773 | 1
A236 | Classroom | 8 | 0 |  |  | 120 | 2 | 0 |  | 8 | 960 | 0.5 | 1 | 0.5 | 0 | 0.5 | 0
A237 | Classroom | 9 | 0 |  |  | 104 | 2 | 0 |  | 8 | 832 | 0.64904 | 1 | 0.64904 | 0 | 0.64904 | 0
A238 | Classroom | 207 | 13 |  |  | 1680 | 38 | 13 |  | 8 | 13440 | 0.92411 | 1 | 0.92411 | 0 | 0.92411 | 0
A239 | Classroom | 1272 | 84 |  |  | 1376 | 31 | 31 |  | 8 | 11008 | 6.9331 | 1 | 6.9331 | 2 | 6.9331 | 2
A240 | Classroom | 249 | 16 |  |  | 224 | 5 | 5 |  | 8 | 1792 | 8.3371 | 1 | 8.3371 | 2 | 8.3371 | 2
A241 | Classroom | 1797 | 119 |  |  | 1364 | 31 | 31 |  | 8 | 10912 | 9.8809 | 1 | 9.8809 | 2 | 9.8809 | 2
A242 | Classroom | 1960 | 130 |  |  | 1320 | 30 | 30 |  | 8 | 10560 | 11.1364 | 1 | 11.1364 | 3 | 11.1364 | 3
A243 | Classroom | 960 | 64 |  |  | 1320 | 30 | 30 |  | 8 | 10560 | 5.4545 | 1 | 5.4545 | 2 | 5.4545 | 2
A244 | Classroom | 1222 | 81 |  |  | 1505 | 34 | 34 |  | 8 | 12040 | 6.0897 | 1 | 6.0897 | 2 | 6.0897 | 2
A245 | Classroom | 695 | 46 |  |  | 1394 | 31 | 31 |  | 8 | 11152 | 3.7392 | 1 | 3.7392 | 1 | 3.7392 | 1
A248 | Hallway | 0 | 0 |  |  |  | 0 | 0
A250 | Hallway | 297 | 19 |  |  |  | 0 | 0
A252 | Hallway | 566 | 37 |  |  |  | 0 | 0
A255 | Classroom | 0 | 0 |  |  | 120 | 2 | 0 |  | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
B100 | Classroom | 0 | 0 |  |  | 930 | 21 | 0 |  | 8 | 7440 | 0 | 1 | 0 | 0 | 0 | 0
B102 | Classroom | 0 | 0 |  |  | 961 | 21 | 0 |  | 8 | 7688 | 0 | 1 | 0 | 0 | 0 | 0
B103 | Classroom | 0 | 0 |  |  | 1023 | 23 | 0 |  | 8 | 8184 | 0 | 1 | 0 | 0 | 0 | 0
B105 | Classroom | 0 | 0 |  |  | 1311 | 29 | 0 |  | 8 | 10488 | 0 | 1 | 0 | 0 | 0 | 0
B106 | Classroom | 0 | 0 |  |  | 280 | 6 | 0 |  | 8 | 2240 | 0 | 1 | 0 | 0 | 0 | 0
B107 | Classroom | 0 | 0 |  |  | 1265 | 28 | 0 |  | 8 | 10120 | 0 | 1 | 0 | 0 | 0 | 0
B108 | Classroom | 0 | 0 |  |  | 961 | 21 | 0 |  | 8 | 7688 | 0 | 1 | 0 | 0 | 0 | 0
B109 | Classroom | 0 | 0 |  |  | 961 | 21 | 0 |  | 8 | 7688 | 0 | 1 | 0 | 0 | 0 | 0
B117 | Classroom | 0 | 0 |  |  | 576 | 13 | 0 |  | 8 | 4608 | 0 | 1 | 0 | 0 | 0 | 0
B118 | Classroom | 0 | 0 |  |  | 961 | 21 | 0 |  | 8 | 7688 | 0 | 1 | 0 | 0 | 0 | 0
B120 | Classroom | 0 | 0 |  |  | 208 | 4 | 0 |  | 8 | 1664 | 0 | 1 | 0 | 0 | 0 | 0
B123 | Classroom | 0 | 0 |  |  | 990 | 22 | 0 |  | 8 | 7920 | 0 | 1 | 0 | 0 | 0 | 0
B124 | Classroom | 0 | 0 |  |  | 990 | 22 | 0 |  | 8 | 7920 | 0 | 1 | 0 | 0 | 0 | 0
B125 | Hallway | 0 | 0 |  |  |  | 0 | 0
B126 | Hallway | 0 | 0 |  |  |  | 0 | 0
B127 | Hallway | 0 | 0 |  |  |  | 0 | 0
B128 | Hallway | 0 | 0 |  |  |  | 0 | 0
B200 | Classroom | 0 | 0 |  |  | 930 | 21 | 0 |  | 8 | 7440 | 0 | 1 | 0 | 0 | 0 | 0
B201 | Classroom | 0 | 0 |  |  | 1316 | 29 | 0 |  | 8 | 10528 | 0 | 1 | 0 | 0 | 0 | 0
B201B | Classroom | 0 | 0 |  |  | 224 | 5 | 0 |  | 8 | 1792 | 0 | 1 | 0 | 0 | 0 | 0
B202 | Classroom | 0 | 0 |  |  | 961 | 21 | 0 |  | 8 | 7688 | 0 | 1 | 0 | 0 | 0 | 0
B203 | Classroom | 0 | 0 |  |  | 1023 | 23 | 0 |  | 8 | 8184 | 0 | 1 | 0 | 0 | 0 | 0
B204 | Classroom | 0 | 0 |  |  | 1311 | 29 | 0 |  | 8 | 10488 | 0 | 1 | 0 | 0 | 0 | 0
B205 | Classroom | 0 | 0 |  |  | 1265 | 28 | 0 |  | 8 | 10120 | 0 | 1 | 0 | 0 | 0 | 0
B208 | Classroom | 0 | 0 |  |  | 961 | 21 | 0 |  | 8 | 7688 | 0 | 1 | 0 | 0 | 0 | 0
B209 | Classroom | 0 | 0 |  |  | 961 | 21 | 0 |  | 8 | 7688 | 0 | 1 | 0 | 0 | 0 | 0
B210 | Classroom | 0 | 0 |  |  | 144 | 3 | 0 |  | 8 | 1152 | 0 | 1 | 0 | 0 | 0 | 0
B218 | Classroom | 0 | 0 |  |  | 990 | 22 | 0 |  | 8 | 7920 | 0 | 1 | 0 | 0 | 0 | 0
B219 | Classroom | 0 | 0 |  |  | 990 | 22 | 0 |  | 8 | 7920 | 0 | 1 | 0 | 0 | 0 | 0
B222 | Hallway | 0 | 0 |  |  |  | 0 | 0
B223 | Hallway | 0 | 0 |  |  |  | 0 | 0
B224 | Hallway | 0 | 0 |  |  |  | 0 | 0
B225 | Hallway | 0 | 0 |  |  |  | 0 | 0
C101 | Front of house | 160 | 10 |  |  | 384 | 8 | 8 |  | 8 | 3072 | 3.125 | 1 | 3.125 | 1 | 3.125 | 1
C103 | Auditorium | 12689 | 845 |  |  | 9310 | 211 | 211 |  | 8 | 74480 | 10.2221 | 1.4912 | 15.2427 | 3 | 15.2427 | 3
C105 | Stage | 770 | 51 |  |  | 3400 | 77 | 51 |  | 8 | 27200 | 1.6985 | 1.062 | 1.8039 | 1 | 1.8039 | 1
C106 | Classroom | 0 | 0 |  |  | 1302 | 29 | 0 |  | 8 | 10416 | 0 | 1 | 0 | 0 | 0 | 0
C107 | Backstage | 59 | 3 |  |  | 870 | 19 | 3 |  | 8 | 6960 | 0.50862 | 1 | 0.50862 | 0 | 0.50862 | 0
C108 | Classroom | 39 | 2 |  |  | 870 | 19 | 2 |  | 8 | 6960 | 0.33621 | 1 | 0.33621 | 0 | 0.33621 | 0
C109 | Classroom | 77 | 5 |  |  | 870 | 19 | 5 |  | 8 | 6960 | 0.66379 | 1 | 0.66379 | 0 | 0.66379 | 0
C110 | Classroom | 89 | 5 |  |  | 870 | 19 | 5 |  | 8 | 6960 | 0.76724 | 1 | 0.76724 | 0 | 0.76724 | 0
C111 | Classroom | 576 | 38 |  |  | 870 | 19 | 19 |  | 8 | 6960 | 4.9655 | 1 | 4.9655 | 2 | 4.9655 | 2
C112 | Classroom | 112 | 7 |  |  | 870 | 19 | 7 |  | 8 | 6960 | 0.96552 | 1 | 0.96552 | 0 | 0.96552 | 0
C113 | Classroom | 1414 | 94 |  |  | 2016 | 45 | 45 |  | 8 | 16128 | 5.2604 | 1 | 5.2604 | 2 | 5.2604 | 2
C114 | Classroom | 20 | 1 |  |  | 870 | 19 | 1 |  | 8 | 6960 | 0.17241 | 1 | 0.17241 | 0 | 0.17241 | 0
C115 | Classroom | 18 | 1 |  |  | 840 | 19 | 1 |  | 8 | 6720 | 0.16071 | 1 | 0.16071 | 0 | 0.16071 | 0
C116 | Classroom | 20 | 1 |  |  | 840 | 19 | 1 |  | 8 | 6720 | 0.17857 | 1 | 0.17857 | 0 | 0.17857 | 0
C117 | Classroom | 18 | 1 |  |  | 840 | 19 | 1 |  | 8 | 6720 | 0.16071 | 1 | 0.16071 | 0 | 0.16071 | 0
C118 | Classroom | 210 | 14 |  |  | 840 | 19 | 14 |  | 8 | 6720 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
C119 | Classroom | 168 | 11 |  |  | 840 | 19 | 11 |  | 8 | 6720 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1
C121 | Classroom | 0 | 0 |  |  | 840 | 19 | 0 |  | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
D104 | Locker room | 4 | 0 |  |  | 1680 | 38 | 0 |  | 8 | 13440 | 0.017857 | 1 | 0.017857 | 0 | 0.017857 | 0
D105 | Locker room | 5 | 0 |  |  | 1680 | 38 | 0 |  | 8 | 13440 | 0.022321 | 1 | 0.022321 | 0 | 0.022321 | 0
D106 | Office | 25 | 1 |  |  | 120 | 2 | 1 |  | 8 | 960 | 1.5625 | 1 | 1.5625 | 1 | 1.5625 | 1
D109 | Locker room | 12 | 0 |  |  | 522 | 11 | 0 |  | 8 | 4176 | 0.17241 | 1 | 0.17241 | 0 | 0.17241 | 0
D111 | Locker room | 8 | 0 |  |  | 522 | 11 | 0 |  | 8 | 4176 | 0.11494 | 1 | 0.11494 | 0 | 0.11494 | 0
D112 | Office | 22 | 1 |  |  | 240 | 5 | 1 |  | 8 | 1920 | 0.6875 | 1 | 0.6875 | 0 | 0.6875 | 0
D113 | Office | 26 | 1 |  |  | 240 | 5 | 1 |  | 8 | 1920 | 0.8125 | 1 | 0.8125 | 0 | 0.8125 | 0
D114 | Locker room | 39 | 2 |  |  | 720 | 16 | 2 |  | 8 | 5760 | 0.40625 | 1 | 0.40625 | 0 | 0.40625 | 0
D115 | Office | 0 | 0 |  |  | 260 | 5 | 0 |  | 8 | 2080 | 0 | 1 | 0 | 0 | 0 | 0
D116 | Weight room | 181 | 12 |  |  | 1392 | 31 | 12 |  | 8 | 11136 | 0.97522 | 1 | 0.97522 | 0 | 0.97522 | 0
D119 | Classroom | 91 | 6 |  |  | 1240 | 28 | 6 |  | 8 | 9920 | 0.5504 | 1 | 0.5504 | 0 | 0.5504 | 0
D126 | Vestibule | 42 | 2 |  |  |  | 0 | 0
D128 | Hallway | 249 | 16 |  |  |  | 0 | 0
E100A | Library | 274 | 18 |  |  | 9200 | 209 | 18 |  | 8 | 73600 | 0.22337 | 1.4912 | 0.33308 | 0 | 0.33308 | 0
E100B | Office | 28 | 1 |  |  | 225 | 5 | 1 |  | 8 | 1800 | 0.93333 | 1 | 0.93333 | 0 | 0.93333 | 0
E101 | Classroom | 17 | 1 |  |  | 992 | 22 | 1 |  | 8 | 7936 | 0.12853 | 1 | 0.12853 | 0 | 0.12853 | 0
E102 | Office | 12 | 0 |  |  | 225 | 5 | 0 |  | 8 | 1800 | 0.4 | 1 | 0.4 | 0 | 0.4 | 0
E103 | Office | 14 | 0 |  |  | 225 | 5 | 0 |  | 8 | 1800 | 0.46667 | 1 | 0.46667 | 0 | 0.46667 | 0
E104 | Office | 0 | 0 |  |  | 150 | 3 | 0 |  | 8 | 1200 | 0 | 1 | 0 | 0 | 0 | 0
E105A | Storage | 6 | 0 |  |  |  | 0 | 0
E105B | Storage | 8 | 0 |  |  |  | 0 | 0
E107 | Office | 52 | 3 |  |  | 286 | 6 | 3 |  | 8 | 2288 | 1.3636 | 1 | 1.3636 | 1 | 1.3636 | 1
E111 | Office | 0 | 0 |  |  | 368 | 8 | 0 |  | 8 | 2944 | 0 | 1 | 0 | 0 | 0 | 0
E112 | Hallway | 0 | 0 |  |  |  | 0 | 0
E113 | Office | 0 | 0 |  |  | 132 | 3 | 0 |  | 8 | 1056 | 0 | 1 | 0 | 0 | 0 | 0
E114 | Office | 0 | 0 |  |  | 84 | 1 | 0 |  | 8 | 672 | 0 | 1 | 0 | 0 | 0 | 0
E115 | Office | 0 | 0 |  |  | 180 | 4 | 0 |  | 8 | 1440 | 0 | 1 | 0 | 0 | 0 | 0
E116 | Office | 0 | 0 |  |  | 72 | 1 | 0 |  | 8 | 576 | 0 | 1 | 0 | 0 | 0 | 0
E117 | Office | 0 | 0 |  |  | 120 | 2 | 0 |  | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
E118 | Hallway | 0 | 0 |  |  |  | 0 | 0
E119 | Office | 0 | 0 |  |  | 400 | 9 | 0 |  | 8 | 3200 | 0 | 1 | 0 | 0 | 0 | 0
E120 | Office | 0 | 0 |  |  | 180 | 4 | 0 |  | 8 | 1440 | 0 | 1 | 0 | 0 | 0 | 0
E121 | Office | 0 | 0 |  |  | 180 | 4 | 0 |  | 8 | 1440 | 0 | 1 | 0 | 0 | 0 | 0
E123 | Office | 0 | 0 |  |  | 220 | 5 | 0 |  | 8 | 1760 | 0 | 1 | 0 | 0 | 0 | 0
E124 | Office | 0 | 0 |  |  | 220 | 5 | 0 |  | 8 | 1760 | 0 | 1 | 0 | 0 | 0 | 0
E125 | Office | 0 | 0 |  |  | 150 | 3 | 0 |  | 8 | 1200 | 0 | 1 | 0 | 0 | 0 | 0
E126 | Office | 0 | 0 |  |  | 216 | 4 | 0 |  | 8 | 1728 | 0 | 1 | 0 | 0 | 0 | 0
E127 | Office | 0 | 0 |  |  | 90 | 2 | 0 |  | 8 | 720 | 0 | 1 | 0 | 0 | 0 | 0
E128 | Office | 0 | 0 |  |  | 150 | 3 | 0 |  | 8 | 1200 | 0 | 1 | 0 | 0 | 0 | 0
E129 | Office | 0 | 0 |  |  | 216 | 4 | 0 |  | 8 | 1728 | 0 | 1 | 0 | 0 | 0 | 0
E130 | Office | 0 | 0 |  |  | 285 | 6 | 0 |  | 8 | 2280 | 0 | 1 | 0 | 0 | 0 | 0
E131 | Office | 0 | 0 |  |  | 195 | 4 | 0 |  | 8 | 1560 | 0 | 1 | 0 | 0 | 0 | 0
E132 | Office | 0 | 0 |  |  | 195 | 4 | 0 |  | 8 | 1560 | 0 | 1 | 0 | 0 | 0 | 0
E133 | Office | 0 | 0 |  |  | 315 | 7 | 0 |  | 8 | 2520 | 0 | 1 | 0 | 0 | 0 | 0
E134 | Office | 0 | 0 |  |  | 315 | 7 | 0 |  | 8 | 2520 | 0 | 1 | 0 | 0 | 0 | 0
E137 | Office | 0 | 0 |  |  | 420 | 9 | 0 |  | 8 | 3360 | 0 | 1 | 0 | 0 | 0 | 0
E139 | Office | 0 | 0 |  |  | 264 | 6 | 0 |  | 8 | 2112 | 0 | 1 | 0 | 0 | 0 | 0
E144 | Server room | 0 | 0 |  |  | 368 | 8 | 0 |  | 8 | 2944 | 0 | 1 | 0 | 0 | 0 | 0
E146 | Hallway | 0 | 0 |  |  |  | 0 | 0
E147 | Hallway | 0 | 0 |  |  |  | 0 | 0
E148 | Hallway | 0 | 0 |  |  |  | 0 | 0
E149 | Vestibule | 0 | 0 |  |  |  | 0 | 0
E150 | Vestibule | 0 | 0 |  |  |  | 0 | 0
E151 | Hallway | 0 | 0 |  |  |  | 0 | 0
E152 | Hallway | 0 | 0 |  |  |  | 0 | 0
E157 | Hallway | 0 | 0 |  |  |  | 0 | 0
E201 | Office | 0 | 0 |  |  | 126 | 2 | 0 |  | 8 | 1008 | 0 | 1 | 0 | 0 | 0 | 0
E202 | Office | 0 | 0 |  |  | 126 | 2 | 0 |  | 8 | 1008 | 0 | 1 | 0 | 0 | 0 | 0
E203B | Office | 0 | 0 |  |  | 266 | 6 | 0 |  | 8 | 2128 | 0 | 1 | 0 | 0 | 0 | 0
E204 | Office | 0 | 0 |  |  | 126 | 2 | 0 |  | 8 | 1008 | 0 | 1 | 0 | 0 | 0 | 0
E205 | Office | 0 | 0 |  |  | 126 | 2 | 0 |  | 8 | 1008 | 0 | 1 | 0 | 0 | 0 | 0
E209 | Office | 0 | 0 |  |  | 1040 | 23 | 0 |  | 8 | 8320 | 0 | 1 | 0 | 0 | 0 | 0
E210 | Hallway | 0 | 0 |  |  |  | 0 | 0
F100 | Cafeteria | 8136 | 542 |  |  | 8448 | 192 | 192 |  | 8 | 67584 | 7.223 | 1.4912 | 10.7706 | 3 | 10.7706 | 3
F101 | Kitchen | 1521 | 101 |  |  | 1636 | 37 | 37 |  | 8 | 13088 | 6.9728 | 1 | 6.9728 | 2 | 6.9728 | 2
F104 | Kitchen | 81 | 5 |  |  | 230 | 5 | 5 |  | 8 | 1840 | 2.6413 | 1 | 2.6413 | 1 | 2.6413 | 1
F106 | Kitchen | 99 | 6 |  |  | 306 | 6 | 6 |  | 8 | 2448 | 2.4265 | 1 | 2.4265 | 1 | 2.4265 | 1
F107 | Kitchen | 0 | 0 |  |  | 401 | 9 | 0 |  | 8 | 3208 | 0 | 1 | 0 | 0 | 0 | 0
F108 | Kitchen | 199 | 13 |  |  | 836 | 19 | 13 |  | 8 | 6688 | 1.7853 | 1 | 1.7853 | 1 | 1.7853 | 1
F109 | Maintenance | 59 | 3 |  |  | 686 | 15 | 3 |  | 8 | 5488 | 0.64504 | 1 | 0.64504 | 0 | 0.64504 | 0
F110 | Maintenance | 40 | 2 |  |  | 256 | 5 | 2 |  | 8 | 2048 | 1.1719 | 1 | 1.1719 | 1 | 1.1719 | 1
F111 | Maintenance | 69 | 4 |  |  | 162 | 3 | 3 |  | 8 | 1296 | 3.1944 | 1 | 3.1944 | 1 | 3.1944 | 1
F112 | Maintenance | 89 | 5 |  |  | 340 | 7 | 5 |  | 8 | 2720 | 1.9632 | 1 | 1.9632 | 1 | 1.9632 | 1
F116 | Kitchen | 0 | 0 |  |  | 1636 | 37 | 0 |  | 8 | 13088 | 0 | 1 | 0 | 0 | 0 | 0
F119 | Engineer's office | 135 | 9 |  |  | 176 | 4 | 4 |  | 8 | 1408 | 5.7528 | 1 | 5.7528 | 2 | 5.7528 | 2
F120 | Hallway | 149 | 9 |  |  |  | 0 | 0
F121 | Hallway | 1306 | 87 |  |  |  | 0 | 0
- | Gym | 2098 | 139 |  |  | 13184 | 299 | 139 |  | 8 | 105472 | 1.1935 | 2.3523 | 2.8075 | 1 | 2.8075 | 1
- | Office | 0 | 0 |  |  | 120 | 2 | 0 |  | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
- | Storage | 0 | 0 |  |  |  | 0 | 0
- | Pool | 5277 | 351 |  |  | 6426 | 146 | 146 |  | 8 | 51408 | 6.159 | 1.4912 | 9.184 | 2 | 9.184 | 2
- | Principal Office | 0 | 0 |  |  | 288 | 6 | 0 |  | 8 | 2304 | 0 | 1 | 0 | 0 | 0 | 0
- | Stage | 3751 | 250 |  |  | 3400 | 77 | 77 |  | 8 | 27200 | 8.2743 | 1.062 | 8.7876 | 2 | 8.7876 | 2
Sheet Last Modified: | 2021-04-06
School: | Feltonville Arts & Sciences Middle School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
104 | Classroom | 256 | 17 |  |  | 775 | 17 | 17 |  | 8 | 6200 | 2.4774 | 1 | 2.4774 | 1 | 2.4774 | 1
105 | Classroom | 614 | 40 |  |  | 810 | 18 | 18 |  | 8 | 6480 | 5.6852 | 1 | 5.6852 | 2 | 5.6852 | 2
106 | Classroom | 599 | 39 |  |  | 802 | 18 | 18 |  | 8 | 6416 | 5.6016 | 1 | 5.6016 | 2 | 5.6016 | 2
107 | Classroom | 428 | 28 |  |  | 804 | 18 | 18 |  | 8 | 6432 | 3.9925 | 1 | 3.9925 | 1 | 3.9925 | 1
108 | Classroom | 352 | 23 |  |  | 802 | 18 | 18 |  | 8 | 6416 | 3.2918 | 1 | 3.2918 | 1 | 3.2918 | 1
109 | Classroom | 699 | 46 |  |  | 791 | 17 | 17 |  | 8 | 6328 | 6.6277 | 1 | 6.6277 | 2 | 6.6277 | 2
110 | Classroom | 311 | 20 |  |  | 838 | 19 | 19 |  | 8 | 6704 | 2.7834 | 1 | 2.7834 | 1 | 2.7834 | 1
111 | Classroom | 232 | 15 |  |  | 953 | 21 | 15 |  | 8 | 7624 | 1.8258 | 1 | 1.8258 | 1 | 1.8258 | 1
112 | Classroom | 311 | 20 |  |  | 633 | 14 | 14 |  | 8 | 5064 | 3.6848 | 1 | 3.6848 | 1 | 3.6848 | 1
205 | Classroom | 455 | 30 |  |  | 774 | 17 | 17 |  | 8 | 6192 | 4.4089 | 1 | 4.4089 | 2 | 4.4089 | 2
206 | Classroom | 398 | 26 |  |  | 759 | 17 | 17 |  | 8 | 6072 | 3.9328 | 1 | 3.9328 | 1 | 3.9328 | 1
207 | Classroom | 352 | 23 |  |  | 749 | 17 | 17 |  | 8 | 5992 | 3.5247 | 1 | 3.5247 | 1 | 3.5247 | 1
208 | Classroom | 313 | 20 |  |  | 812 | 18 | 18 |  | 8 | 6496 | 2.891 | 1 | 2.891 | 1 | 2.891 | 1
210 | Classroom | 0 | 0 | Yes | 20 | 808 | 18 | 18 |  | 8 | 6464 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom | 650 | 43 |  |  | 765 | 17 | 17 |  | 8 | 6120 | 6.3725 | 1 | 6.3725 | 2 | 6.3725 | 2
212 | Classroom | 283 | 18 |  |  | 802 | 18 | 18 |  | 8 | 6416 | 2.6465 | 1 | 2.6465 | 1 | 2.6465 | 1
214 | Classroom | 605 | 40 |  |  | 632 | 14 | 14 |  | 8 | 5056 | 7.1796 | 1 | 7.1796 | 2 | 7.1796 | 2
301 | Classroom | 288 | 19 |  |  | 776 | 17 | 17 |  | 8 | 6208 | 2.7835 | 1 | 2.7835 | 1 | 2.7835 | 1
302 | Classroom | 297 | 19 |  |  | 760 | 17 | 17 |  | 8 | 6080 | 2.9309 | 1 | 2.9309 | 1 | 2.9309 | 1
303 | Classroom | 305 | 20 |  |  | 817 | 18 | 18 |  | 8 | 6536 | 2.7999 | 1 | 2.7999 | 1 | 2.7999 | 1
304 | Classroom | 700 | 46 |  |  | 811 | 18 | 18 |  | 8 | 6488 | 6.4735 | 1 | 6.4735 | 2 | 6.4735 | 2
305 | Classroom | 357 | 23 |  |  | 808 | 18 | 18 |  | 8 | 6464 | 3.3137 | 1 | 3.3137 | 1 | 3.3137 | 1
306 | Classroom | 490 | 32 |  |  | 783 | 17 | 17 |  | 8 | 6264 | 4.6935 | 1 | 4.6935 | 2 | 4.6935 | 2
307 | Classroom | 309 | 20 |  |  | 803 | 18 | 18 |  | 8 | 6424 | 2.8861 | 1 | 2.8861 | 1 | 2.8861 | 1
308 | Classroom | 211 | 14 | Yes | 20 | 809 | 18 | 18 |  | 8 | 6472 | 1.9561 | 1 | 1.9561 | 1 | 21.9561 | 3
309 | Classroom | 1419 | 94 |  |  | 2223 | 50 | 50 |  | 8 | 17784 | 4.7874 | 1 | 4.7874 | 2 | 4.7874 | 2
- | Basement | 4061 | 270 |  |  | 4615 | 104 | 104 |  | 8 | 36920 | 6.5997 | 1.062 | 7.0091 | 2 | 7.0091 | 2
- | Cafeteria, Kitchen, Faculty Room | 761 | 50 |  |  | 5110 | 116 | 50 |  | 8 | 40880 | 1.1169 | 1.062 | 1.1862 | 1 | 1.1862 | 1
- | Classroom above 214 | 403 | 26 |  |  | 631 | 14 | 14 |  | 8 | 5048 | 4.79 | 1 | 4.79 | 2 | 4.79 | 2
- | Classroom Art Lab Computer Lab | 315 | 21 | Yes | 20 | 1017 | 23 | 23 |  | 8 | 8136 | 2.323 | 1 | 2.323 | 1 | 22.323 | 3
- | Classroom Science Lab 1 | 345 | 23 |  |  | 993 | 22 | 22 |  | 8 | 7944 | 2.6057 | 1 | 2.6057 | 1 | 2.6057 | 1
- | Classroom Science Lab 2 3rd Floor | 344 | 22 |  |  | 989 | 22 | 22 |  | 8 | 7912 | 2.6087 | 1 | 2.6087 | 1 | 2.6087 | 1
- | Classroom Science Lab 2 Right | 455 | 30 |  |  | 989 | 22 | 22 |  | 8 | 7912 | 3.4505 | 1 | 3.4505 | 1 | 3.4505 | 1
- | Classroom Science Lab STEM Lab Left | 740 | 49 |  |  | 1631 | 37 | 37 |  | 8 | 13048 | 3.4028 | 1 | 3.4028 | 1 | 3.4028 | 1
- | Dean's Office 1st Floor | 31 | 2 | Yes | 20 | 170 | 3 | 3 |  | 8 | 1360 | 1.3676 | 1 | 1.3676 | 1 | 21.3676 | 3
- | Dean's Office 2nd Floor | 18 | 1 | Yes | 20 | 170 | 3 | 3 |  | 8 | 1360 | 0.79412 | 1 | 0.79412 | 0 | 20.7941 | 3
- | Dean's Office 3rd Floor | 38 | 2 | Yes | 20 | 168 | 3 | 3 |  | 8 | 1344 | 1.6964 | 1 | 1.6964 | 1 | 21.6964 | 3
- | Drama Room | 747 | 49 |  |  | 3095 | 70 | 49 |  | 8 | 24760 | 1.8102 | 1.062 | 1.9225 | 1 | 1.9225 | 1
- | First Floor | 5315 | 354 |  |  | 6974 | 158 | 158 |  | 8 | 55792 | 5.7159 | 1.4912 | 8.5233 | 2 | 8.5233 | 2
- | First Floor Multi-Purpose Room | 572 | 38 |  |  | 3095 | 70 | 38 |  | 8 | 24760 | 1.3861 | 1.062 | 1.4721 | 1 | 1.4721 | 1
- | Gym | 1186 | 79 |  |  | 5237 | 119 | 79 |  | 8 | 41896 | 1.6985 | 1.062 | 1.8039 | 1 | 1.8039 | 1
- | Health Room | 0 | 0 | Yes | 20 | 594 | 13 | 13 |  | 8 | 4752 | 0 | 1 | 0 | 0 | 20 | 3
- | Second Floor | 1094 | 72 |  |  | 4743 | 107 | 72 |  | 8 | 37944 | 1.7299 | 1.062 | 1.8372 | 1 | 1.8372 | 1
Sheet Last Modified: | 2021-04-29
School: | Feltonville Intermediate Elementary School
Vendor: | EMCOR | Exhaust Report
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | - |  | 0 | Yes | 20 | 462 | 10 | 10 |  | 8 | 3696 | 0 | 1 | 0 | 0 | 20 | 3
101 | - |  | 0 |  |  | 948 | 21 | 0 |  | 8 | 7584 | 0 | 1 | 0 | 0 | 0 | 0
101A | - |  | 0 |  |  | 127 | 2 | 0 |  | 8 | 1016 | 0 | 1 | 0 | 0 | 0 | 0
102 | - |  | 0 | Yes | 20 | 243 | 5 | 5 |  | 8 | 1944 | 0 | 1 | 0 | 0 | 20 | 3
103 | - |  | 0 |  |  | 101 | 2 | 0 |  | 8 | 808 | 0 | 1 | 0 | 0 | 0 | 0
103A | - |  | 0 |  |  | 125 | 2 | 0 |  | 8 | 1000 | 0 | 1 | 0 | 0 | 0 | 0
104 | - |  | 0 | Yes | 20 | 967 | 21 | 21 |  | 8 | 7736 | 0 | 1 | 0 | 0 | 20 | 3
106 | - |  | 0 | Yes | 20 | 1120 | 25 | 25 |  | 8 | 8960 | 0 | 1 | 0 | 0 | 20 | 3
107 | - |  | 0 |  |  | 213 | 4 | 0 |  | 8 | 1704 | 0 | 1 | 0 | 0 | 0 | 0
108 | Room |  | 0 | Yes | 20 | 1436 | 32 | 32 |  | 8 | 11488 | 0 | 1 | 0 | 0 | 20 | 3
109 | Room | 0 | 0 | Yes | 20 | 893 | 20 | 20 |  | 8 | 7144 | 0 | 1 | 0 | 0 | 20 | 3
110 | Room | 647 | 43 |  |  | 1479 | 33 | 33 |  | 8 | 11832 | 3.2809 | 1 | 3.2809 | 1 | 3.2809 | 1
112 | Room |  | 0 | Yes | 20 | 1415 | 32 | 32 |  | 8 | 11320 | 0 | 1 | 0 | 0 | 20 | 3
112A | - |  | 0 |  |  | 129 | 2 | 0 |  | 8 | 1032 | 0 | 1 | 0 | 0 | 0 | 0
113 | Room |  | 0 |  |  | 1200 | 27 | 0 |  | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
114 | - |  | 0 | Yes | 20 | 976 | 22 | 22 |  | 8 | 7808 | 0 | 1 | 0 | 0 | 20 | 3
116 | - |  | 0 |  |  | 1064 | 24 | 0 |  | 8 | 8512 | 0 | 1 | 0 | 0 | 0 | 0
118 | Gym Office | 0 | 0 |  |  | 1027 | 23 | 0 |  | 8 | 8216 | 0 | 1 | 0 | 0 | 0 | 0
153A | Small Office Inside M/O |  | 0 |  |  | 108 | 2 | 0 |  | 8 | 864 | 0 | 1 | 0 | 0 | 0 | 0
156B | Counselor #2 |  | 0 |  |  | 182 | 4 | 0 |  | 8 | 1456 | 0 | 1 | 0 | 0 | 0 | 0
157 | - |  | 0 |  |  | 108 | 2 | 0 |  | 8 | 864 | 0 | 1 | 0 | 0 | 0 | 0
200 | - |  | 0 |  |  | 478 | 10 | 0 |  | 8 | 3824 | 0 | 1 | 0 | 0 | 0 | 0
201 | - |  | 0 | Yes | 20 | 1071 | 24 | 24 |  | 8 | 8568 | 0 | 1 | 0 | 0 | 20 | 3
202 | - |  | 0 |  |  | 578 | 13 | 0 |  | 8 | 4624 | 0 | 1 | 0 | 0 | 0 | 0
202A | - |  | 0 |  |  | 179 | 4 | 0 |  | 8 | 1432 | 0 | 1 | 0 | 0 | 0 | 0
203 | - |  | 0 | Yes | 20 | 677 | 15 | 15 |  | 8 | 5416 | 0 | 1 | 0 | 0 | 20 | 3
203A | - |  | 0 |  |  | 436 | 9 | 0 |  | 8 | 3488 | 0 | 1 | 0 | 0 | 0 | 0
204 | - |  | 0 | Yes | 20 | 574 | 13 | 13 |  | 8 | 4592 | 0 | 1 | 0 | 0 | 20 | 3
205 | - |  | 0 |  |  | 829 | 18 | 0 |  | 8 | 6632 | 0 | 1 | 0 | 0 | 0 | 0
206 | - |  | 0 | Yes | 20 | 629 | 14 | 14 |  | 8 | 5032 | 0 | 1 | 0 | 0 | 20 | 3
206A | - |  | 0 |  |  | 220 | 5 | 0 |  | 8 | 1760 | 0 | 1 | 0 | 0 | 0 | 0
207 | - |  | 0 | Yes | 20 | 818 | 18 | 18 |  | 8 | 6544 | 0 | 1 | 0 | 0 | 20 | 3
207A | - |  | 0 |  |  | 126 | 2 | 0 |  | 8 | 1008 | 0 | 1 | 0 | 0 | 0 | 0
208 | - |  | 0 | Yes | 20 | 752 | 17 | 17 |  | 8 | 6016 | 0 | 1 | 0 | 0 | 20 | 3
208A | - |  | 0 |  |  | 113 | 2 | 0 |  | 8 | 904 | 0 | 1 | 0 | 0 | 0 | 0
209 | - |  | 0 | Yes | 20 | 788 | 17 | 17 |  | 8 | 6304 | 0 | 1 | 0 | 0 | 20 | 3
210 | - | 225 | 15 | Yes | 20 | 740 | 16 | 16 |  | 8 | 5920 | 2.2804 | 1 | 2.2804 | 1 | 22.2804 | 3
300 | - |  | 0 | Yes | 20 | 858 | 19 | 19 |  | 8 | 6864 | 0 | 1 | 0 | 0 | 20 | 3
301 | - |  | 0 | Yes | 20 | 491 | 11 | 11 |  | 8 | 3928 | 0 | 1 | 0 | 0 | 20 | 3
302 | - |  | 0 | Yes | 20 | 765 | 17 | 17 |  | 8 | 6120 | 0 | 1 | 0 | 0 | 20 | 3
303 | - |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
304 | - |  | 0 |  |  | 505 | 11 | 0 |  | 8 | 4040 | 0 | 1 | 0 | 0 | 0 | 0
305 | - |  | 0 | Yes | 20 | 626 | 14 | 14 |  | 8 | 5008 | 0 | 1 | 0 | 0 | 20 | 3
306 | - |  | 0 | Yes | 20 | 769 | 17 | 17 |  | 8 | 6152 | 0 | 1 | 0 | 0 | 20 | 3
307 | - |  | 0 | Yes | 20 | 1108 | 25 | 25 |  | 8 | 8864 | 0 | 1 | 0 | 0 | 20 | 3
307A | - |  | 0 |  |  | 73 | 1 | 0 |  | 8 | 584 | 0 | 1 | 0 | 0 | 0 | 0
307B | - |  | 0 |  |  | 127 | 2 | 0 |  | 8 | 1016 | 0 | 1 | 0 | 0 | 0 | 0
309 | - |  | 0 |  |  | 488 | 11 | 0 |  | 8 | 3904 | 0 | 1 | 0 | 0 | 0 | 0
309A | - |  | 0 |  |  | 135 | 3 | 0 |  | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
311 | - |  | 0 | Yes | 20 | 842 | 19 | 19 |  | 8 | 6736 | 0 | 1 | 0 | 0 | 20 | 3
313 | - |  | 0 | Yes | 20 | 662 | 15 | 15 |  | 8 | 5296 | 0 | 1 | 0 | 0 | 20 | 3
315 | - |  | 0 | Yes | 20 | 735 | 16 | 16 |  | 8 | 5880 | 0 | 1 | 0 | 0 | 20 | 3
- | Bradham Office |  | 0 |  |  | 141 | 3 | 0 |  | 8 | 1128 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria (2nd Floor) |  | 0 |  |  | 5423 | 123 | 0 |  | 8 | 43384 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Confrence Room |  | 0 |  |  | 216 | 4 | 0 |  | 8 | 1728 | 0 | 1 | 0 | 0 | 0 | 0
- | Counselor |  | 0 |  |  | 132 | 3 | 0 |  | 8 | 1056 | 0 | 1 | 0 | 0 | 0 | 0
- | Custodial Staff Room |  | 0 |  |  | 118 | 2 | 0 |  | 8 | 944 | 0 | 1 | 0 | 0 | 0 | 0
- | Food Service Locker Room |  | 0 |  |  | 83 | 1 | 0 |  | 8 | 664 | 0 | 1 | 0 | 0 | 0 | 0
- | Food Service Manager's Office |  | 0 |  |  | 56 | 1 | 0 |  | 8 | 448 | 0 | 1 | 0 | 0 | 0 | 0
- | Gymnasium |  | 0 |  |  | 4006 | 91 | 0 |  | 8 | 32048 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Kitchen |  | 0 |  |  | 954 | 21 | 0 |  | 8 | 7632 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office |  | 0 |  |  | 505 | 11 | 0 |  | 8 | 4040 | 0 | 1 | 0 | 0 | 0 | 0
- | MPR / Auditorium |  | 0 | Yes | 20 | 2669 | 60 | 60 |  | 8 | 21352 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Nurse |  | 0 |  |  | 191 | 4 | 0 |  | 8 | 1528 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurse Waiting Area |  | 0 |  |  | 159 | 3 | 0 |  | 8 | 1272 | 0 | 1 | 0 | 0 | 0 | 0
- | Principal's Office |  | 0 |  |  | 351 | 7 | 0 |  | 8 | 2808 | 0 | 1 | 0 | 0 | 0 | 0
- | Psychologist's Office |  | 0 |  |  | 66 | 1 | 0 |  | 8 | 528 | 0 | 1 | 0 | 0 | 0 | 0
- | Storage |  | 0 |  |  | 107 | 2 | 0 |  | 8 | 856 | 0 | 1 | 0 | 0 | 0 | 0
- | Storage Room #2 |  | 0 |  |  | 99 | 2 | 0 |  | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
- | Supply Closet |  | 0 |  |  | 126 | 2 | 0 |  | 8 | 1008 | 0 | 1 | 0 | 0 | 0 | 0
- | Teacher's Lounge |  | 0 |  |  | 226 | 5 | 0 |  | 8 | 1808 | 0 | 1 | 0 | 0 | 0 | 0
- | 1st Floor Lunchroom | 0 | 0 |  |  | 2677 | 60 | 0 |  | 8 | 21416 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Closet | 34 | 2 |  |  | 40 | 0 | 0 |  | 8 | 320 | 6.375 | 1 | 6.375 | 2 | 6.375 | 2
- | 3rd Floor Lunchroom |  | 0 |  |  | 4452 | 101 | 0 |  | 8 | 35616 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria Manager's Office | 75 | 5 |  |  | 55 | 1 | 1 |  | 8 | 440 | 10.2273 | 1 | 10.2273 | 3 | 10.2273 | 3
Sheet Last Modified: | 2021-02-23
School: | Feltonville Headstart | House Fan Abated
Vendor: | N/A
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Sheet Last Modified: | 2021-03-24
School: | Thomas Finletter Academics Plus Elementary School | House fan Abated
Vendor: | Devine |  | Devine Brothers Retest
School: | Finletter LSH
Vendor: | Chadwick
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Finletter Main Building
101 | Classroom | 535 | 35 |  |  | 1056 | 24 | 24 | House Fan | 8 | 8448 | 3.7997 | 1 | 3.7997 | 1 | 3.7997 | 1
102 | Classroom | 458 | 30 |  |  | 1056 | 24 | 24 | House Fan | 8 | 8448 | 3.2528 | 1 | 3.2528 | 1 | 3.2528 | 1
103 | Classroom | 621 | 41 |  |  | 1056 | 24 | 24 | House Fan | 8 | 8448 | 4.4105 | 1 | 4.4105 | 2 | 4.4105 | 2
104 | Classroom | 595 | 39 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 5.1293 | 1 | 5.1293 | 2 | 5.1293 | 2
105 | Classroom | 554 | 36 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 4.7759 | 1 | 4.7759 | 2 | 4.7759 | 2
106 | Classroom | 1227 | 81 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 10.5776 | 1 | 10.5776 | 3 | 10.5776 | 3
107 | Classroom | 980 | 65 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 8.4483 | 1 | 8.4483 | 2 | 8.4483 | 2
108 | Classroom | 817 | 54 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 6.8159 | 1 | 6.8159 | 2 | 6.8159 | 2
109 | Classroom | 876 | 58 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 7.3081 | 1 | 7.3081 | 2 | 7.3081 | 2
110 | Classroom | 535 | 35 |  |  | 928 | 21 | 21 | House Fan | 8 | 7424 | 4.3238 | 1 | 4.3238 | 2 | 4.3238 | 2
201 | Classroom | 477 | 31 |  |  | 1056 | 24 | 24 | House Fan | 8 | 8448 | 3.3878 | 1 | 3.3878 | 1 | 3.3878 | 1
202 | Classroom | 334 | 22 |  |  | 1056 | 24 | 22 | House Fan | 8 | 8448 | 2.3722 | 1 | 2.3722 | 1 | 2.3722 | 1
203 | Classroom | 411 | 27 |  |  | 1056 | 24 | 24 | House Fan | 8 | 8448 | 2.919 | 1 | 2.919 | 1 | 2.919 | 1
204 | Classroom | 916 | 61 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 7.8966 | 1 | 7.8966 | 2 | 7.8966 | 2
205 | Classroom | 1018 | 67 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 8.7759 | 1 | 8.7759 | 2 | 8.7759 | 2
206 | Classroom | 1222 | 81 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 10.5345 | 1 | 10.5345 | 3 | 10.5345 | 3
207 | Classroom | 1203 | 80 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 10.3707 | 1 | 10.3707 | 3 | 10.3707 | 3
208 | Classroom | 450 | 30 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 3.7542 | 1 | 3.7542 | 1 | 3.7542 | 1
209 | Classroom | 363 | 24 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 3.0284 | 1 | 3.0284 | 1 | 3.0284 | 1
210 | Classroom | 434 | 28 |  |  | 928 | 21 | 21 | House Fan | 8 | 7424 | 3.5075 | 1 | 3.5075 | 1 | 3.5075 | 1
211 | Classroom | 0 | 0 |  |  | 195 | 4 | 0 | N/A | 8 | 1560 | 0 | 1 | 0 | 0 | 0 | 0
212 | Classroom | 0 | 0 |  |  | 384 | 8 | 0 | N/A | 8 | 3072 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom | 278 | 18 |  |  | 1056 | 24 | 18 | House Fan | 8 | 8448 | 1.9744 | 1 | 1.9744 | 1 | 1.9744 | 1
302 | Classroom | 458 | 30 |  |  | 1056 | 24 | 24 | House Fan | 8 | 8448 | 3.2528 | 1 | 3.2528 | 1 | 3.2528 | 1
303 | Classroom | 125 | 8 |  |  | 1056 | 24 | 8 | House Fan | 8 | 8448 | 0.88778 | 1 | 0.88778 | 0 | 0.88778 | 0
304 | Classroom | 288 | 19 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 2.4828 | 1 | 2.4828 | 1 | 2.4828 | 1
305 | Classroom | 645 | 43 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 5.5603 | 1 | 5.5603 | 2 | 5.5603 | 2
306 | Classroom | 289 | 19 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 2.4914 | 1 | 2.4914 | 1 | 2.4914 | 1
307 | Classroom | 654 | 43 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 5.6379 | 1 | 5.6379 | 2 | 5.6379 | 2
308 | Classroom | 345 | 23 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 2.8782 | 1 | 2.8782 | 1 | 2.8782 | 1
309 | Classroom | 319 | 21 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 2.6613 | 1 | 2.6613 | 1 | 2.6613 | 1
310 | Classroom | 675 | 45 |  |  | 928 | 21 | 21 | House Fan | 8 | 7424 | 5.4553 | 1 | 5.4553 | 2 | 5.4553 | 2
311 | Classroom | 705 | 47 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 7.9273 | 1 | 7.9273 | 2 | 7.9273 | 2
312 | Classroom | 0 | 0 |  |  | 275 | 6 | 0 | N/A | 8 | 2200 | 0 | 1 | 0 | 0 | 0 | 0
402 | Health | 335 | 22 |  |  | 588 | 13 | 13 | House Fan | 8 | 4704 | 4.273 | 1 | 4.273 | 2 | 4.273 | 2
403 | Music Room | 491 | 32 |  |  | 990 | 22 | 22 | House Fan | 8 | 7920 | 3.7197 | 1 | 3.7197 | 1 | 3.7197 | 1
- | Annex Classroom | 65 | 4 |  |  | 960 | 21 | 4 | House Fan | 8 | 7680 | 0.50781 | 1 | 0.50781 | 0 | 0.50781 | 0
- | Art | 882 | 58 |  |  | 1421 | 32 | 32 | House Fan | 8 | 11368 | 4.6552 | 1 | 4.6552 | 2 | 4.6552 | 2
- | Auditorium | 3675 | 245 |  |  | 3431 | 77 | 77 | House Fan | 8 | 27448 | 8.0334 | 1.062 | 8.5317 | 2 | 8.5317 | 2
- | Health Classroom | 0 | 0 |  |  | 250 | 5 | 0 | House Fan | 8 | 2000 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym/Cafe |  | 0 | Yes | 20 | 3432 | 78 | 78 |  | 8 | 27456 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Main office | 0 | 0 | Yes | 20 | 322 | 7 | 7 | N/A | 8 | 2576 | 0 | 1 | 0 | 0 | 20 | 3
Finletter LSH
105 | Womens Staff Bathroom |  | 0 |  |  | 96 | 2 | 0 | AHU | 8 | 768 | 0 | 1 | 0 | 0 | 0 | 0
105 | Mens Staff Bathroom |  | 0 |  |  | 77 | 1 | 0 | AHU | 8 | 616 | 0 | 1 | 0 | 0 | 0 | 0
106 | Custodial | 57 | 3 |  |  | 36 | 0 | 0 | AHU | 8 | 288 | 11.875 | 1 | 11.875 | 3 | 11.875 | 3
111 | Lobby |  | 0 |  |  | 187 | 4 | 0 | AHU | 8 | 1496 | 0 | 1 | 0 | 0 | 0 | 0
112 | Office | 118 | 7 |  |  | 110 | 2 | 2 | AHU | 8 | 880 | 8.0455 | 1 | 8.0455 | 2 | 8.0455 | 2
113 | Office | 118 | 7 |  |  | 110 | 2 | 2 | AHU | 8 | 880 | 8.0455 | 1 | 8.0455 | 2 | 8.0455 | 2
114 | General Storage | 216 | 14 |  |  | 54 | 1 | 1 | AHU | 8 | 432 | 30 | 1 | 30 | 4 | 30 | 4
115 | Multipurpose Room | 2476 | 165 |  |  | 2166 | 49 | 49 | AHU | 8 | 17328 | 8.5734 | 1 | 8.5734 | 2 | 8.5734 | 2
116 | Corridor #2 |  | 0 |  |  | 120 | 2 | 0 | AHU | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
123 | Custodial Storage | 76 | 5 |  |  | 54 | 1 | 1 | AHU | 8 | 432 | 10.5556 | 1 | 10.5556 | 3 | 10.5556 | 3
125 | Academic Storage | 66 | 4 |  |  | 18 | 0 | 0 | AHU | 8 | 144 | 27.5 | 1 | 27.5 | 4 | 27.5 | 4
A | Classroom | 341 | 22 |  |  | 986 | 22 | 22 | AHU | 8 | 7888 | 2.5938 | 1 | 2.5938 | 1 | 2.5938 | 1
B | Classroom | 332 | 22 |  |  | 986 | 22 | 22 | AHU | 8 | 7888 | 2.5254 | 1 | 2.5254 | 1 | 2.5254 | 1
C | Classroom | 341 | 22 |  |  | 986 | 22 | 22 | AHU | 8 | 7888 | 2.5938 | 1 | 2.5938 | 1 | 2.5938 | 1
D | Classroom | 332 | 22 |  |  | 986 | 22 | 22 | AHU | 8 | 7888 | 2.5254 | 1 | 2.5254 | 1 | 2.5254 | 1
E | Classroom | 327 | 21 |  |  | 986 | 22 | 21 | AHU | 8 | 7888 | 2.4873 | 1 | 2.4873 | 1 | 2.4873 | 1
F | Classroom | 327 | 21 |  |  | 986 | 22 | 21 | AHU | 8 | 7888 | 2.4873 | 1 | 2.4873 | 1 | 2.4873 | 1
G | Classroom | 327 | 21 |  |  | 986 | 22 | 21 | AHU | 8 | 7888 | 2.4873 | 1 | 2.4873 | 1 | 2.4873 | 1
H | Classroom | 327 | 21 |  |  | 986 | 22 | 21 | AHU | 8 | 7888 | 2.4873 | 1 | 2.4873 | 1 | 2.4873 | 1
I | Classroom | 293 | 19 |  |  | 986 | 22 | 19 | AHU | 8 | 7888 | 2.2287 | 1 | 2.2287 | 1 | 2.2287 | 1
J | Classroom | 359 | 23 |  |  | 986 | 22 | 22 | AHU | 8 | 7888 | 2.7307 | 1 | 2.7307 | 1 | 2.7307 | 1
K | Classroom | 293 | 19 |  |  | 986 | 22 | 19 | AHU | 8 | 7888 | 2.2287 | 1 | 2.2287 | 1 | 2.2287 | 1
L | Classroom | 359 | 23 |  |  | 986 | 22 | 22 | AHU | 8 | 7888 | 2.7307 | 1 | 2.7307 | 1 | 2.7307 | 1
- | Custodial Office |  | 0 | Yes | 20 |  | 0 | 0 | AHU
- | Teachers Lounge |  | 0 | No |  | 288 | 6 | 0 | AHU | 8 | 2304 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-22
School: | Fitler Academic Plus Elementary School
Vendor: | Devine | Meehan | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
105 | Classroom | 707 | 47 |  |  | 1024 | 23 | 23 | House Fan | 8 | 8192 | 5.1782 | 1 | 5.1782 | 2 | 5.1782 | 2
106 | Classroom | 796 | 53 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 8.2917 | 1 | 8.2917 | 2 | 8.2917 | 2
107 | Classroom | 0 | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 834 | 55 |  |  | 1024 | 23 | 23 | House Fan | 8 | 8192 | 6.1084 | 1 | 6.1084 | 2 | 6.1084 | 2
202 | Classroom | 879 | 58 |  |  | 1024 | 23 | 23 | House Fan | 8 | 8192 | 6.438 | 1 | 6.438 | 2 | 6.438 | 2
203 | Classroom | 510 | 34 |  |  | 1024 | 23 | 23 | House Fan | 8 | 8192 | 3.7354 | 1 | 3.7354 | 1 | 3.7354 | 1
204 | Classroom | 951 | 63 |  |  | 1024 | 23 | 23 | House Fan | 8 | 8192 | 6.9653 | 1 | 6.9653 | 2 | 6.9653 | 2
205 | Classroom | 716 | 47 |  |  | 1024 | 23 | 23 | House Fan | 8 | 8192 | 5.2441 | 1 | 5.2441 | 2 | 5.2441 | 2
206 | Classroom | 668 | 44 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 6.9583 | 1 | 6.9583 | 2 | 6.9583 | 2
207 | Classroom | 78 | 5 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0.8125 | 1 | 0.8125 | 0 | 20.8125 | 3
301 | Classroom | 860 | 57 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 8.9583 | 1 | 8.9583 | 2 | 8.9583 | 2
302 | Classroom | 550 | 36 |  |  | 1024 | 23 | 23 | House Fan | 8 | 8192 | 4.0283 | 1 | 4.0283 | 2 | 4.0283 | 2
303 | Classroom | 538 | 35 |  |  | 1024 | 23 | 23 | House Fan | 8 | 8192 | 3.9404 | 1 | 3.9404 | 1 | 3.9404 | 1
304 | Classroom | 957 | 63 |  |  | 1024 | 23 | 23 | House Fan | 8 | 8192 | 7.0093 | 1 | 7.0093 | 2 | 7.0093 | 2
305 | Classroom | 746 | 49 |  |  | 1024 | 23 | 23 | House Fan | 8 | 8192 | 5.4639 | 1 | 5.4639 | 2 | 5.4639 | 2
306 | Classroom | 637 | 42 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 6.6354 | 1 | 6.6354 | 2 | 6.6354 | 2
307 | Classroom | 364 | 24 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 3.7917 | 1 | 3.7917 | 1 | 23.7917 | 3
- | Combo room | 883 | 58 |  |  | 1024 | 23 | 23 | House Fan | 8 | 8192 | 6.4673 | 1 | 6.4673 | 2 | 6.4673 | 2
- | Gym | 1325 | 88 |  |  | 1344 | 30 | 30 | House Fan | 8 | 10752 | 7.394 | 1 | 7.394 | 2 | 7.394 | 2
- | Library | 1641 | 109 |  |  | 2400 | 54 | 54 | House Fan | 8 | 19200 | 5.1281 | 1 | 5.1281 | 2 | 5.1281 | 2
- | Main office | 850 | 56 |  |  | 1156 | 26 | 26 | House Fan | 8 | 9248 | 5.5147 | 1 | 5.5147 | 2 | 5.5147 | 2
- | Restroom | 781 | 52 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 8.875 | 1 | 8.875 | 2 | 8.875 | 2
- | Counselors Office | 1062 | 70 |  |  | 175 | 3 | 3 | ERU | 8 | 1400 | 45.5143 | 1 | 45.5143 | 4 | 45.5143 | 4
- | Cafeteria | 0 | 0 |  |  | 1944 | 44 | 0 | NA | 8 | 15552 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurses Office |  | 0 | Yes | 20 | 75 | 1 | 1 |  | 8 | 600 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-12
School: | Aloysius L. Fitzpatrick Elementary School
Vendor: | Devine Brothers | Part 2 | Part 3
School: | Aloysius L. Fitzpatrick Elementary School Annex
Vendor: | Devine Brothers | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
B-10 | Classroom | 313 | 20 |  |  | 704 | 16 | 16 | Unit Ventilator | 8 | 5632 | 3.3345 | 1 | 3.3345 | 1 | 3.3345 | 1
100 | Classroom | 298 | 19 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 3.3864 | 1 | 3.3864 | 1 | 3.3864 | 1
101 | Classroom | 281 | 18 |  |  | 744 | 16 | 16 | Unit Ventilator | 8 | 5952 | 2.8327 | 1 | 2.8327 | 1 | 2.8327 | 1
102 | Classroom | 315 | 21 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.8125 | 1 | 2.8125 | 1 | 2.8125 | 1
103 | Classroom | 289 | 19 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.5804 | 1 | 2.5804 | 1 | 2.5804 | 1
104 | Classroom | 337 | 22 |  |  | 805 | 18 | 18 | Unit Ventilator | 8 | 6440 | 3.1398 | 1 | 3.1398 | 1 | 3.1398 | 1
105 | Classroom | 306 | 20 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.7321 | 1 | 2.7321 | 1 | 2.7321 | 1
106 | Classroom | 293 | 19 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.6161 | 1 | 2.6161 | 1 | 2.6161 | 1
107 | Classroom | 287 | 19 |  |  | 576 | 13 | 13 | Unit Ventilator | 8 | 4608 | 3.737 | 1 | 3.737 | 1 | 3.737 | 1
108 | Classroom | 409 | 27 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 3.7047 | 1 | 3.7047 | 1 | 3.7047 | 1
109 | Classroom | 26 | 1 | Yes | 20 | 600 | 13 | 13 | Unit Ventilator | 8 | 4800 | 0.325 | 1 | 0.325 | 0 | 20.325 | 3
110 | Classroom | 340 | 22 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 3.0357 | 1 | 3.0357 | 1 | 3.0357 | 1
112 | Classroom | 341 | 22 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 3.0888 | 1 | 3.0888 | 1 | 3.0888 | 1
200 | Classroom | 319 | 21 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.8482 | 1 | 2.8482 | 1 | 2.8482 | 1
201 | Classroom | 275 | 18 |  |  | 840 | 19 | 18 | Unit Ventilator | 8 | 6720 | 2.4554 | 1 | 2.4554 | 1 | 2.4554 | 1
202 | Classroom | 300 | 20 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.6786 | 1 | 2.6786 | 1 | 2.6786 | 1
203 | Classroom | 309 | 20 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.7589 | 1 | 2.7589 | 1 | 2.7589 | 1
204 | Classroom | 290 | 19 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.5893 | 1 | 2.5893 | 1 | 2.5893 | 1
205 | Classroom | 314 | 20 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.8036 | 1 | 2.8036 | 1 | 2.8036 | 1
206 | Library | 656 | 43 |  |  | 1680 | 38 | 38 | Unit Ventilator | 8 | 13440 | 2.9286 | 1 | 2.9286 | 1 | 2.9286 | 1
207 | Classroom | 326 | 21 |  |  | 425 | 9 | 9 | Unit Ventilator | 8 | 3400 | 5.7529 | 1 | 5.7529 | 2 | 5.7529 | 2
210 | Classroom | 293 | 19 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.6161 | 1 | 2.6161 | 1 | 2.6161 | 1
212 | Classroom | 334 | 22 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.9821 | 1 | 2.9821 | 1 | 2.9821 | 1
214 | Classroom | 304 | 20 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.7143 | 1 | 2.7143 | 1 | 2.7143 | 1
216 | Classroom | 325 | 21 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.9018 | 1 | 2.9018 | 1 | 2.9018 | 1
218 | Classroom | 307 | 20 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.7411 | 1 | 2.7411 | 1 | 2.7411 | 1
300 | Classroom | 289 | 19 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.5087 | 1 | 2.5087 | 1 | 2.5087 | 1
301 | Classroom | 305 | 20 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.7232 | 1 | 2.7232 | 1 | 2.7232 | 1
302 | Classroom | 281 | 18 |  |  | 840 | 19 | 18 | Unit Ventilator | 8 | 6720 | 2.5089 | 1 | 2.5089 | 1 | 2.5089 | 1
303 | Classroom | 299 | 19 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.6696 | 1 | 2.6696 | 1 | 2.6696 | 1
304 | Classroom | 329 | 21 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.9375 | 1 | 2.9375 | 1 | 2.9375 | 1
305 | Classroom | 294 | 19 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.625 | 1 | 2.625 | 1 | 2.625 | 1
306 | Classroom | 607 | 40 |  |  | 1704 | 38 | 38 | Unit Ventilator | 8 | 13632 | 2.6717 | 1 | 2.6717 | 1 | 2.6717 | 1
307 | Classroom | 340 | 22 |  |  | 425 | 9 | 9 | Unit Ventilator | 8 | 3400 | 6 | 1 | 6 | 2 | 6 | 2
310 | Classroom | 299 | 19 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.6696 | 1 | 2.6696 | 1 | 2.6696 | 1
312 | Classroom | 326 | 21 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.9107 | 1 | 2.9107 | 1 | 2.9107 | 1
314 | Classroom | 304 | 20 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.7143 | 1 | 2.7143 | 1 | 2.7143 | 1
316 | Classroom | 329 | 21 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.9375 | 1 | 2.9375 | 1 | 2.9375 | 1
318 | Classroom | 337 | 22 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 3.0089 | 1 | 3.0089 | 1 | 3.0089 | 1
- | Auditorium | 92 | 6 |  |  | 1825 | 41 | 6 | AHU | 8 | 14600 | 0.37808 | 1 | 0.37808 | 0 | 0.37808 | 0
B-1 | Classroom | 466 | 31 |  |  | 966 | 21 | 21 | Unit Ventilator | 8 | 7728 | 3.618 | 1 | 3.618 | 1 | 3.618 | 1
B-2 | Classroom | 287 | 19 |  |  | 966 | 21 | 19 | Unit Ventilator | 8 | 7728 | 2.2283 | 1 | 2.2283 | 1 | 2.2283 | 1
B-4 | Classroom | 236 | 15 |  |  | 704 | 16 | 15 | Unit Ventilator | 8 | 5632 | 2.5142 | 1 | 2.5142 | 1 | 2.5142 | 1
B-8 | Classroom | 269 | 17 |  |  | 792 | 18 | 17 | Unit Ventilator | 8 | 6336 | 2.5473 | 1 | 2.5473 | 1 | 2.5473 | 1
- | Cafeteria | 72 | 4 |  |  | 2835 | 64 | 4 | Unit Ventilator | 8 | 22680 | 0.19048 | 1.062 | 0.20229 | 0 | 0.20229 | 0
- | Gymnasium | 72 | 4 | Yes | 20 | 3922 | 89 | 89 | AHU | 8 | 31376 | 0.13768 | 1.062 | 0.14623 | 0 | 20.1462 | 3
- | Main Office | 284 | 18 |  |  | 1000 | 22 | 18 | Unit Ventilator | 8 | 8000 | 2.13 | 1 | 2.13 | 1 | 2.13 | 1
- | Music | 29 | 1 |  |  | 768 | 17 | 1 | Unit Ventilator | 8 | 6144 | 0.2832 | 1 | 0.2832 | 0 | 0.2832 | 0
Annex Building
9 | Classroom | 165 | 11 | Yes | 20 | 1040 | 23 | 23 | Unit Ventilator | 8 | 8320 | 1.1899 | 1 | 1.1899 | 1 | 21.1899 | 3
10 | Classroom | 310 | 20 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.691 | 1 | 2.691 | 1 | 2.691 | 1
11 | Classroom | 311 | 20 |  |  | 962 | 21 | 20 | Unit Ventilator | 8 | 7696 | 2.4246 | 1 | 2.4246 | 1 | 2.4246 | 1
12 | Classroom | 291 | 19 |  |  | 1040 | 23 | 19 | Unit Ventilator | 8 | 8320 | 2.0986 | 1 | 2.0986 | 1 | 2.0986 | 1
Sheet Last Modified: | 2021-04-14
School: | Edwin Forrest Elementary School
Vendor: | Devine Brothers
School: | Edwin Forrest Elementary School- Little School House
Vendor: | Devine Brothers | Devine Brothers Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Edwin Forrest Elementary School Main Building
- | Auditorium | 955 | 63 |  |  | 3552 | 80 | 63 | Unit Ventilator | 8 | 28416 | 2.0165 | 1.062 | 2.1416 | 1 | 2.1416 | 1
- | PreK | 281 | 18 |  |  | 1084 | 24 | 18 | Unit Ventilator | 8 | 8672 | 1.9442 | 1 | 1.9442 | 1 | 1.9442 | 1
101 | admin |  | 0 | Yes | 20 | 920 | 20 | 20 | House Fan | 8 | 7360 | 0 | 1 | 0 | 0 | 20 | 3
102 | 2nd |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
103 | admin |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
104 | Specialist K-6 |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
105 | 2nd grade |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
106 | 2nd |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
107 | 4th |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
108 | 2nd |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
109 | 2nd |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 336 | 7 | 7 | House Fan | 8 | 2688 | 0 | 1 | 0 | 0 | 20 | 3
110 | 2nd |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 210 | 4 | 4 | House Fan | 8 | 1680 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses Office |  | 0 | Yes | 20 | 264 | 6 | 6 | House Fan | 8 | 2112 | 0 | 1 | 0 | 0 | 20 | 3
201 | 4th |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
202 | 4th |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
203 | 4th |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
204 | 4th |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
205 | 3rd |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
206 | 3rd |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
207 | 3rd |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
208 | 3rd |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
209 | 3rd |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
210 | 3rd |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
211 | small group instruction |  | 0 | Yes | 20 | 192 | 4 | 4 | House Fan | 8 | 1536 | 0 | 1 | 0 | 0 | 20 | 3
212 | counselor office |  | 0 | Yes | 20 | 108 | 2 | 2 | House Fan | 8 | 864 | 0 | 1 | 0 | 0 | 20 | 3
- | Teachers Lounge |  | 0 | Yes | 20 | 253 | 5 | 5 | House Fan | 8 | 2024 | 0 | 1 | 0 | 0 | 20 | 3
301 | 6th |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
302 | 6th |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
303 | 6th |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
304 | 5th |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
305 | 5th |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
306 | 6th |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
307 | 6th |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
308 | 5th |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
309 | 5th |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
310 | 5th |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
311 | 3rd fl computer room |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
312 | Small group instruction |  | 0 | Yes | 20 | 192 | 4 | 4 | House Fan | 8 | 1536 | 0 | 1 | 0 | 0 | 20 | 3
314 |  |  |  | Yes | 20 | 180 |  |  | House Fan | 8 | 1440 |  | 1 | #VALUE! | #VALUE! | 20
- | Speech Room |  | 0 | Yes | 20 | 180 | 4 | 4 | House Fan | 8 | 1440 | 0 | 1 | 0 | 0 | 20 | 3
b1 | music room |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
b2a | Small group instruction |  | 0 | Yes | 20 | 352 | 8 | 8 | House Fan | 8 | 2816 | 0 | 1 | 0 | 0 | 20 | 3
b2 | Small group instruction |  | 0 | Yes | 20 | 352 | 8 | 8 | House Fan | 8 | 2816 | 0 | 1 | 0 | 0 | 20 | 3
b3 | Small group instruction |  | 0 | Yes | 20 | 506 | 11 | 11 | House Fan | 8 | 4048 | 0 | 1 | 0 | 0 | 20 | 3
B4 | Computer Lab |  | 0 | Yes | 20 | 968 | 22 | 22 | House Fan | 8 | 7744 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym/caf |  | 0 | Yes | 20 | 3432 | 78 | 78 | N/A | 8 | 27456 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Kitchen |  | 0 | Yes | 20 | 609 | 13 | 13 | House Fan | 8 | 4872 | 0 | 1 | 0 | 0 | 20 | 3
- | 2nd Flr Counselor Office |  | 0 | Yes | 20 | 195 | 4 | 4 | House Fan | 8 | 1560 | 0 | 1 | 0 | 0 | 20 | 3
- | 3rd Flr Counselor Office |  | 0 | Yes | 20 | 108 | 2 | 2 | House Fan | 8 | 864 | 0 | 1 | 0 | 0 | 20 | 3
Edwin Forrest Elementary School- Little School House
P1 | - | 348 | 23 |  |  | 986 | 22 | 22 | Unit Ventilator | 8 | 7888 | 2.6471 | 1 | 2.6471 | 1 | 2.6471 | 1
P2 | - | 303 | 20 |  |  | 986 | 22 | 20 | Unit Ventilator | 8 | 7888 | 2.3048 | 1 | 2.3048 | 1 | 2.3048 | 1
P3 | - | 362 | 24 |  |  | 986 | 22 | 22 | Unit Ventilator | 8 | 7888 | 2.7535 | 1 | 2.7535 | 1 | 2.7535 | 1
P4 | - | 327 | 21 |  |  | 986 | 22 | 21 | Unit Ventilator | 8 | 7888 | 2.4873 | 1 | 2.4873 | 1 | 2.4873 | 1
P5 | - | 304 | 20 |  |  | 986 | 22 | 20 | Unit Ventilator | 8 | 7888 | 2.3124 | 1 | 2.3124 | 1 | 2.3124 | 1
P6 | - | 390 | 26 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 3.6022 | 1 | 3.6022 | 1 | 3.6022 | 1
P7 | - | 308 | 20 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 2.8448 | 1 | 2.8448 | 1 | 2.8448 | 1
P8 | - | 308 | 20 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 2.8448 | 1 | 2.8448 | 1 | 2.8448 | 1
P9 | - | 382 | 25 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 3.5283 | 1 | 3.5283 | 1 | 3.5283 | 1
P10 | - | 312 | 20 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 2.8818 | 1 | 2.8818 | 1 | 2.8818 | 1
P11 | - | 311 | 20 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 2.8725 | 1 | 2.8725 | 1 | 2.8725 | 1
P12 | - | 316 | 21 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 2.9187 | 1 | 2.9187 | 1 | 2.9187 | 1
P13 | - | 327 | 21 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 3.0203 | 1 | 3.0203 | 1 | 3.0203 | 1
- | Administration and Corridors | 727 | 48 |  |  | 576 | 13 | 13 | AHU | 8 | 4608 | 9.4661 | 1 | 9.4661 | 2 | 9.4661 | 2
- | Cafeteria | 78 | 5 | Yes | 20 | 2014 | 45 | 45 | AHU | 8 | 16112 | 0.29047 | 1 | 0.29047 | 0 | 20.2905 | 3
- | Faculty Break Room | 312 | 20 |  |  | 210 | 4 | 4 | Unit Ventilator | 8 | 1680 | 11.1429 | 1 | 11.1429 | 3 | 11.1429 | 3
Sheet Last Modified: | 2021-04-08
School: | Fox Chase Elementary School
Fox Chase Farm
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Fox Chase Main Building
101 | Classroom | 338 | 22 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 3.0179 | 1 | 3.0179 | 1 | 3.0179 | 1
102 | Classroom | 316 | 21 |  |  | 1104 | 25 | 21 | Unit Ventilator | 8 | 8832 | 2.1467 | 1 | 2.1467 | 1 | 2.1467 | 1
103 | Classroom | 291 | 19 |  |  | 989 | 22 | 19 | Unit Ventilator | 8 | 7912 | 2.2068 | 1 | 2.2068 | 1 | 2.2068 | 1
104 | Classroom | 302 | 20 |  |  | 960 | 21 | 20 | Unit Ventilator | 8 | 7680 | 2.3594 | 1 | 2.3594 | 1 | 2.3594 | 1
105 | Classroom | 312 | 20 |  |  | 984 | 22 | 20 | Unit Ventilator | 8 | 7872 | 2.378 | 1 | 2.378 | 1 | 2.378 | 1
105A | Office | 0 | 0 | Yes | 20 | 216 | 4 | 4 | Unit Ventilator | 8 | 1728 | 0 | 1 | 0 | 0 | 20 | 3
107 | Examing Room |  | 0 | Yes | 20 | 234 | 5 | 5 | N/A | 8 | 1872 | 0 | 1 | 0 | 0 | 20 | 3
107A | Office | 0 | 0 | Yes | 20 | 225 | 5 | 5 | N/A | 8 | 1800 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom |  | 0 | Yes | 20 | 216 | 4 | 4 |  | 8 | 1728 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 315 | 21 |  |  | 1035 | 23 | 21 | Unit Ventilator | 8 | 8280 | 2.2826 | 1 | 2.2826 | 1 | 2.2826 | 1
110 | Classroom | 300 | 20 |  |  | 1032 | 23 | 20 | Unit Ventilator | 8 | 8256 | 2.1802 | 1 | 2.1802 | 1 | 2.1802 | 1
111 | Classroom | 155 | 10 | Yes | 20 | 1012 | 23 | 23 | Unit Ventilator | 8 | 8096 | 1.1487 | 1 | 1.1487 | 1 | 21.1487 | 3
112 | Classroom | 161 | 10 | Yes | 20 | 1081 | 24 | 24 | Unit Ventilator | 8 | 8648 | 1.117 | 1 | 1.117 | 1 | 21.117 | 3
201 | Classroom | 341 | 22 |  |  | 943 | 21 | 21 | Unit Ventilator | 8 | 7544 | 2.7121 | 1 | 2.7121 | 1 | 2.7121 | 1
202 | Classroom | 382 | 25 |  |  | 897 | 20 | 20 | Unit Ventilator | 8 | 7176 | 3.194 | 1 | 3.194 | 1 | 3.194 | 1
203 | Classroom | 382 | 25 |  |  | 897 | 20 | 20 | Unit Ventilator | 8 | 7176 | 3.194 | 1 | 3.194 | 1 | 3.194 | 1
204 | Classroom | 237 | 15 |  |  | 462 | 10 | 10 | Unit Ventilator | 8 | 3696 | 3.8474 | 1 | 3.8474 | 1 | 3.8474 | 1
205 | Classroom | 192 | 12 | Yes | 20 | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 1.5385 | 1 | 1.5385 | 1 | 21.5385 | 3
206 | Classroom | 391 | 26 |  |  | 912 | 20 | 20 | Unit Ventilator | 8 | 7296 | 3.2155 | 1 | 3.2155 | 1 | 3.2155 | 1
207 | Classroom | 0 | 0 | Yes | 20 | 943 | 21 | 21 | Unit Ventilator | 8 | 7544 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 71 | 4 | Yes | 20 | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 0.55469 | 1 | 0.55469 | 0 | 20.5547 | 3
3340 | Ag Room |  | 0 | Yes | 20 | 1283 | 29 | 29 | Unit Ventilator | 8 | 10264 | 0 | 1 | 0 | 0 | 20 | 3
- | 1st Floor Teacher's Lounge | 0 | 0 |  |  | 336 | 7 | 0 | N/A | 8 | 2688 | 0 | 1 | 0 | 0 | 0 | 0
A-1 | Classroom | 281 | 18 |  |  | 836 | 19 | 18 | Unit Ventilator | 8 | 6688 | 2.5209 | 1 | 2.5209 | 1 | 2.5209 | 1
A-2 | Classroom | 283 | 18 |  |  | 836 | 19 | 18 | Unit Ventilator | 8 | 6688 | 2.5389 | 1 | 2.5389 | 1 | 2.5389 | 1
A-3 | Classroom | 319 | 21 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 2.8618 | 1 | 2.8618 | 1 | 2.8618 | 1
A-4 | Classroom | 252 | 16 |  |  | 836 | 19 | 16 | Unit Ventilator | 8 | 6688 | 2.2608 | 1 | 2.2608 | 1 | 2.2608 | 1
A-5 | Classroom | 241 | 16 |  |  | 836 | 19 | 16 | Unit Ventilator | 8 | 6688 | 2.1621 | 1 | 2.1621 | 1 | 2.1621 | 1
A-6 | Classroom | 295 | 19 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 2.6465 | 1 | 2.6465 | 1 | 2.6465 | 1
C-1 | Classroom |  | 0 | Yes | 20 | 1560 | 35 | 35 | N/A | 8 | 12480 | 0 | 1 | 0 | 0 | 20 | 3
C-4 | Classroom |  | 0 | Yes | 20 | 380 | 8 | 8 | N/A | 8 | 3040 | 0 | 1 | 0 | 0 | 20 | 3
- | Annex | 0 | 0 |  |  | 1283 | 29 | 0 | Unit Ventilator | 8 | 10264 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 |  |  | 4420 | 100 | 0 | AHU | 8 | 35360 | 0 | 1.062 | 0 | 0 | 0 | 0
Instrument Room | Stage Area |  | 0 | Yes | 20 | 228 | 5 | 5 |  | 8 | 1824 | 0 | 1 | 0 | 0 | 20 | 3
- | Cafeteria | 704 | 46 |  |  | 2340 | 53 | 46 | Unit Ventilator | 8 | 18720 | 2.2564 | 1 | 2.2564 | 1 | 2.2564 | 1
- | Counselor | 0 | 0 |  |  | 230 | 5 | 0 | N/A | 8 | 1840 | 0 | 1 | 0 | 0 | 0 | 0
- | Dental Office | 0 | 0 | Yes | 20 | 208 | 4 | 4 | N/A | 8 | 1664 | 0 | 1 | 0 | 0 | 20 | 3
- | Examining Room | 0 | 0 |  |  | 234 | 5 | 0 | N/A | 8 | 1872 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym | 0 | 0 |  |  | 5429 | 123 | 0 | AHU | 8 | 43432 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Kitchen Storage | 296 | 19 |  |  | 260 | 5 | 5 | Unit Ventilator | 8 | 2080 | 8.5385 | 1 | 8.5385 | 2 | 8.5385 | 2
- | Main Office | 0 | 0 | Yes | 20 | 226 | 5 | 5 | N/A | 8 | 1808 | 0 | 1 | 0 | 0 | 20 | 3
- | Music Room | 581 | 38 |  |  | 1400 | 31 | 31 | Unit Ventilator | 8 | 11200 | 3.1125 | 1 | 3.1125 | 1 | 3.1125 | 1
- | Nurse | 0 | 0 | Yes | 20 | 234 | 5 | 5 | N/A | 8 | 1872 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal | 0 | 0 | Yes | 20 | 234 | 5 | 5 | N/A | 8 | 1872 | 0 | 1 | 0 | 0 | 20 | 3
Fox Chase Farm
- | Data Closet | 14 | 0 |  |  | 30 | 0 | 0 | AC | 8 | 240 | 3.5 | 1 | 3.5 | 1 | 3.5 | 1
- | Kitchen | 190 | 12 |  |  | 156 | 3 | 3 | AC | 8 | 1248 | 9.1346 | 1 | 9.1346 | 2 | 9.1346 | 2
- | Men's Bathroom | 56 | 3 |  |  | 225 | 5 | 3 | AC | 8 | 1800 | 1.8667 | 1 | 1.8667 | 1 | 1.8667 | 1
- | Teaching Area Classroom | 658 | 43 |  |  | 1692 | 38 | 38 | AC | 8 | 13536 | 2.9167 | 1 | 2.9167 | 1 | 2.9167 | 1
- | Women's Bathroom | 55 | 3 |  |  | 225 | 5 | 3 | AC | 8 | 1800 | 1.8333 | 1 | 1.8333 | 1 | 1.8333 | 1
Sheet Last Modified: | 2021-04-23
School: | Anne Frank Elementary School
Vendor: | Devine Brothers | Devine Retest
School: | Anne Frank Elementary School- Little School House
Vendor: | Devine Brothers | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Frank Main Building
100 | Classroom | 283 | 18 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.4566 | 1 | 2.4566 | 1 | 22.4566 | 3
101 | Classroom | 284 | 18 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.4653 | 1 | 2.4653 | 1 | 22.4653 | 3
102 | Classroom | 236 | 15 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.0486 | 1 | 2.0486 | 1 | 22.0486 | 3
103 | Classroom | 260 | 17 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.2569 | 1 | 2.2569 | 1 | 22.2569 | 3
104 | Classroom | 56 | 3 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0.48611 | 1 | 0.48611 | 0 | 20.4861 | 3
106 | Classroom | 0 | 0 |  |  | 240 | 5 | 0 | Unit Ventilator | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
108 | Classroom | 191 | 12 | Yes | 20 | 456 | 10 | 10 | Unit Ventilator | 8 | 3648 | 3.1414 | 1 | 3.1414 | 1 | 23.1414 | 3
109 | Classroom | 0 | 0 | Yes | 20 | 456 | 10 | 10 | Unit Ventilator | 8 | 3648 | 0 | 1 | 0 | 0 | 20 | 3
110 | Classroom | 305 | 20 | Yes | 20 | 1032 | 23 | 23 | Unit Ventilator | 8 | 8256 | 2.2166 | 1 | 2.2166 | 1 | 22.2166 | 3
125 | Classroom | 348 | 23 |  |  | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 3.8839 | 1 | 3.8839 | 1 | 3.8839 | 1
- | Admin Office | 0 | 0 |  |  | 135 | 3 | 0 | Unit Ventilator | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
200 | Classroom | 283 | 18 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.4566 | 1 | 2.4566 | 1 | 22.4566 | 3
201 | Library | 60 | 4 | Yes | 20 | 875 | 19 | 19 | Unit Ventilator | 8 | 7000 | 0.51429 | 1 | 0.51429 | 0 | 20.5143 | 3
202 | Classroom | 293 | 19 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.5434 | 1 | 2.5434 | 1 | 2.5434 | 1
203 | Classroom | 304 | 20 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.6389 | 1 | 2.6389 | 1 | 2.6389 | 1
204 | Classroom | 322 | 21 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.7951 | 1 | 2.7951 | 1 | 2.7951 | 1
205 | Classroom | 215 | 14 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 1.8663 | 1 | 1.8663 | 1 | 21.8663 | 3
206 | Classroom | 205 | 13 |  |  | 240 | 5 | 5 | Unit Ventilator | 8 | 1920 | 6.4062 | 1 | 6.4062 | 2 | 6.4062 | 2
207 | Classroom | 257 | 17 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.2309 | 1 | 2.2309 | 1 | 22.2309 | 3
208 | Classroom | 299 | 19 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.5955 | 1 | 2.5955 | 1 | 2.5955 | 1
209 | Classroom | 203 | 13 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 1.7622 | 1 | 1.7622 | 1 | 21.7622 | 3
210 | Classroom | 225 | 15 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 1.9531 | 1 | 1.9531 | 1 | 21.9531 | 3
211 | Classroom | 333 | 22 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.8906 | 1 | 2.8906 | 1 | 2.8906 | 1
212 | Classroom | 153 | 10 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 1.3281 | 1 | 1.3281 | 1 | 21.3281 | 3
213 | Classroom | 226 | 15 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 1.9618 | 1 | 1.9618 | 1 | 21.9618 | 3
214 | Classroom |  | 0 | Yes | 20 | 864 | 19 | 19 |  | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
215 | Classroom | 284 | 18 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.4653 | 1 | 2.4653 | 1 | 22.4653 | 3
- | Library | 0 | 0 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
300 | Classroom | 241 | 16 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.092 | 1 | 2.092 | 1 | 22.092 | 3
301 | Classroom | 0 | 0 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom | 185 | 12 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 1.6059 | 1 | 1.6059 | 1 | 21.6059 | 3
304 | Classroom | 0 | 0 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom | 0 | 0 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 20 | 240 | 5 | 5 | Unit Ventilator | 8 | 1920 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom | 0 | 0 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
310 | Classroom | 127 | 8 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 1.1024 | 1 | 1.1024 | 1 | 21.1024 | 3
311 | Classroom | 42 | 2 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0.36458 | 1 | 0.36458 | 0 | 20.3646 | 3
312 | Classroom | 0 | 0 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
313 | Classroom | 0 | 0 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
315 | Classroom | 0 | 0 | Yes | 20 | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
| Auditorium | 0 | 0 |  |  | 3180 | 72 | 0 |  | 8 | 25440 | 0 | 1.062 | 0 | 0 | 0 | 0
| Cafeteria | 0 | 0 | Yes | 20 | 2720 | 61 | 61 |  | 8 | 21760 | 0 | 1.062 | 0 | 0 | 20 | 3
| Gymnasium | 0 | 0 | Yes | 20 | 3657 | 83 | 83 |  | 8 | 29256 | 0 | 1.062 | 0 | 0 | 20 | 3
| Gymnasium Office |  | 0 |  |  | 165 | 3 | 0 |  | 8 | 1320 | 0 | 1 | 0 | 0 | 0 | 0
- | Counselor Office | 0 | 0 | Yes | 20 | 132 | 3 | 3 | NA | 8 | 1056 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office | 60 | 4 | Yes | 20 | 951 | 21 | 21 | Unit Ventilator | 8 | 7608 | 0.47319 | 1 | 0.47319 | 0 | 20.4732 | 3
- | Nurses Office | 0 | 0 | Yes | 20 | 304 | 6 | 6 | NA | 8 | 2432 | 0 | 1 | 0 | 0 | 20 | 3
- | Principals Office | 0 | 0 | Yes | 20 | 210 | 4 | 4 | NA | 8 | 1680 | 0 | 1 | 0 | 0 | 20 | 3
- | Vice Principals Office | 0 | 0 | Yes | 20 | 72 | 1 | 1 | NA | 8 | 576 | 0 | 1 | 0 | 0 | 20 | 3
Frank LSH
1 | Classroom | 931 | 62 |  |  | 928 | 21 | 21 | BCU | 8 | 7424 | 7.5242 | 1 | 7.5242 | 2 | 7.5242 | 2
2 | Classroom | 595 | 39 |  |  | 928 | 21 | 21 | BCU | 8 | 7424 | 4.8087 | 1 | 4.8087 | 2 | 4.8087 | 2
3 | Classroom | 945 | 63 |  |  | 928 | 21 | 21 | BCU | 8 | 7424 | 7.6374 | 1 | 7.6374 | 2 | 7.6374 | 2
4 | Classroom | 610 | 40 |  |  | 928 | 21 | 21 | BCU | 8 | 7424 | 4.93 | 1 | 4.93 | 2 | 4.93 | 2
5 | Classroom | 322 | 21 |  |  | 928 | 21 | 21 | BCU | 8 | 7424 | 2.6024 | 1 | 2.6024 | 1 | 2.6024 | 1
6 | Classroom | 307 | 20 | Yes | 20 | 928 | 21 | 21 | BCU | 8 | 7424 | 2.4811 | 1 | 2.4811 | 1 | 22.4811 | 3
7 | Classroom | 310 | 20 | Yes | 20 | 928 | 21 | 21 | BCU | 8 | 7424 | 2.5054 | 1 | 2.5054 | 1 | 22.5054 | 3
8 | Classroom | 305 | 20 | Yes | 20 | 928 | 21 | 21 | BCU | 8 | 7424 | 2.465 | 1 | 2.465 | 1 | 22.465 | 3
9 | Classroom | 370 | 24 |  |  | 928 | 21 | 21 | BCU | 8 | 7424 | 2.9903 | 1 | 2.9903 | 1 | 2.9903 | 1
10 | Classroom | 329 | 21 |  |  | 928 | 21 | 21 | BCU | 8 | 7424 | 2.6589 | 1 | 2.6589 | 1 | 2.6589 | 1
11 | Classroom | 396 | 26 |  |  | 928 | 21 | 21 | BCU | 8 | 7424 | 3.2004 | 1 | 3.2004 | 1 | 3.2004 | 1
12 | Classroom | 319 | 21 |  |  | 928 | 21 | 21 | BCU | 8 | 7424 | 2.5781 | 1 | 2.5781 | 1 | 2.5781 | 1
- | Bathrooms, Corridor and Main Entrance | 284 | 18 |  |  | 225 | 5 | 5 | FCU | 8 | 1800 | 9.4667 | 1 | 9.4667 | 2 | 9.4667 | 2
- | Corner Facilities/Guidance Office | 0 | 0 |  |  | 196 | 4 | 0 | FCU | 8 | 1568 | 0 | 1 | 0 | 0 | 0 | 0
- | Counselor Office | 0 | 0 | Yes | 20 | 100 | 2 | 2 | FCU | 8 | 800 | 0 | 1 | 0 | 0 | 20 | 3
- | Janitor Close and Storage Rooms | 262 | 17 |  |  | 24 | 0 | 0 | FCU | 8 | 192 | 81.875 | 1 | 81.875 | 5 | 81.875 | 5
- | Main Office | 587 | 39 |  |  | 315 | 7 | 7 | FCU | 8 | 2520 | 13.9762 | 1 | 13.9762 | 3 | 13.9762 | 3
- | Cafeteria | 922 | 61 |  |  | 1696 | 38 | 38 | BCU | 8 | 13568 | 4.0772 | 1 | 4.0772 | 2 | 4.0772 | 2
- | Art Teacher Office | 102 | 6 |  |  | 100 | 2 | 2 | BCU | 8 | 800 | 7.65 | 1 | 7.65 | 2 | 7.65 | 2
- | ESL Teacher Office | 110 | 7 |  |  | 100 | 2 | 2 | BCU | 8 | 800 | 8.25 | 1 | 8.25 | 2 | 8.25 | 2
- | ESL Room | 241 | 16 |  |  | 80 | 1 | 1 | BCU | 8 | 640 | 22.5938 | 1 | 22.5938 | 3 | 22.5938 | 3
Frank Annex
7 | Classroom | 36 | 2 | Yes | 20 | 1080 | 24 | 24 | Unit Ventilator | 8 | 8640 | 0.25 | 1 | 0.25 | 0 | 20.25 | 3
8 | Classroom | 235 | 15 | Yes | 20 | 1080 | 24 | 24 | Unit Ventilator | 8 | 8640 | 1.6319 | 1 | 1.6319 | 1 | 21.6319 | 3
- | gang girlsnboys |  | 0 |  |  | 480 | 10 | 0 | N/A | 8 | 3840 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-17
School: | Frankford High School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
9 | Classroom | 122 | 8 |  |  | 1836 | 41 | 8 | Unit Ventilator | 8 | 14688 | 0.49837 | 1 | 0.49837 | 0 | 0.49837 | 0
11 | Classroom | 0 | 0 |  |  | 2011 | 45 | 0 | Unit Ventilator | 8 | 16088 | 0 | 1 | 0 | 0 | 0 | 0
12 | Classroom | 0 | 0 |  |  | 2011 | 45 | 0 | Unit Ventilator | 8 | 16088 | 0 | 1 | 0 | 0 | 0 | 0
14 | Classroom | 167 | 11 |  |  | 812 | 18 | 11 | Unit Ventilator | 8 | 6496 | 1.5425 | 1 | 1.5425 | 1 | 1.5425 | 1
15-14 | Classroom | 0 | 0 |  |  | N/A | 0 | 0 | Unit Ventilator
15A | Classroom | 107 | 7 |  |  | 812 | 18 | 7 | Unit Ventilator | 8 | 6496 | 0.9883 | 1 | 0.9883 | 0 | 0.9883 | 0
16 | Classroom | 0 | 0 |  |  | 476 | 10 | 0 | Unit Ventilator | 8 | 3808 | 0 | 1 | 0 | 0 | 0 | 0
17 | Classroom | 0 | 0 |  |  | 952 | 21 | 0 | Unit Ventilator | 8 | 7616 | 0 | 1 | 0 | 0 | 0 | 0
18 | Classroom | 76 | 5 |  |  | 884 | 20 | 5 | Unit Ventilator | 8 | 7072 | 0.6448 | 1 | 0.6448 | 0 | 0.6448 | 0
19 | Classroom | 55 | 3 |  |  | 576 | 13 | 3 | Unit Ventilator | 8 | 4608 | 0.71615 | 1 | 0.71615 | 0 | 0.71615 | 0
20 | Classroom | 0 | 0 |  |  | 1023 | 23 | 0 | Unit Ventilator | 8 | 8184 | 0 | 1 | 0 | 0 | 0 | 0
124 | Classroom | 210 | 14 |  |  | 1702 | 38 | 14 | Unit Ventilator | 8 | 13616 | 0.92538 | 1 | 0.92538 | 0 | 0.92538 | 0
222 | Classroom | 80 | 5 |  |  | 889 | 20 | 5 | Unit Ventilator | 8 | 7112 | 0.67492 | 1 | 0.67492 | 0 | 0.67492 | 0
223 | Classroom | 163 | 10 |  |  | 991 | 22 | 10 | Unit Ventilator | 8 | 7928 | 1.2336 | 1 | 1.2336 | 1 | 1.2336 | 1
224 | Classroom | 80 | 5 |  |  | 991 | 22 | 5 | Unit Ventilator | 8 | 7928 | 0.60545 | 1 | 0.60545 | 0 | 0.60545 | 0
225 | Classroom | 50 | 3 |  |  | 1005 | 22 | 3 | Unit Ventilator | 8 | 8040 | 0.37313 | 1 | 0.37313 | 0 | 0.37313 | 0
226 | Classroom | 149 | 9 |  |  | 991 | 22 | 9 | Unit Ventilator | 8 | 7928 | 1.1276 | 1 | 1.1276 | 1 | 1.1276 | 1
227 | Classroom | 128 | 8 |  |  | 864 | 19 | 8 | Unit Ventilator | 8 | 6912 | 1.1111 | 1 | 1.1111 | 1 | 1.1111 | 1
228 | Classroom | 255 | 17 |  |  | 899 | 20 | 17 | Unit Ventilator | 8 | 7192 | 2.1274 | 1 | 2.1274 | 1 | 2.1274 | 1
229 | Classroom | 0 | 0 |  |  | 462 | 10 | 0 | Unit Ventilator | 8 | 3696 | 0 | 1 | 0 | 0 | 0 | 0
230 | Classroom | 181 | 12 |  |  | 1001 | 22 | 12 | Unit Ventilator | 8 | 8008 | 1.3561 | 1 | 1.3561 | 1 | 1.3561 | 1
231A | Classroom | 286 | 19 |  |  | 986 | 22 | 19 | Unit Ventilator | 8 | 7888 | 2.1755 | 1 | 2.1755 | 1 | 2.1755 | 1
232A | Classroom | 80 | 5 |  |  | 1048 | 23 | 5 | Unit Ventilator | 8 | 8384 | 0.57252 | 1 | 0.57252 | 0 | 0.57252 | 0
233 | Classroom | 40 | 2 |  |  | 1120 | 25 | 2 | Unit Ventilator | 8 | 8960 | 0.26786 | 1 | 0.26786 | 0 | 0.26786 | 0
326 | Classroom | 91 | 6 |  |  | 775 | 17 | 6 | Unit Ventilator | 8 | 6200 | 0.88065 | 1 | 0.88065 | 0 | 0.88065 | 0
327 | Classroom | 48 | 3 |  |  | 775 | 17 | 3 | Unit Ventilator | 8 | 6200 | 0.46452 | 1 | 0.46452 | 0 | 0.46452 | 0
330-331 | Classroom | 166 | 11 |  |  | 969 | 22 | 11 | Unit Ventilator | 8 | 7752 | 1.2848 | 1 | 1.2848 | 1 | 1.2848 | 1
332 | Classroom | 84 | 5 |  |  | 1505 | 34 | 5 | Unit Ventilator | 8 | 12040 | 0.4186 | 1 | 0.4186 | 0 | 0.4186 | 0
333 | Classroom | 0 | 0 |  |  | 1505 | 34 | 0 | Unit Ventilator | 8 | 12040 | 0 | 1 | 0 | 0 | 0 | 0
335 | Classroom | 0 | 0 |  |  | 1120 | 25 | 0 | Unit Ventilator | 8 | 8960 | 0 | 1 | 0 | 0 | 0 | 0
- | IMC | 264 | 17 |  |  | 5398 | 122 | 17 | Unit Ventilator | 8 | 43184 | 0.3668 | 1.062 | 0.38956 | 0 | 0.38956 | 0
Sheet Last Modified: | 2021-04-21
School: | Benjamin Franklin Elementary School
Vendor: | Devine | Devine 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Basement Boy's Restroom | 0 | 0 |  |  | 234 | 5 | 0 | AHU | 8 | 1872 | 0 | 1 | 0 | 0 | 0 | 0
- | Basement Girl's Restroom | 0 | 0 |  |  | 234 | 5 | 0 | AHU | 8 | 1872 | 0 | 1 | 0 | 0 | 0 | 0
- | 1st Floor Boy's Restroom | 27 | 1 |  |  | 234 | 5 | 1 | AHU | 8 | 1872 | 0.86538 | 1 | 0.86538 | 0 | 0.86538 | 0
- | 1st Floor Girl's Restroom | 40 | 2 |  |  | 234 | 5 | 2 | AHU | 8 | 1872 | 1.2821 | 1 | 1.2821 | 1 | 1.2821 | 1
- | 2nd Floor Girl's Restroom | 28 | 1 |  |  | 234 | 5 | 1 | AHU | 8 | 1872 | 0.89744 | 1 | 0.89744 | 0 | 0.89744 | 0
- | 2nd Floor Boy's Restroom | 40 | 2 |  |  | 234 | 5 | 2 | AHU | 8 | 1872 | 1.2821 | 1 | 1.2821 | 1 | 1.2821 | 1
1 | Classroom |  | 0 | Yes | 20 | 304 | 6 | 6 | Unit Ventilator | 8 | 2432 | 0 | 1 | 0 | 0 | 20 | 3
1B | Classroom |  | 0 | Yes | 20 | 667 | 15 |  |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
6 | Classroom | 350 | 23 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 3.3654 | 1 | 3.3654 | 1 | 3.3654 | 1
7 | Cafeteria | 1972 | 131 |  |  | 2800 | 63 | 63 | AHU | 8 | 22400 | 5.2821 | 1.062 | 5.6098 | 2 | 5.6098 | 2
8 | Classroom | 299 | 19 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.875 | 1 | 2.875 | 1 | 2.875 | 1
- | Kitchen | 1585 | 105 |  |  | 1023 | 23 | 23 | AHU | 8 | 8184 | 11.6202 | 1 | 11.6202 | 3 | 11.6202 | 3
- | Kitchen Office | 225 | 15 |  |  | 80 | 1 | 1 | AHU | 8 | 640 | 21.0938 | 1 | 21.0938 | 3 | 21.0938 | 3
101 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom |  | 0 | Yes | 20 | 650 | 14 | 14 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom |  | 0 | Yes | 20 | 650 | 14 | 14 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom |  | 0 | Yes | 20 | 650 | 14 | 14 |  | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 |  |  | 720 | 16 | 0 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
110 | Classroom | 352 | 23 |  |  | 780 | 17 | 17 | House Fan | 8 | 6240 | 3.3846 | 1 | 3.3846 | 1 | 3.3846 | 1
111 | Classroom | 321 | 21 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 3.0865 | 1 | 3.0865 | 1 | 3.0865 | 1
112 | Classroom | 300 | 20 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.8846 | 1 | 2.8846 | 1 | 2.8846 | 1
113 | Classroom | 312 | 20 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 3 | 1 | 3 | 1 | 3 | 1
114 | Classroom | 410 | 27 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 3.9423 | 1 | 3.9423 | 1 | 3.9423 | 1
115 | Classroom | 346 | 23 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 3.3269 | 1 | 3.3269 | 1 | 3.3269 | 1
116 | Asst Principals Office | 352 | 23 |  |  | 207 | 4 | 4 | Unit Ventilator | 8 | 1656 | 12.7536 | 1 | 12.7536 | 3 | 12.7536 | 3
117 | Classroom | 332 | 22 |  |  | 609 | 13 | 13 | Unit Ventilator | 8 | 4872 | 4.0887 | 1 | 4.0887 | 2 | 4.0887 | 2
201 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 | Yes | 20 | 650 | 14 | 14 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 650 | 14 | 14 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 | Yes | 20 | 650 | 14 | 14 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom |  | 0 | Yes | 20 | 650 | 14 | 14 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
209 | Library | 568 | 37 | Yes | 20 | 1600 | 36 | 36 | Unit Ventilator | 8 | 12800 | 2.6625 | 1 | 2.6625 | 1 | 22.6625 | 3
210 | Trs Lounge | 330 | 22 |  |  | 380 | 8 | 8 | Unit Ventilator | 8 | 3040 | 6.5132 | 1 | 6.5132 | 2 | 6.5132 | 2
212 | TECH LAB | 487 | 32 |  |  | 1600 | 36 | 32 | Unit Ventilator | 8 | 12800 | 2.2828 | 1 | 2.2828 | 1 | 2.2828 | 1
214 | Classroom | 305 | 20 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.9327 | 1 | 2.9327 | 1 | 2.9327 | 1
215 | Classroom | 325 | 21 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 3.125 | 1 | 3.125 | 1 | 3.125 | 1
216 | Classroom | 325 | 21 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 3.125 | 1 | 3.125 | 1 | 3.125 | 1
217 | Classroom | 287 | 19 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.7596 | 1 | 2.7596 | 1 | 2.7596 | 1
218 | Classroom | 323 | 21 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 3.1058 | 1 | 3.1058 | 1 | 3.1058 | 1
219 | Classroom | 291 | 19 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.7981 | 1 | 2.7981 | 1 | 2.7981 | 1
220 | Counselor's Office | 287 | 19 |  |  | 207 | 4 | 4 | Unit Ventilator | 8 | 1656 | 10.3986 | 1 | 10.3986 | 3 | 10.3986 | 3
221 | Classroom | 314 | 20 |  |  | 605 | 13 | 13 | Unit Ventilator | 8 | 4840 | 3.8926 | 1 | 3.8926 | 1 | 3.8926 | 1
- | Faculty Lounge | 0 | 0 |  |  | 160 | 3 | 0 | Unit Ventilator | 8 | 1280 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurses Office |  | 0 | Yes | 20 | 132 | 3 | 3 |  | 8 | 1056 | 0 | 1 | 0 | 0 | 20 | 3
- | Psychology Office | 33 | 2 |  |  | 90 | 2 | 2 | Unit Ventilator | 8 | 720 | 2.75 | 1 | 2.75 | 1 | 2.75 | 1
- | Main Office |  | 0 | Yes | 20 | 220 | 5 | 5 |  | 8 | 1760 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-19
School: | Benjamin Franklin High School
Vendor: | Devine | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Weight room | 63 | 4 |  |  | 713 | 16 | 4 | HV+ AHU | 8 | 5704 | 0.66269 | 1 | 0.66269 | 0 | 0.66269 | 0
2 | Weight room | 0 | 0 |  |  | 775 | 17 | 0 | HV | 8 | 6200 | 0 | 1 | 0 | 0 | 0 | 0
3 | Weight room | 0 | 0 |  |  | 1632 | 37 | 0 | HV | 8 | 13056 | 0 | 1 | 0 | 0 | 0 | 0
4 | Welding | 9254 | 616 |  |  | 2176 | 49 | 49 | MUA | 8 | 17408 | 31.8957 | 1 | 31.8957 | 4 | 31.8957 | 4
4A | Classroom | 280 | 18 |  |  | 640 | 14 | 14 | AC | 8 | 5120 | 3.2812 | 1 | 3.2812 | 1 | 3.2812 | 1
6 | Classroom | 0 | 0 | Yes | 20 | 2655 | 60 | 60 | AHU | 8 | 21240 | 0 | 1.062 | 0 | 0 | 20 | 3
7 | Classroom | 0 | 0 |  |  | 216 | 4 | 0 | AHU | 8 | 1728 | 0 | 1 | 0 | 0 | 0 | 0
8 | Classroom | 0 | 0 |  |  | 588 | 13 | 0 | AHU | 8 | 4704 | 0 | 1 | 0 | 0 | 0 | 0
9 | Classroom | 0 | 0 |  |  | 621 | 14 | 0 | AHU | 8 | 4968 | 0 | 1 | 0 | 0 | 0 | 0
10 | Machine Shop | 810 | 54 |  |  | 2961 | 67 | 54 | HV | 8 | 23688 | 2.0517 | 1.062 | 2.1789 | 1 | 2.1789 | 1
11 | Classroom | 176 | 11 |  |  | 1740 | 39 | 11 | AC | 8 | 13920 | 0.75862 | 1 | 0.75862 | 0 | 0.75862 | 0
12 | Classroom | 842 | 56 |  |  | 1581 | 35 | 35 | HV | 8 | 12648 | 3.9943 | 1 | 3.9943 | 1 | 3.9943 | 1
13 | Classroom | 175 | 11 |  |  | 1239 | 28 | 11 | AC | 8 | 9912 | 1.0593 | 1 | 1.0593 | 1 | 1.0593 | 1
13A | Classroom | 93 | 6 |  |  | 552 | 12 | 6 | AC | 8 | 4416 | 1.2636 | 1 | 1.2636 | 1 | 1.2636 | 1
14 | Classroom | 136 | 9 |  |  | 756 | 17 | 9 | AC | 8 | 6048 | 1.3492 | 1 | 1.3492 | 1 | 1.3492 | 1
15 | Classroom | 155 | 10 |  |  | 912 | 20 | 10 | AC | 8 | 7296 | 1.2747 | 1 | 1.2747 | 1 | 1.2747 | 1
15A | Practice Room | 77 | 5 |  |  | 77 | 1 | 1 | HV | 8 | 616 | 7.5 | 1 | 7.5 | 2 | 7.5 | 2
15B | Practice Room | 188 | 12 |  |  | 77 | 1 | 1 | HV | 8 | 616 | 18.3117 | 1 | 18.3117 | 3 | 18.3117 | 3
15C | Practice Room | 143 | 9 |  |  | 77 | 1 | 1 | HV | 8 | 616 | 13.9286 | 1 | 13.9286 | 3 | 13.9286 | 3
15D | Music Office | 142 | 9 |  |  | 180 | 4 | 4 | HV | 8 | 1440 | 5.9167 | 1 | 5.9167 | 2 | 5.9167 | 2
16 | Lecture Hall | 2049 | 136 |  |  | 2068 | 47 | 47 | HV | 8 | 16544 | 7.4311 | 1 | 7.4311 | 2 | 7.4311 | 2
17 | Lecture Hall | 387 | 25 |  |  | 2280 | 51 | 25 | HV | 8 | 18240 | 1.273 | 1 | 1.273 | 1 | 1.273 | 1
18 | Classroom | 803 | 53 |  |  | 1080 | 24 | 24 | AC | 8 | 8640 | 5.5764 | 1 | 5.5764 | 2 | 5.5764 | 2
19 | Classroom | 781 | 52 |  |  | 1344 | 30 | 30 | AC | 8 | 10752 | 4.3583 | 1 | 4.3583 | 2 | 4.3583 | 2
20 | Classroom | 635 | 42 |  |  | 828 | 18 | 18 | AC | 8 | 6624 | 5.7518 | 1 | 5.7518 | 2 | 5.7518 | 2
100 | Classroom | 280 | 18 |  |  | 775 | 17 | 17 | UV | 8 | 6200 | 2.7097 | 1 | 2.7097 | 1 | 2.7097 | 1
102 | Classroom | 382 | 25 |  |  | 961 | 21 | 21 | UV | 8 | 7688 | 2.9813 | 1 | 2.9813 | 1 | 2.9813 | 1
110 | Room | 0 | 0 |  |  | 195 | 4 | 0 | FC | 8 | 1560 | 0 | 1 | 0 | 0 | 0 | 0
111A | Room | 0 | 0 |  |  | 104 | 2 | 0 | FC | 8 | 832 | 0 | 1 | 0 | 0 | 0 | 0
113 | Room | 0 | 0 |  |  | 315 | 7 | 0 | FC | 8 | 2520 | 0 | 1 | 0 | 0 | 0 | 0
115 | Room | 0 | 0 |  |  | 352 | 8 | 0 | FC | 8 | 2816 | 0 | 1 | 0 | 0 | 0 | 0
116 | Room | 0 | 0 |  |  | 196 | 4 | 0 | FC | 8 | 1568 | 0 | 1 | 0 | 0 | 0 | 0
150 | Kitchen | 0 | 0 |  |  | 1955 | 44 | 0 | RTU | 8 | 15640 | 0 | 1 | 0 | 0 | 0 | 0
152 | Cafeteria | 0 | 0 |  |  | 3363 | 76 | 0 | RTU | 8 | 26904 | 0 | 1.062 | 0 | 0 | 0 | 0
200 | Living Room | 140 | 9 |  |  | 819 | 18 | 9 | UV | 8 | 6552 | 1.2821 | 1 | 1.2821 | 1 | 1.2821 | 1
201 | Classroom | 217 | 14 |  |  | 792 | 18 | 14 | UV | 8 | 6336 | 2.0549 | 1 | 2.0549 | 1 | 2.0549 | 1
202 | Office-A | 201 | 13 |  |  | 600 | 13 | 13 | UV | 8 | 4800 | 2.5125 | 1 | 2.5125 | 1 | 2.5125 | 1
202 | Office-B | 171 | 11 |  |  | 396 | 9 | 9 | UV | 8 | 3168 | 3.2386 | 1 | 3.2386 | 1 | 3.2386 | 1
204 | Principal Office | 41 | 2 |  |  | 180 | 4 | 2 | OAS-1A & OAS-1B | 8 | 1440 | 1.7083 | 1 | 1.7083 | 1 | 1.7083 | 1
206 | Co-Principal | 40 | 2 |  |  | 120 | 2 | 2 | OAS-1A & OAS-1B | 8 | 960 | 2.5 | 1 | 2.5 | 1 | 2.5 | 1
207 | Classroom | 257 | 17 |  |  | 792 | 18 | 17 | UV | 8 | 6336 | 2.4337 | 1 | 2.4337 | 1 | 2.4337 | 1
209 | Storage | 189 | 12 |  |  | 165 | 3 | 3 | UV | 8 | 1320 | 8.5909 | 1 | 8.5909 | 2 | 8.5909 | 2
209B | Office | 287 | 19 |  |  | 180 | 4 | 4 | UV | 8 | 1440 | 11.9583 | 1 | 11.9583 | 3 | 11.9583 | 3
211 | Classroom | 358 | 23 |  |  | 713 | 16 | 16 | UV | 8 | 5704 | 3.7658 | 1 | 3.7658 | 1 | 3.7658 | 1
212 | Work Room | 49 | 3 |  |  | 297 | 6 | 3 | OAS-1A & OAS-1B | 8 | 2376 | 1.2374 | 1 | 1.2374 | 1 | 1.2374 | 1
214 | Office | 57 | 3 |  |  | 121 | 2 | 2 | OAS-1A & OAS-1B | 8 | 968 | 3.5331 | 1 | 3.5331 | 1 | 3.5331 | 1
215 | Classroom | 295 | 19 |  |  | 806 | 18 | 18 | UV | 8 | 6448 | 2.745 | 1 | 2.745 | 1 | 2.745 | 1
216 | Conference | 44 | 2 |  |  | 72 | 1 | 1 | OAS-1A & OAS-1B | 8 | 576 | 4.5833 | 1 | 4.5833 | 2 | 4.5833 | 2
217 | Learning Lounge | 263 | 17 |  |  | 572 | 13 | 13 | UV | 8 | 4576 | 3.4484 | 1 | 3.4484 | 1 | 3.4484 | 1
218 | College Office | 50 | 3 |  |  | 132 | 3 | 3 | OAS-1A & OAS-1B | 8 | 1056 | 2.8409 | 1 | 2.8409 | 1 | 2.8409 | 1
220 | College | 49 | 3 |  |  | 120 | 2 | 2 | OAS-1A & OAS-1B | 8 | 960 | 3.0625 | 1 | 3.0625 | 1 | 3.0625 | 1
222 | Health Suite | 45 | 3 |  |  | 256 | 5 | 3 | OAS-1A & OAS-1B | 8 | 2048 | 1.3184 | 1 | 1.3184 | 1 | 1.3184 | 1
222A | Nurse Office | 50 | 3 |  |  | 108 | 2 | 2 | OAS-1A & OAS-1B | 8 | 864 | 3.4722 | 1 | 3.4722 | 1 | 3.4722 | 1
222B | Exam | 48 | 3 |  |  | 99 | 2 | 2 | OAS-1A & OAS-1B | 8 | 792 | 3.6364 | 1 | 3.6364 | 1 | 3.6364 | 1
223A | Dining | 856 | 57 |  |  | 1760 | 40 | 40 | UV | 8 | 14080 | 3.6477 | 1 | 3.6477 | 1 | 3.6477 | 1
229 | Classroom |  | 0 | Yes | 20 | 589 | 13 | 13 |  | 8 | 4712 | 0 | 1 | 0 | 0 | 20 | 3
231 | Office | 150 | 10 |  |  | 210 | 4 | 4 | UV | 8 | 1680 | 5.3571 | 1 | 5.3571 | 2 | 5.3571 | 2
232 | Health Suite | 221 | 14 |  |  | 464 | 10 | 10 | OAS-1A & OAS-1B | 8 | 3712 | 3.5722 | 1 | 3.5722 | 1 | 3.5722 | 1
232B | Storage | 0 | 0 |  |  | 45 | 1 | 0 | OAS-1A & OAS-1B | 8 | 360 | 0 | 1 | 0 | 0 | 0 | 0
232C | Nurse Health | 0 | 0 |  |  | 99 | 2 | 0 | AC | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
232D | Nurse Health | 0 | 0 |  |  | 106 | 2 | 0 | AC | 8 | 848 | 0 | 1 | 0 | 0 | 0 | 0
238 | Conference | 119 | 7 |  |  | 228 | 5 | 5 | OAS-1A & OAS-1B | 8 | 1824 | 3.9145 | 1 | 3.9145 | 1 | 3.9145 | 1
240 | Office | 131 | 8 |  |  | 143 | 3 | 3 | OAS-1A & OAS-1B | 8 | 1144 | 6.8706 | 1 | 6.8706 | 2 | 6.8706 | 2
242 | Storage | 146 | 9 |  |  | 71 | 1 | 1 | OAS-1A & OAS-1B | 8 | 568 | 15.4225 | 1 | 15.4225 | 3 | 15.4225 | 3
244 | Office | 124 | 8 |  |  | 143 | 3 | 3 | OAS-1A & OAS-1B | 8 | 1144 | 6.5035 | 1 | 6.5035 | 2 | 6.5035 | 2
246 | Open Work Area | 119 | 7 |  |  | 252 | 5 | 5 | OAS-1A & OAS-1B | 8 | 2016 | 3.5417 | 1 | 3.5417 | 1 | 3.5417 | 1
248 | Office | 135 | 9 |  |  | 143 | 3 | 3 | OAS-1A & OAS-1B | 8 | 1144 | 7.0804 | 1 | 7.0804 | 2 | 7.0804 | 2
250 | Main Office | 408 | 27 |  |  | 675 | 15 | 15 | UV | 8 | 5400 | 4.5333 | 1 | 4.5333 | 2 | 4.5333 | 2
300 | Collaboration | 25 | 1 |  |  | 264 | 6 | 1 | OAS-1A & OAS-1B | 8 | 2112 | 0.71023 | 1 | 0.71023 | 0 | 0.71023 | 0
301 | Classroom | 192 | 12 |  |  | 792 | 18 | 12 | UV | 8 | 6336 | 1.8182 | 1 | 1.8182 | 1 | 1.8182 | 1
302 | Classroom | 233 | 15 |  |  | 900 | 20 | 15 | UV | 8 | 7200 | 1.9417 | 1 | 1.9417 | 1 | 1.9417 | 1
304 | Classroom | 255 | 17 |  |  | 851 | 19 | 17 | UV | 8 | 6808 | 2.2474 | 1 | 2.2474 | 1 | 2.2474 | 1
306 | Classroom | 218 | 14 |  |  | 897 | 20 | 14 | UV | 8 | 7176 | 1.8227 | 1 | 1.8227 | 1 | 1.8227 | 1
308 | Classroom | 206 | 13 |  |  | 759 | 17 | 13 | UV | 8 | 6072 | 2.0356 | 1 | 2.0356 | 1 | 2.0356 | 1
309 | Classroom | 308 | 20 |  |  | 736 | 16 | 16 | UV | 8 | 5888 | 3.1386 | 1 | 3.1386 | 1 | 3.1386 | 1
311 | Classroom | 301 | 20 |  |  | 576 | 13 | 13 | UV | 8 | 4608 | 3.9193 | 1 | 3.9193 | 1 | 3.9193 | 1
315 | Classroom | 138 | 9 |  |  | 759 | 17 | 9 | UV | 8 | 6072 | 1.3636 | 1 | 1.3636 | 1 | 1.3636 | 1
316 | Classroom | 482 | 32 |  |  | 759 | 17 | 17 | UV | 8 | 6072 | 4.7628 | 1 | 4.7628 | 2 | 4.7628 | 2
317 | Classroom | 182 | 12 | Yes | 20 | 1173 | 26 | 26 | UV | 8 | 9384 | 1.1637 | 1 | 1.1637 | 1 | 21.1637 | 3
318 | Classroom | 146 | 9 | Yes | 20 | 713 | 16 | 16 | UV | 8 | 5704 | 1.5358 | 1 | 1.5358 | 1 | 21.5358 | 3
319 | Classroom | 209 | 13 |  |  | 736 | 16 | 13 | UV | 8 | 5888 | 2.1298 | 1 | 2.1298 | 1 | 2.1298 | 1
320 | Classroom | 165 | 11 |  |  | 736 | 16 | 11 | UV | 8 | 5888 | 1.6814 | 1 | 1.6814 | 1 | 1.6814 | 1
321A | Office | 96 | 6 |  |  | 154 | 3 | 3 | UV | 8 | 1232 | 4.6753 | 1 | 4.6753 | 2 | 4.6753 | 2
321B | Storage | 289 | 19 |  |  | 154 | 3 | 3 | UV | 8 | 1232 | 14.0747 | 1 | 14.0747 | 3 | 14.0747 | 3
322 | Classroom | 154 | 10 | Yes | 20 | 736 | 16 | 16 | UV | 8 | 5888 | 1.5693 | 1 | 1.5693 | 1 | 21.5693 | 3
324 | Classroom | 0 | 0 |  |  | 558 | 12 | 0 | UV | 8 | 4464 | 0 | 1 | 0 | 0 | 0 | 0
326 | Classroom | 225 | 15 |  |  | 900 | 20 | 15 | UV | 8 | 7200 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
327 | Office | 236 | 15 |  |  | 240 | 5 | 5 | UV | 8 | 1920 | 7.375 | 1 | 7.375 | 2 | 7.375 | 2
328 | LSS Community Rm | 43 | 2 |  |  | 288 | 6 | 2 | OAS-1A & OAS-1B | 8 | 2304 | 1.1198 | 1 | 1.1198 | 1 | 1.1198 | 1
329 | Classroom | 224 | 14 |  |  | 936 | 21 | 14 | UV | 8 | 7488 | 1.7949 | 1 | 1.7949 | 1 | 1.7949 | 1
400 | Collaboration | 0 | 0 |  |  | 264 | 6 | 0 | OAS-1A & OAS-1B | 8 | 2112 | 0 | 1 | 0 | 0 | 0 | 0
401 | Classroom | 0 | 0 |  |  | 759 | 17 | 0 | UV | 8 | 6072 | 0 | 1 | 0 | 0 | 0 | 0
402 | Classroom | 264 | 17 |  |  | 1311 | 29 | 17 | UV | 8 | 10488 | 1.5103 | 1 | 1.5103 | 1 | 1.5103 | 1
404 | Classroom | 250 | 16 |  |  | 345 | 7 | 7 | UV | 8 | 2760 | 5.4348 | 1 | 5.4348 | 2 | 5.4348 | 2
406 | Classroom | 330 | 22 |  |  | 1311 | 29 | 22 | UV | 8 | 10488 | 1.8879 | 1 | 1.8879 | 1 | 1.8879 | 1
407 | Classroom | 258 | 17 |  |  | 736 | 16 | 16 | UV | 8 | 5888 | 2.6291 | 1 | 2.6291 | 1 | 2.6291 | 1
409 | Classroom | 97 | 6 |  |  | 736 | 16 | 6 | UV | 8 | 5888 | 0.98845 | 1 | 0.98845 | 0 | 0.98845 | 0
411 | Classroom | 648 | 43 |  |  | 552 | 12 | 12 | UV | 8 | 4416 | 8.8043 | 1 | 8.8043 | 2 | 8.8043 | 2
415 | Classroom | 178 | 11 |  |  | 759 | 17 | 11 | UV | 8 | 6072 | 1.7589 | 1 | 1.7589 | 1 | 1.7589 | 1
416 | Classroom | 155 | 10 |  |  | 851 | 19 | 10 | UV | 8 | 6808 | 1.366 | 1 | 1.366 | 1 | 1.366 | 1
417 | Classroom | 3 | 0 |  |  | 713 | 16 | 0 | UV | 8 | 5704 | 0.031557 | 1 | 0.031557 | 0 | 0.031557 | 0
418 | Classroom | 182 | 12 |  |  | 851 | 19 | 12 | UV | 8 | 6808 | 1.604 | 1 | 1.604 | 1 | 1.604 | 1
419 | Classroom | 219 | 14 |  |  | 736 | 16 | 14 | UV | 8 | 5888 | 2.2317 | 1 | 2.2317 | 1 | 2.2317 | 1
420 | Classroom | 162 | 10 |  |  | 828 | 18 | 10 | UV | 8 | 6624 | 1.4674 | 1 | 1.4674 | 1 | 1.4674 | 1
421 | Office | 86 | 5 |  |  | 529 | 12 | 5 | UV | 8 | 4232 | 1.2193 | 1 | 1.2193 | 1 | 1.2193 | 1
422 | Classroom | 132 | 8 |  |  | 828 | 18 | 8 | UV | 8 | 6624 | 1.1957 | 1 | 1.1957 | 1 | 1.1957 | 1
424 | Office | 158 | 10 |  |  | 99 | 2 | 2 | UV | 8 | 792 | 11.9697 | 1 | 11.9697 | 3 | 11.9697 | 3
426 | Classroom | 73 | 4 |  |  | 900 | 20 | 4 | UV | 8 | 7200 | 0.60833 | 1 | 0.60833 | 0 | 0.60833 | 0
427 | Classroom | 339 | 22 |  |  | 1200 | 27 | 22 | UV | 8 | 9600 | 2.1187 | 1 | 2.1187 | 1 | 2.1187 | 1
428 | Collaboration | 62 | 4 |  |  | 444 | 10 | 4 | OAS-1A & OAS-1B | 8 | 3552 | 1.0473 | 1 | 1.0473 | 1 | 1.0473 | 1
500 | Collaboration | 22 | 1 |  |  | 322 | 7 | 1 | OAS-1A & OAS-1B | 8 | 2576 | 0.51242 | 1 | 0.51242 | 0 | 0.51242 | 0
501 | Classroom | 201 | 13 |  |  | 825 | 18 | 13 | UV | 8 | 6600 | 1.8273 | 1 | 1.8273 | 1 | 1.8273 | 1
502 | Classroom | 681 | 45 |  |  | 1380 | 31 | 31 | UV | 8 | 11040 | 3.7011 | 1 | 3.7011 | 1 | 3.7011 | 1
504 | Storage | 216 | 14 |  |  | 352 | 8 | 8 | UV | 8 | 2816 | 4.6023 | 1 | 4.6023 | 2 | 4.6023 | 2
506 | Classroom | 477 | 31 |  |  | 1357 | 30 | 30 | UV | 8 | 10856 | 2.6363 | 1 | 2.6363 | 1 | 2.6363 | 1
507 | Classroom | 155 | 10 |  |  | 851 | 19 | 10 | UV | 8 | 6808 | 1.366 | 1 | 1.366 | 1 | 1.366 | 1
509 | Classroom | 194 | 12 |  |  | 805 | 18 | 12 | UV | 8 | 6440 | 1.8075 | 1 | 1.8075 | 1 | 1.8075 | 1
515 | Classroom | 269 | 17 |  |  | 920 | 20 | 17 | UV | 8 | 7360 | 2.1929 | 1 | 2.1929 | 1 | 2.1929 | 1
516 | Classroom | 162 | 10 |  |  | 1012 | 23 | 10 | UV | 8 | 8096 | 1.2006 | 1 | 1.2006 | 1 | 1.2006 | 1
517 | Classroom | 647 | 43 |  |  | 943 | 21 | 21 | UV | 8 | 7544 | 5.1458 | 1 | 5.1458 | 2 | 5.1458 | 2
518 | Classroom | 73 | 4 |  |  | 851 | 19 | 4 | UV | 8 | 6808 | 0.64336 | 1 | 0.64336 | 0 | 0.64336 | 0
519 | Classroom | 201 | 13 |  |  | 693 | 15 | 13 | UV | 8 | 5544 | 2.1753 | 1 | 2.1753 | 1 | 2.1753 | 1
520 | Classroom | 515 | 34 |  |  | 858 | 19 | 19 | UV | 8 | 6864 | 4.5017 | 1 | 4.5017 | 2 | 4.5017 | 2
522A | Office | 21 | 1 |  |  | 100 | 2 | 1 | OAS-1A & OAS-1B | 8 | 800 | 1.575 | 1 | 1.575 | 1 | 1.575 | 1
523 | Classroom | 950 | 63 |  |  | 1344 | 30 | 30 | UV | 8 | 10752 | 5.3013 | 1 | 5.3013 | 2 | 5.3013 | 2
524 | Staff Lounge | 527 | 35 |  |  | 375 | 8 | 8 | UV | 8 | 3000 | 10.54 | 1 | 10.54 | 3 | 10.54 | 3
526 | Classroom | 1235 | 82 |  |  | 1175 | 26 | 26 | UV | 8 | 9400 | 7.883 | 1 | 7.883 | 2 | 7.883 | 2
601 | Classroom | 231 | 15 |  |  | 936 | 21 | 15 | UV | 8 | 7488 | 1.851 | 1 | 1.851 | 1 | 1.851 | 1
602 | Classroom | 325 | 21 |  |  | 920 | 20 | 20 | UV | 8 | 7360 | 2.6495 | 1 | 2.6495 | 1 | 2.6495 | 1
603 | Production Studio | 25 | 1 |  |  | 160 | 3 | 1 | OAS-1A & OAS-1B | 8 | 1280 | 1.1719 | 1 | 1.1719 | 1 | 1.1719 | 1
603A | Control Rm | 25 | 1 |  |  | 96 | 2 | 1 | OAS-1A & OAS-1B | 8 | 768 | 1.9531 | 1 | 1.9531 | 1 | 1.9531 | 1
604 | Classroom | 568 | 37 |  |  | 460 | 10 | 10 | UV | 8 | 3680 | 9.2609 | 1 | 9.2609 | 2 | 9.2609 | 2
605 | Classroom | 609 | 40 |  |  | 1152 | 26 | 26 | UV | 8 | 9216 | 3.9648 | 1 | 3.9648 | 1 | 3.9648 | 1
606 | Classroom | 140 | 9 |  |  | 621 | 14 | 9 | UV | 8 | 4968 | 1.6908 | 1 | 1.6908 | 1 | 1.6908 | 1
609 | Classroom | 614 | 40 |  |  | 900 | 20 | 20 | UV | 8 | 7200 | 5.1167 | 1 | 5.1167 | 2 | 5.1167 | 2
611 | Classroom | 256 | 17 |  |  | 900 | 20 | 17 | UV | 8 | 7200 | 2.1333 | 1 | 2.1333 | 1 | 2.1333 | 1
612 | Classroom | 208 | 13 |  |  | 714 | 16 | 13 | UV | 8 | 5712 | 2.1849 | 1 | 2.1849 | 1 | 2.1849 | 1
613 | Classroom | 564 | 37 |  |  | 792 | 18 | 18 | UV | 8 | 6336 | 5.3409 | 1 | 5.3409 | 2 | 5.3409 | 2
614 | Classroom | 290 | 19 |  |  | 756 | 17 | 17 | UV | 8 | 6048 | 2.877 | 1 | 2.877 | 1 | 2.877 | 1
615 | Storage | 261 | 17 |  |  | 336 | 7 | 7 | UV | 8 | 2688 | 5.8259 | 1 | 5.8259 | 2 | 5.8259 | 2
616 | Classroom | 265 | 17 |  |  | 900 | 20 | 17 | UV | 8 | 7200 | 2.2083 | 1 | 2.2083 | 1 | 2.2083 | 1
617 | Office | 92 | 6 |  |  | 300 | 6 | 6 | UV | 8 | 2400 | 2.3 | 1 | 2.3 | 1 | 2.3 | 1
620 | Classroom | 750 | 50 |  |  | 900 | 20 | 20 | UV | 8 | 7200 | 6.25 | 1 | 6.25 | 2 | 6.25 | 2
620 | Classroom | 567 | 37 |  |  | 2304 | 52 | 37 | UV | 8 | 18432 | 1.8457 | 1 | 1.8457 | 1 | 1.8457 | 1
- | Auditorium | 1102 | 73 |  |  | 8648 | 196 | 73 | AHU | 8 | 69184 | 0.95571 | 1.4912 | 1.4251 | 1 | 1.4251 | 1
- | Faculty/Office | 0 | 0 |  |  | 330 | 7 | 0 | AC | 8 | 2640 | 0 | 1 | 0 | 0 | 0 | 0
- | Practice Room 1 | 0 | 0 |  |  | 77 | 1 | 0 | HV | 8 | 616 | 0 | 1 | 0 | 0 | 0 | 0
- | Practice Room 2 | 0 | 0 |  |  | 77 | 1 | 0 | HV | 8 | 616 | 0 | 1 | 0 | 0 | 0 | 0
- | Practice Room 3 | 0 | 0 |  |  | 77 | 1 | 0 | HV | 8 | 616 | 0 | 1 | 0 | 0 | 0 | 0
- | Kitchen Office | 15 | 1 |  |  | 99 | 2 | 1 | RTU | 8 | 792 | 1.1364 | 1 | 1.1364 | 1 | 1.1364 | 1
- | Weight Room | 163 | 10 |  |  | 1632 | 37 | 10 | AHU | 8 | 13056 | 0.74908 | 1 | 0.74908 | 0 | 0.74908 | 0
Sheet Last Modified: | 2021-04-27
School: | Franklin Learning Center
Vendor: | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 318 | 21 |  |  | 840 | 19 | 19 |  | 8 | 6720 | 2.8393 | 1 | 2.8393 | 1 | 2.8393 | 1
101/102 | Classroom | 144 | 9 |  |  | 1426 | 32 | 9 |  | 8 | 11408 | 0.75736 | 1 | 0.75736 | 0 | 0.75736 | 0
103 / 104 | Conference | 811 | 54 |  |  | 1612 | 36 | 36 |  | 8 | 12896 | 3.7733 | 1 | 3.7733 | 1 | 3.7733 | 1
105 | Classroom | 186 | 12 |  |  | 690 | 15 | 12 |  | 8 | 5520 | 2.0217 | 1 | 2.0217 | 1 | 2.0217 | 1
108 | ESOL |  | 0 |  |  | 242 | 5 | 0 |  | 8 | 1936 | 0 | 1 | 0 | 0 | 0 | 0
111 | Classroom | 44 | 2 |  |  | 221 | 5 | 2 |  | 8 | 1768 | 1.4932 | 1 | 1.4932 | 1 | 1.4932 | 1
120 | Classroom | 528 | 35 |  |  | 625 | 14 | 14 |  | 8 | 5000 | 6.336 | 1 | 6.336 | 2 | 6.336 | 2
121 | Classroom | 486 | 32 |  |  | 806 | 18 | 18 |  | 8 | 6448 | 4.5223 | 1 | 4.5223 | 2 | 4.5223 | 2
122 | Classroom | 640 | 42 |  |  | 744 | 16 | 16 |  | 8 | 5952 | 6.4516 | 1 | 6.4516 | 2 | 6.4516 | 2
123 | Classroom | 705 | 47 |  |  | 660 | 15 | 15 |  | 8 | 5280 | 8.0114 | 1 | 8.0114 | 2 | 8.0114 | 2
124 | Classroom | 504 | 33 |  |  | 266 | 6 | 6 |  | 8 | 2128 | 14.2105 | 1 | 14.2105 | 3 | 14.2105 | 3
125 | Classroom | 615 | 41 |  |  | 575 | 13 | 13 |  | 8 | 4600 | 8.0217 | 1 | 8.0217 | 2 | 8.0217 | 2
126 | Classroom | 615 | 41 |  |  | 275 | 6 | 6 |  | 8 | 2200 | 16.7727 | 1 | 16.7727 | 3 | 16.7727 | 3
129 | Classroom | 238 | 15 |  |  | 675 | 15 | 15 |  | 8 | 5400 | 2.6444 | 1 | 2.6444 | 1 | 2.6444 | 1
132 | Classroom | 264 | 17 |  |  | 414 | 9 | 9 |  | 8 | 3312 | 4.7826 | 1 | 4.7826 | 2 | 4.7826 | 2
132a | Classroom | 391 | 26 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 4.25 | 1 | 4.25 | 2 | 4.25 | 2
133 | Classroom | 730 | 48 |  |  | 759 | 17 | 17 |  | 8 | 6072 | 7.2134 | 1 | 7.2134 | 2 | 7.2134 | 2
200 | Classroom | 447 | 29 |  |  | 950 | 21 | 21 |  | 8 | 7600 | 3.5289 | 1 | 3.5289 | 1 | 3.5289 | 1
201 | Classroom | 372 | 24 |  |  | 713 | 16 | 16 |  | 8 | 5704 | 3.913 | 1 | 3.913 | 1 | 3.913 | 1
202 | Classroom | 349 | 23 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 3.7935 | 1 | 3.7935 | 1 | 3.7935 | 1
203 / 204 | Classroom | 655 | 43 |  |  | 1426 | 32 | 32 |  | 8 | 11408 | 3.445 | 1 | 3.445 | 1 | 3.445 | 1
205 | Classroom | 294 | 19 |  |  | 713 | 16 | 16 |  | 8 | 5704 | 3.0926 | 1 | 3.0926 | 1 | 3.0926 | 1
206 | Classroom | 0 | 0 |  |  | 198 | 4 | 0 |  | 8 | 1584 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom | 37 | 2 |  |  | 925 | 21 | 2 |  | 8 | 7400 | 0.3 | 1 | 0.3 | 0 | 0.3 | 0
208 | Classroom | 314 | 20 |  |  | 782 | 17 | 17 |  | 8 | 6256 | 3.0115 | 1 | 3.0115 | 1 | 3.0115 | 1
209 | Classroom | 638 | 42 |  |  | 875 | 19 | 19 |  | 8 | 7000 | 5.4686 | 1 | 5.4686 | 2 | 5.4686 | 2
210 | Classroom | 661 | 44 |  |  | 782 | 17 | 17 |  | 8 | 6256 | 6.3395 | 1 | 6.3395 | 2 | 6.3395 | 2
212 | Classroom | 621 | 41 |  |  | 851 | 19 | 19 |  | 8 | 6808 | 5.473 | 1 | 5.473 | 2 | 5.473 | 2
213 | Classroom | 0 | 0 |  |  | 165 | 3 | 0 |  | 8 | 1320 | 0 | 1 | 0 | 0 | 0 | 0
214 | Classroom | 580 | 38 |  |  | 625 | 14 | 14 |  | 8 | 5000 | 6.96 | 1 | 6.96 | 2 | 6.96 | 2
215 | Classroom | 446 | 29 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 4.6458 | 1 | 4.6458 | 2 | 4.6458 | 2
216 | Classroom | 486 | 32 |  |  | 960 | 21 | 21 |  | 8 | 7680 | 3.7969 | 1 | 3.7969 | 1 | 3.7969 | 1
217 | Classroom | 410 | 27 |  |  | 960 | 21 | 21 |  | 8 | 7680 | 3.2031 | 1 | 3.2031 | 1 | 3.2031 | 1
218 | Classroom | 377 | 25 |  |  | 600 | 13 | 13 |  | 8 | 4800 | 4.7125 | 1 | 4.7125 | 2 | 4.7125 | 2
220 | Classroom | 174 | 11 |  |  | 980 | 22 | 11 |  | 8 | 7840 | 1.3316 | 1 | 1.3316 | 1 | 1.3316 | 1
221 | IMC/ Library | 433 | 28 |  |  | 1536 | 34 | 28 |  | 8 | 12288 | 2.1143 | 1 | 2.1143 | 1 | 2.1143 | 1
221 | Office | 210 | 14 |  |  | 154 | 3 | 3 |  | 8 | 1232 | 10.2273 | 1 | 10.2273 | 3 | 10.2273 | 3
300 | Classroom | 88 | 5 |  |  | 900 | 20 | 5 |  | 8 | 7200 | 0.73333 | 1 | 0.73333 | 0 | 0.73333 | 0
301 | Classroom | 215 | 14 |  |  | 506 | 11 | 11 |  | 8 | 4048 | 3.1868 | 1 | 3.1868 | 1 | 3.1868 | 1
302 | Classroom | 403 | 26 |  |  | 975 | 22 | 22 |  | 8 | 7800 | 3.1 | 1 | 3.1 | 1 | 3.1 | 1
303 | Classroom | 368 | 24 |  |  | 936 | 21 | 21 |  | 8 | 7488 | 2.9487 | 1 | 2.9487 | 1 | 2.9487 | 1
304 | Classroom | 287 | 19 |  |  | 575 | 13 | 13 |  | 8 | 4600 | 3.7435 | 1 | 3.7435 | 1 | 3.7435 | 1
305 | Classroom | 392 | 26 |  |  | 713 | 16 | 16 |  | 8 | 5704 | 4.1234 | 1 | 4.1234 | 2 | 4.1234 | 2
306 | Classroom | 168 | 11 |  |  | 297 | 6 | 6 |  | 8 | 2376 | 4.2424 | 1 | 4.2424 | 2 | 4.2424 | 2
307 | Classroom | 729 | 48 |  |  | 700 | 15 | 15 |  | 8 | 5600 | 7.8107 | 1 | 7.8107 | 2 | 7.8107 | 2
309 | Classroom | 443 | 29 |  |  | 480 | 10 | 10 |  | 8 | 3840 | 6.9219 | 1 | 6.9219 | 2 | 6.9219 | 2
310 | Medical Classroom | 1312 | 87 |  |  | 1403 | 31 | 31 |  | 8 | 11224 | 7.0135 | 1 | 7.0135 | 2 | 7.0135 | 2
310 | Doctor's Office | 3 | 0 |  |  | 77 | 1 | 0 |  | 8 | 616 | 0.29221 | 1 | 0.29221 | 0 | 0.29221 | 0
310 | Bathroom | 12 | 0 |  |  | 120 | 2 | 0 |  | 8 | 960 | 0.75 | 1 | 0.75 | 0 | 0.75 | 0
310 | Storage | 11 | 0 |  |  | 140 | 3 | 0 |  | 8 | 1120 | 0.58929 | 1 | 0.58929 | 0 | 0.58929 | 0
312 | Classroom | 538 | 35 |  |  | 575 | 13 | 13 |  | 8 | 4600 | 7.0174 | 1 | 7.0174 | 2 | 7.0174 | 2
312 | Councelor | 0 | 0 |  |  | 950 | 21 | 0 |  | 8 | 7600 | 0 | 1 | 0 | 0 | 0 | 0
315 | Classroom | 255 | 17 |  |  | 675 | 15 | 15 |  | 8 | 5400 | 2.8333 | 1 | 2.8333 | 1 | 2.8333 | 1
316 | Classroom | 353 | 23 |  |  | 644 | 14 | 14 |  | 8 | 5152 | 4.111 | 1 | 4.111 | 2 | 4.111 | 2
317 | Classroom | 465 | 31 |  |  | 950 | 21 | 21 |  | 8 | 7600 | 3.6711 | 1 | 3.6711 | 1 | 3.6711 | 1
318 | Classroom | 465 | 31 |  |  | 897 | 20 | 20 |  | 8 | 7176 | 3.888 | 1 | 3.888 | 1 | 3.888 | 1
318 | Prep Room / Chemistry |  | 0 |  |  | 156 | 3 | 0 |  | 8 | 1248 | 0 | 1 | 0 | 0 | 0 | 0
318 | Secure Closet |  | 0 |  |  |  | 0 | 0
319 | Classroom | 263 | 17 |  |  | 575 | 13 | 13 |  | 8 | 4600 | 3.4304 | 1 | 3.4304 | 1 | 3.4304 | 1
321 | Classroom | 506 | 33 |  |  | 588 | 13 | 13 |  | 8 | 4704 | 6.4541 | 1 | 6.4541 | 2 | 6.4541 | 2
322 | Computer | 0 | 0 |  |  | 299 | 6 | 0 |  | 8 | 2392 | 0 | 1 | 0 | 0 | 0 | 0
323 | Classroom | 374 | 24 |  |  | 598 | 13 | 13 |  | 8 | 4784 | 4.6906 | 1 | 4.6906 | 2 | 4.6906 | 2
324 | Classroom | 104 | 6 |  |  | 552 | 12 | 6 |  | 8 | 4416 | 1.413 | 1 | 1.413 | 1 | 1.413 | 1
325 | Classroom | 118 | 7 |  |  | 594 | 13 | 7 |  | 8 | 4752 | 1.4899 | 1 | 1.4899 | 1 | 1.4899 | 1
- | Cafeteria | 1320 | 88 |  |  | 2808 | 63 | 63 |  | 8 | 22464 | 3.5256 | 1.062 | 3.7444 | 1 | 3.7444 | 1
- | Gym |  | 0 |  |  | 3649 | 82 | 0 |  | 8 | 29192 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Office | 58 | 3 |  |  | 230 | 5 | 3 |  | 8 | 1840 | 1.8913 | 1 | 1.8913 | 1 | 1.8913 | 1
- | Office | 223 | 14 |  |  | 567 | 12 | 12 |  | 8 | 4536 | 2.9497 | 1 | 2.9497 | 1 | 2.9497 | 1
Sheet Last Modified: | 2021-04-29
School: | Horace H. Furness High School
Vendor: | Chadwick | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom |  | 0 |  |  | 1224 | 27 | 0 |  | 8 | 9792 | 0 | 1 | 0 | 0 | 0 | 0
3 | Classroom |  | 0 |  |  | 672 | 15 | 0 |  | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
4 | Classroom |  | 0 |  |  | 840 | 19 | 0 |  | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
5 | Classroom |  | 0 |  |  | 840 | 19 | 0 |  | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom | 306 | 20 |  |  | 667 | 15 | 15 |  | 8 | 5336 | 3.4408 | 1 | 3.4408 | 1 | 3.4408 | 1
102 | Classroom |  | 0 |  |  | 768 | 17 | 0 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
103 | classroom | 297 | 19 |  |  | 667 | 15 | 15 |  | 8 | 5336 | 3.3396 | 1 | 3.3396 | 1 | 3.3396 | 1
104 | Classroom |  | 0 |  |  | 896 | 20 | 0 |  | 8 | 7168 | 0 | 1 | 0 | 0 | 0 | 0
105 | classroom |  | 0 |  |  | 667 | 15 | 0 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 0 | 0
106 | classroom | 326 | 21 |  |  | 667 | 15 | 15 |  | 8 | 5336 | 3.6657 | 1 | 3.6657 | 1 | 3.6657 | 1
107 | Library | 1463 | 97 |  |  | 2448 | 55 | 55 |  | 8 | 19584 | 4.4822 | 1 | 4.4822 | 2 | 4.4822 | 2
112 | Classroom |  | 0 |  |  | 448 | 10 | 0 |  | 8 | 3584 | 0 | 1 | 0 | 0 | 0 | 0
201 | classroom | 272 | 18 |  |  | 735 | 16 | 16 |  | 8 | 5880 | 2.7755 | 1 | 2.7755 | 1 | 2.7755 | 1
201A | Room |  | 0 |  |  | 448 | 10 | 0 |  | 8 | 3584 | 0 | 1 | 0 | 0 | 0 | 0
202 | Classroom |  | 0 |  |  | 1536 | 34 | 0 |  | 8 | 12288 | 0 | 1 | 0 | 0 | 0 | 0
203 | classroom | 540 | 36 |  |  | 874 | 19 | 19 |  | 8 | 6992 | 4.6339 | 1 | 4.6339 | 2 | 4.6339 | 2
204 | classroom | 443 | 29 |  |  | 814 | 18 | 18 |  | 8 | 6512 | 4.0817 | 1 | 4.0817 | 2 | 4.0817 | 2
205 | classroom | 392 | 26 |  |  | 667 | 15 | 15 |  | 8 | 5336 | 4.4078 | 1 | 4.4078 | 2 | 4.4078 | 2
206 | classroom |  | 0 |  |  | 667 | 15 | 0 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 0 | 0
207 | classroom |  | 0 |  |  | 720 | 16 | 0 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
208 | classroom | 328 | 21 |  |  | 660 | 15 | 15 |  | 8 | 5280 | 3.7273 | 1 | 3.7273 | 1 | 3.7273 | 1
209 | classroom |  | 0 |  |  | 725 | 16 | 0 |  | 8 | 5800 | 0 | 1 | 0 | 0 | 0 | 0
210 | classroom |  | 0 |  |  | 696 | 15 | 0 |  | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
211 | classroom | 319 | 21 |  |  | 696 | 15 | 15 |  | 8 | 5568 | 3.4375 | 1 | 3.4375 | 1 | 3.4375 | 1
212 | classroom | 359 | 23 |  |  | 696 | 15 | 15 |  | 8 | 5568 | 3.8685 | 1 | 3.8685 | 1 | 3.8685 | 1
213 | classroom | 316 | 21 |  |  | 696 | 15 | 15 |  | 8 | 5568 | 3.4052 | 1 | 3.4052 | 1 | 3.4052 | 1
214 | classroom |  | 0 |  |  | 696 | 15 | 0 |  | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
215 | Classroom |  | 0 |  |  | 576 | 13 | 0 |  | 8 | 4608 | 0 | 1 | 0 | 0 | 0 | 0
218 | classroom | 367 | 24 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 3.8229 | 1 | 3.8229 | 1 | 3.8229 | 1
219A | classroom |  | 0 |  |  | 783 | 17 | 0 |  | 8 | 6264 | 0 | 1 | 0 | 0 | 0 | 0
219B | classroom | 275 | 18 |  |  | 1100 | 25 | 18 |  | 8 | 8800 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
220 | classroom | 292 | 19 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 3.1739 | 1 | 3.1739 | 1 | 3.1739 | 1
221 | classroom | 490 | 32 |  |  | 770 | 17 | 17 |  | 8 | 6160 | 4.7727 | 1 | 4.7727 | 2 | 4.7727 | 2
221A | classroom | 380 | 25 |  |  | 770 | 17 | 17 |  | 8 | 6160 | 3.7013 | 1 | 3.7013 | 1 | 3.7013 | 1
222 | classroom |  | 0 |  |  | 161 | 3 | 0 |  | 8 | 1288 | 0 | 1 | 0 | 0 | 0 | 0
222A | Room |  | 0 |  |  | 560 | 12 | 0 |  | 8 | 4480 | 0 | 1 | 0 | 0 | 0 | 0
301A | classroom 301 | 360 | 24 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 3.913 | 1 | 3.913 | 1 | 3.913 | 1
301B | classroom 301 | 345 | 23 |  |  | 672 | 15 | 15 |  | 8 | 5376 | 3.8504 | 1 | 3.8504 | 1 | 3.8504 | 1
302A | classroom 302 | 272 | 18 |  |  | 1056 | 24 | 18 |  | 8 | 8448 | 1.9318 | 1 | 1.9318 | 1 | 1.9318 | 1
302B | classroom 302 | 356 | 23 |  |  | 624 | 14 | 14 |  | 8 | 4992 | 4.2788 | 1 | 4.2788 | 2 | 4.2788 | 2
303 | classroom | 438 | 29 |  |  | 770 | 17 | 17 |  | 8 | 6160 | 4.2662 | 1 | 4.2662 | 2 | 4.2662 | 2
304 | classroom |  | 0 |  |  | 690 | 15 | 0 |  | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
305 | classroom |  | 0 |  |  | 672 | 15 | 0 |  | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
306 | classroom |  | 0 |  |  | 720 | 16 | 0 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
307 | classroom |  | 0 |  |  | 720 | 16 | 0 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
308 | classroom | 246 | 16 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 2.5625 | 1 | 2.5625 | 1 | 2.5625 | 1
309 | classroom |  | 0 |  |  | 720 | 16 | 0 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
310A | classroom |  | 0 |  |  | 1008 | 22 | 0 |  | 8 | 8064 | 0 | 1 | 0 | 0 | 0 | 0
310b | classroom |  | 0 |  |  | 1344 | 30 | 0 |  | 8 | 10752 | 0 | 1 | 0 | 0 | 0 | 0
311A | classroom | 201 | 13 |  |  | 1008 | 22 | 13 |  | 8 | 8064 | 1.4955 | 1 | 1.4955 | 1 | 1.4955 | 1
311B | classroom |  | 0 |  |  | 1148 | 26 | 0 |  | 8 | 9184 | 0 | 1 | 0 | 0 | 0 | 0
312A | classroom |  | 0 |  |  | 960 | 21 | 0 |  | 8 | 7680 | 0 | 1 | 0 | 0 | 0 | 0
312B | classroom |  | 0 |  |  | 400 | 9 | 0 |  | 8 | 3200 | 0 | 1 | 0 | 0 | 0 | 0
313A | classroom | 175 | 11 |  |  | 1008 | 22 | 11 |  | 8 | 8064 | 1.3021 | 1 | 1.3021 | 1 | 1.3021 | 1
313B | classroom |  | 0 |  |  | 480 | 10 | 0 |  | 8 | 3840 | 0 | 1 | 0 | 0 | 0 | 0
314 | Classroom |  | 0 |  |  | 448 | 10 | 0 |  | 8 | 3584 | 0 | 1 | 0 | 0 | 0 | 0
315 | Classroom |  | 0 |  |  | 392 | 8 | 0 |  | 8 | 3136 | 0 | 1 | 0 | 0 | 0 | 0
316 | classroom | 73 | 4 |  |  | 696 | 15 | 4 |  | 8 | 5568 | 0.78664 | 1 | 0.78664 | 0 | 0.78664 | 0
317A | classroom |  | 0 |  |  | 1137 | 25 | 0 |  | 8 | 9096 | 0 | 1 | 0 | 0 | 0 | 0
317B | classroom | 117 | 7 |  |  | 1008 | 22 | 7 |  | 8 | 8064 | 0.87054 | 1 | 0.87054 | 0 | 0.87054 | 0
318A | classroom |  | 0 |  |  | 1152 | 26 | 0 |  | 8 | 9216 | 0 | 1 | 0 | 0 | 0 | 0
318B | classroom |  | 0 |  |  | 720 | 16 | 0 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
319A | classroom | 392 | 26 |  |  | 1056 | 24 | 24 |  | 8 | 8448 | 2.7841 | 1 | 2.7841 | 1 | 2.7841 | 1
319B | classroom | 215 | 14 |  |  | 320 | 7 | 7 |  | 8 | 2560 | 5.0391 | 1 | 5.0391 | 2 | 5.0391 | 2
320A | classroom |  | 0 |  |  | 920 | 20 | 0 |  | 8 | 7360 | 0 | 1 | 0 | 0 | 0 | 0
320B | classroom |  | 0 |  |  | 1056 | 24 | 0 |  | 8 | 8448 | 0 | 1 | 0 | 0 | 0 | 0
321A | classroom |  | 0 |  |  | 1056 | 24 | 0 |  | 8 | 8448 | 0 | 1 | 0 | 0 | 0 | 0
321B | classroom | 302 | 20 |  |  | 1056 | 24 | 20 |  | 8 | 8448 | 2.1449 | 1 | 2.1449 | 1 | 2.1449 | 1
- | Cafeteria | 153 | 10 |  |  | 3665 | 83 | 10 |  | 8 | 29320 | 0.3131 | 1.062 | 0.33252 | 0 | 0.33252 | 0
Main Office | Office |  | 0 |  |  | 1248 | 28 | 0 |  | 8 | 9984 | 0 | 1 | 0 | 0 | 0 | 0
Assistant Principal | Office |  | 0 |  |  | 360 | 8 | 0 |  | 8 | 2880 | 0 | 1 | 0 | 0 | 0 | 0
Burke | Office |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
SSO | Office |  | 0 |  |  | 240 | 5 | 0 |  | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
Nurse | Suite |  | 0 |  |  | 960 | 21 | 0 |  | 8 | 7680 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23
School: | Girard Academic Music Program (GAMP) High School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | CAFE | 9130 | 608 |  |  | 977 | 22 | 22 |  | 8 | 7816 | 70.087 | 1 | 70.087 | 5 | 70.087 | 5
- | GYM |  | 0 |  |  | 6667 | 151 | 0 |  | 8 | 53336 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | GYM OFFICE |  | 0 |  |  | 99 | 2 | 0 |  | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
- | LOWER HALF OF AUDITORIUM | 13845 | 923 |  |  | 6498 | 147 | 147 |  | 8 | 51984 | 15.9799 | 1.4912 | 23.8286 | 3 | 23.8286 | 3
- | UPPER HALF OF AUDITORIUM | 14721 | 981 |  |  | 3247 | 73 | 73 |  | 8 | 25976 | 34.0029 | 1.062 | 36.1123 | 4 | 36.1123 | 4
Principal | Office | 0 | 0 | Yes | 20 | 363 | 8 | 8 |  | 8 | 2904 | 0 | 1 | 0 | 0 | 20 | 3
Assistant Principal | Office | 0 | 0 |  |  | 169 | 3 | 0 |  | 8 | 1352 | 0 | 1 | 0 | 0 | 0 | 0
Main Office | Office | 0 | 0 | Yes | 20 | 266 | 6 | 6 |  | 8 | 2128 | 0 | 1 | 0 | 0 | 20 | 3
Counselor 1 | Office | 0 | 0 | Yes | 20 | 134 | 3 | 3 |  | 8 | 1072 | 0 | 1 | 0 | 0 | 20 | 3
Counselor 2 | Office | 0 | 0 | Yes | 20 | 246 | 5 | 5 |  | 8 | 1968 | 0 | 1 | 0 | 0 | 20 | 3
Nurse | Office | 0 | 0 | Yes | 20 | 88 | 2 | 2 |  | 8 | 704 | 0 | 1 | 0 | 0 | 20 | 3
Lunch Room | Lunch Room | 0 | 0 |  |  | 2580 | 58 | 0 |  | 8 | 20640 | 0 | 1.062 | 0 | 0 | 0 | 0
Orchestra Room | Orchestra Room | 0 | 0 | Yes | 20 | 1082 | 24 | 24 |  | 8 | 8656 | 0 | 1 | 0 | 0 | 20 | 3
Orchestra Room | Office |  | 0 |  |  | 330 | 7 |  |  | 8 | 2640 | 0 | 1 | 0 | 0 | 0 | 0
Band Room | Band Room | 0 | 0 | Yes | 20 | 1221 | 27 | 27 |  | 8 | 9768 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom | 0 | 0 | Yes | 20 | 685 | 15 | 15 |  | 8 | 5480 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom | 0 | 0 | Yes | 20 | 722 | 16 | 16 |  | 8 | 5776 | 0 | 1 | 0 | 0 | 20 | 3
104/105 | Classroom | 0 | 0 | Yes | 20 | 1063 | 24 | 24 |  | 8 | 8504 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom | 0 | 0 | Yes | 20 | 735 | 16 | 16 |  | 8 | 5880 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 20 | 695 | 15 | 15 |  | 8 | 5560 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 0 | 0 | Yes | 20 | 685 | 15 | 15 |  | 8 | 5480 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 20 | 679 | 15 | 15 |  | 8 | 5432 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 | Yes | 20 | 679 | 15 | 15 |  | 8 | 5432 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom | 0 | 0 | Yes | 20 | 715 | 16 | 16 |  | 8 | 5720 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom | 0 | 0 | Yes | 20 | 683 | 15 | 15 |  | 8 | 5464 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom | 0 | 0 | Yes | 20 | 680 | 15 | 15 |  | 8 | 5440 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom | 0 | 0 | Yes | 20 | 711 | 16 | 16 |  | 8 | 5688 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 20 | 734 | 16 | 16 |  | 8 | 5872 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 20 | 634 | 14 | 14 |  | 8 | 5072 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 | Yes | 20 | 686 | 15 | 15 |  | 8 | 5488 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom | 0 | 0 |  |  | 394 | 8 | 0 |  | 8 | 3152 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom | 0 | 0 | Yes | 20 | 689 | 15 | 15 |  | 8 | 5512 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 20 | 645 | 14 | 14 |  | 8 | 5160 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom | 0 | 0 | Yes | 20 | 669 | 15 | 15 |  | 8 | 5352 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom | 0 | 0 | Yes | 20 | 725 | 16 | 16 |  | 8 | 5800 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom | 0 | 0 | Yes | 20 | 729 | 16 | 16 |  | 8 | 5832 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 20 | 950 | 21 | 21 |  | 8 | 7600 | 0 | 1 | 0 | 0 | 20 | 3
307A | Classroom | 0 | 0 | Yes | 20 | 292 | 6 | 6 |  | 8 | 2336 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom | 0 | 0 | Yes | 20 | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 | Yes | 20 | 687 | 15 | 15 |  | 8 | 5496 | 0 | 1 | 0 | 0 | 20 | 3
311 | Classroom | 0 | 0 | Yes | 20 | 348 | 7 | 7 |  | 8 | 2784 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-12
School: | Edward Gideon Elementary School
Vendor: | Emcor Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 309 | 20 |  |  | 815 | 18 | 18 | Unit Ventilator | 8 | 6520 | 2.8436 | 1 | 2.8436 | 1 | 2.8436 | 1
102 | Classroom | 380 | 25 |  |  | 745 | 16 | 16 | Unit Ventilator | 8 | 5960 | 3.8255 | 1 | 3.8255 | 1 | 3.8255 | 1
Hallway @ 102 | Hallway | 0 | 0 |  |  |  | 0 | 0 | Unit Ventilator
- | Girls Bathroom next to Room 102 |  | 0 |  |  | 262 | 5 | 0 | N/A | 8 | 2096 | 0 | 1 | 0 | 0 | 0 | 0
- | Boys Bathroom next to Room 102 |  | 0 |  |  | 294 | 6 | 0 | N/A | 8 | 2352 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom | 247 | 16 |  |  |  | 0 | 0 | Unit Ventilator
103 A | - |  | 0 |  |  | 207 | 4 | 0 | Unit Ventilator | 8 | 1656 | 0 | 1 | 0 | 0 | 0 | 0
103 B | - |  | 0 |  |  | 175 | 3 | 0 | Unit Ventilator | 8 | 1400 | 0 | 1 | 0 | 0 | 0 | 0
104 | Classroom | 226 | 15 |  |  | 450 | 10 | 10 | Unit Ventilator | 8 | 3600 | 3.7667 | 1 | 3.7667 | 1 | 3.7667 | 1
104 A | - |  | 0 |  |  | 97 | 2 | 0 | Unit Ventilator | 8 | 776 | 0 | 1 | 0 | 0 | 0 | 0
104 B | - |  | 0 |  |  | 151 | 3 | 0 | Unit Ventilator | 8 | 1208 | 0 | 1 | 0 | 0 | 0 | 0
104 C | - |  | 0 |  |  | 134 | 3 | 0 | Unit Ventilator | 8 | 1072 | 0 | 1 | 0 | 0 | 0 | 0
104 | Counselor |  | 0 |  |  | 451 | 10 | 0 | Unit Ventilator | 8 | 3608 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom | 323 | 21 |  |  | 872 | 19 | 19 | Unit Ventilator | 8 | 6976 | 2.7781 | 1 | 2.7781 | 1 | 2.7781 | 1
Hallway @ 105 | Hallway | 325 | 21 |  |  |  | 0 | 0 | Unit Ventilator
106A | Main Office |  | 0 | Yes | 20 | 394 | 8 | 8 | Unit Ventilator | 8 | 3152 | 0 | 1 | 0 | 0 | 20 | 3
106E | Principal Office |  | 0 | Yes | 20 | 166 | 3 | 3 | Unit Ventilator | 8 | 1328 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 351 | 23 |  |  | 858 | 19 | 19 | Unit Ventilator | 8 | 6864 | 3.0682 | 1 | 3.0682 | 1 | 3.0682 | 1
110 | Classroom | 374 | 24 |  |  | 811 | 18 | 18 | Unit Ventilator | 8 | 6488 | 3.4587 | 1 | 3.4587 | 1 | 3.4587 | 1
111 | Classroom | 253 | 16 |  |  | 866 | 19 | 16 | Unit Ventilator | 8 | 6928 | 2.1911 | 1 | 2.1911 | 1 | 2.1911 | 1
113 A | School police |  | 0 |  |  | 317 | 7 | 0 | Unit Ventilator | 8 | 2536 | 0 | 1 | 0 | 0 | 0 | 0
113 b | inner office |  | 0 |  |  | 153 | 3 | 0 | Unit Ventilator | 8 | 1224 | 0 | 1 | 0 | 0 | 0 | 0
113 c | inner office |  | 0 | Yes | 20 | 164 | 3 | 3 | Unit Ventilator | 8 | 1312 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 154 | 10 |  |  | 1019 | 23 | 10 | Unit Ventilator | 8 | 8152 | 1.1335 | 1 | 1.1335 | 1 | 1.1335 | 1
Hallway @ 201 | Hallway | 225 | 15 |  |  |  | 0 | 0 | Unit Ventilator
202 | Classroom | 537 | 35 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 4.3588 | 1 | 4.3588 | 2 | 4.3588 | 2
203 | Classroom | 0 | 0 | Yes | 20 | 938 | 21 | 21 | Unit Ventilator | 8 | 7504 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom | 319 | 21 |  |  | 788 | 17 | 17 | Unit Ventilator | 8 | 6304 | 3.0362 | 1 | 3.0362 | 1 | 3.0362 | 1
205 | Classroom | 296 | 19 |  |  | 822 | 18 | 18 | Unit Ventilator | 8 | 6576 | 2.7007 | 1 | 2.7007 | 1 | 2.7007 | 1
206 | Classroom | 310 | 20 |  |  | 822 | 18 | 18 | Unit Ventilator | 8 | 6576 | 2.8285 | 1 | 2.8285 | 1 | 2.8285 | 1
Hallway @ 206 | Hallway | 0 | 0 |  |  |  | 0 | 0 | Unit Ventilator
207 | Classroom | 350 | 23 |  |  | 822 | 18 | 18 | Unit Ventilator | 8 | 6576 | 3.1934 | 1 | 3.1934 | 1 | 3.1934 | 1
- | Boys Bathroom outside Room 207 |  | 0 |  |  | 164 | 3 | 0 | N/A | 8 | 1312 | 0 | 1 | 0 | 0 | 0 | 0
208 | Classroom | 328 | 21 |  |  | 825 | 18 | 18 | Unit Ventilator | 8 | 6600 | 2.9818 | 1 | 2.9818 | 1 | 2.9818 | 1
- | Female Staff Bathroom outside Room 208 |  | 0 |  |  | 61 | 1 | 0 | N/A | 8 | 488 | 0 | 1 | 0 | 0 | 0 | 0
- | Girls Bathroom outside Room 208 |  | 0 |  |  | 127 | 2 | 0 | N/A | 8 | 1016 | 0 | 1 | 0 | 0 | 0 | 0
209 | Classroom | 310 | 20 |  |  | 822 | 18 | 18 | Unit Ventilator | 8 | 6576 | 2.8285 | 1 | 2.8285 | 1 | 2.8285 | 1
210 | Classroom | 253 | 16 |  |  | 811 | 18 | 16 | Unit Ventilator | 8 | 6488 | 2.3397 | 1 | 2.3397 | 1 | 2.3397 | 1
211 | Classroom | 262 | 17 |  |  | 829 | 18 | 17 | Unit Ventilator | 8 | 6632 | 2.3703 | 1 | 2.3703 | 1 | 2.3703 | 1
212 | Classroom | 365 | 24 |  |  | 825 | 18 | 18 | Unit Ventilator | 8 | 6600 | 3.3182 | 1 | 3.3182 | 1 | 3.3182 | 1
Hallway @ 212 | Hallway | 215 | 14 |  |  |  | 0 | 0 | Unit Ventilator
213 | Classroom | 357 | 23 |  |  | 426 | 9 | 9 | Unit Ventilator | 8 | 3408 | 6.2852 | 1 | 6.2852 | 2 | 6.2852 | 2
301 | Classroom | 189 | 12 | Yes | 20 | 829 | 18 | 18 | Unit Ventilator | 8 | 6632 | 1.7099 | 1 | 1.7099 | 1 | 21.7099 | 3
302 | Classroom | 298 | 19 |  |  | 822 | 18 | 18 | Unit Ventilator | 8 | 6576 | 2.719 | 1 | 2.719 | 1 | 2.719 | 1
302 A | Bathroom |  | 0 |  |  | 232 | 5 | 0 | N/A | 8 | 1856 | 0 | 1 | 0 | 0 | 0 | 0
302 B | Bathroom |  | 0 |  |  | 147 | 3 | 0 | N/A | 8 | 1176 | 0 | 1 | 0 | 0 | 0 | 0
303 | Classroom | 0 | 0 | Yes | 20 | 894 | 20 | 20 | Unit Ventilator | 8 | 7152 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom | 316 | 21 |  |  | 788 | 17 | 17 | Unit Ventilator | 8 | 6304 | 3.0076 | 1 | 3.0076 | 1 | 3.0076 | 1
305 | Classroom | 422 | 28 |  |  | 820 | 18 | 18 | Unit Ventilator | 8 | 6560 | 3.8598 | 1 | 3.8598 | 1 | 3.8598 | 1
306 | Classroom | 288 | 19 |  |  | 822 | 18 | 18 | Unit Ventilator | 8 | 6576 | 2.6277 | 1 | 2.6277 | 1 | 2.6277 | 1
Hallway @ 306 | Hallway | 0 | 0 |  |  |  | 0 | 0 | Unit Ventilator
307 | Classroom | 351 | 23 |  |  | 822 | 18 | 18 | Unit Ventilator | 8 | 6576 | 3.2026 | 1 | 3.2026 | 1 | 3.2026 | 1
308 | Classroom | 476 | 31 |  |  | 826 | 18 | 18 | Unit Ventilator | 8 | 6608 | 4.322 | 1 | 4.322 | 2 | 4.322 | 2
Hallway @ 308 | Hallway | 250 | 16 |  |  |  | 0 | 0 | Unit Ventilator
309 | Classroom | 349 | 23 |  |  | 826 | 18 | 18 | Unit Ventilator | 8 | 6608 | 3.1689 | 1 | 3.1689 | 1 | 3.1689 | 1
310 | Classroom | 321 | 21 |  |  | 811 | 18 | 18 | Unit Ventilator | 8 | 6488 | 2.9686 | 1 | 2.9686 | 1 | 2.9686 | 1
311 | Classroom | 331 | 22 |  |  | 829 | 18 | 18 | Unit Ventilator | 8 | 6632 | 2.9946 | 1 | 2.9946 | 1 | 2.9946 | 1
312 | Classroom | 367 | 24 |  |  | 822 | 18 | 18 | Unit Ventilator | 8 | 6576 | 3.3485 | 1 | 3.3485 | 1 | 3.3485 | 1
Hallway @ 312 | Hallway | 215 | 14 |  |  |  | 0 | 0 | Unit Ventilator
- | Auditorium | 630 | 42 |  |  |  | 0 | 0 | AHU
GYM | GYM | 572 | 38 |  |  |  | 0 | 0 | Unit Ventilator
Hallway @ Elevator | Hallway | 0 | 0 |  |  |  | 0 | 0 | Unit Ventilator
Hallway @ Stair D | Hallway | 231 | 15 |  |  |  | 0 | 0 | Unit Ventilator
- | Nurse | 0 | 0 |  |  |  | 0 | 0 | Unit Ventilator
- | Teachers Lounge | 0 | 0 |  |  |  | 0 | 0 | Unit Ventilator
- | Auditorium |  | 0 |  |  | 2998 | 68 | 0 | AHU | 8 | 23984 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Auditorium Rear classroom |  | 0 |  |  | 251 | 5 | 0 | AHU | 8 | 2008 | 0 | 1 | 0 | 0 | 0 | 0
- | Boys bathroom outside main offce |  | 0 |  |  | 303 | 6 | 0 | N/A | 8 | 2424 | 0 | 1 | 0 | 0 | 0 | 0
- | 3rd floor Boys bathroom |  | 0 |  |  | 220 | 4 | 0 | N/A | 8 | 1760 | 0 | 1 | 0 | 0 | 0 | 0
- | Building Engineer Office |  | 0 |  |  | 99 | 2 | 0 | N/A | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
- | 3rd floor Girls bathroom |  | 0 |  |  | 192 | 4 | 0 | N/A | 8 | 1536 | 0 | 1 | 0 | 0 | 0 | 0
- | Girls bathroom outside main offce |  | 0 |  |  | 300 | 6 | 0 | N/A | 8 | 2400 | 0 | 1 | 0 | 0 | 0 | 0
- | 3rd floor Gym Teacher office |  | 0 |  |  | 284 | 6 | 0 | N/A | 8 | 2272 | 0 | 1 | 0 | 0 | 0 | 0
- | 3rd floor Gym/Lunchroom |  | 0 |  |  | 3603 | 81 | 0 | Unit Ventilator | 8 | 28824 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Kitchen |  | 0 |  |  | 509 | 11 | 0 | N/A | 8 | 4072 | 0 | 1 | 0 | 0 | 0 | 0
- | Parent & teacher conf rm |  | 0 |  |  | 123 | 2 | 0 | Unit Ventilator | 8 | 984 | 0 | 1 | 0 | 0 | 0 | 0
- | Principal Conf rm |  | 0 |  |  | 159 | 3 | 0 | Unit Ventilator | 8 | 1272 | 0 | 1 | 0 | 0 | 0 | 0
- | Teacher Lounge |  | 0 |  |  | 436 | 9 | 0 | Unit Ventilator | 8 | 3488 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29
School: | Stephen Girard Elementary School
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | 100 | 51 | 3 | Yes | 20 | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 0.5692 | 1 | 0.5692 | 0 | 20.5692 | 3
101 | 101 | 114 | 7 | Yes | 20 | 1200 | 27 | 27 | Unit Ventilator | 8 | 9600 | 0.7125 | 1 | 0.7125 | 0 | 20.7125 | 3
103 | 103 | 27 | 1 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0.24107 | 1 | 0.24107 | 0 | 20.2411 | 3
105 | 105 | 62 | 4 |  |  | 840 | 19 | 4 | Unit Ventilator | 8 | 6720 | 0.55357 | 1 | 0.55357 | 0 | 0.55357 | 0
118 | Speech Classroom |  | 0 | Yes | 20 | 275 | 6 | 6 | N/A | 8 | 2200 | 0 | 1 | 0 | 0 | 20 | 3
200 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom |  | 0 | Yes | 20 | 375 | 8 | 8 | Unit Ventilator | 8 | 3000 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
216 | Classroom |  | 0 |  |  | 200 | 4 | 0 |  | 8 | 1600 | 0 | 1 | 0 | 0 | 0 | 0
300 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 |  |  | 840 | 19 | 0 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
307 / 309 | Classroom |  | 0 | Yes | 20 | 1375 | 31 | 31 | Unit Ventilator | 8 | 11000 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
308A | Classroom |  | 0 |  |  | 364 | 8 | 0 |  | 8 | 2912 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 11536 | 769 |  |  | 2600 | 59 | 59 | AHU | 8 | 20800 | 33.2769 | 1.062 | 35.3412 | 4 | 35.3412 | 4
- | Gymnasium | 1656 | 110 |  |  | 3550 | 80 | 80 | AHU | 8 | 28400 | 3.4986 | 1.062 | 3.7156 | 1 | 3.7156 | 1
- | IMC | 227 | 15 |  |  | 1846 | 41 | 15 | Unit Ventilator | 8 | 14768 | 0.92226 | 1 | 0.92226 | 0 | 0.92226 | 0
- | Nurse |  | 0 | Yes | 20 | 170 | 3 | 3 | N/A | 8 | 1360 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 294 | 6 | 6 |  | 8 | 2352 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 396 | 9 | 9 | Unit Ventilator | 8 | 3168 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-27
School: | Philadelphia High School for Girls
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B-12 | Showers | 2144 | 142 |  |  | 2163 | 49 | 49 | AHU | 8 | 17304 | 7.4341 | 1 | 7.4341 | 2 | 7.4341 | 2
B-13 | Visitors' Lockers | 0 | 0 |  |  | 256 | 5 | 0 | Unit Ventilator | 8 | 2048 | 0 | 1 | 0 | 0 | 0 | 0
B-14 | Home Lockers | 0 | 0 |  |  | 316 | 7 | 0 | Unit Ventilator | 8 | 2528 | 0 | 1 | 0 | 0 | 0 | 0
B-16 | Girls' Locker Room | 1254 | 83 |  |  | 4702 | 106 | 83 | Unit Ventilator | 8 | 37616 | 2.0002 | 1.062 | 2.1243 | 1 | 2.1243 | 1
G-1 | Classroom | 292 | 19 |  |  | 1032 | 23 | 19 | Unit Ventilator | 8 | 8256 | 2.1221 | 1 | 2.1221 | 1 | 2.1221 | 1
G-3 | Classroom | 459 | 30 |  |  | 1216 | 27 | 27 | Unit Ventilator | 8 | 9728 | 2.831 | 1 | 2.831 | 1 | 2.831 | 1
G-6 | - | 0 | 0 |  |  | 734 | 16 | 0 | Unit Ventilator | 8 | 5872 | 0 | 1 | 0 | 0 | 0 | 0
G-8 | Dance | 277 | 18 |  |  | 1275 | 28 | 18 | Unit Ventilator | 8 | 10200 | 1.6294 | 1 | 1.6294 | 1 | 1.6294 | 1
G-10 | Classroom | 281 | 18 |  |  | 741 | 16 | 16 | Unit Ventilator | 8 | 5928 | 2.8441 | 1 | 2.8441 | 1 | 2.8441 | 1
G-11 | Classroom | 274 | 18 |  |  | 745 | 16 | 16 | Unit Ventilator | 8 | 5960 | 2.7584 | 1 | 2.7584 | 1 | 2.7584 | 1
G-12 | Classroom | 222 | 14 |  |  | 714 | 16 | 14 | Unit Ventilator | 8 | 5712 | 2.3319 | 1 | 2.3319 | 1 | 2.3319 | 1
G-17 | Classroom | 93 | 6 |  |  | 748 | 17 | 6 | Unit Ventilator | 8 | 5984 | 0.93249 | 1 | 0.93249 | 0 | 0.93249 | 0
G-19 | Classroom | 277 | 18 |  |  | 718 | 16 | 16 | Unit Ventilator | 8 | 5744 | 2.8935 | 1 | 2.8935 | 1 | 2.8935 | 1
1 | Fitness Room | 227 | 15 |  |  | 1169 | 26 | 15 | Unit Ventilator | 8 | 9352 | 1.4564 | 1 | 1.4564 | 1 | 1.4564 | 1
2 | Fitness Room | 506 | 33 |  |  | 2048 | 46 | 33 | Unit Ventilator | 8 | 16384 | 1.853 | 1 | 1.853 | 1 | 1.853 | 1
100 | Classroom | 306 | 20 |  |  | 756 | 17 | 17 | Unit Ventilator | 8 | 6048 | 3.0357 | 1 | 3.0357 | 1 | 3.0357 | 1
101 | Classroom | 275 | 18 |  |  | 756 | 17 | 17 | Unit Ventilator | 8 | 6048 | 2.7282 | 1 | 2.7282 | 1 | 2.7282 | 1
102 | Archives | 145 | 9 |  |  | 689 | 15 | 9 | Unit Ventilator | 8 | 5512 | 1.5784 | 1 | 1.5784 | 1 | 1.5784 | 1
104 | Classroom | 221 | 14 |  |  | 756 | 17 | 14 | Unit Ventilator | 8 | 6048 | 2.1925 | 1 | 2.1925 | 1 | 2.1925 | 1
105 | Instruments | 612 | 40 |  |  | 2376 | 54 | 40 | Unit Ventilator | 8 | 19008 | 1.9318 | 1 | 1.9318 | 1 | 1.9318 | 1
106 | Roster Office | 208 | 13 |  |  | 778 | 17 | 13 | Unit Ventilator | 8 | 6224 | 2.0051 | 1 | 2.0051 | 1 | 2.0051 | 1
107 | Office | 290 | 19 |  |  | 799 | 18 | 18 | Unit Ventilator | 8 | 6392 | 2.7222 | 1 | 2.7222 | 1 | 2.7222 | 1
108 | Office | 0 | 0 |  |  | 769 | 17 | 0 | Unit Ventilator | 8 | 6152 | 0 | 1 | 0 | 0 | 0 | 0
109 | Office | 291 | 19 |  |  | 790 | 17 | 17 | Unit Ventilator | 8 | 6320 | 2.7627 | 1 | 2.7627 | 1 | 2.7627 | 1
110 | Office | 203 | 13 |  |  | 768 | 17 | 13 | Unit Ventilator | 8 | 6144 | 1.9824 | 1 | 1.9824 | 1 | 1.9824 | 1
111 | Poetry | 188 | 12 |  |  | 1182 | 26 | 12 | Unit Ventilator | 8 | 9456 | 1.1929 | 1 | 1.1929 | 1 | 1.1929 | 1
111-A | Health Office | 0 | 0 |  |  | 462 | 10 | 0 | Unit Ventilator | 8 | 3696 | 0 | 1 | 0 | 0 | 0 | 0
112 | Classroom | 0 | 0 |  |  | 767 | 17 | 0 | Unit Ventilator | 8 | 6136 | 0 | 1 | 0 | 0 | 0 | 0
113 | Classroom | 0 | 0 |  |  | 1655 | 37 | 0 | Unit Ventilator | 8 | 13240 | 0 | 1 | 0 | 0 | 0 | 0
114 | Classroom | 0 | 0 |  |  | 769 | 17 | 0 | Unit Ventilator | 8 | 6152 | 0 | 1 | 0 | 0 | 0 | 0
115 | Classroom | 0 | 0 |  |  | 1749 | 39 | 0 | Unit Ventilator | 8 | 13992 | 0 | 1 | 0 | 0 | 0 | 0
116 | Classroom | 0 | 0 |  |  | 749 | 17 | 0 | Unit Ventilator | 8 | 5992 | 0 | 1 | 0 | 0 | 0 | 0
118 | Classroom | 0 | 0 |  |  | 752 | 17 | 0 | Unit Ventilator | 8 | 6016 | 0 | 1 | 0 | 0 | 0 | 0
200 | Classroom | 0 | 0 |  |  | 775 | 17 | 0 | Unit Ventilator | 8 | 6200 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom | 221 | 14 |  |  | 763 | 17 | 14 | Unit Ventilator | 8 | 6104 | 2.1723 | 1 | 2.1723 | 1 | 2.1723 | 1
202 | Classroom | 213 | 14 |  |  | 771 | 17 | 14 | Unit Ventilator | 8 | 6168 | 2.072 | 1 | 2.072 | 1 | 2.072 | 1
204 | Classroom | 0 | 0 |  |  | 771 | 17 | 0 | Unit Ventilator | 8 | 6168 | 0 | 1 | 0 | 0 | 0 | 0
205 | Music Office | 472 | 31 |  |  | 2334 | 53 | 31 | Unit Ventilator | 8 | 18672 | 1.5167 | 1 | 1.5167 | 1 | 1.5167 | 1
206 | Classroom | 0 | 0 |  |  | 780 | 17 | 0 | Unit Ventilator | 8 | 6240 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom | 289 | 19 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 2.8223 | 1 | 2.8223 | 1 | 2.8223 | 1
208 | Classroom | 213 | 14 |  |  | 776 | 17 | 14 | Unit Ventilator | 8 | 6208 | 2.0586 | 1 | 2.0586 | 1 | 2.0586 | 1
209 | Classroom | 251 | 16 |  |  | 786 | 17 | 16 | Unit Ventilator | 8 | 6288 | 2.395 | 1 | 2.395 | 1 | 2.395 | 1
210 | Classroom | 255 | 17 |  |  | 781 | 17 | 17 | Unit Ventilator | 8 | 6248 | 2.4488 | 1 | 2.4488 | 1 | 2.4488 | 1
211 | Classroom | 268 | 17 |  |  | 744 | 16 | 16 | Unit Ventilator | 8 | 5952 | 2.7016 | 1 | 2.7016 | 1 | 2.7016 | 1
212 | Classroom | 388 | 25 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 3.7308 | 1 | 3.7308 | 1 | 3.7308 | 1
214 | Classroom | 251 | 16 |  |  | 776 | 17 | 16 | Unit Ventilator | 8 | 6208 | 2.4259 | 1 | 2.4259 | 1 | 2.4259 | 1
215 | Classroom | 402 | 26 |  |  | 781 | 17 | 17 | Unit Ventilator | 8 | 6248 | 3.8604 | 1 | 3.8604 | 1 | 3.8604 | 1
216 | Classroom | 244 | 16 |  |  | 772 | 17 | 16 | Unit Ventilator | 8 | 6176 | 2.3705 | 1 | 2.3705 | 1 | 2.3705 | 1
217 | Classroom | 178 | 11 |  |  | 787 | 17 | 11 | Unit Ventilator | 8 | 6296 | 1.6963 | 1 | 1.6963 | 1 | 1.6963 | 1
218 | Classroom | 0 | 0 |  |  | 789 | 17 | 0 | Unit Ventilator | 8 | 6312 | 0 | 1 | 0 | 0 | 0 | 0
219 | Classroom | 54 | 3 |  |  | 783 | 17 | 3 | Unit Ventilator | 8 | 6264 | 0.51724 | 1 | 0.51724 | 0 | 0.51724 | 0
221 | Classroom | 290 | 19 |  |  | 841 | 19 | 19 | Unit Ventilator | 8 | 6728 | 2.5862 | 1 | 2.5862 | 1 | 2.5862 | 1
223 | Classroom | 0 | 0 |  |  | 891 | 20 | 0 | Unit Ventilator | 8 | 7128 | 0 | 1 | 0 | 0 | 0 | 0
300 | Classroom | 270 | 18 |  |  | 786 | 17 | 17 | Unit Ventilator | 8 | 6288 | 2.5763 | 1 | 2.5763 | 1 | 2.5763 | 1
302 | Classroom | 416 | 27 |  |  | 996 | 22 | 22 | Unit Ventilator | 8 | 7968 | 3.1325 | 1 | 3.1325 | 1 | 3.1325 | 1
303 | Classroom | 555 | 37 |  |  | 1052 | 23 | 23 | Unit Ventilator | 8 | 8416 | 3.9567 | 1 | 3.9567 | 1 | 3.9567 | 1
304 | Classroom | 525 | 35 |  |  | 1007 | 22 | 22 | Unit Ventilator | 8 | 8056 | 3.9101 | 1 | 3.9101 | 1 | 3.9101 | 1
305 | Classroom | 279 | 18 |  |  | 791 | 17 | 17 | Unit Ventilator | 8 | 6328 | 2.6454 | 1 | 2.6454 | 1 | 2.6454 | 1
306 | Classroom | 378 | 25 |  |  | 1034 | 23 | 23 | Unit Ventilator | 8 | 8272 | 2.7418 | 1 | 2.7418 | 1 | 2.7418 | 1
307 | Classroom | 0 | 0 |  |  | 781 | 17 | 0 | Unit Ventilator | 8 | 6248 | 0 | 1 | 0 | 0 | 0 | 0
308 | Classroom | 158 | 10 |  |  | 1048 | 23 | 10 | Unit Ventilator | 8 | 8384 | 1.1307 | 1 | 1.1307 | 1 | 1.1307 | 1
309 | Classroom | 188 | 12 |  |  | 787 | 17 | 12 | Unit Ventilator | 8 | 6296 | 1.7916 | 1 | 1.7916 | 1 | 1.7916 | 1
310 | Classroom | 403 | 26 |  |  | 1115 | 25 | 25 | Unit Ventilator | 8 | 8920 | 2.7108 | 1 | 2.7108 | 1 | 2.7108 | 1
311 | Classroom | 186 | 12 |  |  | 792 | 18 | 12 | Unit Ventilator | 8 | 6336 | 1.7614 | 1 | 1.7614 | 1 | 1.7614 | 1
312 | Classroom | 240 | 16 |  |  | 1015 | 23 | 16 | Unit Ventilator | 8 | 8120 | 1.7734 | 1 | 1.7734 | 1 | 1.7734 | 1
313 | Classroom | 202 | 13 |  |  | 779 | 17 | 13 | Unit Ventilator | 8 | 6232 | 1.9448 | 1 | 1.9448 | 1 | 1.9448 | 1
314 | Classroom | 329 | 21 |  |  | 1008 | 22 | 21 | Unit Ventilator | 8 | 8064 | 2.4479 | 1 | 2.4479 | 1 | 2.4479 | 1
315 | Classroom | 289 | 19 |  |  | 790 | 17 | 17 | Unit Ventilator | 8 | 6320 | 2.7437 | 1 | 2.7437 | 1 | 2.7437 | 1
316 | Classroom | 326 | 21 |  |  | 788 | 17 | 17 | Unit Ventilator | 8 | 6304 | 3.1028 | 1 | 3.1028 | 1 | 3.1028 | 1
317 | Classroom | 169 | 11 |  |  | 780 | 17 | 11 | Unit Ventilator | 8 | 6240 | 1.625 | 1 | 1.625 | 1 | 1.625 | 1
319 | Classroom | 351 | 23 |  |  | 706 | 16 | 16 | Unit Ventilator | 8 | 5648 | 3.7288 | 1 | 3.7288 | 1 | 3.7288 | 1
321 | Classroom | 293 | 19 |  |  | 716 | 16 | 16 | Unit Ventilator | 8 | 5728 | 3.0691 | 1 | 3.0691 | 1 | 3.0691 | 1
- | Auditorium | 946 | 63 |  |  | 10546 | 239 | 63 | AHU | 8 | 84368 | 0.67277 | 1.4912 | 1.0032 | 1 | 1.0032 | 1
- | Gymnasium | 287 | 19 |  |  | 10449 | 237 | 19 | AHU | 8 | 83592 | 0.206 | 1.4912 | 0.30718 | 0 | 0.30718 | 0
- | Main Cafeteria | 2523 | 168 |  |  | 12220 | 277 | 168 | Unit Ventilator | 8 | 97760 | 1.5485 | 1.4912 | 2.309 | 1 | 2.309 | 1
- | Faculty Cafeteria | 549 | 36 |  |  | 1172 | 26 | 26 | Unit Ventilator | 8 | 9376 | 3.5132 | 1 | 3.5132 | 1 | 3.5132 | 1
- | Main Office | 192 | 12 |  |  | 1054 | 23 | 12 | Unit Ventilator | 8 | 8432 | 1.3662 | 1 | 1.3662 | 1 | 1.3662 | 1
- | Library | 538 | 35 |  |  | 5853 | 133 | 35 | Unit Ventilator | 8 | 46824 | 0.68939 | 1.062 | 0.73216 | 0 | 0.73216 | 0
Sheet Last Modified: | 2021-04-23
School: | Samuel Gompers Elementary-Middle School
Vendor: | Capital
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Kindergarten | 334 | 22 |  |  | 2002 | 45 | 22 | Unit Ventilator | 8 | 16016 | 1.2512 | 1 | 1.2512 | 1 | 1.2512 | 1
102 | Classroom | 429 | 28 |  |  | 1106 | 25 | 25 | Unit Ventilator | 8 | 8848 | 2.9091 | 1 | 2.9091 | 1 | 2.9091 | 1
104 | Classroom | 450 | 30 |  |  | 1099 | 24 | 24 | Unit Ventilator | 8 | 8792 | 3.071 | 1 | 3.071 | 1 | 3.071 | 1
105 | Classroom | 444 | 29 |  |  | 1094 | 24 | 24 | Unit Ventilator | 8 | 8752 | 3.0439 | 1 | 3.0439 | 1 | 3.0439 | 1
106 | Classroom | 436 | 29 |  |  | 1095 | 24 | 24 | Unit Ventilator | 8 | 8760 | 2.9863 | 1 | 2.9863 | 1 | 2.9863 | 1
107 | Classroom | 432 | 28 |  |  | 1102 | 25 | 25 | Unit Ventilator | 8 | 8816 | 2.9401 | 1 | 2.9401 | 1 | 2.9401 | 1
B-107 | Library | 492 | 32 |  |  | 1241 | 28 | 28 | Unit Ventilator | 8 | 9928 | 2.9734 | 1 | 2.9734 | 1 | 2.9734 | 1
B-107A | Workroom | 28 | 1 |  |  | 204 | 4 | 1 | Unit Ventilator | 8 | 1632 | 1.0294 | 1 | 1.0294 | 1 | 1.0294 | 1
A-108 | Teacher Room | 138 | 9 |  |  | 387 | 8 | 8 | Unit Ventilator | 8 | 3096 | 2.6744 | 1 | 2.6744 | 1 | 2.6744 | 1
A-112 | Infirmary | 21 | 1 |  |  | 198 | 4 | 1 | Unit Ventilator | 8 | 1584 | 0.79545 | 1 | 0.79545 | 0 | 0.79545 | 0
A-113 | Waiting | 80 | 5 |  |  | 155 | 3 | 3 | FCU | 8 | 1240 | 3.871 | 1 | 3.871 | 1 | 3.871 | 1
A-114 | Nurse’s Office | 339 | 22 |  |  | 186 | 4 | 4 | FCU | 8 | 1488 | 13.6694 | 1 | 13.6694 | 3 | 13.6694 | 3
A-121 | Examination | 226 | 15 |  |  | 310 | 7 | 7 | FCU | 8 | 2480 | 5.4677 | 1 | 5.4677 | 2 | 5.4677 | 2
A-122 | Office | 22 | 1 |  |  | 133 | 3 | 1 | Unit Ventilator | 8 | 1064 | 1.2406 | 1 | 1.2406 | 1 | 1.2406 | 1
A-124 | Counselor Office | 34 | 2 |  |  | 178 | 4 | 2 | Unit Ventilator | 8 | 1424 | 1.4326 | 1 | 1.4326 | 1 | 1.4326 | 1
A-131 | General Office | 51 | 3 |  |  | 488 | 11 | 3 | Unit Ventilator | 8 | 3904 | 0.78381 | 1 | 0.78381 | 0 | 0.78381 | 0
A-133 | Principal Office | 32 | 2 |  |  | 232 | 5 | 2 | Unit Ventilator | 8 | 1856 | 1.0345 | 1 | 1.0345 | 1 | 1.0345 | 1
A-137 | Conference | 96 | 6 |  |  | 333 | 7 | 6 | Unit Ventilator | 8 | 2664 | 2.1622 | 1 | 2.1622 | 1 | 2.1622 | 1
A-150 | Office | 117 | 7 |  |  | 324 | 7 | 7 | FCU | 8 | 2592 | 2.7083 | 1 | 2.7083 | 1 | 2.7083 | 1
A-153 | Office | 122 | 8 |  |  | 322 | 7 | 7 | FCU | 8 | 2576 | 2.8416 | 1 | 2.8416 | 1 | 2.8416 | 1
201 | Classroom | 429 | 28 |  |  | 1083 | 24 | 24 | Unit Ventilator | 8 | 8664 | 2.9709 | 1 | 2.9709 | 1 | 2.9709 | 1
202 | Classroom | 431 | 28 |  |  | 1074 | 24 | 24 | Unit Ventilator | 8 | 8592 | 3.0098 | 1 | 3.0098 | 1 | 3.0098 | 1
203 | Classroom | 432 | 28 |  |  | 1075 | 24 | 24 | Unit Ventilator | 8 | 8600 | 3.014 | 1 | 3.014 | 1 | 3.014 | 1
204 | Classroom | 265 | 17 |  |  | 544 | 12 | 12 | Unit Ventilator | 8 | 4352 | 3.6535 | 1 | 3.6535 | 1 | 3.6535 | 1
205 | Classroom | 418 | 27 |  |  | 1109 | 25 | 25 | Unit Ventilator | 8 | 8872 | 2.8269 | 1 | 2.8269 | 1 | 2.8269 | 1
A-205 | Teachers Room | 156 | 10 |  |  | 353 | 8 | 8 | Unit Ventilator | 8 | 2824 | 3.3144 | 1 | 3.3144 | 1 | 3.3144 | 1
206 | Classroom | 433 | 28 |  |  | 1110 | 25 | 25 | Unit Ventilator | 8 | 8880 | 2.9257 | 1 | 2.9257 | 1 | 2.9257 | 1
207 | Classroom | 435 | 29 |  |  | 1112 | 25 | 25 | Unit Ventilator | 8 | 8896 | 2.9339 | 1 | 2.9339 | 1 | 2.9339 | 1
208 | Classroom | 438 | 29 |  |  | 1095 | 24 | 24 | Unit Ventilator | 8 | 8760 | 3 | 1 | 3 | 1 | 3 | 1
A-208 | After School Programs | 65 | 4 |  |  | 441 | 10 | 4 | Unit Ventilator | 8 | 3528 | 1.1054 | 1 | 1.1054 | 1 | 1.1054 | 1
B-209 | Classroom | 262 | 17 |  |  | 537 | 12 | 12 | Unit Ventilator | 8 | 4296 | 3.6592 | 1 | 3.6592 | 1 | 3.6592 | 1
B-210 | Classroom | 437 | 29 |  |  | 1093 | 24 | 24 | Unit Ventilator | 8 | 8744 | 2.9986 | 1 | 2.9986 | 1 | 2.9986 | 1
B-211 | Classroom | 435 | 29 |  |  | 1095 | 24 | 24 | Unit Ventilator | 8 | 8760 | 2.9795 | 1 | 2.9795 | 1 | 2.9795 | 1
212 | Classroom | 419 | 27 |  |  | 1084 | 24 | 24 | Unit Ventilator | 8 | 8672 | 2.899 | 1 | 2.899 | 1 | 2.899 | 1
213 | Classroom | 454 | 30 |  |  | 1087 | 24 | 24 | Unit Ventilator | 8 | 8696 | 3.1325 | 1 | 3.1325 | 1 | 3.1325 | 1
A-217 | Cafeteria | 466 | 31 |  |  | 1943 | 44 | 31 | AHU | 8 | 15544 | 1.7988 | 1 | 1.7988 | 1 | 1.7988 | 1
A-218 | Gymnasium | 1290 | 86 |  |  | 3950 | 89 | 86 | AHU | 8 | 31600 | 2.4494 | 1.062 | 2.6013 | 1 | 2.6013 | 1
Portable | R1 |  | 0 | Yes | 20 | 843 | 19 | 19 |  | 8 | 6744 | 0 | 1 | 0 | 0 | 20 | 3
Portable | R2 |  | 0 | Yes | 20 | 842 | 19 | 19 |  | 8 | 6736 | 0 | 1 | 0 | 0 | 20 | 3
Portable | R3 |  | 0 | Yes | 20 | 852 | 19 | 19 |  | 8 | 6816 | 0 | 1 | 0 | 0 | 20 | 3
Portable | R4 |  | 0 | Yes | 20 | 1033 | 23 | 23 |  | 8 | 8264 | 0 | 1 | 0 | 0 | 20 | 3
Portable | R5 |  | 0 | Yes | 20 | 1022 | 23 | 23 |  | 8 | 8176 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-22
School: | Joseph Greenberg Elementary-Middle School
Vendor: | Devine Borthers | Devine Brothers Retest
Devine Brothers 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 325 | 21 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.9438 | 1 | 2.9438 | 1 | 2.9438 | 1
101 | Classroom | 335 | 22 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 3.0344 | 1 | 3.0344 | 1 | 3.0344 | 1
102 | Classroom | 380 | 25 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 3.442 | 1 | 3.442 | 1 | 3.442 | 1
103 | Classroom | 288 | 19 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.6087 | 1 | 2.6087 | 1 | 2.6087 | 1
104 | Classroom | 284 | 18 |  |  | 384 | 8 | 8 | Unit Ventilator | 8 | 3072 | 5.5469 | 1 | 5.5469 | 2 | 5.5469 | 2
105 | Nurse | 300 | 20 |  |  | 432 | 9 | 9 | Unit Ventilator | 8 | 3456 | 5.2083 | 1 | 5.2083 | 2 | 5.2083 | 2
106 | Classroom | 530 | 35 |  |  | 1012 | 23 | 23 | Unit Ventilator | 8 | 8096 | 3.9279 | 1 | 3.9279 | 1 | 3.9279 | 1
107 | Classroom | 671 | 44 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 5.8247 | 1 | 5.8247 | 2 | 5.8247 | 2
107A | Meeting room |  | 0 | Yes | 20 | 432 | 9 | 9 | Unit Ventilator | 8 | 3456 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom | 441 | 29 |  |  | 1012 | 23 | 23 | Unit Ventilator | 8 | 8096 | 3.2683 | 1 | 3.2683 | 1 | 3.2683 | 1
109 | Classroom | 298 | 19 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.6993 | 1 | 2.6993 | 1 | 2.6993 | 1
111 | Classroom | 291 | 19 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.6359 | 1 | 2.6359 | 1 | 2.6359 | 1
200 | Classroom | 308 | 20 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.7899 | 1 | 2.7899 | 1 | 2.7899 | 1
201 | Classroom | 281 | 18 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.5453 | 1 | 2.5453 | 1 | 2.5453 | 1
202 | Classroom | 295 | 19 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.6721 | 1 | 2.6721 | 1 | 2.6721 | 1
203 | Classroom | 351 | 23 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 3.1793 | 1 | 3.1793 | 1 | 3.1793 | 1
204 | Classroom | 317 | 21 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.8714 | 1 | 2.8714 | 1 | 2.8714 | 1
205 | Classroom | 326 | 21 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.9529 | 1 | 2.9529 | 1 | 2.9529 | 1
207 | Classroom | 320 | 21 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.8986 | 1 | 2.8986 | 1 | 2.8986 | 1
209 | Classroom | 345 | 23 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 3.125 | 1 | 3.125 | 1 | 3.125 | 1
210 | Classroom | 316 | 21 |  |  | 384 | 8 | 8 | Unit Ventilator | 8 | 3072 | 6.1719 | 1 | 6.1719 | 2 | 6.1719 | 2
211 | Classroom | 281 | 18 |  |  | 368 | 8 | 8 | Unit Ventilator | 8 | 2944 | 5.7269 | 1 | 5.7269 | 2 | 5.7269 | 2
211a | Classroom | 375 | 25 |  |  | 621 | 14 | 14 | Unit Ventilator | 8 | 4968 | 4.529 | 1 | 4.529 | 2 | 4.529 | 2
211b | Classroom | 307 | 20 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.7808 | 1 | 2.7808 | 1 | 2.7808 | 1
212 | Classroom | 351 | 23 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 3.1793 | 1 | 3.1793 | 1 | 3.1793 | 1
213 | Classroom | 344 | 22 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 3.1159 | 1 | 3.1159 | 1 | 3.1159 | 1
214 | Classroom | 345 | 23 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 3.125 | 1 | 3.125 | 1 | 3.125 | 1
215 | Classroom | 375 | 25 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 3.3967 | 1 | 3.3967 | 1 | 3.3967 | 1
216 | Classroom | 312 | 20 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.8261 | 1 | 2.8261 | 1 | 2.8261 | 1
217 | Classroom | 326 | 21 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.9529 | 1 | 2.9529 | 1 | 2.9529 | 1
300 | Classroom | 325 | 21 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.9438 | 1 | 2.9438 | 1 | 2.9438 | 1
301 | Classroom | 291 | 19 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.6359 | 1 | 2.6359 | 1 | 2.6359 | 1
302 | Classroom | 285 | 19 |  |  | 552 | 12 | 12 | Unit Ventilator | 8 | 4416 | 3.8723 | 1 | 3.8723 | 1 | 3.8723 | 1
303 | Classroom | 330 | 22 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.9891 | 1 | 2.9891 | 1 | 2.9891 | 1
304 | Classroom | 325 | 21 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.9438 | 1 | 2.9438 | 1 | 2.9438 | 1
305 | Classroom | 321 | 21 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.9076 | 1 | 2.9076 | 1 | 2.9076 | 1
306 | Classroom | 289 | 19 |  |  | 384 | 8 | 8 | Unit Ventilator | 8 | 3072 | 5.6445 | 1 | 5.6445 | 2 | 5.6445 | 2
307 | Classroom | 345 | 23 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 3.125 | 1 | 3.125 | 1 | 3.125 | 1
309 | Classroom | 350 | 23 |  |  | 1242 | 28 | 23 | Unit Ventilator | 8 | 9936 | 2.1135 | 1 | 2.1135 | 1 | 2.1135 | 1
313 | Classroom | 302 | 20 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.7355 | 1 | 2.7355 | 1 | 2.7355 | 1
314 | Classroom | 289 | 19 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.6178 | 1 | 2.6178 | 1 | 2.6178 | 1
315 | Classroom | 321 | 21 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.9076 | 1 | 2.9076 | 1 | 2.9076 | 1
316 | Classroom | 311 | 20 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.817 | 1 | 2.817 | 1 | 2.817 | 1
317 | Classroom | 331 | 22 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.9982 | 1 | 2.9982 | 1 | 2.9982 | 1
318 | Classroom | 314 | 20 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.8442 | 1 | 2.8442 | 1 | 2.8442 | 1
319 | Classroom | 311 | 20 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.817 | 1 | 2.817 | 1 | 2.817 | 1
321 | Classroom | 288 | 19 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.6087 | 1 | 2.6087 | 1 | 2.6087 | 1
400 | Classroom | 375 | 25 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 3.2552 | 1 | 3.2552 | 1 | 3.2552 | 1
401 | IMC Classroom | 310 | 20 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 2.808 | 1 | 2.808 | 1 | 2.808 | 1
- | Auditorium | 12200 | 813 |  |  | 3213 | 73 | 73 | AHU | 8 | 25704 | 28.4781 | 1.062 | 30.2447 | 4 | 30.2447 | 4
- | Cafeteria | 7911 | 527 |  |  | 5250 | 119 | 119 | AHU | 8 | 42000 | 11.3014 | 1.062 | 12.0025 | 3 | 12.0025 | 3
- | Gym | 8800 | 586 |  |  | 3978 | 90 | 90 | AHU | 8 | 31824 | 16.5913 | 1.062 | 17.6205 | 3 | 17.6205 | 3
- | IMC Classroom | 220 | 14 |  |  | 828 | 18 | 14 | Unit Ventilator | 8 | 6624 | 1.9928 | 1 | 1.9928 | 1 | 1.9928 | 1
- | Teacher Lounge | 448 | 29 |  |  | 168 | 3 | 3 | Unit Ventilator | 8 | 1344 | 20 | 1 | 20 | 3 | 20 | 3
- | Main Office | 280 | 18 |  |  | 1134 | 25 | 18 | Unit Ventilator | 8 | 9072 | 1.8519 | 1 | 1.8519 | 1 | 1.8519 | 1
- | Dean's office |  | 0 | Yes | 20 | 135 | 3 | 3 | Unit Ventilator | 8 | 1080 | 0 | 1 | 0 | 0 | 20 | 3
- | Assistant principal office |  | 0 | Yes | 20 | 135 | 3 | 3 | Unit Ventilator | 8 | 1080 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 20 | 432 | 9 | 9 | Unit Ventilator | 8 | 3456 | 0 | 1 | 0 | 0 | 20 | 3
- | Kitchen |  | 0 | Yes | 20 | 864 | 19 | 19 | N/A | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
- | BE office | 275 | 18 |  |  | 441 | 10 | 10 | N/A | 8 | 3528 | 4.6769 | 1 | 4.6769 | 2 | 4.6769 | 2
- | Custodial office | 95 | 6 |  |  | 195 | 4 | 4 | N/A | 8 | 1560 | 3.6538 | 1 | 3.6538 | 1 | 3.6538 | 1
Sheet Last Modified: | 2021-04-26
School: | Albert M. Greenfield Elementary School
Vendor: | Meehan | Devine | Capital Part I
Vendor: | Capital Part II | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B06 | Music rm. | 329 | 21 |  |  | 416 | 9 | 9 | AHU | 8 | 3328 | 5.9315 | 1 | 5.9315 | 2 | 5.9315 | 2
B17 | Storage | 229 | 15 |  |  | 320 | 7 | 7 | N/A | 8 | 2560 | 5.3672 | 1 | 5.3672 | 2 | 5.3672 | 2
B36 | Music main | 452 | 30 |  |  | 962 | 21 | 21 | AHU | 8 | 7696 | 3.5239 | 1 | 3.5239 | 1 | 3.5239 | 1
B37 | Music Office | 151 | 10 |  |  | 168 | 3 | 3 | AHU | 8 | 1344 | 6.7411 | 1 | 6.7411 | 2 | 6.7411 | 2
B38 | Practice rm | 44 | 2 |  |  | 64 | 1 | 1 | AHU | 8 | 512 | 5.1562 | 1 | 5.1562 | 2 | 5.1562 | 2
B40 | Music Ensamble | 163 | 10 |  |  | 312 | 7 | 7 | AHU | 8 | 2496 | 3.9183 | 1 | 3.9183 | 1 | 3.9183 | 1
101 | Reception | 121 | 8 |  |  | 360 | 8 | 8 | AHU | 8 | 2880 | 2.5208 | 1 | 2.5208 | 1 | 2.5208 | 1
102 |  | 0 |  | Yes | 20 | 120 |  |  | N/A | 8 | 960 |  | 1 | #VALUE! | #VALUE! | 20
103 | Offices | 0 | 0 | Yes | 20 | 120 | 2 | 2 | AHU | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
104 | Offices | 0 | 0 | Yes | 20 | 120 | 2 | 2 | AHU | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
105 | Sensory Room | 46 | 3 |  |  | 120 | 2 | 2 | AHU | 8 | 960 | 2.875 | 1 | 2.875 | 1 | 2.875 | 1
106 | Office | 76 | 5 |  |  | 231 | 5 | 5 | AHU | 8 | 1848 | 2.4675 | 1 | 2.4675 | 1 | 2.4675 | 1
107 | Nurse Reception | 0 | 0 | Yes | 20 | 81 | 1 | 1 | AHU | 8 | 648 | 0 | 1 | 0 | 0 | 20 | 3
107A | Nurse Office | 48 | 3 | Yes | 20 | 189 | 4 | 4 | AHU | 8 | 1512 | 1.9048 | 1 | 1.9048 | 1 | 21.9048 | 3
107B | Offices | 0 | 0 | Yes | 20 | 99 | 2 | 2 | AHU | 8 | 792 | 0 | 1 | 0 | 0 | 20 | 3
107C | Storage | 0 | 0 |  |  | 110 | 2 | 0 | N/A | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
108 | Conference | 65 | 4 |  |  | 238 | 5 | 4 | AHU | 8 | 1904 | 2.0483 | 1 | 2.0483 | 1 | 2.0483 | 1
109 | Admin | 0 | 0 | Yes | 20 | 130 | 2 | 2 | AHU | 8 | 1040 | 0 | 1 | 0 | 0 | 20 | 3
110 | Classroom | 340 | 22 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 2.7244 | 1 | 2.7244 | 1 | 2.7244 | 1
111 | Classroom | 491 | 32 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 3.9343 | 1 | 3.9343 | 1 | 3.9343 | 1
112 | Classroom | 366 | 24 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 2.9327 | 1 | 2.9327 | 1 | 2.9327 | 1
113A | Classroom | 1038 | 69 |  |  | 676 | 15 | 15 | Unit Ventilator | 8 | 5408 | 11.5163 | 1 | 11.5163 | 3 | 11.5163 | 3
126 | Lobby | 55 | 3 |  |  | 676 | 15 | 3 | Unit Ventilator | 8 | 5408 | 0.61021 | 1 | 0.61021 | 0 | 0.61021 | 0
128 | Corridor | 60 | 4 |  |  | 456 | 10 | 4 | Unit Ventilator | 8 | 3648 | 0.98684 | 1 | 0.98684 | 0 | 0.98684 | 0
129 | Principal Office | 94 | 6 |  |  | 220 | 5 | 5 | Unit Ventilator | 8 | 1760 | 3.2045 | 1 | 3.2045 | 1 | 3.2045 | 1
201 | Classroom | 150 | 10 |  |  | 260 | 5 | 5 | Unit Ventilator | 8 | 2080 | 4.3269 | 1 | 4.3269 | 2 | 4.3269 | 2
202 | Classroom | 390 | 26 |  |  | 884 | 20 | 20 | Unit Ventilator | 8 | 7072 | 3.3088 | 1 | 3.3088 | 1 | 3.3088 | 1
203 | Classroom | 302 | 20 |  |  | 884 | 20 | 20 | Unit Ventilator | 8 | 7072 | 2.5622 | 1 | 2.5622 | 1 | 2.5622 | 1
204 | Classroom | 493 | 32 |  |  | 725 | 16 | 16 | Unit Ventilator | 8 | 5800 | 5.1 | 1 | 5.1 | 2 | 5.1 | 2
205 | Classroom | 475 | 31 |  |  | 850 | 19 | 19 | Unit Ventilator | 8 | 6800 | 4.1912 | 1 | 4.1912 | 2 | 4.1912 | 2
206 | Classroom | 488 | 32 |  |  | 918 | 20 | 20 | Unit Ventilator | 8 | 7344 | 3.9869 | 1 | 3.9869 | 1 | 3.9869 | 1
207 | Classroom | 570 | 38 |  |  | 990 | 22 | 22 | Unit Ventilator | 8 | 7920 | 4.3182 | 1 | 4.3182 | 2 | 4.3182 | 2
208 | Classroom | 407 | 27 |  |  | 362 | 8 | 8 | Unit Ventilator | 8 | 2896 | 8.4323 | 1 | 8.4323 | 2 | 8.4323 | 2
208A | Classroom | 74 | 4 |  |  | 195 | 4 | 4 | Unit Ventilator | 8 | 1560 | 2.8462 | 1 | 2.8462 | 1 | 2.8462 | 1
209 | Classroom | 461 | 30 |  |  | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 5.1451 | 1 | 5.1451 | 2 | 5.1451 | 2
210 | Classroom | 357 | 23 |  |  | 957 | 21 | 21 | Unit Ventilator | 8 | 7656 | 2.7978 | 1 | 2.7978 | 1 | 2.7978 | 1
211 | Classroom | 545 | 36 |  |  | 990 | 22 | 22 | Unit Ventilator | 8 | 7920 | 4.1288 | 1 | 4.1288 | 2 | 4.1288 | 2
212 | Classroom | 416 | 27 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 3.8424 | 1 | 3.8424 | 1 | 3.8424 | 1
213 | Classroom | 444 | 29 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 3.6039 | 1 | 3.6039 | 1 | 3.6039 | 1
214 | Classroom | 430 | 28 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 3.7326 | 1 | 3.7326 | 1 | 3.7326 | 1
215 | Classroom | 429 | 28 |  |  | 952 | 21 | 21 | Unit Ventilator | 8 | 7616 | 3.3797 | 1 | 3.3797 | 1 | 3.3797 | 1
216 | Classroom | 180 | 12 |  |  | 325 | 7 | 7 | Unit Ventilator | 8 | 2600 | 4.1538 | 1 | 4.1538 | 2 | 4.1538 | 2
217 | Classroom | 206 | 13 |  |  | 420 | 9 | 9 | Unit Ventilator | 8 | 3360 | 3.6786 | 1 | 3.6786 | 1 | 3.6786 | 1
218 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Unit Ventilator
225 | Library | 1255 | 83 |  |  | 3628 | 82 | 82 | Unit Ventilator | 8 | 29024 | 2.5944 | 1.062 | 2.7553 | 1 | 2.7553 | 1
301 | Classroom | 570 | 38 |  |  | 957 | 21 | 21 | Unit Ventilator | 8 | 7656 | 4.4671 | 1 | 4.4671 | 2 | 4.4671 | 2
302 | Classroom | 289 | 19 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.5087 | 1 | 2.5087 | 1 | 2.5087 | 1
303 | Classroom | 328 | 21 |  |  | 957 | 21 | 21 | Unit Ventilator | 8 | 7656 | 2.5705 | 1 | 2.5705 | 1 | 2.5705 | 1
304 | Classroom | 501 | 33 |  |  | 754 | 17 | 17 | Unit Ventilator | 8 | 6032 | 4.9834 | 1 | 4.9834 | 2 | 4.9834 | 2
305 | Classroom | 336 | 22 |  |  | 1020 | 23 | 22 | Unit Ventilator | 8 | 8160 | 2.4706 | 1 | 2.4706 | 1 | 2.4706 | 1
306 | Classroom | 545 | 36 |  |  | 1020 | 23 | 23 | Unit Ventilator | 8 | 8160 | 4.0074 | 1 | 4.0074 | 2 | 4.0074 | 2
307 | Classroom | 374 | 24 |  |  | 506 | 11 | 11 | Unit Ventilator | 8 | 4048 | 5.5435 | 1 | 5.5435 | 2 | 5.5435 | 2
308 | Classroom | 418 | 27 |  |  | 460 | 10 | 10 | Unit Ventilator | 8 | 3680 | 6.8152 | 1 | 6.8152 | 2 | 6.8152 | 2
309 | Classroom | 550 | 36 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 4.4643 | 1 | 4.4643 | 2 | 4.4643 | 2
310 | Classroom | 441 | 29 |  |  | 1020 | 23 | 23 | Unit Ventilator | 8 | 8160 | 3.2426 | 1 | 3.2426 | 1 | 3.2426 | 1
311 | Classroom | 439 | 29 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 3.5633 | 1 | 3.5633 | 1 | 3.5633 | 1
312 | Classroom | 401 | 26 |  |  | 696 | 15 | 15 | Unit Ventilator | 8 | 5568 | 4.3211 | 1 | 4.3211 | 2 | 4.3211 | 2
313 | Classroom | 530 | 35 |  |  | 957 | 21 | 21 | Unit Ventilator | 8 | 7656 | 4.1536 | 1 | 4.1536 | 2 | 4.1536 | 2
314 | Classroom | 325 | 21 |  |  | 858 | 19 | 19 | Unit Ventilator | 8 | 6864 | 2.8409 | 1 | 2.8409 | 1 | 2.8409 | 1
315 | Classroom | 568 | 37 |  |  | 1650 | 37 | 37 | Unit Ventilator | 8 | 13200 | 2.5818 | 1 | 2.5818 | 1 | 2.5818 | 1
316 | Classroom | 318 | 21 |  |  | 1650 | 37 | 21 | Unit Ventilator | 8 | 13200 | 1.4455 | 1 | 1.4455 | 1 | 1.4455 | 1
317 | Classroom | 300 | 20 |  |  | 1664 | 37 | 20 | Unit Ventilator | 8 | 13312 | 1.3522 | 1 | 1.3522 | 1 | 1.3522 | 1
318 | Classroom | 62 | 4 |  |  |  | 0 | 0 | Unit Ventilator
- | B.E. Office | 139 | 9 |  |  | 88 | 2 | 2 | AHU | 8 | 704 | 11.8466 | 1 | 11.8466 | 3 | 11.8466 | 3
- | GYM | 1357 | 90 |  |  | 6110 | 138 | 90 | AHU | 8 | 48880 | 1.6657 | 1.062 | 1.769 | 1 | 1.769 | 1
- | Stage/Auditorium/Cafeteria | 0 | 0 |  |  | 4588 | 104 | 0 | AHU | 8 | 36704 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Kitchen | 47 | 3 |  |  | 403 | 9 | 3 | AHU | 8 | 3224 | 0.87469 | 1 | 0.87469 | 0 | 0.87469 | 0
Sheet Last Modified: | 2021-04-07
School: | Horatio Hackett Elementary School
Vendor: | Devine Brothers | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
104 | Library | 501 | 33 | Yes | 20 | 1920 | 43 | 43 | Unit Ventilator | 8 | 15360 | 1.957 | 1 | 1.957 | 1 | 21.957 | 3
106 | Gym Mechanical | 497 | 33 |  |  | 624 | 14 | 14 | AHU | 8 | 4992 | 5.9736 | 1 | 5.9736 | 2 | 5.9736 | 2
107 | Gym Mechanical | 959 | 63 |  |  | 1400 | 31 | 31 | AHU | 8 | 11200 | 5.1375 | 1 | 5.1375 | 2 | 5.1375 | 2
108 | Lounge | 299 | 19 |  |  | 560 | 12 | 12 | Unit Ventilator | 8 | 4480 | 4.0045 | 1 | 4.0045 | 2 | 4.0045 | 2
109 | Classroom | 394 | 26 |  |  | 1136 | 25 | 25 | Unit Ventilator | 8 | 9088 | 2.6012 | 1 | 2.6012 | 1 | 2.6012 | 1
110 | Classroom | 323 | 21 |  |  | 1024 | 23 | 21 | Unit Ventilator | 8 | 8192 | 2.3657 | 1 | 2.3657 | 1 | 2.3657 | 1
111 | Classroom | 284 | 18 |  |  | 776 | 17 | 17 | Unit Ventilator | 8 | 6208 | 2.7448 | 1 | 2.7448 | 1 | 2.7448 | 1
112 | Classroom | 280 | 18 |  |  | 720 | 16 | 16 | Unit Ventilator | 8 | 5760 | 2.9167 | 1 | 2.9167 | 1 | 2.9167 | 1
201 | Classroom | 279 | 18 |  |  | 840 | 19 | 18 | Unit Ventilator | 8 | 6720 | 2.4911 | 1 | 2.4911 | 1 | 2.4911 | 1
202 | Classroom | 658 | 43 |  |  | 784 | 17 | 17 | Unit Ventilator | 8 | 6272 | 6.2946 | 1 | 6.2946 | 2 | 6.2946 | 2
203 | Classroom | 335 | 22 |  |  | 784 | 17 | 17 | Unit Ventilator | 8 | 6272 | 3.2047 | 1 | 3.2047 | 1 | 3.2047 | 1
204 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom | 475 | 31 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 4.2411 | 1 | 4.2411 | 2 | 4.2411 | 2
205A | Sm office / Speech Room | 223 | 14 |  |  | 304 | 6 | 6 | Unit Ventilator | 8 | 2432 | 5.5016 | 1 | 5.5016 | 2 | 5.5016 | 2
206 | Classroom | 0 | 0 | Yes | 20 | 696 | 15 | 15 | Unit Ventilator | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 20 | 488 | 11 | 11 | Unit Ventilator | 8 | 3904 | 0 | 1 | 0 | 0 | 20 | 3
207A | Small Office | 120 | 8 |  |  | 248 | 5 | 5 | Unit Ventilator | 8 | 1984 | 3.629 | 1 | 3.629 | 1 | 3.629 | 1
208 | Classroom | 278 | 18 |  |  | 784 | 17 | 17 | Unit Ventilator | 8 | 6272 | 2.6594 | 1 | 2.6594 | 1 | 2.6594 | 1
209 | Classroom | 362 | 24 |  |  | 672 | 15 | 15 | Unit Ventilator | 8 | 5376 | 4.0402 | 1 | 4.0402 | 2 | 4.0402 | 2
210 | Classroom | 0 | 0 | Yes | 20 | 784 | 17 | 17 | Unit Ventilator | 8 | 6272 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom | 334 | 22 |  |  | 784 | 17 | 17 | Unit Ventilator | 8 | 6272 | 3.1952 | 1 | 3.1952 | 1 | 3.1952 | 1
212 | Classroom | 355 | 23 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 3.1696 | 1 | 3.1696 | 1 | 3.1696 | 1
212A | Office/Councelors |  | 0 |  |  | 336 | 7 | 0 | N/A | 8 | 2688 | 0 | 1 | 0 | 0 | 0 | 0
214 | Classroom | 455 | 30 |  |  | 864 | 19 | 19 | AHU | 8 | 6912 | 3.9497 | 1 | 3.9497 | 1 | 3.9497 | 1
215 | Classroom | 405 | 27 |  |  | 920 | 20 | 20 | AHU | 8 | 7360 | 3.3016 | 1 | 3.3016 | 1 | 3.3016 | 1
216 | Classroom | 505 | 33 |  |  | 832 | 18 | 18 | AHU | 8 | 6656 | 4.5523 | 1 | 4.5523 | 2 | 4.5523 | 2
217 | Classroom | 390 | 26 |  |  | 768 | 17 | 17 | Unit Ventilator | 8 | 6144 | 3.8086 | 1 | 3.8086 | 1 | 3.8086 | 1
218 | Classroom | 311 | 20 | Yes | 20 | 976 | 22 | 22 | AHU | 8 | 7808 | 2.3899 | 1 | 2.3899 | 1 | 22.3899 | 3
219 | Classroom | 405 | 27 |  |  | 880 | 20 | 20 | AHU | 8 | 7040 | 3.4517 | 1 | 3.4517 | 1 | 3.4517 | 1
219c | Classroom | 123 | 8 |  |  | 288 | 6 | 6 | Unit Ventilator | 8 | 2304 | 3.2031 | 1 | 3.2031 | 1 | 3.2031 | 1
305 | Classroom | 400 | 26 |  |  | 1000 | 22 | 22 | Unit Ventilator | 8 | 8000 | 3 | 1 | 3 | 1 | 3 | 1
306 | Classroom | 0 | 0 | Yes | 20 | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom | 315 | 21 |  |  | 824 | 18 | 18 | Unit Ventilator | 8 | 6592 | 2.8671 | 1 | 2.8671 | 1 | 2.8671 | 1
308 | Classroom | 329 | 21 |  |  | 824 | 18 | 18 | Unit Ventilator | 8 | 6592 | 2.9945 | 1 | 2.9945 | 1 | 2.9945 | 1
308D | Councelors | 38 | 2 | Yes | 20 | 384 | 8 | 8 | Unit Ventilator | 8 | 3072 | 0.74219 | 1 | 0.74219 | 0 | 20.7422 | 3
309 | Classroom | 395 | 26 |  |  | 944 | 21 | 21 | Unit Ventilator | 8 | 7552 | 3.1382 | 1 | 3.1382 | 1 | 3.1382 | 1
- | Caf/Auditorium | 1435 | 95 |  |  | 6914 | 157 | 95 | AHU | 8 | 55312 | 1.5566 | 1.4912 | 2.3212 | 1 | 2.3212 | 1
- | GYM | 964 | 64 |  |  | 4770 | 108 | 64 | AHU | 8 | 38160 | 1.5157 | 1.062 | 1.6098 | 1 | 1.6098 | 1
- | Kitchen | 413 | 27 |  |  | 954 | 21 | 21 | AHU | 8 | 7632 | 3.2469 | 1 | 3.2469 | 1 | 3.2469 | 1
- | Main Office | 304 | 20 |  |  | 832 | 18 | 18 | Unit Ventilator | 8 | 6656 | 2.7404 | 1 | 2.7404 | 1 | 2.7404 | 1
- | Nurses Office | 50 | 3 | Yes | 20 | 564 | 12 | 12 | Unit Ventilator | 8 | 4512 | 0.66489 | 1 | 0.66489 | 0 | 20.6649 | 3
Sheet Last Modified: | 2021-04-08
School: | Andrew Hamilton Elementary School
Vendor: | Capital | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
104 | Classroom | 398 | 26 |  |  | 598 | 13 | 13 | Unit Ventilator | 8 | 4784 | 4.9916 | 1 | 4.9916 | 2 | 4.9916 | 2
106 | Classroom | 407 | 27 |  |  | 755 | 17 | 17 | Unit Ventilator | 8 | 6040 | 4.043 | 1 | 4.043 | 2 | 4.043 | 2
107 | Classroom | 376 | 25 |  |  | 599 | 13 | 13 | Unit Ventilator | 8 | 4792 | 4.7078 | 1 | 4.7078 | 2 | 4.7078 | 2
111 | Cafeteria | 1724 | 114 |  |  | 2444 | 55 | 55 | AHU | 8 | 19552 | 5.2905 | 1 | 5.2905 | 2 | 5.2905 | 2
112 | Auditorium | 813 | 54 |  |  | 3875 | 88 | 54 | AHU | 8 | 31000 | 1.5735 | 1.062 | 1.6712 | 1 | 1.6712 | 1
119 | Music | 391 | 26 |  |  | 827 | 18 | 18 | AHU | 8 | 6616 | 3.5459 | 1 | 3.5459 | 1 | 3.5459 | 1
121 | Gym | 1663 | 110 |  |  | 4628 | 105 | 105 | AHU | 8 | 37024 | 2.695 | 1.062 | 2.8622 | 1 | 2.8622 | 1
127 | Classroom | 595 | 39 |  |  | 1186 | 26 | 26 | Unit Ventilator | 8 | 9488 | 3.7626 | 1 | 3.7626 | 1 | 3.7626 | 1
128 | Classroom | 628 | 41 |  |  | 1370 | 31 | 31 | Unit Ventilator | 8 | 10960 | 3.438 | 1 | 3.438 | 1 | 3.438 | 1
129 | Classroom | 565 | 37 |  |  | 1112 | 25 | 25 | Unit Ventilator | 8 | 8896 | 3.8107 | 1 | 3.8107 | 1 | 3.8107 | 1
130 | Classroom | 608 | 40 |  |  | 1378 | 31 | 31 | Unit Ventilator | 8 | 11024 | 3.3091 | 1 | 3.3091 | 1 | 3.3091 | 1
131 | Classroom | 575 | 38 |  |  | 1169 | 26 | 26 | Unit Ventilator | 8 | 9352 | 3.6891 | 1 | 3.6891 | 1 | 3.6891 | 1
200 | Classroom | 415 | 27 |  |  | 763 | 17 | 17 | Unit Ventilator | 8 | 6104 | 4.0793 | 1 | 4.0793 | 2 | 4.0793 | 2
201 | Classroom | 527 | 35 |  |  | 776 | 17 | 17 | Unit Ventilator | 8 | 6208 | 5.0934 | 1 | 5.0934 | 2 | 5.0934 | 2
202 | Teachers Lounge | 300 | 20 |  |  | 469 | 10 | 10 | Unit Ventilator | 8 | 3752 | 4.7974 | 1 | 4.7974 | 2 | 4.7974 | 2
205 | Team Planning | 353 | 23 |  |  | 431 | 9 | 9 | Unit Ventilator | 8 | 3448 | 6.1427 | 1 | 6.1427 | 2 | 6.1427 | 2
206 | Classroom | 454 | 30 |  |  | 595 | 13 | 13 | Unit Ventilator | 8 | 4760 | 5.7227 | 1 | 5.7227 | 2 | 5.7227 | 2
207 | Classroom | 454 | 30 |  |  | 847 | 19 | 19 | Unit Ventilator | 8 | 6776 | 4.0201 | 1 | 4.0201 | 2 | 4.0201 | 2
209 | General Office | 750 | 50 |  |  | 866 | 19 | 19 | Unit Ventilator | 8 | 6928 | 6.4954 | 1 | 6.4954 | 2 | 6.4954 | 2
223 | Classroom | 432 | 28 |  |  | 847 | 19 | 19 | Unit Ventilator | 8 | 6776 | 3.8253 | 1 | 3.8253 | 1 | 3.8253 | 1
224 | Classroom | 426 | 28 |  |  | 837 | 19 | 19 | Unit Ventilator | 8 | 6696 | 3.8172 | 1 | 3.8172 | 1 | 3.8172 | 1
225 | Classroom | 394 | 26 |  |  | 837 | 19 | 19 | Unit Ventilator | 8 | 6696 | 3.5305 | 1 | 3.5305 | 1 | 3.5305 | 1
226 | Classroom | 393 | 26 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 3.5089 | 1 | 3.5089 | 1 | 3.5089 | 1
227 | Classroom | 395 | 26 |  |  | 832 | 18 | 18 | Unit Ventilator | 8 | 6656 | 3.5607 | 1 | 3.5607 | 1 | 3.5607 | 1
228 | Classroom | 477 | 31 |  |  | 847 | 19 | 19 | Unit Ventilator | 8 | 6776 | 4.2237 | 1 | 4.2237 | 2 | 4.2237 | 2
300 | Classroom | 400 | 26 |  |  | 793 | 18 | 18 | Unit Ventilator | 8 | 6344 | 3.7831 | 1 | 3.7831 | 1 | 3.7831 | 1
301 | Classroom | 421 | 28 |  |  | 791 | 17 | 17 | Unit Ventilator | 8 | 6328 | 3.9918 | 1 | 3.9918 | 1 | 3.9918 | 1
302 | Classroom | 393 | 26 |  |  | 786 | 17 | 17 | Unit Ventilator | 8 | 6288 | 3.75 | 1 | 3.75 | 1 | 3.75 | 1
303 | Classroom | 365 | 24 |  |  | 640 | 14 | 14 | Unit Ventilator | 8 | 5120 | 4.2773 | 1 | 4.2773 | 2 | 4.2773 | 2
306 | Classroom | 413 | 27 |  |  | 793 | 18 | 18 | Unit Ventilator | 8 | 6344 | 3.9061 | 1 | 3.9061 | 1 | 3.9061 | 1
307 | Classroom | 464 | 30 |  |  | 793 | 18 | 18 | Unit Ventilator | 8 | 6344 | 4.3884 | 1 | 4.3884 | 2 | 4.3884 | 2
309 | Classroom | 306 | 20 |  |  | 597 | 13 | 13 | Unit Ventilator | 8 | 4776 | 3.8442 | 1 | 3.8442 | 1 | 3.8442 | 1
310 | Classroom | 0 | 0 | Yes | 20 | 708 | 16 | 16 |  | 8 | 5664 | 0 | 1 | 0 | 0 | 20 | 3
311J | Janitors | 173 | 11 |  |  | 59 | 1 | 1 | Unit Ventilator | 8 | 472 | 21.9915 | 1 | 21.9915 | 3 | 21.9915 | 3
314 | Office | 551 | 36 |  |  | 214 | 4 | 4 | Unit Ventilator | 8 | 1712 | 19.3107 | 1 | 19.3107 | 3 | 19.3107 | 3
315 | Office | 724 | 48 |  |  | 214 | 4 | 4 | Unit Ventilator | 8 | 1712 | 25.3738 | 1 | 25.3738 | 4 | 25.3738 | 4
318 | Classroom | 382 | 25 |  |  | 911 | 20 | 20 | Unit Ventilator | 8 | 7288 | 3.1449 | 1 | 3.1449 | 1 | 3.1449 | 1
319 | Classroom | 0 | 0 | Yes | 20 | 616 | 14 | 14 | Unit Ventilator | 8 | 4928 | 0 | 1 | 0 | 0 | 20 | 3
320 | Team Planning | 0 | 0 | Yes | 20 | 235 | 5 | 5 | Unit Ventilator | 8 | 1880 | 0 | 1 | 0 | 0 | 20 | 3
321 | Team Planning | 300 | 20 |  |  | 243 | 5 | 5 | Unit Ventilator | 8 | 1944 | 9.2593 | 1 | 9.2593 | 2 | 9.2593 | 2
322 | Classroom | 450 | 30 |  |  | 820 | 18 | 18 | Unit Ventilator | 8 | 6560 | 4.1159 | 1 | 4.1159 | 2 | 4.1159 | 2
323 | Classroom | 0 | 0 | Yes | 20 | 620 | 14 | 14 | Unit Ventilator | 8 | 4960 | 0 | 1 | 0 | 0 | 20 | 3
327 | Office | 432 | 28 |  |  | 201 | 4 | 4 | Unit Ventilator | 8 | 1608 | 16.1194 | 1 | 16.1194 | 3 | 16.1194 | 3
328 | Office | 735 | 49 |  |  | 233 | 5 | 5 | Unit Ventilator | 8 | 1864 | 23.6588 | 1 | 23.6588 | 3 | 23.6588 | 3
331 | Classroom | 0 | 0 | Yes | 20 | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
332 | Classroom | 339 | 22 |  |  | 625 | 14 | 14 | Unit Ventilator | 8 | 5000 | 4.068 | 1 | 4.068 | 2 | 4.068 | 2
333 | Classroom | 423 | 28 |  |  | 894 | 20 | 20 | Unit Ventilator | 8 | 7152 | 3.5487 | 1 | 3.5487 | 1 | 3.5487 | 1
334 | Classroom | 393 | 26 |  |  | 800 | 18 | 18 | Unit Ventilator | 8 | 6400 | 3.6844 | 1 | 3.6844 | 1 | 3.6844 | 1
335 | Classroom | 838 | 55 |  |  | 1684 | 38 | 38 | Unit Ventilator | 8 | 13472 | 3.7322 | 1 | 3.7322 | 1 | 3.7322 | 1
336 | Classroom | 375 | 25 |  |  | 908 | 20 | 20 | Unit Ventilator | 8 | 7264 | 3.0975 | 1 | 3.0975 | 1 | 3.0975 | 1
337 | Classroom | 0 | 0 | Yes | 20 | 932 | 21 | 21 | Unit Ventilator | 8 | 7456 | 0 | 1 | 0 | 0 | 20 | 3
- | Library | 2442 | 162 |  |  | 3672 | 83 | 83 | Unit Ventilator | 8 | 29376 | 4.9877 | 1.062 | 5.2972 | 2 | 5.2972 | 2
Sheet Last Modified: | 2021-04-21
School: | John Hancock Demonstrative Elementary School
Vendor: | Devine Brothers | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 127 | 8 |  |  | 528 | 12 | 8 | Unit Ventilator | 8 | 4224 | 1.804 | 1 | 1.804 | 1 | 1.804 | 1
102 | Classroom | 416 | 27 |  |  | 750 | 17 | 17 | Unit Ventilator | 8 | 6000 | 4.16 | 1 | 4.16 | 2 | 4.16 | 2
103 | Classroom | 123 | 8 |  |  | 567 | 12 | 8 | Unit Ventilator | 8 | 4536 | 1.627 | 1 | 1.627 | 1 | 1.627 | 1
104 | Classroom | 283 | 18 |  |  | 483 | 10 | 10 | Unit Ventilator | 8 | 3864 | 4.3944 | 1 | 4.3944 | 2 | 4.3944 | 2
105 | Classroom | 0 | 0 | Yes | 20 | 567 | 12 | 12 | Unit Ventilator | 8 | 4536 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom | 171 | 11 |  |  | 756 | 17 | 11 | Unit Ventilator | 8 | 6048 | 1.6964 | 1 | 1.6964 | 1 | 1.6964 | 1
107 | Classroom | 237 | 15 |  |  | 806 | 18 | 15 | Unit Ventilator | 8 | 6448 | 2.2053 | 1 | 2.2053 | 1 | 2.2053 | 1
108 | Classroom | 0 | 0 | Yes | 20 | 648 | 14 | 14 | Unit Ventilator | 8 | 5184 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 173 | 11 |  |  | 638 | 14 | 11 | Unit Ventilator | 8 | 5104 | 2.0337 | 1 | 2.0337 | 1 | 2.0337 | 1
110 | Classroom | 233 | 15 |  |  | 812 | 18 | 15 | Unit Ventilator | 8 | 6496 | 2.1521 | 1 | 2.1521 | 1 | 2.1521 | 1
111 | Classroom | 168 | 11 |  |  | 588 | 13 | 11 | Unit Ventilator | 8 | 4704 | 2.1429 | 1 | 2.1429 | 1 | 2.1429 | 1
200 | Classroom | 323 | 21 | Yes | 20 | 510 | 11 | 11 | Unit Ventilator | 8 | 4080 | 4.75 | 1 | 4.75 | 2 | 24.75 | 4
200A | Office |  | 0 | Yes | 20 |  | 0 | 0
202 | Classroom | 432 | 28 |  |  | 1271 | 28 | 28 | Unit Ventilator | 8 | 10168 | 2.5492 | 1 | 2.5492 | 1 | 2.5492 | 1
203 | Classroom | 299 | 19 |  |  | 588 | 13 | 13 | Unit Ventilator | 8 | 4704 | 3.8138 | 1 | 3.8138 | 1 | 3.8138 | 1
204 | Classroom | 324 | 21 |  |  | 575 | 13 | 13 | Unit Ventilator | 8 | 4600 | 4.2261 | 1 | 4.2261 | 2 | 4.2261 | 2
205 | Classroom | 255 | 17 |  |  | 616 | 14 | 14 | Unit Ventilator | 8 | 4928 | 3.1047 | 1 | 3.1047 | 1 | 3.1047 | 1
206 | Classroom | 324 | 21 |  |  | 1116 | 25 | 21 | Unit Ventilator | 8 | 8928 | 2.1774 | 1 | 2.1774 | 1 | 2.1774 | 1
207 | Classroom | 310 | 20 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.691 | 1 | 2.691 | 1 | 2.691 | 1
208 | Classroom | 308 | 20 |  |  | 837 | 19 | 19 | Unit Ventilator | 8 | 6696 | 2.7599 | 1 | 2.7599 | 1 | 2.7599 | 1
209 | Classroom | 312 | 20 |  |  | 868 | 19 | 19 | Unit Ventilator | 8 | 6944 | 2.6959 | 1 | 2.6959 | 1 | 2.6959 | 1
210 | Classroom | 303 | 20 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 3.1216 | 1 | 3.1216 | 1 | 3.1216 | 1
211 | Classroom | 298 | 19 |  |  | 754 | 17 | 17 | Unit Ventilator | 8 | 6032 | 2.9642 | 1 | 2.9642 | 1 | 2.9642 | 1
212 | Classroom |  | 0 | Yes | 20 | 744 | 16 | 16 | Unit Ventilator | 8 | 5952 | 0 | 1 | 0 | 0 | 20 | 3
213 | Classroom | 174 | 11 | Yes | 20 | 806 | 18 | 18 | Unit Ventilator | 8 | 6448 | 1.6191 | 1 | 1.6191 | 1 | 21.6191 | 3
214 | Computer Lab | 312 | 20 |  |  | 462 | 10 | 10 | Unit Ventilator | 8 | 3696 | 5.0649 | 1 | 5.0649 | 2 | 5.0649 | 2
215 | Classroom | 0 | 0 | Yes | 20 | 364 | 8 | 8 | Unit Ventilator | 8 | 2912 | 0 | 1 | 0 | 0 | 20 | 3
216 | Classroom | 0 | 0 |  |  | 364 | 8 | 0 | Unit Ventilator | 8 | 2912 | 0 | 1 | 0 | 0 | 0 | 0
217 | Classroom | 334 | 22 |  |  | 875 | 19 | 19 | Unit Ventilator | 8 | 7000 | 2.8629 | 1 | 2.8629 | 1 | 2.8629 | 1
219 | Classroom | 294 | 19 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 2.7841 | 1 | 2.7841 | 1 | 2.7841 | 1
218 | Nurse Office |  | 0 | Yes | 20 | 252 | 5 | 5 |  | 8 | 2016 | 0 | 1 | 0 | 0 | 20 | 3
220 | Office | 0 | 0 | Yes | 20 | 126 | 2 | 2 | Unit Ventilator | 8 | 1008 | 0 | 1 | 0 | 0 | 20 | 3
B213 | Classroom |  | 0 | Yes | 20 | 363 | 8 | 8 |  | 8 | 2904 | 0 | 1 | 0 | 0 | 20 | 3
B3 | Faculty Lounge | 184 | 12 | Yes | 20 | 540 | 12 | 12 | Unit Ventilator | 8 | 4320 | 2.5556 | 1 | 2.5556 | 1 | 22.5556 | 3
B13 | Classroom |  | 0 | Yes | 20 |  | 0 | 0
HS215 | Classroom |  | 0 | Yes | 20 | 608 | 13 | 13 |  | 8 | 4864 | 0 | 1 | 0 | 0 | 20 | 3
HS216 | Classroom |  | 0 | Yes | 20 | 608 | 13 | 13 |  | 8 | 4864 | 0 | 1 | 0 | 0 | 20 | 3
- | Classroom Behind kitchen | 37 | 2 |  |  | 224 | 5 | 2 | Unit Ventilator | 8 | 1792 | 1.2388 | 1 | 1.2388 | 1 | 1.2388 | 1
- | Gym Office | 0 | 0 | Yes | 20 | 100 | 2 | 2 | Unit Ventilator | 8 | 800 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 |  |  | 288 | 6 | 0 | AHU | 8 | 2304 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 |  |  | 4600 | 104 | 0 | AHU | 8 | 36800 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Kitchen | 0 | 0 | Yes | 20 | 448 | 10 | 10 | Unit Ventilator | 8 | 3584 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Lobby | 0 | 0 |  |  | 720 | 16 | 0 | Unit Ventilator | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office | 201 | 13 |  |  | 340 | 7 | 7 | Unit Ventilator | 8 | 2720 | 4.4338 | 1 | 4.4338 | 2 | 4.4338 | 2
- | Main Office Side Office | 0 | 0 |  |  | 104 | 2 | 0 | Unit Ventilator | 8 | 832 | 0 | 1 | 0 | 0 | 0 | 0
- | Principals Office | 196 | 13 |  |  | 238 | 5 | 5 | Unit Ventilator | 8 | 1904 | 6.1765 | 1 | 6.1765 | 2 | 6.1765 | 2
Assistant Principal | Office |  | 0 | Yes | 20 |  | 0 | 0
Dean | Office |  | 0 | Yes | 20 |  | 0 | 0
- | Library | 692 | 46 |  |  | 1520 | 34 | 34 | Unit Ventilator | 8 | 12160 | 3.4145 | 1 | 3.4145 | 1 | 3.4145 | 1
- | Office Across from 210 | 0 | 0 |  |  | 120 | 2 | 0 | N/A | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
- | Office across from gym | 0 | 0 |  |  | 204 | 4 | 0 | Unit Ventilator | 8 | 1632 | 0 | 1 | 0 | 0 | 0 | 0
- | Office across from Room 107 | 76 | 5 |  |  | 140 | 3 | 3 | Unit Ventilator | 8 | 1120 | 4.0714 | 1 | 4.0714 | 2 | 4.0714 | 2
- | Office across from room 110 | 115 | 7 |  |  | 140 | 3 | 3 | Unit Ventilator | 8 | 1120 | 6.1607 | 1 | 6.1607 | 2 | 6.1607 | 2
- | Office Next to gym | 0 | 0 |  |  | 80 | 1 | 0 | Unit Ventilator | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-05-03
School: | Warren G. Harding Middle School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | - |  | 0 |  |  | 288 | 6 | 0 |  | 8 | 2304 | 0 | 1 | 0 | 0 | 0 | 0
101a | - |  | 0 |  |  | 288 | 6 | 0 |  | 8 | 2304 | 0 | 1 | 0 | 0 | 0 | 0
102 | - |  | 0 | Yes | 20 | 1128 | 25 | 25 |  | 8 | 9024 | 0 | 1 | 0 | 0 | 20 | 3
102a | - |  | 0 |  |  | 100 | 2 | 0 |  | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
103 | - |  | 0 |  |  | 720 | 16 | 0 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
104 | - |  | 0 | Yes | 20 | 888 | 20 | 20 |  | 8 | 7104 | 0 | 1 | 0 | 0 | 20 | 3
104a | - |  | 0 |  |  | 110 | 2 | 0 |  | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
105 | - |  | 0 |  |  | 648 | 14 | 0 |  | 8 | 5184 | 0 | 1 | 0 | 0 | 0 | 0
105b | - |  | 0 |  |  | 770 | 17 | 0 |  | 8 | 6160 | 0 | 1 | 0 | 0 | 0 | 0
106c | - |  | 0 |  |  | 248 | 5 | 0 |  | 8 | 1984 | 0 | 1 | 0 | 0 | 0 | 0
107 | - |  | 0 |  |  | 936 | 21 | 0 |  | 8 | 7488 | 0 | 1 | 0 | 0 | 0 | 0
107a | - |  | 0 |  |  | 248 | 5 | 0 |  | 8 | 1984 | 0 | 1 | 0 | 0 | 0 | 0
107b | - |  | 0 |  |  | 50 | 1 | 0 |  | 8 | 400 | 0 | 1 | 0 | 0 | 0 | 0
107c | - |  | 0 |  |  | 25 | 0 | 0 |  | 8 | 200 | 0 | 1 | 0 | 0 | 0 | 0
108 | - |  | 0 | Yes | 20 | 886 | 20 | 20 |  | 8 | 7088 | 0 | 1 | 0 | 0 | 20 | 3
108a | - |  | 0 |  |  | 130 | 2 | 0 |  | 8 | 1040 | 0 | 1 | 0 | 0 | 0 | 0
108b | - |  | 0 |  |  | 25 | 0 | 0 |  | 8 | 200 | 0 | 1 | 0 | 0 | 0 | 0
108c | - |  | 0 |  |  | 50 | 1 | 0 |  | 8 | 400 | 0 | 1 | 0 | 0 | 0 | 0
109 | - |  | 0 |  |  | 576 | 13 | 0 |  | 8 | 4608 | 0 | 1 | 0 | 0 | 0 | 0
109a | - |  | 0 |  |  | 135 | 3 | 0 |  | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
110 | - |  | 0 |  |  | 912 | 20 | 0 |  | 8 | 7296 | 0 | 1 | 0 | 0 | 0 | 0
110a | - |  | 0 |  |  | 40 | 0 | 0 |  | 8 | 320 | 0 | 1 | 0 | 0 | 0 | 0
111 | - |  | 0 |  |  | 624 | 14 | 0 |  | 8 | 4992 | 0 | 1 | 0 | 0 | 0 | 0
112 | - |  | 0 |  |  | 576 | 13 | 0 |  | 8 | 4608 | 0 | 1 | 0 | 0 | 0 | 0
112a | - |  | 0 |  |  | 308 | 7 | 0 |  | 8 | 2464 | 0 | 1 | 0 | 0 | 0 | 0
113 | - |  | 0 |  |  | 360 | 8 | 0 |  | 8 | 2880 | 0 | 1 | 0 | 0 | 0 | 0
113a | - |  | 0 |  |  | 242 | 5 | 0 |  | 8 | 1936 | 0 | 1 | 0 | 0 | 0 | 0
113b | - |  | 0 |  |  | 352 | 8 | 0 |  | 8 | 2816 | 0 | 1 | 0 | 0 | 0 | 0
114 | - |  | 0 | Yes | 20 | 204 | 4 | 4 |  | 8 | 1632 | 0 | 1 | 0 | 0 | 20 | 3
116 | - |  | 0 |  |  | 2120 | 48 | 0 |  | 8 | 16960 | 0 | 1 | 0 | 0 | 0 | 0
116a | - |  | 0 |  |  | 416 | 9 | 0 |  | 8 | 3328 | 0 | 1 | 0 | 0 | 0 | 0
117 | - |  | 0 |  |  | 2700 | 61 | 0 |  | 8 | 21600 | 0 | 1.062 | 0 | 0 | 0 | 0
201 | - |  | 0 | Yes | 20 | 360 | 8 | 8 |  | 8 | 2880 | 0 | 1 | 0 | 0 | 20 | 3
201a | - |  | 0 |  |  | 432 | 9 | 0 |  | 8 | 3456 | 0 | 1 | 0 | 0 | 0 | 0
202 | - |  | 0 | Yes | 20 | 768 | 17 | 17 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
203 | - |  | 0 |  |  | 288 | 6 | 0 |  | 8 | 2304 | 0 | 1 | 0 | 0 | 0 | 0
203B | - |  | 0 | Yes | 20 | 200 | 4 | 4 |  | 8 | 1600 | 0 | 1 | 0 | 0 | 20 | 3
204 | - |  | 0 | Yes | 20 | 720 | 16 | 16 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
205 | - |  | 0 | Yes | 20 | 768 | 17 | 17 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
206 | - |  | 0 |  |  | 319 | 7 | 0 |  | 8 | 2552 | 0 | 1 | 0 | 0 | 0 | 0
206a | - |  | 0 |  |  | 224 | 5 | 0 |  | 8 | 1792 | 0 | 1 | 0 | 0 | 0 | 0
206b | - |  | 0 |  |  | 112 | 2 | 0 |  | 8 | 896 | 0 | 1 | 0 | 0 | 0 | 0
208 | - |  | 0 | Yes | 20 | 792 | 18 | 18 |  | 8 | 6336 | 0 | 1 | 0 | 0 | 20 | 3
209 | IMC |  | 0 | Yes | 20 | 2160 | 49 | 49 |  | 8 | 17280 | 0 | 1 | 0 | 0 | 20 | 3
211 | - |  | 0 |  |  | 936 | 21 | 0 |  | 8 | 7488 | 0 | 1 | 0 | 0 | 0 | 0
212 | - |  | 0 |  |  | 888 | 20 | 0 |  | 8 | 7104 | 0 | 1 | 0 | 0 | 0 | 0
213 | - |  | 0 |  |  | 336 | 7 | 0 |  | 8 | 2688 | 0 | 1 | 0 | 0 | 0 | 0
214 | - |  | 0 |  |  | 696 | 15 | 0 |  | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
215 | - |  | 0 | Yes | 20 | 648 | 14 | 14 |  | 8 | 5184 | 0 | 1 | 0 | 0 | 20 | 3
216 | - |  | 0 |  |  | 744 | 16 | 0 |  | 8 | 5952 | 0 | 1 | 0 | 0 | 0 | 0
217 | - |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
218 | - |  | 0 |  |  | 792 | 18 | 0 |  | 8 | 6336 | 0 | 1 | 0 | 0 | 0 | 0
219 | - |  | 0 |  |  | 768 | 17 | 0 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
220 | - |  | 0 |  |  | 744 | 16 | 0 |  | 8 | 5952 | 0 | 1 | 0 | 0 | 0 | 0
221 | - |  | 0 |  |  | 744 | 16 | 0 |  | 8 | 5952 | 0 | 1 | 0 | 0 | 0 | 0
222 | - |  | 0 | Yes | 20 | 768 | 17 | 17 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
223 | - |  | 0 | Yes | 20 | 816 | 18 | 18 |  | 8 | 6528 | 0 | 1 | 0 | 0 | 20 | 3
224 | - |  | 0 | Yes | 20 | 638 | 14 | 14 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
225 | - |  | 0 |  |  | 144 | 3 | 0 |  | 8 | 1152 | 0 | 1 | 0 | 0 | 0 | 0
301 | - |  | 0 |  |  | 648 | 14 | 0 |  | 8 | 5184 | 0 | 1 | 0 | 0 | 0 | 0
302 | - |  | 0 |  |  | 768 | 17 | 0 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
303 | - |  | 0 | Yes | 20 | 390 | 8 | 8 |  | 8 | 3120 | 0 | 1 | 0 | 0 | 20 | 3
304 | - |  | 0 |  |  | 720 | 16 | 0 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
305 | - |  | 0 |  |  | 768 | 17 | 0 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
306 | - |  | 0 |  |  | 966 | 21 | 0 |  | 8 | 7728 | 0 | 1 | 0 | 0 | 0 | 0
307a | - |  | 0 |  |  | 360 | 8 | 0 |  | 8 | 2880 | 0 | 1 | 0 | 0 | 0 | 0
307b | - |  | 0 |  |  | 600 | 13 | 0 |  | 8 | 4800 | 0 | 1 | 0 | 0 | 0 | 0
308a | - |  | 0 |  |  | 480 | 10 | 0 |  | 8 | 3840 | 0 | 1 | 0 | 0 | 0 | 0
308b | - |  | 0 |  |  | 336 | 7 | 0 |  | 8 | 2688 | 0 | 1 | 0 | 0 | 0 | 0
309 | - |  | 0 |  |  | 816 | 18 | 0 |  | 8 | 6528 | 0 | 1 | 0 | 0 | 0 | 0
310 | - |  | 0 |  |  | 1056 | 24 | 0 |  | 8 | 8448 | 0 | 1 | 0 | 0 | 0 | 0
311 | - |  | 0 |  |  | 960 | 21 | 0 |  | 8 | 7680 | 0 | 1 | 0 | 0 | 0 | 0
311a | - |  | 0 |  |  | 143 | 3 | 0 |  | 8 | 1144 | 0 | 1 | 0 | 0 | 0 | 0
312 | - |  | 0 | Yes | 20 | 936 | 21 | 21 |  | 8 | 7488 | 0 | 1 | 0 | 0 | 20 | 3
313 | - |  | 0 |  |  | 984 | 22 | 0 |  | 8 | 7872 | 0 | 1 | 0 | 0 | 0 | 0
314 | - |  | 0 |  |  | 768 | 17 | 0 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
315 | - |  | 0 |  |  | 360 | 8 | 0 |  | 8 | 2880 | 0 | 1 | 0 | 0 | 0 | 0
316 | - |  | 0 |  |  | 720 | 16 | 0 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
317 | - |  | 0 | Yes | 20 | 720 | 16 | 16 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
318 | - |  | 0 |  |  | 744 | 16 | 0 |  | 8 | 5952 | 0 | 1 | 0 | 0 | 0 | 0
320 | - |  | 0 |  |  | 816 | 18 | 0 |  | 8 | 6528 | 0 | 1 | 0 | 0 | 0 | 0
321 | - |  | 0 |  |  | 768 | 17 | 0 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
322 | - |  | 0 |  |  | 768 | 17 | 0 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
323 | - |  | 0 |  |  | 768 | 17 | 0 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
324 | - |  | 0 | Yes | 20 | 768 | 17 | 17 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
325 | - |  | 0 |  |  | 816 | 18 | 0 |  | 8 | 6528 | 0 | 1 | 0 | 0 | 0 | 0
326 | - |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office |  | 0 | Yes | 20 | 468 | 10 | 10 |  | 8 | 3744 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 144 | 3 | 3 |  | 8 | 1152 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium |  | 0 |  |  | 1944 | 44 | 0 |  | 8 | 15552 | 0 | 1 | 0 | 0 | 0 | 0
- | Girls Lunchroom |  | 0 |  |  | 2173 | 49 | 0 |  | 8 | 17384 | 0 | 1 | 0 | 0 | 0 | 0
- | Girls Gym |  | 0 |  |  | 1419 | 32 | 0 |  | 8 | 11352 | 0 | 1 | 0 | 0 | 0 | 0
- | Boy's Lunchroom |  | 0 |  |  | 2173 | 49 | 0 |  | 8 | 17384 | 0 | 1 | 0 | 0 | 0 | 0
- | Boy's Gym |  | 0 |  |  | 1419 | 32 | 0 |  | 8 | 11352 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21
School: | Avery D. Harrington Elementary-Middle School
Vendor: | EMCOR Fluidics | Devine Retest
EMCOR Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B1 | Classroom | 0 | 0 | Yes | 20 | 805 | 18 | 18 | House Fan | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
B2 | Classroom | 0 | 0 | Yes | 20 | 594 | 13 | 13 | House Fan | 8 | 4752 | 0 | 1 | 0 | 0 | 20 | 3
B3 | Classroom | 530 | 35 |  |  | 1122 | 25 | 25 | Unit Ventilator | 8 | 8976 | 3.5428 | 1 | 3.5428 | 1 | 3.5428 | 1
B4 | B4 | 295 | 19 |  |  | 1064 | 24 | 19 | Unit Ventilator | 8 | 8512 | 2.0794 | 1 | 2.0794 | 1 | 2.0794 | 1
B5 | Classroom | 299 | 19 |  |  | 910 | 20 | 19 | Unit Ventilator | 8 | 7280 | 2.4643 | 1 | 2.4643 | 1 | 2.4643 | 1
B6 | - | 363 | 24 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 3.3528 | 1 | 3.3528 | 1 | 3.3528 | 1
B8 | Classroom | 0 | 0 | Yes | 20 | 651 | 14 | 0 | House Fan | 8 | 5208 | 0 | 1 | 0 | 0 | 20 | 3
B9 | - |  | 0 | Yes | 20 | 600 | 13 | 13 |  | 8 | 4800 | 0 | 1 | 0 | 0 | 20 | 3
10A | Classroom |  | 0 | Yes | 20 | 253 | 5 |  |  | 8 | 2024 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom | 0 | 0 | Yes | 20 | 968 | 22 | 22 | House Fan | 8 | 7744 | 0 | 1 | 0 | 0 | 20 | 3
102 | Teachers Lounge |  | 0 |  |  | 216 | 4 | 0 | House Fan | 8 | 1728 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | House Fan | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom |  | 0 |  |  | 720 | 16 | 0 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
107 | Classroom | 0 | 0 | Yes | 20 | 725 | 16 | 16 | House Fan | 8 | 5800 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 20 | 750 | 17 | 17 | House Fan | 8 | 6000 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 651 | 43 |  |  | 1120 | 25 | 25 | Unit Ventilator | 8 | 8960 | 4.3594 | 1 | 4.3594 | 2 | 4.3594 | 2
109A | Classroom |  | 0 | Yes | 20 | 168 | 3 |  |  | 8 | 1344 | 0 | 1 | 0 | 0 | 20 | 3
109B | Classroom |  | 0 | Yes | 20 | 170 | 3 |  |  | 8 | 1360 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 775 | 17 | 17 | House Fan | 8 | 6200 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 750 | 17 | 17 | House Fan | 8 | 6000 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 644 | 14 | 14 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 20 | 3
203a | Asst Princ Office |  | 0 | Yes | 20 | 403 | 9 | 9 | House Fan | 8 | 3224 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 | Yes | 20 | 900 | 20 | 20 | House Fan | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 864 | 19 | 19 | House Fan | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | House Fan | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom |  | 0 | Yes | 20 | 696 | 15 | 15 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 | Yes | 20 | 900 | 20 | 20 | House Fan | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom |  | 0 | Yes | 20 | 780 | 17 | 17 | House Fan | 8 | 6240 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom |  | 0 | Yes | 20 | 644 | 14 | 14 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 20 | 3
303a | Counselor Office |  | 0 | Yes | 20 | 403 | 9 | 9 | House Fan | 8 | 3224 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom |  | 0 | Yes | 20 | 930 | 21 | 21 | House Fan | 8 | 7440 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom |  | 0 | Yes | 20 | 810 | 18 | 18 | House Fan | 8 | 6480 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom |  | 0 | Yes | 20 | 870 | 19 | 19 | House Fan | 8 | 6960 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom |  | 0 | Yes | 20 | 725 | 16 | 16 | House Fan | 8 | 5800 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom |  | 0 | Yes | 20 | 754 | 17 | 17 | House Fan | 8 | 6032 | 0 | 1 | 0 | 0 | 20 | 3
- | Library | 1190 | 79 |  |  | 3822 | 86 | 79 | Unit Ventilator | 8 | 30576 | 2.3352 | 1.062 | 2.48 | 1 | 2.48 | 1
- | Auditorium | 130 | 8 |  |  | 90 | 2 | 2 | AHU | 8 | 720 | 10.8333 | 1 | 10.8333 | 3 | 10.8333 | 3
- | Gym |  | 0 |  |  | 2760 | 62 | 0 |  | 8 | 22080 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Gym / Storeroom | 0 | 0 |  |  | 513 | 11 | 0 | AHU | 8 | 4104 | 0 | 1 | 0 | 0 | 0 | 0
| Kitchen |  | 0 | Yes | 20 | 120 | 2 |  |  | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 190 | 4 | 4 | House Fan | 8 | 1520 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 420 | 9 | 9 | House Fan | 8 | 3360 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 377 | 8 | 8 | House Fan | 8 | 3016 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-06
School: | John F. Hartranft Elementary-Middle School
Vendor: | Devine Brothers | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 560 | 37 |  |  | 1519 | 34 | 34 | Unit Ventilator | 8 | 12152 | 2.765 | 1 | 2.765 | 1 | 2.765 | 1
100A | Office | 0 | 0 |  |  | 108 | 2 | 0 | AHU | 8 | 864 | 0 | 1 | 0 | 0 | 0 | 0
100C | Office |  | 0 | Yes | 20 | 144 | 3 | 3 |  | 8 | 1152 | 0 | 1 | 0 | 0 | 20 | 3
100E | Office | 0 | 0 |  |  | 304 | 6 | 0 | AHU | 8 | 2432 | 0 | 1 | 0 | 0 | 0 | 0
100G | Office |  | 0 | Yes | 20 | 304 | 6 | 6 | AHU | 8 | 2432 | 0 | 1 | 0 | 0 | 20 | 3
100J | Office | 0 | 0 | Yes | 20 | 77 | 1 | 1 | AHU | 8 | 616 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom | 310 | 20 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.7679 | 1 | 2.7679 | 1 | 2.7679 | 1
102 | Classroom | 309 | 20 | Yes | 20 | 1302 | 29 | 29 | Unit Ventilator | 8 | 10416 | 1.78 | 1 | 1.78 | 1 | 21.78 | 3
103 | Classroom | 344 | 22 | Yes | 20 | 1302 | 29 | 29 | Unit Ventilator | 8 | 10416 | 1.9816 | 1 | 1.9816 | 1 | 21.9816 | 3
104 | Classroom | 440 | 29 |  |  | 1178 | 26 | 26 | Unit Ventilator | 8 | 9424 | 2.8014 | 1 | 2.8014 | 1 | 2.8014 | 1
105 | Classroom | 348 | 23 |  |  | 1178 | 26 | 23 | Unit Ventilator | 8 | 9424 | 2.2156 | 1 | 2.2156 | 1 | 2.2156 | 1
106 | Classroom | 258 | 17 | Yes | 20 | 1302 | 29 | 29 | Unit Ventilator | 8 | 10416 | 1.4862 | 1 | 1.4862 | 1 | 21.4862 | 3
107 | Classroom | 488 | 32 |  |  | 1302 | 29 | 29 | Unit Ventilator | 8 | 10416 | 2.8111 | 1 | 2.8111 | 1 | 2.8111 | 1
108 | Classroom | 346 | 23 |  |  | 1178 | 26 | 23 | Unit Ventilator | 8 | 9424 | 2.2029 | 1 | 2.2029 | 1 | 2.2029 | 1
109 | Classroom | 226 | 15 | Yes | 20 | 1178 | 26 | 26 | Unit Ventilator | 8 | 9424 | 1.4389 | 1 | 1.4389 | 1 | 21.4389 | 3
110 | Classroom | 277 | 18 | Yes | 20 | 1302 | 29 | 29 | Unit Ventilator | 8 | 10416 | 1.5956 | 1 | 1.5956 | 1 | 21.5956 | 3
111 | Classroom | 519 | 34 |  |  | 966 | 21 | 21 | Unit Ventilator | 8 | 7728 | 4.0295 | 1 | 4.0295 | 2 | 4.0295 | 2
112 | Classroom | 500 | 33 |  |  | 1302 | 29 | 29 | Unit Ventilator | 8 | 10416 | 2.8802 | 1 | 2.8802 | 1 | 2.8802 | 1
113 | Classroom | 485 | 32 |  |  | 874 | 19 | 19 | Unit Ventilator | 8 | 6992 | 4.1619 | 1 | 4.1619 | 2 | 4.1619 | 2
114 | Classroom | 407 | 27 |  |  | 950 | 21 | 21 | Unit Ventilator | 8 | 7600 | 3.2132 | 1 | 3.2132 | 1 | 3.2132 | 1
115 | Classroom | 316 | 21 | Yes | 20 | 1305 | 29 | 29 | Unit Ventilator | 8 | 10440 | 1.8161 | 1 | 1.8161 | 1 | 21.8161 | 3
116 | Classroom | 261 | 17 | Yes | 20 | 1305 | 29 | 29 | Unit Ventilator | 8 | 10440 | 1.5 | 1 | 1.5 | 1 | 21.5 | 3
117 | Classroom | 313 | 20 | Yes | 20 | 1305 | 29 | 29 | Unit Ventilator | 8 | 10440 | 1.7989 | 1 | 1.7989 | 1 | 21.7989 | 3
118 | Classroom | 473 | 31 |  |  | 1305 | 29 | 29 | Unit Ventilator | 8 | 10440 | 2.7184 | 1 | 2.7184 | 1 | 2.7184 | 1
118A | Classroom | 12 | 0 | Yes | 20 | 680 | 15 | 15 | AHU | 8 | 5440 | 0.13235 | 1 | 0.13235 | 0 | 20.1324 | 3
121 | Classroom | 55 | 3 | Yes | 20 | 792 | 18 | 18 | AHU | 8 | 6336 | 0.52083 | 1 | 0.52083 | 0 | 20.5208 | 3
121 | Backroom | 59 | 3 |  |  | 310 | 7 | 3 | AHU | 8 | 2480 | 1.4274 | 1 | 1.4274 | 1 | 1.4274 | 1
200 | Classroom | 368 | 24 | Yes | 20 | 1462 | 33 | 33 | Unit Ventilator | 8 | 11696 | 1.8878 | 1 | 1.8878 | 1 | 21.8878 | 3
201 | Classroom | 647 | 43 |  |  | 1178 | 26 | 26 | Unit Ventilator | 8 | 9424 | 4.1193 | 1 | 4.1193 | 2 | 4.1193 | 2
202 | Classroom | 454 | 30 |  |  | 1302 | 29 | 29 | Unit Ventilator | 8 | 10416 | 2.6152 | 1 | 2.6152 | 1 | 2.6152 | 1
203 | Classroom | 355 | 23 | Yes | 20 | 1302 | 29 | 29 | Unit Ventilator | 8 | 10416 | 2.0449 | 1 | 2.0449 | 1 | 22.0449 | 3
204 | Classroom | 258 | 17 | Yes | 20 | 1178 | 26 | 26 | Unit Ventilator | 8 | 9424 | 1.6426 | 1 | 1.6426 | 1 | 21.6426 | 3
205 | Classroom | 491 | 32 |  |  | 1178 | 26 | 26 | Unit Ventilator | 8 | 9424 | 3.1261 | 1 | 3.1261 | 1 | 3.1261 | 1
206 | Classroom | 282 | 18 | Yes | 20 | 1302 | 29 | 29 | Unit Ventilator | 8 | 10416 | 1.6244 | 1 | 1.6244 | 1 | 21.6244 | 3
207 | Classroom | 225 | 15 | Yes | 20 | 1302 | 29 | 29 | Unit Ventilator | 8 | 10416 | 1.2961 | 1 | 1.2961 | 1 | 21.2961 | 3
208 | Classroom | 247 | 16 | Yes | 20 | 1179 | 26 | 26 | Unit Ventilator | 8 | 9432 | 1.5712 | 1 | 1.5712 | 1 | 21.5712 | 3
209 | Classroom | 274 | 18 | Yes | 20 | 1179 | 26 | 26 | Unit Ventilator | 8 | 9432 | 1.743 | 1 | 1.743 | 1 | 21.743 | 3
210 | Classroom | 485 | 32 |  |  | 1302 | 29 | 29 | Unit Ventilator | 8 | 10416 | 2.7938 | 1 | 2.7938 | 1 | 2.7938 | 1
211 | Classroom | 519 | 34 |  |  | 1302 | 29 | 29 | Unit Ventilator | 8 | 10416 | 2.9896 | 1 | 2.9896 | 1 | 2.9896 | 1
212 | Classroom | 309 | 20 | Yes | 20 | 1178 | 26 | 26 | Unit Ventilator | 8 | 9424 | 1.9673 | 1 | 1.9673 | 1 | 21.9673 | 3
214 | Classroom | 325 | 21 |  |  | 782 | 17 | 17 | Unit Ventilator | 8 | 6256 | 3.117 | 1 | 3.117 | 1 | 3.117 | 1
- | Cafeteria | 2300 | 153 |  |  | 1593 | 36 | 36 | AHU | 8 | 12744 | 10.8286 | 1 | 10.8286 | 3 | 10.8286 | 3
- | Cafeteria Entrance Hallway | 0 | 0 |  |  | 730 | 16 | 0 | AHU | 8 | 5840 | 0 | 1 | 0 | 0 | 0 | 0
- | Conference/Office | 0 | 0 |  |  | 304 | 6 | 0 | AHU | 8 | 2432 | 0 | 1 | 0 | 0 | 0 | 0
- | Engineer Office | 0 | 0 |  |  | 112 | 2 | 0 | AHU | 8 | 896 | 0 | 1 | 0 | 0 | 0 | 0
- | Engineer Breakroom | 0 | 0 |  |  | 99 | 2 | 0 | AHU | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym | 3499 | 233 |  |  | 6160 | 140 | 140 | AHU | 8 | 49280 | 4.2601 | 1.062 | 4.5244 | 2 | 4.5244 | 2
- | Kitchen | 0 | 0 |  |  | 864 | 19 | 0 | AHU | 8 | 6912 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office | 0 | 0 | Yes | 20 | 1056 | 24 | 24 | AHU | 8 | 8448 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office | 0 | 0 | Yes | 20 | 425 | 9 | 9 | AHU | 8 | 3400 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office | 0 | 0 | Yes | 20 | 228 | 5 | 5 | AHU | 8 | 1824 | 0 | 1 | 0 | 0 | 20 | 3
- | Rear Entrance Hallway | 0 | 0 |  |  | 736 | 16 | 0 | AHU | 8 | 5888 | 0 | 1 | 0 | 0 | 0 | 0
- | Teacher Office | 0 | 0 |  |  | 77 | 1 | 0 | AHU | 8 | 616 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23
School: | Haverford Child Development Center
Vendor: | Devine Brothers | Devine Brothers Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
2 | Classroom | 291 | 19 | Yes | 20 | 1058 | 24 | 24 | RTU | 8 | 8464 | 2.0629 | 1 | 2.0629 | 1 | 22.0629 | 3
3 | Classroom | 323 | 21 | Yes | 20 | 1058 | 24 | 24 | RTU | 8 | 8464 | 2.2897 | 1 | 2.2897 | 1 | 22.2897 | 3
4 | Classroom | 277 | 18 | Yes | 20 | 1058 | 24 | 24 | RTU | 8 | 8464 | 1.9636 | 1 | 1.9636 | 1 | 21.9636 | 3
5 | Classroom | 374 | 24 |  |  | 1058 | 24 | 24 | RTU | 8 | 8464 | 2.6512 | 1 | 2.6512 | 1 | 2.6512 | 1
5A | Office | 15 | 1 |  |  | 170 | 3 | 1 | RTU | 8 | 1360 | 0.66176 | 1 | 0.66176 | 0 | 0.66176 | 0
6 | Conference | 418 | 27 |  |  | 621 | 14 | 14 | RTU | 8 | 4968 | 5.0483 | 1 | 5.0483 | 2 | 5.0483 | 2
7 | Conference | 415 | 27 |  |  | 621 | 14 | 14 | RTU | 8 | 4968 | 5.0121 | 1 | 5.0121 | 2 | 5.0121 | 2
8 | Classroom | 287 | 19 |  |  | 560 | 12 | 12 | RTU | 8 | 4480 | 3.8438 | 1 | 3.8438 | 1 | 3.8438 | 1
8A | Office | 336 | 22 |  |  | 210 | 4 | 4 | RTU | 8 | 1680 | 12 | 1 | 12 | 3 | 12 | 3
9 | Classroom | 723 | 48 |  |  | 962 | 21 | 21 | RTU | 8 | 7696 | 5.6367 | 1 | 5.6367 | 2 | 5.6367 | 2
10A | Lounge | 34 | 2 |  |  | 216 | 4 | 2 | RTU | 8 | 1728 | 1.1806 | 1 | 1.1806 | 1 | 1.1806 | 1
10B | Book Storage | 11 | 0 |  |  | 288 | 6 | 0 | RTU | 8 | 2304 | 0.28646 | 1 | 0.28646 | 0 | 0.28646 | 0
- | Gym | 1065 | 71 |  |  | 2204 | 50 | 50 | RTU | 8 | 17632 | 3.6241 | 1 | 3.6241 | 1 | 3.6241 | 1
- | Lobby | 18 | 1 |  |  | 608 | 13 | 1 | RTU | 8 | 4864 | 0.22204 | 1 | 0.22204 | 0 | 0.22204 | 0
- | Storage | 89 | 5 |  |  | 572 | 13 | 5 | RTU | 8 | 4576 | 1.167 | 1 | 1.167 | 1 | 1.167 | 1
- | BE Office | 18 | 1 |  |  | 128 | 2 | 1 | RTU | 8 | 1024 | 1.0547 | 1 | 1.0547 | 1 | 1.0547 | 1
Sheet Last Modified: | 2021-04-05
School: | Charles W. Henry Elementary School
Vendor: | Devine | Devine Part 2 | Devine Part 3 | Devine Part 4
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 0 | 0 | Yes | 20 | 650 | 14 | 14 | Unit Ventilator | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom | 443 | 29 |  |  | 837 | 19 | 19 | Unit Ventilator | 8 | 6696 | 3.9695 | 1 | 3.9695 | 1 | 3.9695 | 1
103 | Classroom | 371 | 24 |  |  | 817 | 18 | 18 | Unit Ventilator | 8 | 6536 | 3.4058 | 1 | 3.4058 | 1 | 3.4058 | 1
104 | Classroom | 374 | 24 |  |  | 818 | 18 | 18 | Unit Ventilator | 8 | 6544 | 3.4291 | 1 | 3.4291 | 1 | 3.4291 | 1
104A | Office | 0 | 0 | Yes | 20 | 57 | 1 | 1 |  | 8 | 456 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom | 397 | 26 |  |  | 951 | 21 | 21 | Unit Ventilator | 8 | 7608 | 3.1309 | 1 | 3.1309 | 1 | 3.1309 | 1
106 | Classroom | 308 | 20 |  |  | 815 | 18 | 18 | Unit Ventilator | 8 | 6520 | 2.8344 | 1 | 2.8344 | 1 | 2.8344 | 1
108 | Classroom | 481 | 32 |  |  | 650 | 14 | 14 | Unit Ventilator | 8 | 5200 | 5.55 | 1 | 5.55 | 2 | 5.55 | 2
109 | Classroom | 763 | 50 |  |  | 712 | 16 | 16 | Unit Ventilator | 8 | 5696 | 8.0372 | 1 | 8.0372 | 2 | 8.0372 | 2
110 | Classroom | 756 | 50 |  |  | 650 | 14 | 14 | Unit Ventilator | 8 | 5200 | 8.7231 | 1 | 8.7231 | 2 | 8.7231 | 2
110A | Office | 0 | 0 | Yes | 20 | 98 | 2 | 2 |  | 8 | 784 | 0 | 1 | 0 | 0 | 20 | 3
114 | Classroom | 773 | 51 |  |  | 749 | 17 | 17 |  | 8 | 5992 | 7.7403 | 1 | 7.7403 | 2 | 7.7403 | 2
201 | Classroom | 289 | 19 |  |  | 775 | 17 | 17 | Unit Ventilator | 8 | 6200 | 2.7968 | 1 | 2.7968 | 1 | 2.7968 | 1
202 | Classroom | 314 | 20 |  |  | 765 | 17 | 17 | Unit Ventilator | 8 | 6120 | 3.0784 | 1 | 3.0784 | 1 | 3.0784 | 1
203 | Classroom | 282 | 18 |  |  | 781 | 17 | 17 | Unit Ventilator | 8 | 6248 | 2.7081 | 1 | 2.7081 | 1 | 2.7081 | 1
203A | Office | 0 | 0 | Yes | 20 | 115 | 2 | 2 |  | 8 | 920 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom | 262 | 17 | Yes | 20 | 847 | 19 | 19 | Unit Ventilator | 8 | 6776 | 2.32 | 1 | 2.32 | 1 | 22.32 | 3
206 | Classroom | 285 | 19 |  |  | 546 | 12 | 12 | Unit Ventilator | 8 | 4368 | 3.9148 | 1 | 3.9148 | 1 | 3.9148 | 1
207 | Classroom | 273 | 18 |  |  | 815 | 18 | 18 | Unit Ventilator | 8 | 6520 | 2.5123 | 1 | 2.5123 | 1 | 2.5123 | 1
208 | Classroom | 265 | 17 |  |  | 787 | 17 | 17 | Unit Ventilator | 8 | 6296 | 2.5254 | 1 | 2.5254 | 1 | 2.5254 | 1
208A | Office | 0 | 0 | Yes | 20 | 170 | 3 | 3 |  | 8 | 1360 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 | Yes | 20 | 800 | 18 | 18 | Unit Ventilator | 8 | 6400 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom | 398 | 26 |  |  | 946 | 21 | 21 | Unit Ventilator | 8 | 7568 | 3.1554 | 1 | 3.1554 | 1 | 3.1554 | 1
214 | Classroom | 282 | 18 | Yes | 20 | 1736 | 39 | 39 | Unit Ventilator | 8 | 13888 | 1.2183 | 1 | 1.2183 | 1 | 21.2183 | 3
215 | Classroom | 387 | 25 |  |  | 1128 | 25 | 25 | Unit Ventilator | 8 | 9024 | 2.5731 | 1 | 2.5731 | 1 | 2.5731 | 1
216 | Classroom | 284 | 18 |  |  | 546 | 12 | 12 | Unit Ventilator | 8 | 4368 | 3.9011 | 1 | 3.9011 | 1 | 3.9011 | 1
217 | Classroom | 393 | 26 |  |  | 544 | 12 | 12 | Unit Ventilator | 8 | 4352 | 5.4182 | 1 | 5.4182 | 2 | 5.4182 | 2
218 | Classroom | 307 | 20 | Yes | 20 | 1023 | 23 | 23 | Unit Ventilator | 8 | 8184 | 2.2507 | 1 | 2.2507 | 1 | 22.2507 | 3
- | Art Classroom | 249 | 16 |  |  | 778 | 17 | 16 | Unit Ventilator | 8 | 6224 | 2.4004 | 1 | 2.4004 | 1 | 2.4004 | 1
- | Auditorium | 1908 | 127 |  |  | 2417 | 54 | 54 | Unit Ventilator | 8 | 19336 | 5.9206 | 1 | 5.9206 | 2 | 5.9206 | 2
- | Cafe | 0 | 0 | Yes | 20 | 2104 | 47 | 47 | Unit Ventilator | 8 | 16832 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym | 1076 | 71 | Yes | 20 | 3199 | 72 | 72 | Unit Ventilator | 8 | 25592 | 2.5227 | 1.062 | 2.6792 | 1 | 22.6792 | 3
- | Janitor Office | 0 | 0 |  |  |  | 0 | 0 | N/A
- | Music Classroom | 292 | 19 |  |  | 833 | 18 | 18 | Unit Ventilator | 8 | 6664 | 2.6291 | 1 | 2.6291 | 1 | 2.6291 | 1
- | Sensory Classroom | 0 | 0 | Yes | 20 | 377 | 8 | 8 | Unit Ventilator | 8 | 3016 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor's Office | 0 | 0 |  |  | 299 | 6 | 0 |  | 8 | 2392 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurse's Office | 0 | 0 | Yes | 20 | 263 | 5 | 5 |  | 8 | 2104 | 0 | 1 | 0 | 0 | 20 | 3
- | Medical Waiting Room | 0 | 0 | Yes | 20 | 177 | 4 | 4 |  | 8 | 1416 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office | 0 | 0 | Yes | 20 | 307 | 6 | 6 |  | 8 | 2456 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-16
School: | Edward Heston Elementary School
Vendor: | Devine Brothers | Devine Brothers 2nd Retest
Devine Brothers 3rd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 148 | 9 |  |  | 440 | 10 | 9 | AHU | 8 | 3520 | 2.5227 | 1 | 2.5227 | 1 | 2.5227 | 1
102 | Office | 44 | 2 |  |  | 180 | 4 | 2 | AHU | 8 | 1440 | 1.8333 | 1 | 1.8333 | 1 | 1.8333 | 1
103 | Classroom | 70 | 4 |  |  | 308 | 7 | 4 | AHU | 8 | 2464 | 1.7045 | 1 | 1.7045 | 1 | 1.7045 | 1
103B | Office | 53 | 3 |  |  | 418 | 9 | 3 | AHU | 8 | 3344 | 0.95096 | 1 | 0.95096 | 0 | 0.95096 | 0
104 | Vestible | 25 | 1 |  |  | 220 | 5 | 1 | Unit Ventilator | 8 | 1760 | 0.85227 | 1 | 0.85227 | 0 | 0.85227 | 0
104A | Office | 36 | 2 |  |  | 102 | 2 | 2 | AHU | 8 | 816 | 2.6471 | 1 | 2.6471 | 1 | 2.6471 | 1
104B | Security Office | 56 | 3 |  |  | 123 | 2 | 2 | AHU | 8 | 984 | 3.4146 | 1 | 3.4146 | 1 | 3.4146 | 1
104C | Office | 27 | 1 |  |  | 99 | 2 | 1 | AHU | 8 | 792 | 2.0455 | 1 | 2.0455 | 1 | 2.0455 | 1
106 | Classroom | 328 | 21 | Yes | 20 | 1540 | 35 | 35 | Unit Ventilator | 8 | 12320 | 1.5974 | 1 | 1.5974 | 1 | 21.5974 | 3
107 | Classroom | 35 | 2 | Yes | 20 | 440 | 10 | 10 | AHU | 8 | 3520 | 0.59659 | 1 | 0.59659 | 0 | 20.5966 | 3
107A | Office | 74 | 4 |  |  | 840 | 19 | 4 | AHU | 8 | 6720 | 0.66071 | 1 | 0.66071 | 0 | 0.66071 | 0
107B | Storage | 17 | 1 |  |  | 196 | 4 | 1 | AHU | 8 | 1568 | 0.65051 | 1 | 0.65051 | 0 | 0.65051 | 0
108 | Classroom | 296 | 19 | Yes | 20 | 1540 | 35 | 35 | Unit Ventilator | 8 | 12320 | 1.4416 | 1 | 1.4416 | 1 | 21.4416 | 3
109 | Classroom | 275 | 18 |  |  | 440 | 10 | 10 | AHU | 8 | 3520 | 4.6875 | 1 | 4.6875 | 2 | 4.6875 | 2
110 | Classroom | 322 | 21 | Yes | 20 | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 2.2869 | 1 | 2.2869 | 1 | 22.2869 | 3
112 | Classroom | 312 | 20 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 2.799 | 1 | 2.799 | 1 | 2.799 | 1
114 | Classroom | 276 | 18 |  |  | 1012 | 23 | 18 | Unit Ventilator | 8 | 8096 | 2.0455 | 1 | 2.0455 | 1 | 2.0455 | 1
116 | Classroom | 279 | 18 | Yes | 20 | 968 | 22 | 22 | Unit Ventilator | 8 | 7744 | 2.1617 | 1 | 2.1617 | 1 | 22.1617 | 3
127 | Kitchen | 169 | 11 |  |  | 972 | 22 | 11 | AHU | 8 | 7776 | 1.304 | 1 | 1.304 | 1 | 1.304 | 1
200 | Classroom | 296 | 19 |  |  | 264 | 6 | 6 | Unit Ventilator | 8 | 2112 | 8.4091 | 1 | 8.4091 | 2 | 8.4091 | 2
202 | Classroom | 276 | 18 |  |  | 704 | 16 | 16 | Unit Ventilator | 8 | 5632 | 2.9403 | 1 | 2.9403 | 1 | 2.9403 | 1
204 | Classroom | 316 | 21 |  |  | 396 | 9 | 9 | Unit Ventilator | 8 | 3168 | 5.9848 | 1 | 5.9848 | 2 | 5.9848 | 2
206 | Classroom | 317 | 21 |  |  | 704 | 16 | 16 | Unit Ventilator | 8 | 5632 | 3.3771 | 1 | 3.3771 | 1 | 3.3771 | 1
208 | Classroom | 281 | 18 |  |  | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 2.8175 | 1 | 2.8175 | 1 | 2.8175 | 1
210 | Classroom | 318 | 21 |  |  | 528 | 12 | 12 | Unit Ventilator | 8 | 4224 | 4.517 | 1 | 4.517 | 2 | 4.517 | 2
212 | Classroom | 329 | 21 |  |  | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 3.2988 | 1 | 3.2988 | 1 | 3.2988 | 1
214 | Classroom | 318 | 21 |  |  | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 3.1885 | 1 | 3.1885 | 1 | 3.1885 | 1
216 | Classroom | 270 | 18 |  |  | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 2.7072 | 1 | 2.7072 | 1 | 2.7072 | 1
218 | Classroom | 291 | 19 |  |  | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 2.9178 | 1 | 2.9178 | 1 | 2.9178 | 1
220 | Classroom | 424 | 28 |  |  | 748 | 17 | 17 | AHU | 8 | 5984 | 4.2513 | 1 | 4.2513 | 2 | 4.2513 | 2
222 | Classroom | 289 | 19 |  |  | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 2.8977 | 1 | 2.8977 | 1 | 2.8977 | 1
224 | Classroom | 284 | 18 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 2.6894 | 1 | 2.6894 | 1 | 2.6894 | 1
228 | Room | 55 | 3 | Yes | 20 | 264 | 6 | 6 | Unit Ventilator | 8 | 2112 | 1.5625 | 1 | 1.5625 | 1 | 21.5625 | 3
232 | Classroom | 285 | 19 |  |  | 264 | 6 | 6 | Unit Ventilator | 8 | 2112 | 8.0966 | 1 | 8.0966 | 2 | 8.0966 | 2
300 | Lounge | 347 | 23 |  |  | 264 | 6 | 6 | Unit Ventilator | 8 | 2112 | 9.858 | 1 | 9.858 | 2 | 9.858 | 2
301 | Classroom | 175 | 11 | Yes | 20 | 1568 | 35 | 35 | AHU | 8 | 12544 | 0.83705 | 1 | 0.83705 | 0 | 20.8371 | 3
302 | Classroom | 291 | 19 |  |  | 704 | 16 | 16 | Unit Ventilator | 8 | 5632 | 3.1001 | 1 | 3.1001 | 1 | 3.1001 | 1
304 | Classroom | 284 | 18 |  |  | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 2.8476 | 1 | 2.8476 | 1 | 2.8476 | 1
306 | Classroom | 327 | 21 |  |  | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 3.2787 | 1 | 3.2787 | 1 | 3.2787 | 1
308 | Classroom | 321 | 21 |  |  | 704 | 16 | 16 | Unit Ventilator | 8 | 5632 | 3.4197 | 1 | 3.4197 | 1 | 3.4197 | 1
310 | Room | 0 | 0 | Yes | 20 | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 0 | 1 | 0 | 0 | 20 | 3
312 | Classroom | 289 | 19 |  |  | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 2.8977 | 1 | 2.8977 | 1 | 2.8977 | 1
314 | Room | 53 | 3 | Yes | 20 | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 0.50189 | 1 | 0.50189 | 0 | 20.5019 | 3
316 | Classroom | 290 | 19 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 2.7462 | 1 | 2.7462 | 1 | 2.7462 | 1
318 | Room | 0 | 0 | Yes | 20 | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 0 | 1 | 0 | 0 | 20 | 3
320 | Classroom | 303 | 20 |  |  | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 3.0381 | 1 | 3.0381 | 1 | 3.0381 | 1
322 | Room | 249 | 16 |  |  | 748 | 17 | 16 | Unit Ventilator | 8 | 5984 | 2.4967 | 1 | 2.4967 | 1 | 2.4967 | 1
324 | Classroom | 302 | 20 |  |  | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 3.0281 | 1 | 3.0281 | 1 | 3.0281 | 1
328 | Classroom | 298 | 19 |  |  | 264 | 6 | 6 | Unit Ventilator | 8 | 2112 | 8.4659 | 1 | 8.4659 | 2 | 8.4659 | 2
- | Copy Room | 38 | 2 |  |  | 44 | 1 | 1 | Unit Ventilator | 8 | 352 | 6.4773 | 1 | 6.4773 | 2 | 6.4773 | 2
- | Main office | 78 | 5 | Yes | 20 | 484 | 11 | 11 | Unit Ventilator | 8 | 3872 | 1.2087 | 1 | 1.2087 | 1 | 21.2087 | 3
- | Nurse | 30 | 2 |  |  | 176 | 4 | 2 | Unit Ventilator | 8 | 1408 | 1.2784 | 1 | 1.2784 | 1 | 1.2784 | 1
- | Nurse Examination | 76 | 5 |  |  | 88 | 2 | 2 | Unit Ventilator | 8 | 704 | 6.4773 | 1 | 6.4773 | 2 | 6.4773 | 2
- | Principal | 43 | 2 |  |  | 176 | 4 | 2 | Unit Ventilator | 8 | 1408 | 1.8324 | 1 | 1.8324 | 1 | 1.8324 | 1
- | Cafeteria/Aud | 4461 | 297 |  |  | 4268 | 97 | 97 | AHU | 8 | 34144 | 7.8392 | 1.062 | 8.3255 | 2 | 8.3255 | 2
- | Gym | 2645 | 176 |  |  | 4620 | 105 | 105 | AHU | 8 | 36960 | 4.2938 | 1.062 | 4.5602 | 2 | 4.5602 | 2
- | IMC | 1002 | 66 |  |  | 2948 | 67 | 66 | AHU | 8 | 23584 | 2.5492 | 1.062 | 2.7073 | 1 | 2.7073 | 1
- | IMC/Classrooms | 58 | 3 |  |  | 176 | 4 | 3 | AHU | 8 | 1408 | 2.4716 | 1 | 2.4716 | 1 | 2.4716 | 1
- | Teachers Lounge | 52 | 3 | Yes | 20 | 296 | 6 | 6 | AHU | 8 | 2368 | 1.3176 | 1 | 1.3176 | 1 | 21.3176 | 3
- | Dean's Office | 31 | 2 |  |  | 117 | 2 | 2 | AHU | 8 | 936 | 1.9872 | 1 | 1.9872 | 1 | 1.9872 | 1
Sheet Last Modified: | 2021-04-23
School: | Hill-Freedman World Academy at Leeds Campus
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Room |  | 0 |  |  | 775 | 17 | 0 |  | 8 | 6200 | 0 | 1 | 0 | 0 | 0 | 0
2 | Room |  | 0 |  |  | 1008 | 22 | 0 |  | 8 | 8064 | 0 | 1 | 0 | 0 | 0 | 0
3 | Room | 0 | 0 |  |  | 832 | 18 | 0 |  | 8 | 6656 | 0 | 1 | 0 | 0 | 0 | 0
4 | Room |  | 0 |  |  | 784 | 17 | 0 |  | 8 | 6272 | 0 | 1 | 0 | 0 | 0 | 0
5 | Office |  | 0 |  |  | 240 | 5 | 0 |  | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
5 | Room |  | 0 |  |  | 1300 | 29 | 0 |  | 8 | 10400 | 0 | 1 | 0 | 0 | 0 | 0
6 | Office |  | 0 |  |  | 64 | 1 | 0 |  | 8 | 512 | 0 | 1 | 0 | 0 | 0 | 0
6 | Room | 0 | 0 |  |  | 300 | 6 | 0 |  | 8 | 2400 | 0 | 1 | 0 | 0 | 0 | 0
7 | Room | 0 | 0 |  |  | 672 | 15 | 0 |  | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
8 | Room |  | 0 |  |  | 500 | 11 | 0 |  | 8 | 4000 | 0 | 1 | 0 | 0 | 0 | 0
9 | Room |  | 0 |  |  | 1300 | 29 | 0 |  | 8 | 10400 | 0 | 1 | 0 | 0 | 0 | 0
10 | Room |  | 0 |  |  | 840 | 19 | 0 |  | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
119 | Classroom |  | 0 | Yes | 20 | 504 | 11 | 11 |  | 8 | 4032 | 0 | 1 | 0 | 0 | 20 | 3
121 | Classroom |  | 0 | Yes | 20 | 525 | 11 | 11 |  | 8 | 4200 | 0 | 1 | 0 | 0 | 20 | 3
124 | Classroom |  | 0 | Yes | 20 | 616 | 14 | 14 |  | 8 | 4928 | 0 | 1 | 0 | 0 | 20 | 3
131 | Classroom |  | 0 | Yes | 20 | 735 | 16 | 16 |  | 8 | 5880 | 0 | 1 | 0 | 0 | 20 | 3
134 | Classroom |  | 0 | Yes | 20 | 1224 | 27 | 27 |  | 8 | 9792 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium |  | 0 |  |  | 8760 | 199 | 0 |  | 8 | 70080 | 0 | 1.4912 | 0 | 0 | 0 | 0
Main Office | Office |  | 0 |  |  | 588 | 13 | 0 |  | 8 | 4704 | 0 | 1 | 0 | 0 | 0 | 0
Principal | Office |  | 0 |  |  | 154 | 3 | 0 |  | 8 | 1232 | 0 | 1 | 0 | 0 | 0 | 0
Nurse | Office Suite |  | 0 | Yes | 20 | 892 | 20 | 20 |  | 8 | 7136 | 0 | 1 | 0 | 0 | 20 | 3
- | Boys Gym | 1074 | 71 |  |  | 5760 | 130 | 71 |  | 8 | 46080 | 1.3984 | 1.062 | 1.4852 | 1 | 1.4852 | 1
- | Boys Locker Room |  | 0 |  |  | 3420 | 77 | 0 |  | 8 | 27360 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria |  | 0 |  |  | 11360 | 258 | 0 |  | 8 | 90880 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | Conference Room |  | 0 |  |  | 390 | 8 | 0 |  | 8 | 3120 | 0 | 1 | 0 | 0 | 0 | 0
- | Girls Gym |  | 0 |  |  | 5760 | 130 | 0 |  | 8 | 46080 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Girls Locker Room |  | 0 |  |  | 3420 | 77 | 0 |  | 8 | 27360 | 0 | 1.062 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-28
School: | Thomas Holme Elementary School
Vendor: | Devine Brothers | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 619 | 41 |  |  | 989 | 22 | 22 | Unit Ventilator | 8 | 7912 | 4.6941 | 1 | 4.6941 | 2 | 4.6941 | 2
2 | Classroom | 524 | 34 |  |  | 989 | 22 | 22 | Unit Ventilator | 8 | 7912 | 3.9737 | 1 | 3.9737 | 1 | 3.9737 | 1
3 | Classroom | 285 | 19 |  |  | 920 | 20 | 19 | Unit Ventilator | 8 | 7360 | 2.3234 | 1 | 2.3234 | 1 | 2.3234 | 1
4 | Classroom | 576 | 38 |  |  | 1058 | 24 | 24 | Unit Ventilator | 8 | 8464 | 4.0832 | 1 | 4.0832 | 2 | 4.0832 | 2
5 | Classroom | 550 | 36 |  |  | 1058 | 24 | 24 | Unit Ventilator | 8 | 8464 | 3.8989 | 1 | 3.8989 | 1 | 3.8989 | 1
61 | Classroom | 214 | 14 | Yes | 20 | 1040 | 23 | 23 | Unit Ventilator | 8 | 8320 | 1.5433 | 1 | 1.5433 | 1 | 21.5433 | 3
62 | Truancy Court | 207 | 13 | Yes | 20 | 520 | 11 | 11 | Unit Ventilator | 8 | 4160 | 2.9856 | 1 | 2.9856 | 1 | 22.9856 | 3
63 | Classroom | 312 | 20 | Yes | 20 | 1040 | 23 | 23 | Unit Ventilator | 8 | 8320 | 2.25 | 1 | 2.25 | 1 | 22.25 | 3
64 | Classroom | 527 | 35 |  |  | 1040 | 23 | 23 | Unit Ventilator | 8 | 8320 | 3.8005 | 1 | 3.8005 | 1 | 3.8005 | 1
65 | Classroom | 300 | 20 | Yes | 20 | 1040 | 23 | 23 | Unit Ventilator | 8 | 8320 | 2.1635 | 1 | 2.1635 | 1 | 22.1635 | 3
66 | Classroom | 423 | 28 |  |  | 1040 | 23 | 23 | Unit Ventilator | 8 | 8320 | 3.0505 | 1 | 3.0505 | 1 | 3.0505 | 1
101 | Classroom | 679 | 45 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 5.5353 | 1 | 5.5353 | 2 | 5.5353 | 2
102 | Classroom | 626 | 41 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 5.1033 | 1 | 5.1033 | 2 | 5.1033 | 2
103 | Classroom | 500 | 33 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 4.0761 | 1 | 4.0761 | 2 | 4.0761 | 2
104 | Classroom | 615 | 41 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 5.0136 | 1 | 5.0136 | 2 | 5.0136 | 2
105 | Classroom | 628 | 41 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 5.1196 | 1 | 5.1196 | 2 | 5.1196 | 2
106 | Classroom | 697 | 46 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 7.5761 | 1 | 7.5761 | 2 | 7.5761 | 2
107 | Classroom | 321 | 21 |  |  | 960 | 21 | 21 | Unit Ventilator | 8 | 7680 | 2.5078 | 1 | 2.5078 | 1 | 2.5078 | 1
108 | Classroom |  | 0 | Yes | 20 | 108 | 2 | 2 |  | 8 | 864 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 503 | 33 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 4.1005 | 1 | 4.1005 | 2 | 4.1005 | 2
110 | Classroom | 483 | 32 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 3.9375 | 1 | 3.9375 | 1 | 3.9375 | 1
111 | Classroom | 553 | 36 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 4.5082 | 1 | 4.5082 | 2 | 4.5082 | 2
112 | Classroom | 568 | 37 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 4.6304 | 1 | 4.6304 | 2 | 4.6304 | 2
113 | Classroom | 622 | 41 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 5.0707 | 1 | 5.0707 | 2 | 5.0707 | 2
201 | Classroom | 649 | 43 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 5.2908 | 1 | 5.2908 | 2 | 5.2908 | 2
202 | Classroom | 320 | 21 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 2.6087 | 1 | 2.6087 | 1 | 2.6087 | 1
203 | Classroom | 261 | 17 |  |  | 920 | 20 | 17 | Unit Ventilator | 8 | 7360 | 2.1277 | 1 | 2.1277 | 1 | 2.1277 | 1
204 | Classroom | 469 | 31 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 3.8234 | 1 | 3.8234 | 1 | 3.8234 | 1
205 | Classroom | 658 | 43 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 5.3641 | 1 | 5.3641 | 2 | 5.3641 | 2
206 | Classroom | 624 | 41 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 5.087 | 1 | 5.087 | 2 | 5.087 | 2
207 | Classroom | 607 | 40 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 4.9484 | 1 | 4.9484 | 2 | 4.9484 | 2
208 | Classroom | 626 | 41 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 5.1033 | 1 | 5.1033 | 2 | 5.1033 | 2
209 | Classroom | 764 | 50 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 6.2283 | 1 | 6.2283 | 2 | 6.2283 | 2
210 | Classroom | 589 | 39 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 4.8016 | 1 | 4.8016 | 2 | 4.8016 | 2
211 | Classroom | 279 | 18 |  |  | 920 | 20 | 18 | Unit Ventilator | 8 | 7360 | 2.2745 | 1 | 2.2745 | 1 | 2.2745 | 1
212 | Classroom | 597 | 39 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 4.8668 | 1 | 4.8668 | 2 | 4.8668 | 2
213 | Classroom | 664 | 44 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 5.413 | 1 | 5.413 | 2 | 5.413 | 2
214 | Classroom | 681 | 45 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 5.5516 | 1 | 5.5516 | 2 | 5.5516 | 2
215 | Classroom |  | 0 | Yes | 20 | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 0 | 1 | 0 | 0 | 20 | 3
216 | Classroom |  | 0 | Yes | 20 | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 0 | 0 |  |  | 2880 | 65 | 0 | AHU | 8 | 23040 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria | 127 | 8 |  |  | 2250 | 51 | 8 | Unit Ventilator | 8 | 18000 | 0.42333 | 1 | 0.42333 | 0 | 0.42333 | 0
- | Kitchen |  | 0 | Yes | 20 | 475 | 10 | 10 |  | 8 | 3800 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 231 | 5 | 5 | Purifier | 8 | 1848 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 150 | 3 | 3 |  | 8 | 1200 | 0 | 1 | 0 | 0 | 20 | 3
- | Vice Principal Office |  | 0 | Yes | 20 | 84 | 1 | 1 |  | 8 | 672 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 204 | 4 | 4 |  | 8 | 1632 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office |  | 0 | Yes | 20 | 135 | 3 | 3 |  | 8 | 1080 | 0 | 1 | 0 | 0 | 20 | 3
- | Admin Office |  | 0 | Yes | 20 | 156 | 3 | 3 |  | 8 | 1248 | 0 | 1 | 0 | 0 | 20 | 3
- | Dean Office |  | 0 | Yes | 20 | 140 | 3 | 3 |  | 8 | 1120 | 0 | 1 | 0 | 0 | 20 | 3
- | School Police Office |  | 0 | Yes | 20 | 99 | 2 | 2 |  | 8 | 792 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym | 189 | 12 | Yes | 20 | 3950 | 89 | 89 | Unit Ventilator | 8 | 31600 | 0.35886 | 1.062 | 0.38112 | 0 | 20.3811 | 3
- | Music | 0 | 0 |  |  | 2340 | 53 | 0 | AHU | 8 | 18720 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23
School: | Francis Hopkinson Elementary School
Vendor: | Devine Brothers | Main Building Retest
School: | Francis Hopkinson Elementary School- Little School House
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
101 | Classrooms | 1030 | 68 |  |  | 687 | 15 | 15 | House Fan | 8 | 5496 | 11.2445 | 1 | 11.2445 | 3 | 11.2445 | 3
102 | Classrooms | 873 | 58 |  |  | 627 | 14 | 14 | House Fan | 8 | 5016 | 10.4426 | 1 | 10.4426 | 3 | 10.4426 | 3
103 | Classrooms | 276 | 18 |  |  | 696 | 15 | 15 | House Fan | 8 | 5568 | 2.9741 | 1 | 2.9741 | 1 | 2.9741 | 1
104 | Classrooms | 1044 | 69 |  |  | 643 | 14 | 14 | House Fan | 8 | 5144 | 12.1773 | 1 | 12.1773 | 3 | 12.1773 | 3
105 | Classrooms | 562 | 37 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 6.6066 | 1 | 6.6066 | 2 | 6.6066 | 2
106 | Classroom | 953 | 63 |  |  | 648 | 14 | 14 | House Fan | 8 | 5184 | 11.0301 | 1 | 11.0301 | 3 | 11.0301 | 3
107 | Classroom | 1035 | 69 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 12.1669 | 1 | 12.1669 | 3 | 12.1669 | 3
108 | Classrooms | 432 | 28 |  |  | 675 | 15 | 15 | House Fan | 8 | 5400 | 4.8 | 1 | 4.8 | 2 | 4.8 | 2
109 | Classrooms | 635 | 42 |  |  | 631 | 14 | 14 | House Fan | 8 | 5048 | 7.5475 | 1 | 7.5475 | 2 | 7.5475 | 2
110 | Classroom | 322 | 21 |  |  | 695 | 15 | 15 | House Fan | 8 | 5560 | 3.4748 | 1 | 3.4748 | 1 | 3.4748 | 1
201 | Classrooms | 707 | 47 |  |  | 696 | 15 | 15 | House Fan | 8 | 5568 | 7.6185 | 1 | 7.6185 | 2 | 7.6185 | 2
202 | Classroom | 767 | 51 |  |  | 656 | 14 | 14 | House Fan | 8 | 5248 | 8.7691 | 1 | 8.7691 | 2 | 8.7691 | 2
203 | Classrooms | 734 | 48 |  |  | 693 | 15 | 15 | House Fan | 8 | 5544 | 7.9437 | 1 | 7.9437 | 2 | 7.9437 | 2
204 | Classrooms | 787 | 52 |  |  | 647 | 14 | 14 | House Fan | 8 | 5176 | 9.1229 | 1 | 9.1229 | 2 | 9.1229 | 2
205 | Classroom | 737 | 49 |  |  | 674 | 15 | 15 | House Fan | 8 | 5392 | 8.201 | 1 | 8.201 | 2 | 8.201 | 2
206 | Classroom | 792 | 52 |  |  | 657 | 14 | 14 | House Fan | 8 | 5256 | 9.0411 | 1 | 9.0411 | 2 | 9.0411 | 2
207 | Classrooms | 618 | 41 |  |  | 679 | 15 | 15 | House Fan | 8 | 5432 | 6.8262 | 1 | 6.8262 | 2 | 6.8262 | 2
208 | Classroom | 702 | 46 |  |  | 686 | 15 | 15 | House Fan | 8 | 5488 | 7.6749 | 1 | 7.6749 | 2 | 7.6749 | 2
209 | Classroom | 892 | 59 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 10.03 | 1 | 10.03 | 3 | 10.03 | 3
210 | Classroom | 386 | 25 |  |  | 687 | 15 | 15 | House Fan | 8 | 5496 | 4.214 | 1 | 4.214 | 2 | 4.214 | 2
300 | Office |  | 0 | Yes | 20 | 275 | 6 | 6 | House Fan | 8 | 2200 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classrooms | 425 | 28 |  |  | 677 | 15 | 15 | House Fan | 8 | 5416 | 4.7083 | 1 | 4.7083 | 2 | 4.7083 | 2
302 | Classroom | 0 | 0 | Yes | 20 | 668 | 15 | 15 | House Fan | 8 | 5344 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classrooms | 263 | 17 |  |  | 694 | 15 | 15 | House Fan | 8 | 5552 | 2.8422 | 1 | 2.8422 | 1 | 2.8422 | 1
304 | Classrooms | 612 | 40 |  |  | 614 | 13 | 13 | House Fan | 8 | 4912 | 7.4756 | 1 | 7.4756 | 2 | 7.4756 | 2
305 | Classroom | 437 | 29 |  |  | 672 | 15 | 15 | House Fan | 8 | 5376 | 4.8772 | 1 | 4.8772 | 2 | 4.8772 | 2
306 | Classroom | 497 | 33 |  |  | 696 | 15 | 15 | House Fan | 8 | 5568 | 5.3556 | 1 | 5.3556 | 2 | 5.3556 | 2
307 | Classrooms | 1017 | 67 |  |  | 661 | 15 | 15 | House Fan | 8 | 5288 | 11.5393 | 1 | 11.5393 | 3 | 11.5393 | 3
308 | Classroom | 604 | 40 |  |  | 664 | 15 | 15 | House Fan | 8 | 5312 | 6.8223 | 1 | 6.8223 | 2 | 6.8223 | 2
309 | Classroom | 702 | 46 |  |  | 673 | 15 | 15 | House Fan | 8 | 5384 | 7.8232 | 1 | 7.8232 | 2 | 7.8232 | 2
310 | Classroom | 321 | 21 |  |  | 668 | 15 | 15 | House Fan | 8 | 5344 | 3.604 | 1 | 3.604 | 1 | 3.604 | 1
311 | Classrooms | 393 | 26 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 4.6199 | 1 | 4.6199 | 2 | 4.6199 | 2
- | Auditorium | 1307 | 87 |  |  | 3184 | 72 | 72 | House Fan | 8 | 25472 | 3.0787 | 1.062 | 3.2697 | 1 | 3.2697 | 1
- | B Art Room | 242 | 16 |  |  | 570 | 12 | 12 | House Fan | 8 | 4560 | 3.1842 | 1 | 3.1842 | 1 | 3.1842 | 1
- | B Café / Gym | 0 | 0 | Yes | 20 | 3572 | 81 | 81 | N/A | 8 | 28576 | 0 | 1.062 | 0 | 0 | 20 | 3
- | B ESOL Room | 269 | 17 |  |  | 683 | 15 | 15 | House Fan | 8 | 5464 | 2.9539 | 1 | 2.9539 | 1 | 2.9539 | 1
- | B Music Room | 603 | 40 |  |  | 688 | 15 | 15 | House Fan | 8 | 5504 | 6.5734 | 1 | 6.5734 | 2 | 6.5734 | 2
- | B Science Room | 864 | 57 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 9.2045 | 1 | 9.2045 | 2 | 9.2045 | 2
- | Main Office |  | 0 | Yes | 20 | 345 | 7 | 7 |  | 8 | 2760 | 0 | 1 | 0 | 0 | 20 | 3
- | Vice Principal's Office |  | 0 | Yes | 20 | 126 | 2 | 2 |  | 8 | 1008 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 275 | 6 | 6 |  | 8 | 2200 | 0 | 1 | 0 | 0 | 20 | 3
P1 | Classroom | 198 | 13 | Yes | 20 | 1184 | 26 | 26 | Unit Ventilator | 8 | 9472 | 1.2542 | 1 | 1.2542 | 1 | 21.2542 | 3
P2 | Classroom | 348 | 23 |  |  | 747 | 16 | 16 | Unit Ventilator | 8 | 5976 | 3.494 | 1 | 3.494 | 1 | 3.494 | 1
Hopkinson LSH
1 | Room | 308 | 20 |  |  | 877 | 19 | 19 | AHU | 8 | 7016 | 2.634 | 1 | 2.634 | 1 | 2.634 | 1
2 | Room | 323 | 21 |  |  | 900 | 20 | 20 | AHU | 8 | 7200 | 2.6917 | 1 | 2.6917 | 1 | 2.6917 | 1
3 | Room | 318 | 21 |  |  | 885 | 20 | 20 | AHU | 8 | 7080 | 2.6949 | 1 | 2.6949 | 1 | 2.6949 | 1
4 | Room | 349 | 23 |  |  | 908 | 20 | 20 | AHU | 8 | 7264 | 2.8827 | 1 | 2.8827 | 1 | 2.8827 | 1
5 | Room | 308 | 20 |  |  | 863 | 19 | 19 | AHU | 8 | 6904 | 2.6767 | 1 | 2.6767 | 1 | 2.6767 | 1
6 | Room | 256 | 17 | Yes | 20 | 876 | 19 | 19 | AHU | 8 | 7008 | 2.1918 | 1 | 2.1918 | 1 | 22.1918 | 3
- | Corridor and Bathrooms | 46 | 3 |  |  |  | 0 | 0 | AHU
- | Multi-Purpose Room | 626 | 41 |  |  | 2003 | 45 | 41 | AHU | 8 | 16024 | 2.344 | 1 | 2.344 | 1 | 2.344 | 1
- | Office Area | 204 | 13 |  |  | 352 | 8 | 8 | AHU | 8 | 2816 | 4.3466 | 1 | 4.3466 | 2 | 4.3466 | 2
Sheet Last Modified: | 2021-04-01
School: | Henry H. Houston Elementary School
Vendor: | EMCOR | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 | Yes | 20 | 784 | 17 | 17 | House Fan | 8 | 6272 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 651 | 14 | 14 | House Fan | 8 | 5208 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 664 | 15 | 15 | House Fan | 8 | 5312 | 0 | 1 | 0 | 0 | 20 | 3
103A | Classroom |  | 0 |  |  | 157 | 3 | 0 | House Fan | 8 | 1256 | 0 | 1 | 0 | 0 | 0 | 0
104 | Classroom |  | 0 | Yes | 20 | 675 | 15 | 15 | House Fan | 8 | 5400 | 0 | 1 | 0 | 0 | 20 | 3
105 | Office/Principal |  | 0 |  |  | 354 | 8 | 0 | House Fan | 8 | 2832 | 0 | 1 | 0 | 0 | 0 | 0
106 | Classroom |  | 0 | Yes | 20 | 651 | 14 | 14 | House Fan | 8 | 5208 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 | Yes | 20 | 459 | 10 | 10 | House Fan | 8 | 3672 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom |  | 0 | Yes | 20 | 681 | 15 | 15 | House Fan | 8 | 5448 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom |  | 0 | Yes | 20 | 950 | 21 | 21 | House Fan | 8 | 7600 | 0 | 1 | 0 | 0 | 20 | 3
111 | Classroom | 276 | 18 |  |  | 375 | 8 | 8 | House Fan and Univent | 8 | 3000 | 5.52 | 1 | 5.52 | 2 | 5.52 | 2
112 | Classroom | 350 | 23 |  |  | 312 | 7 | 7 | House Fan and Univent | 8 | 2496 | 8.4135 | 1 | 8.4135 | 2 | 8.4135 | 2
201 | Classroom |  | 0 |  |  | 561 | 12 | 0 | House Fan | 8 | 4488 | 0 | 1 | 0 | 0 | 0 | 0
202 | Classroom |  | 0 |  |  | 701 | 15 | 0 | House Fan | 8 | 5608 | 0 | 1 | 0 | 0 | 0 | 0
203 | Classroom |  | 0 |  |  | 207 | 4 | 0 | House Fan | 8 | 1656 | 0 | 1 | 0 | 0 | 0 | 0
204 | Classroom |  | 0 |  |  | 710 | 16 | 0 | House Fan | 8 | 5680 | 0 | 1 | 0 | 0 | 0 | 0
205 | Classroom |  | 0 |  |  | 653 | 14 | 0 | House Fan | 8 | 5224 | 0 | 1 | 0 | 0 | 0 | 0
206 | Classroom |  | 0 |  |  | 660 | 15 | 0 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom |  | 0 |  |  | 769 | 17 | 0 | House Fan | 8 | 6152 | 0 | 1 | 0 | 0 | 0 | 0
208 | Classroom |  | 0 |  |  | 750 | 17 | 0 | House Fan | 8 | 6000 | 0 | 1 | 0 | 0 | 0 | 0
209 | Classroom |  | 0 |  |  | 693 | 15 | 0 | House Fan | 8 | 5544 | 0 | 1 | 0 | 0 | 0 | 0
210 | Classroom |  | 0 |  |  | 437 | 9 | 0 | N/A | 8 | 3496 | 0 | 1 | 0 | 0 | 0 | 0
211 | Classroom | 329 | 21 |  |  | 795 | 18 | 18 | Unit Ventilator | 8 | 6360 | 3.1038 | 1 | 3.1038 | 1 | 3.1038 | 1
212 | Classroom | 309 | 20 |  |  | 396 | 9 | 9 | Unit Ventilator | 8 | 3168 | 5.8523 | 1 | 5.8523 | 2 | 5.8523 | 2
213 | Classroom | 274 | 18 |  |  |  | 0 | 0 | Unit Ventilator
301 | Classroom |  | 0 |  |  | 667 | 15 | 0 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom |  | 0 | Yes | 20 | 661 | 15 | 15 | House Fan | 8 | 5288 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom |  | 0 |  |  | 664 | 15 | 0 | House Fan | 8 | 5312 | 0 | 1 | 0 | 0 | 0 | 0
304 | Classroom |  | 0 |  |  | 729 | 16 | 0 | House Fan | 8 | 5832 | 0 | 1 | 0 | 0 | 0 | 0
305 | Classroom |  | 0 |  |  | 674 | 15 | 0 | House Fan | 8 | 5392 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom |  | 0 |  |  | 670 | 15 | 0 | House Fan | 8 | 5360 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom |  | 0 |  |  | 758 | 17 | 0 | House Fan | 8 | 6064 | 0 | 1 | 0 | 0 | 0 | 0
308 | Classroom |  | 0 |  |  | 716 | 16 | 0 | House Fan | 8 | 5728 | 0 | 1 | 0 | 0 | 0 | 0
309 | Classroom |  | 0 |  |  | 613 | 13 | 0 | House Fan | 8 | 4904 | 0 | 1 | 0 | 0 | 0 | 0
309A | Small Office |  | 0 |  |  | 201 | 4 | 0 | House Fan | 8 | 1608 | 0 | 1 | 0 | 0 | 0 | 0
- | Kitchen | 0 | 0 |  |  | 638 | 14 | 0 | N/A | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium | 1853 | 123 |  |  | 1500 | 34 | 34 | AHU 1 and 2 | 8 | 12000 | 9.265 | 1 | 9.265 | 2 | 9.265 | 2
- | Library | 0 | 0 |  |  | 1404 | 31 | 0 | RTU | 8 | 11232 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym |  | 0 | Yes | 20 | 2232 | 50 | 50 | N/A | 8 | 17856 | 0 | 1 | 0 | 0 | 20 | 3
- | Old Art Room |  | 0 |  |  | 631 | 14 | 0 | N/A | 8 | 5048 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 |  |  | 4500 | 102 | 0 | Nesbitt Unit Ventilator | 8 | 36000 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Old School Store A | 230 | 15 |  |  | 863 | 19 | 15 | Nesbitt Unit Ventilator | 8 | 6904 | 1.9988 | 1 | 1.9988 | 1 | 1.9988 | 1
- | Old School Store B | 345 | 23 |  |  | 311 | 7 | 7 | Nesbitt Unit Ventilator | 8 | 2488 | 8.3199 | 1 | 8.3199 | 2 | 8.3199 | 2
- | New School Store | 347 | 23 |  |  | 291 | 6 | 6 | Nesbitt Unit Ventilator | 8 | 2328 | 8.9433 | 1 | 8.9433 | 2 | 8.9433 | 2
- | Medical Suite Large |  | 0 |  |  | 242 | 5 |  |  | 8 | 1936 | 0 | 1 | 0 | 0 | 0 | 0
- | Medical Suite Small |  | 0 |  |  | 126 | 2 |  |  | 8 | 1008 | 0 | 1 | 0 | 0 | 0 | 0
- | Medical Suite Medium |  | 0 |  |  | 238 | 5 | 0 | House Fan | 8 | 1904 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-21
School: | Julia Ward Howe Academics Plus Elementary School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B-1 | Art | 751 | 50 |  |  | 754 | 17 | 17 | House Fan | 8 | 6032 | 7.4702 | 1 | 7.4702 | 2 | 7.4702 | 2
1 | Classroom | 1269 | 84 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 13.7935 | 1 | 13.7935 | 3 | 13.7935 | 3
2 | Classroom | 1240 | 82 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 13.4783 | 1 | 13.4783 | 3 | 13.4783 | 3
3 | Classroom | 344 | 22 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 3.7391 | 1 | 3.7391 | 1 | 3.7391 | 1
4 | Classroom | 455 | 30 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 4.9457 | 1 | 4.9457 | 2 | 4.9457 | 2
5 | Classroom | 1500 | 100 |  |  | 196 | 4 | 4 | House Fan | 8 | 1568 | 57.398 | 1 | 57.398 | 5 | 57.398 | 5
6 | Classroom | 479 | 31 |  |  | 713 | 16 | 16 | House Fan | 8 | 5704 | 5.0386 | 1 | 5.0386 | 2 | 5.0386 | 2
7 | Classroom | 1470 | 98 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 15.9783 | 1 | 15.9783 | 3 | 15.9783 | 3
8 | Classroom | 1454 | 96 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 15.8043 | 1 | 15.8043 | 3 | 15.8043 | 3
9 | Classroom | 564 | 37 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 5.875 | 1 | 5.875 | 2 | 5.875 | 2
10 | Classroom | 1739 | 115 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 18.9022 | 1 | 18.9022 | 3 | 18.9022 | 3
11 | Classroom | 628 | 41 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 6.8261 | 1 | 6.8261 | 2 | 6.8261 | 2
12 | Classroom | 829 | 55 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 8.6354 | 1 | 8.6354 | 2 | 8.6354 | 2
13 | Library | 0 | 0 |  |  | 720 | 16 | 0 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
14 | Classroom | 1302 | 86 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 14.1522 | 1 | 14.1522 | 3 | 14.1522 | 3
15 | Classroom | 1044 | 69 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 11.3478 | 1 | 11.3478 | 3 | 11.3478 | 3
16 | Computer Lab | 0 | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
17 | Classroom | 548 | 36 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 5.9565 | 1 | 5.9565 | 2 | 5.9565 | 2
18 | Classroom | 824 | 54 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 8.9565 | 1 | 8.9565 | 2 | 8.9565 | 2
19 | Classroom | 869 | 57 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 9.4457 | 1 | 9.4457 | 2 | 9.4457 | 2
20 | Classroom | 0 | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
21 | Classroom | 149 | 9 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 1.6196 | 1 | 1.6196 | 1 | 21.6196 | 3
22 | Classroom | 898 | 59 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 9.7609 | 1 | 9.7609 | 2 | 9.7609 | 2
23 | Classroom | 210 | 14 |  |  | 690 | 15 | 14 | House Fan | 8 | 5520 | 2.2826 | 1 | 2.2826 | 1 | 2.2826 | 1
23A | - |  | 0 | Yes | 20 | 91 | 2 | 2 | House Fan | 8 | 728 | 0 | 1 | 0 | 0 | 20 | 3
24 | Classroom | 0 | 0 |  |  | 350 | 7 | 0 | House Fan | 8 | 2800 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 | Yes | 20 | 1566 | 35 | 35 | House Fan | 8 | 12528 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 | Yes | 20 | 1060 | 24 | 24 | House Fan | 8 | 8480 | 0 | 1 | 0 | 0 | 20 | 3
- | Jugg Room |  | 0 |  |  | 195 | 4 | 0 | House Fan | 8 | 1560 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office |  | 0 |  |  | 238 | 5 | 0 | House Fan | 8 | 1904 | 0 | 1 | 0 | 0 | 0 | 0
- | Principals Office |  | 0 | Yes | 20 | 180 | 4 | 4 | House Fan | 8 | 1440 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselors Office |  | 0 |  |  | 162 | 3 | 0 | House Fan | 8 | 1296 | 0 | 1 | 0 | 0 | 0 | 0
- | Psychologists Office |  | 0 | Yes | 20 | 99 | 2 | 2 | House Fan | 8 | 792 | 0 | 1 | 0 | 0 | 20 | 3
- | Lounge |  | 0 |  |  | 266 | 6 | 0 | House Fan | 8 | 2128 | 0 | 1 | 0 | 0 | 0 | 0
- | Security |  | 0 | Yes | 20 | 91 | 2 | 2 | House Fan | 8 | 728 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-06
School: | New William H. Hunter Elementary School
Vendor: | Devine Brothers | Devine Retest
Devine 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Office | 40 | 2 |  |  | 149 | 3 | 2 | AHU-3 | 8 | 1192 | 2.0134 | 1 | 2.0134 | 1 | 2.0134 | 1
2 | Office | 33 | 2 |  |  | 143 | 3 | 2 | AHU-3 | 8 | 1144 | 1.7308 | 1 | 1.7308 | 1 | 1.7308 | 1
3 | Office | 24 | 1 |  |  | 72 | 1 | 1 | AHU-3 | 8 | 576 | 2.5 | 1 | 2.5 | 1 | 2.5 | 1
4 | Office | 48 | 3 |  |  | 92 | 2 | 2 | AHU-3 | 8 | 736 | 3.913 | 1 | 3.913 | 1 | 3.913 | 1
101A | Classroom | 363 | 24 |  |  | 695 | 15 | 15 | AHU-1 | 8 | 5560 | 3.9173 | 1 | 3.9173 | 1 | 3.9173 | 1
101B | Classroom | 378 | 25 |  |  | 695 | 15 | 15 | AHU-1 + UV | 8 | 5560 | 4.0791 | 1 | 4.0791 | 2 | 4.0791 | 2
101C | Classroom | 358 | 23 |  |  | 650 | 14 | 14 | AHU-1 | 8 | 5200 | 4.1308 | 1 | 4.1308 | 2 | 4.1308 | 2
101D | Classroom | 551 | 36 |  |  | 650 | 14 | 14 | AHU-1 + UV | 8 | 5200 | 6.3577 | 1 | 6.3577 | 2 | 6.3577 | 2
101E | Classroom | 351 | 23 |  |  | 610 | 13 | 13 | AHU-1 | 8 | 4880 | 4.3156 | 1 | 4.3156 | 2 | 4.3156 | 2
101F | Classroom | 393 | 26 |  |  | 650 | 14 | 14 | AHU-1 + UV | 8 | 5200 | 4.5346 | 1 | 4.5346 | 2 | 4.5346 | 2
102 | Classroom | 375 | 25 |  |  | 410 | 9 | 9 | AHU-1 and UV | 8 | 3280 | 6.8598 | 1 | 6.8598 | 2 | 6.8598 | 2
107 | Main Office Entry | 103 | 6 |  |  | 350 | 7 | 6 | AHU-3 | 8 | 2800 | 2.2071 | 1 | 2.2071 | 1 | 2.2071 | 1
107 | Main Office | 195 | 13 | Yes | 20 | 1125 | 25 | 25 | AHU-3 | 8 | 9000 | 1.3 | 1 | 1.3 | 1 | 21.3 | 3
108 | Classroom | 666 | 44 |  |  | 715 | 16 | 16 | AHU-5 + UV | 8 | 5720 | 6.986 | 1 | 6.986 | 2 | 6.986 | 2
109 | Classroom | 497 | 33 |  |  | 695 | 15 | 15 | AHU-5 + UV | 8 | 5560 | 5.3633 | 1 | 5.3633 | 2 | 5.3633 | 2
110 | Classroom | 477 | 31 |  |  | 695 | 15 | 15 | AHU-5 + UV | 8 | 5560 | 5.1475 | 1 | 5.1475 | 2 | 5.1475 | 2
111 | Classroom | 632 | 42 |  |  | 695 | 15 | 15 | AHU-5 + UV | 8 | 5560 | 6.8201 | 1 | 6.8201 | 2 | 6.8201 | 2
112 | Classroom | 496 | 33 |  |  | 695 | 15 | 15 | AHU-5 + UV | 8 | 5560 | 5.3525 | 1 | 5.3525 | 2 | 5.3525 | 2
113 | Music Room | 456 | 30 |  |  | 1430 | 32 | 30 | AHU-7 | 8 | 11440 | 2.3916 | 1 | 2.3916 | 1 | 2.3916 | 1
113 | Practice Rm 1 | 23 | 1 |  |  | 72 | 1 | 1 | AHU-7 | 8 | 576 | 2.3958 | 1 | 2.3958 | 1 | 2.3958 | 1
113 | Practice Rm 2 | 27 | 1 |  |  | 78 | 1 | 1 | AHU-7 | 8 | 624 | 2.5962 | 1 | 2.5962 | 1 | 2.5962 | 1
201 | IMC | 1373 | 91 |  |  | 2995 | 68 | 68 | AHU-10 + UV | 8 | 23960 | 3.4382 | 1.062 | 3.6515 | 1 | 3.6515 | 1
202 | Classroom | 467 | 31 |  |  | 1125 | 25 | 25 | Unit Ventilator and AHU | 8 | 9000 | 3.1133 | 1 | 3.1133 | 1 | 3.1133 | 1
202 | Media | 0 | 0 | Yes | 20 | 385 | 8 | 8 | Unit Ventilator and AHU | 8 | 3080 | 0 | 1 | 0 | 0 | 20 | 3
BAS 205 | IMC - Reading Small Classroom | 303 | 20 |  |  | 102 | 2 | 2 | Tightened damper Actuator to the shaft | 8 | 816 | 22.2794 | 1 | 22.2794 | 3 | 22.2794 | 3
BAS 206 | IMC - Reading Small Classroom | 317 | 21 |  |  | 859 | 19 | 19 | Tightened damper Actuator to the shaft | 8 | 6872 | 2.7678 | 1 | 2.7678 | 1 | 2.7678 | 1
206 | Classroom | 464 | 30 |  |  | 842 | 19 | 19 | AHU-1 + UV | 8 | 6736 | 4.133 | 1 | 4.133 | 2 | 4.133 | 2
207 | Classroom | 610 | 40 |  |  | 1325 | 30 | 30 | Unit Ventilator and AHU | 8 | 10600 | 3.4528 | 1 | 3.4528 | 1 | 3.4528 | 1
208 | Classroom | 318 | 21 | Yes | 20 | 1395 | 31 | 31 | Unit Ventilator and AHU | 8 | 11160 | 1.7097 | 1 | 1.7097 | 1 | 21.7097 | 3
208 | Computer Lab | 81 | 5 |  |  | 1210 | 27 | 5 |  | 8 | 9680 | 0.50207 | 1 | 0.50207 | 0 | 0.50207 | 0
209 | Classroom | 293 | 19 |  |  | 750 | 17 | 17 | AHU-1 + UV | 8 | 6000 | 2.93 | 1 | 2.93 | 1 | 2.93 | 1
210 | Classroom | 526 | 35 |  |  | 754 | 17 | 17 | Unit Ventilator and AHU | 8 | 6032 | 5.2321 | 1 | 5.2321 | 2 | 5.2321 | 2
211 | Classroom | 551 | 36 |  |  | 754 | 17 | 17 | Unit Ventilator and AHU | 8 | 6032 | 5.4808 | 1 | 5.4808 | 2 | 5.4808 | 2
212 | Classroom | 426 | 28 |  |  | 753 | 17 | 17 | Unit Ventilator and AHU | 8 | 6024 | 4.243 | 1 | 4.243 | 2 | 4.243 | 2
213 | Classroom | 497 | 33 |  |  | 753 | 17 | 17 | Unit Ventilator and AHU | 8 | 6024 | 4.9502 | 1 | 4.9502 | 2 | 4.9502 | 2
214 | Classroom | 478 | 31 |  |  | 724 | 16 | 16 | Unit Ventilator and AHU | 8 | 5792 | 4.9517 | 1 | 4.9517 | 2 | 4.9517 | 2
215 | Art Room | 367 | 24 | Yes | 20 | 1324 | 30 | 30 | AHU-12 | 8 | 10592 | 2.0789 | 1 | 2.0789 | 1 | 22.0789 | 3
304 | Classroom | 367 | 24 |  |  | 725 | 16 | 16 | Unit Ventilator and AHU | 8 | 5800 | 3.7966 | 1 | 3.7966 | 1 | 3.7966 | 1
305 | Classroom | 431 | 28 |  |  | 754 | 17 | 17 | Unit Ventilator and AHU | 8 | 6032 | 4.2871 | 1 | 4.2871 | 2 | 4.2871 | 2
306 | Classroom | 395 | 26 |  |  | 754 | 17 | 17 | Unit Ventilator and AHU | 8 | 6032 | 3.929 | 1 | 3.929 | 1 | 3.929 | 1
307 | Classroom | 315 | 21 |  |  | 753 | 17 | 17 | Unit Ventilator and AHU | 8 | 6024 | 3.1375 | 1 | 3.1375 | 1 | 3.1375 | 1
308 | Classroom | 350 | 23 |  |  | 753 | 17 | 17 | Unit Ventilator and AHU | 8 | 6024 | 3.4861 | 1 | 3.4861 | 1 | 3.4861 | 1
309 | Classroom | 340 | 22 |  |  | 754 | 17 | 17 | Unit Ventilator and AHU | 8 | 6032 | 3.382 | 1 | 3.382 | 1 | 3.382 | 1
310 | Classroom | 361 | 24 |  |  | 754 | 17 | 17 | Unit Ventilator and AHU | 8 | 6032 | 3.5908 | 1 | 3.5908 | 1 | 3.5908 | 1
311 | Classroom | 317 | 21 |  |  | 753 | 17 | 17 | Unit Ventilator and AHU | 8 | 6024 | 3.1574 | 1 | 3.1574 | 1 | 3.1574 | 1
312 | Classroom | 427 | 28 |  |  | 753 | 17 | 17 | Unit Ventilator and AHU | 8 | 6024 | 4.253 | 1 | 4.253 | 2 | 4.253 | 2
313 | Classroom | 387 | 25 |  |  | 754 | 17 | 17 | Unit Ventilator and AHU | 8 | 6032 | 3.8495 | 1 | 3.8495 | 1 | 3.8495 | 1
314 | Classroom | 411 | 27 |  |  | 715 | 16 | 16 | Unit Ventilator and AHU | 8 | 5720 | 4.3112 | 1 | 4.3112 | 2 | 4.3112 | 2
315 | Classroom | 363 | 24 |  |  | 810 | 18 | 18 | Unit Ventilator and AHU | 8 | 6480 | 3.3611 | 1 | 3.3611 | 1 | 3.3611 | 1
- | Auditorium | 2966 | 197 |  |  | 2910 | 66 | 66 | AHU-6 | 8 | 23280 | 7.6443 | 1.062 | 8.1185 | 2 | 8.1185 | 2
- | Cafeteria | 2006 | 133 |  |  | 3590 | 81 | 81 | AHU | 8 | 28720 | 4.1908 | 1.062 | 4.4508 | 2 | 4.4508 | 2
- | Kitchen | 35 | 2 | Yes | 20 | 1116 | 25 | 25 | AHU-3 | 8 | 8928 | 0.23522 | 1 | 0.23522 | 0 | 20.2352 | 3
- | Nurses Office | 98 | 6 |  |  | 105 | 2 | 2 | FC 5-1 | 8 | 840 | 7 | 1 | 7 | 2 | 7 | 2
- | Nurse Exam Room | 110 | 7 |  |  | 94 | 2 | 2 | FC 5-1 | 8 | 752 | 8.7766 | 1 | 8.7766 | 2 | 8.7766 | 2
- | Nurses Waiting Room | 108 | 7 |  |  | 130 | 2 | 2 | FC 5-1 | 8 | 1040 | 6.2308 | 1 | 6.2308 | 2 | 6.2308 | 2
- | Principal Office | 74 | 4 | Yes | 20 | 322 | 7 | 7 | AHU-3 | 8 | 2576 | 1.7236 | 1 | 1.7236 | 1 | 21.7236 | 3
- | Conference Room | 147 | 9 |  |  | 429 | 9 | 9 | AHU-3 | 8 | 3432 | 2.5699 | 1 | 2.5699 | 1 | 2.5699 | 1
- | Gym | 1430 | 95 |  |  | 4969 | 112 | 95 | AHU-8 + AHU-9 | 8 | 39752 | 2.1584 | 1.062 | 2.2923 | 1 | 2.2923 | 1
Sheet Last Modified: | 2021-04-13
School: | Andrew Jackson Elementary School | House fan Abated
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B1 | Music Room | 324 | 21 |  |  | 1036 | 23 | 21 | AHU | 8 | 8288 | 2.3456 | 1 | 2.3456 | 1 | 2.3456 | 1
101 | Classroom | 536 | 35 |  |  | 1190 | 27 | 27 | AHU | 8 | 9520 | 3.3782 | 1 | 3.3782 | 1 | 3.3782 | 1
102 | Classroom | 436 | 29 |  |  | 638 | 14 | 14 | AHU | 8 | 5104 | 5.1254 | 1 | 5.1254 | 2 | 5.1254 | 2
103 | Classroom | 567 | 37 |  |  | 805 | 18 | 18 | AHU | 8 | 6440 | 5.2826 | 1 | 5.2826 | 2 | 5.2826 | 2
104 | Classroom | 363 | 24 |  |  | 840 | 19 | 19 | AHU | 8 | 6720 | 3.2411 | 1 | 3.2411 | 1 | 3.2411 | 1
105 | Classroom | 398 | 26 |  |  | 828 | 18 | 18 | AHU | 8 | 6624 | 3.6051 | 1 | 3.6051 | 1 | 3.6051 | 1
106 | Classroom | 740 | 49 |  |  | 748 | 17 | 17 | AHU | 8 | 5984 | 7.4198 | 1 | 7.4198 | 2 | 7.4198 | 2
107 | Classroom | 567 | 37 |  |  | 736 | 16 | 16 | AHU | 8 | 5888 | 5.7779 | 1 | 5.7779 | 2 | 5.7779 | 2
107B | - |  | 0 | Yes | 20 | 132 | 3 | 3 | N/A | 8 | 1056 | 0 | 1 | 0 | 0 | 20 | 3
107C | - |  | 0 | Yes | 20 | 220 | 5 | 5 | N/A | 8 | 1760 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom | 396 | 26 |  |  | 841 | 19 | 19 | AHU | 8 | 6728 | 3.5315 | 1 | 3.5315 | 1 | 3.5315 | 1
109 | Classroom | 669 | 44 |  |  | 1218 | 27 | 27 | AHU | 8 | 9744 | 4.1195 | 1 | 4.1195 | 2 | 4.1195 | 2
110 | Classroom | 482 | 32 |  |  | 848 | 19 | 19 | AHU | 8 | 6784 | 4.263 | 1 | 4.263 | 2 | 4.263 | 2
201 | Classroom | 581 | 38 |  |  | 1225 | 27 | 27 | AHU | 8 | 9800 | 3.5571 | 1 | 3.5571 | 1 | 3.5571 | 1
202 | Classroom | 346 | 23 |  |  | 726 | 16 | 16 | AHU | 8 | 5808 | 3.5744 | 1 | 3.5744 | 1 | 3.5744 | 1
203 | Classroom | 384 | 25 |  |  | 864 | 19 | 19 | AHU | 8 | 6912 | 3.3333 | 1 | 3.3333 | 1 | 3.3333 | 1
204 | Classroom | 453 | 30 |  |  | 850 | 19 | 19 | AHU | 8 | 6800 | 3.9971 | 1 | 3.9971 | 1 | 3.9971 | 1
204A | Office | 0 | 0 | Yes | 20 | 468 | 10 | 10 |  | 8 | 3744 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom | 304 | 20 |  |  | 840 | 19 | 19 | AHU | 8 | 6720 | 2.7143 | 1 | 2.7143 | 1 | 2.7143 | 1
206 | Classroom | 531 | 35 |  |  | 864 | 19 | 19 | AHU | 8 | 6912 | 4.6094 | 1 | 4.6094 | 2 | 4.6094 | 2
207 | Classroom | 614 | 40 |  |  | 805 | 18 | 18 | AHU | 8 | 6440 | 5.7205 | 1 | 5.7205 | 2 | 5.7205 | 2
208 | Classroom | 367 | 24 |  |  | 850 | 19 | 19 | AHU | 8 | 6800 | 3.2382 | 1 | 3.2382 | 1 | 3.2382 | 1
209/210 | Classroom | 1387 | 92 |  |  | 1680 | 38 | 38 | AHU | 8 | 13440 | 6.192 | 1 | 6.192 | 2 | 6.192 | 2
211 | Classroom | 490 | 32 |  |  | 840 | 19 | 19 | AHU | 8 | 6720 | 4.375 | 1 | 4.375 | 2 | 4.375 | 2
301 | Classroom | 530 | 35 |  |  | 980 | 22 | 22 | AHU | 8 | 7840 | 4.0561 | 1 | 4.0561 | 2 | 4.0561 | 2
302 | Classroom | 303 | 20 |  |  | 816 | 18 | 18 | AHU | 8 | 6528 | 2.7849 | 1 | 2.7849 | 1 | 2.7849 | 1
303 | Classroom | 88 | 5 | Yes | 20 | 828 | 18 | 18 |  | 8 | 6624 | 0.7971 | 1 | 0.7971 | 0 | 20.7971 | 3
304 | Classroom | 427 | 28 |  |  | 805 | 18 | 18 | AHU | 8 | 6440 | 3.9783 | 1 | 3.9783 | 1 | 3.9783 | 1
304A | Office | 0 | 0 | Yes | 20 | 442 | 10 | 10 |  | 8 | 3536 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom | 619 | 41 |  |  | 840 | 19 | 19 | AHU | 8 | 6720 | 5.5268 | 1 | 5.5268 | 2 | 5.5268 | 2
306 | Classroom | 528 | 35 |  |  | 840 | 19 | 19 | AHU | 8 | 6720 | 4.7143 | 1 | 4.7143 | 2 | 4.7143 | 2
307 | Classroom | 375 | 25 |  |  | 782 | 17 | 17 | AHU | 8 | 6256 | 3.5965 | 1 | 3.5965 | 1 | 3.5965 | 1
308 | Classroom | 417 | 27 |  |  | 816 | 18 | 18 | AHU | 8 | 6528 | 3.8327 | 1 | 3.8327 | 1 | 3.8327 | 1
- | Gym/Cafeteria | 2408 | 160 |  |  | 3005 | 68 | 68 | AHU | 8 | 24040 | 6.01 | 1.062 | 6.3828 | 2 | 6.3828 | 2
- | Library | 740 | 49 |  |  | 2320 | 52 | 49 | AHU | 8 | 18560 | 2.3922 | 1 | 2.3922 | 1 | 2.3922 | 1
- | I.M.C. Office | 160 | 10 |  |  | 400 | 9 | 9 | AHU | 8 | 3200 | 3 | 1 | 3 | 1 | 3 | 1
- | Main Office | 0 | 0 | Yes | 20 | 484 | 11 | 11 |  | 8 | 3872 | 0 | 1 | 0 | 0 | 20 | 3
- | Princpal's Office |  | 0 | Yes | 20 | 308 | 7 | 7 | N/A | 8 | 2464 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse's Office |  | 0 | Yes | 20 | 264 | 6 | 6 | N/A | 8 | 2112 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-26
School: | James Martin- Alternative Middle Years (Middle School)
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 0 | 0 | Yes | 20 | 696 | 15 | 15 |  | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom | 280 | 18 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 2.9167 | 1 | 2.9167 | 1 | 2.9167 | 1
107 | Classroom | 313 | 20 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 3.2604 | 1 | 3.2604 | 1 | 3.2604 | 1
108 | Classroom | 0 | 0 | Yes | 20 | 696 | 15 | 15 |  | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 0 | 0 | Yes | 20 | 672 | 15 | 15 |  | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 20 | 720 | 16 | 16 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 | Yes | 20 | 750 | 17 | 17 |  | 8 | 6000 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom | 306 | 20 |  |  | 750 | 17 | 17 |  | 8 | 6000 | 3.06 | 1 | 3.06 | 1 | 3.06 | 1
204 | Lounge | 371 | 24 |  |  | 480 | 10 | 10 |  | 8 | 3840 | 5.7969 | 1 | 5.7969 | 2 | 5.7969 | 2
205 | Classroom | 345 | 23 |  |  | 912 | 20 | 20 |  | 8 | 7296 | 2.8372 | 1 | 2.8372 | 1 | 2.8372 | 1
206 | School Store | 291 | 19 |  |  | 384 | 8 | 8 |  | 8 | 3072 | 5.6836 | 1 | 5.6836 | 2 | 5.6836 | 2
207 | Classroom | 309 | 20 |  |  | 750 | 17 | 17 |  | 8 | 6000 | 3.09 | 1 | 3.09 | 1 | 3.09 | 1
208 | Classroom | 331 | 22 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 3.4479 | 1 | 3.4479 | 1 | 3.4479 | 1
209 | Classroom | 303 | 20 |  |  | 667 | 15 | 15 |  | 8 | 5336 | 3.407 | 1 | 3.407 | 1 | 3.407 | 1
210 | Classroom | 292 | 19 |  |  | 667 | 15 | 15 |  | 8 | 5336 | 3.2834 | 1 | 3.2834 | 1 | 3.2834 | 1
211 | Classroom | 0 | 0 | Yes | 20 | 672 | 15 | 15 |  | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
214 | Security Office | 0 | 0 | Yes | 20 | 256 | 5 | 5 |  | 8 | 2048 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 | Yes | 20 | 696 | 15 | 15 |  | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 20 | 696 | 15 | 15 |  | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom | 301 | 20 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 3.1354 | 1 | 3.1354 | 1 | 3.1354 | 1
304 | Classroom | 275 | 18 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 2.8646 | 1 | 2.8646 | 1 | 2.8646 | 1
305 | Classroom | 297 | 19 |  |  | 696 | 15 | 15 |  | 8 | 5568 | 3.2004 | 1 | 3.2004 | 1 | 3.2004 | 1
306 | Classroom | 284 | 18 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 2.9583 | 1 | 2.9583 | 1 | 2.9583 | 1
307 | Classroom | 297 | 19 |  |  | 768 | 17 | 17 |  | 8 | 6144 | 2.9004 | 1 | 2.9004 | 1 | 2.9004 | 1
308 | Classroom | 317 | 21 |  |  | 696 | 15 | 15 |  | 8 | 5568 | 3.4159 | 1 | 3.4159 | 1 | 3.4159 | 1
309 | Classroom | 272 | 18 |  |  | 696 | 15 | 15 |  | 8 | 5568 | 2.931 | 1 | 2.931 | 1 | 2.931 | 1
310 | Classroom | 293 | 19 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 3.0521 | 1 | 3.0521 | 1 | 3.0521 | 1
311 | Art Room | 0 | 0 | Yes | 20 | 928 | 21 | 21 |  | 8 | 7424 | 0 | 1 | 0 | 0 | 20 | 3
314 | Office | 0 | 0 | Yes | 20 | 256 | 5 | 5 |  | 8 | 2048 | 0 | 1 | 0 | 0 | 20 | 3
- | Boys Cafeteria | 0 | 0 | Yes | 20 | 851 | 19 | 19 |  | 8 | 6808 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselors Office | 0 | 0 | Yes | 20 | 160 | 3 | 3 |  | 8 | 1280 | 0 | 1 | 0 | 0 | 20 | 3
- | Girls Cafeteria | 0 | 0 | Yes | 20 | 1728 | 39 | 39 |  | 8 | 13824 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym | 0 | 0 |  |  | 1760 | 40 | 0 |  | 8 | 14080 | 0 | 1 | 0 | 0 | 0 | 0
- | IMC-A | 270 | 18 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 2.8125 | 1 | 2.8125 | 1 | 2.8125 | 1
- | IMC-B | 292 | 19 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 3.0417 | 1 | 3.0417 | 1 | 3.0417 | 1
- | IMC-C | 283 | 18 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 2.9479 | 1 | 2.9479 | 1 | 2.9479 | 1
- | Main Office | 0 | 0 | Yes | 20 | 360 | 8 | 8 |  | 8 | 2880 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses Office | 0 | 0 | Yes | 20 | 256 | 5 | 5 |  | 8 | 2048 | 0 | 1 | 0 | 0 | 20 | 3
- | Teachers Lounge | 0 | 0 |  |  | 480 | 10 | 0 |  | 8 | 3840 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-26
School: | Abraham S. Jenks Elementary School | House fan Abated
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
14 | Classroom | 422 | 28 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 4.9608 | 1 | 4.9608 | 2 | 4.9608 | 2
15 | Cafeteria | 221 | 14 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 2.598 | 1 | 2.598 | 1 | 2.598 | 1
101 | Classroom | 459 | 30 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 5.2159 | 1 | 5.2159 | 2 | 5.2159 | 2
102 | Classroom | 1235 | 82 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 14.0341 | 1 | 14.0341 | 3 | 14.0341 | 3
103 | Classroom | 1253 | 83 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 14.2386 | 1 | 14.2386 | 3 | 14.2386 | 3
104 | Classroom | 919 | 61 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 10.4432 | 1 | 10.4432 | 3 | 10.4432 | 3
105 | Classroom | 632 | 42 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 7.1818 | 1 | 7.1818 | 2 | 7.1818 | 2
106 | Classroom | 748 | 49 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 8.5 | 1 | 8.5 | 2 | 8.5 | 2
201 | Classroom | 1277 | 85 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 13.8804 | 1 | 13.8804 | 3 | 13.8804 | 3
202 | Classroom | 522 | 34 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 5.6739 | 1 | 5.6739 | 2 | 5.6739 | 2
203 | Classroom | 1094 | 72 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 11.8913 | 1 | 11.8913 | 3 | 11.8913 | 3
204 | Classroom | 803 | 53 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 8.7283 | 1 | 8.7283 | 2 | 8.7283 | 2
205 | Classroom | 749 | 49 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 8.1413 | 1 | 8.1413 | 2 | 8.1413 | 2
206 | Classroom | 1198 | 79 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 13.0217 | 1 | 13.0217 | 3 | 13.0217 | 3
207 | Classroom | 1279 | 85 |  |  | 744 | 16 | 16 | House Fan | 8 | 5952 | 12.8931 | 1 | 12.8931 | 3 | 12.8931 | 3
- | Principals Office |  | 0 | Yes | 20 | 165 | 3 | 3 |  | 8 | 1320 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 195 | 4 | 4 |  | 8 | 1560 | 0 | 1 | 0 | 0 | 20 | 3
- | Teacher Lounge |  | 0 |  |  | 165 | 3 | 0 |  | 8 | 1320 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurses Office |  | 0 | Yes | 20 | 190 | 4 | 4 |  | 8 | 1520 | 0 | 1 | 0 | 0 | 20 | 3
- | Library | 176 | 11 |  |  | 638 | 14 | 11 | House Fan | 8 | 5104 | 2.069 | 1 | 2.069 | 1 | 2.069 | 1
- | Auditorium | 217 | 14 |  |  | 1540 | 35 | 14 | UV | 8 | 12320 | 1.0568 | 1 | 1.0568 | 1 | 1.0568 | 1
- | Cafeteria | 362 | 24 |  |  | 638 | 14 | 14 | House Fan | 8 | 5104 | 4.2555 | 1 | 4.2555 | 2 | 4.2555 | 2
- | North Trailer Classroom | 227 | 15 |  |  | N/A | 0 | 0 | N/A used for storage
- | South Trailer Classroom | 261 | 17 |  |  | 638 | 14 | 14 | AHU | 8 | 5104 | 3.0682 | 1 | 3.0682 | 1 | 3.0682 | 1
- | Gym |  | 0 | Yes | 20 | 1700 | 38 | 38 | N/A | 8 | 13600 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-28
School: | John S. Jenks Elementary-Middle School
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
322 | Classroom |  | 0 | Yes | 20 | 658 | 14 | 14 | House Fan | 8 | 5264 | 0 | 1 | 0 | 0 | 20 | 3
321 | Classroom |  | 0 | Yes | 20 | 692 | 15 | 15 | House Fan | 8 | 5536 | 0 | 1 | 0 | 0 | 20 | 3
320 | Classroom |  | 0 | Yes | 20 | 685 | 15 | 15 | House Fan | 8 | 5480 | 0 | 1 | 0 | 0 | 20 | 3
319B | - |  | 0 | Yes | 20 | 658 | 14 | 14 | House Fan | 8 | 5264 | 0 | 1 | 0 | 0 | 20 | 3
319A | - |  | 0 | Yes | 20 | 305 | 6 | 6 | House Fan | 8 | 2440 | 0 | 1 | 0 | 0 | 20 | 3
318 | Classroom |  | 0 | Yes | 20 | 654 | 14 | 14 | House Fan | 8 | 5232 | 0 | 1 | 0 | 0 | 20 | 3
317 | Classroom |  | 0 | Yes | 20 | 674 | 15 | 15 | House Fan | 8 | 5392 | 0 | 1 | 0 | 0 | 20 | 3
316 | Classroom |  | 0 | Yes | 20 | 693 | 15 | 15 | House Fan | 8 | 5544 | 0 | 1 | 0 | 0 | 20 | 3
315 | Classroom |  | 0 | Yes | 20 | 654 | 14 | 14 | House Fan | 8 | 5232 | 0 | 1 | 0 | 0 | 20 | 3
214 | Classroom |  | 0 | Yes | 20 | 671 | 15 | 15 | House Fan | 8 | 5368 | 0 | 1 | 0 | 0 | 20 | 3
213 | Classroom |  | 0 | Yes | 20 | 689 | 15 | 15 | House Fan | 8 | 5512 | 0 | 1 | 0 | 0 | 20 | 3
212 | Classroom |  | 0 | Yes | 20 | 683 | 15 | 15 | House Fan | 8 | 5464 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom |  | 0 | Yes | 20 | 673 | 15 | 15 | House Fan | 8 | 5384 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom |  | 0 | Yes | 20 | 671 | 15 | 15 | House Fan | 8 | 5368 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom |  | 0 | Yes | 20 | 680 | 15 | 15 | House Fan | 8 | 5440 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom |  | 0 | Yes | 20 | 695 | 15 | 15 | House Fan | 8 | 5560 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom |  | 0 | Yes | 20 | 636 | 14 | 14 | House Fan | 8 | 5088 | 0 | 1 | 0 | 0 | 20 | 3
110 | - |  | 0 | Yes | 20 | 336 | 7 | 7 | House Fan | 8 | 2688 | 0 | 1 | 0 | 0 | 20 | 3
109 | - |  | 0 | Yes | 20 | 156 | 3 | 3 | house Fan | 8 | 1248 | 0 | 1 | 0 | 0 | 20 | 3
106 | IMC |  | 0 | Yes | 20 | 671 | 15 | 15 | House Fan | 8 | 5368 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom |  | 0 | Yes | 20 | 640 | 14 | 14 | House Fan | 8 | 5120 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom |  | 0 | Yes | 20 | 627 | 14 | 14 | House Fan | 8 | 5016 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 666 | 15 | 15 | House Fan | 8 | 5328 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 668 | 15 | 15 | House Fan | 8 | 5344 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom |  | 0 | Yes | 20 | 602 | 13 | 13 | House Fan | 8 | 4816 | 0 | 1 | 0 | 0 | 20 | 3
100 | Classroom |  | 0 | Yes | 20 | 1053 | 23 | 23 | House Fan | 8 | 8424 | 0 | 1 | 0 | 0 | 20 | 3
- | Kindergarten Classroom |  | 0 | Yes | 20 | 1512 | 34 | 34 | House Fan | 8 | 12096 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 | Yes | 20 | 4500 | 102 | 102 |  | 8 | 36000 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 385 | 8 | 8 |  | 8 | 3080 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 112 | 2 | 2 |  | 8 | 896 | 0 | 1 | 0 | 0 | 20 | 3
- | Library |  | 0 | Yes | 20 | 616 | 13 | 13 |  | 8 | 4928 | 0 | 1 | 0 | 0 | 20 | 3
- | Teachers Lounge |  | 0 | Yes | 20 | 402 | 9 | 9 |  | 8 | 3216 | 0 | 1 | 0 | 0 | 20 | 3
- | Spo |  | 0 | Yes | 20 | 180 | 4 | 4 |  | 8 | 1440 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office |  | 0 | Yes | 20 | 165 | 3 | 3 |  | 8 | 1320 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 263 | 5 | 5 |  | 8 | 2104 | 0 | 1 | 0 | 0 | 20 | 3
- | Speech Room |  | 0 | Yes | 20 | 103 | 2 | 2 |  | 8 | 824 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium |  | 0 |  |  | 3463 | 78 | 0 |  | 8 | 27704 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Copy Room |  | 0 |  |  | 166 | 3 | 0 |  | 8 | 1328 | 0 | 1 | 0 | 0 | 0 | 0
- | Art Room |  | 0 | Yes | 20 | 1085 | 24 | 24 |  | 8 | 8680 | 0 | 1 | 0 | 0 | 20 | 3
- | Lego Room |  | 0 | Yes | 20 | 165 | 3 | 3 |  | 8 | 1320 | 0 | 1 | 0 | 0 | 20 | 3
- | Kitchen |  | 0 | Yes | 20 | 578 | 13 | 13 |  | 8 | 4624 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym Office |  | 0 |  |  | 588 | 13 | 0 |  | 8 | 4704 | 0 | 1 | 0 | 0 | 0 | 0
- | Home & school |  | 0 |  |  | 364 | 8 | 0 |  | 8 | 2912 | 0 | 1 | 0 | 0 | 0 | 0
- | Boys Room |  | 0 |  |  | 144 | 3 | 0 |  | 8 | 1152 | 0 | 1 | 0 | 0 | 0 | 0
- | Girls Room |  | 0 |  |  | 144 | 3 | 0 |  | 8 | 1152 | 0 | 1 | 0 | 0 | 0 | 0
- | Boys room by gym |  | 0 |  |  | 614 | 13 | 0 |  | 8 | 4912 | 0 | 1 | 0 | 0 | 0 | 0
- | Girls room by gym |  | 0 |  |  | 614 | 13 | 0 |  | 8 | 4912 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-06
School: | Juniata Park Academy Elementary-Middle School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 1020 | 68 |  |  | 1100 | 25 | 25 | RTU/UV | 8 | 8800 | 6.9545 | 1 | 6.9545 | 2 | 6.9545 | 2
2 | Classroom | 897 | 59 |  |  | 1108 | 25 | 25 | RTU/UV | 8 | 8864 | 6.0718 | 1 | 6.0718 | 2 | 6.0718 | 2
3 | Classroom | 1328 | 88 |  |  | 1108 | 25 | 25 | RTU/UV | 8 | 8864 | 8.9892 | 1 | 8.9892 | 2 | 8.9892 | 2
4 | Classroom | 1321 | 88 |  |  | 1093 | 24 | 24 | RTU/UV | 8 | 8744 | 9.0645 | 1 | 9.0645 | 2 | 9.0645 | 2
5 | Classroom | 975 | 65 |  |  | 1123 | 25 | 25 | RTU/UV | 8 | 8984 | 6.5116 | 1 | 6.5116 | 2 | 6.5116 | 2
6 | Classroom | 874 | 58 |  |  | 1125 | 25 | 25 | RTU/UV | 8 | 9000 | 5.8267 | 1 | 5.8267 | 2 | 5.8267 | 2
100 | Classroom | 750 | 50 |  |  | 660 | 15 | 15 | RTU/UV | 8 | 5280 | 8.5227 | 1 | 8.5227 | 2 | 8.5227 | 2
101 | Classroom | 969 | 64 |  |  | 660 | 15 | 15 | RTU/UV | 8 | 5280 | 11.0114 | 1 | 11.0114 | 3 | 11.0114 | 3
102 | Classroom | 836 | 55 |  |  | 952 | 21 | 21 | RTU/UV | 8 | 7616 | 6.5861 | 1 | 6.5861 | 2 | 6.5861 | 2
103 | Classroom | 1212 | 80 |  |  | 792 | 18 | 18 | RTU/UV | 8 | 6336 | 11.4773 | 1 | 11.4773 | 3 | 11.4773 | 3
104 | Classroom | 1119 | 74 |  |  | 792 | 18 | 18 | RTU/UV | 8 | 6336 | 10.5966 | 1 | 10.5966 | 3 | 10.5966 | 3
105 | Classroom | 2327 | 155 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 21.9805 | 1 | 21.9805 | 3 | 21.9805 | 3
106 | Classroom | 1053 | 70 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 9.9465 | 1 | 9.9465 | 2 | 9.9465 | 2
107 | Classroom | 789 | 52 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 7.4528 | 1 | 7.4528 | 2 | 7.4528 | 2
108 | Classroom | 952 | 63 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 8.9924 | 1 | 8.9924 | 2 | 8.9924 | 2
109 | Classroom | 910 | 60 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 8.5957 | 1 | 8.5957 | 2 | 8.5957 | 2
110 | Classroom | 817 | 54 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 7.7173 | 1 | 7.7173 | 2 | 7.7173 | 2
111 | Classroom | 1240 | 82 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 11.7128 | 1 | 11.7128 | 3 | 11.7128 | 3
112 | Classroom | 1129 | 75 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 10.6644 | 1 | 10.6644 | 3 | 10.6644 | 3
113 | Classroom | 967 | 64 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 9.1341 | 1 | 9.1341 | 2 | 9.1341 | 2
114 | Classroom | 906 | 60 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 8.5579 | 1 | 8.5579 | 2 | 8.5579 | 2
115 | Classroom | 1064 | 70 |  |  | 792 | 18 | 18 | RTU/UV | 8 | 6336 | 10.0758 | 1 | 10.0758 | 3 | 10.0758 | 3
117 | Girls' Toilet Room | 115 | 7 |  |  | 140 | 3 | 3 | RTU/UV | 8 | 1120 | 6.1607 | 1 | 6.1607 | 2 | 6.1607 | 2
116 | Classroom | 853 | 56 |  |  | 792 | 18 | 18 | RTU/UV | 8 | 6336 | 8.0777 | 1 | 8.0777 | 2 | 8.0777 | 2
117 | Classroom | 636 | 42 |  |  | 672 | 15 | 15 | RTU/UV | 8 | 5376 | 7.0982 | 1 | 7.0982 | 2 | 7.0982 | 2
120 | Boys' Toilet Room | 120 | 8 |  |  | 200 | 4 | 4 | RTU/UV | 8 | 1600 | 4.5 | 1 | 4.5 | 2 | 4.5 | 2
200 | Classroom | 661 | 44 |  |  | 609 | 13 | 13 | RTU/UV | 8 | 4872 | 8.1404 | 1 | 8.1404 | 2 | 8.1404 | 2
201 | Classroom | 638 | 42 |  |  | 772 | 17 | 17 | RTU/UV | 8 | 6176 | 6.1982 | 1 | 6.1982 | 2 | 6.1982 | 2
202 | Classroom | 449 | 29 |  |  | 721 | 16 | 16 | RTU/UV | 8 | 5768 | 4.6706 | 1 | 4.6706 | 2 | 4.6706 | 2
203 | Classroom | 691 | 46 |  |  | 673 | 15 | 15 | RTU/UV | 8 | 5384 | 7.7006 | 1 | 7.7006 | 2 | 7.7006 | 2
204 | Classroom | 534 | 35 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 5.0441 | 1 | 5.0441 | 2 | 5.0441 | 2
205 | Classroom | 627 | 41 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 5.9225 | 1 | 5.9225 | 2 | 5.9225 | 2
205 | Girls' Toilet Room | 22 | 1 |  |  | 182 | 4 | 1 | RTU/UV | 8 | 1456 | 0.90659 | 1 | 0.90659 | 0 | 0.90659 | 0
206 | Classroom | 530 | 35 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 5.0063 | 1 | 5.0063 | 2 | 5.0063 | 2
207 | Classroom | 539 | 35 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 5.0913 | 1 | 5.0913 | 2 | 5.0913 | 2
208 | Classroom | 665 | 44 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 6.2815 | 1 | 6.2815 | 2 | 6.2815 | 2
208 | Boys' Toilet Room | 24 | 1 |  |  | 195 | 4 | 1 | RTU/UV | 8 | 1560 | 0.92308 | 1 | 0.92308 | 0 | 0.92308 | 0
209 | Classroom | 509 | 33 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 4.8079 | 1 | 4.8079 | 2 | 4.8079 | 2
210 | Classroom | 310 | 20 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 2.9282 | 1 | 2.9282 | 1 | 2.9282 | 1
211 | Classroom | 418 | 27 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 3.9484 | 1 | 3.9484 | 1 | 3.9484 | 1
212 | Classroom | 487 | 32 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 4.6001 | 1 | 4.6001 | 2 | 4.6001 | 2
213 | Classroom | 539 | 35 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 5.0913 | 1 | 5.0913 | 2 | 5.0913 | 2
215 | Classroom | 538 | 35 |  |  | 794 | 18 | 18 | RTU/UV | 8 | 6352 | 5.0819 | 1 | 5.0819 | 2 | 5.0819 | 2
217 | Classroom | 683 | 45 |  |  | 793 | 18 | 18 | RTU/UV | 8 | 6344 | 6.4596 | 1 | 6.4596 | 2 | 6.4596 | 2
229 | Girls' Toilet Room | 330 | 22 |  |  | 195 | 4 | 4 | RTU/UV | 8 | 1560 | 12.6923 | 1 | 12.6923 | 3 | 12.6923 | 3
235 | Boys' Toilet Room | 140 | 9 |  |  | 200 | 4 | 4 | RTU/UV | 8 | 1600 | 5.25 | 1 | 5.25 | 2 | 5.25 | 2
- | Main Office | 740 | 49 |  |  | 500 | 11 | 11 | RTU/UV | 8 | 4000 | 11.1 | 1 | 11.1 | 3 | 11.1 | 3
- | Confrence Room | 475 | 31 |  |  | 203 | 4 | 4 | RTU/UV | 8 | 1624 | 17.5493 | 1 | 17.5493 | 3 | 17.5493 | 3
- | Main Office 4 | 255 | 17 |  |  | 153 | 3 | 3 | RTU/UV | 8 | 1224 | 12.5 | 1 | 12.5 | 3 | 12.5 | 3
- | Main Office 3 | 255 | 17 |  |  | 120 | 2 | 2 | RTU/UV | 8 | 960 | 15.9375 | 1 | 15.9375 | 3 | 15.9375 | 3
- | Main Office 2 | 260 | 17 |  |  | 120 | 2 | 2 | RTU/UV | 8 | 960 | 16.25 | 1 | 16.25 | 3 | 16.25 | 3
- | Main Office 1 | 310 | 20 |  |  | 162 | 3 | 3 | RTU/UV | 8 | 1296 | 14.3519 | 1 | 14.3519 | 3 | 14.3519 | 3
- | Main Office Work Room | 245 | 16 |  |  | 165 | 3 | 3 | RTU/UV | 8 | 1320 | 11.1364 | 1 | 11.1364 | 3 | 11.1364 | 3
- | Principals Office | 365 | 24 |  |  | 201 | 4 | 4 | RTU/UV | 8 | 1608 | 13.6194 | 1 | 13.6194 | 3 | 13.6194 | 3
- | Principal Bathroom | 52 | 3 |  |  | 77 | 1 | 1 | RTU/UV | 8 | 616 | 5.0649 | 1 | 5.0649 | 2 | 5.0649 | 2
- | IMC Workroom | 79 | 5 |  |  | 347 | 7 | 5 | RTU/UV | 8 | 2776 | 1.7075 | 1 | 1.7075 | 1 | 1.7075 | 1
- | IMC Conference Rm | 128 | 8 |  |  | 360 | 8 | 8 | RTU/UV | 8 | 2880 | 2.6667 | 1 | 2.6667 | 1 | 2.6667 | 1
- | IMC Reference | 62 | 4 |  |  | 260 | 5 | 4 | RTU/UV | 8 | 2080 | 1.7885 | 1 | 1.7885 | 1 | 1.7885 | 1
- | IMC Main Area North | 320 | 21 |  |  | 1432 | 32 | 21 | RTU/UV | 8 | 11456 | 1.676 | 1 | 1.676 | 1 | 1.676 | 1
- | IMC Main Area South | 217 | 14 |  |  | 1432 | 32 | 14 | RTU/UV | 8 | 11456 | 1.1365 | 1 | 1.1365 | 1 | 1.1365 | 1
- | Library | 710 | 47 |  |  | 2864 | 65 | 47 | RTU/UV | 8 | 22912 | 1.8593 | 1.062 | 1.9746 | 1 | 1.9746 | 1
- | Art Room | 701 | 46 |  |  | 1202 | 27 | 27 | RTU/UV | 8 | 9616 | 4.374 | 1 | 4.374 | 2 | 4.374 | 2
- | Music Classroom | 738 | 49 |  |  | 1248 | 28 | 28 | RTU/UV | 8 | 9984 | 4.4351 | 1 | 4.4351 | 2 | 4.4351 | 2
- | Cafeteria | 9535 | 635 |  |  | 4250 | 96 | 96 | RTU/UV | 8 | 34000 | 16.8265 | 1.062 | 17.8703 | 3 | 17.8703 | 3
- | Food Service | 135 | 9 | Yes | 20 | 1600 | 36 | 36 | RTU/UV | 8 | 12800 | 0.63281 | 1 | 0.63281 | 0 | 20.6328 | 3
- | Computer Lab | 1062 | 70 |  |  | 1000 | 22 | 22 | RTU/UV | 8 | 8000 | 7.965 | 1 | 7.965 | 2 | 7.965 | 2
- | Science Lab | 1041 | 69 |  |  | 1436 | 32 | 32 | RTU/UV | 8 | 11488 | 5.437 | 1 | 5.437 | 2 | 5.437 | 2
- | Tech Ed | 1222 | 81 |  |  | 1415 | 32 | 32 | RTU/UV | 8 | 11320 | 6.477 | 1 | 6.477 | 2 | 6.477 | 2
- | Health Suite | 575 | 38 |  |  | 250 | 5 | 5 | RTU/UV | 8 | 2000 | 17.25 | 1 | 17.25 | 3 | 17.25 | 3
- | Conference Rm | 37 | 2 |  |  | 99 | 2 | 2 | RTU/UV | 8 | 792 | 2.803 | 1 | 2.803 | 1 | 2.803 | 1
- | Corridor | 405 | 27 |  |  |  | 0 | 0 | RTU/UV
- | Lounge | 220 | 14 |  |  | 418 | 9 | 9 | RTU/UV | 8 | 3344 | 3.9474 | 1 | 3.9474 | 1 | 3.9474 | 1
- | Refrence Rm | 165 | 11 |  |  | 120 | 2 | 2 | RTU/UV | 8 | 960 | 10.3125 | 1 | 10.3125 | 3 | 10.3125 | 3
- | Boys' Toilet Room | 327 | 21 |  |  | 200 | 4 | 4 | RTU/UV | 8 | 1600 | 12.2625 | 1 | 12.2625 | 3 | 12.2625 | 3
- | Girls' Toilet Room | 227 | 15 |  |  | 140 | 3 | 3 | RTU/UV | 8 | 1120 | 12.1607 | 1 | 12.1607 | 3 | 12.1607 | 3
- | Storage | 190 | 12 |  |  | 156 | 3 | 3 | RTU/UV | 8 | 1248 | 9.1346 | 1 | 9.1346 | 2 | 9.1346 | 2
- | Trash Rm | 160 | 10 |  |  | 213 | 4 | 4 | RTU/UV | 8 | 1704 | 5.6338 | 1 | 5.6338 | 2 | 5.6338 | 2
- | Work Room | 160 | 10 |  |  | 152 | 3 | 3 | RTU/UV | 8 | 1216 | 7.8947 | 1 | 7.8947 | 2 | 7.8947 | 2
- | Workshop | 210 | 14 |  |  | 153 | 3 | 3 | RTU/UV | 8 | 1224 | 10.2941 | 1 | 10.2941 | 3 | 10.2941 | 3
- | Bldg Engineer | 160 | 10 |  |  | 150 | 3 | 3 | RTU/UV | 8 | 1200 | 8 | 1 | 8 | 2 | 8 | 2
- | Gym |  | 0 |  |  | 6809 | 154 | 0 | AHU | 8 | 54472 | 0 | 1.4912 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-13
School: | General Philip Kearny Elementary School
Vendor: | Chadwick | Exhaust Report | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 0 | 0 |  |  | 780 | 17 | 0 | UV | 8 | 6240 | 0 | 1 | 0 | 0 | 0 | 0
2 | classroom | 900 | 60 |  |  | 780 | 17 | 17 | UV | 8 | 6240 | 8.6538 | 1 | 8.6538 | 2 | 8.6538 | 2
3 | classroom | 1129 | 75 |  |  | 780 | 17 | 17 | UV | 8 | 6240 | 10.8558 | 1 | 10.8558 | 3 | 10.8558 | 3
4 | classroom | 1177 | 78 |  |  | 780 | 17 | 17 | UV | 8 | 6240 | 11.3173 | 1 | 11.3173 | 3 | 11.3173 | 3
100 | classroom | 1118 | 74 |  |  | 750 | 17 | 17 | House Fan | 8 | 6000 | 11.18 | 1 | 11.18 | 3 | 11.18 | 3
101 | classroom | 1353 | 90 |  |  | 700 | 15 | 15 | House Fan | 8 | 5600 | 14.4964 | 1 | 14.4964 | 3 | 14.4964 | 3
103 | classroom | 1342 | 89 |  |  | 945 | 21 | 21 | House Fan | 8 | 7560 | 10.6508 | 1 | 10.6508 | 3 | 10.6508 | 3
105 | classroom | 1642 | 109 |  |  | 696 | 15 | 15 | House Fan | 8 | 5568 | 17.694 | 1 | 17.694 | 3 | 17.694 | 3
107 | classroom | 314 | 20 |  |  | 744 | 16 | 16 | House Fan | 8 | 5952 | 3.1653 | 1 | 3.1653 | 1 | 3.1653 | 1
200 | classroom | 1129 | 75 |  |  | 696 | 15 | 15 | House Fan | 8 | 5568 | 12.1659 | 1 | 12.1659 | 3 | 12.1659 | 3
201 | classroom | 1048 | 69 |  |  | 696 | 15 | 15 | House Fan | 8 | 5568 | 11.2931 | 1 | 11.2931 | 3 | 11.2931 | 3
202 | classroom | 1034 | 68 |  |  | 783 | 17 | 17 | House Fan | 8 | 6264 | 9.9042 | 1 | 9.9042 | 2 | 9.9042 | 2
203 | classroom | 1345 | 89 |  |  | 810 | 18 | 18 | House Fan | 8 | 6480 | 12.4537 | 1 | 12.4537 | 3 | 12.4537 | 3
204 | classroom | 1224 | 81 |  |  | 324 | 7 | 7 | House Fan | 8 | 2592 | 28.3333 | 1 | 28.3333 | 4 | 28.3333 | 4
207 | classroom | 1653 | 110 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 16.1426 | 1 | 16.1426 | 3 | 16.1426 | 3
300 | classroom | 1129 | 75 |  |  | 672 | 15 | 15 | House Fan | 8 | 5376 | 12.6004 | 1 | 12.6004 | 3 | 12.6004 | 3
301 | classroom | 990 | 66 |  |  | 725 | 16 | 16 | House Fan | 8 | 5800 | 10.2414 | 1 | 10.2414 | 3 | 10.2414 | 3
302 | classroom | 623 | 41 |  |  | 783 | 17 | 17 | House Fan | 8 | 6264 | 5.9674 | 1 | 5.9674 | 2 | 5.9674 | 2
303 | classroom | 986 | 65 |  |  | 810 | 18 | 18 | House Fan | 8 | 6480 | 9.1296 | 1 | 9.1296 | 2 | 9.1296 | 2
305 | classroom | 1268 | 84 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 13.2083 | 1 | 13.2083 | 3 | 13.2083 | 3
306 | classroom | 1338 | 89 |  |  | 414 | 9 | 9 | House Fan | 8 | 3312 | 24.2391 | 1 | 24.2391 | 4 | 24.2391 | 4
307 | classroom | 1067 | 71 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 10.4199 | 1 | 10.4199 | 3 | 10.4199 | 3
308 | classroom | 931 | 62 |  |  | 675 | 15 | 15 | House Fan | 8 | 5400 | 10.3444 | 1 | 10.3444 | 3 | 10.3444 | 3
309 | classroom | 1059 | 70 |  |  | 675 | 15 | 15 | House Fan | 8 | 5400 | 11.7667 | 1 | 11.7667 | 3 | 11.7667 | 3
310 | classroom | 1114 | 74 |  |  | 675 | 15 | 15 | House Fan | 8 | 5400 | 12.3778 | 1 | 12.3778 | 3 | 12.3778 | 3
311 | classroom | 1191 | 79 |  |  | 675 | 15 | 15 | House Fan | 8 | 5400 | 13.2333 | 1 | 13.2333 | 3 | 13.2333 | 3
312 | classroom | 924 | 61 |  |  | 414 | 9 | 9 | House Fan | 8 | 3312 | 16.7391 | 1 | 16.7391 | 3 | 16.7391 | 3
312 | classroom | 1529 | 101 |  |  | 414 | 9 | 9 | House Fan | 8 | 3312 | 27.6993 | 1 | 27.6993 | 4 | 27.6993 | 4
315 | classroom | 1386 | 92 |  |  | 702 | 15 | 15 | House Fan | 8 | 5616 | 14.8077 | 1 | 14.8077 | 3 | 14.8077 | 3
- | Gym | 9069 | 604 |  |  | 6100 | 138 | 138 | RTU | 8 | 48800 | 11.1504 | 1.062 | 11.8421 | 3 | 11.8421 | 3
- | Main office |  | 0 | Yes | 20 | 340 | 7 | 7 | House Fan | 8 | 2720 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal office |  | 0 | Yes | 20 | 320 | 7 | 7 | House Fan | 8 | 2560 | 0 | 1 | 0 | 0 | 20 | 3
| Cafeteria |  | 0 | Yes | 20 | 3240 | 73 | 73 |  | 8 | 25920 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Auditorium |  | 0 |  |  | 3240 | 73 | 0 | House Fan | 8 | 25920 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Faculty |  | 0 |  |  | 336 | 7 | 0 |  | 8 | 2688 | 0 | 1 | 0 | 0 | 0 | 0
- | Kitchen |  | 0 |  |  | 700 | 15 | 0 | House Fan | 8 | 5600 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurse |  | 0 | Yes | 20 | 171 | 3 | 3 | House Fan | 8 | 1368 | 0 | 1 | 0 | 0 | 20 | 3
- | Lunchroom |  | 0 | Yes | 20 | 3078 | 69 | 69 | House Fan | 8 | 24624 | 0 | 1.062 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-22
School: | William D. Kelley Elementary School
Vendor: | Devine Brothers | Devine Part 2
| Devine Part 3 | Devine Part 4
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 315 | 21 |  |  | 1053 | 23 | 21 | UV | 8 | 8424 | 2.2436 | 1 | 2.2436 | 1 | 2.2436 | 1
102 | Classroom | 322 | 21 |  |  | 880 | 20 | 20 | UV | 8 | 7040 | 2.7443 | 1 | 2.7443 | 1 | 2.7443 | 1
103 | Classroom | 319 | 21 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.2551 | 1 | 3.2551 | 1 | 3.2551 | 1
104 | Classroom | 318 | 21 |  |  | 805 | 18 | 18 | UV | 8 | 6440 | 2.9627 | 1 | 2.9627 | 1 | 2.9627 | 1
104B | Classroom | 301 | 20 |  |  | 870 | 19 | 19 | UV | 8 | 6960 | 2.5948 | 1 | 2.5948 | 1 | 2.5948 | 1
105 | Classroom | 357 | 23 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.6429 | 1 | 3.6429 | 1 | 3.6429 | 1
106 | Classroom | 395 | 26 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 4.0306 | 1 | 4.0306 | 2 | 4.0306 | 2
108 | Classroom | 376 | 25 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.8367 | 1 | 3.8367 | 1 | 3.8367 | 1
109 | Classroom | 302 | 20 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.0816 | 1 | 3.0816 | 1 | 3.0816 | 1
110 | Classroom | 321 | 21 |  |  | 442 | 10 | 10 | UV | 8 | 3536 | 5.4468 | 1 | 5.4468 | 2 | 5.4468 | 2
111 | Classroom | 339 | 22 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.4592 | 1 | 3.4592 | 1 | 3.4592 | 1
200 | Classroom | 357 | 23 |  |  | 700 | 15 | 15 | UV | 8 | 5600 | 3.825 | 1 | 3.825 | 1 | 3.825 | 1
201 | Classroom | 302 | 20 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 3.1458 | 1 | 3.1458 | 1 | 3.1458 | 1
202 | Classroom | 330 | 22 |  |  | 770 | 17 | 17 | UV | 8 | 6160 | 3.2143 | 1 | 3.2143 | 1 | 3.2143 | 1
203 | Classroom | 314 | 20 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.2041 | 1 | 3.2041 | 1 | 3.2041 | 1
204 | Classroom | 355 | 23 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.6224 | 1 | 3.6224 | 1 | 3.6224 | 1
205 | Classroom | 344 | 22 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.5102 | 1 | 3.5102 | 1 | 3.5102 | 1
206 | Classroom | 284 | 18 |  |  | 406 | 9 | 9 | UV | 8 | 3248 | 5.2463 | 1 | 5.2463 | 2 | 5.2463 | 2
207 | Classroom | 332 | 22 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.3878 | 1 | 3.3878 | 1 | 3.3878 | 1
208 | IMC | 302 | 20 |  |  | 1540 | 35 | 20 | UV | 8 | 12320 | 1.4708 | 1 | 1.4708 | 1 | 1.4708 | 1
209 | Classroom | 341 | 22 |  |  | 770 | 17 | 17 | UV | 8 | 6160 | 3.3214 | 1 | 3.3214 | 1 | 3.3214 | 1
210 | IMC | 323 | 21 |  |  | 1540 | 35 | 21 | UV | 8 | 12320 | 1.5731 | 1 | 1.5731 | 1 | 1.5731 | 1
211 | Classroom | 307 | 20 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.1327 | 1 | 3.1327 | 1 | 3.1327 | 1
212 | Classroom | 305 | 20 |  |  | 510 | 11 | 11 | UV | 8 | 4080 | 4.4853 | 1 | 4.4853 | 2 | 4.4853 | 2
214 | Classroom | 339 | 22 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.4592 | 1 | 3.4592 | 1 | 3.4592 | 1
216 | Classroom | 330 | 22 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.3673 | 1 | 3.3673 | 1 | 3.3673 | 1
218 | Classroom | 180 | 12 |  |  | 143 | 3 | 3 | UV | 8 | 1144 | 9.4406 | 1 | 9.4406 | 2 | 9.4406 | 2
300 | Classroom | 311 | 20 |  |  | 700 | 15 | 15 | UV | 8 | 5600 | 3.3321 | 1 | 3.3321 | 1 | 3.3321 | 1
301 | Classroom | 320 | 21 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 3.3333 | 1 | 3.3333 | 1 | 3.3333 | 1
302 | Classroom | 416 | 27 |  |  | 770 | 17 | 17 | UV | 8 | 6160 | 4.0519 | 1 | 4.0519 | 2 | 4.0519 | 2
303 | Classroom | 380 | 25 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.8776 | 1 | 3.8776 | 1 | 3.8776 | 1
304 | Classroom | 305 | 20 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.1122 | 1 | 3.1122 | 1 | 3.1122 | 1
306 | Classroom | 281 | 18 |  |  | 406 | 9 | 9 | UV | 8 | 3248 | 5.1909 | 1 | 5.1909 | 2 | 5.1909 | 2
307 | Classroom | 292 | 19 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 2.9796 | 1 | 2.9796 | 1 | 2.9796 | 1
308 | Classroom | 385 | 25 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.9286 | 1 | 3.9286 | 1 | 3.9286 | 1
309 | Classroom | 318 | 21 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.2449 | 1 | 3.2449 | 1 | 3.2449 | 1
310 | Classroom | 163 | 10 | Yes | 20 | 735 | 16 | 16 | UV | 8 | 5880 | 1.6633 | 1 | 1.6633 | 1 | 21.6633 | 3
311 | Classroom | 334 | 22 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.4082 | 1 | 3.4082 | 1 | 3.4082 | 1
312 | Classroom | 275 | 18 |  |  | 510 | 11 | 11 | UV | 8 | 4080 | 4.0441 | 1 | 4.0441 | 2 | 4.0441 | 2
314 | Classroom | 325 | 21 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.3163 | 1 | 3.3163 | 1 | 3.3163 | 1
316 | Classroom | 302 | 20 |  |  | 735 | 16 | 16 | UV | 8 | 5880 | 3.0816 | 1 | 3.0816 | 1 | 3.0816 | 1
318 | Classroom | 181 | 12 |  |  | 143 | 3 | 3 | UV | 8 | 1144 | 9.493 | 1 | 9.493 | 2 | 9.493 | 2
- | Auditorium | 1841 | 122 |  |  | 4278 | 97 | 97 | AHU | 8 | 34224 | 3.2276 | 1.062 | 3.4278 | 1 | 3.4278 | 1
- | Gymnasium | 899 | 59 |  |  | 3588 | 81 | 59 | AHU | 8 | 28704 | 1.8792 | 1.062 | 1.9958 | 1 | 1.9958 | 1
- | Library | 625 | 41 |  |  | 1540 | 35 | 35 | UV | 8 | 12320 | 3.0438 | 1 | 3.0438 | 1 | 3.0438 | 1
- | Main Office | 101 | 6 | Yes | 20 | 483 | 10 | 10 | AHU | 8 | 3864 | 1.5683 | 1 | 1.5683 | 1 | 21.5683 | 3
- | Nurse Office | 84 | 5 | Yes | 20 | 368 | 8 | 8 |  | 8 | 2944 | 1.712 | 1 | 1.712 | 1 | 21.712 | 3
- | Admin Asst. Office | 38 | 2 |  |  | 99 | 2 | 2 |  | 8 | 792 | 2.8788 | 1 | 2.8788 | 1 | 2.8788 | 1
- | Principal's Office | 41 | 2 |  |  | 315 | 7 | 2 |  | 8 | 2520 | 0.97619 | 1 | 0.97619 | 0 | 0.97619 | 0
- | Conference/Office | 90 | 6 |  |  | 384 | 8 | 6 |  | 8 | 3072 | 1.7578 | 1 | 1.7578 | 1 | 1.7578 | 1
- | Counselor's Office | 0 | 0 |  |  | 442 | 10 | 0 |  | 8 | 3536 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30
School: | John B. Kelly Elementary School
Vendor: | Capital
Vendor: | Devine Brothers | Retest | 2nd Retest
| Devine 3rd Retest | Devine 4th Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Teachers Dining | 340 | 22 |  |  | 868 | 19 | 19 | UV | 8 | 6944 | 2.9378 | 1 | 2.9378 | 1 | 2.9378 | 1
102 | Classroom | 497 | 33 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 4.3853 | 1 | 4.3853 | 2 | 4.3853 | 2
102A | Classroom | 155 | 10 |  |  | 550 | 12 | 10 | UV | 8 | 4400 | 2.1136 | 1 | 2.1136 | 1 | 2.1136 | 1
103 | Classroom | 673 | 44 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 5.9382 | 1 | 5.9382 | 2 | 5.9382 | 2
103A | Classroom | 216 | 14 |  |  | 550 | 12 | 12 | UV | 8 | 4400 | 2.9455 | 1 | 2.9455 | 1 | 2.9455 | 1
104 | Classroom | 607 | 40 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 5.3559 | 1 | 5.3559 | 2 | 5.3559 | 2
105 | Classroom | 592 | 39 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 5.2235 | 1 | 5.2235 | 2 | 5.2235 | 2
106 | Classroom | 576 | 38 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 5.0824 | 1 | 5.0824 | 2 | 5.0824 | 2
107 | Classroom | 572 | 38 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 5.0471 | 1 | 5.0471 | 2 | 5.0471 | 2
108 | Classroom | 576 | 38 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 5.0824 | 1 | 5.0824 | 2 | 5.0824 | 2
109 | Classroom | 539 | 35 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 4.7559 | 1 | 4.7559 | 2 | 4.7559 | 2
110 | Classroom | 434 | 28 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 3.8294 | 1 | 3.8294 | 1 | 3.8294 | 1
111 | Classroom | 336 | 22 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 2.9647 | 1 | 2.9647 | 1 | 2.9647 | 1
112 | Classroom | 627 | 41 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 5.5324 | 1 | 5.5324 | 2 | 5.5324 | 2
113 | Classroom | 320 | 21 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 2.8235 | 1 | 2.8235 | 1 | 2.8235 | 1
114 | Classroom | 534 | 35 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 4.7118 | 1 | 4.7118 | 2 | 4.7118 | 2
160 | Classroom | 305 | 20 |  |  | 942 | 21 | 20 | UV | 8 | 7536 | 2.4283 | 1 | 2.4283 | 1 | 2.4283 | 1
160 | Main Office | 182 | 12 |  |  | 232 | 5 | 5 | UV | 8 | 1856 | 5.8836 | 1 | 5.8836 | 2 | 5.8836 | 2
201 | Classroom | 370 | 24 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 3.2647 | 1 | 3.2647 | 1 | 3.2647 | 1
202 | Classroom | 494 | 32 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 4.3588 | 1 | 4.3588 | 2 | 4.3588 | 2
202A | Office | 33 | 2 |  |  | 140 | 3 | 2 | UV | 8 | 1120 | 1.7679 | 1 | 1.7679 | 1 | 1.7679 | 1
203 | Classroom | 744 | 49 |  |  | 1088 | 24 | 24 | UV | 8 | 8704 | 5.1287 | 1 | 5.1287 | 2 | 5.1287 | 2
204 | Classroom | 609 | 40 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 5.3735 | 1 | 5.3735 | 2 | 5.3735 | 2
204A | Classroom | 282 | 18 |  |  | 550 | 12 | 12 | UV | 8 | 4400 | 3.8455 | 1 | 3.8455 | 1 | 3.8455 | 1
205 | Classroom | 327 | 21 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 2.8853 | 1 | 2.8853 | 1 | 2.8853 | 1
205A | Classroom | 293 | 19 |  |  | 550 | 12 | 12 | UV | 8 | 4400 | 3.9955 | 1 | 3.9955 | 1 | 3.9955 | 1
206 | Classroom | 284 | 18 |  |  | 1088 | 24 | 18 | UV | 8 | 8704 | 1.9577 | 1 | 1.9577 | 1 | 1.9577 | 1
207 | Classroom | 468 | 31 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 4.1294 | 1 | 4.1294 | 2 | 4.1294 | 2
208 | Classroom | 586 | 39 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 5.1706 | 1 | 5.1706 | 2 | 5.1706 | 2
209 | Classroom | 381 | 25 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 3.3618 | 1 | 3.3618 | 1 | 3.3618 | 1
210 | Classroom | 341 | 22 |  |  | 1088 | 24 | 22 | UV | 8 | 8704 | 2.3506 | 1 | 2.3506 | 1 | 2.3506 | 1
210A | Office | 188 | 12 |  |  | 136 | 3 | 3 | UV | 8 | 1088 | 10.3676 | 1 | 10.3676 | 3 | 10.3676 | 3
211 | Classroom | 530 | 35 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 4.6765 | 1 | 4.6765 | 2 | 4.6765 | 2
212 | Classroom | 729 | 48 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 6.4324 | 1 | 6.4324 | 2 | 6.4324 | 2
212A | Classroom | 289 | 19 |  |  | 550 | 12 | 12 | UV | 8 | 4400 | 3.9409 | 1 | 3.9409 | 1 | 3.9409 | 1
213 | Classroom | 661 | 44 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 5.8324 | 1 | 5.8324 | 2 | 5.8324 | 2
213A | Classroom | 233 | 15 |  |  | 550 | 12 | 12 | UV | 8 | 4400 | 3.1773 | 1 | 3.1773 | 1 | 3.1773 | 1
214 | Classroom | 588 | 39 |  |  | 1088 | 24 | 24 | UV | 8 | 8704 | 4.0533 | 1 | 4.0533 | 2 | 4.0533 | 2
215 | Classroom | 341 | 22 |  |  | 676 | 15 | 15 | UV | 8 | 5408 | 3.7833 | 1 | 3.7833 | 1 | 3.7833 | 1
216 | Classroom | 425 | 28 |  |  | 850 | 19 | 19 | UV | 8 | 6800 | 3.75 | 1 | 3.75 | 1 | 3.75 | 1
217 East | Classroom | 294 | 19 |  |  | 1006 | 22 | 19 | UV | 8 | 8048 | 2.1918 | 1 | 2.1918 | 1 | 2.1918 | 1
217 North | Classroom | 227 | 15 |  |  | 1093 | 24 | 15 | UV | 8 | 8744 | 1.5576 | 1 | 1.5576 | 1 | 1.5576 | 1
217 South Center | Classroom | 382 | 25 |  |  | 1069 | 24 | 24 | UV | 8 | 8552 | 2.6801 | 1 | 2.6801 | 1 | 2.6801 | 1
217 West Center | Classroom | 285 | 19 |  |  | 1093 | 24 | 19 | UV | 8 | 8744 | 1.9556 | 1 | 1.9556 | 1 | 1.9556 | 1
- | Admin/Asst. Office | 66 | 4 |  |  | 179 | 4 | 4 | UV | 8 | 1432 | 2.7654 | 1 | 2.7654 | 1 | 2.7654 | 1
- | Administration Offices | 1305 | 87 |  |  | 535 | 12 | 12 | UV | 8 | 4280 | 18.2944 | 1 | 18.2944 | 3 | 18.2944 | 3
ART | Art Classroom | 731 | 48 |  |  | 1350 | 30 | 30 | UV | 8 | 10800 | 4.0611 | 1 | 4.0611 | 2 | 4.0611 | 2
ART -A | Art Classroom | 401 | 26 |  |  |  | 0 | 0 | UV
ART -B | Art Classroom | 557 | 37 |  |  |  | 0 | 0 | UV
ART -C | Art Classroom | 111 | 7 |  |  |  | 0 | 0 | UV
ART -D | Art Classroom | 318 | 21 |  |  |  | 0 | 0 | UV
- | Auditorium | 1721 | 114 |  |  | 6080 | 138 | 114 | UV | 8 | 48640 | 2.1229 | 1.062 | 2.2546 | 1 | 2.2546 | 1
- | 1st Flr A-Wing Left Boys Bathroom | 53 | 3 |  |  | 88 | 2 | 2 | AHU | 8 | 704 | 4.517 | 1 | 4.517 | 2 | 4.517 | 2
- | 2nd Flr A-Wing Left Boys Bathroom | 101 | 6 |  |  | 96 | 2 | 2 | AHU | 8 | 768 | 7.8906 | 1 | 7.8906 | 2 | 7.8906 | 2
- | 2nd Flr A-Wing Right Boys Bathroom | 43 | 2 |  |  | 103 | 2 | 2 | AHU | 8 | 824 | 3.1311 | 1 | 3.1311 | 1 | 3.1311 | 1
- | Conference Room | 139 | 9 |  |  | 211 | 4 | 4 | AHU | 8 | 1688 | 4.9408 | 1 | 4.9408 | 2 | 4.9408 | 2
- | Copy/Storage Room | 110 | 7 |  |  | 165 | 3 | 3 | AHU | 8 | 1320 | 5 | 1 | 5 | 2 | 5 | 2
- | Corridor | 41 | 2 |  |  |  | 0 | 0 | AHU
- | Counselor Office | 58 | 3 |  |  | 123 | 2 | 2 | AHU | 8 | 984 | 3.5366 | 1 | 3.5366 | 1 | 3.5366 | 1
- | Dressing - A Backstage | 307 | 20 |  |  | 232 | 5 | 5 | UV | 8 | 1856 | 9.9246 | 1 | 9.9246 | 2 | 9.9246 | 2
- | Dressing - B Backstage | 461 | 30 |  |  | 196 | 4 | 4 | UV | 8 | 1568 | 17.6403 | 1 | 17.6403 | 3 | 17.6403 | 3
- | Dressing - C Backstage | 493 | 32 |  |  | 190 | 4 | 4 | UV | 8 | 1520 | 19.4605 | 1 | 19.4605 | 3 | 19.4605 | 3
- | Dressing - D Backstage | 275 | 18 |  |  | 199 | 4 | 4 | UV | 8 | 1592 | 10.3643 | 1 | 10.3643 | 3 | 10.3643 | 3
- | 1st Flr A-Wing Left Girls Bathroom | 41 | 2 |  |  | 109 | 2 | 2 | AHU | 8 | 872 | 2.8211 | 1 | 2.8211 | 1 | 2.8211 | 1
- | 2nd Flr A-Wing Left Girls Bathroom | 78 | 5 |  |  | 106 | 2 | 2 | AHU | 8 | 848 | 5.5189 | 1 | 5.5189 | 2 | 5.5189 | 2
- | 2nd Flr A-Wing Right Girls Bathroom | 54 | 3 |  |  | 103 | 2 | 2 | AHU | 8 | 824 | 3.932 | 1 | 3.932 | 1 | 3.932 | 1
- | IMC | 0 | 0 |  |  | 8471 | 192 | 0 | AHU | 8 | 67768 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | IMC North Side | 947 | 63 |  |  | 480 | 10 | 10 | AHU | 8 | 3840 | 14.7969 | 1 | 14.7969 | 3 | 14.7969 | 3
- | IMC South Side | 822 | 54 |  |  | 480 | 10 | 10 | AHU | 8 | 3840 | 12.8438 | 1 | 12.8438 | 3 | 12.8438 | 3
- | IMC Entry from Office | 0 | 0 |  |  |  | 0 | 0 | AHU
- | IMC Entry to Hall | 0 | 0 |  |  |  | 0 | 0 | AHU
- | IMC-1 Office | 80 | 5 |  |  | 293 | 6 | 5 | AHU | 8 | 2344 | 2.0478 | 1 | 2.0478 | 1 | 2.0478 | 1
- | IMC-2 Storage | 151 | 10 |  |  | 330 | 7 | 7 | AHU | 8 | 2640 | 3.4318 | 1 | 3.4318 | 1 | 3.4318 | 1
- | IMC-4 Storage | 175 | 11 |  |  | 372 | 8 | 8 | AHU | 8 | 2976 | 3.5282 | 1 | 3.5282 | 1 | 3.5282 | 1
- | IMC-5 Data/Storage | 68 | 4 |  |  | 277 | 6 | 4 | AHU | 8 | 2216 | 1.8412 | 1 | 1.8412 | 1 | 1.8412 | 1
- | Cafeteria | 0 | 0 |  |  | 1195 | 27 | 0 | AHU | 8 | 9560 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria | 1928 | 128 |  |  | 4807 | 109 | 109 | AHU | 8 | 38456 | 3.0081 | 1.062 | 3.1947 | 1 | 3.1947 | 1
- | Gym | 2934 | 195 |  |  | 387 | 8 | 8 | AHU | 8 | 3096 | 56.8605 | 1 | 56.8605 | 5 | 56.8605 | 5
- | Music Classroom A | 326 | 21 |  |  |  | 0 | 0 | UV
- | Music Classroom B | 555 | 37 |  |  |  | 0 | 0 | UV
- | Music Classroom C | 152 | 10 |  |  |  | 0 | 0 | UV
- | Music Classroom D | 106 | 7 |  |  |  | 0 | 0 | UV
- | Main Music Classroom | 463 | 30 |  |  | 380 | 8 | 8 | UV | 8 | 3040 | 9.1382 | 1 | 9.1382 | 2 | 9.1382 | 2
- | Music Office | 136 | 9 |  |  | 355 | 8 | 8 | AHU | 8 | 2840 | 2.8732 | 1 | 2.8732 | 1 | 2.8732 | 1
- | Nurse Exam Room | 0 | 0 |  |  | 209 | 4 | 0 | AHU | 8 | 1672 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurse Exam Room | 43 | 2 |  |  |  | 0 | 0 | AHU
- | Nurses Office | 0 | 0 |  |  |  | 0 | 0 | AHU
- | Nurses Rest | 68 | 4 |  |  |  | 0 | 0 | AHU
- | Nurses Suite | 411 | 27 |  |  |  | 0 | 0 | UV
- | Aud & Dental | 31 | 2 |  |  | 270 | 6 | 2 | AHU | 8 | 2160 | 0.86111 | 1 | 0.86111 | 0 | 0.86111 | 0
- | Principals Office | 98 | 6 |  |  | 270 | 6 | 6 | AHU | 8 | 2160 | 2.7222 | 1 | 2.7222 | 1 | 2.7222 | 1
- | Speech/Com | 388 | 25 |  |  | 736 | 16 | 16 | UV | 8 | 5888 | 3.9538 | 1 | 3.9538 | 1 | 3.9538 | 1
- | Server Room | 55 | 3 |  |  | 121 | 2 | 2 | Split System | 8 | 968 | 3.4091 | 1 | 3.4091 | 1 | 3.4091 | 1
- | Storage | 247 | 16 |  |  | 809 | 18 | 16 | AHU | 8 | 6472 | 2.2899 | 1 | 2.2899 | 1 | 2.2899 | 1
- | Office / Waiting Room | 277 | 18 |  |  |  | 0 | 0 | AHU
K - 1 | Kindergarten | 452 | 30 |  |  | 1488 | 33 | 30 | UV | 8 | 11904 | 2.2782 | 1 | 2.2782 | 1 | 2.2782 | 1
K - 2 | Kindergarten | 490 | 32 |  |  | 1488 | 33 | 32 | UV | 8 | 11904 | 2.4698 | 1 | 2.4698 | 1 | 2.4698 | 1
K - 3 | Kindergarten | 498 | 33 |  |  | 1488 | 33 | 33 | UV | 8 | 11904 | 2.5101 | 1 | 2.5101 | 1 | 2.5101 | 1
K - 4 | Kindergarten | 635 | 42 |  |  | 1488 | 33 | 33 | UV | 8 | 11904 | 3.2006 | 1 | 3.2006 | 1 | 3.2006 | 1
K - 5 | Kindergarten | 280 | 18 |  |  | 1488 | 33 | 18 | UV | 8 | 11904 | 1.4113 | 1 | 1.4113 | 1 | 1.4113 | 1
K - 6 | Kindergarten | 300 | 20 |  |  | 1488 | 33 | 20 | UV | 8 | 11904 | 1.5121 | 1 | 1.5121 | 1 | 1.5121 | 1
Sheet Last Modified: | 2021-04-23
School: | Kenderton Elementary School
Vendor: | Chadwick | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 229 | 15 |  |  | 1012 | 23 | 15 | UV | 8 | 8096 | 1.6971 | 1 | 1.6971 | 1 | 1.6971 | 1
101 | Classroom | 451 | 30 |  |  | 1680 | 38 | 30 | UV | 8 | 13440 | 2.0134 | 1 | 2.0134 | 1 | 2.0134 | 1
102 | Classroom | 458 | 30 |  |  | 1652 | 37 | 30 | UV | 8 | 13216 | 2.0793 | 1 | 2.0793 | 1 | 2.0793 | 1
103 | Classroom | 331 | 22 | Yes | 20 | 1344 | 30 | 30 | UV | 8 | 10752 | 1.8471 | 1 | 1.8471 | 1 | 21.8471 | 3
104 | Nurse |  | 0 | Yes | 20 | 275 | 6 | 6 |  | 8 | 2200 | 0 | 1 | 0 | 0 | 20 | 3
200A | Classroom | 198 | 13 |  |  | 442 | 10 | 10 | UV | 8 | 3536 | 3.3597 | 1 | 3.3597 | 1 | 3.3597 | 1
200 | Classroom | 0 | 0 |  |  | 891 | 20 | 0 | UV | 8 | 7128 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom | 278 | 18 | Yes | 20 | 891 | 20 | 20 | UV | 8 | 7128 | 2.3401 | 1 | 2.3401 | 1 | 22.3401 | 3
202 | Classroom | 331 | 22 |  |  | 918 | 20 | 20 | UV | 8 | 7344 | 2.7042 | 1 | 2.7042 | 1 | 2.7042 | 1
203 | Classroom | 297 | 19 |  |  | 980 | 22 | 19 | UV | 8 | 7840 | 2.273 | 1 | 2.273 | 1 | 2.273 | 1
204 | Classroom | 302 | 20 |  |  | 918 | 20 | 20 | UV | 8 | 7344 | 2.4673 | 1 | 2.4673 | 1 | 2.4673 | 1
205 | Classroom | 198 | 13 |  |  | 918 | 20 | 13 | UV | 8 | 7344 | 1.6176 | 1 | 1.6176 | 1 | 1.6176 | 1
206 | Classroom | 273 | 18 |  |  | 616 | 14 | 14 | UV | 8 | 4928 | 3.3239 | 1 | 3.3239 | 1 | 3.3239 | 1
207 | Classroom | 273 | 18 |  |  | 918 | 20 | 18 | UV | 8 | 7344 | 2.2304 | 1 | 2.2304 | 1 | 2.2304 | 1
208 | Classroom | 191 | 12 | Yes | 20 | 120 | 2 | 2 | UV | 8 | 960 | 11.9375 | 1 | 11.9375 | 3 | 31.9375 | 4
209 | Classroom | 283 | 18 |  |  | 918 | 20 | 18 | UV | 8 | 7344 | 2.3121 | 1 | 2.3121 | 1 | 2.3121 | 1
211 | Classroom | 276 | 18 |  |  | 286 | 6 | 6 | UV | 8 | 2288 | 7.2378 | 1 | 7.2378 | 2 | 7.2378 | 2
213 | Classroom | 271 | 18 |  |  | 918 | 20 | 18 | UV | 8 | 7344 | 2.2141 | 1 | 2.2141 | 1 | 2.2141 | 1
300 | Classroom | 278 | 18 | Yes | 20 | 918 | 20 | 20 | UV | 8 | 7344 | 2.2712 | 1 | 2.2712 | 1 | 22.2712 | 3
301 | Classroom | 271 | 18 |  |  | 918 | 20 | 18 | UV | 8 | 7344 | 2.2141 | 1 | 2.2141 | 1 | 2.2141 | 1
302 | Classroom | 272 | 18 | Yes | 20 | 918 | 20 | 20 | UV | 8 | 7344 | 2.2222 | 1 | 2.2222 | 1 | 22.2222 | 3
303 | Classroom | 296 | 19 |  |  | 980 | 22 | 19 | UV | 8 | 7840 | 2.2653 | 1 | 2.2653 | 1 | 2.2653 | 1
304 | Classroom | 276 | 18 |  |  | 864 | 19 | 18 | UV | 8 | 6912 | 2.3958 | 1 | 2.3958 | 1 | 2.3958 | 1
306 | Classroom | 316 | 21 |  |  | 918 | 20 | 20 | UV | 8 | 7344 | 2.5817 | 1 | 2.5817 | 1 | 2.5817 | 1
307 | Classroom | 281 | 18 | Yes | 20 | 924 | 21 | 21 | UV | 8 | 7392 | 2.2808 | 1 | 2.2808 | 1 | 22.2808 | 3
308 | Classroom | 0 | 0 | Yes | 20 | 924 | 21 | 21 | UV | 8 | 7392 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 |  |  | 980 | 22 | 0 | UV | 8 | 7840 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom | 0 | 0 | Yes | 20 | 616 | 14 | 14 | UV | 8 | 4928 | 0 | 1 | 0 | 0 | 20 | 3
311 | Classroom | 0 | 0 | Yes | 20 | 918 | 20 | 20 | UV | 8 | 7344 | 0 | 1 | 0 | 0 | 20 | 3
312 | Computer Room |  | 0 | Yes | 20 | 860 | 19 | 19 |  | 8 | 6880 | 0 | 1 | 0 | 0 | 20 | 3
313 | Classroom | 0 | 0 | Yes | 20 | 918 | 20 | 20 | UV | 8 | 7344 | 0 | 1 | 0 | 0 | 20 | 3
314 | Classroom | 0 | 0 |  |  | 280 | 6 | 0 | UV | 8 | 2240 | 0 | 1 | 0 | 0 | 0 | 0
315 | Classroom | 0 | 0 | Yes | 20 | 918 | 20 | 20 | UV | 8 | 7344 | 0 | 1 | 0 | 0 | 20 | 3
316 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | UV | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
319 | Classroom | 0 | 0 |  |  | 918 | 20 | 0 | UV | 8 | 7344 | 0 | 1 | 0 | 0 | 0 | 0
400 | Classroom | 286 | 19 |  |  | 2660 | 60 | 19 | UV | 8 | 21280 | 0.80639 | 1.062 | 0.85642 | 0 | 0.85642 | 0
401 | Classroom | 279 | 18 |  |  | 918 | 20 | 18 | UV | 8 | 7344 | 2.2794 | 1 | 2.2794 | 1 | 2.2794 | 1
402 | Classroom | 313 | 20 |  |  | 918 | 20 | 20 | UV | 8 | 7344 | 2.5572 | 1 | 2.5572 | 1 | 2.5572 | 1
403 | Classroom | 340 | 22 |  |  | 918 | 20 | 20 | UV | 8 | 7344 | 2.7778 | 1 | 2.7778 | 1 | 2.7778 | 1
404 | Classroom | 0 | 0 |  |  | 868 | 19 | 0 | UV | 8 | 6944 | 0 | 1 | 0 | 0 | 0 | 0
406 | Classroom | 291 | 19 |  |  | 918 | 20 | 19 | UV | 8 | 7344 | 2.3775 | 1 | 2.3775 | 1 | 2.3775 | 1
407 | Classroom | 0 | 0 | Yes | 20 | 924 | 21 | 21 | UV | 8 | 7392 | 0 | 1 | 0 | 0 | 20 | 3
408 | Classroom | 0 | 0 | Yes | 20 | 918 | 20 | 20 | UV | 8 | 7344 | 0 | 1 | 0 | 0 | 20 | 3
409 | Classroom | 0 | 0 | Yes | 20 | 980 | 22 | 22 | UV | 8 | 7840 | 0 | 1 | 0 | 0 | 20 | 3
410 | Classroom | 335 | 22 | Yes | 20 | 644 | 14 | 14 | UV | 8 | 5152 | 3.9014 | 1 | 3.9014 | 1 | 23.9014 | 3
411 | Classroom | 0 | 0 |  |  | 918 | 20 | 0 | UV | 8 | 7344 | 0 | 1 | 0 | 0 | 0 | 0
412 | Classroom | 276 | 18 |  |  | 308 | 7 | 7 | UV | 8 | 2464 | 6.7208 | 1 | 6.7208 | 2 | 6.7208 | 2
413 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | UV | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
414 | Classroom | 0 | 0 | Yes | 20 | 270 | 6 | 6 | UV | 8 | 2160 | 0 | 1 | 0 | 0 | 20 | 3
415 | Classroom | 0 | 0 |  |  | 918 | 20 | 0 | UV | 8 | 7344 | 0 | 1 | 0 | 0 | 0 | 0
- | Parent Resource | 0 | 0 |  |  | 2 | 0 | 0 | UV | 8 | 16 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office | 42 | 2 |  |  | 406 | 9 | 2 | UV | 8 | 3248 | 0.77586 | 1 | 0.77586 | 0 | 0.77586 | 0
- | Principal's Office |  | 0 |  |  | 320 | 7 | 0 |  | 8 | 2560 | 0 | 1 | 0 | 0 | 0 | 0
- | Asist Prince | 172 | 11 |  |  | 11 | 0 | 0 | UV | 8 | 88 | 117.2727 | 1 | 117.2727 | 5 | 117.2727 | 5
Sheet Last Modified: | 2021-04-19
School: | Kensington High School | House fan Abated
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | - |  | 0 |  |  | 675 | 15 | 0 |  | 8 | 5400 | 0 | 1 | 0 | 0 | 0 | 0
2 | - |  | 0 |  |  | 1014 | 23 | 0 |  | 8 | 8112 | 0 | 1 | 0 | 0 | 0 | 0
3 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
4 | - |  | 0 |  |  | 364 | 8 | 0 |  | 8 | 2912 | 0 | 1 | 0 | 0 | 0 | 0
5 | - |  | 0 |  |  | 850 | 19 | 0 |  | 8 | 6800 | 0 | 1 | 0 | 0 | 0 | 0
100 | Main Office |  | 0 |  |  | 1014 | 23 | 0 |  | 8 | 8112 | 0 | 1 | 0 | 0 | 0 | 0
102 | - |  | 0 | Yes | 20 | 800 | 18 | 18 |  | 8 | 6400 | 0 | 1 | 0 | 0 | 20 | 3
103 | IMC |  | 0 |  |  | 1690 | 38 | 0 |  | 8 | 13520 | 0 | 1 | 0 | 0 | 0 | 0
104 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
105 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
107 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
108 | - |  | 0 |  |  | 962 | 21 | 0 |  | 8 | 7696 | 0 | 1 | 0 | 0 | 0 | 0
109 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
111 | - |  | 0 |  |  | 910 | 20 | 0 |  | 8 | 7280 | 0 | 1 | 0 | 0 | 0 | 0
114 | - |  | 0 | Yes | 20 | 728 | 16 | 16 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 20 | 3
115 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
116 | - |  | 0 |  |  | 702 | 15 | 0 |  | 8 | 5616 | 0 | 1 | 0 | 0 | 0 | 0
117 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
118 | - |  | 0 | Yes | 20 | 728 | 16 | 16 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 20 | 3
120 | - |  | 0 |  |  | 845 | 19 | 0 |  | 8 | 6760 | 0 | 1 | 0 | 0 | 0 | 0
125 | - |  | 0 |  |  | 1020 | 23 | 0 |  | 8 | 8160 | 0 | 1 | 0 | 0 | 0 | 0
200 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
201 | - |  | 0 |  |  | 962 | 21 | 0 |  | 8 | 7696 | 0 | 1 | 0 | 0 | 0 | 0
202 | - |  | 0 |  |  | 910 | 20 | 0 |  | 8 | 7280 | 0 | 1 | 0 | 0 | 0 | 0
203 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
204 | - |  | 0 |  |  | 702 | 15 | 0 |  | 8 | 5616 | 0 | 1 | 0 | 0 | 0 | 0
205 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
207 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
208 | - |  | 0 |  |  | 884 | 20 | 0 |  | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
209 | - |  | 0 |  |  | 546 | 12 | 0 |  | 8 | 4368 | 0 | 1 | 0 | 0 | 0 | 0
210 | - |  | 0 |  |  | 546 | 12 | 0 |  | 8 | 4368 | 0 | 1 | 0 | 0 | 0 | 0
211 | - |  | 0 |  |  | 884 | 20 | 0 |  | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
214 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
215 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
217 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
218 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
221 | - |  | 0 |  |  | 1037 | 23 | 0 |  | 8 | 8296 | 0 | 1 | 0 | 0 | 0 | 0
300 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
301 | - |  | 0 |  |  | 910 | 20 | 0 |  | 8 | 7280 | 0 | 1 | 0 | 0 | 0 | 0
302 | - |  | 0 |  |  | 910 | 20 | 0 |  | 8 | 7280 | 0 | 1 | 0 | 0 | 0 | 0
303 | - |  | 0 |  |  | 702 | 15 | 0 |  | 8 | 5616 | 0 | 1 | 0 | 0 | 0 | 0
304 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
305 | - |  | 0 |  |  | 702 | 15 | 0 |  | 8 | 5616 | 0 | 1 | 0 | 0 | 0 | 0
307 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
308 | - |  | 0 |  |  | 910 | 20 | 0 |  | 8 | 7280 | 0 | 1 | 0 | 0 | 0 | 0
309 | - |  | 0 |  |  | 546 | 12 | 0 |  | 8 | 4368 | 0 | 1 | 0 | 0 | 0 | 0
310 | - |  | 0 |  |  | 546 | 12 | 0 |  | 8 | 4368 | 0 | 1 | 0 | 0 | 0 | 0
311 | - |  | 0 |  |  | 884 | 20 | 0 |  | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
314 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
315 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
316 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
317 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
318 | - |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
322 | Gym |  | 0 |  |  | 6360 | 144 | 0 |  | 8 | 50880 | 0 | 1.4912 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-22
School: | Kensington Creative and Performing Arts (CAPA) High School
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Auditorium |  | 0 |  |  | 5100 | 115 | 0 |  | 8 | 40800 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Gymnasium |  | 0 |  |  | 8400 | 190 | 0 |  | 8 | 67200 | 0 | 1.4912 | 0 | 0 | 0 | 0
101b | - |  | 0 |  |  | 450 | 10 | 0 |  | 8 | 3600 | 0 | 1 | 0 | 0 | 0 | 0
101 | - |  | 0 |  |  | 400 | 9 | 0 |  | 8 | 3200 | 0 | 1 | 0 | 0 | 0 | 0
103 | - |  | 0 |  |  | 1200 | 27 | 0 |  | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
106 | - |  | 0 |  |  | 1200 | 27 | 0 |  | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
118 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
119 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
121 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
122 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
123 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
131 | - |  | 0 |  |  | 1150 | 26 | 0 |  | 8 | 9200 | 0 | 1 | 0 | 0 | 0 | 0
134 | - |  | 0 | Yes | 20 | 700 | 15 | 15 |  | 8 | 5600 | 0 | 1 | 0 | 0 | 20 | 3
135 | - |  | 0 |  |  | 750 | 17 | 0 |  | 8 | 6000 | 0 | 1 | 0 | 0 | 0 | 0
201 | - |  | 0 |  |  | 1200 | 27 | 0 |  | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
209 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
210 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
212 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
213 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
214 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
216 | - |  | 0 | Yes | 20 | 1400 | 31 | 31 |  | 8 | 11200 | 0 | 1 | 0 | 0 | 20 | 3
217 | - |  | 0 |  |  | 1400 | 31 | 0 |  | 8 | 11200 | 0 | 1 | 0 | 0 | 0 | 0
218 | - |  | 0 |  |  | 1200 | 27 | 0 |  | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
220 | - |  | 0 |  |  | 1200 | 27 | 0 |  | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
221 | - |  | 0 |  |  | 1200 | 27 | 0 |  | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
224 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
225 | - |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafe |  | 0 |  |  | 2400 | 54 | 0 |  | 8 | 19200 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23
School: | Kensington Health Sciences Academy High School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Room | 247 | 16 |  |  | 857 | 19 | 16 |  | 8 | 6856 | 2.1616 | 1 | 2.1616 | 1 | 2.1616 | 1
102 | Room | 338 | 22 |  |  | 792 | 18 | 18 |  | 8 | 6336 | 3.2008 | 1 | 3.2008 | 1 | 3.2008 | 1
103 | Room | 206 | 13 |  |  | 854 | 19 | 13 |  | 8 | 6832 | 1.8091 | 1 | 1.8091 | 1 | 1.8091 | 1
104 | Room | 248 | 16 |  |  | 834 | 18 | 16 |  | 8 | 6672 | 2.2302 | 1 | 2.2302 | 1 | 2.2302 | 1
105 | Room | 212 | 14 |  |  | 854 | 19 | 14 |  | 8 | 6832 | 1.8618 | 1 | 1.8618 | 1 | 1.8618 | 1
106 | Room | 548 | 36 |  |  | 834 | 18 | 18 |  | 8 | 6672 | 4.9281 | 1 | 4.9281 | 2 | 4.9281 | 2
107 & 107A | Room | 613 | 40 |  |  | 783 | 17 | 17 |  | 8 | 6264 | 5.8716 | 1 | 5.8716 | 2 | 5.8716 | 2
110 | Room | 184 | 12 |  |  | 793 | 18 | 12 |  | 8 | 6344 | 1.7402 | 1 | 1.7402 | 1 | 1.7402 | 1
114 | Nurse |  | 0 |  |  | 114 | 2 | 0 |  | 8 | 912 | 0 | 1 | 0 | 0 | 0 | 0
115 | Room | 191 | 12 |  |  | 337 | 7 | 7 |  | 8 | 2696 | 4.2507 | 1 | 4.2507 | 2 | 4.2507 | 2
116 | Room | 171 | 11 |  |  | 848 | 19 | 11 |  | 8 | 6784 | 1.5124 | 1 | 1.5124 | 1 | 1.5124 | 1
201 | Room | 506 | 33 |  |  | 919 | 20 | 20 |  | 8 | 7352 | 4.1295 | 1 | 4.1295 | 2 | 4.1295 | 2
203 | Room | 0 | 0 |  |  | 795 | 18 | 0 |  | 8 | 6360 | 0 | 1 | 0 | 0 | 0 | 0
208 | 2nd Floor Bed and Dental Area | 1803 | 120 |  |  | 943 | 21 | 21 |  | 8 | 7544 | 14.3399 | 1 | 14.3399 | 3 | 14.3399 | 3
211 | Room | 273 | 18 |  |  | 860 | 19 | 18 |  | 8 | 6880 | 2.3808 | 1 | 2.3808 | 1 | 2.3808 | 1
212 | Room | 77 | 5 |  |  | 456 | 10 | 5 |  | 8 | 3648 | 1.2664 | 1 | 1.2664 | 1 | 1.2664 | 1
213 | Room | 250 | 16 |  |  | 681 | 15 | 15 |  | 8 | 5448 | 2.7533 | 1 | 2.7533 | 1 | 2.7533 | 1
214 | Dental Classroom | 171 | 11 |  |  | 794 | 18 | 11 |  | 8 | 6352 | 1.6152 | 1 | 1.6152 | 1 | 1.6152 | 1
215 | Room | 204 | 13 |  |  | 689 | 15 | 13 |  | 8 | 5512 | 2.2206 | 1 | 2.2206 | 1 | 2.2206 | 1
216 | Room | 191 | 12 |  |  | 756 | 17 | 12 |  | 8 | 6048 | 1.8948 | 1 | 1.8948 | 1 | 1.8948 | 1
217 | Room | 222 | 14 |  |  | 681 | 15 | 14 |  | 8 | 5448 | 2.4449 | 1 | 2.4449 | 1 | 2.4449 | 1
218 | Room | 276 | 18 |  |  | 599 | 13 | 13 |  | 8 | 4792 | 3.4558 | 1 | 3.4558 | 1 | 3.4558 | 1
- | Cafeteria | 586 | 39 |  |  | 1697 | 38 | 38 |  | 8 | 13576 | 2.5899 | 1 | 2.5899 | 1 | 2.5899 | 1
Sheet Last Modified: | 2021-03-30
School: | Francis Scott Key Elementary School
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Gym |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 713 | 16 | 16 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 713 | 16 | 16 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 |  |  | 437 | 9 | 0 | House Fan | 8 | 3496 | 0 | 1 | 0 | 0 | 0 | 0
108 | Classroom |  | 0 |  |  | 667 | 15 | 0 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 0 | 0
109 | Classroom |  | 0 |  |  | 667 | 15 | 0 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 0 | 0
110 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
111 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
212 | Classroom |  | 0 | Yes | 20 | 713 | 16 | 16 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 20 | 3
213 | Classroom |  | 0 | Yes | 20 | 837 | 19 | 19 | House Fan | 8 | 6696 | 0 | 1 | 0 | 0 | 20 | 3
215 | IMC |  | 0 | Yes | 20 | 1536 | 34 | 34 | House Fan | 8 | 12288 | 0 | 1 | 0 | 0 | 20 | 3
216 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
217 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
218 | Classroom |  | 0 | Yes | 20 | 713 | 16 | 16 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 20 | 3
219 | Classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
220 | Classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
221 | Classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
222 | Computer Lab |  | 0 |  |  | 720 | 16 | 0 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
323 | Classroom |  | 0 |  |  | 713 | 16 | 0 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 0 | 0
324 | Classroom |  | 0 |  |  | 713 | 16 | 0 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 0 | 0
325 | Classroom |  | 0 |  |  | 713 | 16 | 0 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 0 | 0
326 | Classroom |  | 0 |  |  | 736 | 16 | 0 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 0 | 0
327 | Classroom |  | 0 |  |  | 713 | 16 | 0 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 0 | 0
328 | Classroom |  | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
329 | Classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
330 | Classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
331 | Classroom |  | 0 |  |  | 720 | 16 | 0 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
332 | Classroom |  | 0 |  |  | 720 | 16 | 0 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
333 | Classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
- | Boy's Gang Bathrrom |  | 0 |  |  | 620 | 14 | 0 | N/A | 8 | 4960 | 0 | 1 | 0 | 0 | 0 | 0
- | Caferteria |  | 0 | Yes | 20 | 2240 | 50 | 50 | House Fan | 8 | 17920 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor's Office |  | 0 |  |  | 180 | 4 | 0 | House Fan | 8 | 1440 | 0 | 1 | 0 | 0 | 0 | 0
- | Girls Gang Bathrrom |  | 0 |  |  | 620 | 14 | 0 | N/A | 8 | 4960 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office |  | 0 | Yes | 20 | 361 | 8 | 8 | House Fan | 8 | 2888 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse |  | 0 | Yes | 20 | 391 | 8 | 8 | House Fan | 8 | 3128 | 0 | 1 | 0 | 0 | 20 | 3
- | Principle's Office |  | 0 |  |  | 276 | 6 | 0 | House Fan | 8 | 2208 | 0 | 1 | 0 | 0 | 0 | 0
- | Teachers' Lounge |  | 0 |  |  | 391 | 8 | 0 | House Fan | 8 | 3128 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-24
School: | Eliza B. Kirkbride Elementary-Middle
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | - |  | 0 | Yes | 20 | 805 | 18 | 18 | House Fan | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
102 | - |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
103 | - |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
104 | - |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
106 | - |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
107 | - |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
108 | - |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
109 | - |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
110 | - |  | 0 | Yes | 20 | 841 | 19 | 19 | House Fan | 8 | 6728 | 0 | 1 | 0 | 0 | 20 | 3
201 | - |  | 0 | Yes | 20 | 814 | 18 | 18 | House Fan | 8 | 6512 | 0 | 1 | 0 | 0 | 20 | 3
202 | - |  | 0 |  |  | 660 | 15 | 0 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
203 | - |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
204 | - |  | 0 |  |  | 660 | 15 | 0 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
205 | - |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
208 | - |  | 0 | Yes | 20 | 638 | 14 | 14 | House Fan | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
209 | - |  | 0 |  |  | 638 | 14 | 0 | House Fan | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
210 | - |  | 0 | Yes | 20 | 841 | 19 | 19 | House Fan | 8 | 6728 | 0 | 1 | 0 | 0 | 20 | 3
211 | - |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
212 | - |  | 0 |  |  | 638 | 14 | 0 | House Fan | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
301 | - |  | 0 |  |  | 851 | 19 | 0 | House Fan | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
302 | - |  | 0 |  |  | 660 | 15 | 0 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
303 | - |  | 0 |  |  | 704 | 16 | 0 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
304 | - |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
305/306 | - |  | 0 |  |  | 1357 | 30 | 0 | House Fan | 8 | 10856 | 0 | 1 | 0 | 0 | 0 | 0
307 | - |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
308 | - |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
309 | - |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
310 | - |  | 0 |  |  | 841 | 19 | 0 | House Fan | 8 | 6728 | 0 | 1 | 0 | 0 | 0 | 0
311 | - |  | 0 |  |  | 660 | 15 | 0 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
312 | - |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
- | Art |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
- | Counselor Suite |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 | Yes | 20 | 3680 | 83 | 83 | House Fan | 8 | 29440 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Library |  | 0 | Yes | 20 | 1380 | 31 | 31 | House Fan | 8 | 11040 | 0 | 1 | 0 | 0 | 20 | 3
- | Lunchroom1 |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
- | Lunchroom2 |  | 0 | Yes | 20 | 1100 | 25 | 25 | House Fan | 8 | 8800 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 322 | 7 | 7 | House Fan | 8 | 2576 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 96 | 2 | 2 | House Fan | 8 | 768 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 240 | 5 | 5 | House Fan | 8 | 1920 | 0 | 1 | 0 | 0 | 20 | 3
- | Teacher Lounge/BE office |  | 0 | Yes | 20 | 960 | 21 | 21 | House Fan | 8 | 7680 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-20
School: | John Hancock Demonstration Middle School @ General J Harry LaBrum Campus
| LaBrum Building | LaBrum Retest
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
102 | Classroom | 391 | 26 |  |  | 875 | 19 | 19 | UV | 8 | 7000 | 3.3514 | 1 | 3.3514 | 1 | 3.3514 | 1
102A | Classroom | 230 | 15 |  |  | 578 | 13 | 13 | UV | 8 | 4624 | 2.9844 | 1 | 2.9844 | 1 | 2.9844 | 1
103 | Classroom | 0 | 0 | Yes | 20 | 910 | 20 | 20 | UV | 8 | 7280 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom | 622 | 41 |  |  | 612 | 13 | 13 | UV | 8 | 4896 | 7.6225 | 1 | 7.6225 | 2 | 7.6225 | 2
105 | Classroom | 150 | 10 | Yes | 20 | 1152 | 26 | 26 | UV | 8 | 9216 | 0.97656 | 1 | 0.97656 | 0 | 20.9766 | 3
106 | Classroom | 320 | 21 |  |  | 342 | 7 | 7 | UV | 8 | 2736 | 7.0175 | 1 | 7.0175 | 2 | 7.0175 | 2
107 | Classroom | 221 | 14 | Yes | 20 | 1044 | 23 | 23 | UV | 8 | 8352 | 1.5876 | 1 | 1.5876 | 1 | 21.5876 | 3
201 | Classroom | 362 | 24 |  |  | 864 | 19 | 19 | UV | 8 | 6912 | 3.1424 | 1 | 3.1424 | 1 | 3.1424 | 1
202 | Classroom | 267 | 17 |  |  | 782 | 17 | 17 | UV | 8 | 6256 | 2.5607 | 1 | 2.5607 | 1 | 2.5607 | 1
203 | Classroom | 245 | 16 | Yes | 20 | 884 | 20 | 20 | UV | 8 | 7072 | 2.0786 | 1 | 2.0786 | 1 | 22.0786 | 3
204 | Classroom | 240 | 16 | Yes | 20 | 1116 | 25 | 25 | UV | 8 | 8928 | 1.6129 | 1 | 1.6129 | 1 | 21.6129 | 3
205 | Classroom | 311 | 20 |  |  | 900 | 20 | 20 | UV | 8 | 7200 | 2.5917 | 1 | 2.5917 | 1 | 2.5917 | 1
206 | Classroom | 583 | 38 |  |  | 858 | 19 | 19 | UV | 8 | 6864 | 5.0962 | 1 | 5.0962 | 2 | 5.0962 | 2
207 | Classroom | 340 | 22 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 3.0357 | 1 | 3.0357 | 1 | 3.0357 | 1
208 | Classroom | 462 | 30 |  |  | 816 | 18 | 18 | UV | 8 | 6528 | 4.2463 | 1 | 4.2463 | 2 | 4.2463 | 2
209 | Classroom | 410 | 27 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 4.2708 | 1 | 4.2708 | 2 | 4.2708 | 2
210 | Classroom | 327 | 21 |  |  | 888 | 20 | 20 | UV | 8 | 7104 | 2.7618 | 1 | 2.7618 | 1 | 2.7618 | 1
212 | Classroom | 390 | 26 |  |  | 875 | 19 | 19 | UV | 8 | 7000 | 3.3429 | 1 | 3.3429 | 1 | 3.3429 | 1
213 | Classroom | 336 | 22 |  |  | 864 | 19 | 19 | UV | 8 | 6912 | 2.9167 | 1 | 2.9167 | 1 | 2.9167 | 1
214 | Classroom | 366 | 24 |  |  | 828 | 18 | 18 | UV | 8 | 6624 | 3.3152 | 1 | 3.3152 | 1 | 3.3152 | 1
- | Admin | 0 | 0 | Yes | 20 | 286 | 6 | 6 | UV | 8 | 2288 | 0 | 1 | 0 | 0 | 20 | 3
- | Cafeteria | 450 | 30 |  |  | 2765 | 62 | 30 | UV | 8 | 22120 | 1.2206 | 1.062 | 1.2963 | 1 | 1.2963 | 1
- | Gym | 0 | 0 |  |  | 5248 | 119 | 0 |  | 8 | 41984 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Library | 538 | 35 |  |  | 2016 | 45 | 35 | UV | 8 | 16128 | 2.0015 | 1 | 2.0015 | 1 | 2.0015 | 1
- | Nurse's Room | 0 | 0 | Yes | 20 | 550 | 12 | 12 | UV | 8 | 4400 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-27
School: | Robert E. Lamberton Elementary School
School: | Robert E. Lamberton Elementary- Little School House
School: | Robert E. Lamberton Elementary- Little School House- Part 2
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
1A | Music Room | 261 | 17 |  |  | 506 | 11 | 11 | UV | 8 | 4048 | 3.8686 | 1 | 3.8686 | 1 | 3.8686 | 1
1B | Classroom | 0 | 0 | Yes | 20 | 720 | 16 | 16 | UV | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
2A | Classroom | 264 | 17 |  |  | 504 | 11 | 11 | UV | 8 | 4032 | 3.9286 | 1 | 3.9286 | 1 | 3.9286 | 1
4 | Classroom | 159 | 10 | Yes | 20 | 2024 | 46 | 46 | UV | 8 | 16192 | 0.58918 | 1 | 0.58918 | 0 | 20.5892 | 3
5A | Classroom | 0 | 0 | Yes | 20 | 600 | 13 | 13 | UV | 8 | 4800 | 0 | 1 | 0 | 0 | 20 | 3
6 | Classroom | 0 | 0 | Yes | 20 | 625 | 14 | 14 | UV | 8 | 5000 | 0 | 1 | 0 | 0 | 20 | 3
7 | Classroom |  | 0 | Yes | 20 | 1206 | 27 | 27 | UV | 8 | 9648 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom | 457 | 30 |  |  | 506 | 11 | 11 | UV | 8 | 4048 | 6.7737 | 1 | 6.7737 | 2 | 6.7737 | 2
102 | Classroom | 348 | 23 |  |  | 1012 | 23 | 23 | UV | 8 | 8096 | 2.5791 | 1 | 2.5791 | 1 | 2.5791 | 1
103 | Classroom | 466 | 31 |  |  | 989 | 22 | 22 | UV | 8 | 7912 | 3.5339 | 1 | 3.5339 | 1 | 3.5339 | 1
104 | Classroom | 335 | 22 | Yes | 20 | 1012 | 23 | 23 | UV | 8 | 8096 | 2.4827 | 1 | 2.4827 | 1 | 22.4827 | 3
105 | Classroom | 277 | 18 | Yes | 20 | 989 | 22 | 22 | UV | 8 | 7912 | 2.1006 | 1 | 2.1006 | 1 | 22.1006 | 3
106 | Classroom | 198 | 13 | Yes | 20 | 1012 | 23 | 23 | UV | 8 | 8096 | 1.4674 | 1 | 1.4674 | 1 | 21.4674 | 3
107 | Classroom | 406 | 27 |  |  | 1012 | 23 | 23 | UV | 8 | 8096 | 3.0089 | 1 | 3.0089 | 1 | 3.0089 | 1
108 | Classroom | 271 | 18 |  |  | 667 | 15 | 15 | UV | 8 | 5336 | 3.0472 | 1 | 3.0472 | 1 | 3.0472 | 1
109 | Classroom | 351 | 23 |  |  | 1012 | 23 | 23 | UV | 8 | 8096 | 2.6013 | 1 | 2.6013 | 1 | 2.6013 | 1
110 | Classroom | 420 | 28 |  |  | 989 | 22 | 22 | UV | 8 | 7912 | 3.185 | 1 | 3.185 | 1 | 3.185 | 1
111 | Classroom | 338 | 22 |  |  | 989 | 22 | 22 | UV | 8 | 7912 | 2.5632 | 1 | 2.5632 | 1 | 2.5632 | 1
112 | Classroom | 0 | 0 | Yes | 20 | 989 | 22 | 22 | UV | 8 | 7912 | 0 | 1 | 0 | 0 | 20 | 3
113 | Classroom | 280 | 18 |  |  | 575 | 13 | 13 | UV | 8 | 4600 | 3.6522 | 1 | 3.6522 | 1 | 3.6522 | 1
114 | Classroom | 271 | 18 | Yes | 20 | 874 | 19 | 19 | UV | 8 | 6992 | 2.3255 | 1 | 2.3255 | 1 | 22.3255 | 3
115 | Classroom | 278 | 18 | Yes | 20 | 874 | 19 | 19 | UV | 8 | 6992 | 2.3856 | 1 | 2.3856 | 1 | 22.3856 | 3
116 | Classroom | 387 | 25 |  |  | 874 | 19 | 19 | UV | 8 | 6992 | 3.3209 | 1 | 3.3209 | 1 | 3.3209 | 1
117 | Classroom | 176 | 11 | Yes | 20 | 874 | 19 | 19 | UV | 8 | 6992 | 1.5103 | 1 | 1.5103 | 1 | 21.5103 | 3
118 | Classroom | 243 | 16 | Yes | 20 | 1012 | 23 | 23 | UV | 8 | 8096 | 1.8009 | 1 | 1.8009 | 1 | 21.8009 | 3
119 | Assitant Principal |  | 0 | Yes | 20 | 361 | 8 | 8 |  | 8 | 2888 | 0 | 1 | 0 | 0 | 20 | 3
120A | Tescher's Lounge |  | 0 | Yes | 20 | 377 | 8 | 8 |  | 8 | 3016 | 0 | 1 | 0 | 0 | 20 | 3
120 | Nurse |  | 0 |  |  | 501 | 11 | 0 |  | 8 | 4008 | 0 | 1 | 0 | 0 | 0 | 0
121 | Special Education |  | 0 | Yes | 20 | 531 | 12 | 12 |  | 8 | 4248 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 320 | 21 | Yes | 20 | 989 | 22 | 22 | UV | 8 | 7912 | 2.4267 | 1 | 2.4267 | 1 | 22.4267 | 3
202 | Classroom | 0 | 0 | Yes | 20 | 667 | 15 | 15 | UV | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom | 418 | 27 |  |  | 989 | 22 | 22 | UV | 8 | 7912 | 3.1699 | 1 | 3.1699 | 1 | 3.1699 | 1
204 | Classroom | 511 | 34 |  |  | 1012 | 23 | 23 | UV | 8 | 8096 | 3.7871 | 1 | 3.7871 | 1 | 3.7871 | 1
205 | Classroom | 560 | 37 |  |  | 1012 | 23 | 23 | UV | 8 | 8096 | 4.1502 | 1 | 4.1502 | 2 | 4.1502 | 2
206 | Classroom | 770 | 51 |  |  | 1012 | 23 | 23 | UV | 8 | 8096 | 5.7065 | 1 | 5.7065 | 2 | 5.7065 | 2
207 | Classroom | 0 | 0 | Yes | 20 | 1012 | 23 | 23 | UV | 8 | 8096 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 246 | 16 | Yes | 20 | 989 | 22 | 22 | UV | 8 | 7912 | 1.8655 | 1 | 1.8655 | 1 | 21.8655 | 3
209 | Classroom | 446 | 29 |  |  | 1012 | 23 | 23 | UV | 8 | 8096 | 3.3053 | 1 | 3.3053 | 1 | 3.3053 | 1
210A | Classroom | 233 | 15 |  |  | 504 | 11 | 11 | UV | 8 | 4032 | 3.4673 | 1 | 3.4673 | 1 | 3.4673 | 1
210B | Classroom | 0 | 0 | Yes | 20 | 504 | 11 | 11 | UV | 8 | 4032 | 0 | 1 | 0 | 0 | 20 | 3
215 | Classroom | 0 | 0 | Yes | 20 | 874 | 19 | 19 | UV | 8 | 6992 | 0 | 1 | 0 | 0 | 20 | 3
216 | Classroom | 0 | 0 | Yes | 20 | 874 | 19 | 19 | UV | 8 | 6992 | 0 | 1 | 0 | 0 | 20 | 3
217 | Classroom | 220 | 14 | Yes | 20 | 874 | 19 | 19 | UV | 8 | 6992 | 1.8879 | 1 | 1.8879 | 1 | 21.8879 | 3
218 | Classroom | 359 | 23 |  |  | 874 | 19 | 19 | UV | 8 | 6992 | 3.0807 | 1 | 3.0807 | 1 | 3.0807 | 1
220 | Classroom | 232 | 15 | Yes | 20 | 1012 | 23 | 23 | UV | 8 | 8096 | 1.7194 | 1 | 1.7194 | 1 | 21.7194 | 3
221 | Classroom | 441 | 29 |  |  | 1058 | 24 | 24 | UV | 8 | 8464 | 3.1262 | 1 | 3.1262 | 1 | 3.1262 | 1
- | Principal |  | 0 | Yes | 20 | 387 | 8 | 8 |  | 8 | 3096 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 784 | 17 | 17 |  | 8 | 6272 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 4864 | 324 |  |  | 5832 | 132 | 132 | AHU | 8 | 46656 | 6.2551 | 1.062 | 6.6432 | 2 | 6.6432 | 2
Lamberton LSH
15 | Classroom | 313 | 20 | Yes | 20 | 928 | 21 | 21 | AHU | 8 | 7424 | 2.5296 | 1 | 2.5296 | 1 | 22.5296 | 3
16 | Classroom | 299 | 19 | Yes | 20 | 928 | 21 | 21 | AHU | 8 | 7424 | 2.4165 | 1 | 2.4165 | 1 | 22.4165 | 3
17 | Classroom | 317 | 21 |  |  | 928 | 21 | 21 | AHU | 8 | 7424 | 2.562 | 1 | 2.562 | 1 | 2.562 | 1
18 | Classroom | 329 | 21 |  |  | 928 | 21 | 21 | AHU | 8 | 7424 | 2.6589 | 1 | 2.6589 | 1 | 2.6589 | 1
19 | Classroom | 291 | 19 | Yes | 20 | 928 | 21 | 21 | AHU | 8 | 7424 | 2.3518 | 1 | 2.3518 | 1 | 22.3518 | 3
20 | Classroom | 295 | 19 | Yes | 20 | 928 | 21 | 21 | AHU | 8 | 7424 | 2.3842 | 1 | 2.3842 | 1 | 22.3842 | 3
21 | Classroom | 316 | 21 |  |  | 928 | 21 | 21 | AHU | 8 | 7424 | 2.5539 | 1 | 2.5539 | 1 | 2.5539 | 1
22 | Classroom | 324 | 21 |  |  | 928 | 21 | 21 | AHU | 8 | 7424 | 2.6185 | 1 | 2.6185 | 1 | 2.6185 | 1
23 | Classroom | 314 | 20 | Yes | 20 | 928 | 21 | 21 | AHU | 8 | 7424 | 2.5377 | 1 | 2.5377 | 1 | 22.5377 | 3
24 | Classroom | 327 | 21 |  |  | 928 | 21 | 21 | AHU | 8 | 7424 | 2.6428 | 1 | 2.6428 | 1 | 2.6428 | 1
25 | Classroom | 287 | 19 | Yes | 20 | 928 | 21 | 21 | AHU | 8 | 7424 | 2.3195 | 1 | 2.3195 | 1 | 22.3195 | 3
26 | Classroom | 303 | 20 | Yes | 20 | 928 | 21 | 21 | AHU | 8 | 7424 | 2.4488 | 1 | 2.4488 | 1 | 22.4488 | 3
- | Main Office | 4 | 0 | Yes | 20 | 300 | 6 | 6 | AHU | 8 | 2400 | 0.1 | 1 | 0.1 | 0 | 20.1 | 3
- | Multi Purpose | 1539 | 102 |  |  | 1749 | 39 | 39 | AHU | 8 | 13992 | 6.5995 | 1 | 6.5995 | 2 | 6.5995 | 2
- | Janitor | 0 | 0 |  |  | 80 | 1 | 0 | AHU | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-16
School: | Lankenau Environmental Science High School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
201 | Classroom | 407 | 27 |  |  | 585 | 13 | 13 |  | 8 | 4680 | 5.2179 | 1 | 5.2179 | 2 | 5.2179 | 2
205 | Classroom | 242 | 16 |  |  | 534 | 12 | 12 |  | 8 | 4272 | 3.3989 | 1 | 3.3989 | 1 | 3.3989 | 1
206 | Classroom | 183 | 12 |  |  | 529 | 12 | 12 |  | 8 | 4232 | 2.5945 | 1 | 2.5945 | 1 | 2.5945 | 1
207 | Classroom | 182 | 12 |  |  | 529 | 12 | 12 |  | 8 | 4232 | 2.5803 | 1 | 2.5803 | 1 | 2.5803 | 1
208 | Classroom | 178 | 11 |  |  | 522 | 11 | 11 |  | 8 | 4176 | 2.5575 | 1 | 2.5575 | 1 | 2.5575 | 1
210 | Classroom | 117 | 7 |  |  | 493 | 11 | 7 |  | 8 | 3944 | 1.7799 | 1 | 1.7799 | 1 | 1.7799 | 1
211 | Classroom | 120 | 8 |  |  | 475 | 10 | 8 |  | 8 | 3800 | 1.8947 | 1 | 1.8947 | 1 | 1.8947 | 1
212 | Classroom | 63 | 4 |  |  | 507 | 11 | 4 |  | 8 | 4056 | 0.93195 | 1 | 0.93195 | 0 | 0.93195 | 0
213 | Classroom | 63 | 4 |  |  | 531 | 12 | 4 |  | 8 | 4248 | 0.88983 | 1 | 0.88983 | 0 | 0.88983 | 0
214 | Classroom | 67 | 4 |  |  | 603 | 13 | 4 |  | 8 | 4824 | 0.83333 | 1 | 0.83333 | 0 | 0.83333 | 0
302 | Classroom | 84 | 5 |  |  | 586 | 13 | 5 |  | 8 | 4688 | 1.0751 | 1 | 1.0751 | 1 | 1.0751 | 1
303 | Classroom | 87 | 5 |  |  | 589 | 13 | 5 |  | 8 | 4712 | 1.1078 | 1 | 1.1078 | 1 | 1.1078 | 1
304 | Classroom | 85 | 5 |  |  | 573 | 13 | 5 |  | 8 | 4584 | 1.1126 | 1 | 1.1126 | 1 | 1.1126 | 1
305 | Classroom | 73 | 4 |  |  | 613 | 13 | 4 |  | 8 | 4904 | 0.89315 | 1 | 0.89315 | 0 | 0.89315 | 0
307 | Classroom | 517 | 34 |  |  | 1146 | 26 | 26 |  | 8 | 9168 | 3.3835 | 1 | 3.3835 | 1 | 3.3835 | 1
308 | 308 | 412 | 27 |  |  | 879 | 19 | 19 |  | 8 | 7032 | 3.5154 | 1 | 3.5154 | 1 | 3.5154 | 1
308B | 308B | 38 | 2 |  |  | 350 | 7 | 2 |  | 8 | 2800 | 0.81429 | 1 | 0.81429 | 0 | 0.81429 | 0
309 | Classroom | 611 | 40 |  |  | 1120 | 25 | 25 |  | 8 | 8960 | 4.0915 | 1 | 4.0915 | 2 | 4.0915 | 2
- | Auditorium storage 1 | 23 | 1 |  |  | 67 | 1 | 1 |  | 8 | 536 | 2.5746 | 1 | 2.5746 | 1 | 2.5746 | 1
- | Auditorium storage 2 | 22 | 1 |  |  | 109 | 2 | 1 |  | 8 | 872 | 1.5138 | 1 | 1.5138 | 1 | 1.5138 | 1
- | Botany / Storage area | 198 | 13 |  |  | 3264 | 74 | 13 |  | 8 | 26112 | 0.45496 | 1.062 | 0.48319 | 0 | 0.48319 | 0
- | Cafeteria | 706 | 47 |  |  | 1326 | 30 | 30 |  | 8 | 10608 | 3.9932 | 1 | 3.9932 | 1 | 3.9932 | 1
- | Cafeteria 2 (Small) | 158 | 10 |  |  | 518 | 11 | 10 |  | 8 | 4144 | 2.2876 | 1 | 2.2876 | 1 | 2.2876 | 1
- | Cafeteria 3 (Main) | 662 | 44 |  |  | 1536 | 34 | 34 |  | 8 | 12288 | 3.2324 | 1 | 3.2324 | 1 | 3.2324 | 1
- | Conference Room | 55 | 3 |  |  | 254 | 5 | 3 |  | 8 | 2032 | 1.624 | 1 | 1.624 | 1 | 1.624 | 1
- | Counselors Office | 241 | 16 |  |  | 700 | 15 | 15 |  | 8 | 5600 | 2.5821 | 1 | 2.5821 | 1 | 2.5821 | 1
- | Dean's Office | 54 | 3 |  |  | 280 | 6 | 3 |  | 8 | 2240 | 1.4464 | 1 | 1.4464 | 1 | 1.4464 | 1
- | Gym | 606 | 40 |  |  | 2089 | 47 | 40 |  | 8 | 16712 | 2.1757 | 1 | 2.1757 | 1 | 2.1757 | 1
- | Lounge | 141 | 9 |  |  | 409 | 9 | 9 |  | 8 | 3272 | 2.5856 | 1 | 2.5856 | 1 | 2.5856 | 1
- | Main Office | 166 | 11 |  |  | 605 | 13 | 11 |  | 8 | 4840 | 2.0579 | 1 | 2.0579 | 1 | 2.0579 | 1
- | Music Assembly | 1020 | 68 |  |  | 2424 | 55 | 55 |  | 8 | 19392 | 3.1559 | 1 | 3.1559 | 1 | 3.1559 | 1
- | Nurse's Office | 44 | 2 |  |  | 247 | 5 | 2 |  | 8 | 1976 | 1.336 | 1 | 1.336 | 1 | 1.336 | 1
- | Principal's office | 109 | 7 |  |  | 280 | 6 | 6 |  | 8 | 2240 | 2.9196 | 1 | 2.9196 | 1 | 2.9196 | 1
- | Science Storage | 60 | 4 |  |  | 355 | 8 | 4 |  | 8 | 2840 | 1.2676 | 1 | 1.2676 | 1 | 1.2676 | 1
202 | - |  | 0 |  |  | 585 | 13 | 13 |  | 8 | 4680 | 0 | 1 | 0 | 0 | 0 | 0
203 | - |  | 0 |  |  | 527 | 11 | 11 |  | 8 | 4216 | 0 | 1 | 0 | 0 | 0 | 0
204 | - |  | 0 |  |  | 535 | 12 | 13 |  | 8 | 4280 | 0 | 1 | 0 | 0 | 0 | 0
209 | - |  | 0 |  |  | 535 | 12 | 13 |  | 8 | 4280 | 0 | 1 | 0 | 0 | 0 | 0
- | Roster Chair |  | 0 |  |  | 156 | 3 | 3 |  | 8 | 1248 | 0 | 1 | 0 | 0 | 0 | 0
306 | - |  | 0 |  |  | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18
School: | Henry W. Lawton Elementary School
Vendor: | Devine Brothers | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 956 | 63 |  |  | 990 | 22 | 22 | UV | 8 | 7920 | 7.2424 | 1 | 7.2424 | 2 | 7.2424 | 2
102 | Classroom | 407 | 27 |  |  | 990 | 22 | 22 | UV | 8 | 7920 | 3.0833 | 1 | 3.0833 | 1 | 3.0833 | 1
103 | Classroom | 547 | 36 |  |  | 730 | 16 | 16 | UV | 8 | 5840 | 5.6199 | 1 | 5.6199 | 2 | 5.6199 | 2
104 | Classroom | 327 | 21 |  |  | 796 | 18 | 18 | UV | 8 | 6368 | 3.081 | 1 | 3.081 | 1 | 3.081 | 1
105 | Classroom | 464 | 30 |  |  | 730 | 16 | 16 | UV | 8 | 5840 | 4.7671 | 1 | 4.7671 | 2 | 4.7671 | 2
106 | Classroom | 432 | 28 |  |  | 796 | 18 | 18 | UV | 8 | 6368 | 4.0704 | 1 | 4.0704 | 2 | 4.0704 | 2
107 | Classroom | 376 | 25 |  |  | 730 | 16 | 16 | UV | 8 | 5840 | 3.863 | 1 | 3.863 | 1 | 3.863 | 1
108 | Classroom | 641 | 42 |  |  | 676 | 15 | 15 | UV | 8 | 5408 | 7.1117 | 1 | 7.1117 | 2 | 7.1117 | 2
109 | Classroom | 519 | 34 |  |  | 730 | 16 | 16 | UV | 8 | 5840 | 5.3322 | 1 | 5.3322 | 2 | 5.3322 | 2
110 | Classroom | 699 | 46 |  |  | 676 | 15 | 15 | UV | 8 | 5408 | 7.7552 | 1 | 7.7552 | 2 | 7.7552 | 2
111 | Classroom | 685 | 45 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 7.1354 | 1 | 7.1354 | 2 | 7.1354 | 2
112 | Classroom | 929 | 61 |  |  | 930 | 21 | 21 | UV | 8 | 7440 | 7.4919 | 1 | 7.4919 | 2 | 7.4919 | 2
113 | Classroom | 742 | 49 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 7.7292 | 1 | 7.7292 | 2 | 7.7292 | 2
114 | Classroom | 705 | 47 |  |  | 930 | 21 | 21 | UV | 8 | 7440 | 5.6855 | 1 | 5.6855 | 2 | 5.6855 | 2
115 | Classroom | 712 | 47 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 7.4167 | 1 | 7.4167 | 2 | 7.4167 | 2
117 | Classroom | 671 | 44 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 6.9896 | 1 | 6.9896 | 2 | 6.9896 | 2
119 | Classroom | 713 | 47 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 7.4271 | 1 | 7.4271 | 2 | 7.4271 | 2
121 | Classroom | 571 | 38 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 5.9479 | 1 | 5.9479 | 2 | 5.9479 | 2
123 | Classroom | 400 | 26 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 4.1667 | 1 | 4.1667 | 2 | 4.1667 | 2
201 | Classroom | 411 | 27 |  |  | 816 | 18 | 18 | UV | 8 | 6528 | 3.7776 | 1 | 3.7776 | 1 | 3.7776 | 1
202 | Classroom | 658 | 43 |  |  | 816 | 18 | 18 | UV | 8 | 6528 | 6.0478 | 1 | 6.0478 | 2 | 6.0478 | 2
203 | Classroom | 455 | 30 |  |  | 816 | 18 | 18 | UV | 8 | 6528 | 4.182 | 1 | 4.182 | 2 | 4.182 | 2
204 | Classroom | 790 | 52 |  |  | 816 | 18 | 18 | UV | 8 | 6528 | 7.261 | 1 | 7.261 | 2 | 7.261 | 2
205 | Classroom | 802 | 53 |  |  | 816 | 18 | 18 | UV | 8 | 6528 | 7.3713 | 1 | 7.3713 | 2 | 7.3713 | 2
206 | Classroom | 611 | 40 |  |  | 816 | 18 | 18 | UV | 8 | 6528 | 5.6158 | 1 | 5.6158 | 2 | 5.6158 | 2
207 | Classroom | 814 | 54 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 8.4792 | 1 | 8.4792 | 2 | 8.4792 | 2
208 | Classroom | 320 | 21 |  |  | 816 | 18 | 18 | UV | 8 | 6528 | 2.9412 | 1 | 2.9412 | 1 | 2.9412 | 1
209 | Classroom | 653 | 43 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 6.8021 | 1 | 6.8021 | 2 | 6.8021 | 2
211 | Classroom | 707 | 47 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 7.3646 | 1 | 7.3646 | 2 | 7.3646 | 2
213 | Classroom | 649 | 43 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 6.7604 | 1 | 6.7604 | 2 | 6.7604 | 2
214 | Classroom | 289 | 19 |  |  | 540 | 12 | 12 | UV | 8 | 4320 | 4.0139 | 1 | 4.0139 | 2 | 4.0139 | 2
215 | Classroom | 730 | 48 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 7.6042 | 1 | 7.6042 | 2 | 7.6042 | 2
216 | Classroom | 332 | 22 |  |  | 768 | 17 | 17 | UV | 8 | 6144 | 3.2422 | 1 | 3.2422 | 1 | 3.2422 | 1
217 | Classroom | 364 | 24 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 3.7917 | 1 | 3.7917 | 1 | 3.7917 | 1
218 | Classroom | 716 | 47 |  |  | 676 | 15 | 15 | UV | 8 | 5408 | 7.9438 | 1 | 7.9438 | 2 | 7.9438 | 2
219 | Classroom | 672 | 44 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 7 | 1 | 7 | 2 | 7 | 2
220 | Classroom | 639 | 42 |  |  | 676 | 15 | 15 | UV | 8 | 5408 | 7.0895 | 1 | 7.0895 | 2 | 7.0895 | 2
222 | Classroom | 683 | 45 |  |  | 540 | 12 | 12 | UV | 8 | 4320 | 9.4861 | 1 | 9.4861 | 2 | 9.4861 | 2
224 | Classroom | 633 | 42 |  |  | 720 | 16 | 16 | UV | 8 | 5760 | 6.5938 | 1 | 6.5938 | 2 | 6.5938 | 2
226 | Classroom | 1102 | 73 |  |  | 540 | 12 | 12 | UV | 8 | 4320 | 15.3056 | 1 | 15.3056 | 3 | 15.3056 | 3
- | Art (Large) | 477 | 31 |  |  | 1258 | 28 | 28 | UV | 8 | 10064 | 2.8438 | 1 | 2.8438 | 1 | 2.8438 | 1
- | Cafeteria | 632 | 42 |  |  | 2310 | 52 | 42 | AHU | 8 | 18480 | 2.0519 | 1 | 2.0519 | 1 | 2.0519 | 1
- | Computer | 886 | 59 |  |  | 1440 | 32 | 32 | UV | 8 | 11520 | 4.6146 | 1 | 4.6146 | 2 | 4.6146 | 2
- | IMC | 426 | 28 |  |  | 2620 | 59 | 28 | UV | 8 | 20960 | 1.2195 | 1.062 | 1.2951 | 1 | 1.2951 | 1
- | Main Office | 232 | 15 |  |  | 275 | 6 | 6 | UV | 8 | 2200 | 6.3273 | 1 | 6.3273 | 2 | 6.3273 | 2
- | Nurse's Office | 283 | 18 |  |  | 363 | 8 | 8 | UV | 8 | 2904 | 5.8471 | 1 | 5.8471 | 2 | 5.8471 | 2
- | Science (Large) | 375 | 25 |  |  | 1088 | 24 | 24 | UV | 8 | 8704 | 2.585 | 1 | 2.585 | 1 | 2.585 | 1
Sheet Last Modified: | 2021-04-26
School: | Henry C. Lea Elementary School
Vendor: | Devine | Chadwick | Devine Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
L1 | Classroom | 166 | 11 |  |  | 696 | 15 | 11 | UV | 8 | 5568 | 1.7888 | 1 | 1.7888 | 1 | 1.7888 | 1
L3 | Classroom | 0 | 0 |  |  | 624 | 14 | 0 | UV | 8 | 4992 | 0 | 1 | 0 | 0 | 0 | 0
L4 | Classroom | 191 | 12 |  |  | 696 | 15 | 12 | UV | 8 | 5568 | 2.0582 | 1 | 2.0582 | 1 | 2.0582 | 1
L5 | Classroom | 208 | 13 |  |  | 864 | 19 | 13 | UV | 8 | 6912 | 1.8056 | 1 | 1.8056 | 1 | 1.8056 | 1
L7 | Classroom | 247 | 16 |  |  | 768 | 17 | 16 | UV | 8 | 6144 | 2.4121 | 1 | 2.4121 | 1 | 2.4121 | 1
B2 | Classroom |  | 0 | Yes | 20 | 1457 | 33 | 33 |  | 8 | 11656 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom | 312 | 20 |  |  | 1225 | 27 | 20 | UV | 8 | 9800 | 1.9102 | 1 | 1.9102 | 1 | 1.9102 | 1
102 | Classroom | 319 | 21 |  |  | 1295 | 29 | 21 | UV | 8 | 10360 | 1.8475 | 1 | 1.8475 | 1 | 1.8475 | 1
103 | Classroom | 284 | 18 |  |  | 810 | 18 | 18 | AHU | 8 | 6480 | 2.6296 | 1 | 2.6296 | 1 | 2.6296 | 1
105 | Classroom | 287 | 19 |  |  | 840 | 19 | 19 | AHU | 8 | 6720 | 2.5625 | 1 | 2.5625 | 1 | 2.5625 | 1
106 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom | 289 | 19 |  |  | 840 | 19 | 19 | AHU | 8 | 6720 | 2.5804 | 1 | 2.5804 | 1 | 2.5804 | 1
108 | Classroom | 301 | 20 |  |  | 840 | 19 | 19 | AHU | 8 | 6720 | 2.6875 | 1 | 2.6875 | 1 | 2.6875 | 1
109 | Classroom | 295 | 19 |  |  | 840 | 19 | 19 | AHU | 8 | 6720 | 2.6339 | 1 | 2.6339 | 1 | 2.6339 | 1
110 | Classroom | 298 | 19 |  |  | 840 | 19 | 19 | AHU | 8 | 6720 | 2.6607 | 1 | 2.6607 | 1 | 2.6607 | 1
111 | Classroom | 289 | 19 |  |  | 840 | 19 | 19 | AHU | 8 | 6720 | 2.5804 | 1 | 2.5804 | 1 | 2.5804 | 1
125 | Counselor's Office |  | 0 | Yes | 20 | 126 | 2 | 2 |  | 8 | 1008 | 0 | 1 | 0 | 0 | 20 | 3
127 | Classroom |  | 0 | Yes | 20 | 126 | 2 | 2 |  | 8 | 1008 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 20 | 1015 | 23 | 23 | UV | 8 | 8120 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 | Yes | 20 | 980 | 22 | 22 | UV | 8 | 7840 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 |  | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
204a | Classroom | 0 | 0 | Yes | 20 | 252 | 5 | 5 | AHU | 8 | 2016 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom | 0 | 0 | Yes | 20 | 810 | 18 | 18 | AHU | 8 | 6480 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom | 0 | 0 | Yes | 20 | 870 | 19 | 19 | AHU | 8 | 6960 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
212 | Classroom | 0 | 0 | Yes | 20 | 212 | 4 | 4 | AHU | 8 | 1696 | 0 | 1 | 0 | 0 | 20 | 3
301/302 | Library | 380 | 25 | Yes | 20 | 5400 | 122 | 122 | UV | 8 | 43200 | 0.52778 | 1.062 | 0.56052 | 0 | 20.5605 | 3
303 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom | 0 | 0 | Yes | 20 | 690 | 15 | 15 | AHU | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
304A | Room |  | 0 | Yes | 20 | 266 | 6 | 6 |  | 8 | 2128 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
310 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
311 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
312 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
313 | Classroom | 0 | 0 |  |  | 840 | 19 | 0 | AHU | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 |  |  | 2296 | 52 | 0 | AHU | 8 | 18368 | 0 | 1 | 0 | 0 | 0 | 0
- | Side Cafeteria | 490 | 32 | Yes | 20 | 1800 | 40 | 40 | AHU | 8 | 14400 | 2.0417 | 1 | 2.0417 | 1 | 22.0417 | 3
- | Front Cafeteria | 352 | 23 | Yes | 20 | 1560 | 35 | 35 | AHU | 8 | 12480 | 1.6923 | 1 | 1.6923 | 1 | 21.6923 | 3
- | Computer Lab | 276 | 18 |  |  | 1456 | 33 | 18 | AHU | 8 | 11648 | 1.4217 | 1 | 1.4217 | 1 | 1.4217 | 1
- | Corridor | 156 | 10 |  |  | 650 | 14 | 10 | UV | 8 | 5200 | 1.8 | 1 | 1.8 | 1 | 1.8 | 1
- | Gym | 0 | 0 | Yes | 20 | 3950 | 89 | 89 | AHU | 8 | 31600 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Main Office | 212 | 14 |  |  | 460 | 10 | 10 | AHU | 8 | 3680 | 3.4565 | 1 | 3.4565 | 1 | 3.4565 | 1
- | Nurse's Bathroom | 0 | 0 |  |  | 28 | 0 | 0 | AHU | 8 | 224 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurse's Office |  | 0 | Yes | 20 | 168 | 3 | 3 | AHU | 8 | 1344 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse's Exam Room |  | 0 |  |  | 88 | 2 | 0 | AHU | 8 | 704 | 0 | 1 | 0 | 0 | 0 | 0
- | Office Bathroom | 0 | 0 |  |  | 25 | 0 | 0 | AHU | 8 | 200 | 0 | 1 | 0 | 0 | 0 | 0
- | Principal's Office | 0 | 0 | Yes | 20 | 160 | 3 | 3 | UV | 8 | 1280 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-22
School: | Amy Northwest @ Levering Middle School
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 |  |  | 750 | 17 | 0 |  | 8 | 6000 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom |  | 0 | Yes | 20 | 725 | 16 | 16 |  | 8 | 5800 | 0 | 1 | 0 | 0 | 20 | 3
106 | Nurse Office |  | 0 | Yes | 20 | 668 | 15 | 15 |  | 8 | 5344 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 |  |  | 666 | 15 | 0 |  | 8 | 5328 | 0 | 1 | 0 | 0 | 0 | 0
109 | IMC |  | 0 | Yes | 20 | 1457 | 33 | 33 |  | 8 | 11656 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 675 | 15 | 15 |  | 8 | 5400 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 | Yes | 20 | 683 | 15 | 15 |  | 8 | 5464 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 663 | 15 | 15 |  | 8 | 5304 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 |  |  | 691 | 15 | 0 |  | 8 | 5528 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom |  | 0 |  |  | 672 | 15 | 0 |  | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
209 | Classroom |  | 0 | Yes | 20 | 685 | 15 | 15 |  | 8 | 5480 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom |  | 0 |  |  | 677 | 15 | 0 |  | 8 | 5416 | 0 | 1 | 0 | 0 | 0 | 0
303/304 | Classroom |  | 0 | Yes | 20 | 1253 | 28 | 28 |  | 8 | 10024 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom |  | 0 | Yes | 20 | 675 | 15 | 15 |  | 8 | 5400 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom |  | 0 | Yes | 20 | 692 | 15 | 15 |  | 8 | 5536 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom |  | 0 | Yes | 20 | 670 | 15 | 15 |  | 8 | 5360 | 0 | 1 | 0 | 0 | 20 | 3
310 | Classroom |  | 0 |  |  | 1065 | 24 | 0 |  | 8 | 8520 | 0 | 1 | 0 | 0 | 0 | 0
Annex 1 | Classroom |  | 0 | Yes | 20 | 733 | 16 | 16 |  | 8 | 5864 | 0 | 1 | 0 | 0 | 20 | 3
Annex 2 | Classroom |  | 0 | Yes | 20 | 709 | 16 | 16 |  | 8 | 5672 | 0 | 1 | 0 | 0 | 20 | 3
Annex 3 | Classroom |  | 0 |  |  | 730 | 16 | 0 |  | 8 | 5840 | 0 | 1 | 0 | 0 | 0 | 0
Annex 4 | Classroom |  | 0 | Yes | 20 | 707 | 16 | 16 |  | 8 | 5656 | 0 | 1 | 0 | 0 | 20 | 3
Annex 5 | Classroom |  | 0 | Yes | 20 | 723 | 16 | 16 |  | 8 | 5784 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-01
School: | Abraham Lincoln High School
Vendor: | Devine Brothers | EMCOR Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
2 | Room 2 Office | 93 | 6 |  |  | 576 | 13 | 6 | AHU #7 | 8 | 4608 | 1.2109 | 1 | 1.2109 | 1 | 1.2109 | 1
3 | Room 3 Storage | 99 | 6 |  |  | 576 | 13 | 6 | AHU #8 | 8 | 4608 | 1.2891 | 1 | 1.2891 | 1 | 1.2891 | 1
4 | Room 4 Electrical | 103 | 6 |  |  | 576 | 13 | 6 | AHU #9 | 8 | 4608 | 1.3411 | 1 | 1.3411 | 1 | 1.3411 | 1
5 | Room 5 Kitchen | 461 | 30 |  |  | 576 | 13 | 13 | AHU #10 | 8 | 4608 | 6.0026 | 1 | 6.0026 | 2 | 6.0026 | 2
6 | Child Care | 1116 | 74 |  |  | 576 | 13 | 13 | AHU #11 | 8 | 4608 | 14.5312 | 1 | 14.5312 | 3 | 14.5312 | 3
8 | Child Care | 2029 | 135 |  |  | 1665 | 37 | 37 | AHU #12 | 8 | 13320 | 9.1396 | 1 | 9.1396 | 2 | 9.1396 | 2
100 | Classroom | 760 | 50 |  |  | 363 | 8 | 8 | UV1+UV2+AHU-2 | 8 | 2904 | 15.7025 | 1 | 15.7025 | 3 | 15.7025 | 3
100A | Classroom | 615 | 41 |  |  |  | 0 | 0 | UV+AHU-2
101 | Classroom | 1715 | 114 |  |  | 1247 | 28 | 28 | UV1+UV2+AHU-2 | 8 | 9976 | 10.3148 | 1 | 10.3148 | 3 | 10.3148 | 3
102 | Classroom | 1244 | 82 |  |  | 130 | 2 | 2 | UV+AHU-2 | 8 | 1040 | 71.7692 | 1 | 71.7692 | 5 | 71.7692 | 5
102A | Office | 25 | 1 |  |  | 140 | 3 | 1 | AHU-2 | 8 | 1120 | 1.3393 | 1 | 1.3393 | 1 | 1.3393 | 1
102B | Office | 35 | 2 |  |  | 107 | 2 | 2 | AHU-2 | 8 | 856 | 2.4533 | 1 | 2.4533 | 1 | 2.4533 | 1
103 | Classroom | 1636 | 109 |  |  | 1410 | 32 | 32 | UV1+UV2+AHU-2 | 8 | 11280 | 8.7021 | 1 | 8.7021 | 2 | 8.7021 | 2
104 | Classroom | 1067 | 71 |  |  | 806 | 18 | 18 | UV1+UV2+AHU-2 | 8 | 6448 | 9.9287 | 1 | 9.9287 | 2 | 9.9287 | 2
105 | Classroom | 1322 | 88 |  |  | 1140 | 25 | 25 | UV1+UV2+AHU-2 | 8 | 9120 | 8.6974 | 1 | 8.6974 | 2 | 8.6974 | 2
106 | Classroom | 1182 | 78 |  |  | 957 | 21 | 21 | UV1+UV2+AHU-2 | 8 | 7656 | 9.2633 | 1 | 9.2633 | 2 | 9.2633 | 2
107 | Classroom | 1894 | 126 |  |  | 1426 | 32 | 32 | UV1+UV2+AHU-2 | 8 | 11408 | 9.9614 | 1 | 9.9614 | 2 | 9.9614 | 2
107A | Storage Room | 300 | 20 |  |  |  | 0 | 0 | AHU-1
108 | Classroom | 1212 | 80 |  |  | 899 | 20 | 20 | UV1+UV2+AHU-2 | 8 | 7192 | 10.1112 | 1 | 10.1112 | 3 | 10.1112 | 3
109 | 109 OFFICE | 144 | 9 |  |  | 99 | 2 | 2 | AHU-2 / FC | 8 | 792 | 10.9091 | 1 | 10.9091 | 3 | 10.9091 | 3
110 | Classroom | 1159 | 77 |  |  | 868 | 19 | 19 | UV1+UV2+AHU-1 | 8 | 6944 | 10.0144 | 1 | 10.0144 | 3 | 10.0144 | 3
111 | Classroom | 1827 | 121 |  |  | 1426 | 32 | 32 | UV1+UV2+AHU-1 | 8 | 11408 | 9.609 | 1 | 9.609 | 2 | 9.609 | 2
112 | Classroom | 990 | 66 |  |  | 868 | 19 | 19 | UV1+UV2+AHU-1 | 8 | 6944 | 8.5541 | 1 | 8.5541 | 2 | 8.5541 | 2
114 | Classroom | 1114 | 74 |  |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 8 | 6696 | 9.9821 | 1 | 9.9821 | 2 | 9.9821 | 2
116 | Classroom | 663 | 44 |  |  | 896 | 20 | 20 | UV1+UV2+AHU-1 | 8 | 7168 | 5.5497 | 1 | 5.5497 | 2 | 5.5497 | 2
118 | Classroom | 932 | 62 |  |  | 1748 | 39 | 39 | UV1+UV2+AHU-1 | 8 | 13984 | 3.9989 | 1 | 3.9989 | 1 | 3.9989 | 1
120 | Classroom | 1141 | 76 |  |  | 864 | 19 | 19 | UV1+UV2+AHU-1 | 8 | 6912 | 9.9045 | 1 | 9.9045 | 2 | 9.9045 | 2
121 | Classroom | 1025 | 68 |  |  | 945 | 21 | 21 | UV1+UV2+AHU-1 | 8 | 7560 | 8.1349 | 1 | 8.1349 | 2 | 8.1349 | 2
122 | Classroom | 941 | 62 |  |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 8 | 6696 | 8.4319 | 1 | 8.4319 | 2 | 8.4319 | 2
123 | Classroom | 1848 | 123 |  |  | 2208 | 50 | 50 | UV1+UV2+UV1+UV2+AHU-1 | 8 | 17664 | 6.2772 | 1 | 6.2772 | 2 | 6.2772 | 2
124 | Classroom | 865 | 57 |  |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 8 | 6696 | 7.7509 | 1 | 7.7509 | 2 | 7.7509 | 2
125 | Classroom | 984 | 65 |  |  | 888 | 20 | 20 | UV1+UV2+AHU-1 | 8 | 7104 | 8.3108 | 1 | 8.3108 | 2 | 8.3108 | 2
126 | Classroom | 843 | 56 |  |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 8 | 6696 | 7.5538 | 1 | 7.5538 | 2 | 7.5538 | 2
128 | Classroom | 598 | 39 |  |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 8 | 6696 | 5.3584 | 1 | 5.3584 | 2 | 5.3584 | 2
129 | Classroom | 740 | 49 |  |  | 890 | 20 | 20 | UV1+UV2+AHU-1 | 8 | 7120 | 6.236 | 1 | 6.236 | 2 | 6.236 | 2
130 | Security | 0 | 0 |  |  | 108 | 2 | 0 | AHU-4 | 8 | 864 | 0 | 1 | 0 | 0 | 0 | 0
131 | Police | 0 | 0 |  |  | 180 | 4 | 0 | AHU-4 | 8 | 1440 | 0 | 1 | 0 | 0 | 0 | 0
132 | Classroom | 728 | 48 |  |  |  | 0 | 0 | UV1+UV2+UV3+UV4
133a | book room | 0 | 0 |  |  |  | 0 | 0 | AHU-4
135 | Classroom | 0 | 0 |  |  | 840 | 19 | 0 | UV1+UV2 | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
136 | office | 0 | 0 |  |  | 140 | 3 | 0 | AHU-4 | 8 | 1120 | 0 | 1 | 0 | 0 | 0 | 0
136a | storage | 0 | 0 |  |  |  | 0 | 0 | AHU-4
137 | storage | 0 | 0 |  |  |  | 0 | 0 | AHU-4
137a | storage | 0 | 0 |  |  |  | 0 | 0 | AHU-4
139 | office | 0 | 0 |  |  | 74.75 | 1 | 0 | AHU-4 | 8 | 598 | 0 | 1 | 0 | 0 | 0 | 0
140 | Main Office and waiting | 0 | 0 |  |  | 338 | 7 | 0 | AHU-4 | 8 | 2704 | 0 | 1 | 0 | 0 | 0 | 0
141 | Office | 0 | 0 |  |  |  | 0 | 0 | AHU-4
142 | Office | 0 | 0 |  |  |  | 0 | 0 | AHU-4
143 | Office | 0 | 0 |  |  | 99 | 2 | 0 | AHU-4 | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
144 | Office | 0 | 0 |  |  | 105 | 2 | 0 | AHU-4 | 8 | 840 | 0 | 1 | 0 | 0 | 0 | 0
145 | Office | 0 | 0 |  |  | 110 | 2 | 0 | AHU-4 | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
146 | Work Room | 0 | 0 |  |  | 636 | 14 | 0 | AHU-4 | 8 | 5088 | 0 | 1 | 0 | 0 | 0 | 0
147 | Conference | 0 | 0 |  |  | 192 | 4 | 0 | AHU-4 | 8 | 1536 | 0 | 1 | 0 | 0 | 0 | 0
147A | records | 0 | 0 |  |  | 300 | 6 | 0 | AHU-4 | 8 | 2400 | 0 | 1 | 0 | 0 | 0 | 0
149 | Health Suite | 0 | 0 |  |  | 495 | 11 | 0 | AHU-4 | 8 | 3960 | 0 | 1 | 0 | 0 | 0 | 0
149a | Exam | 0 | 0 |  |  | 188 | 4 | 0 | AHU-4 | 8 | 1504 | 0 | 1 | 0 | 0 | 0 | 0
149b | Exam | 0 | 0 |  |  | 197 | 4 | 0 | AHU-4 | 8 | 1576 | 0 | 1 | 0 | 0 | 0 | 0
149c | Office | 0 | 0 |  |  | 197 | 4 | 0 | AHU-4 | 8 | 1576 | 0 | 1 | 0 | 0 | 0 | 0
149D | Office | 0 | 0 |  |  | 109 | 2 | 0 | AHU-4 | 8 | 872 | 0 | 1 | 0 | 0 | 0 | 0
149E | Meditation | 0 | 0 |  |  | 209 | 4 | 0 | AHU-4 | 8 | 1672 | 0 | 1 | 0 | 0 | 0 | 0
150 | office | 0 | 0 |  |  | 117 | 2 | 0 | AHU-4 | 8 | 936 | 0 | 1 | 0 | 0 | 0 | 0
151 | copy center | 0 | 0 |  |  | 418 | 9 | 0 | AHU-4 | 8 | 3344 | 0 | 1 | 0 | 0 | 0 | 0
154 | office | 0 | 0 |  |  | 117 | 2 | 0 | AHU-4 | 8 | 936 | 0 | 1 | 0 | 0 | 0 | 0
155 | office | 0 | 0 |  |  | 121 | 2 | 0 | AHU-4 | 8 | 968 | 0 | 1 | 0 | 0 | 0 | 0
156 | work room | 0 | 0 |  |  | 875 | 19 | 0 | AHU-4 | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
157 | Records | 0 | 0 |  |  | 96 | 2 | 0 | AHU-4 | 8 | 768 | 0 | 1 | 0 | 0 | 0 | 0
158 | Roster Room | 0 | 0 |  |  | 143 | 3 | 0 | AHU-4 | 8 | 1144 | 0 | 1 | 0 | 0 | 0 | 0
159 | Office | 0 | 0 |  |  | 96 | 2 | 0 | AHU-4 | 8 | 768 | 0 | 1 | 0 | 0 | 0 | 0
160 | Classroom | 1346 | 89 |  |  | 1428 | 32 | 32 | UV1+UV2+AHU-3 | 8 | 11424 | 7.0693 | 1 | 7.0693 | 2 | 7.0693 | 2
160's | Men's Staff Restroom | 740 | 49 |  |  |  | 0 | 0 | AHU-3
160's | Women's Staff Restroom | 685 | 45 |  |  |  | 0 | 0 | AHU-3
160A | Science Prep | 423 | 28 |  |  | 891 | 20 | 20 | AHU-3 | 8 | 7128 | 3.5606 | 1 | 3.5606 | 1 | 3.5606 | 1
161 | Classroom | 829 | 55 |  |  | 891 | 20 | 20 | UV1+UV2+AHU-3 | 8 | 7128 | 6.9781 | 1 | 6.9781 | 2 | 6.9781 | 2
162 | Classroom | 1327 | 88 |  |  | 688 | 15 | 15 | UV1+UV2+AHU-3 | 8 | 5504 | 14.4658 | 1 | 14.4658 | 3 | 14.4658 | 3
163 | Classroom | 895 | 59 |  |  | 868 | 19 | 19 | UV1+UV2+AHU-3 | 8 | 6944 | 7.7333 | 1 | 7.7333 | 2 | 7.7333 | 2
164 | Classroom | 1334 | 88 |  |  | 1419 | 32 | 32 | UV1+UV2+AHU-3 | 8 | 11352 | 7.0507 | 1 | 7.0507 | 2 | 7.0507 | 2
164a | Science Prep | 44 | 2 |  |  |  | 0 | 0 | AHU-3
165 | Classroom | 942 | 62 |  |  | 868 | 19 | 19 | UV1+UV2+AHU-3 | 8 | 6944 | 8.1394 | 1 | 8.1394 | 2 | 8.1394 | 2
166 | Classroom | 1071 | 71 |  |  | 1155 | 26 | 26 | UV1+UV2+AHU-3 | 8 | 9240 | 6.9545 | 1 | 6.9545 | 2 | 6.9545 | 2
167 | Classroom | 458 | 30 |  |  | 918 | 20 | 20 | UV1+UV2+AHU-3 | 8 | 7344 | 3.7418 | 1 | 3.7418 | 1 | 3.7418 | 1
168 | Classroom | 1150 | 76 |  |  | 868 | 19 | 19 | UV1+UV2+AHU-3 | 8 | 6944 | 9.9366 | 1 | 9.9366 | 2 | 9.9366 | 2
169 | Classroom | 684 | 45 |  |  | 952 | 21 | 21 | UV1+UV2+AHU-3 | 8 | 7616 | 5.3887 | 1 | 5.3887 | 2 | 5.3887 | 2
170 | Classroom | 787 | 52 |  |  | 891 | 20 | 20 | UV+UV+AHU-3 | 8 | 7128 | 6.6246 | 1 | 6.6246 | 2 | 6.6246 | 2
171 | Classroom | 1006 | 67 |  |  | 918 | 20 | 20 | UV1+UV2+AHU-3 | 8 | 7344 | 8.219 | 1 | 8.219 | 2 | 8.219 | 2
172 | Classroom | 994 | 66 |  |  | 891 | 20 | 20 | UV1+UV2+AHU-3 | 8 | 7128 | 8.367 | 1 | 8.367 | 2 | 8.367 | 2
173 | Classroom | 565 | 37 |  |  | 891 | 20 | 20 | AHU-3 | 8 | 7128 | 4.7559 | 1 | 4.7559 | 2 | 4.7559 | 2
174 | Classroom | 736 | 49 |  |  | 896 | 20 | 20 | UV1+UV2+AHU-3 | 8 | 7168 | 6.1607 | 1 | 6.1607 | 2 | 6.1607 | 2
175 | Classroom | 1415 | 94 |  |  | 891 | 20 | 20 | UV1+UV2+AHU-3 | 8 | 7128 | 11.9108 | 1 | 11.9108 | 3 | 11.9108 | 3
176 | Classroom | 903 | 60 |  |  | 800 | 18 | 18 | UV1+UV2+AHU-3 | 8 | 6400 | 8.4656 | 1 | 8.4656 | 2 | 8.4656 | 2
177 | Classroom | 867 | 57 |  |  | 918 | 20 | 20 | UV1+UV2+AHU-3 | 8 | 7344 | 7.0833 | 1 | 7.0833 | 2 | 7.0833 | 2
190 | Music Classroom | 1656 | 110 |  |  | 1395 | 31 | 31 | AHU-8 | 8 | 11160 | 8.9032 | 1 | 8.9032 | 2 | 8.9032 | 2
190 | Office | 82 | 5 |  |  | 225 | 5 | 5 | AHU-8 | 8 | 1800 | 2.7333 | 1 | 2.7333 | 1 | 2.7333 | 1
190 | Storage | 52 | 3 |  |  | 1716 | 39 | 3 | AHU-8 | 8 | 13728 | 0.22727 | 1 | 0.22727 | 0 | 0.22727 | 0
190A | Classroom | 315 | 21 |  |  | 90 | 2 | 2 | AHU-8 | 8 | 720 | 26.25 | 1 | 26.25 | 4 | 26.25 | 4
190D | Classroom | 166 | 11 |  |  | 623 | 14 | 11 | AHU-8 | 8 | 4984 | 1.9984 | 1 | 1.9984 | 1 | 1.9984 | 1
190E | Classroom | 191 | 12 |  |  | 336 | 7 | 7 | AHU-8 | 8 | 2688 | 4.2634 | 1 | 4.2634 | 2 | 4.2634 | 2
191 | Music Classroom | 1393 | 92 |  |  | 2100 | 47 | 47 | AHU-8 | 8 | 16800 | 4.975 | 1 | 4.975 | 2 | 4.975 | 2
191A | Classroom | 68 | 4 |  |  | 56 | 1 | 1 | AHU-8 | 8 | 448 | 9.1071 | 1 | 9.1071 | 2 | 9.1071 | 2
191B | Classroom | 72 | 4 |  |  | 90 | 2 | 2 | AHU-8 | 8 | 720 | 6 | 1 | 6 | 2 | 6 | 2
191C | Classroom | 83 | 5 |  |  | 90 | 2 | 2 | AHU-8 | 8 | 720 | 6.9167 | 1 | 6.9167 | 2 | 6.9167 | 2
192 | Classroom | 998 | 66 |  |  | 1189 | 27 | 27 | AHU-8 | 8 | 9512 | 6.2952 | 1 | 6.2952 | 2 | 6.2952 | 2
200 | Classroom | 1117 | 74 |  |  | 1240 | 28 | 28 | UV1+UV2+AHU-2 | 8 | 9920 | 6.756 | 1 | 6.756 | 2 | 6.756 | 2
201 | Classroom | 1325 | 88 |  |  | 1485 | 33 | 33 | UV1+UV2+AHU-2 | 8 | 11880 | 6.6919 | 1 | 6.6919 | 2 | 6.6919 | 2
201A | Science Prep | 255 | 17 |  |  | 1486 | 33 | 17 | AHU-2 | 8 | 11888 | 1.287 | 1 | 1.287 | 1 | 1.287 | 1
202 | Classroom | 1325 | 88 |  |  | 2270 | 51 | 51 | UV1+UV2+UV3+AHU-2 | 8 | 18160 | 4.3778 | 1 | 4.3778 | 2 | 4.3778 | 2
202A | Office | 44 | 2 |  |  | 99 | 2 | 2 | AHU-2 | 8 | 792 | 3.3333 | 1 | 3.3333 | 1 | 3.3333 | 1
203 | Classroom | 1339 | 89 |  |  | 1575 | 35 | 35 | UV1+UV2+AHU-2 | 8 | 12600 | 6.3762 | 1 | 6.3762 | 2 | 6.3762 | 2
204 | Classroom | 403 | 26 |  |  | 806 | 18 | 18 | UV1+UV2+AHU-2 | 8 | 6448 | 3.75 | 1 | 3.75 | 1 | 3.75 | 1
205 | Classroom | 652 | 43 |  |  | 1395 | 31 | 31 | UV1+UV2+AHU-2 | 8 | 11160 | 3.5054 | 1 | 3.5054 | 1 | 3.5054 | 1
206 | Office Suite toilet |  | 0 |  |  | 1254 | 28 | 0 | AHU-2 | 8 | 10032 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom | 1006 | 67 |  |  | 891 | 20 | 20 | UV1+UV2+AHU-2 | 8 | 7128 | 8.468 | 1 | 8.468 | 2 | 8.468 | 2
208 | Classroom | 759 | 50 |  |  | 1152 | 26 | 26 | UV1+UV2+AHU-2 | 8 | 9216 | 4.9414 | 1 | 4.9414 | 2 | 4.9414 | 2
209 | Classroom | 419 | 27 |  |  | 864 | 19 | 19 | UV1+UV2+AHU-2 | 8 | 6912 | 3.6372 | 1 | 3.6372 | 1 | 3.6372 | 1
210 | Classroom | 614 | 40 |  |  | 837 | 19 | 19 | UV1+UV2+AHU-2 | 8 | 6696 | 5.5018 | 1 | 5.5018 | 2 | 5.5018 | 2
211 | Classroom | 994 | 66 |  |  | 390 | 8 | 8 | UV1+UV2+AHU-1 | 8 | 3120 | 19.1154 | 1 | 19.1154 | 3 | 19.1154 | 3
212 | Classroom | 615 | 41 |  |  | 858 | 19 | 19 | UV1+UV2+AHU-2 | 8 | 6864 | 5.3759 | 1 | 5.3759 | 2 | 5.3759 | 2
213 | Classroom | 995 | 66 |  |  | 891 | 20 | 20 | UV1+UV2+AHU-1 | 8 | 7128 | 8.3754 | 1 | 8.3754 | 2 | 8.3754 | 2
214 | Classroom | 625 | 41 |  |  | 924 | 21 | 21 | UV1+UV2+AHU-1 | 8 | 7392 | 5.0731 | 1 | 5.0731 | 2 | 5.0731 | 2
216 | Classroom | 564 | 37 |  |  | 918 | 20 | 20 | UV1+UV2+AHU-1 | 8 | 7344 | 4.6078 | 1 | 4.6078 | 2 | 4.6078 | 2
218 | Classroom | 729 | 48 |  |  | 837 | 19 | 19 | UV1+UV2+AHU-1 | 8 | 6696 | 6.5323 | 1 | 6.5323 | 2 | 6.5323 | 2
220 | Classroom | 1242 | 82 |  |  | 1395 | 31 | 31 | UV1+UV2+AHU-1 | 8 | 11160 | 6.6774 | 1 | 6.6774 | 2 | 6.6774 | 2
221 | Classroom | 653 | 43 |  |  | 924 | 21 | 21 | UV1+UV2+AHU-1 | 8 | 7392 | 5.3003 | 1 | 5.3003 | 2 | 5.3003 | 2
222 | Classroom | 909 | 60 |  |  | 891 | 20 | 20 | UV1+UV2+AHU-1 | 8 | 7128 | 7.6515 | 1 | 7.6515 | 2 | 7.6515 | 2
223 | Classroom | 848 | 56 |  |  | 864 | 19 | 19 | UV1+UV2+AHU-1 | 8 | 6912 | 7.3611 | 1 | 7.3611 | 2 | 7.3611 | 2
224 | Classroom | 2035 | 135 |  |  | 1972 | 44 | 44 | UV1+UV2+UV3+UV4+AHU-1 | 8 | 15776 | 7.7396 | 1 | 7.7396 | 2 | 7.7396 | 2
224A | Office | 96 | 6 |  |  | 121 | 2 | 2 | AHU-1 | 8 | 968 | 5.9504 | 1 | 5.9504 | 2 | 5.9504 | 2
225 | Classroom | 639 | 42 |  |  | 918 | 20 | 20 | UV1+UV2+AHU-1 | 8 | 7344 | 5.2206 | 1 | 5.2206 | 2 | 5.2206 | 2
226 | Classroom | 1282 | 85 |  |  | 1870 | 42 | 42 | UV1+UV2+UV3+UV4+AHU-1 | 8 | 14960 | 5.1417 | 1 | 5.1417 | 2 | 5.1417 | 2
226A | Office | 41 | 2 |  |  | 123 | 2 | 2 | AHU-1 | 8 | 984 | 2.5 | 1 | 2.5 | 1 | 2.5 | 1
227 | Classroom | 825 | 55 |  |  | 891 | 20 | 20 | UV1+UV2+AHU-1 | 8 | 7128 | 6.9444 | 1 | 6.9444 | 2 | 6.9444 | 2
228 | Classroom | 551 | 36 |  |  | 924 | 21 | 21 | UV1+UV2+AHU-1 | 8 | 7392 | 4.4724 | 1 | 4.4724 | 2 | 4.4724 | 2
229 | Classroom | 800 | 53 |  |  | 878 | 19 | 19 | UV1+UV2+AHU-1 | 8 | 7024 | 6.8337 | 1 | 6.8337 | 2 | 6.8337 | 2
- | 2nd floor Corridor | 1498 | 99 |  |  |  | 0 | 0 | AHU-1
- | Gym | 40145 | 2676 |  |  | 18327 | 416 | 416 | AHU-9+AHU-10 | 8 | 146616 | 16.4286 | 2.3523 | 38.6458 | 4 | 38.6458 | 4
- | 2nd Floor B Corridor | 543 | 36 |  |  |  | 0 | 0 | AHU-2
- | 2nd Floor Staff toilet |  | 0 |  |  |  | 0 | 0 | AHU-2
- | Auditorium | 16961 | 1130 |  |  | 6745 | 153 | 153 | AHU-6 | 8 | 53960 | 18.8595 | 1.4912 | 28.1225 | 4 | 28.1225 | 4
- | Small Gym | 0 | 0 |  |  | 6438 | 146 | 0 | AHU-11 | 8 | 51504 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | Weight Room | 0 | 0 |  |  | 2450 | 55 | 0 | AHU-12 | 8 | 19600 | 0 | 1 | 0 | 0 | 0 | 0
- | Counselor Center | 0 | 0 |  |  |  | 0 | 0 | AHU-4
- | Child Care- Hallway | 240 | 16 |  |  |  | 0 | 0 | AHU #13
- | Child Care- Kitchen | 47 | 3 |  |  | 330 | 7 | 3 | AHU-7 | 8 | 2640 | 1.0682 | 1 | 1.0682 | 1 | 1.0682 | 1
- | Child Care- Lending Library | 96 | 6 | Yes | 20 | 1184 | 26 | 26 | AHU-7 | 8 | 9472 | 0.60811 | 1 | 0.60811 | 0 | 20.6081 | 3
- | Library/IMC | 1522 | 101 |  |  | 8640 | 196 | 101 | AHU #14 | 8 | 69120 | 1.3212 | 1.4912 | 1.9701 | 1 | 1.9701 | 1
- | Child Care Office | 9 | 0 |  |  | 99 | 2 | 0 | AHU-7 | 8 | 792 | 0.68182 | 1 | 0.68182 | 0 | 0.68182 | 0
- | Admin 140's Area Corridor | 0 | 0 |  |  | 375 | 8 | 0 | AHU-4 | 8 | 3000 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym Office |  | 0 |  |  | 343 | 7 | 0 |  | 8 | 2744 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym office 2 |  | 0 |  |  | 280 | 6 | 0 |  | 8 | 2240 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym office 3 |  | 0 |  |  | 260 | 5 | 0 |  | 8 | 2080 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-12
School: | Lingelbach Elementary School
Vendor: | Devine Brothers | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 227 | 15 |  |  | 968 | 22 | 15 | UV | 8 | 7744 | 1.7588 | 1 | 1.7588 | 1 | 1.7588 | 1
102 | Classroom | 477 | 31 |  |  | 968 | 22 | 22 | UV | 8 | 7744 | 3.6958 | 1 | 3.6958 | 1 | 3.6958 | 1
103 | Classroom | 219 | 14 |  |  | 889 | 20 | 14 | UV | 8 | 7112 | 1.8476 | 1 | 1.8476 | 1 | 1.8476 | 1
104 | Classroom | 0 | 0 |  |  | 963 | 21 | 0 | UV | 8 | 7704 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom | 268 | 17 |  |  | 941 | 21 | 17 | UV | 8 | 7528 | 2.136 | 1 | 2.136 | 1 | 2.136 | 1
106 | Classroom | 293 | 19 |  |  | 971 | 22 | 19 | UV | 8 | 7768 | 2.2631 | 1 | 2.2631 | 1 | 2.2631 | 1
200 | Classroom | 444 | 29 |  |  | 1394 | 31 | 29 | UV | 8 | 11152 | 2.3888 | 1 | 2.3888 | 1 | 2.3888 | 1
200A | Classroom | 675 | 45 |  |  | 1235 | 28 | 28 | UV | 8 | 9880 | 4.0992 | 1 | 4.0992 | 2 | 4.0992 | 2
201 | Classroom | 514 | 34 |  |  | 969 | 22 | 22 | UV | 8 | 7752 | 3.9783 | 1 | 3.9783 | 1 | 3.9783 | 1
202 | Classroom | 280 | 18 |  |  | 969 | 22 | 18 | UV | 8 | 7752 | 2.1672 | 1 | 2.1672 | 1 | 2.1672 | 1
203 | Classroom | 278 | 18 |  |  | 971 | 22 | 18 | UV | 8 | 7768 | 2.1473 | 1 | 2.1473 | 1 | 2.1473 | 1
204 | Classroom | 290 | 19 |  |  | 971 | 22 | 19 | UV | 8 | 7768 | 2.24 | 1 | 2.24 | 1 | 2.24 | 1
205 | Classroom | 336 | 22 |  |  | 955 | 21 | 21 | UV | 8 | 7640 | 2.6387 | 1 | 2.6387 | 1 | 2.6387 | 1
206 | Classroom | 278 | 18 |  |  | 969 | 22 | 18 | UV | 8 | 7752 | 2.1517 | 1 | 2.1517 | 1 | 2.1517 | 1
301 | Classroom | 285 | 19 |  |  | 940 | 21 | 19 | UV | 8 | 7520 | 2.2739 | 1 | 2.2739 | 1 | 2.2739 | 1
302 | Classroom | 795 | 53 |  |  | 937 | 21 | 21 | UV | 8 | 7496 | 6.3634 | 1 | 6.3634 | 2 | 6.3634 | 2
303 | Classroom | 837 | 55 |  |  | 933 | 21 | 21 | UV | 8 | 7464 | 6.7283 | 1 | 6.7283 | 2 | 6.7283 | 2
303A | Classroom | 357 | 23 |  |  | 463 | 10 | 10 | UV | 8 | 3704 | 5.7829 | 1 | 5.7829 | 2 | 5.7829 | 2
304 | Classroom | 406 | 27 |  |  | 464 | 10 | 10 | UV | 8 | 3712 | 6.5625 | 1 | 6.5625 | 2 | 6.5625 | 2
305 | Classroom | 395 | 26 |  |  | 967 | 21 | 21 | UV | 8 | 7736 | 3.0636 | 1 | 3.0636 | 1 | 3.0636 | 1
306 | Classroom | 906 | 60 |  |  | 944 | 21 | 21 | UV | 8 | 7552 | 7.1981 | 1 | 7.1981 | 2 | 7.1981 | 2
- | Main Office |  | 0 | Yes | 20 | 332 | 7 | 7 |  | 8 | 2656 | 0 | 1 | 0 | 0 | 20 | 3
- | Principals Office |  | 0 | Yes | 20 | 262 | 5 | 5 |  | 8 | 2096 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses Office |  | 0 | Yes | 20 | 269 | 6 | 6 |  | 8 | 2152 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 841 | 56 |  |  | 2847 | 64 | 56 | AHU | 8 | 22776 | 2.2155 | 1.062 | 2.3529 | 1 | 2.3529 | 1
- | Gym/Cafeteria | 1451 | 96 |  |  | 2340 | 53 | 53 | AHU | 8 | 18720 | 4.6506 | 1 | 4.6506 | 2 | 4.6506 | 2
- | North Stairwell | 0 | 0 |  |  | 168 | 3 | 0 | UV | 8 | 1344 | 0 | 1 | 0 | 0 | 0 | 0
- | South Stairwell | 0 | 0 |  |  | 168 | 3 | 0 | UV | 8 | 1344 | 0 | 1 | 0 | 0 | 0 | 0
- | Library | 855 | 57 |  |  | 2312 | 52 | 52 | UV | 8 | 18496 | 2.7736 | 1 | 2.7736 | 1 | 2.7736 | 1
Sheet Last Modified: | 2021-04-05
School: | Alain Locke Elementary School
Vendor: | Devine Brothers | Devine Brothers Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Auditorium | 2700 | 180 |  |  | 3658 | 83 | 83 | AHU | 8 | 29264 | 5.5358 | 1.062 | 5.8792 | 2 | 5.8792 | 2
- | Gym/Cafeteria | 2014 | 134 |  |  | 4464 | 101 | 101 | AHU | 8 | 35712 | 3.3837 | 1.062 | 3.5936 | 1 | 3.5936 | 1
- | Library | 585 | 39 |  |  | 1352 | 30 | 30 | UV | 8 | 10816 | 3.2452 | 1 | 3.2452 | 1 | 3.2452 | 1
- | Main Office | 425 | 28 |  |  | 1213 | 27 | 27 | UV | 8 | 9704 | 2.6278 | 1 | 2.6278 | 1 | 2.6278 | 1
- | Principals Office | 0 | 0 | Yes | 20 | 384 | 8 | 8 | UV | 8 | 3072 | 0 | 1 | 0 | 0 | 20 | 3
100 | Classroom | 421 | 28 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 3.7589 | 1 | 3.7589 | 1 | 3.7589 | 1
101 | Classroom | 454 | 30 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 4.0536 | 1 | 4.0536 | 2 | 4.0536 | 2
102 | Classroom | 425 | 28 |  |  | 864 | 19 | 19 | UV | 8 | 6912 | 3.6892 | 1 | 3.6892 | 1 | 3.6892 | 1
103 | Classroom | 318 | 21 |  |  | 432 | 9 | 9 | UV | 8 | 3456 | 5.5208 | 1 | 5.5208 | 2 | 5.5208 | 2
104 | Classroom | 405 | 27 |  |  | 744 | 16 | 16 | UV | 8 | 5952 | 4.0827 | 1 | 4.0827 | 2 | 4.0827 | 2
105 | Classroom | 453 | 30 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 4.0446 | 1 | 4.0446 | 2 | 4.0446 | 2
107 | Classroom | 435 | 29 |  |  | 1064 | 24 | 24 | UV | 8 | 8512 | 3.0663 | 1 | 3.0663 | 1 | 3.0663 | 1
108A | Office A Library |  | 0 | Yes | 20 | 156 | 3 | 3 |  | 8 | 1248 | 0 | 1 | 0 | 0 | 20 | 3
108B | Office B Library |  | 0 | Yes | 20 | 156 | 3 | 3 |  | 8 | 1248 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 428 | 28 |  |  | 864 | 19 | 19 | UV | 8 | 6912 | 3.7153 | 1 | 3.7153 | 1 | 3.7153 | 1
111 | Classroom | 394 | 26 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 3.5179 | 1 | 3.5179 | 1 | 3.5179 | 1
112 | Classroom | 330 | 22 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 2.9464 | 1 | 2.9464 | 1 | 2.9464 | 1
113 | Classroom | 416 | 27 |  |  | 980 | 22 | 22 | UV | 8 | 7840 | 3.1837 | 1 | 3.1837 | 1 | 3.1837 | 1
115 | Classroom | 393 | 26 |  |  | 1248 | 28 | 26 | UV | 8 | 9984 | 2.3618 | 1 | 2.3618 | 1 | 2.3618 | 1
116A | Counselor Office |  | 0 | Yes | 20 | 132 | 3 | 3 |  | 8 | 1056 | 0 | 1 | 0 | 0 | 20 | 3
116B | COVID Quarantine |  | 0 | Yes | 20 | 132 | 3 | 3 |  | 8 | 1056 | 0 | 1 | 0 | 0 | 20 | 3
117 | Classroom | 321 | 21 |  |  | 1440 | 32 | 21 | UV | 8 | 11520 | 1.6719 | 1 | 1.6719 | 1 | 1.6719 | 1
200 | Classroom | 592 | 39 |  |  | 875 | 19 | 19 | UV | 8 | 7000 | 5.0743 | 1 | 5.0743 | 2 | 5.0743 | 2
201 | Classroom | 340 | 22 |  |  | 864 | 19 | 19 | UV | 8 | 6912 | 2.9514 | 1 | 2.9514 | 1 | 2.9514 | 1
202 | Classroom | 341 | 22 |  |  | 875 | 19 | 19 | UV | 8 | 7000 | 2.9229 | 1 | 2.9229 | 1 | 2.9229 | 1
203 | Classroom | 485 | 32 |  |  | 864 | 19 | 19 | UV | 8 | 6912 | 4.2101 | 1 | 4.2101 | 2 | 4.2101 | 2
204 | Classroom | 279 | 18 |  |  | 875 | 19 | 18 | UV | 8 | 7000 | 2.3914 | 1 | 2.3914 | 1 | 2.3914 | 1
205 | Classroom | 295 | 19 |  |  | 864 | 19 | 19 | UV | 8 | 6912 | 2.5608 | 1 | 2.5608 | 1 | 2.5608 | 1
207A | Classroom | 0 | 0 | Yes | 20 | 168 | 3 | 3 | UV | 8 | 1344 | 0 | 1 | 0 | 0 | 20 | 3
207B | Classroom | 300 | 20 |  |  | 336 | 7 | 7 | UV | 8 | 2688 | 6.6964 | 1 | 6.6964 | 2 | 6.6964 | 2
208 | Classroom | 349 | 23 |  |  | 1225 | 27 | 23 | UV | 8 | 9800 | 2.1367 | 1 | 2.1367 | 1 | 2.1367 | 1
209 | Classroom | 348 | 23 |  |  | 864 | 19 | 19 | UV | 8 | 6912 | 3.0208 | 1 | 3.0208 | 1 | 3.0208 | 1
210 | Classroom | 295 | 19 |  |  | 480 | 10 | 10 | UV | 8 | 3840 | 4.6094 | 1 | 4.6094 | 2 | 4.6094 | 2
211 | Classroom | 360 | 24 |  |  | 864 | 19 | 19 | UV | 8 | 6912 | 3.125 | 1 | 3.125 | 1 | 3.125 | 1
212 | Classroom | 332 | 22 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 2.9643 | 1 | 2.9643 | 1 | 2.9643 | 1
213 | Classroom | 297 | 19 |  |  | 875 | 19 | 19 | UV | 8 | 7000 | 2.5457 | 1 | 2.5457 | 1 | 2.5457 | 1
300 | Classroom | 419 | 27 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 3.7411 | 1 | 3.7411 | 1 | 3.7411 | 1
301 | Classroom | 416 | 27 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 3.7143 | 1 | 3.7143 | 1 | 3.7143 | 1
302 | Classroom | 375 | 25 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 3.3482 | 1 | 3.3482 | 1 | 3.3482 | 1
303 | Classroom | 395 | 26 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 3.5268 | 1 | 3.5268 | 1 | 3.5268 | 1
304 | Classroom | 398 | 26 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 3.5536 | 1 | 3.5536 | 1 | 3.5536 | 1
305 | Classroom | 411 | 27 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 3.6696 | 1 | 3.6696 | 1 | 3.6696 | 1
307A | Office | 205 | 13 |  |  | 336 | 7 | 7 | UV | 8 | 2688 | 4.5759 | 1 | 4.5759 | 2 | 4.5759 | 2
307B | Office | 0 | 0 | Yes | 20 | 168 | 3 | 3 | UV | 8 | 1344 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom | 383 | 25 |  |  | 864 | 19 | 19 | UV | 8 | 6912 | 3.3247 | 1 | 3.3247 | 1 | 3.3247 | 1
309 | Classroom | 365 | 24 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 3.2589 | 1 | 3.2589 | 1 | 3.2589 | 1
310 | Classroom | 325 | 21 |  |  | 875 | 19 | 19 | UV | 8 | 7000 | 2.7857 | 1 | 2.7857 | 1 | 2.7857 | 1
311 | Classroom | 309 | 20 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 2.7589 | 1 | 2.7589 | 1 | 2.7589 | 1
312 | Classroom | 419 | 27 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 3.7411 | 1 | 3.7411 | 1 | 3.7411 | 1
313 | Classroom | 346 | 23 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 3.0893 | 1 | 3.0893 | 1 | 3.0893 | 1
- | Nurses office |  | 0 | Yes | 20 | 352 | 8 | 8 | UV | 8 | 2816 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-08
School: | William Loesche Elementary School
Vendor: | Devine Brothers | Devine Brothers Retest
Devine Brothers 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 286 | 19 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 2.5536 | 1 | 2.5536 | 1 | 2.5536 | 1
101 | Classroom | 282 | 18 |  |  | 840 | 19 | 18 | UV | 8 | 6720 | 2.5179 | 1 | 2.5179 | 1 | 2.5179 | 1
102 | Classroom | 82 | 5 | Yes | 20 | 784 | 17 | 17 | UV | 8 | 6272 | 0.78444 | 1 | 0.78444 | 0 | 20.7844 | 3
103 | Classroom | 288 | 19 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 2.5714 | 1 | 2.5714 | 1 | 2.5714 | 1
104 | Classroom | 0 | 0 |  |  | 840 | 19 | 0 | UV | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom | 300 | 20 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 2.6786 | 1 | 2.6786 | 1 | 2.6786 | 1
107 | Classroom | 288 | 19 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 2.5714 | 1 | 2.5714 | 1 | 2.5714 | 1
108 | Classroom | 213 | 14 | Yes | 20 | 1122 | 25 | 25 | UV | 8 | 8976 | 1.4238 | 1 | 1.4238 | 1 | 21.4238 | 3
109 | Classroom | 185 | 12 |  |  | 840 | 19 | 12 | UV | 8 | 6720 | 1.6518 | 1 | 1.6518 | 1 | 1.6518 | 1
110 | Classroom | 156 | 10 | Yes | 20 | 840 | 19 | 19 | UV | 8 | 6720 | 1.3929 | 1 | 1.3929 | 1 | 21.3929 | 3
111 | Classroom | 190 | 12 | Yes | 20 | 882 | 20 | 20 | UV | 8 | 7056 | 1.6156 | 1 | 1.6156 | 1 | 21.6156 | 3
112 | Classroom | 285 | 19 |  |  | 729 | 16 | 16 | UV | 8 | 5832 | 2.9321 | 1 | 2.9321 | 1 | 2.9321 | 1
200 | Classroom | 258 | 17 |  |  | 840 | 19 | 17 | UV | 8 | 6720 | 2.3036 | 1 | 2.3036 | 1 | 2.3036 | 1
201 | Classroom | 292 | 19 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 2.6071 | 1 | 2.6071 | 1 | 2.6071 | 1
202 | Classroom | 283 | 18 |  |  | 840 | 19 | 18 | UV | 8 | 6720 | 2.5268 | 1 | 2.5268 | 1 | 2.5268 | 1
203 | Classroom | 158 | 10 | Yes | 20 | 840 | 19 | 19 | UV | 8 | 6720 | 1.4107 | 1 | 1.4107 | 1 | 21.4107 | 3
204 | Classroom | 262 | 17 |  |  | 840 | 19 | 17 | UV | 8 | 6720 | 2.3393 | 1 | 2.3393 | 1 | 2.3393 | 1
205 | Classroom | 205 | 13 | Yes | 20 | 840 | 19 | 19 | UV | 8 | 6720 | 1.8304 | 1 | 1.8304 | 1 | 21.8304 | 3
206 | Classroom | 153 | 10 |  |  | 476 | 10 | 10 | UV | 8 | 3808 | 2.4107 | 1 | 2.4107 | 1 | 2.4107 | 1
207 | Classroom | 297 | 19 |  |  | 840 | 19 | 19 | UV | 8 | 6720 | 2.6518 | 1 | 2.6518 | 1 | 2.6518 | 1
208 | Classroom | 210 | 14 |  |  | 840 | 19 | 14 | UV | 8 | 6720 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
208A | Classroom | 150 | 10 |  |  | 252 | 5 | 5 | UV | 8 | 2016 | 4.4643 | 1 | 4.4643 | 2 | 4.4643 | 2
209 | Classroom | 184 | 12 | Yes | 20 | 840 | 19 | 19 | UV | 8 | 6720 | 1.6429 | 1 | 1.6429 | 1 | 21.6429 | 3
210 | Classroom | 193 | 12 |  |  | 780 | 17 | 12 | UV | 8 | 6240 | 1.8558 | 1 | 1.8558 | 1 | 1.8558 | 1
211 | Classroom | 142 | 9 | Yes | 20 | 783 | 17 | 17 | UV | 8 | 6264 | 1.3602 | 1 | 1.3602 | 1 | 21.3602 | 3
212 | Classroom | 267 | 17 |  |  | 840 | 19 | 17 | UV | 8 | 6720 | 2.3839 | 1 | 2.3839 | 1 | 2.3839 | 1
214 | Classroom | 280 | 18 |  |  | 1212 | 27 | 18 | UV | 8 | 9696 | 1.7327 | 1 | 1.7327 | 1 | 1.7327 | 1
215 | Classroom | 268 | 17 |  |  | 1232 | 28 | 17 | UV | 8 | 9856 | 1.6315 | 1 | 1.6315 | 1 | 1.6315 | 1
216 | Classroom | 415 | 27 |  |  | 756 | 17 | 17 | UV | 8 | 6048 | 4.1171 | 1 | 4.1171 | 2 | 4.1171 | 2
217 | Classroom | 276 | 18 |  |  | 841 | 19 | 18 | UV | 8 | 6728 | 2.4614 | 1 | 2.4614 | 1 | 2.4614 | 1
218 | Classroom | 144 | 9 | Yes | 20 | 840 | 19 | 19 | UV | 8 | 6720 | 1.2857 | 1 | 1.2857 | 1 | 21.2857 | 3
219 | Classroom | 106 | 7 | Yes | 20 | 840 | 19 | 19 | UV | 8 | 6720 | 0.94643 | 1 | 0.94643 | 0 | 20.9464 | 3
220 | Classroom | 246 | 16 |  |  | 870 | 19 | 16 | UV | 8 | 6960 | 2.1207 | 1 | 2.1207 | 1 | 2.1207 | 1
221 | Classroom | 140 | 9 |  |  | 870 | 19 | 9 | UV | 8 | 6960 | 1.2069 | 1 | 1.2069 | 1 | 1.2069 | 1
222 | Classroom | 106 | 7 |  |  | 840 | 19 | 7 | UV | 8 | 6720 | 0.94643 | 1 | 0.94643 | 0 | 0.94643 | 0
223 | Classroom | 175 | 11 |  |  | 840 | 19 | 11 | UV | 8 | 6720 | 1.5625 | 1 | 1.5625 | 1 | 1.5625 | 1
224 | Classroom | 94 | 6 |  |  | 840 | 19 | 6 | UV | 8 | 6720 | 0.83929 | 1 | 0.83929 | 0 | 0.83929 | 0
A-1 | Classroom | 242 | 16 |  |  | 884 | 20 | 16 | UV | 8 | 7072 | 2.0532 | 1 | 2.0532 | 1 | 2.0532 | 1
A-2 | Classroom | 254 | 16 |  |  | 884 | 20 | 16 | UV | 8 | 7072 | 2.155 | 1 | 2.155 | 1 | 2.155 | 1
A-3 | Classroom | 298 | 19 |  |  | 884 | 20 | 19 | UV | 8 | 7072 | 2.5283 | 1 | 2.5283 | 1 | 2.5283 | 1
A-4 | Classroom | 281 | 18 |  |  | 884 | 20 | 18 | UV | 8 | 7072 | 2.384 | 1 | 2.384 | 1 | 2.384 | 1
- | A-wing Mech. Rm | 0 | 0 |  |  | 358 | 8 | 0 | UV | 8 | 2864 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 |  |  | 3600 | 81 | 0 | AHU | 8 | 28800 | 0 | 1.062 | 0 | 0 | 0 | 0
B-1 | Classroom | 314 | 20 |  |  | 806 | 18 | 18 | UV | 8 | 6448 | 2.9218 | 1 | 2.9218 | 1 | 2.9218 | 1
B-2 | Classroom | 311 | 20 |  |  | 806 | 18 | 18 | UV | 8 | 6448 | 2.8939 | 1 | 2.8939 | 1 | 2.8939 | 1
B-3 | Classroom | 300 | 20 |  |  | 806 | 18 | 18 | UV | 8 | 6448 | 2.7916 | 1 | 2.7916 | 1 | 2.7916 | 1
B-4 | Classroom | 313 | 20 |  |  | 806 | 18 | 18 | UV | 8 | 6448 | 2.9125 | 1 | 2.9125 | 1 | 2.9125 | 1
B-5 | Classroom | 287 | 19 |  |  | 806 | 18 | 18 | UV | 8 | 6448 | 2.6706 | 1 | 2.6706 | 1 | 2.6706 | 1
B-6 | Classroom | 297 | 19 |  |  | 905 | 20 | 19 | UV | 8 | 7240 | 2.4613 | 1 | 2.4613 | 1 | 2.4613 | 1
B-7 | Classroom | 285 | 19 |  |  | 905 | 20 | 19 | UV | 8 | 7240 | 2.3619 | 1 | 2.3619 | 1 | 2.3619 | 1
B-8 | Classroom | 304 | 20 |  |  | 905 | 20 | 20 | UV | 8 | 7240 | 2.5193 | 1 | 2.5193 | 1 | 2.5193 | 1
B-9 | Classroom | 282 | 18 |  |  | 905 | 20 | 18 | UV | 8 | 7240 | 2.337 | 1 | 2.337 | 1 | 2.337 | 1
- | Backstage | 0 | 0 |  |  | 180 | 4 | 0 | UV | 8 | 1440 | 0 | 1 | 0 | 0 | 0 | 0
- | Backstage Dressing Rm. | 172 | 11 |  |  | 252 | 5 | 5 | UV | 8 | 2016 | 5.119 | 1 | 5.119 | 2 | 5.119 | 2
- | Cafeteria | 0 | 0 | Yes | 20 | 5540 | 125 | 125 | AHU | 8 | 44320 | 0 | 1.062 | 0 | 0 | 20 | 3
- | GYM | 0 | 0 |  |  | 4496 | 102 | 0 | AHU | 8 | 35968 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Library | 0 | 0 |  |  | 1131 | 25 | 0 | UV | 8 | 9048 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office | 292 | 19 |  |  | 992 | 22 | 19 | UV | 8 | 7936 | 2.2077 | 1 | 2.2077 | 1 | 2.2077 | 1
- | Nurse's Office | 94 | 6 |  |  | 706 | 16 | 6 | UV | 8 | 5648 | 0.99858 | 1 | 0.99858 | 0 | 0.99858 | 0
- | Principal's Office | 148 | 9 |  |  | 308 | 7 | 7 | UV | 8 | 2464 | 3.6039 | 1 | 3.6039 | 1 | 3.6039 | 1
Sheet Last Modified: | 2021-03-24
School: | James Logan Elementary-Middle School | House Fan Abated
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B-1 | Classroom | 1228 | 81 |  |  | 889 | 20 | 20 | House Fan | 8 | 7112 | 10.36 | 1 | 10.36 | 3 | 10.36 | 3
B-2 | Classroom | 975 | 65 |  |  | 737 | 16 | 16 | House Fan | 8 | 5896 | 9.922 | 1 | 9.922 | 2 | 9.922 | 2
B-3 | Classroom | 1131 | 75 |  |  | 1017 | 23 | 23 | House Fan | 8 | 8136 | 8.3407 | 1 | 8.3407 | 2 | 8.3407 | 2
101 | Classroom | 539 | 35 |  |  | 729 | 16 | 16 | House Fan | 8 | 5832 | 5.5453 | 1 | 5.5453 | 2 | 5.5453 | 2
102 | Classroom | 578 | 38 |  |  | 732 | 16 | 16 | House Fan | 8 | 5856 | 5.9221 | 1 | 5.9221 | 2 | 5.9221 | 2
103 | Classroom | 593 | 39 |  |  | 724 | 16 | 16 | House Fan | 8 | 5792 | 6.143 | 1 | 6.143 | 2 | 6.143 | 2
104 | Classroom | 674 | 44 |  |  | 676 | 15 | 15 | House Fan | 8 | 5408 | 7.4778 | 1 | 7.4778 | 2 | 7.4778 | 2
104A | Office | 0 | 0 |  |  | 177 | 4 | 0 | House Fan | 8 | 1416 | 0 | 1 | 0 | 0 | 0 | 0
105 | Teacher's Lounge | 617 | 41 |  |  | 650 | 14 | 14 | House Fan | 8 | 5200 | 7.1192 | 1 | 7.1192 | 2 | 7.1192 | 2
106 | Classroom | 621 | 41 |  |  | 726 | 16 | 16 | House Fan | 8 | 5808 | 6.4153 | 1 | 6.4153 | 2 | 6.4153 | 2
107 | Classroom | 376 | 25 |  |  | 722 | 16 | 16 | House Fan | 8 | 5776 | 3.9058 | 1 | 3.9058 | 1 | 3.9058 | 1
108 | Classroom | 849 | 56 |  |  | 717 | 16 | 16 | House Fan | 8 | 5736 | 8.8808 | 1 | 8.8808 | 2 | 8.8808 | 2
201 | IMC | 509 | 33 |  |  | 639 | 14 | 14 | House Fan | 8 | 5112 | 5.9742 | 1 | 5.9742 | 2 | 5.9742 | 2
202 | IMC | 632 | 42 |  |  | 639 | 14 | 14 | House Fan | 8 | 5112 | 7.4178 | 1 | 7.4178 | 2 | 7.4178 | 2
203 | Classroom | 551 | 36 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 5.7396 | 1 | 5.7396 | 2 | 5.7396 | 2
204 | Office Storage | 0 | 0 |  |  | 201 | 4 | 0 | House Fan | 8 | 1608 | 0 | 1 | 0 | 0 | 0 | 0
205 | Classroom | 519 | 34 |  |  | 718 | 16 | 16 | House Fan | 8 | 5744 | 5.4213 | 1 | 5.4213 | 2 | 5.4213 | 2
205A | Office | 0 | 0 |  |  | 164 | 3 | 0 | House Fan | 8 | 1312 | 0 | 1 | 0 | 0 | 0 | 0
206 | Classroom | 715 | 47 |  |  | 735 | 16 | 16 | House Fan | 8 | 5880 | 7.2959 | 1 | 7.2959 | 2 | 7.2959 | 2
206A | Counselor | 0 | 0 |  |  | 231 | 5 | 0 | House Fan | 8 | 1848 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom | 394 | 26 |  |  | 723 | 16 | 16 | House Fan | 8 | 5784 | 4.0871 | 1 | 4.0871 | 2 | 4.0871 | 2
208 | Classroom | 423 | 28 |  |  | 724 | 16 | 16 | House Fan | 8 | 5792 | 4.3819 | 1 | 4.3819 | 2 | 4.3819 | 2
209 | Classroom | 575 | 38 |  |  | 725 | 16 | 16 | House Fan | 8 | 5800 | 5.9483 | 1 | 5.9483 | 2 | 5.9483 | 2
209A | Classroom | 0 | 0 |  |  | 260 | 5 | 0 | House Fan | 8 | 2080 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom | 522 | 34 |  |  | 679 | 15 | 15 | House Fan | 8 | 5432 | 5.7658 | 1 | 5.7658 | 2 | 5.7658 | 2
302 | Classroom | 549 | 36 |  |  | 679 | 15 | 15 | House Fan | 8 | 5432 | 6.0641 | 1 | 6.0641 | 2 | 6.0641 | 2
303 | Classroom | 458 | 30 |  |  | 724 | 16 | 16 | House Fan | 8 | 5792 | 4.7445 | 1 | 4.7445 | 2 | 4.7445 | 2
304 | Classroom | 481 | 32 |  |  | 714 | 16 | 16 | House Fan | 8 | 5712 | 5.0525 | 1 | 5.0525 | 2 | 5.0525 | 2
305 | Classroom | 347 | 23 |  |  | 890 | 20 | 20 | House Fan | 8 | 7120 | 2.9242 | 1 | 2.9242 | 1 | 2.9242 | 1
306 | Classroom | 381 | 25 |  |  | 750 | 17 | 17 | House Fan | 8 | 6000 | 3.81 | 1 | 3.81 | 1 | 3.81 | 1
307 | Classroom | 312 | 20 |  |  | 992 | 22 | 20 | House Fan | 8 | 7936 | 2.3589 | 1 | 2.3589 | 1 | 2.3589 | 1
308 | Classroom | 466 | 31 |  |  | 751 | 17 | 17 | House Fan | 8 | 6008 | 4.6538 | 1 | 4.6538 | 2 | 4.6538 | 2
309 | Classroom | 508 | 33 |  |  | 992 | 22 | 22 | House Fan | 8 | 7936 | 3.8407 | 1 | 3.8407 | 1 | 3.8407 | 1
310 | Classroom | 477 | 31 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 4.9688 | 1 | 4.9688 | 2 | 4.9688 | 2
311 | Classroom | 409 | 27 |  |  | 703 | 15 | 15 | House Fan | 8 | 5624 | 4.3634 | 1 | 4.3634 | 2 | 4.3634 | 2
312 | Classroom | 491 | 32 |  |  | 730 | 16 | 16 | House Fan | 8 | 5840 | 5.0445 | 1 | 5.0445 | 2 | 5.0445 | 2
313 | Classroom | 570 | 38 |  |  | 721 | 16 | 16 | House Fan | 8 | 5768 | 5.9293 | 1 | 5.9293 | 2 | 5.9293 | 2
- | Auditorium | 2427 | 161 |  |  | 3685 | 83 | 83 | House Fan | 8 | 29480 | 4.9396 | 1.062 | 5.246 | 2 | 5.246 | 2
- | Boys' Bathroom | 125 | 8 |  |  | 561 | 12 | 8 | N/A | 8 | 4488 | 1.6711 | 1 | 1.6711 | 1 | 1.6711 | 1
- | Girls' Bathroom | 73 | 4 |  |  | 547 | 12 | 4 | N/A | 8 | 4376 | 1.0009 | 1 | 1.0009 | 1 | 1.0009 | 1
- | Cafeteria | 1258 | 83 |  |  | 1726 | 39 | 39 | House Fan | 8 | 13808 | 5.4664 | 1 | 5.4664 | 2 | 5.4664 | 2
- | Speech Classroom | 0 | 0 | Yes | 20 | 192 | 4 | 4 | House Fan | 8 | 1536 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym | 0 | 0 | Yes | 20 | 3970 | 90 | 90 | N/A | 8 | 31760 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Nurse's Office | 0 | 0 | Yes | 20 | 220 | 5 | 5 | House Fan | 8 | 1760 | 0 | 1 | 0 | 0 | 20 | 3
- | IMC Office | 0 | 0 |  |  | 158 | 3 | 0 | House Fan | 8 | 1264 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office | 0 | 0 | Yes | 20 | 333 | 7 | 7 | House Fan | 8 | 2664 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office | 0 | 0 | Yes | 20 | 342 | 7 | 7 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-26
School: | W.C. Longstreth Elementary School
Vendor: | EMCOR Fluidics | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100D | Faculty Dining | 96 | 6 |  |  | 625 | 14 | 6 | AHU-6 | 8 | 5000 | 1.152 | 1 | 1.152 | 1 | 1.152 | 1
102 | Main Office | 110 | 7 |  |  | 646 | 14 | 7 | AHU-6 | 8 | 5168 | 1.2771 | 1 | 1.2771 | 1 | 1.2771 | 1
102C | Principal Office | 77 | 5 |  |  | 225 | 5 | 5 | AHU-6 | 8 | 1800 | 2.5667 | 1 | 2.5667 | 1 | 2.5667 | 1
102D | Comference Room | 72 | 4 |  |  | 198 | 4 | 4 | AHU-6 | 8 | 1584 | 2.7273 | 1 | 2.7273 | 1 | 2.7273 | 1
103 | Classroom | 141 | 9 |  |  | 704 | 16 | 9 | AHU-1 | 8 | 5632 | 1.5021 | 1 | 1.5021 | 1 | 1.5021 | 1
105 | Classroom | 206 | 13 |  |  | 609 | 13 | 13 | AHU-1 | 8 | 4872 | 2.5369 | 1 | 2.5369 | 1 | 2.5369 | 1
106 | Art Room | 610 | 40 |  |  | 1333 | 30 | 30 | AHU-2 | 8 | 10664 | 3.4321 | 1 | 3.4321 | 1 | 3.4321 | 1
107 | Classroom | 468 | 31 |  |  | 1320 | 30 | 30 | AHU-1 | 8 | 10560 | 2.6591 | 1 | 2.6591 | 1 | 2.6591 | 1
109 | Classroom | 469 | 31 |  |  | 1276 | 29 | 29 | AHU-1 | 8 | 10208 | 2.7567 | 1 | 2.7567 | 1 | 2.7567 | 1
110 | Nurses Suite | 45 | 3 |  |  | 180 | 4 | 3 | AHU-6 | 8 | 1440 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
110C | Nurses Office | 102 | 6 |  |  | 132 | 3 | 3 | AHU-6 | 8 | 1056 | 5.7955 | 1 | 5.7955 | 2 | 5.7955 | 2
110D | Audio Rm | 101 | 6 |  |  | 132 | 3 | 3 | AHU-6 | 8 | 1056 | 5.7386 | 1 | 5.7386 | 2 | 5.7386 | 2
110E | Audio Rm | 78 | 5 |  |  | 48 | 1 | 1 | AHU-6 | 8 | 384 | 12.1875 | 1 | 12.1875 | 3 | 12.1875 | 3
111 | Classroom | 487 | 32 |  |  | 1232 | 28 | 28 | AHU-1 | 8 | 9856 | 2.9647 | 1 | 2.9647 | 1 | 2.9647 | 1
112A | Building Engineers Office | 90 | 6 |  |  | 88 | 2 | 2 | AHU-6 | 8 | 704 | 7.6705 | 1 | 7.6705 | 2 | 7.6705 | 2
113 | Classroom | 361 | 24 |  |  | 1364 | 31 | 24 | AHU-1 | 8 | 10912 | 1.985 | 1 | 1.985 | 1 | 1.985 | 1
200 | Library | 715 | 47 |  |  | 2859 | 64 | 47 | AHU-5 | 8 | 22872 | 1.8757 | 1.062 | 1.992 | 1 | 1.992 | 1
200A | Computer Lab | 119 | 7 |  |  | 704 | 16 | 7 | AHU-5 | 8 | 5632 | 1.2678 | 1 | 1.2678 | 1 | 1.2678 | 1
200B | Consortium | 67 | 4 |  |  | 552 | 12 | 4 | AHU-5 | 8 | 4416 | 0.91033 | 1 | 0.91033 | 0 | 0.91033 | 0
201 | Classroom | 403 | 26 |  |  | 818 | 18 | 18 | AHU-1 | 8 | 6544 | 3.695 | 1 | 3.695 | 1 | 3.695 | 1
202 | Classroom | 360 | 24 |  |  | 510 | 11 | 11 | AHU-2 | 8 | 4080 | 5.2941 | 1 | 5.2941 | 2 | 5.2941 | 2
203 | Classroom | 321 | 21 |  |  | 544 | 12 | 12 | AHU-1 | 8 | 4352 | 4.4256 | 1 | 4.4256 | 2 | 4.4256 | 2
204 | Classroom | 206 | 13 | Yes | 20 | 510 | 11 | 11 | AHU-2 | 8 | 4080 | 3.0294 | 1 | 3.0294 | 1 | 23.0294 | 3
205 | Classroom | 273 | 18 |  |  | 544 | 12 | 12 | AHU-1 | 8 | 4352 | 3.7638 | 1 | 3.7638 | 1 | 3.7638 | 1
206 | Classroom | 364 | 24 |  |  | 510 | 11 | 11 | AHU-2 | 8 | 4080 | 5.3529 | 1 | 5.3529 | 2 | 5.3529 | 2
207 | Classroom | 419 | 27 |  |  | 544 | 12 | 12 | AHU-1 | 8 | 4352 | 5.7767 | 1 | 5.7767 | 2 | 5.7767 | 2
208 | Classroom | 309 | 20 |  |  | 510 | 11 | 11 | AHU-2 | 8 | 4080 | 4.5441 | 1 | 4.5441 | 2 | 4.5441 | 2
209 | Classroom | 417 | 27 |  |  | 544 | 12 | 12 | AHU-1 | 8 | 4352 | 5.7491 | 1 | 5.7491 | 2 | 5.7491 | 2
210 | Classroom | 276 | 18 |  |  | 510 | 11 | 11 | AHU-2 | 8 | 4080 | 4.0588 | 1 | 4.0588 | 2 | 4.0588 | 2
211 | Classroom | 88 | 5 |  |  | 576 | 13 | 5 | AHU-1 | 8 | 4608 | 1.1458 | 1 | 1.1458 | 1 | 1.1458 | 1
212 | Classroom | 304 | 20 |  |  | 765 | 17 | 17 | AHU-2 | 8 | 6120 | 2.9804 | 1 | 2.9804 | 1 | 2.9804 | 1
213 | Classroom | 303 | 20 |  |  | 810 | 18 | 18 | AHU-1 | 8 | 6480 | 2.8056 | 1 | 2.8056 | 1 | 2.8056 | 1
214 | Classroom - WEIGHT ROOM | 669 | 44 |  |  | 1204 | 27 | 27 | AHU-2 | 8 | 9632 | 4.1674 | 1 | 4.1674 | 2 | 4.1674 | 2
215 | Classroom | 141 | 9 |  |  | 285 | 6 | 6 | AHU-1 | 8 | 2280 | 3.7105 | 1 | 3.7105 | 1 | 3.7105 | 1
219 | Classroom | 175 | 11 |  |  | 220 | 5 | 5 | AHU-1 | 8 | 1760 | 5.9659 | 1 | 5.9659 | 2 | 5.9659 | 2
220 | Classroom | 61 | 4 |  |  | 612 | 13 | 4 | AHU-2 | 8 | 4896 | 0.74755 | 1 | 0.74755 | 0 | 0.74755 | 0
301 | Classroom | 311 | 20 |  |  | 595 | 13 | 13 | AHU-1 | 8 | 4760 | 3.9202 | 1 | 3.9202 | 1 | 3.9202 | 1
303 | Classroom | 323 | 21 |  |  | 561 | 12 | 12 | AHU-1 | 8 | 4488 | 4.3182 | 1 | 4.3182 | 2 | 4.3182 | 2
304 | Classroom | 220 | 14 |  |  | 570 | 12 | 12 | AHU-2 | 8 | 4560 | 2.8947 | 1 | 2.8947 | 1 | 2.8947 | 1
305 | Classroom | 316 | 21 |  |  | 577 | 13 | 13 | AHU-1 | 8 | 4616 | 4.1075 | 1 | 4.1075 | 2 | 4.1075 | 2
306 | Classroom | 462 | 30 |  |  | 510 | 11 | 11 | AHU-2 | 8 | 4080 | 6.7941 | 1 | 6.7941 | 2 | 6.7941 | 2
307 | Classroom | 331 | 22 |  |  | 577 | 13 | 13 | AHU-1 | 8 | 4616 | 4.3024 | 1 | 4.3024 | 2 | 4.3024 | 2
308 | Classroom | 327 | 21 |  |  | 510 | 11 | 11 | AHU-2 | 8 | 4080 | 4.8088 | 1 | 4.8088 | 2 | 4.8088 | 2
309 | Classroom | 356 | 23 |  |  | 594 | 13 | 13 | AHU-1 | 8 | 4752 | 4.4949 | 1 | 4.4949 | 2 | 4.4949 | 2
310 | Classroom | 320 | 21 |  |  | 527 | 11 | 11 | AHU-2 | 8 | 4216 | 4.5541 | 1 | 4.5541 | 2 | 4.5541 | 2
311 | Classroom | 340 | 22 |  |  | 576 | 13 | 13 | AHU-1 | 8 | 4608 | 4.4271 | 1 | 4.4271 | 2 | 4.4271 | 2
312 | Classroom | 332 | 22 |  |  | 544 | 12 | 12 | AHU-2 | 8 | 4352 | 4.5772 | 1 | 4.5772 | 2 | 4.5772 | 2
313 | Classroom | 422 | 28 |  |  | 840 | 19 | 19 | AHU-1 | 8 | 6720 | 3.7679 | 1 | 3.7679 | 1 | 3.7679 | 1
314 | Classroom | 577 | 38 |  |  | 1290 | 29 | 29 | AHU-2 | 8 | 10320 | 3.3547 | 1 | 3.3547 | 1 | 3.3547 | 1
315 | Classroom | 145 | 9 |  |  | 280 | 6 | 6 | AHU-1 | 8 | 2240 | 3.8839 | 1 | 3.8839 | 1 | 3.8839 | 1
319 | Classroom | 129 | 8 |  |  | 220 | 5 | 5 | AHU-1 | 8 | 1760 | 4.3977 | 1 | 4.3977 | 2 | 4.3977 | 2
320 | Classroom | 171 | 11 |  |  | 210 | 4 | 4 | AHU-2 | 8 | 1680 | 6.1071 | 1 | 6.1071 | 2 | 6.1071 | 2
- | Auditorium | 1337 | 89 |  |  | 3540 | 80 | 80 | AHU-3 | 8 | 28320 | 2.8326 | 1.062 | 3.0083 | 1 | 3.0083 | 1
- | Cafeteria | 2211 | 147 |  |  | 3658 | 83 | 83 | AHU-4 | 8 | 29264 | 4.5332 | 1.062 | 4.8144 | 2 | 4.8144 | 2
- | Diagnostic Center | 213 | 14 |  |  | 306 | 6 | 6 | AHU-6 | 8 | 2448 | 5.2206 | 1 | 5.2206 | 2 | 5.2206 | 2
- | Main Office Admin | 82 | 5 |  |  | 110 | 2 | 2 | AHU-6 | 8 | 880 | 5.5909 | 1 | 5.5909 | 2 | 5.5909 | 2
- | Main Storage Room | 27 | 1 |  |  | 192 | 4 | 1 | AHU-6 | 8 | 1536 | 1.0547 | 1 | 1.0547 | 1 | 1.0547 | 1
- | Nurses Suite Laundry | 115 | 7 |  |  | 372 | 8 | 7 | AHU-6 | 8 | 2976 | 2.3185 | 1 | 2.3185 | 1 | 2.3185 | 1
- | Gym | 0 | 0 |  |  | 4720 | 107 | 0 | AHU 1 and 2 | 8 | 37760 | 0 | 1.062 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-26
School: | James R. Lowell Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B010A | Boys Bathroom | 725 | 48 |  |  | 667 | 15 | 15 | N/A | 8 | 5336 | 8.1522 | 1 | 8.1522 | 2 | 8.1522 | 2
B10 | Music | 0 | 0 |  |  | 925 | 21 | 0 | N/A | 8 | 7400 | 0 | 1 | 0 | 0 | 0 | 0
B11 | Classroom | 346 | 23 |  |  | 695 | 15 | 15 | House Fan | 8 | 5560 | 3.7338 | 1 | 3.7338 | 1 | 3.7338 | 1
B12 | Girls Bathroom | 305 | 20 |  |  | 695 | 15 | 15 | House Fan | 8 | 5560 | 3.2914 | 1 | 3.2914 | 1 | 3.2914 | 1
B8 | Classroom | 175 | 11 |  |  | 576 | 13 | 11 | House Fan | 8 | 4608 | 2.2786 | 1 | 2.2786 | 1 | 2.2786 | 1
B9 | Classroom | 388 | 25 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 4.3628 | 1 | 4.3628 | 2 | 4.3628 | 2
100 | Classroom | 0 | 0 |  |  | 240 | 5 | 0 | House Fan | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom | 285 | 19 |  |  | 566 | 12 | 12 | House Fan | 8 | 4528 | 3.7765 | 1 | 3.7765 | 1 | 3.7765 | 1
102 | Classroom | 327 | 21 |  |  | 559 | 12 | 12 | House Fan | 8 | 4472 | 4.3873 | 1 | 4.3873 | 2 | 4.3873 | 2
103 | Classroom | 325 | 21 |  |  | 100 | 2 | 2 | House Fan | 8 | 800 | 24.375 | 1 | 24.375 | 4 | 24.375 | 4
104 | Classroom | 102 | 6 |  |  | 640 | 14 | 6 | House Fan | 8 | 5120 | 1.1953 | 1 | 1.1953 | 1 | 1.1953 | 1
105 | Classroom | 593 | 39 |  |  | 654 | 14 | 14 | House Fan | 8 | 5232 | 6.8005 | 1 | 6.8005 | 2 | 6.8005 | 2
106 | Classroom | 399 | 26 |  |  | 566 | 12 | 12 | House Fan | 8 | 4528 | 5.2871 | 1 | 5.2871 | 2 | 5.2871 | 2
107 | Classroom | 0 | 0 |  |  | 667 | 15 | 0 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 0 | 0
108 | Classroom | 154 | 10 |  |  | 650 | 14 | 10 | House Fan | 8 | 5200 | 1.7769 | 1 | 1.7769 | 1 | 1.7769 | 1
109 | Classroom | 304 | 20 |  |  | 602 | 13 | 13 | House Fan | 8 | 4816 | 3.7874 | 1 | 3.7874 | 1 | 3.7874 | 1
110 | Classroom | 0 | 0 |  |  | 207 | 4 | 0 | House Fan | 8 | 1656 | 0 | 1 | 0 | 0 | 0 | 0
111 | Counselor |  | 0 |  |  | 154 | 3 | 0 |  | 8 | 1232 | 0 | 1 | 0 | 0 | 0 | 0
200 | Classroom | 0 | 0 |  |  | 240 | 5 | 0 | House Fan | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom | 300 | 20 |  |  | 654 | 14 | 14 | House Fan | 8 | 5232 | 3.4404 | 1 | 3.4404 | 1 | 3.4404 | 1
202 | Computer Room |  | 0 |  |  | 810 | 18 | 0 |  | 8 | 6480 | 0 | 1 | 0 | 0 | 0 | 0
203 | Classroom | 647 | 43 |  |  | 654 | 14 | 14 | House Fan | 8 | 5232 | 7.4197 | 1 | 7.4197 | 2 | 7.4197 | 2
204 | Classroom | 457 | 30 |  |  | 650 | 14 | 14 | House Fan | 8 | 5200 | 5.2731 | 1 | 5.2731 | 2 | 5.2731 | 2
205 | Classroom | 531 | 35 |  |  | 650 | 14 | 14 | House Fan | 8 | 5200 | 6.1269 | 1 | 6.1269 | 2 | 6.1269 | 2
206 | Classroom | 247 | 16 |  |  | 695 | 15 | 15 | House Fan | 8 | 5560 | 2.6655 | 1 | 2.6655 | 1 | 2.6655 | 1
207 | Classroom | 102 | 6 |  |  | 694 | 15 | 6 | House Fan | 8 | 5552 | 1.1023 | 1 | 1.1023 | 1 | 1.1023 | 1
207 | Faculty Room | 0 | 0 |  |  | 207 | 4 | 0 | N/A | 8 | 1656 | 0 | 1 | 0 | 0 | 0 | 0
208 | Classroom | 200 | 13 |  |  | 695 | 15 | 13 | House Fan | 8 | 5560 | 2.1583 | 1 | 2.1583 | 1 | 2.1583 | 1
209 | Classroom | 139 | 9 |  |  | 650 | 14 | 9 | House Fan | 8 | 5200 | 1.6038 | 1 | 1.6038 | 1 | 1.6038 | 1
210 | Classroom | 275 | 18 |  |  | 560 | 12 | 12 | House Fan | 8 | 4480 | 3.683 | 1 | 3.683 | 1 | 3.683 | 1
211 | Classroom | 0 | 0 |  |  | 420 | 9 | 0 | House Fan | 8 | 3360 | 0 | 1 | 0 | 0 | 0 | 0
300 | Classroom | 0 | 0 |  |  | 240 | 5 | 0 | House Fan | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
301A | Classroom | 132 | 8 |  |  | 566 | 12 | 8 | House Fan | 8 | 4528 | 1.7491 | 1 | 1.7491 | 1 | 1.7491 | 1
301B | Classroom | 139 | 9 |  |  | 300 | 6 | 6 | House Fan | 8 | 2400 | 3.475 | 1 | 3.475 | 1 | 3.475 | 1
302 | Classroom | 145 | 9 |  |  | 240 | 5 | 5 | House Fan | 8 | 1920 | 4.5312 | 1 | 4.5312 | 2 | 4.5312 | 2
303 | Classroom | 318 | 21 |  |  | 666 | 15 | 15 | House Fan | 8 | 5328 | 3.5811 | 1 | 3.5811 | 1 | 3.5811 | 1
304 | Classroom | 387 | 25 |  |  | 610 | 13 | 13 | House Fan | 8 | 4880 | 4.7582 | 1 | 4.7582 | 2 | 4.7582 | 2
305 | Classroom | 432 | 28 |  |  | 620 | 14 | 14 | House Fan | 8 | 4960 | 5.2258 | 1 | 5.2258 | 2 | 5.2258 | 2
306 | Classroom | 249 | 16 |  |  | 650 | 14 | 14 | House Fan | 8 | 5200 | 2.8731 | 1 | 2.8731 | 1 | 2.8731 | 1
307 | Classroom | 325 | 21 |  |  | 650 | 14 | 14 | House Fan | 8 | 5200 | 3.75 | 1 | 3.75 | 1 | 3.75 | 1
308 | Classroom | 322 | 21 |  |  | 650 | 14 | 14 | House Fan | 8 | 5200 | 3.7154 | 1 | 3.7154 | 1 | 3.7154 | 1
309 | Classroom | 262 | 17 |  |  | 654 | 14 | 14 | House Fan | 8 | 5232 | 3.0046 | 1 | 3.0046 | 1 | 3.0046 | 1
310 | Classroom | 203 | 13 |  |  | 636 | 14 | 13 | House Fan | 8 | 5088 | 2.3939 | 1 | 2.3939 | 1 | 2.3939 | 1
311 | Classroom | 0 | 0 |  |  | 221 | 5 | 0 | House Fan | 8 | 1768 | 0 | 1 | 0 | 0 | 0 | 0
312 | Classroom | 0 | 0 |  |  | 273 | 6 | 0 | House Fan | 8 | 2184 | 0 | 1 | 0 | 0 | 0 | 0
- | Library | 213 | 14 |  |  | 1040 | 23 | 14 | AHU | 8 | 8320 | 1.5361 | 1 | 1.5361 | 1 | 1.5361 | 1
- | Entrance Lobby | 290 | 19 |  |  | 325 | 7 | 7 | N/A | 8 | 2600 | 6.6923 | 1 | 6.6923 | 2 | 6.6923 | 2
- | Gym | 0 | 0 |  |  | 4368 | 99 | 0 | AHU | 8 | 34944 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Music Rm | 127 | 8 |  |  | 286 | 6 | 6 | Unit Ventilator | 8 | 2288 | 3.3304 | 1 | 3.3304 | 1 | 3.3304 | 1
S-11 | Classroom | 419 | 27 |  |  | 810 | 18 | 18 | Unit Ventilator | 8 | 6480 | 3.8796 | 1 | 3.8796 | 1 | 3.8796 | 1
S-12 | Classroom | 906 | 60 |  |  | 692 | 15 | 15 | Unit Ventilator | 8 | 5536 | 9.8194 | 1 | 9.8194 | 2 | 9.8194 | 2
S-13 | Classroom | 635 | 42 |  |  | 692 | 15 | 15 | Unit Ventilator | 8 | 5536 | 6.8822 | 1 | 6.8822 | 2 | 6.8822 | 2
S-14 | Classroom | 715 | 47 |  |  | 695 | 15 | 15 | Unit Ventilator | 8 | 5560 | 7.7158 | 1 | 7.7158 | 2 | 7.7158 | 2
S-15 | Classroom | 411 | 27 |  |  | 692 | 15 | 15 | Unit Ventilator | 8 | 5536 | 4.4545 | 1 | 4.4545 | 2 | 4.4545 | 2
S-16 | Classroom | 502 | 33 |  |  | 692 | 15 | 15 | Unit Ventilator | 8 | 5536 | 5.4408 | 1 | 5.4408 | 2 | 5.4408 | 2
S-17 | Classroom | 371 | 24 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 3.3605 | 1 | 3.3605 | 1 | 3.3605 | 1
S-18 | Classroom | 482 | 32 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 4.3659 | 1 | 4.3659 | 2 | 4.3659 | 2
S-19 | Classroom | 742 | 49 |  |  | 828 | 18 | 18 | Unit Ventilator | 8 | 6624 | 6.721 | 1 | 6.721 | 2 | 6.721 | 2
S-21 | Classroom | 429 | 28 |  |  | 640 | 14 | 14 | Unit Ventilator | 8 | 5120 | 5.0273 | 1 | 5.0273 | 2 | 5.0273 | 2
S-22 | Classroom | 663 | 44 |  |  | 640 | 14 | 14 | Unit Ventilator | 8 | 5120 | 7.7695 | 1 | 7.7695 | 2 | 7.7695 | 2
S-23 | Classroom | 480 | 32 |  |  | 654 | 14 | 14 | Unit Ventilator | 8 | 5232 | 5.5046 | 1 | 5.5046 | 2 | 5.5046 | 2
S-24 | Classroom | 333 | 22 |  |  | 636 | 14 | 14 | Unit Ventilator | 8 | 5088 | 3.9269 | 1 | 3.9269 | 1 | 3.9269 | 1
S-25 | Classroom | 844 | 56 |  |  | 636 | 14 | 14 | Unit Ventilator | 8 | 5088 | 9.9528 | 1 | 9.9528 | 2 | 9.9528 | 2
S-26 | Classroom | 490 | 32 |  |  | 654 | 14 | 14 | Unit Ventilator | 8 | 5232 | 5.6193 | 1 | 5.6193 | 2 | 5.6193 | 2
S-27 | Storage | 393 | 26 |  |  | 610 | 13 | 13 | Unit Ventilator | 8 | 4880 | 4.832 | 1 | 4.832 | 2 | 4.832 | 2
S-27 | Classroom | 266 | 17 |  |  | 610 | 13 | 13 | Unit Ventilator | 8 | 4880 | 3.2705 | 1 | 3.2705 | 1 | 3.2705 | 1
S-28 | Classroom | 450 | 30 |  |  | 610 | 13 | 13 | Unit Ventilator | 8 | 4880 | 5.5328 | 1 | 5.5328 | 2 | 5.5328 | 2
S-29 | Classroom | 260 | 17 |  |  | 610 | 13 | 13 | Unit Ventilator | 8 | 4880 | 3.1967 | 1 | 3.1967 | 1 | 3.1967 | 1
S-30 | Teacher's Lounge | 378 | 25 |  |  | 858 | 19 | 19 | Unit Ventilator | 8 | 6864 | 3.3042 | 1 | 3.3042 | 1 | 3.3042 | 1
S-31 | Office | 508 | 33 |  |  | 140 | 3 | 3 | Unit Ventilator | 8 | 1120 | 27.2143 | 1 | 27.2143 | 4 | 27.2143 | 4
- | Main Office |  | 0 |  |  | 338 | 7 | 0 |  | 8 | 2704 | 0 | 1 | 0 | 0 | 0 | 0
- | Principals Office |  | 0 |  |  | 364 | 8 | 0 |  | 8 | 2912 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurses Office |  | 0 |  |  | 240 | 5 | 0 |  | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-27
School: | James R. Ludlow Elementary-Middle School
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
3 | Art |  | 0 |  |  | 667 | 15 | 0 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 0 | 0
100B | Home and School |  | 0 |  |  | 121 | 2 | 0 | House Fan | 8 | 968 | 0 | 1 | 0 | 0 | 0 | 0
100C | Counselor |  | 0 |  |  | 195 | 4 | 0 | House Fan | 8 | 1560 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 672 | 15 | 15 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom |  | 0 | Yes | 20 | 638 | 14 | 14 | House Fan | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 |  |  | 920 | 20 | 0 | House Fan | 8 | 7360 | 0 | 1 | 0 | 0 | 0 | 0
108 | Classroom |  | 0 | Yes | 20 | 638 | 14 | 14 | House Fan | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom |  | 0 | Yes | 20 | 841 | 19 | 19 | House Fan | 8 | 6728 | 0 | 1 | 0 | 0 | 20 | 3
110 | Counselor |  | 0 |  |  | 128 | 2 | 0 | House Fan | 8 | 1024 | 0 | 1 | 0 | 0 | 0 | 0
200 | Classroom |  | 0 | Yes | 20 | 552 | 12 | 12 | House Fan | 8 | 4416 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom |  | 0 | Yes | 20 | 841 | 19 | 19 | House Fan | 8 | 6728 | 0 | 1 | 0 | 0 | 20 | 3
300 | Ladies lounge |  | 0 |  |  | 276 | 6 | 0 | House Fan | 8 | 2208 | 0 | 1 | 0 | 0 | 0 | 0
300A | Ladies lounge |  | 0 |  |  | 276 | 6 | 0 | House Fan | 8 | 2208 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom |  | 0 | Yes | 20 | 782 | 17 | 17 | House Fan | 8 | 6256 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom |  | 0 | Yes | 20 | 672 | 15 | 15 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
311 | Classroom |  | 0 | Yes | 20 | 406 | 9 | 9 | House Fan | 8 | 3248 | 0 | 1 | 0 | 0 | 20 | 3
- | Library |  | 0 | Yes | 20 | 1298 | 29 | 29 | House Fan | 8 | 10384 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 | Yes | 20 | 5208 | 118 | 118 |  | 8 | 41664 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Kitchen |  | 0 | Yes | 20 | 1288 | 29 | 29 | House Fan | 8 | 10304 | 0 | 1 | 0 | 0 | 20 | 3
- | Lunchroom/Cafetorium |  | 0 |  |  | 3157 | 71 | 0 | House Fan | 8 | 25256 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Main office |  | 0 | Yes | 20 | 322 | 7 | 7 | House Fan | 8 | 2576 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses Office |  | 0 | Yes | 20 | 128 | 2 | 2 | House Fan | 8 | 1024 | 0 | 1 | 0 | 0 | 20 | 3
- | Principals office |  | 0 | Yes | 20 | 165 | 3 | 3 | House Fan | 8 | 1320 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-08
School: | John Marshall Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
102 | Classroom | 723 | 48 |  |  | 832 | 18 | 18 | House Fan | 8 | 6656 | 6.5174 | 1 | 6.5174 | 2 | 6.5174 | 2
103 | Classroom | 653 | 43 |  |  | 449 | 10 | 10 | House Fan | 8 | 3592 | 10.9076 | 1 | 10.9076 | 3 | 10.9076 | 3
104 | Classroom | 684 | 45 |  |  | 781 | 17 | 17 | House Fan | 8 | 6248 | 6.5685 | 1 | 6.5685 | 2 | 6.5685 | 2
105 | Classroom | 717 | 47 |  |  | 738 | 16 | 16 | House Fan | 8 | 5904 | 7.2866 | 1 | 7.2866 | 2 | 7.2866 | 2
106 | Classroom | 624 | 41 |  |  | 893 | 20 | 20 | House Fan | 8 | 7144 | 5.2408 | 1 | 5.2408 | 2 | 5.2408 | 2
107 | Classroom | 575 | 38 |  |  | 623 | 14 | 14 | House Fan | 8 | 4984 | 6.9222 | 1 | 6.9222 | 2 | 6.9222 | 2
200 | Classroom | 640 | 42 |  |  | 790 | 17 | 17 | House Fan | 8 | 6320 | 6.0759 | 1 | 6.0759 | 2 | 6.0759 | 2
201 | Classroom | 692 | 46 |  |  | 803 | 18 | 18 | House Fan | 8 | 6424 | 6.4633 | 1 | 6.4633 | 2 | 6.4633 | 2
202 | Classroom | 691 | 46 |  |  | 746 | 16 | 16 | House Fan | 8 | 5968 | 6.9471 | 1 | 6.9471 | 2 | 6.9471 | 2
203 | Classroom | 556 | 37 |  |  | 770 | 17 | 17 | House Fan | 8 | 6160 | 5.4156 | 1 | 5.4156 | 2 | 5.4156 | 2
204 | Classroom | 678 | 45 |  |  | 715 | 16 | 16 | House Fan | 8 | 5720 | 7.1119 | 1 | 7.1119 | 2 | 7.1119 | 2
205 | Classroom | 765 | 51 |  |  | 225 | 5 | 5 | House Fan | 8 | 1800 | 25.5 | 1 | 25.5 | 4 | 25.5 | 4
206 | Classroom | 535 | 35 |  |  | 548 | 12 | 12 | House Fan | 8 | 4384 | 7.3221 | 1 | 7.3221 | 2 | 7.3221 | 2
300 | Classroom | 596 | 39 |  |  | 766 | 17 | 17 | House Fan | 8 | 6128 | 5.8355 | 1 | 5.8355 | 2 | 5.8355 | 2
300A | Classroom |  | 0 | Yes | 20 | 510 | 11 | 11 | Wndow Fan | 8 | 4080 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 531 | 35 |  |  | 884 | 20 | 20 | House Fan | 8 | 7072 | 4.5051 | 1 | 4.5051 | 2 | 4.5051 | 2
302 | Classroom | 683 | 45 |  |  | 766 | 17 | 17 | House Fan | 8 | 6128 | 6.6873 | 1 | 6.6873 | 2 | 6.6873 | 2
303 | Classroom | 785 | 52 |  |  | 748 | 17 | 17 | House Fan | 8 | 5984 | 7.871 | 1 | 7.871 | 2 | 7.871 | 2
304 | Classroom | 793 | 52 |  |  | 779 | 17 | 17 | House Fan | 8 | 6232 | 7.6348 | 1 | 7.6348 | 2 | 7.6348 | 2
305 | Classroom | 668 | 44 |  |  | 757 | 17 | 17 | House Fan | 8 | 6056 | 6.6182 | 1 | 6.6182 | 2 | 6.6182 | 2
306 | Classroom | 609 | 40 |  |  | 876 | 19 | 19 | House Fan | 8 | 7008 | 5.214 | 1 | 5.214 | 2 | 5.214 | 2
- | 1st Fl. Corridor | 1954 | 130 |  |  | 352 | 8 | 8 | N/A | 8 | 2816 | 41.6335 | 1 | 41.6335 | 4 | 41.6335 | 4
- | Grnd. Fl. Boys Bathrm. | 402 | 26 |  |  | 234 | 5 | 5 | N/A | 8 | 1872 | 12.8846 | 1 | 12.8846 | 3 | 12.8846 | 3
- | Grnd. Fl. Girls Bathrm. | 333 | 22 |  |  | 156 | 3 | 3 | N/A | 8 | 1248 | 16.0096 | 1 | 16.0096 | 3 | 16.0096 | 3
- | Main Office | 343 | 22 |  |  | 298 | 6 | 6 | House Fan | 8 | 2384 | 8.6326 | 1 | 8.6326 | 2 | 8.6326 | 2
- | Nurse / office | 340 | 22 |  |  | 420 | 9 | 9 | House Fan | 8 | 3360 | 6.0714 | 1 | 6.0714 | 2 | 6.0714 | 2
- | Cafeteria |  | 0 | Yes | 20 | 3129 | 71 | 71 | Wndow Fan | 8 | 25032 | 0 | 1.062 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-24
School: | Thurgood Marshall Elementary School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 99 | 6 | Yes | 20 | 875 | 19 | 19 |  | 8 | 7000 | 0.84857 | 1 | 0.84857 | 0 | 20.8486 | 3
101 | Classroom | 112 | 7 | Yes | 20 | 875 | 19 | 19 |  | 8 | 7000 | 0.96 | 1 | 0.96 | 0 | 20.96 | 3
102 | Classroom | 53 | 3 | Yes | 20 | 875 | 19 | 19 |  | 8 | 7000 | 0.45429 | 1 | 0.45429 | 0 | 20.4543 | 3
103 | Classroom | 60 | 4 | Yes | 20 | 875 | 19 | 19 |  | 8 | 7000 | 0.51429 | 1 | 0.51429 | 0 | 20.5143 | 3
104 | Classroom | 310 | 20 |  |  | 589 | 13 | 13 |  | 8 | 4712 | 3.9474 | 1 | 3.9474 | 1 | 3.9474 | 1
105 | Classroom | 143 | 9 | Yes | 20 | 624 | 14 | 14 |  | 8 | 4992 | 1.7188 | 1 | 1.7188 | 1 | 21.7188 | 3
106 | Office | 154 | 10 |  |  | 143 | 3 | 3 |  | 8 | 1144 | 8.0769 | 1 | 8.0769 | 2 | 8.0769 | 2
106A | Office | 0 | 0 |  |  | 99 | 2 | 0 |  | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
106B | Office | 0 | 0 |  |  | 99 | 2 | 0 |  | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
106C | Office | 168 | 11 |  |  | 99 | 2 | 2 |  | 8 | 792 | 12.7273 | 1 | 12.7273 | 3 | 12.7273 | 3
106D | Office | 180 | 12 |  |  | 126 | 2 | 2 |  | 8 | 1008 | 10.7143 | 1 | 10.7143 | 3 | 10.7143 | 3
106E | Office | 165 | 11 |  |  | 130 | 2 | 2 |  | 8 | 1040 | 9.5192 | 1 | 9.5192 | 2 | 9.5192 | 2
106G | Office | 191 | 12 |  |  | 130 | 2 | 2 |  | 8 | 1040 | 11.0192 | 1 | 11.0192 | 3 | 11.0192 | 3
106H | Hallway | 0 | 0 |  |  | 528 | 12 | 0 |  | 8 | 4224 | 0 | 1 | 0 | 0 | 0 | 0
106 RR | Office | 513 | 34 |  |  | 52.5 | 1 | 1 |  | 8 | 420 | 73.2857 | 1 | 73.2857 | 5 | 73.2857 | 5
107 | Classroom | 82 | 5 |  |  | 720 | 16 | 5 |  | 8 | 5760 | 0.85417 | 1 | 0.85417 | 0 | 0.85417 | 0
107-2 | Classroom | 0 | 0 |  |  | 215 | 4 | 0 |  | 8 | 1720 | 0 | 1 | 0 | 0 | 0 | 0
107A | Classroom | 89 | 5 |  |  | 816 | 18 | 5 |  | 8 | 6528 | 0.81801 | 1 | 0.81801 | 0 | 0.81801 | 0
108 | Classroom | 38 | 2 |  |  | 506 | 11 | 2 |  | 8 | 4048 | 0.56324 | 1 | 0.56324 | 0 | 0.56324 | 0
108A | Classroom | 37 | 2 |  |  | 128 | 2 | 2 |  | 8 | 1024 | 2.168 | 1 | 2.168 | 1 | 2.168 | 1
109 | Classroom | 71 | 4 |  |  | 1196 | 27 | 4 |  | 8 | 9568 | 0.44523 | 1 | 0.44523 | 0 | 0.44523 | 0
110 | Classroom | 382 | 25 |  |  | 682 | 15 | 15 |  | 8 | 5456 | 4.2009 | 1 | 4.2009 | 2 | 4.2009 | 2
111 | Classroom | 216 | 14 | Yes | 20 | 630 | 14 | 14 |  | 8 | 5040 | 2.5714 | 1 | 2.5714 | 1 | 22.5714 | 3
113A | Principals Office | 18 | 1 |  |  | 340 | 7 | 1 |  | 8 | 2720 | 0.39706 | 1 | 0.39706 | 0 | 0.39706 | 0
113D | Admin Office | 33 | 2 |  |  | 99 | 2 | 2 |  | 8 | 792 | 2.5 | 1 | 2.5 | 1 | 2.5 | 1
113E | Admin Office | 24 | 1 |  |  | 99 | 2 | 1 |  | 8 | 792 | 1.8182 | 1 | 1.8182 | 1 | 1.8182 | 1
113F | Admin Office | 25 | 1 |  |  | 99 | 2 | 1 |  | 8 | 792 | 1.8939 | 1 | 1.8939 | 1 | 1.8939 | 1
113G | Admin Office | 20 | 1 |  |  | 99 | 2 | 1 |  | 8 | 792 | 1.5152 | 1 | 1.5152 | 1 | 1.5152 | 1
115 | Classroom | 142 | 9 |  |  | 782 | 17 | 9 |  | 8 | 6256 | 1.3619 | 1 | 1.3619 | 1 | 1.3619 | 1
200 | Classroom | 88 | 5 |  |  | 875 | 19 | 5 |  | 8 | 7000 | 0.75429 | 1 | 0.75429 | 0 | 0.75429 | 0
201 | Classroom | 157 | 10 | Yes | 20 | 875 | 19 | 19 |  | 8 | 7000 | 1.3457 | 1 | 1.3457 | 1 | 21.3457 | 3
202 | Classroom | 75 | 5 | Yes | 20 | 875 | 19 | 19 |  | 8 | 7000 | 0.64286 | 1 | 0.64286 | 0 | 20.6429 | 3
203 | Classroom | 73 | 4 | Yes | 20 | 875 | 19 | 19 |  | 8 | 7000 | 0.62571 | 1 | 0.62571 | 0 | 20.6257 | 3
204 | Classroom | 90 | 6 | Yes | 20 | 993 | 22 | 22 |  | 8 | 7944 | 0.67976 | 1 | 0.67976 | 0 | 20.6798 | 3
205 | Classroom | 53 | 3 |  |  | 327.75 | 7 | 3 |  | 8 | 2622 | 1.2128 | 1 | 1.2128 | 1 | 1.2128 | 1
206A | Classroom | 42 | 2 |  |  | 154 | 3 | 2 |  | 8 | 1232 | 2.0455 | 1 | 2.0455 | 1 | 2.0455 | 1
206B | Classroom | 31 | 2 |  |  | 270 | 6 | 2 |  | 8 | 2160 | 0.86111 | 1 | 0.86111 | 0 | 0.86111 | 0
206C | Classroom | 49 | 3 |  |  | 127 | 2 | 2 |  | 8 | 1016 | 2.8937 | 1 | 2.8937 | 1 | 2.8937 | 1
207 | Library | 519 | 34 |  |  | 2108 | 47 | 34 |  | 8 | 16864 | 1.8465 | 1 | 1.8465 | 1 | 1.8465 | 1
208 | Computer Lab | 73 | 4 | Yes | 20 | 1024 | 23 | 23 |  | 8 | 8192 | 0.53467 | 1 | 0.53467 | 0 | 20.5347 | 3
209 | Music Room | 0 | 0 |  |  | 1171 | 26 | 0 |  | 8 | 9368 | 0 | 1 | 0 | 0 | 0 | 0
215 | Faculty Lounge | 279 | 18 |  |  | 400 | 9 | 9 |  | 8 | 3200 | 5.2313 | 1 | 5.2313 | 2 | 5.2313 | 2
300 | Classroom | 140 | 9 | Yes | 20 | 875 | 19 | 19 |  | 8 | 7000 | 1.2 | 1 | 1.2 | 1 | 21.2 | 3
301 | Classroom | 125 | 8 | Yes | 20 | 875 | 19 | 19 |  | 8 | 7000 | 1.0714 | 1 | 1.0714 | 1 | 21.0714 | 3
302 | Classroom | 200 | 13 | Yes | 20 | 875 | 19 | 19 |  | 8 | 7000 | 1.7143 | 1 | 1.7143 | 1 | 21.7143 | 3
303 | Classroom | 37 | 2 |  |  | 875 | 19 | 2 |  | 8 | 7000 | 0.31714 | 1 | 0.31714 | 0 | 0.31714 | 0
304 | Classroom | 86 | 5 | Yes | 20 | 960 | 21 | 21 |  | 8 | 7680 | 0.67188 | 1 | 0.67188 | 0 | 20.6719 | 3
305 | Classroom | 111 | 7 |  |  | 782 | 17 | 7 |  | 8 | 6256 | 1.0646 | 1 | 1.0646 | 1 | 1.0646 | 1
306 | Classroom | 200 | 13 |  |  | 782 | 17 | 13 |  | 8 | 6256 | 1.9182 | 1 | 1.9182 | 1 | 1.9182 | 1
307 | Classroom | 132 | 8 |  |  | 782 | 17 | 8 |  | 8 | 6256 | 1.266 | 1 | 1.266 | 1 | 1.266 | 1
308 | Classroom | 33 | 2 |  |  | 782 | 17 | 2 |  | 8 | 6256 | 0.3165 | 1 | 0.3165 | 0 | 0.3165 | 0
310 | Classroom | 65 | 4 |  |  | 782 | 17 | 4 |  | 8 | 6256 | 0.6234 | 1 | 0.6234 | 0 | 0.6234 | 0
311 | Classroom | 632 | 42 |  |  | 782 | 17 | 17 |  | 8 | 6256 | 6.0614 | 1 | 6.0614 | 2 | 6.0614 | 2
312 | Classroom | 99 | 6 |  |  | 782 | 17 | 6 |  | 8 | 6256 | 0.94949 | 1 | 0.94949 | 0 | 0.94949 | 0
313 | Classroom | 76 | 5 |  |  | 782 | 17 | 5 |  | 8 | 6256 | 0.7289 | 1 | 0.7289 | 0 | 0.7289 | 0
314 | Classroom | 87 | 5 |  |  | 782 | 17 | 5 |  | 8 | 6256 | 0.8344 | 1 | 0.8344 | 0 | 0.8344 | 0
315 | Classroom | 112 | 7 |  |  | 782 | 17 | 7 |  | 8 | 6256 | 1.0742 | 1 | 1.0742 | 1 | 1.0742 | 1
404 | Classroom | 90 | 6 |  |  | 1156 | 26 | 6 |  | 8 | 9248 | 0.58391 | 1 | 0.58391 | 0 | 0.58391 | 0
405 | Classroom | 129 | 8 |  |  | 782 | 17 | 8 |  | 8 | 6256 | 1.2372 | 1 | 1.2372 | 1 | 1.2372 | 1
405A | Office | 0 | 0 |  |  | 112 | 2 | 0 |  | 8 | 896 | 0 | 1 | 0 | 0 | 0 | 0
406 | Classroom | 93 | 6 |  |  | 782 | 17 | 6 |  | 8 | 6256 | 0.89194 | 1 | 0.89194 | 0 | 0.89194 | 0
407 | Classroom | 147 | 9 |  |  | 782 | 17 | 9 |  | 8 | 6256 | 1.4098 | 1 | 1.4098 | 1 | 1.4098 | 1
408 | Classroom | 40 | 2 |  |  | 782 | 17 | 2 |  | 8 | 6256 | 0.38363 | 1 | 0.38363 | 0 | 0.38363 | 0
409A | Office | 23 | 1 |  |  | 140 | 3 | 1 |  | 8 | 1120 | 1.2321 | 1 | 1.2321 | 1 | 1.2321 | 1
410 | Classroom | 0 | 0 |  |  | 782 | 17 | 0 |  | 8 | 6256 | 0 | 1 | 0 | 0 | 0 | 0
411 | Classroom | 86 | 5 |  |  | 782 | 17 | 5 |  | 8 | 6256 | 0.82481 | 1 | 0.82481 | 0 | 0.82481 | 0
412 | Classroom | 94 | 6 |  |  | 782 | 17 | 6 |  | 8 | 6256 | 0.90153 | 1 | 0.90153 | 0 | 0.90153 | 0
413 | Classroom | 76 | 5 |  |  | 782 | 17 | 5 |  | 8 | 6256 | 0.7289 | 1 | 0.7289 | 0 | 0.7289 | 0
414 | Classroom | 84 | 5 |  |  | 782 | 17 | 5 |  | 8 | 6256 | 0.80563 | 1 | 0.80563 | 0 | 0.80563 | 0
415 | Classroom | 100 | 6 |  |  | 782 | 17 | 6 |  | 8 | 6256 | 0.95908 | 1 | 0.95908 | 0 | 0.95908 | 0
- | Auditorium | 369 | 24 |  |  | 2162 | 49 | 24 |  | 8 | 17296 | 1.2801 | 1 | 1.2801 | 1 | 1.2801 | 1
- | Stage | 0 | 0 |  |  | 630 | 14 | 0 |  | 8 | 5040 | 0 | 1 | 0 | 0 | 0 | 0
- | Building Engineer Office | 0 | 0 |  |  | 120 | 2 | 0 |  | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria | 3225 | 215 |  |  | 4400 | 100 | 100 |  | 8 | 35200 | 5.4972 | 1.062 | 5.8382 | 2 | 5.8382 | 2
- | East Kitchen | 0 | 0 |  |  | 360 | 8 | 0 |  | 8 | 2880 | 0 | 1 | 0 | 0 | 0 | 0
- | West Kitchen | 0 | 0 |  |  | 1040 | 23 | 0 |  | 8 | 8320 | 0 | 1 | 0 | 0 | 0 | 0
- | Kitchen Office | 75 | 5 |  |  | 120 | 2 | 2 |  | 8 | 960 | 4.6875 | 1 | 4.6875 | 2 | 4.6875 | 2
- | Gym | 4507 | 300 |  |  | 5005 | 113 | 113 |  | 8 | 40040 | 6.7537 | 1.062 | 7.1727 | 2 | 7.1727 | 2
- | Nurses Office | 154 | 10 |  |  | 143 | 3 | 3 |  | 8 | 1144 | 8.0769 | 1 | 8.0769 | 2 | 8.0769 | 2
Sheet Last Modified: | 2021-04-19
School: | Jules E. Mastbaum High School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
SDP Building Name | Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) |  | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room
Old Building | 101 | Classroom | 0 | 0 |  |  | 959 | 21 | 0
Old Building | 102 | Classroom | 0 | 0 |  |  | 967 | 21 | 0
Old Building | 103 | Classroom | 304 | 20 |  |  | 1130 | 25 | 20
Old Building | 104 | Classroom | 455 | 30 |  |  | 801 | 18 | 18
Old Building | 105 | Carpentry Shop |  | 0 |  | Yes | 2502 | 56 | 56
Old Building | 201 | Classroom | 0 | 0 |  |  | 585 | 13 | 0
Old Building | 202 | Classroom | 237 | 15 |  |  | 190 | 4 | 4
Old Building | 206 | Classroom | 569 | 37 |  |  | 1045 | 23 | 23
Old Building | 207 | Classroom | 0 | 0 |  |  | 906 | 20 | 0
Old Building | 209 | Classroom | 738 | 49 |  |  | 603 | 13 | 13
Old Building | 301 | Classroom | 680 | 45 |  |  | 583 | 13 | 13
Old Building | 302 | Classroom | 271 | 18 |  |  | 915 | 20 | 18
Old Building | 304 | Classroom | 256 | 17 |  |  | 943 | 21 | 17
Old Building | 306 | Classroom | 1285 | 85 |  |  | 1099 | 24 | 24
Old Building | 308 | Classroom | 292 | 19 |  |  | 971 | 22 | 19
Old Building | 310A | Classroom | 279 | 18 |  |  | 1015 | 23 | 18
Old Building | 311 | Classroom | 0 | 0 |  |  | 940 | 21 | 0
Old Building | 313 | Classroom | 572 | 38 |  |  | 939 | 21 | 21
Old Building | 315 | Classroom | 404 | 26 |  |  | 611 | 13 | 13
Old Building | 401 | Classroom | 194 | 12 |  |  | 562 | 12 | 12
Old Building | 402 | Classroom | 588 | 39 |  |  | 924 | 20 | 20
Old Building | 404 | Classroom | 337 | 22 |  |  | 936 | 21 | 21
Old Building | 406 | Classroom | 590 | 39 |  |  | 658 | 14 | 14
Old Building | 407 | Classroom | 0 | 0 |  |  | 750 | 17 | 0
Old Building | 408 | Classroom | 0 | 0 |  |  | 677 | 15 | 0
Old Building | 409 | Classroom | 0 | 0 |  |  | 659 | 14 | 0
Old Building | 410 | Classroom | 737 | 49 |  |  | 539 | 12 | 12
Old Building | 412 | Classroom | 956 | 63 |  |  | 935 | 21 | 21
Old Building | 413 | Classroom | 349 | 23 |  |  | 460 | 10 | 10
Old Building | 414 | Classroom | 446 | 29 |  |  | 462 | 10 | 10
Old Building | 415 | Classroom | 600 | 40 |  |  | 601 | 13 | 13
Old Building | 501 | Classroom | 0 | 0 |  |  | 583 | 13 | 0
Old Building | 505 | Classroom | 1040 | 69 |  |  | 701 | 15 | 15
Old Building | 506 | Classroom | 0 | 0 |  |  | 110 | 2 | 0
Old Building | 510 | Classroom | 595 | 39 |  |  | 652 | 14 | 14
Old Building | 511 | Classroom |  | 0 |  | Yes | 917 | 20
Old Building | 512 | Classroom | 0 | 0 |  |  | 734 | 16 | 0
Old Building | 513 | Classroom | 708 | 47 |  |  | 745 | 16 | 16
Old Building | 601 | Classroom | 352 | 23 |  |  | 562 | 12 | 12
Old Building | 602 | Classroom | 838 | 55 |  |  | 935 | 21 | 21
Old Building | 603 | Classroom | 1066 | 71 |  |  | 929 | 21 | 21
Old Building | 604 | Classroom | 604 | 40 |  |  | 884 | 20 | 20
Old Building | 605 | Classroom | 555 | 37 |  |  | 964 | 21 | 21
Old Building | 607 | Classroom | 733 | 48 |  |  | 930 | 21 | 21
Old Building | 609 | Classroom | 350 | 23 |  |  | 498 | 11 | 11
Old Building | 610 | Classroom | 1042 | 69 |  |  | 939 | 21 | 21
Old Building | 611 | Classroom | 944 | 62 |  |  | 943 | 21 | 21
Old Building | 612 | Classroom | 357 | 23 |  |  | 598 | 13 | 13
Old Building | 613 | Classroom | 312 | 20 |  |  | 696 | 15 | 15
Old Building | 614 | Classroom | 0 | 0 |  |  | 823 | 18 | 0
Old Building | 615 | Classroom | 411 | 27 |  |  | 1008 | 22 | 22
Old Building | 616 | Classroom | 1153 | 76 |  |  | 901 | 20 | 20
Old Building | 617 | Classroom | 0 | 0 |  |  | 899 | 20 | 0
Old Building | B1 A | Wood Shop | 475 | 31 |  |  | 2780 | 63 | 31
Old Building | B2 A | Classroom | 499 | 33 |  |  | 967 | 21 | 21
Old Building | - | Auditorium | 1222 | 81 |  |  | 4005 | 91 | 81
Old Building | - | 3rd Flr. Gym | 2212 | 147 |  |  | 3295 | 74 | 74
Old Building | - | 3rd Flr.Gym Locker Room | 3013 | 200 |  |  | 1903 | 43 | 43
Old Building | - | Stage | 532 | 35 |  |  | 993 | 22 | 22
Old Building | - | 1st Floor N Corridor | 301 | 20 |  |  | 160 | 3 | 3
Old Building | - | 1st Floor E Corridor | 536 | 35 |  |  | 160 | 3 | 3
Old Building | - | 1st Floor S Corridor | 427 | 28 |  |  | 2120 | 48 | 28
Old Building | - | 1st Floor W Corridor | 382 | 25 |  |  | 160 | 3 | 3
Old Building | - | 2nd Floor S Corridor | 438 | 29 |  |  | 2120 | 48 | 29
Old Building | - | 2nd Floor W Corridor | 465 | 31 |  |  | 160 | 3 | 3
Old Building | - | 2nd Floor N Corridor | 711 | 47 |  |  | 2120 | 48 | 47
Old Building | - | 2nd Floor E Corridor | 720 | 48 |  |  | 160 | 3 | 3
Old Building | - | 3rd Floor E Corridor | 504 | 33 |  |  |  | 0 | 0
Old Building | - | 3rd Floor N Corridor | 619 | 41 |  |  | 2120 | 48 | 41
Old Building | - | 3rd Floor W Corridor | 761 | 50 |  |  |  | 0 | 0
Old Building | - | 3rd Floor S Corridor | 569 | 37 |  |  | 2120 | 48 | 37
Old Building | - | 4th Floor N Corridor | 502 | 33 |  |  | 2120 | 48 | 33
Old Building | - | 4th Floor E Corridor | 633 | 42 |  |  |  | 0 | 0
Old Building | - | 4th Floor S Corridor | 0 | 0 |  |  | 2120 | 48 | 0
Old Building | - | 4th Floor W Corridor | 0 | 0 |  |  |  | 0 | 0
Old Building | - | 5th Floor N Corridor | 593 | 39 |  |  | 2120 | 48 | 39
Old Building | - | 5th Floor Library | 1677 | 111 |  |  | 2115 | 48 | 48
Old Building | - | 6th Floor S Corridor | 683 | 45 |  |  | 2120 | 48 | 45
Old Building | - | 6th Floor W Corridor | 918 | 61 |  |  |  | 0 | 0
Old Building | - | 6th Floor N Corridor | 530 | 35 |  |  | 2120 | 48 | 35
Old Building | - | 6th Floor E Corridor | 0 | 0 |  |  |  | 0 | 0
Old Building | - | Café | 1559 | 103 |  |  | 734 | 16 | 16
New Building | 120 | Auto Shop | 1016 | 67 |  |  | 2981 | 67 | 67
New Building | 124 | Auto Shop | 8220 | 548 |  |  | 4344 | 98 | 98
New Building | 220-221 | Electrical Shop | 0 | 0 |  |  | 1973 | 44 | 0
New Building | 224-223 | Shop | 2067 | 137 |  |  | 1150 | 26 | 26
New Building | 225-226 | Shop | 2858 | 190 |  |  | 3743 | 85 | 85
New Building | 324-323 | 324-323 | 877 | 58 |  |  | 2781 | 63 | 58
New Building | 326-325 | 326-325 | 1135 | 75 |  |  | 2395 | 54 | 54
New Building | 420 | 420 | 0 | 0 |  |  | 1250 | 28 | 0
New Building | 421 | 421 | 0 | 0 |  |  | 1873 | 42 | 0
New Building | 423 | 423 | 487 | 32 |  |  | 1693 | 38 | 32
New Building | 426 | 426 Plumbing Shop | 1678 | 111 |  |  | 1265 | 28 | 28
New Building | 427-426 | 427-426 | 0 | 0 |  |  | 1583 | 35 | 0
New Building | - | Gym | 958 | 63 |  |  | 7556 | 171 | 63
New Building | - | Gym Locker Rm. | 0 | 0 |  |  | 5738 | 130 | 0
New Building | 321 | Nursing | 614 | 40 |  |  | 1898 | 43 | 40
New Building | - | Weld Shop | 2329 | 155 |  |  | 625 | 14 | 14
Sheet Last Modified: | 2021-04-07
School: | Julia R. Masterman Laboratory and Demonstration High School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
8 | Music Room |  | 0 |  |  | 630 | 14 | 0 |  | 8 | 5040 | 0 | 1 | 0 | 0 | 0 | 0
9 | Classroom | 0 | 0 |  |  | 874 | 19 | 0 |  | 8 | 6992 | 0 | 1 | 0 | 0 | 0 | 0
11 | Classroom | 0 | 0 |  |  | 825 | 18 | 0 | AHU Inoperable | 8 | 6600 | 0 | 1 | 0 | 0 | 0 | 0
11A | Classroom | 0 | 0 |  |  | 368 | 8 | 0 | AHU Inoperable | 8 | 2944 | 0 | 1 | 0 | 0 | 0 | 0
12 | Classroom | 0 | 0 |  |  | 832 | 18 | 0 | AHU Inoperable | 8 | 6656 | 0 | 1 | 0 | 0 | 0 | 0
14 | Art Room |  | 0 |  |  | 1023 | 23 | 0 | AHU Inoperable | 8 | 8184 | 0 | 1 | 0 | 0 | 0 | 0
15 | Classroom | 0 | 0 |  |  | 1148 | 26 | 0 |  | 8 | 9184 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom | 0 | 0 | Yes | 20 | 704 | 16 | 16 | AHU Inoperable | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
102 | Music Room | 0 | 0 |  |  | 836 | 19 | 0 | AHU Inoperable | 8 | 6688 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom | 0 | 0 |  |  | 638 | 14 | 0 | AHU Inoperable | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
104 | Classroom | 0 | 0 |  |  | 660 | 15 | 0 | AHU Inoperable | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom | 0 | 0 | Yes | 20 | 704 | 16 | 16 | AHU Inoperable | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 |  |  | 682 | 15 | 0 | AHU Inoperable | 8 | 5456 | 0 | 1 | 0 | 0 | 0 | 0
203 | Classroom | 0 | 0 | Yes | 20 | 644 | 14 | 14 | AHU Inoperable | 8 | 5152 | 0 | 1 | 0 | 0 | 20 | 3
204 | Library | 0 | 0 |  |  | 682 | 15 | 0 | AHU Inoperable | 8 | 5456 | 0 | 1 | 0 | 0 | 0 | 0
205 | Fitness Storage | 0 | 0 | Yes | 20 | 690 | 15 | 15 | AHU Inoperable | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
206 | Fitness Storage | 0 | 0 |  |  | 704 | 16 | 0 | AHU Inoperable | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 20 | 660 | 15 | 15 | AHU Inoperable | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 |  |  | 682 | 15 | 0 | AHU Inoperable | 8 | 5456 | 0 | 1 | 0 | 0 | 0 | 0
209 | Classroom | 0 | 0 |  |  | 187 | 4 | 0 | AHU Inoperable | 8 | 1496 | 0 | 1 | 0 | 0 | 0 | 0
210 | Classroom | 0 | 0 |  |  | 187 | 4 | 0 | AHU Inoperable | 8 | 1496 | 0 | 1 | 0 | 0 | 0 | 0
211 | Classroom | 0 | 0 | Yes | 20 | 682 | 15 | 15 | AHU Inoperable | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
212 | Classroom | 0 | 0 |  |  | 682 | 15 | 0 | AHU Inoperable | 8 | 5456 | 0 | 1 | 0 | 0 | 0 | 0
213 | Classroom | 0 | 0 |  |  | 374 | 8 | 0 | AHU Inoperable | 8 | 2992 | 0 | 1 | 0 | 0 | 0 | 0
214 | Classroom | 0 | 0 |  |  | 374 | 8 | 0 | AHU Inoperable | 8 | 2992 | 0 | 1 | 0 | 0 | 0 | 0
218 | Main Office |  | 0 | Yes | 20 | 210 | 4 | 4 | AHU Inoperable | 8 | 1680 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 | Yes | 20 | 682 | 15 | 15 |  | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 |  |  | 682 | 15 | 0 | AHU Inoperable | 8 | 5456 | 0 | 1 | 0 | 0 | 0 | 0
303 | Classroom | 0 | 0 |  |  | 660 | 15 | 0 | AHU Inoperable | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
304 | Classroom | 0 | 0 |  |  | 682 | 15 | 0 | AHU Inoperable | 8 | 5456 | 0 | 1 | 0 | 0 | 0 | 0
305 | Classroom | 0 | 0 | Yes | 20 | 638 | 14 | 14 | AHU Inoperable | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 |  |  | 144 | 3 | 0 | AHU Inoperable | 8 | 1152 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom |  | 0 |  |  | 726 | 16 | 0 | AHU Inoperable | 8 | 5808 | 0 | 1 | 0 | 0 | 0 | 0
307A | Office |  | 0 |  |  | 264 | 6 | 0 |  | 8 | 2112 | 0 | 1 | 0 | 0 | 0 | 0
308 | Classroom | 0 | 0 |  |  | 1210 | 27 | 0 |  | 8 | 9680 | 0 | 1 | 0 | 0 | 0 | 0
309 | Office | 0 | 0 |  |  | 300 | 6 | 0 | AHU Inoperable | 8 | 2400 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom | 0 | 0 |  |  | 96 | 2 | 0 | AHU Inoperable | 8 | 768 | 0 | 1 | 0 | 0 | 0 | 0
311 | Classroom | 0 | 0 |  |  | 682 | 15 | 0 | AHU Inoperable | 8 | 5456 | 0 | 1 | 0 | 0 | 0 | 0
312 | Classroom | 0 | 0 |  |  | 1078 | 24 | 0 | AHU Inoperable | 8 | 8624 | 0 | 1 | 0 | 0 | 0 | 0
313 | Room |  | 0 |  |  | 374 | 8 | 0 | AHU Inoperable | 8 | 2992 | 0 | 1 | 0 | 0 | 0 | 0
402 | Classroom | 0 | 0 |  |  | 880 | 20 | 0 |  | 8 | 7040 | 0 | 1 | 0 | 0 | 0 | 0
404 | Classroom | 0 | 0 |  |  | 704 | 16 | 0 | AHU Inoperable | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
406 | Classroom | 0 | 0 |  |  | 504 | 11 | 0 | AHU Inoperable | 8 | 4032 | 0 | 1 | 0 | 0 | 0 | 0
408 | Classroom | 0 | 0 |  |  | 672 | 15 | 0 | AHU Inoperable | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
410 | Classroom | 0 | 0 |  |  | 1008 | 22 | 0 | AHU Inoperable | 8 | 8064 | 0 | 1 | 0 | 0 | 0 | 0
412 | Office | 0 | 0 |  |  | 205 | 4 | 0 | AHU Inoperable | 8 | 1640 | 0 | 1 | 0 | 0 | 0 | 0
502 | Classroom | 0 | 0 |  |  | 880 | 20 | 0 | AHU Inoperable | 8 | 7040 | 0 | 1 | 0 | 0 | 0 | 0
506 | Classroom | 0 | 0 |  |  | 690 | 15 | 0 | AHU Inoperable | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
- | Game Room |  | 0 |  |  | 790 | 17 | 0 | AHU Inoperable | 8 | 6320 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 |  |  | 5850 | 132 | 0 |  | 8 | 46800 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 |  |  | 3600 | 81 | 0 | AHU Inoperable | 8 | 28800 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Counselor's Office |  | 0 |  |  | 110 | 2 | 0 | AHU Inoperable | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
- | Counselor's Office |  | 0 |  |  | 110 | 2 | 0 |  | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
- | Faculty Cafeteria | 0 | 0 |  |  | 726 | 16 | 0 |  | 8 | 5808 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym | 0 | 0 | Yes | 20 | 6208 | 141 | 141 | AHU Inoperable | 8 | 49664 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Boy's Locker Room |  | 0 |  |  | 580 | 13 | 0 |  | 8 | 4640 | 0 | 1 | 0 | 0 | 0 | 0
- | Girl's Locker Room |  | 0 |  |  | 209 | 4 | 0 |  | 8 | 1672 | 0 | 1 | 0 | 0 | 0 | 0
- | Health room |  | 0 |  |  | 100 | 2 | 0 |  | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
- | Kitchen | 0 | 0 |  |  | 828 | 18 | 0 | AHU Inoperable | 8 | 6624 | 0 | 1 | 0 | 0 | 0 | 0
- | LIbrary Room |  | 0 |  |  | 620 | 14 | 0 |  | 8 | 4960 | 0 | 1 | 0 | 0 | 0 | 0
- | Library Office |  | 0 |  |  | 231 | 5 | 0 |  | 8 | 1848 | 0 | 1 | 0 | 0 | 0 | 0
- | Library A |  | 0 |  |  | 506 | 11 | 0 |  | 8 | 4048 | 0 | 1 | 0 | 0 | 0 | 0
- | Library B |  | 0 |  |  | 651 | 14 | 0 |  | 8 | 5208 | 0 | 1 | 0 | 0 | 0 | 0
- | Library C |  | 0 |  |  | 230 | 5 | 0 |  | 8 | 1840 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurse Office | 0 | 0 | Yes | 20 | 170 | 3 | 3 | AHU Inoperable | 8 | 1360 | 0 | 1 | 0 | 0 | 20 | 3
| Nurse Examining |  | 0 | Yes | 20 | 100 | 2 | 2 |  | 8 | 800 | 0 | 1 | 0 | 0 | 20 | 3
| Nurse Roster Room |  | 0 | Yes | 20 | 288 | 6 | 6 |  | 8 | 2304 | 0 | 1 | 0 | 0 | 20 | 3
- | Robotics | 0 | 0 |  |  | 420 | 9 | 0 | AHU Inoperable | 8 | 3360 | 0 | 1 | 0 | 0 | 0 | 0
- | Science Office |  | 0 |  |  | 187 | 4 | 0 |  | 8 | 1496 | 0 | 1 | 0 | 0 | 0 | 0
- | Principal 's Office |  | 0 |  |  | 210 | 4 | 0 |  | 8 | 1680 | 0 | 1 | 0 | 0 | 0 | 0
- | Assant Principal's Office |  | 0 |  |  | 140 | 3 | 0 |  | 8 | 1120 | 0 | 1 | 0 | 0 | 0 | 0
- | Operations Office |  | 0 |  |  | 56 | 1 | 0 |  | 8 | 448 | 0 | 1 | 0 | 0 | 0 | 0
- | Office Waiting Area |  | 0 |  |  | 275 | 6 | 0 |  | 8 | 2200 | 0 | 1 | 0 | 0 | 0 | 0
- | Roster Office |  | 0 |  |  | 136 | 3 | 0 |  | 8 | 1088 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23
School: | Mayfair Elementary School
Vendor: | Devine Brothers | Devine Part 2 | Devine Part 3
Vendor: | Capital | Capital Update | Capital Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 207 | 13 |  |  | 696 | 15 | 13 | Unit Ventilator | 8 | 5568 | 2.2306 | 1 | 2.2306 | 1 | 2.2306 | 1
101 | Classroom | 201 | 13 |  |  | 696 | 15 | 13 | Unit Ventilator | 8 | 5568 | 2.1659 | 1 | 2.1659 | 1 | 2.1659 | 1
102 | Classroom | 197 | 13 |  |  | 598 | 13 | 13 | Unit Ventilator | 8 | 4784 | 2.4707 | 1 | 2.4707 | 1 | 2.4707 | 1
103 | Classroom | 189 | 12 |  |  | 720 | 16 | 12 | Unit Ventilator | 8 | 5760 | 1.9688 | 1 | 1.9688 | 1 | 1.9688 | 1
104 | Classroom | 355 | 23 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.8587 | 1 | 3.8587 | 1 | 3.8587 | 1
105 | Classroom | 231 | 15 |  |  | 624 | 14 | 14 | Unit Ventilator | 8 | 4992 | 2.7764 | 1 | 2.7764 | 1 | 2.7764 | 1
106 | Classroom | 237 | 15 |  |  | 720 | 16 | 15 | Unit Ventilator | 8 | 5760 | 2.4688 | 1 | 2.4688 | 1 | 2.4688 | 1
107 | Classroom | 458 | 30 |  |  | 720 | 16 | 16 | Unit Ventilator | 8 | 5760 | 4.7708 | 1 | 4.7708 | 2 | 4.7708 | 2
108 | Classroom | 115 | 7 |  |  | 600 | 13 | 7 | Unit Ventilator | 8 | 4800 | 1.4375 | 1 | 1.4375 | 1 | 1.4375 | 1
109 | Classroom | 186 | 12 |  |  | 744 | 16 | 12 | Unit Ventilator | 8 | 5952 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
110 | Classroom | 418 | 27 |  |  | 696 | 15 | 15 | Unit Ventilator | 8 | 5568 | 4.5043 | 1 | 4.5043 | 2 | 4.5043 | 2
111 | Classroom | 202 | 13 |  |  | 624 | 14 | 13 | Unit Ventilator | 8 | 4992 | 2.4279 | 1 | 2.4279 | 1 | 2.4279 | 1
112 | Classroom | 461 | 30 |  |  | 1032 | 23 | 23 | Unit Ventilator | 8 | 8256 | 3.3503 | 1 | 3.3503 | 1 | 3.3503 | 1
113 | Classroom | 211 | 14 |  |  | 720 | 16 | 14 | Unit Ventilator | 8 | 5760 | 2.1979 | 1 | 2.1979 | 1 | 2.1979 | 1
114 | Classroom | 377 | 25 |  |  | 644 | 14 | 14 | Unit Ventilator | 8 | 5152 | 4.3905 | 1 | 4.3905 | 2 | 4.3905 | 2
115 | Classroom | 271 | 18 |  |  | 620 | 14 | 14 | Unit Ventilator | 8 | 4960 | 3.2782 | 1 | 3.2782 | 1 | 3.2782 | 1
116 | Classroom | 395 | 26 |  |  | 989 | 22 | 22 | Unit Ventilator | 8 | 7912 | 2.9954 | 1 | 2.9954 | 1 | 2.9954 | 1
118 | Classroom | 384 | 25 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.1739 | 1 | 4.1739 | 2 | 4.1739 | 2
119 | Classroom | 320 | 21 |  |  | 624 | 14 | 14 | Unit Ventilator | 8 | 4992 | 3.8462 | 1 | 3.8462 | 1 | 3.8462 | 1
120 | Classroom | 311 | 20 |  |  | 1610 | 36 | 20 | Unit Ventilator | 8 | 12880 | 1.4488 | 1 | 1.4488 | 1 | 1.4488 | 1
200 | Classroom |  | 0 | Yes | 20 | 205 | 4 | 4 |  | 8 | 1640 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 286 | 19 |  |  | 696 | 15 | 15 | Unit Ventilator | 8 | 5568 | 3.0819 | 1 | 3.0819 | 1 | 3.0819 | 1
202 | Classroom | 560 | 37 |  |  | 696 | 15 | 15 | Unit Ventilator | 8 | 5568 | 6.0345 | 1 | 6.0345 | 2 | 6.0345 | 2
203 | Classroom | 381 | 25 |  |  | 725 | 16 | 16 | Unit Ventilator | 8 | 5800 | 3.9414 | 1 | 3.9414 | 1 | 3.9414 | 1
204 | Classroom | 323 | 21 |  |  | 884 | 20 | 20 | Unit Ventilator | 8 | 7072 | 2.7404 | 1 | 2.7404 | 1 | 2.7404 | 1
205 | Classroom | 271 | 18 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.6058 | 1 | 2.6058 | 1 | 2.6058 | 1
206 | Classroom | 316 | 21 |  |  | 806 | 18 | 18 | Unit Ventilator | 8 | 6448 | 2.9404 | 1 | 2.9404 | 1 | 2.9404 | 1
207 | Classroom | 295 | 19 |  |  | 806 | 18 | 18 | Unit Ventilator | 8 | 6448 | 2.745 | 1 | 2.745 | 1 | 2.745 | 1
207A | Asst. Principal Office | 0 | 0 | Yes | 20 | 293 | 6 | 6 | Unit Ventilator | 8 | 2344 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 305 | 20 |  |  | 528 | 12 | 12 | Unit Ventilator | 8 | 4224 | 4.3324 | 1 | 4.3324 | 2 | 4.3324 | 2
209 | Classroom | 560 | 37 |  |  | 884 | 20 | 20 | Unit Ventilator | 8 | 7072 | 4.7511 | 1 | 4.7511 | 2 | 4.7511 | 2
210 | Classroom | 290 | 19 |  |  | 1118 | 25 | 19 | Unit Ventilator | 8 | 8944 | 1.9454 | 1 | 1.9454 | 1 | 1.9454 | 1
211 | Classroom | 307 | 20 |  |  | 648 | 14 | 14 | Unit Ventilator | 8 | 5184 | 3.5532 | 1 | 3.5532 | 1 | 3.5532 | 1
212 | Classroom | 483 | 32 |  |  | 665 | 15 | 15 | Unit Ventilator | 8 | 5320 | 5.4474 | 1 | 5.4474 | 2 | 5.4474 | 2
213 | Classroom | 590 | 39 |  |  | 806 | 18 | 18 | Unit Ventilator | 8 | 6448 | 5.4901 | 1 | 5.4901 | 2 | 5.4901 | 2
214 | Classroom | 300 | 20 |  |  | 806 | 18 | 18 | Unit Ventilator | 8 | 6448 | 2.7916 | 1 | 2.7916 | 1 | 2.7916 | 1
215 | Classroom | 294 | 19 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 3.0288 | 1 | 3.0288 | 1 | 3.0288 | 1
216 | Classroom | 317 | 21 |  |  | 648 | 14 | 14 | Unit Ventilator | 8 | 5184 | 3.669 | 1 | 3.669 | 1 | 3.669 | 1
217 | Classroom | 350 | 23 |  |  | 782 | 17 | 17 | Unit Ventilator | 8 | 6256 | 3.3568 | 1 | 3.3568 | 1 | 3.3568 | 1
218 | Classroom | 271 | 18 |  |  | 621 | 14 | 14 | Unit Ventilator | 8 | 4968 | 3.2729 | 1 | 3.2729 | 1 | 3.2729 | 1
219 | Classroom | 137 | 9 |  |  | 648 | 14 | 9 | Unit Ventilator | 8 | 5184 | 1.5856 | 1 | 1.5856 | 1 | 1.5856 | 1
220 | Classroom | 235 | 15 |  |  | 648 | 14 | 14 | Unit Ventilator | 8 | 5184 | 2.7199 | 1 | 2.7199 | 1 | 2.7199 | 1
221 | Classroom | 325 | 21 |  |  | 744 | 16 | 16 | Unit Ventilator | 8 | 5952 | 3.2762 | 1 | 3.2762 | 1 | 3.2762 | 1
222 | Classroom | 180 | 12 |  |  | 648 | 14 | 12 | Unit Ventilator | 8 | 5184 | 2.0833 | 1 | 2.0833 | 1 | 2.0833 | 1
301 | Classroom | 325 | 21 |  |  | 720 | 16 | 16 | ERU | 8 | 5760 | 3.3854 | 1 | 3.3854 | 1 | 3.3854 | 1
302 | Classroom | 304 | 20 |  |  | 720 | 16 | 16 | ERU | 8 | 5760 | 3.1667 | 1 | 3.1667 | 1 | 3.1667 | 1
303 | Classroom | 270 | 18 |  |  | 720 | 16 | 16 | ERU | 8 | 5760 | 2.8125 | 1 | 2.8125 | 1 | 2.8125 | 1
304 | Classroom | 435 | 29 |  |  | 720 | 16 | 16 | ERU | 8 | 5760 | 4.5312 | 1 | 4.5312 | 2 | 4.5312 | 2
305 | Classroom | 453 | 30 |  |  | 720 | 16 | 16 | ERU | 8 | 5760 | 4.7188 | 1 | 4.7188 | 2 | 4.7188 | 2
306 | Classroom | 480 | 32 |  |  | 720 | 16 | 16 | ERU | 8 | 5760 | 5 | 1 | 5 | 2 | 5 | 2
401 | Classroom | 320 | 21 |  |  | 720 | 16 | 16 | ERU | 8 | 5760 | 3.3333 | 1 | 3.3333 | 1 | 3.3333 | 1
402 | Classroom | 282 | 18 |  |  | 720 | 16 | 16 | ERU | 8 | 5760 | 2.9375 | 1 | 2.9375 | 1 | 2.9375 | 1
403 | Classroom | 551 | 36 |  |  | 720 | 16 | 16 | ERU | 8 | 5760 | 5.7396 | 1 | 5.7396 | 2 | 5.7396 | 2
404 | Classroom | 412 | 27 |  |  | 720 | 16 | 16 | ERU | 8 | 5760 | 4.2917 | 1 | 4.2917 | 2 | 4.2917 | 2
405 | Classroom | 412 | 27 |  |  | 720 | 16 | 16 | ERU | 8 | 5760 | 4.2917 | 1 | 4.2917 | 2 | 4.2917 | 2
406 | Classroom | 406 | 27 |  |  | 720 | 16 | 16 | ERU | 8 | 5760 | 4.2292 | 1 | 4.2292 | 2 | 4.2292 | 2
510 | Classroom | 282 | 18 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 2.805 | 1 | 2.805 | 1 | 2.805 | 1
511 | Classroom | 430 | 28 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 4.2772 | 1 | 4.2772 | 2 | 4.2772 | 2
512 | Classroom | 447 | 29 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 4.4463 | 1 | 4.4463 | 2 | 4.4463 | 2
513 | Classroom | 543 | 36 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 5.4012 | 1 | 5.4012 | 2 | 5.4012 | 2
515 | Classroom | 652 | 43 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 6.4854 | 1 | 6.4854 | 2 | 6.4854 | 2
516 | Classroom | 519 | 34 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 5.1625 | 1 | 5.1625 | 2 | 5.1625 | 2
517 | Classroom | 605 | 40 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 6.0179 | 1 | 6.0179 | 2 | 6.0179 | 2
520 | Classroom | 500 | 33 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 4.9735 | 1 | 4.9735 | 2 | 4.9735 | 2
521 | Classroom | 548 | 36 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 5.4509 | 1 | 5.4509 | 2 | 5.4509 | 2
522 | Classroom | 530 | 35 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 5.2719 | 1 | 5.2719 | 2 | 5.2719 | 2
523 | Classroom | 509 | 33 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 5.063 | 1 | 5.063 | 2 | 5.063 | 2
525 | Classroom | 676 | 45 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 6.7241 | 1 | 6.7241 | 2 | 6.7241 | 2
526 | Classroom | 646 | 43 |  |  | 754 | 17 | 17 | ERU | 8 | 6032 | 6.4257 | 1 | 6.4257 | 2 | 6.4257 | 2
527 | Classroom | 568 | 37 |  |  | 774 | 17 | 17 | ERU | 8 | 6192 | 5.5039 | 1 | 5.5039 | 2 | 5.5039 | 2
- | Main Office |  | 0 | Yes | 20 | 493 | 11 | 11 |  | 8 | 3944 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office |  | 0 | Yes | 20 | 126 | 2 | 2 |  | 8 | 1008 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office |  | 0 | Yes | 20 | 231 | 5 | 5 |  | 8 | 1848 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 196 | 4 | 4 |  | 8 | 1568 | 0 | 1 | 0 | 0 | 20 | 3
- | Special Education |  | 0 | Yes | 20 | 275 | 6 | 6 |  | 8 | 2200 | 0 | 1 | 0 | 0 | 20 | 3
- | Conference Room |  | 0 | Yes | 20 | 135 | 3 | 3 |  | 8 | 1080 | 0 | 1 | 0 | 0 | 20 | 3
- | Faculty Room |  | 0 | Yes | 20 | 171 | 3 | 3 |  | 8 | 1368 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 372 | 8 | 8 |  | 8 | 2976 | 0 | 1 | 0 | 0 | 20 | 3
- | Asst. Principal 1 |  | 0 | Yes | 20 | 86 | 1 | 1 |  | 8 | 688 | 0 | 1 | 0 | 0 | 20 | 3
- | Asst. Principal 2 |  | 0 | Yes | 20 | 97 | 2 | 2 |  | 8 | 776 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium |  | 0 |  |  | 4920 | 111 | 0 | AHU | 8 | 39360 | 0 | 1.062 | 0 | 0 | 0 | 0
| Auditorium Room 1 |  | 0 | Yes | 20 | 263 | 5 | 5 |  | 8 | 2104 | 0 | 1 | 0 | 0 | 20 | 3
| Auditorium Room 2 |  | 0 | Yes | 20 | 254 | 5 | 5 |  | 8 | 2032 | 0 | 1 | 0 | 0 | 20 | 3
Music 1 | Room |  | 0 | Yes | 20 | 354 | 8 | 8 |  | 8 | 2832 | 0 | 1 | 0 | 0 | 20 | 3
Music 2 | Room |  | 0 | Yes | 20 | 711 | 16 | 16 |  | 8 | 5688 | 0 | 1 | 0 | 0 | 20 | 3
- | Cafeteria | 998 | 66 |  |  | 3257 | 74 | 66 | RTU | 8 | 26056 | 2.2981 | 1.062 | 2.4407 | 1 | 2.4407 | 1
- | Gym |  | 0 | Yes | 20 | 3982 | 90 | 90 | AHU | 8 | 31856 | 0 | 1.062 | 0 | 0 | 20 | 3
School Police | Office |  | 0 | Yes | 20 | 54 | 1 | 1 |  | 8 | 432 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office | 292 | 19 |  |  | 372 | 8 | 8 | Unit Ventilator | 8 | 2976 | 5.8871 | 1 | 5.8871 | 2 | 5.8871 | 2
1 | Mobile Classroom | 326 | 21 |  |  | 594 | 13 | 13 | AHU | 8 | 4752 | 4.1162 | 1 | 4.1162 | 2 | 4.1162 | 2
2 | Mobile Classroom | 328 | 21 |  |  | 594 | 13 | 13 | AHU | 8 | 4752 | 4.1414 | 1 | 4.1414 | 2 | 4.1414 | 2
3 | Mobile Classroom | 644 | 42 |  |  | 594 | 13 | 13 | AHU | 8 | 4752 | 8.1313 | 1 | 8.1313 | 2 | 8.1313 | 2
4 | Mobile Classroom | 451 | 30 |  |  | 594 | 13 | 13 | AHU | 8 | 4752 | 5.6944 | 1 | 5.6944 | 2 | 5.6944 | 2
5 | Mobile Classroom | 580 | 38 |  |  | 594 | 13 | 13 | AHU | 8 | 4752 | 7.3232 | 1 | 7.3232 | 2 | 7.3232 | 2
6 | Mobile Classroom | 438 | 29 |  |  | 594 | 13 | 13 | AHU | 8 | 4752 | 5.5303 | 1 | 5.5303 | 2 | 5.5303 | 2
7 | Mobile Classroom | 414 | 27 |  |  | 594 | 13 | 13 | AHU | 8 | 4752 | 5.2273 | 1 | 5.2273 | 2 | 5.2273 | 2
8 | Mobile Classroom | 574 | 38 |  |  | 594 | 13 | 13 | AHU | 8 | 4752 | 7.2475 | 1 | 7.2475 | 2 | 7.2475 | 2
Sheet Last Modified: | 2021-04-06
School: | General George A. McCall Elementary School
Vendor: | Devine | 2nd Retest | 3rd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
0 | Classroom | 0 | 0 | Yes | 20 | 572 | 13 | 13 | N/A | 8 | 4576 | 0 | 1 | 0 | 0 | 20 | 3
1 | Classroom | 370 | 24 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 3.0032 | 1 | 3.0032 | 1 | 3.0032 | 1
2 | Music Room | 453 | 30 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 4.064 | 1 | 4.064 | 2 | 4.064 | 2
4 | Classroom | 1631 | 108 |  |  | 660 | 15 | 15 | AHU | 8 | 5280 | 18.5341 | 1 | 18.5341 | 3 | 18.5341 | 3
5 | Classroom | 478 | 31 |  |  | 1012 | 23 | 23 | AHU | 8 | 8096 | 3.5425 | 1 | 3.5425 | 1 | 3.5425 | 1
6 | Classroom | 535 | 35 |  |  | 1100 | 25 | 25 | AHU | 8 | 8800 | 3.6477 | 1 | 3.6477 | 1 | 3.6477 | 1
101 | Office | 0 | 0 | Yes | 20 | 276 | 6 | 6 | N/A | 8 | 2208 | 0 | 1 | 0 | 0 | 20 | 3
101A | Office | 182 | 12 | Yes | 20 | 440 | 10 | 10 | Unit Ventilator | 8 | 3520 | 3.1023 | 1 | 3.1023 | 1 | 23.1023 | 3
102 | Classroom | 332 | 22 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 2.9785 | 1 | 2.9785 | 1 | 2.9785 | 1
103 | Classroom | 283 | 18 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 2.4119 | 1 | 2.4119 | 1 | 22.4119 | 3
105 | Classroom | 278 | 18 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 2.3693 | 1 | 2.3693 | 1 | 22.3693 | 3
106 | Classroom | 340 | 22 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 2.7597 | 1 | 2.7597 | 1 | 2.7597 | 1
107 | Classroom | 292 | 19 | Yes | 20 | 968 | 22 | 22 | Unit Ventilator | 8 | 7744 | 2.2624 | 1 | 2.2624 | 1 | 22.2624 | 3
108 | Classroom | 303 | 20 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 2.7183 | 1 | 2.7183 | 1 | 2.7183 | 1
109 | Classroom | 375 | 25 |  |  | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 3.196 | 1 | 3.196 | 1 | 3.196 | 1
110 | Classroom | 0 | 0 | Yes | 20 | 220 | 5 | 5 | N/A | 8 | 1760 | 0 | 1 | 0 | 0 | 20 | 3
110A | Office | 336 | 22 |  |  | 440 | 10 | 10 | Unit Ventilator | 8 | 3520 | 5.7273 | 1 | 5.7273 | 2 | 5.7273 | 2
209 | Classroom | 0 | 0 | Yes | 20 | 440 | 10 | 10 | Unit Ventilator | 8 | 3520 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom | 273 | 18 | Yes | 20 | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 2.3267 | 1 | 2.3267 | 1 | 22.3267 | 3
211 | Classroom | 293 | 19 | Yes | 20 | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 2.3782 | 1 | 2.3782 | 1 | 22.3782 | 3
212 | Classroom | 294 | 19 |  |  | 880 | 20 | 19 | Unit Ventilator | 8 | 7040 | 2.5057 | 1 | 2.5057 | 1 | 2.5057 | 1
213 | Classroom | 320 | 21 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 2.5974 | 1 | 2.5974 | 1 | 2.5974 | 1
214 | Classroom | 376 | 25 |  |  | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 3.2045 | 1 | 3.2045 | 1 | 3.2045 | 1
216A | Office | 0 | 0 | Yes | 20 | 480 | 10 | 10 | N/A | 8 | 3840 | 0 | 1 | 0 | 0 | 20 | 3
217 | Classroom | 297 | 19 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 2.8125 | 1 | 2.8125 | 1 | 2.8125 | 1
218 | Classroom | 309 | 20 |  |  | 924 | 21 | 20 | Unit Ventilator | 8 | 7392 | 2.5081 | 1 | 2.5081 | 1 | 2.5081 | 1
219 | Classroom | 313 | 20 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 2.964 | 1 | 2.964 | 1 | 2.964 | 1
318 | Classroom | 172 | 11 | Yes | 20 | 748 | 17 | 17 | Unit Ventilator | 8 | 5984 | 1.7246 | 1 | 1.7246 | 1 | 21.7246 | 3
319 | Classroom | 368 | 24 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 2.987 | 1 | 2.987 | 1 | 2.987 | 1
320 | Classroom | 401 | 26 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 3.5975 | 1 | 3.5975 | 1 | 3.5975 | 1
321 | Classroom | 329 | 21 |  |  | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 2.804 | 1 | 2.804 | 1 | 2.804 | 1
322 | Classroom | 292 | 19 |  |  | 924 | 21 | 19 | Unit Ventilator | 8 | 7392 | 2.3701 | 1 | 2.3701 | 1 | 2.3701 | 1
323 | Classroom | 351 | 23 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 2.849 | 1 | 2.849 | 1 | 2.849 | 1
324 | Classroom | 284 | 18 |  |  | 880 | 20 | 18 | Unit Ventilator | 8 | 7040 | 2.4205 | 1 | 2.4205 | 1 | 2.4205 | 1
325 | Classroom | 396 | 26 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 3.2143 | 1 | 3.2143 | 1 | 3.2143 | 1
326 | Classroom | 309 | 20 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 2.7721 | 1 | 2.7721 | 1 | 2.7721 | 1
327 | Classroom | 345 | 23 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 3.267 | 1 | 3.267 | 1 | 3.267 | 1
327A | Classroom | 261 | 17 |  |  | 484 | 11 | 11 | Unit Ventilator | 8 | 3872 | 4.0444 | 1 | 4.0444 | 2 | 4.0444 | 2
- | Auditorium | 1451 | 96 |  |  | 4224 | 96 | 96 | AHU | 8 | 33792 | 2.5763 | 1.062 | 2.7362 | 1 | 2.7362 | 1
- | Gym/Cafeteria | 1279 | 85 |  |  | 3740 | 85 | 85 | AHU | 8 | 29920 | 2.5648 | 1.062 | 2.7239 | 1 | 2.7239 | 1
- | Main Office | 311 | 20 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 2.9451 | 1 | 2.9451 | 1 | 2.9451 | 1
- | Library | 492 | 32 |  |  | 1584 | 36 | 32 | Unit Ventilator | 8 | 12672 | 2.3295 | 1 | 2.3295 | 1 | 2.3295 | 1
- | Engineer Office | 0 | 0 |  |  | 432 | 9 | 0 | N/A | 8 | 3456 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym Office | 0 | 0 |  |  | 110 | 2 | 0 | AHU | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
- | Kitchen | 9 | 0 | Yes | 20 | 384 | 8 | 8 | AHU | 8 | 3072 | 0.17578 | 1 | 0.17578 | 0 | 20.1758 | 3
- | Principals Office | 0 | 0 | Yes | 20 | 493 | 11 | 11 | AHU | 8 | 3944 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-13
School: | John F. McCloskey Elementary School
Vendor: | Chadwick | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
2 | IMC |  | 0 | Yes | 20 | 1044 | 23 | 23 | Unit Ventilator | 8 | 8352 | 0 | 1 | 0 | 0 | 20 | 3
7 | Recovery. room |  | 0 | Yes | 20 | 180 | 4 | 4 | Convector | 8 | 1440 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom | 229 | 15 |  |  | 936 | 21 | 15 | Unit Ventilator | 8 | 7488 | 1.8349 | 1 | 1.8349 | 1 | 1.8349 | 1
102 | Classroom | 192 | 12 |  |  | 936 | 21 | 12 | Unit Ventilator | 8 | 7488 | 1.5385 | 1 | 1.5385 | 1 | 1.5385 | 1
103 | Classroom | 394 | 26 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 3.1571 | 1 | 3.1571 | 1 | 3.1571 | 1
104 | Classroom | 155 | 10 | Yes | 20 | 1056 | 24 | 24 | Unit Ventilator | 8 | 8448 | 1.1009 | 1 | 1.1009 | 1 | 21.1009 | 3
105 | Classroom | 342 | 22 |  |  | 897 | 20 | 20 | Unit Ventilator | 8 | 7176 | 2.8595 | 1 | 2.8595 | 1 | 2.8595 | 1
106 | Classroom | 203 | 13 |  |  | 936 | 21 | 13 | Unit Ventilator | 8 | 7488 | 1.6266 | 1 | 1.6266 | 1 | 1.6266 | 1
107 | Classroom | 206 | 13 |  |  | 936 | 21 | 13 | Unit Ventilator | 8 | 7488 | 1.6506 | 1 | 1.6506 | 1 | 1.6506 | 1
108 | Classroom | 390 | 26 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 3.125 | 1 | 3.125 | 1 | 3.125 | 1
109 | Classroom | 282 | 18 |  |  | 736 | 16 | 16 | Unit Ventilator | 8 | 5888 | 2.8736 | 1 | 2.8736 | 1 | 2.8736 | 1
111 | Classroom | 356 | 23 |  |  | 736 | 16 | 16 | Unit Ventilator | 8 | 5888 | 3.6277 | 1 | 3.6277 | 1 | 3.6277 | 1
113 | Classroom | 320 | 21 |  |  | 736 | 16 | 16 | Unit Ventilator | 8 | 5888 | 3.2609 | 1 | 3.2609 | 1 | 3.2609 | 1
114 | Classroom | 319 | 21 |  |  | 736 | 16 | 16 | Unit Ventilator | 8 | 5888 | 3.2507 | 1 | 3.2507 | 1 | 3.2507 | 1
201 | Classroom |  | 0 |  |  | 916 | 20 | 0 | Unit Ventilator | 8 | 7328 | 0 | 1 | 0 | 0 | 0 | 0
202 | Classroom | 200 | 13 |  |  | 936 | 21 | 13 | Unit Ventilator | 8 | 7488 | 1.6026 | 1 | 1.6026 | 1 | 1.6026 | 1
203 | Classroom | 194 | 12 |  |  | 936 | 21 | 12 | Unit Ventilator | 8 | 7488 | 1.5545 | 1 | 1.5545 | 1 | 1.5545 | 1
204 | Classroom | 378 | 25 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 3.0288 | 1 | 3.0288 | 1 | 3.0288 | 1
205 | Classroom | 342 | 22 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 2.7404 | 1 | 2.7404 | 1 | 2.7404 | 1
206 | Classroom | 487 | 32 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 3.9022 | 1 | 3.9022 | 1 | 3.9022 | 1
208 | Classroom | 346 | 23 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 2.7724 | 1 | 2.7724 | 1 | 2.7724 | 1
209 | Classroom | 514 | 34 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 4.1186 | 1 | 4.1186 | 2 | 4.1186 | 2
210 | Classroom | 247 | 16 |  |  | 936 | 21 | 16 | Unit Ventilator | 8 | 7488 | 1.9792 | 1 | 1.9792 | 1 | 1.9792 | 1
211 | Classroom | 374 | 24 |  |  | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 2.9968 | 1 | 2.9968 | 1 | 2.9968 | 1
- | Auditorium |  | 0 |  |  | 2700 | 61 | 0 | AHU | 8 | 21600 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Computer Room | 40 | 2 |  |  | 1080 | 24 | 2 | Unit Ventilator | 8 | 8640 | 0.27778 | 1 | 0.27778 | 0 | 0.27778 | 0
- | Gym |  | 0 | Yes | 20 | 3744 | 85 | 85 | AHU | 8 | 29952 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 338 | 7 | 7 | Convector | 8 | 2704 | 0 | 1 | 0 | 0 | 20 | 3
- | Prin. Office |  | 0 | Yes | 20 | 312 | 7 | 7 | Convector | 8 | 2496 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse. Office |  | 0 | Yes | 20 | 225 | 5 | 5 | Convector | 8 | 1800 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-18
School: | Alexander K. McClure Elementary School
Vendor: | Devine Brothers | Retest | 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
0 | Building Engineer | 0 | 0 |  |  |  | 0 | 0 | N/A
1 | Gym | 650 | 43 |  |  | 2486 | 56 | 43 | House Fan | 8 | 19888 | 1.961 | 1 | 1.961 | 1 | 1.961 | 1
6 | Art | 302 | 20 |  |  | 894 | 20 | 20 | House Fan | 8 | 7152 | 2.5336 | 1 | 2.5336 | 1 | 2.5336 | 1
7 | Classroom | 559 | 37 |  |  | 839 | 19 | 19 | House Fan | 8 | 6712 | 4.997 | 1 | 4.997 | 2 | 4.997 | 2
11 | Classroom | 523 | 34 |  |  | 821 | 18 | 18 | House Fan | 8 | 6568 | 4.7777 | 1 | 4.7777 | 2 | 4.7777 | 2
101 | Classroom | 603 | 40 |  |  | 887 | 20 | 20 | House Fan | 8 | 7096 | 5.0986 | 1 | 5.0986 | 2 | 5.0986 | 2
106 | Classroom | 419 | 27 |  |  | 927 | 21 | 21 | House Fan | 8 | 7416 | 3.39 | 1 | 3.39 | 1 | 3.39 | 1
106A | Asst. Principal | 0 | 0 | Yes | 20 | 104 | 2 | 2 | House Fan | 8 | 832 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom | 505 | 33 |  |  | 753 | 17 | 17 | House Fan | 8 | 6024 | 5.0299 | 1 | 5.0299 | 2 | 5.0299 | 2
108 | Classroom | 329 | 21 |  |  | 849 | 19 | 19 | House Fan | 8 | 6792 | 2.9064 | 1 | 2.9064 | 1 | 2.9064 | 1
109 | Classroom | 454 | 30 |  |  | 791 | 17 | 17 | House Fan | 8 | 6328 | 4.3047 | 1 | 4.3047 | 2 | 4.3047 | 2
110 | Classroom | 603 | 40 |  |  | 725 | 16 | 16 | House Fan | 8 | 5800 | 6.2379 | 1 | 6.2379 | 2 | 6.2379 | 2
111 | Classroom | 537 | 35 |  |  | 699 | 15 | 15 | House Fan | 8 | 5592 | 5.7618 | 1 | 5.7618 | 2 | 5.7618 | 2
201 | Classroom | 585 | 39 |  |  | 847 | 19 | 19 | House Fan | 8 | 6776 | 5.18 | 1 | 5.18 | 2 | 5.18 | 2
202 | Classroom | 597 | 39 |  |  | 883 | 20 | 20 | House Fan | 8 | 7064 | 5.0708 | 1 | 5.0708 | 2 | 5.0708 | 2
203 | Classroom | 423 | 28 |  |  | 903 | 20 | 20 | House Fan | 8 | 7224 | 3.5133 | 1 | 3.5133 | 1 | 3.5133 | 1
204 | Classroom | 461 | 30 |  |  | 887 | 20 | 20 | House Fan | 8 | 7096 | 3.898 | 1 | 3.898 | 1 | 3.898 | 1
205 | Classroom | 482 | 32 |  |  | 945 | 21 | 21 | House Fan | 8 | 7560 | 3.8254 | 1 | 3.8254 | 1 | 3.8254 | 1
206 | Library | 431 | 28 |  |  | 890 | 20 | 20 | House Fan | 8 | 7120 | 3.632 | 1 | 3.632 | 1 | 3.632 | 1
206A | Nurse Office | 0 | 0 |  |  | 194 | 4 | 0 | N/A | 8 | 1552 | 0 | 1 | 0 | 0 | 0 | 0
206B | Nurse Exam | 0 | 0 | Yes | 20 | 362 | 8 | 8 | House Fan | 8 | 2896 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom | 442 | 29 |  |  | 869 | 19 | 19 | House Fan | 8 | 6952 | 3.8147 | 1 | 3.8147 | 1 | 3.8147 | 1
208 | Classroom | 309 | 20 |  |  | 812 | 18 | 18 | House Fan | 8 | 6496 | 2.8541 | 1 | 2.8541 | 1 | 2.8541 | 1
209 | Classroom | 412 | 27 |  |  | 823 | 18 | 18 | House Fan | 8 | 6584 | 3.7546 | 1 | 3.7546 | 1 | 3.7546 | 1
210 | Classroom | 602 | 40 |  |  | 714 | 16 | 16 | House Fan | 8 | 5712 | 6.3235 | 1 | 6.3235 | 2 | 6.3235 | 2
211 | Classroom | 595 | 39 |  |  | 740 | 16 | 16 | House Fan | 8 | 5920 | 6.0304 | 1 | 6.0304 | 2 | 6.0304 | 2
301 | Classroom | 559 | 37 |  |  | 882 | 20 | 20 | House Fan | 8 | 7056 | 4.7534 | 1 | 4.7534 | 2 | 4.7534 | 2
302 | Classroom | 501 | 33 |  |  | 902 | 20 | 20 | House Fan | 8 | 7216 | 4.1657 | 1 | 4.1657 | 2 | 4.1657 | 2
303 | Classroom | 377 | 25 |  |  | 900 | 20 | 20 | House Fan | 8 | 7200 | 3.1417 | 1 | 3.1417 | 1 | 3.1417 | 1
304 | Classroom | 483 | 32 |  |  | 875 | 19 | 19 | House Fan | 8 | 7000 | 4.14 | 1 | 4.14 | 2 | 4.14 | 2
305 | Classroom | 469 | 31 |  |  | 910 | 20 | 20 | House Fan | 8 | 7280 | 3.8654 | 1 | 3.8654 | 1 | 3.8654 | 1
306 | Classroom | 402 | 26 |  |  | 894 | 20 | 20 | House Fan | 8 | 7152 | 3.3725 | 1 | 3.3725 | 1 | 3.3725 | 1
306A | Office | 0 | 0 | Yes | 20 | 185 | 4 | 4 | House Fan | 8 | 1480 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom | 470 | 31 |  |  | 932 | 21 | 21 | House Fan | 8 | 7456 | 3.7822 | 1 | 3.7822 | 1 | 3.7822 | 1
308 | Classroom | 301 | 20 |  |  | 815 | 18 | 18 | House Fan | 8 | 6520 | 2.7699 | 1 | 2.7699 | 1 | 2.7699 | 1
309 | Classroom | 313 | 20 |  |  | 851 | 19 | 19 | House Fan | 8 | 6808 | 2.7585 | 1 | 2.7585 | 1 | 2.7585 | 1
310 | Classroom | 396 | 26 |  |  | 726 | 16 | 16 | House Fan | 8 | 5808 | 4.0909 | 1 | 4.0909 | 2 | 4.0909 | 2
311 | Classroom | 406 | 27 |  |  | 732 | 16 | 16 | House Fan | 8 | 5856 | 4.1598 | 1 | 4.1598 | 2 | 4.1598 | 2
312 | Classroom | 0 | 0 | Yes | 20 | 435 | 9 | 9 | N/A | 8 | 3480 | 0 | 1 | 0 | 0 | 20 | 3
- | 4th Floor Office N | 0 | 0 |  |  |  | 0 | 0 | N/A
- | 4th Floor Office S | 0 | 0 |  |  |  | 0 | 0 | N/A
- | Cafeteria | 1876 | 125 |  |  | 2974 | 67 | 67 | House Fan | 8 | 23792 | 4.731 | 1.062 | 5.0245 | 2 | 5.0245 | 2
- | Main Office | 0 | 0 | Yes | 20 | 262 | 5 | 5 | N/A | 8 | 2096 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office | 0 | 0 | Yes | 20 | 194 | 4 | 4 | N/A | 8 | 1552 | 0 | 1 | 0 | 0 | 20 | 3
- | Portable Classroom | 289 | 19 |  |  | 1290 | 29 | 19 | Unit Ventilators | 8 | 10320 | 1.6802 | 1 | 1.6802 | 1 | 1.6802 | 1
Sheet Last Modified: | 2021-04-29
School: | Delaplaine McDaniel Elementary-Middle School
McDaniel Annex (St. Edmunds)
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
McDaniel Main
102 | Classroom | 865 | 57 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 9.8295 | 1 | 9.8295 | 2 | 9.8295 | 2
103 | Classroom | 250 | 16 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 2.8409 | 1 | 2.8409 | 1 | 2.8409 | 1
104 | Classroom | 340 | 22 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 3.0502 | 1 | 3.0502 | 1 | 3.0502 | 1
105 | Classroom | 275 | 18 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 3.125 | 1 | 3.125 | 1 | 3.125 | 1
107 | Classroom | 1025 | 68 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 11.6477 | 1 | 11.6477 | 3 | 11.6477 | 3
108 | Classroom |  | 0 | Yes | 20 | 464 | 10 | 10 |  | 8 | 3712 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 550 | 36 |  |  | 1260 | 28 | 28 | Unit Ventilator | 8 | 10080 | 3.2738 | 1 | 3.2738 | 1 | 3.2738 | 1
200 | Classroom | 430 | 28 |  |  | 1260 | 28 | 28 | Unit Ventilator | 8 | 10080 | 2.5595 | 1 | 2.5595 | 1 | 2.5595 | 1
201 | Classroom | 0 | 0 |  |  | 396 | 9 | 0 | Unit Ventilator | 8 | 3168 | 0 | 1 | 0 | 0 | 0 | 0
203 | Classroom | 635 | 42 |  |  | 630 | 14 | 14 | Unit Ventilator | 8 | 5040 | 7.5595 | 1 | 7.5595 | 2 | 7.5595 | 2
204 | Computer Lab | 949 | 63 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 7.7029 | 1 | 7.7029 | 2 | 7.7029 | 2
205 | Classroom | 635 | 42 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 7.2159 | 1 | 7.2159 | 2 | 7.2159 | 2
206 | Classroom | 475 | 31 |  |  | 858 | 19 | 19 | Unit Ventilator | 8 | 6864 | 4.1521 | 1 | 4.1521 | 2 | 4.1521 | 2
207 | Classroom | 0 | 0 |  |  | 783 | 17 | 0 | Unit Ventilator | 8 | 6264 | 0 | 1 | 0 | 0 | 0 | 0
209 | Classroom | 0 | 0 |  |  | 777 | 17 | 0 | Unit Ventilator | 8 | 6216 | 0 | 1 | 0 | 0 | 0 | 0
300 | Classroom | 0 | 0 | Yes | 20 | 819 | 18 | 18 | Unit Ventilator | 8 | 6552 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 |  |  | 691 | 15 | 0 | Unit Ventilator | 8 | 5528 | 0 | 1 | 0 | 0 | 0 | 0
303 | Classroom | 428 | 28 |  |  | 945 | 21 | 21 | Unit Ventilator | 8 | 7560 | 3.3968 | 1 | 3.3968 | 1 | 3.3968 | 1
304 | Classroom | 134 | 8 |  |  | 704 | 16 | 8 | Unit Ventilator | 8 | 5632 | 1.4276 | 1 | 1.4276 | 1 | 1.4276 | 1
305 | Classroom | 374 | 24 |  |  | 638 | 14 | 14 | Unit Ventilator | 8 | 5104 | 4.3966 | 1 | 4.3966 | 2 | 4.3966 | 2
306 | Classroom | 185 | 12 |  |  | 638 | 14 | 12 | Unit Ventilator | 8 | 5104 | 2.1748 | 1 | 2.1748 | 1 | 2.1748 | 1
307 | Classroom | 570 | 38 |  |  | 638 | 14 | 14 | Unit Ventilator | 8 | 5104 | 6.7006 | 1 | 6.7006 | 2 | 6.7006 | 2
308 | Classroom | 470 | 31 |  |  | 638 | 14 | 14 | Unit Ventilator | 8 | 5104 | 5.5251 | 1 | 5.5251 | 2 | 5.5251 | 2
309 | Classroom | 400 | 26 |  |  | 638 | 14 | 14 | Unit Ventilator | 8 | 5104 | 4.7022 | 1 | 4.7022 | 2 | 4.7022 | 2
310 | Classroom | 494 | 32 |  |  | 880 | 20 | 20 | Unit Ventilator | 8 | 7040 | 4.2102 | 1 | 4.2102 | 2 | 4.2102 | 2
311 | Classroom | 430 | 28 |  |  | 638 | 14 | 14 | Unit Ventilator | 8 | 5104 | 5.0549 | 1 | 5.0549 | 2 | 5.0549 | 2
313 | Classroom | 1099 | 73 |  |  | 814 | 18 | 18 | Unit Ventilator | 8 | 6512 | 10.1259 | 1 | 10.1259 | 3 | 10.1259 | 3
- | Gym | 0 | 0 | Yes | 20 | 3300 | 75 | 75 | AHU | 8 | 26400 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Gym Office |  | 0 | Yes | 20 | 77 | 1 | 1 |  | 8 | 616 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 280 | 6 | 6 |  | 8 | 2240 | 0 | 1 | 0 | 0 | 20 | 3
- | Media Center | 700 | 46 |  |  | 1078 | 24 | 24 | Unit Ventilator | 8 | 8624 | 4.8701 | 1 | 4.8701 | 2 | 4.8701 | 2
- | Kitchen |  | 0 | Yes | 20 | 294 | 6 | 6 |  | 8 | 2352 | 0 | 1 | 0 | 0 | 20 | 3
- | School Police |  | 0 | Yes | 20 | 90 | 2 | 2 |  | 8 | 720 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office |  | 0 | Yes | 20 | 117 | 2 | 2 |  | 8 | 936 | 0 | 1 | 0 | 0 | 20 | 3
- | Principals Office |  | 0 | Yes | 20 | 196 | 4 | 4 |  | 8 | 1568 | 0 | 1 | 0 | 0 | 20 | 3
- | Vice Principal |  | 0 | Yes | 20 | 187 | 4 | 4 |  | 8 | 1496 | 0 | 1 | 0 | 0 | 20 | 3
- | Office | 0 | 0 | Yes | 20 | 392 | 8 | 8 | AHU | 8 | 3136 | 0 | 1 | 0 | 0 | 20 | 3
McDaniel Annex (St. Edmunds)
K-1 | Classroom | 269 | 17 |  |  | 516 | 11 | 11 | Unit Ventilator | 8 | 4128 | 3.9099 | 1 | 3.9099 | 1 | 3.9099 | 1
K-2 | Classroom | 449 | 29 |  |  | 616 | 14 | 14 | Unit Ventilator | 8 | 4928 | 5.4667 | 1 | 5.4667 | 2 | 5.4667 | 2
K-3 | Classroom | 407 | 27 |  |  | 616 | 14 | 14 | Unit Ventilator | 8 | 4928 | 4.9554 | 1 | 4.9554 | 2 | 4.9554 | 2
K-4 | Classroom | 348 | 23 |  |  | 516 | 11 | 11 | Unit Ventilator | 8 | 4128 | 5.0581 | 1 | 5.0581 | 2 | 5.0581 | 2
206 | Classroom | 350 | 23 |  |  | 616 | 14 | 14 | Unit Ventilator | 8 | 4928 | 4.2614 | 1 | 4.2614 | 2 | 4.2614 | 2
207 | Classroom | 530 | 35 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 5.0189 | 1 | 5.0189 | 2 | 5.0189 | 2
208 | Classroom | 632 | 42 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 7.1818 | 1 | 7.1818 | 2 | 7.1818 | 2
209 | Classroom | 495 | 33 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 5.625 | 1 | 5.625 | 2 | 5.625 | 2
210 | Classroom | 375 | 25 |  |  | 440 | 10 | 10 | Unit Ventilator | 8 | 3520 | 6.392 | 1 | 6.392 | 2 | 6.392 | 2
213 | Classroom | 447 | 29 |  |  | 440 | 10 | 10 | Unit Ventilator | 8 | 3520 | 7.6193 | 1 | 7.6193 | 2 | 7.6193 | 2
215 | Classroom | 640 | 42 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 6.0606 | 1 | 6.0606 | 2 | 6.0606 | 2
306 | Classroom | 525 | 35 |  |  | 616 | 14 | 14 | Unit Ventilator | 8 | 4928 | 6.392 | 1 | 6.392 | 2 | 6.392 | 2
307 | Classroom | 653 | 43 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 6.1837 | 1 | 6.1837 | 2 | 6.1837 | 2
308 | Classroom | 425 | 28 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 4.8295 | 1 | 4.8295 | 2 | 4.8295 | 2
309 | Classroom | 630 | 42 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 7.1591 | 1 | 7.1591 | 2 | 7.1591 | 2
310 | Classroom | 471 | 31 |  |  | 660 | 15 | 15 | Unit Ventilator | 8 | 5280 | 5.3523 | 1 | 5.3523 | 2 | 5.3523 | 2
312 | Classroom | 481 | 32 |  |  | 704 | 16 | 16 | Unit Ventilator | 8 | 5632 | 5.1243 | 1 | 5.1243 | 2 | 5.1243 | 2
313 | Classroom | 611 | 40 |  |  | 704 | 16 | 16 | Unit Ventilator | 8 | 5632 | 6.5092 | 1 | 6.5092 | 2 | 6.5092 | 2
- | Cafeteria / Gym | 14007 | 933 |  |  | 3960 | 90 | 90 | AHU | 8 | 31680 | 26.5284 | 1.062 | 28.1741 | 4 | 28.1741 | 4
- | Classroom | 15010 | 1000 |  |  | 1431 | 32 | 32 | AHU | 8 | 11448 | 78.6688 | 1 | 78.6688 | 5 | 78.6688 | 5
Sheet Last Modified: | 2021-04-06
School: | William McKinley Elementary School
Vendor: | Devine Brothers | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | A1/11 | 529 | 35 |  |  | 858 | 19 | 19 | Unit Ventilator | 8 | 6864 | 4.6241 | 1 | 4.6241 | 2 | 4.6241 | 2
- | A2/12 | 627 | 41 |  |  | 832 | 18 | 18 | Unit Ventilator | 8 | 6656 | 5.652 | 1 | 5.652 | 2 | 5.652 | 2
- | A3/13 | 298 | 19 |  |  | 858 | 19 | 19 | Unit Ventilator | 8 | 6864 | 2.6049 | 1 | 2.6049 | 1 | 2.6049 | 1
- | A4/14 | 512 | 34 |  |  | 858 | 19 | 19 | Unit Ventilator | 8 | 6864 | 4.4755 | 1 | 4.4755 | 2 | 4.4755 | 2
- | Autistic Support 8 | 231 | 15 |  |  | 726 | 16 | 15 | Unit Ventilator | 8 | 5808 | 2.3864 | 1 | 2.3864 | 1 | 2.3864 | 1
- | B1/21 | 711 | 47 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 6.733 | 1 | 6.733 | 2 | 6.733 | 2
- | B2/22 | 630 | 42 |  |  | 754 | 17 | 17 | Unit Ventilator | 8 | 6032 | 6.2666 | 1 | 6.2666 | 2 | 6.2666 | 2
- | B3/23 | 660 | 44 |  |  | 754 | 17 | 17 | Unit Ventilator | 8 | 6032 | 6.565 | 1 | 6.565 | 2 | 6.565 | 2
- | B4/24 | 538 | 35 |  |  | 744 | 16 | 16 | Unit Ventilator | 8 | 5952 | 5.4234 | 1 | 5.4234 | 2 | 5.4234 | 2
- | C1/31 | 604 | 40 |  |  | 726 | 16 | 16 | Unit Ventilator | 8 | 5808 | 6.2397 | 1 | 6.2397 | 2 | 6.2397 | 2
- | C2/32 | 271 | 18 |  |  | 675 | 15 | 15 | Unit Ventilator | 8 | 5400 | 3.0111 | 1 | 3.0111 | 1 | 3.0111 | 1
- | C3/33 | 605 | 40 |  |  | 700 | 15 | 15 | Unit Ventilator | 8 | 5600 | 6.4821 | 1 | 6.4821 | 2 | 6.4821 | 2
- | C4/34 | 669 | 44 |  |  | 720 | 16 | 16 | Unit Ventilator | 8 | 5760 | 6.9688 | 1 | 6.9688 | 2 | 6.9688 | 2
- | CCTC 11 | 1062 | 70 |  |  | 1215 | 27 | 27 | Unit Ventilator | 8 | 9720 | 6.5556 | 1 | 6.5556 | 2 | 6.5556 | 2
- | D1 | 426 | 28 |  |  | 858 | 19 | 19 | Unit Ventilator | 8 | 6864 | 3.7238 | 1 | 3.7238 | 1 | 3.7238 | 1
- | D2 | 553 | 36 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 5.3173 | 1 | 5.3173 | 2 | 5.3173 | 2
- | D3 | 290 | 19 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.7885 | 1 | 2.7885 | 1 | 2.7885 | 1
- | D4 | 310 | 20 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.9808 | 1 | 2.9808 | 1 | 2.9808 | 1
- | Gymnasium | 1525 | 101 |  |  | 2860 | 65 | 65 | AHU | 8 | 22880 | 3.9991 | 1.062 | 4.2472 | 2 | 4.2472 | 2
- | Kindergarten 1 | 355 | 23 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 2.8815 | 1 | 2.8815 | 1 | 2.8815 | 1
- | Kindergarten 2 | 290 | 19 | Yes | 20 | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 2.3539 | 1 | 2.3539 | 1 | 22.3539 | 3
- | Kindergarten 3 | 282 | 18 | Yes | 20 | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 2.289 | 1 | 2.289 | 1 | 22.289 | 3
- | Pre K 4 | 739 | 49 |  |  | 924 | 21 | 21 | Unit Ventilator | 8 | 7392 | 5.9984 | 1 | 5.9984 | 2 | 5.9984 | 2
- | Room 5 | 611 | 40 |  |  | 726 | 16 | 16 | Unit Ventilator | 8 | 5808 | 6.312 | 1 | 6.312 | 2 | 6.312 | 2
-- | Room 6 | 467 | 31 |  |  | 726 | 16 | 16 | Unit Ventilator | 8 | 5808 | 4.8244 | 1 | 4.8244 | 2 | 4.8244 | 2
- | Room 9 / Visual Arts | 748 | 49 |  |  | 726 | 16 | 16 | AHU | 8 | 5808 | 7.7273 | 1 | 7.7273 | 2 | 7.7273 | 2
- | Room 12 | 587 | 39 |  |  | 809 | 18 | 18 | AHU | 8 | 6472 | 5.4419 | 1 | 5.4419 | 2 | 5.4419 | 2
A-0 | Small Classroom | 37 | 2 |  |  | 150 | 3 | 2 | AHU | 8 | 1200 | 1.85 | 1 | 1.85 | 1 | 1.85 | 1
7 | Teachers Lounge | 59 | 3 | Yes | 20 | 351 | 7 | 7 | AHU | 8 | 2808 | 1.2607 | 1 | 1.2607 | 1 | 21.2607 | 3
- | Nurse Exam Large | 69 | 4 | Yes | 20 | 252 | 5 | 5 | AHU | 8 | 2016 | 2.0536 | 1 | 2.0536 | 1 | 22.0536 | 3
- | Nurse Office | 38 | 2 |  |  | 119 | 2 | 2 | AHU | 8 | 952 | 2.395 | 1 | 2.395 | 1 | 2.395 | 1
- | Nurse Exam | 59 | 3 |  |  | 153 | 3 | 3 | AHU | 8 | 1224 | 2.8922 | 1 | 2.8922 | 1 | 2.8922 | 1
- | Storage Large | 61 | 4 |  |  | 216 | 4 | 4 | AHU | 8 | 1728 | 2.1181 | 1 | 2.1181 | 1 | 2.1181 | 1
- | Storage | 24 | 1 |  |  |  | 0 | 0 | AHU
- | Auditorium | 1667 | 111 |  |  | 2453 | 55 | 55 | AHU | 8 | 19624 | 5.0968 | 1 | 5.0968 | 2 | 5.0968 | 2
- | Music Room | 319 | 21 |  |  | 727 | 16 | 16 | AHU | 8 | 5816 | 3.2909 | 1 | 3.2909 | 1 | 3.2909 | 1
- | Library | 1047 | 69 |  |  | 3888 | 88 | 69 | AHU | 8 | 31104 | 2.0197 | 1.062 | 2.145 | 1 | 2.145 | 1
- | Cafeteria | 894 | 59 |  |  | 2331 | 52 | 52 | AHU | 8 | 18648 | 2.8764 | 1 | 2.8764 | 1 | 2.8764 | 1
D-0 | Small Classroom | 36 | 2 |  |  | 150 | 3 | 2 | AHU | 8 | 1200 | 1.8 | 1 | 1.8 | 1 | 1.8 | 1
C-0 | Small Classroom | 21 | 1 |  |  | 150 | 3 | 1 | AHU | 8 | 1200 | 1.05 | 1 | 1.05 | 1 | 1.05 | 1
B-0 | Small Classroom | 53 | 3 |  |  | 150 | 3 | 3 | AHU | 8 | 1200 | 2.65 | 1 | 2.65 | 1 | 2.65 | 1
10 | Small Classroom | 26 | 1 | Yes | 20 | 364 | 8 | 8 | AHU | 8 | 2912 | 0.53571 | 1 | 0.53571 | 0 | 20.5357 | 3
- | Main Office | 50 | 3 | Yes | 20 | 817 | 18 | 18 | AHU | 8 | 6536 | 0.459 | 1 | 0.459 | 0 | 20.459 | 3
- | Admin Office 1 | 52 | 3 |  |  | 128 | 2 | 2 | AHU | 8 | 1024 | 3.0469 | 1 | 3.0469 | 1 | 3.0469 | 1
- | Admin Office 2 | 73 | 4 |  |  | 128 | 2 | 2 | AHU | 8 | 1024 | 4.2773 | 1 | 4.2773 | 2 | 4.2773 | 2
- | Admin Office 3 | 43 | 2 |  |  | 128 | 2 | 2 | AHU | 8 | 1024 | 2.5195 | 1 | 2.5195 | 1 | 2.5195 | 1
- | Admin Office 5 | 50 | 3 |  |  | 160 | 3 | 3 | AHU | 8 | 1280 | 2.3438 | 1 | 2.3438 | 1 | 2.3438 | 1
- | Admin Office 6 | 49 | 3 |  |  | 285 | 6 | 3 | AHU | 8 | 2280 | 1.2895 | 1 | 1.2895 | 1 | 1.2895 | 1
- | Admin Office 7 | 22 | 1 | Yes | 20 | 120 | 2 | 2 | AHU | 8 | 960 | 1.375 | 1 | 1.375 | 1 | 21.375 | 3
- | Equip Storage | 0 | 0 |  |  | 120 | 2 | 0 | AHU | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
- | Corridor | 35 | 2 |  |  | 440 | 10 | 2 | AHU | 8 | 3520 | 0.59659 | 1 | 0.59659 | 0 | 0.59659 | 0
- | Principals Office | 35 | 2 | Yes | 20 | 180 | 4 | 4 | AHU | 8 | 1440 | 1.4583 | 1 | 1.4583 | 1 | 21.4583 | 3
Sheet Last Modified: | 2021-04-29
School: | Morton McMichael Elementary School
Vendor: | Chadwick | Part 2 | Part 3
Part 4
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Staff Lounge | 125 | 8 |  |  | 468 | 10 | 8 | Unit Ventilator | 8 | 3744 | 2.0032 | 1 | 2.0032 | 1 | 2.0032 | 1
101 | Admin | 281 | 18 |  |  | 1056 | 24 | 18 | Unit Ventilator | 8 | 8448 | 1.9957 | 1 | 1.9957 | 1 | 1.9957 | 1
102 | Superintendants | 284 | 18 |  |  | 600 | 13 | 13 | Unit Ventilator | 8 | 4800 | 3.55 | 1 | 3.55 | 1 | 3.55 | 1
- | IT Office |  | 0 |  |  | 459 | 10 | 0 |  | 8 | 3672 | 0 | 1 | 0 | 0 | 0 | 0
104 | Small Conf/Assis. Super | 110 | 7 |  |  | 252 | 5 | 5 | Unit Ventilator | 8 | 2016 | 3.2738 | 1 | 3.2738 | 1 | 3.2738 | 1
105 | Large Conference | 319 | 21 |  |  | 1188 | 27 | 21 | Unit Ventilator | 8 | 9504 | 2.0139 | 1 | 2.0139 | 1 | 2.0139 | 1
108 | Classroom | 375 | 25 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 3.2552 | 1 | 3.2552 | 1 | 3.2552 | 1
110 | Classroom | 279 | 18 |  |  | 840 | 19 | 18 | Unit Ventilator | 8 | 6720 | 2.4911 | 1 | 2.4911 | 1 | 2.4911 | 1
114 | Classroom | 284 | 18 |  |  | 576 | 13 | 13 | Unit Ventilator | 8 | 4608 | 3.6979 | 1 | 3.6979 | 1 | 3.6979 | 1
200 | Classroom | 340 | 22 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 3.0357 | 1 | 3.0357 | 1 | 3.0357 | 1
201 | Classroom | 328 | 21 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.9286 | 1 | 2.9286 | 1 | 2.9286 | 1
201A | Classroom | 320 | 21 |  |  | 336 | 7 | 7 | Unit Ventilator | 8 | 2688 | 7.1429 | 1 | 7.1429 | 2 | 7.1429 | 2
202 | Classroom | 292 | 19 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.6071 | 1 | 2.6071 | 1 | 2.6071 | 1
204 | Classroom | 272 | 18 |  |  | 2592 | 58 | 18 | Unit Ventilator | 8 | 20736 | 0.78704 | 1.062 | 0.83586 | 0 | 0.83586 | 0
205 | Classroom | 326 | 21 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.9107 | 1 | 2.9107 | 1 | 2.9107 | 1
206 | Classroom | 275 | 18 |  |  | 2592 | 58 | 18 | Unit Ventilator | 8 | 20736 | 0.79572 | 1.062 | 0.84508 | 0 | 0.84508 | 0
207 | Classroom | 318 | 21 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.8393 | 1 | 2.8393 | 1 | 2.8393 | 1
208 | Classroom | 249 | 16 |  |  | 2592 | 58 | 16 | Unit Ventilator | 8 | 20736 | 0.72049 | 1.062 | 0.76518 | 0 | 0.76518 | 0
210 | Classroom | 351 | 23 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 3.1339 | 1 | 3.1339 | 1 | 3.1339 | 1
212 | Classroom | 363 | 24 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 3.2411 | 1 | 3.2411 | 1 | 3.2411 | 1
214 | Classroom | 282 | 18 |  |  | 840 | 19 | 18 | Unit Ventilator | 8 | 6720 | 2.5179 | 1 | 2.5179 | 1 | 2.5179 | 1
216 | Classroom | 262 | 17 |  |  | 864 | 19 | 17 | Unit Ventilator | 8 | 6912 | 2.2743 | 1 | 2.2743 | 1 | 2.2743 | 1
217 | Classroom | 368 | 24 |  |  | 1944 | 44 | 24 | Unit Ventilator | 8 | 15552 | 1.4198 | 1 | 1.4198 | 1 | 1.4198 | 1
218 | Classroom | 320 | 21 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.8571 | 1 | 2.8571 | 1 | 2.8571 | 1
219 | Classroom | 351 | 23 |  |  | 1944 | 44 | 23 | Unit Ventilator | 8 | 15552 | 1.3542 | 1 | 1.3542 | 1 | 1.3542 | 1
220 | Classroom | 403 | 26 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 3.5982 | 1 | 3.5982 | 1 | 3.5982 | 1
222 | Classroom | 280 | 18 |  |  | 504 | 11 | 11 | Unit Ventilator | 8 | 4032 | 4.1667 | 1 | 4.1667 | 2 | 4.1667 | 2
224 | Classroom |  | 0 |  |  | 840 | 19 | 0 | Unit Ventilator | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
226 | Classroom | 240 | 16 |  |  | 840 | 19 | 16 | Unit Ventilator | 8 | 6720 | 2.1429 | 1 | 2.1429 | 1 | 2.1429 | 1
300 | Classroom | 239 | 15 |  |  | 840 | 19 | 15 | Unit Ventilator | 8 | 6720 | 2.1339 | 1 | 2.1339 | 1 | 2.1339 | 1
301 | Classroom | 291 | 19 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.5982 | 1 | 2.5982 | 1 | 2.5982 | 1
302 | Classroom | 302 | 20 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.6964 | 1 | 2.6964 | 1 | 2.6964 | 1
303 | Classroom | 288 | 19 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.5714 | 1 | 2.5714 | 1 | 2.5714 | 1
305 | Classroom | 317 | 21 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.8304 | 1 | 2.8304 | 1 | 2.8304 | 1
306 | Classroom | 546 | 36 |  |  | 1248 | 28 | 28 | Unit Ventilator | 8 | 9984 | 3.2812 | 1 | 3.2812 | 1 | 3.2812 | 1
307 | Classroom | 274 | 18 |  |  | 840 | 19 | 18 | Unit Ventilator | 8 | 6720 | 2.4464 | 1 | 2.4464 | 1 | 2.4464 | 1
308 | Classroom | 273 | 18 |  |  | 864 | 19 | 18 | Unit Ventilator | 8 | 6912 | 2.3698 | 1 | 2.3698 | 1 | 2.3698 | 1
310 | Classroom | 272 | 18 |  |  | 840 | 19 | 18 | Unit Ventilator | 8 | 6720 | 2.4286 | 1 | 2.4286 | 1 | 2.4286 | 1
312 | Classroom | 281 | 18 |  |  | 840 | 19 | 18 | Unit Ventilator | 8 | 6720 | 2.5089 | 1 | 2.5089 | 1 | 2.5089 | 1
314 | Classroom | 306 | 20 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.7321 | 1 | 2.7321 | 1 | 2.7321 | 1
316 | Classroom | 315 | 21 |  |  | 864 | 19 | 19 | Unit Ventilator | 8 | 6912 | 2.7344 | 1 | 2.7344 | 1 | 2.7344 | 1
317 | Classroom | 392 | 26 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 3.5 | 1 | 3.5 | 1 | 3.5 | 1
318 | Classroom | 274 | 18 |  |  | 840 | 19 | 18 | Unit Ventilator | 8 | 6720 | 2.4464 | 1 | 2.4464 | 1 | 2.4464 | 1
319 | Classroom | 276 | 18 |  |  | 840 | 19 | 18 | Unit Ventilator | 8 | 6720 | 2.4643 | 1 | 2.4643 | 1 | 2.4643 | 1
320 | Classroom | 281 | 18 |  |  | 840 | 19 | 18 | Unit Ventilator | 8 | 6720 | 2.5089 | 1 | 2.5089 | 1 | 2.5089 | 1
322 | Classroom | 270 | 18 |  |  | 576 | 13 | 13 | Unit Ventilator | 8 | 4608 | 3.5156 | 1 | 3.5156 | 1 | 3.5156 | 1
323 | Classroom | 279 | 18 |  |  | 864 | 19 | 18 | Unit Ventilator | 8 | 6912 | 2.4219 | 1 | 2.4219 | 1 | 2.4219 | 1
324 | Classroom | 326 | 21 |  |  | 840 | 19 | 19 | Unit Ventilator | 8 | 6720 | 2.9107 | 1 | 2.9107 | 1 | 2.9107 | 1
325 | Classroom | 285 | 19 |  |  | 888 | 20 | 19 | Unit Ventilator | 8 | 7104 | 2.4071 | 1 | 2.4071 | 1 | 2.4071 | 1
326 | Classroom | 262 | 17 |  |  | 864 | 19 | 17 | Unit Ventilator | 8 | 6912 | 2.2743 | 1 | 2.2743 | 1 | 2.2743 | 1
- | Auditorium | 520 | 34 |  |  | 4914 | 111 | 34 | AHU | 8 | 39312 | 0.79365 | 1.062 | 0.84288 | 0 | 0.84288 | 0
- | Cafe | 590 | 39 |  |  | 2485 | 56 | 39 | AHU | 8 | 19880 | 1.7807 | 1 | 1.7807 | 1 | 1.7807 | 1
- | Gym | 690 | 46 |  |  | 3621 | 82 | 46 | AHU | 8 | 28968 | 1.4292 | 1.062 | 1.5178 | 1 | 1.5178 | 1
- | Main Office |  | 0 | Yes | 20 | 1401 | 31 | 31 |  | 8 | 11208 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 616 | 14 | 14 |  | 8 | 4928 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-06
School: | General George G. Meade Elementary-Middle School
Vendor: | EMCOR | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
15 | Classroom | 378 | 25 | Yes | 20 | 644 | 14 | 14 | Unit Ventilator | 8 | 5152 | 4.4022 | 1 | 4.4022 | 2 | 24.4022 | 4
16 | Classroom | 336 | 22 |  |  | 833 | 18 | 18 | Unit Ventilator | 8 | 6664 | 3.0252 | 1 | 3.0252 | 1 | 3.0252 | 1
17 | Classroom | 184 | 12 |  |  | 330 | 7 | 7 | Unit Ventilator | 8 | 2640 | 4.1818 | 1 | 4.1818 | 2 | 4.1818 | 2
18 | Classroom | 686 | 45 | Yes | 20 | 1101 | 25 | 25 | Unit Ventilator | 8 | 8808 | 4.673 | 1 | 4.673 | 2 | 24.673 | 4
101 | Classroom | 294 | 19 |  |  | 892 | 20 | 19 | Unit Ventilator | 8 | 7136 | 2.472 | 1 | 2.472 | 1 | 2.472 | 1
102 | Classroom | 299 | 19 | Yes | 20 | 765 | 17 | 17 | Unit Ventilator | 8 | 6120 | 2.9314 | 1 | 2.9314 | 1 | 22.9314 | 3
103 | Classroom | 360 | 24 | Yes | 20 | 823 | 18 | 18 | Unit Ventilator | 8 | 6584 | 3.2807 | 1 | 3.2807 | 1 | 23.2807 | 3
104 | Classroom | 281 | 18 |  |  | 705 | 16 | 16 | Unit Ventilator | 8 | 5640 | 2.9894 | 1 | 2.9894 | 1 | 2.9894 | 1
105 | Classroom | 445 | 29 |  |  | 674 | 15 | 15 | Unit Ventilator | 8 | 5392 | 4.9518 | 1 | 4.9518 | 2 | 4.9518 | 2
106 | Classroom | 405 | 27 |  |  | 846 | 19 | 19 | Unit Ventilator | 8 | 6768 | 3.5904 | 1 | 3.5904 | 1 | 3.5904 | 1
107 | Classroom | 332 | 22 |  |  | 526 | 11 | 11 | Unit Ventilator | 8 | 4208 | 4.7338 | 1 | 4.7338 | 2 | 4.7338 | 2
108 | Classroom | 294 | 19 |  |  | 670 | 15 | 15 | Unit Ventilator | 8 | 5360 | 3.291 | 1 | 3.291 | 1 | 3.291 | 1
109 | Classroom | 279 | 18 |  |  | 705 | 16 | 16 | Unit Ventilator | 8 | 5640 | 2.9681 | 1 | 2.9681 | 1 | 2.9681 | 1
115 | Classroom | 640 | 42 | Yes | 20 | 865 | 19 | 19 | Unit Ventilator | 8 | 6920 | 5.5491 | 1 | 5.5491 | 2 | 25.5491 | 4
116 | Classroom | 325 | 21 | Yes | 20 | 413 | 9 | 9 | Unit Ventilator | 8 | 3304 | 5.9019 | 1 | 5.9019 | 2 | 25.9019 | 4
117 | Classroom | 433 | 28 | Yes | 20 | 837 | 19 | 19 | Unit Ventilator | 8 | 6696 | 3.8799 | 1 | 3.8799 | 1 | 23.8799 | 3
118 | Classroom | 664 | 44 | Yes | 20 | 849 | 19 | 19 | Unit Ventilator | 8 | 6792 | 5.8657 | 1 | 5.8657 | 2 | 25.8657 | 4
200 | Classroom | 193 | 12 |  |  | 349 | 7 | 7 | Unit Ventilator | 8 | 2792 | 4.1476 | 1 | 4.1476 | 2 | 4.1476 | 2
201 | Classroom | 414 | 27 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 4.6552 | 1 | 4.6552 | 2 | 4.6552 | 2
202 | Classroom | 53 | 3 |  |  | 673 | 15 | 3 | Unit Ventilator | 8 | 5384 | 0.59064 | 1 | 0.59064 | 0 | 0.59064 | 0
203 | Classroom | 275 | 18 |  |  | 666 | 15 | 15 | Unit Ventilator | 8 | 5328 | 3.0968 | 1 | 3.0968 | 1 | 3.0968 | 1
204 | Classroom | 360 | 24 |  |  | 669 | 15 | 15 | Unit Ventilator | 8 | 5352 | 4.0359 | 1 | 4.0359 | 2 | 4.0359 | 2
205 | Classroom | 343 | 22 |  |  | 701 | 15 | 15 | Unit Ventilator | 8 | 5608 | 3.6698 | 1 | 3.6698 | 1 | 3.6698 | 1
206 | Classroom | 280 | 18 |  |  | 705 | 16 | 16 | Unit Ventilator | 8 | 5640 | 2.9787 | 1 | 2.9787 | 1 | 2.9787 | 1
207 | Classroom | 303 | 20 |  |  | 671 | 15 | 15 | Unit Ventilator | 8 | 5368 | 3.3867 | 1 | 3.3867 | 1 | 3.3867 | 1
208 | Classroom | 259 | 17 |  |  | 576 | 13 | 13 | Unit Ventilator | 8 | 4608 | 3.3724 | 1 | 3.3724 | 1 | 3.3724 | 1
209 | Classroom | 0 | 0 |  |  | 540 | 12 | 0 | Unit Ventilator | 8 | 4320 | 0 | 1 | 0 | 0 | 0 | 0
210 | Classroom | 311 | 20 |  |  | 511 | 11 | 11 | Unit Ventilator | 8 | 4088 | 4.5646 | 1 | 4.5646 | 2 | 4.5646 | 2
211 | Classroom | 222 | 14 |  |  | 720 | 16 | 14 | Unit Ventilator | 8 | 5760 | 2.3125 | 1 | 2.3125 | 1 | 2.3125 | 1
215 | Classroom | 550 | 36 |  |  | 843 | 19 | 19 | Unit Ventilator | 8 | 6744 | 4.8932 | 1 | 4.8932 | 2 | 4.8932 | 2
216 | Classroom | 306 | 20 |  |  | 855 | 19 | 19 | Unit Ventilator | 8 | 6840 | 2.6842 | 1 | 2.6842 | 1 | 2.6842 | 1
217 | Classroom | 169 | 11 |  |  | 842 | 19 | 11 | Unit Ventilator | 8 | 6736 | 1.5053 | 1 | 1.5053 | 1 | 1.5053 | 1
218 | Classroom | 631 | 42 |  |  | 852 | 19 | 19 | Unit Ventilator | 8 | 6816 | 5.5546 | 1 | 5.5546 | 2 | 5.5546 | 2
285 | Classroom | 273 | 18 |  |  | 0 | 0 | 0 | Unit Ventilator | 8 | 0 | #DIV/0! | 1 | #DIV/0! | #DIV/0! | #DIV/0!
301 | Classroom | 883 | 58 |  |  | 2031 | 46 | 46 | Unit Ventilator | 8 | 16248 | 3.2607 | 1 | 3.2607 | 1 | 3.2607 | 1
304 | Classroom | 276 | 18 |  |  | 670 | 15 | 15 | Unit Ventilator | 8 | 5360 | 3.0896 | 1 | 3.0896 | 1 | 3.0896 | 1
305 | Classroom | 346 | 23 |  |  | 702 | 15 | 15 | Unit Ventilator | 8 | 5616 | 3.6966 | 1 | 3.6966 | 1 | 3.6966 | 1
306 | Classroom | 319 | 21 |  |  | 706 | 16 | 16 | Unit Ventilator | 8 | 5648 | 3.3888 | 1 | 3.3888 | 1 | 3.3888 | 1
307 | Classroom | 347 | 23 |  |  | 670 | 15 | 15 | Unit Ventilator | 8 | 5360 | 3.8843 | 1 | 3.8843 | 1 | 3.8843 | 1
308 | Classroom | 112 | 7 |  |  | 852 | 19 | 7 | Unit Ventilator | 8 | 6816 | 0.98592 | 1 | 0.98592 | 0 | 0.98592 | 0
309 | Classroom | 333 | 22 |  |  | 309 | 7 | 7 | Unit Ventilator | 8 | 2472 | 8.0825 | 1 | 8.0825 | 2 | 8.0825 | 2
310 | Classroom | 247 | 16 |  |  | 510 | 11 | 11 | Unit Ventilator | 8 | 4080 | 3.6324 | 1 | 3.6324 | 1 | 3.6324 | 1
311 | Classroom | 351 | 23 |  |  | 706 | 16 | 16 | Unit Ventilator | 8 | 5648 | 3.7288 | 1 | 3.7288 | 1 | 3.7288 | 1
312 | Classroom | 305 | 20 |  |  | 514 | 11 | 11 | Unit Ventilator | 8 | 4112 | 4.4504 | 1 | 4.4504 | 2 | 4.4504 | 2
315 | Classroom | 289 | 19 |  |  | 838 | 19 | 19 | Unit Ventilator | 8 | 6704 | 2.5865 | 1 | 2.5865 | 1 | 2.5865 | 1
316 | Classroom | 285 | 19 |  |  | 855 | 19 | 19 | Unit Ventilator | 8 | 6840 | 2.5 | 1 | 2.5 | 1 | 2.5 | 1
317 | Classroom | 548 | 36 |  |  | 847 | 19 | 19 | Unit Ventilator | 8 | 6776 | 4.8524 | 1 | 4.8524 | 2 | 4.8524 | 2
318 | Classroom | 647 | 43 |  |  | 852 | 19 | 19 | Unit Ventilator | 8 | 6816 | 5.6954 | 1 | 5.6954 | 2 | 5.6954 | 2
- | Main Office |  | 0 | Yes | 20 | 305.08 | 6 | 6 |  | 8 | 2440.64 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 242.55 | 5 | 5 |  | 8 | 1940.4 | 0 | 1 | 0 | 0 | 20 | 3
- | 1st Floor Hall | 310 | 20 |  |  | 2688 | 61 | 20 | Unit Ventilator | 8 | 21504 | 0.86496 | 1.062 | 0.91861 | 0 | 0.91861 | 0
- | 1st Floor Nurse RR | 0 | 0 |  |  | 244 | 5 | 0 | N/A | 8 | 1952 | 0 | 1 | 0 | 0 | 0 | 0
- | 1st Floor Staff Womens RR | 0 | 0 |  |  | 393 | 8 | 0 | N/A | 8 | 3144 | 0 | 1 | 0 | 0 | 0 | 0
- | 2nd Floor Hall | 0 | 0 |  |  | 2066 | 46 | 0 | Unit Ventilator | 8 | 16528 | 0 | 1 | 0 | 0 | 0 | 0
- | 2nd Floor Mens RR | 99 | 6 |  |  | 355 | 8 | 6 | N/A | 8 | 2840 | 2.0915 | 1 | 2.0915 | 1 | 2.0915 | 1
- | 2nd Floor Womens RR | 236 | 15 |  |  | 328 | 7 | 7 | N/A | 8 | 2624 | 5.3963 | 1 | 5.3963 | 2 | 5.3963 | 2
- | 3rd Floor Hall | 289 | 19 |  |  | 2661 | 60 | 19 | Unit Ventilator | 8 | 21288 | 0.81454 | 1.062 | 0.86507 | 0 | 0.86507 | 0
- | 3rd Floor Mens RR | 95 | 6 |  |  | 259 | 5 | 5 | N/A | 8 | 2072 | 2.751 | 1 | 2.751 | 1 | 2.751 | 1
- | 3rd Floor Womens RR | 219 | 14 |  |  | 328 | 7 | 7 | N/A | 8 | 2624 | 5.0076 | 1 | 5.0076 | 2 | 5.0076 | 2
- | Cafeteria | 754 | 50 |  |  | 5223 | 118 | 50 | Unit Ventilator | 8 | 41784 | 1.0827 | 1.062 | 1.1499 | 1 | 1.1499 | 1
- | Bsmt: Boys RR | 0 | 0 |  |  | 765 | 17 | 0 | N/A | 8 | 6120 | 0 | 1 | 0 | 0 | 0 | 0
- | Bsmt: Grils RR | 0 | 0 |  |  | 697 | 15 | 0 | N/A | 8 | 5576 | 0 | 1 | 0 | 0 | 0 | 0
- | Staff Restroom: 1st Floor | 0 | 0 |  |  | 168 | 3 | 0 | N/A | 8 | 1344 | 0 | 1 | 0 | 0 | 0 | 0
- | Library | 0 | 0 |  |  | 2062.2 | 46 | 0 | Unit Ventilator | 8 | 16497.6 | 0 | 1 | 0 | 0 | 0 | 0
- | Staff Restroom: 2nd Floor | 0 | 0 |  |  | 305 | 6 | 0 | N/A | 8 | 2440 | 0 | 1 | 0 | 0 | 0 | 0
- | Staff Restroom: 3rd Floor | 0 | 0 |  |  | 308 | 7 | 0 | N/A | 8 | 2464 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-08
School: | Austin Meehan Middle School
Vendor: | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
3 | Classroom | 280 | 18 |  |  | 1537 | 34 | 18 | Unit Ventilator | 8 | 12296 | 1.3663 | 1 | 1.3663 | 1 | 1.3663 | 1
111 | Classroom | 323 | 21 |  |  | 917 | 20 | 20 | Unit Ventilator | 8 | 7336 | 2.6418 | 1 | 2.6418 | 1 | 2.6418 | 1
112 | Classroom | 309 | 20 |  |  | 1490 | 33 | 20 | Unit Ventilator | 8 | 11920 | 1.5554 | 1 | 1.5554 | 1 | 1.5554 | 1
113 | Classroom | 287 | 19 |  |  | 208 | 4 | 4 | Unit Ventilator | 8 | 1664 | 10.3486 | 1 | 10.3486 | 3 | 10.3486 | 3
114 | Classroom | 307 | 20 |  |  | 1193 | 27 | 20 | Unit Ventilator | 8 | 9544 | 1.93 | 1 | 1.93 | 1 | 1.93 | 1
115 | Classroom | 274 | 18 |  |  | 1192 | 27 | 18 | Unit Ventilator | 8 | 9536 | 1.724 | 1 | 1.724 | 1 | 1.724 | 1
121 | Classroom | 0 | 0 |  |  | 944 | 21 | 0 | Unit Ventilator | 8 | 7552 | 0 | 1 | 0 | 0 | 0 | 0
122 | Classroom | 503 | 33 |  |  | 1085 | 24 | 24 | Unit Ventilator | 8 | 8680 | 3.477 | 1 | 3.477 | 1 | 3.477 | 1
123 | Classroom | 350 | 23 |  |  | 1175 | 26 | 23 | Unit Ventilator | 8 | 9400 | 2.234 | 1 | 2.234 | 1 | 2.234 | 1
124 | Classroom | 283 | 18 |  |  | 1123 | 25 | 18 | Unit Ventilator | 8 | 8984 | 1.89 | 1 | 1.89 | 1 | 1.89 | 1
125 | Classroom | 413 | 27 |  |  | 1156 | 26 | 26 | Unit Ventilator | 8 | 9248 | 2.6795 | 1 | 2.6795 | 1 | 2.6795 | 1
126 | Classroom | 400 | 26 |  |  | 1064 | 24 | 24 | Unit Ventilator | 8 | 8512 | 2.8195 | 1 | 2.8195 | 1 | 2.8195 | 1
127 | Classroom | 333 | 22 |  |  | 1198 | 27 | 22 | Unit Ventilator | 8 | 9584 | 2.0847 | 1 | 2.0847 | 1 | 2.0847 | 1
128 | Classroom | 343 | 22 |  |  | 933 | 21 | 21 | Unit Ventilator | 8 | 7464 | 2.7572 | 1 | 2.7572 | 1 | 2.7572 | 1
211 | Classroom | 327 | 21 |  |  | 867 | 19 | 19 | Unit Ventilator | 8 | 6936 | 2.8287 | 1 | 2.8287 | 1 | 2.8287 | 1
212 | Classroom | 382 | 25 |  |  | 1630 | 37 | 25 | Unit Ventilator | 8 | 13040 | 1.7577 | 1 | 1.7577 | 1 | 1.7577 | 1
213 | Classroom | 281 | 18 |  |  | 269 | 6 | 6 | Unit Ventilator | 8 | 2152 | 7.8346 | 1 | 7.8346 | 2 | 7.8346 | 2
214 | Classroom | 372 | 24 |  |  | 1317 | 29 | 24 | Unit Ventilator | 8 | 10536 | 2.1185 | 1 | 2.1185 | 1 | 2.1185 | 1
215 | Classroom | 396 | 26 |  |  | 1199 | 27 | 26 | Unit Ventilator | 8 | 9592 | 2.4771 | 1 | 2.4771 | 1 | 2.4771 | 1
221 | Classroom | 0 | 0 |  |  | 1054 | 23 | 0 | Unit Ventilator | 8 | 8432 | 0 | 1 | 0 | 0 | 0 | 0
222 | Classroom | 337 | 22 |  |  | 1286 | 29 | 22 | Unit Ventilator | 8 | 10288 | 1.9654 | 1 | 1.9654 | 1 | 1.9654 | 1
223 | Classroom | 343 | 22 |  |  | 1230 | 27 | 22 | Unit Ventilator | 8 | 9840 | 2.0915 | 1 | 2.0915 | 1 | 2.0915 | 1
224 | Classroom | 0 | 0 |  |  | 1091 | 24 | 0 | Unit Ventilator | 8 | 8728 | 0 | 1 | 0 | 0 | 0 | 0
225 | Classroom | 420 | 28 |  |  | 1151 | 26 | 26 | Unit Ventilator | 8 | 9208 | 2.7368 | 1 | 2.7368 | 1 | 2.7368 | 1
226 | Classroom | 397 | 26 |  |  | 1175 | 26 | 26 | Unit Ventilator | 8 | 9400 | 2.534 | 1 | 2.534 | 1 | 2.534 | 1
227 | Classroom | 327 | 21 |  |  | 1292 | 29 | 21 | Unit Ventilator | 8 | 10336 | 1.8982 | 1 | 1.8982 | 1 | 1.8982 | 1
228 | Classroom | 0 | 0 |  |  | 931 | 21 | 0 | Unit Ventilator | 8 | 7448 | 0 | 1 | 0 | 0 | 0 | 0
311 | Classroom | 310 | 20 |  |  | 1041 | 23 | 20 | Unit Ventilator | 8 | 8328 | 2.2334 | 1 | 2.2334 | 1 | 2.2334 | 1
312 | Classroom | 309 | 20 |  |  | 1602 | 36 | 20 | Unit Ventilator | 8 | 12816 | 1.4466 | 1 | 1.4466 | 1 | 1.4466 | 1
313 | Classroom | 0 | 0 |  |  | 756 | 17 | 0 | Unit Ventilator | 8 | 6048 | 0 | 1 | 0 | 0 | 0 | 0
314 | Classroom | 0 | 0 |  |  | 1279 | 29 | 0 | Unit Ventilator | 8 | 10232 | 0 | 1 | 0 | 0 | 0 | 0
315 | Classroom | 0 | 0 |  |  | 1219 | 27 | 0 | Unit Ventilator | 8 | 9752 | 0 | 1 | 0 | 0 | 0 | 0
321 | Classroom | 0 | 0 |  |  | 1064 | 24 | 0 | Unit Ventilator | 8 | 8512 | 0 | 1 | 0 | 0 | 0 | 0
322 | Classroom | 460 | 30 |  |  | 1199 | 27 | 27 | Unit Ventilator | 8 | 9592 | 2.8774 | 1 | 2.8774 | 1 | 2.8774 | 1
323 | Classroom | 0 | 0 |  |  | 1365 | 31 | 0 | Unit Ventilator | 8 | 10920 | 0 | 1 | 0 | 0 | 0 | 0
324 | Classroom | 377 | 25 |  |  | 1039 | 23 | 23 | Unit Ventilator | 8 | 8312 | 2.7214 | 1 | 2.7214 | 1 | 2.7214 | 1
325 | Classroom | 270 | 18 |  |  | 1247 | 28 | 18 | Unit Ventilator | 8 | 9976 | 1.6239 | 1 | 1.6239 | 1 | 1.6239 | 1
326 | Classroom | 493 | 32 |  |  | 1322 | 30 | 30 | Unit Ventilator | 8 | 10576 | 2.7969 | 1 | 2.7969 | 1 | 2.7969 | 1
327 | Classroom | 417 | 27 |  |  | 1184 | 26 | 26 | Unit Ventilator | 8 | 9472 | 2.6415 | 1 | 2.6415 | 1 | 2.6415 | 1
328 | Classroom | 397 | 26 |  |  | 955 | 21 | 21 | Unit Ventilator | 8 | 7640 | 3.1178 | 1 | 3.1178 | 1 | 3.1178 | 1
411 | Classroom | 576 | 38 |  |  | 947 | 21 | 21 | Unit Ventilator | 8 | 7576 | 4.5618 | 1 | 4.5618 | 2 | 4.5618 | 2
412 | Classroom | 352 | 23 |  |  | 1474 | 33 | 23 | Unit Ventilator | 8 | 11792 | 1.791 | 1 | 1.791 | 1 | 1.791 | 1
413 | Classroom | 307 | 20 |  |  | 208 | 4 | 4 | Unit Ventilator | 8 | 1664 | 11.0697 | 1 | 11.0697 | 3 | 11.0697 | 3
414 | Classroom | 313 | 20 |  |  | 1255 | 28 | 20 | Unit Ventilator | 8 | 10040 | 1.8705 | 1 | 1.8705 | 1 | 1.8705 | 1
415 | Classroom | 347 | 23 |  |  | 1215 | 27 | 23 | Unit Ventilator | 8 | 9720 | 2.142 | 1 | 2.142 | 1 | 2.142 | 1
421 | Classroom |  | 0 | Yes | 20 | 1058 | 24 | 24 | N/A | 8 | 8464 | 0 | 1 | 0 | 0 | 20 | 3
422 | Classroom | 463 | 30 |  |  | 1199 | 27 | 27 | Unit Ventilator | 8 | 9592 | 2.8962 | 1 | 2.8962 | 1 | 2.8962 | 1
423 | Classroom | 363 | 24 |  |  | 1327 | 30 | 24 | Unit Ventilator | 8 | 10616 | 2.0516 | 1 | 2.0516 | 1 | 2.0516 | 1
424 | Classroom | 300 | 20 |  |  | 1365 | 31 | 20 | Unit Ventilator | 8 | 10920 | 1.6484 | 1 | 1.6484 | 1 | 1.6484 | 1
425 | Classroom | 383 | 25 |  |  | 1350 | 30 | 25 | Unit Ventilator | 8 | 10800 | 2.1278 | 1 | 2.1278 | 1 | 2.1278 | 1
426 | Classroom | 450 | 30 |  |  | 1201 | 27 | 27 | Unit Ventilator | 8 | 9608 | 2.8102 | 1 | 2.8102 | 1 | 2.8102 | 1
427 | Classroom | 357 | 23 |  |  | 1242 | 28 | 23 | Unit Ventilator | 8 | 9936 | 2.1558 | 1 | 2.1558 | 1 | 2.1558 | 1
428 | Classroom | 390 | 26 |  |  | 1054 | 23 | 23 | Unit Ventilator | 8 | 8432 | 2.7751 | 1 | 2.7751 | 1 | 2.7751 | 1
A-01 A | Art | 599 | 39 |  |  | 1692 | 38 | 38 | Unit Ventilator | 8 | 13536 | 2.6551 | 1 | 2.6551 | 1 | 2.6551 | 1
A-02 | Art | 288 | 19 |  |  |  | 0 | 0 | Unit Ventilator
A-03 A | Art | 648 | 43 |  |  | 1692 | 38 | 38 | Unit Ventilator | 8 | 13536 | 2.8723 | 1 | 2.8723 | 1 | 2.8723 | 1
- | Boys Locker Room | 1404 | 93 |  |  | 700 | 15 | 15 | AHU | 8 | 5600 | 15.0429 | 1 | 15.0429 | 3 | 15.0429 | 3
- | Girls Locker Room | 1531 | 102 |  |  | 700 | 15 | 15 | AHU | 8 | 5600 | 16.4036 | 1 | 16.4036 | 3 | 16.4036 | 3
Ground Level Pod #1 | Auditorium Control room | 0 | 0 |  |  | 102 | 2 | 0 | AHU | 8 | 816 | 0 | 1 | 0 | 0 | 0 | 0
Ground Level Pod #1 | Center Core | 163 | 10 |  |  | 528 | 12 | 10 | AHU | 8 | 4224 | 2.3153 | 1 | 2.3153 | 1 | 2.3153 | 1
Ground Level Pod #1 | Center Core | 297 | 19 |  |  | 1012 | 23 | 19 | AHU | 8 | 8096 | 2.2011 | 1 | 2.2011 | 1 | 2.2011 | 1
Ground Level Pod #1 | Conference | 38 | 2 |  |  | 150 | 3 | 2 | AHU | 8 | 1200 | 1.9 | 1 | 1.9 | 1 | 1.9 | 1
Ground Level Pod #1 | Counselor | 0 | 0 |  |  | 80 | 1 | 0 | AHU | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Ground Level Pod #1 | Entryway | 0 | 0 |  |  | 238 | 5 | 0 | AHU | 8 | 1904 | 0 | 1 | 0 | 0 | 0 | 0
Ground Level Pod #1 | Entryway | 32 | 2 |  |  | 238 | 5 | 2 | AHU | 8 | 1904 | 1.0084 | 1 | 1.0084 | 1 | 1.0084 | 1
Ground Level Pod #1 | Lobby | 113 | 7 |  |  | 1625 | 36 | 7 | AHU | 8 | 13000 | 0.52154 | 1 | 0.52154 | 0 | 0.52154 | 0
Ground Level Pod #1 | Lobby Entryway | 55 | 3 |  |  | 238 | 5 | 3 | AHU | 8 | 1904 | 1.7332 | 1 | 1.7332 | 1 | 1.7332 | 1
Ground Level Pod #1 | Main Office - Waiting | 143 | 9 |  |  | 1550 | 35 | 9 | AHU | 8 | 12400 | 0.69194 | 1 | 0.69194 | 0 | 0.69194 | 0
Ground Level Pod #1 | Main Office 1 | 63 | 4 |  |  | 130 | 2 | 2 | AHU | 8 | 1040 | 3.6346 | 1 | 3.6346 | 1 | 3.6346 | 1
Ground Level Pod #1 | Main Office 2 | 74 | 4 |  |  | 231 | 5 | 4 | AHU | 8 | 1848 | 2.4026 | 1 | 2.4026 | 1 | 2.4026 | 1
Ground Level Pod #1 | Main Office 3 | 41 | 2 |  |  | 110 | 2 | 2 | AHU | 8 | 880 | 2.7955 | 1 | 2.7955 | 1 | 2.7955 | 1
Ground Level Pod #1 | Main Office 4 | 135 | 9 |  |  | 156 | 3 | 3 | AHU | 8 | 1248 | 6.4904 | 1 | 6.4904 | 2 | 6.4904 | 2
Ground Level Pod #1 | Office | 28 | 1 |  |  | 143 | 3 | 1 | AHU | 8 | 1144 | 1.4685 | 1 | 1.4685 | 1 | 1.4685 | 1
Ground Level Pod #1 | Office Floor | 0 | 0 |  |  | 500 | 11 | 0 | AHU | 8 | 4000 | 0 | 1 | 0 | 0 | 0 | 0
Ground Level Pod #1 | Ticket Booth | 0 | 0 |  |  |  | 0 | 0 | AHU
Ground level Pod #2 | Cafeteria | 374 | 24 |  |  | 2900 | 65 | 24 | AHU | 8 | 23200 | 0.96724 | 1.062 | 1.0272 | 1 | 1.0272 | 1
Ground level Pod #2 | Center Core | 68 | 4 |  |  | 400 | 9 | 4 | AHU | 8 | 3200 | 1.275 | 1 | 1.275 | 1 | 1.275 | 1
Ground level Pod #2 | Entryway | 32 | 2 |  |  | 300 | 6 | 2 | AHU | 8 | 2400 | 0.8 | 1 | 0.8 | 0 | 0.8 | 0
Ground level Pod #2 | Office | 8 | 0 |  |  |  | 0 | 0 | AHU
Ground level Pod #2 | Pod Center Core | 116 | 7 |  |  | 925 | 21 | 7 | AHU | 8 | 7400 | 0.94054 | 1 | 0.94054 | 0 | 0.94054 | 0
Ground Level Pod #3 | Cafeteria | 59 | 3 |  |  | 2900 | 65 | 3 | AHU | 8 | 23200 | 0.15259 | 1.062 | 0.16205 | 0 | 0.16205 | 0
Ground Level Pod #3 | Center Core | 272 | 18 |  |  | 425 | 9 | 9 | AHU | 8 | 3400 | 4.8 | 1 | 4.8 | 2 | 4.8 | 2
Ground Level Pod #3 | Entryway | 68 | 4 |  |  | 460 | 10 | 4 | AHU | 8 | 3680 | 1.1087 | 1 | 1.1087 | 1 | 1.1087 | 1
Ground Level Pod #3 | Pod Center Core | 174 | 11 |  |  | 900 | 20 | 11 | AHU | 8 | 7200 | 1.45 | 1 | 1.45 | 1 | 1.45 | 1
Ground Level Pod #3 | Pod Center Prep | 30 | 2 |  |  | 945 | 21 | 2 | AHU | 8 | 7560 | 0.2381 | 1 | 0.2381 | 0 | 0.2381 | 0
Ground level Pod #4 | Center Ring - Counselor | 34 | 2 |  |  | 110 | 2 | 2 | AHU | 8 | 880 | 2.3182 | 1 | 2.3182 | 1 | 2.3182 | 1
Ground level Pod #4 | Center Ring - Police | 0 | 0 |  |  | 187 | 4 | 0 | AHU | 8 | 1496 | 0 | 1 | 0 | 0 | 0 | 0
Ground level Pod #4 | Center Ring - Social Work | 36 | 2 |  |  | 110 | 2 | 2 | AHU | 8 | 880 | 2.4545 | 1 | 2.4545 | 1 | 2.4545 | 1
Ground Level Pod #4 | Mayfair Center Core | 63 | 4 |  |  | 425 | 9 | 4 | AHU | 8 | 3400 | 1.1118 | 1 | 1.1118 | 1 | 1.1118 | 1
Ground Level Pod #4 | Mayfair Conference | 27 | 1 |  |  | 156 | 3 | 1 | AHU | 8 | 1248 | 1.2981 | 1 | 1.2981 | 1 | 1.2981 | 1
Ground Level Pod #4 | Mayfair Entry way | 0 | 0 |  |  | 204 | 4 | 0 | AHU | 8 | 1632 | 0 | 1 | 0 | 0 | 0 | 0
Ground Level Pod #4 | Mayfair Nurse Office | 0 | 0 |  |  | 216 | 4 | 0 | AHU | 8 | 1728 | 0 | 1 | 0 | 0 | 0 | 0
Ground Level Pod #4 | Mayfair Office | 0 | 0 |  |  | 144 | 3 | 0 | AHU | 8 | 1152 | 0 | 1 | 0 | 0 | 0 | 0
Ground Level Pod #4 | Mayfair Pod Center Core | 21 | 1 |  |  | 969 | 22 | 1 | AHU | 8 | 7752 | 0.16254 | 1 | 0.16254 | 0 | 0.16254 | 0
Ground Level Pod #4 | Mayfair Pod Center Prep | 0 | 0 |  |  | 646 | 14 | 0 | AHU | 8 | 5168 | 0 | 1 | 0 | 0 | 0 | 0
Ground Level Pod #4 | Mayfair Principal Office | 0 | 0 |  |  | 190 | 4 | 0 | AHU | 8 | 1520 | 0 | 1 | 0 | 0 | 0 | 0
Ground Level Pod #4 | Nurse Exam | 62 | 4 |  |  | 54 | 1 | 1 | AHU | 8 | 432 | 8.6111 | 1 | 8.6111 | 2 | 8.6111 | 2
Ground Level Pod #4 | Nurse Office | 93 | 6 |  |  | 420 | 9 | 6 | AHU | 8 | 3360 | 1.6607 | 1 | 1.6607 | 1 | 1.6607 | 1
Ground Level Pod #4 | Roster Area Entry | 134 | 8 |  |  | 150 | 3 | 3 | AHU | 8 | 1200 | 6.7 | 1 | 6.7 | 2 | 6.7 | 2
Ground Level Pod #4 | Roster Room | 64 | 4 |  |  | 80 | 1 | 1 | AHU | 8 | 640 | 6 | 1 | 6 | 2 | 6 | 2
- | Gym | 3715 | 247 |  |  | 3700 | 84 | 84 | AHU | 8 | 29600 | 7.5304 | 1.062 | 7.9976 | 2 | 7.9976 | 2
Lower Level Pod #2 | M-1 Band - Ensemble | 60 | 4 |  |  | 459 | 10 | 4 | AHU | 8 | 3672 | 0.98039 | 1 | 0.98039 | 0 | 0.98039 | 0
Lower Level Pod #2 | M-1 Band - Office | 30 | 2 |  |  | 600 | 13 | 2 | AHU | 8 | 4800 | 0.375 | 1 | 0.375 | 0 | 0.375 | 0
Lower Level Pod #2 | M-1 Band - Practice 1 | 59 | 3 |  |  | 450 | 10 | 3 | AHU | 8 | 3600 | 0.98333 | 1 | 0.98333 | 0 | 0.98333 | 0
Lower Level Pod #2 | Math Rm - Office | 30 | 2 |  |  | 104 | 2 | 2 | AHU | 8 | 832 | 2.1635 | 1 | 2.1635 | 1 | 2.1635 | 1
Lower Level Pod #2 | Math Rm - Storage | 0 | 0 |  |  | 50 | 1 | 0 | AHU | 8 | 400 | 0 | 1 | 0 | 0 | 0 | 0
Lower Level Pod #2 | Storage | 0 | 0 |  |  |  | 0 | 0 | AHU
Lower Level Pod #2 | Visual Com. Lab - Darkroom | 58 | 3 |  |  | 380 | 8 | 3 | AHU | 8 | 3040 | 1.1447 | 1 | 1.1447 | 1 | 1.1447 | 1
Lower Level Pod #4 | Center Core Art-01,02,03 | 60 | 4 |  |  | 1692 | 38 | 4 | AHU | 8 | 13536 | 0.26596 | 1 | 0.26596 | 0 | 0.26596 | 0
Lower Level Pod #4 | Center Core Storage | 21 | 1 |  |  |  | 0 | 0 | AHU
Lower Level Pod #4 | Classroom #3 Office | 25 | 1 |  |  | 144 | 3 | 1 | AHU | 8 | 1152 | 1.3021 | 1 | 1.3021 | 1 | 1.3021 | 1
Lower Level Pod #4 | Classroom #3 Prep | 27 | 1 |  |  | 50 | 1 | 1 | AHU | 8 | 400 | 4.05 | 1 | 4.05 | 2 | 4.05 | 2
Lower Level Pod #4 | Classroom #3 Storage | 24 | 1 |  |  | 126 | 2 | 1 | AHU | 8 | 1008 | 1.4286 | 1 | 1.4286 | 1 | 1.4286 | 1
Lower Level Pod #4 | M-5 Band Rm Ensemble | 46 | 3 |  |  | 1734 | 39 | 3 | AHU | 8 | 13872 | 0.19896 | 1 | 0.19896 | 0 | 0.19896 | 0
Lower Level Pod #4 | M-5 Band Rm Office | 0 | 0 |  |  | 100 | 2 | 0 | AHU | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
Lower Level Pod #4 | M-5 Band Rm Practice 1 | 0 | 0 |  |  | 40 | 0 | 0 | AHU | 8 | 320 | 0 | 1 | 0 | 0 | 0 | 0
Lower Level Pod #4 | M-5 Band Rm Practice 2 | 0 | 0 |  |  | 40 | 0 | 0 | AHU | 8 | 320 | 0 | 1 | 0 | 0 | 0 | 0
M-1 B | Band Room | 323 | 21 |  |  | 1178 | 26 | 21 | Unit Ventilator | 8 | 9424 | 2.0565 | 1 | 2.0565 | 1 | 2.0565 | 1
M-5 | Band Room | 0 | 0 |  |  | 1734 | 39 | 0 | Unit Ventilator | 8 | 13872 | 0 | 1 | 0 | 0 | 0 | 0
Math Lab | Classroom | 338 | 22 |  |  | 1337 | 30 | 22 | Unit Ventilator | 8 | 10696 | 1.896 | 1 | 1.896 | 1 | 1.896 | 1
S-01 A | Power Tech Lab | 312 | 20 |  |  | 1472 | 33 | 20 | Unit Ventilator | 8 | 11776 | 1.5897 | 1 | 1.5897 | 1 | 1.5897 | 1
S-02 A | Engineering Lab | 797 | 53 |  |  | 1985 | 45 | 45 | Unit Ventilator | 8 | 15880 | 3.0113 | 1 | 3.0113 | 1 | 3.0113 | 1
S-03 | Visual Comm. Lab | 321 | 21 |  |  | 1379 | 31 | 21 | Unit Ventilator | 8 | 11032 | 1.7458 | 1 | 1.7458 | 1 | 1.7458 | 1
Technology Lab | Classroom | 326 | 21 |  |  | 1025 | 23 | 21 | Unit Ventilator | 8 | 8200 | 2.3854 | 1 | 2.3854 | 1 | 2.3854 | 1
- | Auditorium | 4818 | 321 |  |  | 4485 | 101 | 101 | AHU | 8 | 35880 | 8.0569 | 1.062 | 8.5567 | 2 | 8.5567 | 2
Upper Level | Mayfair Multi-Purpose Room | 835 | 55 |  |  | 5781 | 131 | 55 | AHU | 8 | 46248 | 1.0833 | 1.062 | 1.1505 | 1 | 1.1505 | 1
129A | Upper Level Pod #1 Classroom | 264 | 17 |  |  | 731 | 16 | 16 | AHU | 8 | 5848 | 2.7086 | 1 | 2.7086 | 1 | 2.7086 | 1
Upper Level Pod #1 | Core | 309 | 20 |  |  | 540 | 12 | 12 | AHU | 8 | 4320 | 4.2917 | 1 | 4.2917 | 2 | 4.2917 | 2
Upper Level Pod #1 | Deans Office | 355 | 23 |  |  | 480 | 10 | 10 | AHU | 8 | 3840 | 5.5469 | 1 | 5.5469 | 2 | 5.5469 | 2
Upper Level Pod #1 | Pod Center Core | 0 | 0 |  |  | 616 | 14 | 0 | AHU | 8 | 4928 | 0 | 1 | 0 | 0 | 0 | 0
430 | Upper Level Multi-Purpose Mayfair Classroom | 90 | 6 | Yes | 20 | 1249 | 28 | 28 | AHU | 8 | 9992 | 0.54043 | 1 | 0.54043 | 0 | 20.5404 | 3
431 | Upper Level Multi-Purpose Mayfair Classroom | 136 | 9 | Yes | 20 | 789 | 17 | 17 | AHU | 8 | 6312 | 1.2928 | 1 | 1.2928 | 1 | 21.2928 | 3
Upper Level Pod #2 | Core | 0 | 0 |  |  | 425 | 9 | 0 | AHU | 8 | 3400 | 0 | 1 | 0 | 0 | 0 | 0
432 | Upper Level Pod #2 Lab B/C (Mayfair Room) | 212 | 14 | Yes | 20 | 928 | 21 | 21 | AHU | 8 | 7424 | 1.7134 | 1 | 1.7134 | 1 | 21.7134 | 3
433 | Upper Level Pod #2 Mayfair Kindergarten (Mayfair Room) | 184 | 12 | Yes | 20 | 1145 | 26 | 26 | AHU | 8 | 9160 | 1.2052 | 1 | 1.2052 | 1 | 21.2052 | 3
Upper Level Pod #2 | Pod Center Core | 0 | 0 |  |  | 2968 | 67 | 0 | AHU | 8 | 23744 | 0 | 1.062 | 0 | 0 | 0 | 0
Upper Level Pod #3 | Center Core | 0 | 0 |  |  | 616 | 14 | 0 | AHU | 8 | 4928 | 0 | 1 | 0 | 0 | 0 | 0
Upper Level Pod #3 | Lab C Classroom | 187 | 12 |  |  | 806 | 18 | 12 | AHU | 8 | 6448 | 1.7401 | 1 | 1.7401 | 1 | 1.7401 | 1
Upper Level Pod #3 | Lab Office | 28 | 1 |  |  | 120 | 2 | 1 | AHU | 8 | 960 | 1.75 | 1 | 1.75 | 1 | 1.75 | 1
Upper Level Pod #3 | Pod Center Core | 0 | 0 |  |  | 2968 | 67 | 0 | AHU | 8 | 23744 | 0 | 1.062 | 0 | 0 | 0 | 0
Upper Level Pod #4 | Mayfair Center Core | 174 | 11 |  |  | 4366 | 99 | 11 | AHU | 8 | 34928 | 0.2989 | 1.062 | 0.31744 | 0 | 0.31744 | 0
429 | Upper Level Pod #4 Mayfair Classroom | 263 | 17 |  |  | 1008 | 22 | 17 | AHU | 8 | 8064 | 1.9568 | 1 | 1.9568 | 1 | 1.9568 | 1
Upper Level Pod #4 | Mayfair Counselor Office | 79 | 5 |  |  | 132 | 3 | 3 | AHU | 8 | 1056 | 4.4886 | 1 | 4.4886 | 2 | 4.4886 | 2
Upper Level Pod #4 | Mayfair Multi-Purpose Room | 424 | 28 |  |  | 4662 | 105 | 28 | AHU | 8 | 37296 | 0.68211 | 1.062 | 0.72443 | 0 | 0.72443 | 0
Upper Level Pod #4 | Mayfair Principal Office | 83 | 5 |  |  | 180 | 4 | 4 | AHU | 8 | 1440 | 3.4583 | 1 | 3.4583 | 1 | 3.4583 | 1
Weight Room | Classroom | 107 | 7 |  |  | 210 | 4 | 4 | AHU | 8 | 1680 | 3.8214 | 1 | 3.8214 | 1 | 3.8214 | 1
Sheet Last Modified: | 2021-04-27
School: | William M. Meredith Elementary-Middle School
William M. Meredith Elementary-Middle School Modular Building
Vendor: | Capital
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
B5 | Classroom |  | 0 | Yes | 20 | 696 | 15 | 15 |  | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 |  | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 |  | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 |  | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom |  | 0 | Yes | 20 | 920 | 20 | 20 |  | 8 | 7360 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom |  | 0 | Yes | 20 | 816 | 18 | 18 |  | 8 | 6528 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 | Yes | 20 | 664 | 15 | 15 |  | 8 | 5312 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom |  | 0 | Yes | 20 | 664 | 15 | 15 |  | 8 | 5312 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 |  | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
204.5 | Classroom |  | 0 | Yes | 20 | 425 | 9 | 9 |  | 8 | 3400 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 782 | 17 | 17 |  | 8 | 6256 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 | Yes | 20 | 759 | 17 | 17 |  | 8 | 6072 | 0 | 1 | 0 | 0 | 20 | 3
206A | Classroom |  | 0 | Yes | 20 | 368 | 8 | 8 |  | 8 | 2944 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom |  | 0 | Yes | 20 | 506 | 11 | 11 |  | 8 | 4048 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom |  | 0 | Yes | 20 | 664 | 15 | 15 |  | 8 | 5312 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 | Yes | 20 | 696 | 15 | 15 |  | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom |  | 0 | Yes | 20 | 682 | 15 | 15 |  | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom |  | 0 | Yes | 20 | 638 | 14 | 14 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom |  | 0 | Yes | 20 | 1210 | 27 | 27 |  | 8 | 9680 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom |  | 0 | Yes | 20 | 782 | 17 | 17 |  | 8 | 6256 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom |  | 0 | Yes | 20 | 648 | 14 | 14 |  | 8 | 5184 | 0 | 1 | 0 | 0 | 20 | 3
309A | Classroom |  | 0 |  |  | 420 | 9 | 0 |  | 8 | 3360 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium |  | 0 |  |  | 3185 | 72 | 0 |  | 8 | 25480 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Counselors Office |  | 0 | Yes | 20 | 375 | 8 | 8 |  | 8 | 3000 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 |  |  | 3723 | 84 | 0 |  | 8 | 29784 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Library |  | 0 | Yes | 20 | 1298 | 29 | 29 |  | 8 | 10384 | 0 | 1 | 0 | 0 | 20 | 3
- | Lunchroom |  | 0 |  |  | 2250 | 51 | 0 |  | 8 | 18000 | 0 | 1 | 0 | 0 | 0 | 0
- | Main office |  | 0 | Yes | 20 | 368 | 8 | 8 |  | 8 | 2944 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses Office |  | 0 | Yes | 20 | 168 | 3 | 3 |  | 8 | 1344 | 0 | 1 | 0 | 0 | 20 | 3
- | Principals office |  | 0 | Yes | 20 | 256 | 5 | 5 |  | 8 | 2048 | 0 | 1 | 0 | 0 | 20 | 3
- | Psych Office #1 |  | 0 |  |  | 138 | 3 | 0 |  | 8 | 1104 | 0 | 1 | 0 | 0 | 0 | 0
- | Psych Office #2 |  | 0 |  |  | 88 | 2 | 0 |  | 8 | 704 | 0 | 1 | 0 | 0 | 0 | 0
- | Teachers Lounge |  | 0 |  |  | 322 | 7 | 0 |  | 8 | 2576 | 0 | 1 | 0 | 0 | 0 | 0
Modular Building
1 | Classroom | 368 | 24 |  |  | 720 | 16 | 16 | AHU | 8 | 5760 | 3.8333 | 1 | 3.8333 | 1 | 3.8333 | 1
2 | Classroom | 378 | 25 |  |  | 720 | 16 | 16 | AHU | 8 | 5760 | 3.9375 | 1 | 3.9375 | 1 | 3.9375 | 1
3 | Classroom | 381 | 25 |  |  | 720 | 16 | 16 | AHU | 8 | 5760 | 3.9688 | 1 | 3.9688 | 1 | 3.9688 | 1
4 | Classroom | 374 | 24 |  |  | 720 | 16 | 16 | AHU | 8 | 5760 | 3.8958 | 1 | 3.8958 | 1 | 3.8958 | 1
Sheet Last Modified: | 2021-04-26
School: | Thomas Mifflin Elementary School
Vendor: | EMCOR | Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 253 | 16 | Yes | 20 | 794 | 18 | 18 | Unit Ventilator | 8 | 6352 | 2.3898 | 1 | 2.3898 | 1 | 22.3898 | 3
102 | Classroom | 555 | 37 |  |  | 1040 | 23 | 23 | Unit Ventilator | 8 | 8320 | 4.0024 | 1 | 4.0024 | 2 | 4.0024 | 2
103 | Classroom | 288 | 19 |  |  | 375 | 8 | 8 | Unit Ventilator | 8 | 3000 | 5.76 | 1 | 5.76 | 2 | 5.76 | 2
104 | Classroom | 270 | 18 |  |  | 537 | 12 | 12 | Unit Ventilator | 8 | 4296 | 3.7709 | 1 | 3.7709 | 1 | 3.7709 | 1
105 | Classroom | 395 | 26 |  |  | 484 | 11 | 11 | Unit Ventilator | 8 | 3872 | 6.1209 | 1 | 6.1209 | 2 | 6.1209 | 2
106 | Classroom | 422 | 28 |  |  | 682 | 15 | 15 | Unit Ventilator | 8 | 5456 | 4.6408 | 1 | 4.6408 | 2 | 4.6408 | 2
107 | Classroom | 330 | 22 |  |  | 658 | 14 | 14 | Unit Ventilator | 8 | 5264 | 3.7614 | 1 | 3.7614 | 1 | 3.7614 | 1
108 | Classroom | 439 | 29 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.7717 | 1 | 4.7717 | 2 | 4.7717 | 2
109 | Classroom | 230 | 15 |  |  | 662 | 15 | 15 | Unit Ventilator | 8 | 5296 | 2.6057 | 1 | 2.6057 | 1 | 2.6057 | 1
110 | Classroom | 348 | 23 |  |  | 669 | 15 | 15 | Unit Ventilator | 8 | 5352 | 3.9013 | 1 | 3.9013 | 1 | 3.9013 | 1
111 | Classroom | 587 | 39 |  |  | 531 | 12 | 12 | Unit Ventilator | 8 | 4248 | 8.291 | 1 | 8.291 | 2 | 8.291 | 2
114 | Classroom | 0 | 0 | Yes | 20 | 630 | 14 | 14 | Unit Ventilator | 8 | 5040 | 0 | 1 | 0 | 0 | 20 | 3
115 | Classroom | 0 | 0 | Yes | 20 | 684 | 15 | 15 | Unit Ventilator | 8 | 5472 | 0 | 1 | 0 | 0 | 20 | 3
128 (117) | Counselor Office | 376 | 25 |  |  | 350 | 7 | 7 | Unit Ventilator | 8 | 2800 | 8.0571 | 1 | 8.0571 | 2 | 8.0571 | 2
201 | Classroom | 595 | 39 |  |  | 775 | 17 | 17 | Unit Ventilator | 8 | 6200 | 5.7581 | 1 | 5.7581 | 2 | 5.7581 | 2
202 | Classroom | 638 | 42 |  |  | 764 | 17 | 17 | Unit Ventilator | 8 | 6112 | 6.2631 | 1 | 6.2631 | 2 | 6.2631 | 2
203 | Classroom | 300 | 20 |  |  | 340 | 7 | 7 | Unit Ventilator | 8 | 2720 | 6.6176 | 1 | 6.6176 | 2 | 6.6176 | 2
204 | Classroom | 354 | 23 |  |  | 639 | 14 | 14 | Unit Ventilator | 8 | 5112 | 4.1549 | 1 | 4.1549 | 2 | 4.1549 | 2
205 | Classroom | 458 | 30 |  |  | 682 | 15 | 15 | Unit Ventilator | 8 | 5456 | 5.0367 | 1 | 5.0367 | 2 | 5.0367 | 2
206 | Classroom | 432 | 28 |  |  | 688 | 15 | 15 | Unit Ventilator | 8 | 5504 | 4.7093 | 1 | 4.7093 | 2 | 4.7093 | 2
207 | Classroom | 606 | 40 |  |  | 686 | 15 | 15 | Unit Ventilator | 8 | 5488 | 6.6254 | 1 | 6.6254 | 2 | 6.6254 | 2
209 | Classroom | 241 | 16 |  |  | 686 | 15 | 15 | Unit Ventilator | 8 | 5488 | 2.6348 | 1 | 2.6348 | 1 | 2.6348 | 1
210 | Classroom | 598 | 39 |  |  | 1380 | 31 | 31 | Unit Ventilator | 8 | 11040 | 3.25 | 1 | 3.25 | 1 | 3.25 | 1
211 | Classroom | 408 | 27 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 4.4348 | 1 | 4.4348 | 2 | 4.4348 | 2
212 | Meeting Room | 1055 | 70 |  |  | 312 | 7 | 7 | Unit Ventilator | 8 | 2496 | 25.3606 | 1 | 25.3606 | 4 | 25.3606 | 4
215 | Classroom |  | 0 | Yes | 20 | 323 | 7 | 7 | Unit Ventilator | 8 | 2584 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 0 | 0 |  |  | 3837 | 87 | 0 | House Fan | 8 | 30696 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria | 270 | 18 | Yes | 20 | 2128 | 48 | 48 | Unit Ventilator | 8 | 17024 | 0.9516 | 1 | 0.9516 | 0 | 20.9516 | 3
- | Cafeteria Hall | 0 | 0 |  |  | 738 | 16 | 0 | Unit Ventilator | 8 | 5904 | 0 | 1 | 0 | 0 | 0 | 0
- | Library | 403 | 26 |  |  | 3024 | 68 | 26 | Unit Ventilator | 8 | 24192 | 0.9995 | 1.062 | 1.0615 | 1 | 1.0615 | 1
- | Music Room | 425 | 28 |  |  | 966 | 21 | 21 | Unit Ventilator | 8 | 7728 | 3.2997 | 1 | 3.2997 | 1 | 3.2997 | 1
Pre-K 3 | Classroom | 489 | 32 |  |  | 972 | 22 | 22 | Unit Ventilator | 8 | 7776 | 3.7731 | 1 | 3.7731 | 1 | 3.7731 | 1
Pre-K 4 | Classroom | 335 | 22 |  |  | 920 | 20 | 20 | Unit Ventilator | 8 | 7360 | 2.731 | 1 | 2.731 | 1 | 2.731 | 1
- | Main Office |  | 0 | Yes | 20 | 552 | 12 | 12 |  | 8 | 4416 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 390 | 8 | 8 |  | 8 | 3120 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses Office |  | 0 | Yes | 20 | 192 | 4 | 4 |  | 8 | 1536 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym | 4205 | 280 |  |  | 5280 | 120 | 120 | RTU | 8 | 42240 | 5.973 | 1.062 | 6.3435 | 2 | 6.3435 | 2
6 | Speech |  | 0 | Yes | 20 | 544 | 12 | 12 |  | 8 | 4352 | 0 | 1 | 0 | 0 | 20 | 3
8 | Classroom |  | 0 | Yes | 20 | 851 | 19 | 19 |  | 8 | 6808 | 0 | 1 | 0 | 0 | 20 | 3
20 | Special Needs |  | 0 | Yes | 20 | 661 | 15 | 15 |  | 8 | 5288 | 0 | 1 | 0 | 0 | 20 | 3
- | Spanish Classroom | 0 | 0 | Yes | 20 | 900 | 20 | 20 | Unit Ventilator | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-28
School: | E. Spencer Miller- Philadelphia Learning Academy South (9-12) and Crossroads Acelerated Academy (7-8)
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
153 | Office | 0 | 0 |  |  | 187 | 4 | 0 |  | 8 | 1496 | 0 | 1 | 0 | 0 | 0 | 0
158 | School Police Office | 267 | 17 |  |  | 540 | 12 | 12 |  | 8 | 4320 | 3.7083 | 1 | 3.7083 | 1 | 3.7083 | 1
167 | Staff Lounge | 0 | 0 |  |  | 532 | 12 | 0 |  | 8 | 4256 | 0 | 1 | 0 | 0 | 0 | 0
170 | Office | 0 | 0 |  |  | 99 | 2 | 0 |  | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
175 | Office | 0 | 0 |  |  | 154 | 3 | 0 |  | 8 | 1232 | 0 | 1 | 0 | 0 | 0 | 0
181 | Office | 49 | 3 |  |  | 344 | 7 | 3 |  | 8 | 2752 | 1.0683 | 1 | 1.0683 | 1 | 1.0683 | 1
183 | Office | 10 | 0 |  |  | 110 | 2 | 0 |  | 8 | 880 | 0.68182 | 1 | 0.68182 | 0 | 0.68182 | 0
184 | Office | 7 | 0 |  |  | 100 | 2 | 0 |  | 8 | 800 | 0.525 | 1 | 0.525 | 0 | 0.525 | 0
185 | Office | 17 | 1 |  |  | 220 | 5 | 1 |  | 8 | 1760 | 0.57955 | 1 | 0.57955 | 0 | 0.57955 | 0
186 | Office | 27 | 1 |  |  | 208 | 4 | 1 |  | 8 | 1664 | 0.97356 | 1 | 0.97356 | 0 | 0.97356 | 0
188 | Office | 201 | 13 |  |  | 77 | 1 | 1 |  | 8 | 616 | 19.5779 | 1 | 19.5779 | 3 | 19.5779 | 3
192 | Office | 289 | 19 |  |  | 111 | 2 | 2 |  | 8 | 888 | 19.527 | 1 | 19.527 | 3 | 19.527 | 3
245 | Office | 17 | 1 |  |  | 170 | 3 | 1 |  | 8 | 1360 | 0.75 | 1 | 0.75 | 0 | 0.75 | 0
246 | Office | 41 | 2 |  |  | 131 | 2 | 2 |  | 8 | 1048 | 2.3473 | 1 | 2.3473 | 1 | 2.3473 | 1
247 | Office | 33 | 2 |  |  | 167 | 3 | 2 |  | 8 | 1336 | 1.482 | 1 | 1.482 | 1 | 1.482 | 1
248 | Office | 0 | 0 |  |  | 152 | 3 | 0 |  | 8 | 1216 | 0 | 1 | 0 | 0 | 0 | 0
252 | Office | 0 | 0 |  |  | 516 | 11 | 0 |  | 8 | 4128 | 0 | 1 | 0 | 0 | 0 | 0
254 | Office | 166 | 11 |  |  | 231 | 5 | 5 |  | 8 | 1848 | 5.3896 | 1 | 5.3896 | 2 | 5.3896 | 2
255 | Office | 46 | 3 |  |  | 98 | 2 | 2 |  | 8 | 784 | 3.5204 | 1 | 3.5204 | 1 | 3.5204 | 1
256 | Office | 94 | 6 |  |  | 140 | 3 | 3 |  | 8 | 1120 | 5.0357 | 1 | 5.0357 | 2 | 5.0357 | 2
257 | Office | 396 | 26 |  |  | 120 | 2 | 2 |  | 8 | 960 | 24.75 | 1 | 24.75 | 4 | 24.75 | 4
258 | Office | 58 | 3 |  |  | 531 | 12 | 3 |  | 8 | 4248 | 0.81921 | 1 | 0.81921 | 0 | 0.81921 | 0
262 | Office | 111 | 7 |  |  | 102 | 2 | 2 |  | 8 | 816 | 8.1618 | 1 | 8.1618 | 2 | 8.1618 | 2
266 | Office | 762 | 50 |  |  | 381 | 8 | 8 |  | 8 | 3048 | 15 | 1 | 15 | 3 | 15 | 3
267 | Office | 949 | 63 |  |  | 437 | 9 | 9 |  | 8 | 3496 | 16.2872 | 1 | 16.2872 | 3 | 16.2872 | 3
274 | Office | 192 | 12 |  |  | 148 | 3 | 3 |  | 8 | 1184 | 9.7297 | 1 | 9.7297 | 2 | 9.7297 | 2
275 | Office | 130 | 8 |  |  | 117 | 2 | 2 |  | 8 | 936 | 8.3333 | 1 | 8.3333 | 2 | 8.3333 | 2
276 | Office | 72 | 4 |  |  | 101 | 2 | 2 |  | 8 | 808 | 5.3465 | 1 | 5.3465 | 2 | 5.3465 | 2
277 | Office | 176 | 11 |  |  | 147 | 3 | 3 |  | 8 | 1176 | 8.9796 | 1 | 8.9796 | 2 | 8.9796 | 2
278 | Office | 107 | 7 |  |  | 109 | 2 | 2 |  | 8 | 872 | 7.3624 | 1 | 7.3624 | 2 | 7.3624 | 2
279 | Office | 104 | 6 |  |  | 106 | 2 | 2 |  | 8 | 848 | 7.3585 | 1 | 7.3585 | 2 | 7.3585 | 2
280 | Office | 287 | 19 |  |  | 254 | 5 | 5 |  | 8 | 2032 | 8.4744 | 1 | 8.4744 | 2 | 8.4744 | 2
282 | Office | 311 | 20 |  |  | 272 | 6 | 6 |  | 8 | 2176 | 8.5754 | 1 | 8.5754 | 2 | 8.5754 | 2
286 | Office | 636 | 42 |  |  | 290 | 6 | 6 |  | 8 | 2320 | 16.4483 | 1 | 16.4483 | 3 | 16.4483 | 3
287 | Office | 104 | 6 |  |  | 107 | 2 | 2 |  | 8 | 856 | 7.2897 | 1 | 7.2897 | 2 | 7.2897 | 2
290 | Office | 108 | 7 |  |  | 132 | 3 | 3 |  | 8 | 1056 | 6.1364 | 1 | 6.1364 | 2 | 6.1364 | 2
291 | Office | 107 | 7 |  |  | 151 | 3 | 3 |  | 8 | 1208 | 5.3146 | 1 | 5.3146 | 2 | 5.3146 | 2
292 | Office | 210 | 14 |  |  | 150 | 3 | 3 |  | 8 | 1200 | 10.5 | 1 | 10.5 | 3 | 10.5 | 3
293 | Office | 186 | 12 |  |  | 153 | 3 | 3 |  | 8 | 1224 | 9.1176 | 1 | 9.1176 | 2 | 9.1176 | 2
- | 1st Flr Computer Room | 0 | 0 |  |  | 240 | 5 | 0 |  | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
- | 1st Flr Corrider by B & E Section | 0 | 0 |  |  | 320 | 7 | 0 |  | 8 | 2560 | 0 | 1 | 0 | 0 | 0 | 0
- | 1st Flr Kitchen | 8316 | 554 |  |  | 924 | 21 | 21 |  | 8 | 7392 | 67.5 | 1 | 67.5 | 5 | 67.5 | 5
- | 1st Flr Kitchen Dry Food Area | 171 | 11 |  |  | 187 | 4 | 4 |  | 8 | 1496 | 6.8583 | 1 | 6.8583 | 2 | 6.8583 | 2
- | 1st Flr Kitchen Freezer Area | 85 | 5 |  |  | 420 | 9 | 5 |  | 8 | 3360 | 1.5179 | 1 | 1.5179 | 1 | 1.5179 | 1
- | 1st Flr Mechanical Room | 19 | 1 |  |  | 336 | 7 | 1 |  | 8 | 2688 | 0.42411 | 1 | 0.42411 | 0 | 0.42411 | 0
- | 2nd Floor Conference Room | 359 | 23 |  |  | 216 | 4 | 4 |  | 8 | 1728 | 12.4653 | 1 | 12.4653 | 3 | 12.4653 | 3
- | 2nd Floor Corridor by Elevator | 363 | 24 |  |  | 463 | 10 | 10 |  | 8 | 3704 | 5.8801 | 1 | 5.8801 | 2 | 5.8801 | 2
- | 2nd Floor Meeting Room | 139 | 9 |  |  | 79 | 1 | 1 |  | 8 | 632 | 13.1962 | 1 | 13.1962 | 3 | 13.1962 | 3
- | 2nd Floor Mens Restroom by Elevator | 138 | 9 |  |  | 255 | 5 | 5 |  | 8 | 2040 | 4.0588 | 1 | 4.0588 | 2 | 4.0588 | 2
- | 2nd Floor Restroom Vestibule by Elevator | 157 | 10 |  |  | 73 | 1 | 1 |  | 8 | 584 | 16.1301 | 1 | 16.1301 | 3 | 16.1301 | 3
- | 2nd Floor Womans Restroom by Elevator | 114 | 7 |  |  | 167 | 3 | 3 |  | 8 | 1336 | 5.1198 | 1 | 5.1198 | 2 | 5.1198 | 2
- | 2nd Flr Corridor by Admin Office | 195 | 13 |  |  | 218 | 4 | 4 |  | 8 | 1744 | 6.7087 | 1 | 6.7087 | 2 | 6.7087 | 2
- | 2nd Flr Corridor by G Section | 45 | 3 |  |  | 458 | 10 | 3 |  | 8 | 3664 | 0.7369 | 1 | 0.7369 | 0 | 0.7369 | 0
- | 2nd Flr Reception Office | 170 | 11 |  |  | 116 | 2 | 2 |  | 8 | 928 | 10.9914 | 1 | 10.9914 | 3 | 10.9914 | 3
- | 1st Flr A - Common Area | 48 | 3 |  |  | 1251 | 28 | 3 |  | 8 | 10008 | 0.28777 | 1 | 0.28777 | 0 | 0.28777 | 0
A1 | Classroom | 58 | 3 |  |  | 960 | 21 | 3 |  | 8 | 7680 | 0.45312 | 1 | 0.45312 | 0 | 0.45312 | 0
A2 | Classroom | 66 | 4 |  |  | 990 | 22 | 4 |  | 8 | 7920 | 0.5 | 1 | 0.5 | 0 | 0.5 | 0
A3 | Classroom | 60 | 4 |  |  | 990 | 22 | 4 |  | 8 | 7920 | 0.45455 | 1 | 0.45455 | 0 | 0.45455 | 0
A4 | Classroom | 56 | 3 |  |  | 997 | 22 | 3 |  | 8 | 7976 | 0.42126 | 1 | 0.42126 | 0 | 0.42126 | 0
- | 1st Flr B - Common Area | 747 | 49 |  |  | 960 | 21 | 21 |  | 8 | 7680 | 5.8359 | 1 | 5.8359 | 2 | 5.8359 | 2
B1 | Classroom | 304 | 20 |  |  | 868 | 19 | 19 |  | 8 | 6944 | 2.6267 | 1 | 2.6267 | 1 | 2.6267 | 1
B2 | Classroom | 488 | 32 |  |  | 945 | 21 | 21 |  | 8 | 7560 | 3.873 | 1 | 3.873 | 1 | 3.873 | 1
B3 | Classroom | 942 | 62 |  |  | 980 | 22 | 22 |  | 8 | 7840 | 7.2092 | 1 | 7.2092 | 2 | 7.2092 | 2
B4 | Classroom | 961 | 64 |  |  | 910 | 20 | 20 |  | 8 | 7280 | 7.9203 | 1 | 7.9203 | 2 | 7.9203 | 2
- | C - Common Area 1st Flr | 1014 | 67 |  |  | 1285 | 29 | 29 |  | 8 | 10280 | 5.9183 | 1 | 5.9183 | 2 | 5.9183 | 2
C-1 | Classroom | 885 | 59 |  |  | 816 | 18 | 18 |  | 8 | 6528 | 8.1342 | 1 | 8.1342 | 2 | 8.1342 | 2
C-2 | Classroom | 1047 | 69 |  |  | 840 | 19 | 19 |  | 8 | 6720 | 9.3482 | 1 | 9.3482 | 2 | 9.3482 | 2
C-3 | Classroom | 1200 | 80 |  |  | 840 | 19 | 19 |  | 8 | 6720 | 10.7143 | 1 | 10.7143 | 3 | 10.7143 | 3
C-4 | Classroom | 828 | 55 |  |  | 868 | 19 | 19 |  | 8 | 6944 | 7.1544 | 1 | 7.1544 | 2 | 7.1544 | 2
- | Climate Masters Office | 150 | 10 |  |  | 821 | 18 | 10 |  | 8 | 6568 | 1.3703 | 1 | 1.3703 | 1 | 1.3703 | 1
- | Computer Support Specialist Office | 102 | 6 |  |  | 88 | 2 | 2 |  | 8 | 704 | 8.6932 | 1 | 8.6932 | 2 | 8.6932 | 2
- | Corridor 2nd Floor near office 252 | 0 | 0 |  |  | 376 | 8 | 0 |  | 8 | 3008 | 0 | 1 | 0 | 0 | 0 | 0
- | 1st Flr Corridor By B Section | 0 | 0 |  |  | 360 | 8 | 0 |  | 8 | 2880 | 0 | 1 | 0 | 0 | 0 | 0
- | Corridor by D Section | 713 | 47 |  |  | 438 | 9 | 9 |  | 8 | 3504 | 12.2089 | 1 | 12.2089 | 3 | 12.2089 | 3
- | Corridor by Main Office | 38 | 2 |  |  | 610 | 13 | 2 |  | 8 | 4880 | 0.46721 | 1 | 0.46721 | 0 | 0.46721 | 0
- | Corridor by Office 258 | 107 | 7 |  |  | 160 | 3 | 3 |  | 8 | 1280 | 5.0156 | 1 | 5.0156 | 2 | 5.0156 | 2
- | 2nd Flr D - Common Area | 202 | 13 |  |  | 910 | 20 | 13 |  | 8 | 7280 | 1.6648 | 1 | 1.6648 | 1 | 1.6648 | 1
D1 | Classroom | 206 | 13 |  |  | 960 | 21 | 13 |  | 8 | 7680 | 1.6094 | 1 | 1.6094 | 1 | 1.6094 | 1
D2 | Classroom | 132 | 8 |  |  | 901 | 20 | 8 |  | 8 | 7208 | 1.0988 | 1 | 1.0988 | 1 | 1.0988 | 1
D3 | Classroom | 268 | 17 |  |  | 1007 | 22 | 17 |  | 8 | 8056 | 1.996 | 1 | 1.996 | 1 | 1.996 | 1
D4 | Classroom | 209 | 13 |  |  | 972 | 22 | 13 |  | 8 | 7776 | 1.6127 | 1 | 1.6127 | 1 | 1.6127 | 1
- | Dr. Graham Principal Office | 111 | 7 |  |  | 823 | 18 | 7 |  | 8 | 6584 | 1.0115 | 1 | 1.0115 | 1 | 1.0115 | 1
- | 2nd Flr E - Common Area | 431 | 28 |  |  | 934 | 21 | 21 |  | 8 | 7472 | 3.4609 | 1 | 3.4609 | 1 | 3.4609 | 1
E1 | Classroom | 633 | 42 |  |  | 919 | 20 | 20 |  | 8 | 7352 | 5.1659 | 1 | 5.1659 | 2 | 5.1659 | 2
E2 | Classroom | 593 | 39 |  |  | 1021 | 23 | 23 |  | 8 | 8168 | 4.356 | 1 | 4.356 | 2 | 4.356 | 2
E3 | Classroom | 594 | 39 |  |  | 1046 | 23 | 23 |  | 8 | 8368 | 4.2591 | 1 | 4.2591 | 2 | 4.2591 | 2
E4 | Classroom | 647 | 43 |  |  | 984 | 22 | 22 |  | 8 | 7872 | 4.9314 | 1 | 4.9314 | 2 | 4.9314 | 2
- | 2nd Flr G - Common Area | 12 | 0 |  |  | 1214 | 27 | 0 |  | 8 | 9712 | 0.074135 | 1 | 0.074135 | 0 | 0.074135 | 0
G1 | Classroom | 40 | 2 |  |  | 862 | 19 | 2 |  | 8 | 6896 | 0.34803 | 1 | 0.34803 | 0 | 0.34803 | 0
G2 | Classroom | 29 | 1 |  |  | 878 | 19 | 1 |  | 8 | 7024 | 0.24772 | 1 | 0.24772 | 0 | 0.24772 | 0
G3 | Classroom | 26 | 1 |  |  | 884 | 20 | 1 |  | 8 | 7072 | 0.22059 | 1 | 0.22059 | 0 | 0.22059 | 0
G4 | Classroom | 33 | 2 |  |  | 872 | 19 | 2 |  | 8 | 6976 | 0.28383 | 1 | 0.28383 | 0 | 0.28383 | 0
- | 1 st Flr Gym | 5785 | 385 |  |  | 3888 | 88 | 88 |  | 8 | 31104 | 11.1593 | 1.062 | 11.8516 | 3 | 11.8516 | 3
- | Late Check Office | 0 | 0 |  |  | 96 | 2 | 0 |  | 8 | 768 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Entrance | 5 | 0 |  |  | 64 | 1 | 0 |  | 8 | 512 | 0.58594 | 1 | 0.58594 | 0 | 0.58594 | 0
- | 1st Flr Media Room | 524 | 34 |  |  | 1539 | 34 | 34 |  | 8 | 12312 | 2.5536 | 1 | 2.5536 | 1 | 2.5536 | 1
- | Meeting Room | 21 | 1 |  |  | 90 | 2 | 1 |  | 8 | 720 | 1.75 | 1 | 1.75 | 1 | 1.75 | 1
- | Mens Restroom by Elevator | 26 | 1 |  |  | 190 | 4 | 1 |  | 8 | 1520 | 1.0263 | 1 | 1.0263 | 1 | 1.0263 | 1
- | Nurses Office | 584 | 38 |  |  | 412 | 9 | 9 |  | 8 | 3296 | 10.6311 | 1 | 10.6311 | 3 | 10.6311 | 3
- | Office Corridor | 228 | 15 |  |  | 702 | 15 | 15 |  | 8 | 5616 | 2.4359 | 1 | 2.4359 | 1 | 2.4359 | 1
- | Parking Lot Entry | 0 | 0 |  |  | 135 | 3 | 0 |  | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
- | Reception | 47 | 3 |  |  | 521 | 11 | 3 |  | 8 | 4168 | 0.67658 | 1 | 0.67658 | 0 | 0.67658 | 0
- | Restroom Vestibule Between A1/A2 | 6 | 0 |  |  | 56 | 1 | 0 |  | 8 | 448 | 0.80357 | 1 | 0.80357 | 0 | 0.80357 | 0
- | Restroom Vestibule Between A3/A4 | 4 | 0 |  |  | 56 | 1 | 0 |  | 8 | 448 | 0.53571 | 1 | 0.53571 | 0 | 0.53571 | 0
- | Restroom Vestibule Between B1/B2 | 83 | 5 |  |  | 63 | 1 | 1 |  | 8 | 504 | 9.881 | 1 | 9.881 | 2 | 9.881 | 2
- | Restroom Vestibule Between B3/B4 | 49 | 3 |  |  | 63 | 1 | 1 |  | 8 | 504 | 5.8333 | 1 | 5.8333 | 2 | 5.8333 | 2
- | Restroom Vestibule Between C1/C2 | 89 | 5 |  |  | 56 | 1 | 1 |  | 8 | 448 | 11.9196 | 1 | 11.9196 | 3 | 11.9196 | 3
- | Restroom Vestibule Between C3/C4 | 93 | 6 |  |  | 63 | 1 | 1 |  | 8 | 504 | 11.0714 | 1 | 11.0714 | 3 | 11.0714 | 3
- | Restroom Vestibule Between D1/D2 | 20 | 1 |  |  | 50 | 1 | 1 |  | 8 | 400 | 3 | 1 | 3 | 1 | 3 | 1
- | Restroom Vestibule Between D3/D4 | 27 | 1 |  |  | 51 | 1 | 1 |  | 8 | 408 | 3.9706 | 1 | 3.9706 | 1 | 3.9706 | 1
- | Restroom Vestibule Between E1/E2 | 55 | 3 |  |  | 51 | 1 | 1 |  | 8 | 408 | 8.0882 | 1 | 8.0882 | 2 | 8.0882 | 2
- | Restroom Vestibule Between E3/E4 | 54 | 3 |  |  | 51 | 1 | 1 |  | 8 | 408 | 7.9412 | 1 | 7.9412 | 2 | 7.9412 | 2
- | Restroom Vestibule Between G1/G2 | 3 | 0 |  |  | 50 | 1 | 0 |  | 8 | 400 | 0.45 | 1 | 0.45 | 0 | 0.45 | 0
- | Restroom Vestibule Between G3/G4 | 2 | 0 |  |  | 51 | 1 | 0 |  | 8 | 408 | 0.29412 | 1 | 0.29412 | 0 | 0.29412 | 0
- | 1st Flr Storage Room | 61 | 4 |  |  | 475 | 10 | 4 |  | 8 | 3800 | 0.96316 | 1 | 0.96316 | 0 | 0.96316 | 0
- | Truancy Office 1st Floor | 0 | 0 |  |  | 727 | 16 | 0 |  | 8 | 5816 | 0 | 1 | 0 | 0 | 0 | 0
- | Vestibule by stairs/Rooms 266 & 267 | 153 | 10 |  |  | 219 | 4 | 4 |  | 8 | 1752 | 5.2397 | 1 | 5.2397 | 2 | 5.2397 | 2
- | Vistibule by Meeting Room | 132 | 8 |  |  | 252 | 5 | 5 |  | 8 | 2016 | 3.9286 | 1 | 3.9286 | 1 | 3.9286 | 1
- | Womans Restroom by 1st Floor Elevator | 26 | 1 |  |  | 169 | 3 | 1 |  | 8 | 1352 | 1.1538 | 1 | 1.1538 | 1 | 1.1538 | 1
Sheet Last Modified: | 2021-05-03
School: | Mitchell Elementary School
EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
110 | Counselor's Office |  | 0 | Yes | 20 | 255 | 5 | 5 | House Fan | 8 | 2040 | 0 | 1 | 0 | 0 | 20 | 3
111 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
112 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
213 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
214 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
215 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
216 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
217 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
218 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
219 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
220 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
221 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
222 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
223 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
225 | Nurse |  | 0 | Yes | 20 | 378 | 8 | 8 | House Fan | 8 | 3024 | 0 | 1 | 0 | 0 | 20 | 3
324 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
325 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
326 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
327 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
328 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
329 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
330 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
331 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
332 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
333 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
334 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
B1 | Classroom |  | 0 | Yes | 20 | 756 | 17 | 17 | Unit Ventilator | 8 | 6048 | 0 | 1 | 0 | 0 | 20 | 3
B2 | B.E. Office |  | 0 | Yes | 20 | 200 | 4 | 4 |  | 8 | 1600 | 0 | 1 | 0 | 0 | 20 | 3
B3 | Classroom |  | 0 | Yes | 20 | 609 | 13 | 13 | Unit Ventilator | 8 | 4872 | 0 | 1 | 0 | 0 | 20 | 3
B4 | Classroom |  | 0 | Yes | 20 | 980 | 22 | 22 | Unit Ventilator | 8 | 7840 | 0 | 1 | 0 | 0 | 20 | 3
B6 | Classroom |  | 0 | Yes | 20 | 1344 | 30 | 30 | Unit Ventilator | 8 | 10752 | 0 | 1 | 0 | 0 | 20 | 3
- | SP Office |  | 0 | Yes | 20 | 88 | 2 | 2 |  | 8 | 704 | 0 | 1 | 0 | 0 | 20 | 3
- | Library |  | 0 | Yes | 20 | 1504 | 34 | 34 |  | 8 | 12032 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 | Yes | 20 | 3495 | 79 | 79 | House Fan | 8 | 27960 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Cafeteria Office |  | 0 | Yes | 20 | 134 | 3 | 3 |  | 8 | 1072 | 0 | 1 | 0 | 0 | 20 | 3
- | Cafeteria |  | 0 | Yes | 20 | 2452 | 55 | 55 | House Fan | 8 | 19616 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 494 | 11 | 11 | House Fan | 8 | 3952 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 20 | 216 | 4 | 4 | House Fan | 8 | 1728 | 0 | 1 | 0 | 0 | 20 | 3
110C | Vice Principal's Office |  | 0 | Yes | 20 | 101 | 2 | 2 |  | 8 | 808 | 0 | 1 | 0 | 0 | 20 | 3
110A | Administrative Assistant's Office |  | 0 | Yes | 20 | 191 | 4 | 4 |  | 8 | 1528 | 0 | 1 | 0 | 0 | 20 | 3
- | Teacher's Lounge/Multipurpose |  | 0 | Yes | 20 | 390 | 8 | 8 | House Fan | 8 | 3120 | 0 | 1 | 0 | 0 | 20 | 3
110B | Counselor's Office |  | 0 | Yes | 20 | 242 | 5 | 5 | House Fan | 8 | 1936 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-19
School: | The Promise Academy @ Martin Luther King High School
Vendor: | Meehan (Auditorium) | Chadwick (Building) | Exhaust
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 464 | 30 |  |  | 828 | 18 | 18 |  | 8 | 6624 | 4.2029 | 1 | 4.2029 | 2 | 4.2029 | 2
102 | Classroom | 315 | 21 |  |  | 828 | 18 | 18 |  | 8 | 6624 | 2.8533 | 1 | 2.8533 | 1 | 2.8533 | 1
104 | Classroom | 260 | 17 |  |  | 900 | 20 | 17 |  | 8 | 7200 | 2.1667 | 1 | 2.1667 | 1 | 2.1667 | 1
105 | Classroom | 162 | 10 |  |  | 1050 | 23 | 10 |  | 8 | 8400 | 1.1571 | 1 | 1.1571 | 1 | 1.1571 | 1
106 | Classroom | 476 | 31 |  |  | 900 | 20 | 20 |  | 8 | 7200 | 3.9667 | 1 | 3.9667 | 1 | 3.9667 | 1
107 | Classroom | 229 | 15 |  |  | 864 | 19 | 15 |  | 8 | 6912 | 1.9878 | 1 | 1.9878 | 1 | 1.9878 | 1
108 | Classroom | 489 | 32 |  |  | 850 | 19 | 19 |  | 8 | 6800 | 4.3147 | 1 | 4.3147 | 2 | 4.3147 | 2
109 | Classroom | 304 | 20 |  |  | 896 | 20 | 20 |  | 8 | 7168 | 2.5446 | 1 | 2.5446 | 1 | 2.5446 | 1
110 | Classroom |  | 0 |  |  | 800 | 18 | 0 |  | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
116 | Classroom |  | 0 |  |  | 800 | 18 | 0 |  | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
117 | Classroom | 296 | 19 |  |  | 924 | 21 | 19 |  | 8 | 7392 | 2.4026 | 1 | 2.4026 | 1 | 2.4026 | 1
118 | Classroom | 278 | 18 |  |  | 864 | 19 | 18 |  | 8 | 6912 | 2.4132 | 1 | 2.4132 | 1 | 2.4132 | 1
120 | Classroom | 105 | 7 |  |  | 864 | 19 | 7 |  | 8 | 6912 | 0.91146 | 1 | 0.91146 | 0 | 0.91146 | 0
121 | Classroom | 176 | 11 |  |  | 864 | 19 | 11 |  | 8 | 6912 | 1.5278 | 1 | 1.5278 | 1 | 1.5278 | 1
122 | Classroom | 420 | 28 |  |  | 1152 | 26 | 26 |  | 8 | 9216 | 2.7344 | 1 | 2.7344 | 1 | 2.7344 | 1
123 | Classroom | 86 | 5 |  |  | 864 | 19 | 5 |  | 8 | 6912 | 0.74653 | 1 | 0.74653 | 0 | 0.74653 | 0
124 | Classroom | 252 | 16 |  |  | 900 | 20 | 16 |  | 8 | 7200 | 2.1 | 1 | 2.1 | 1 | 2.1 | 1
125 | Classroom | 203 | 13 |  |  | 864 | 19 | 13 |  | 8 | 6912 | 1.7622 | 1 | 1.7622 | 1 | 1.7622 | 1
201 | Classroom | 215 | 14 |  |  | 828 | 18 | 14 |  | 8 | 6624 | 1.9475 | 1 | 1.9475 | 1 | 1.9475 | 1
202 | Classroom | 201 | 13 |  |  | 864 | 19 | 13 |  | 8 | 6912 | 1.7448 | 1 | 1.7448 | 1 | 1.7448 | 1
204 | Classroom |  | 0 |  |  | 900 | 20 | 0 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
205 | Classroom | 416 | 27 |  |  | 1050 | 23 | 23 |  | 8 | 8400 | 2.9714 | 1 | 2.9714 | 1 | 2.9714 | 1
206 | Classroom | 47 | 3 |  |  | 900 | 20 | 3 |  | 8 | 7200 | 0.39167 | 1 | 0.39167 | 0 | 0.39167 | 0
207 | Classroom | 90 | 6 |  |  | 864 | 19 | 6 |  | 8 | 6912 | 0.78125 | 1 | 0.78125 | 0 | 0.78125 | 0
208 | Classroom | 212 | 14 |  |  | 850 | 19 | 14 |  | 8 | 6800 | 1.8706 | 1 | 1.8706 | 1 | 1.8706 | 1
209 | Classroom | 360 | 24 |  |  | 896 | 20 | 20 |  | 8 | 7168 | 3.0134 | 1 | 3.0134 | 1 | 3.0134 | 1
210 | Classroom | 0 | 0 |  |  | 800 | 18 | 0 |  | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
216 | Classroom | 469 | 31 |  |  | 800 | 18 | 18 |  | 8 | 6400 | 4.3969 | 1 | 4.3969 | 2 | 4.3969 | 2
217 | Classroom | 130 | 8 |  |  | 924 | 21 | 8 |  | 8 | 7392 | 1.0552 | 1 | 1.0552 | 1 | 1.0552 | 1
218 | Classroom | 293 | 19 |  |  | 864 | 19 | 19 |  | 8 | 6912 | 2.5434 | 1 | 2.5434 | 1 | 2.5434 | 1
220 | Classroom | 318 | 21 |  |  | 864 | 19 | 19 |  | 8 | 6912 | 2.7604 | 1 | 2.7604 | 1 | 2.7604 | 1
221 | Classroom | 204 | 13 |  |  | 864 | 19 | 13 |  | 8 | 6912 | 1.7708 | 1 | 1.7708 | 1 | 1.7708 | 1
222 | Classroom | 210 | 14 |  |  | 1152 | 26 | 14 |  | 8 | 9216 | 1.3672 | 1 | 1.3672 | 1 | 1.3672 | 1
223 | Classroom | 170 | 11 |  |  | 864 | 19 | 11 |  | 8 | 6912 | 1.4757 | 1 | 1.4757 | 1 | 1.4757 | 1
224 | Classroom | 207 | 13 |  |  | 900 | 20 | 13 |  | 8 | 7200 | 1.725 | 1 | 1.725 | 1 | 1.725 | 1
225 | Classroom | 150 | 10 |  |  | 864 | 19 | 10 |  | 8 | 6912 | 1.3021 | 1 | 1.3021 | 1 | 1.3021 | 1
301 | Classroom | 161 | 10 |  |  | 828 | 18 | 10 |  | 8 | 6624 | 1.4583 | 1 | 1.4583 | 1 | 1.4583 | 1
302 | Classroom | 178 | 11 |  |  | 864 | 19 | 11 |  | 8 | 6912 | 1.5451 | 1 | 1.5451 | 1 | 1.5451 | 1
303 | Classroom |  | 0 | Yes | 20 | 805 | 18 | 18 |  | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom | 391 | 26 |  |  | 900 | 20 | 20 |  | 8 | 7200 | 3.2583 | 1 | 3.2583 | 1 | 3.2583 | 1
305 | Classroom | 244 | 16 |  |  | 1050 | 23 | 16 |  | 8 | 8400 | 1.7429 | 1 | 1.7429 | 1 | 1.7429 | 1
306 | Classroom | 347 | 23 |  |  | 900 | 20 | 20 |  | 8 | 7200 | 2.8917 | 1 | 2.8917 | 1 | 2.8917 | 1
307 | Classroom | 99 | 6 |  |  | 864 | 19 | 6 |  | 8 | 6912 | 0.85938 | 1 | 0.85938 | 0 | 0.85938 | 0
308 | Classroom | 217 | 14 |  |  | 850 | 19 | 14 |  | 8 | 6800 | 1.9147 | 1 | 1.9147 | 1 | 1.9147 | 1
309 | Classroom | 65 | 4 |  |  | 896 | 20 | 4 |  | 8 | 7168 | 0.54408 | 1 | 0.54408 | 0 | 0.54408 | 0
310 | Classroom | 347 | 23 |  |  | 800 | 18 | 18 |  | 8 | 6400 | 3.2531 | 1 | 3.2531 | 1 | 3.2531 | 1
313 | Classroom |  | 0 | Yes | 20 | 1368 | 31 | 31 |  | 8 | 10944 | 0 | 1 | 0 | 0 | 20 | 3
316 | Classroom | 297 | 19 |  |  | 800 | 18 | 18 |  | 8 | 6400 | 2.7844 | 1 | 2.7844 | 1 | 2.7844 | 1
317 | Classroom | 201 | 13 |  |  | 924 | 21 | 13 |  | 8 | 7392 | 1.6315 | 1 | 1.6315 | 1 | 1.6315 | 1
318 | Classroom | 275 | 18 |  |  | 864 | 19 | 18 |  | 8 | 6912 | 2.3872 | 1 | 2.3872 | 1 | 2.3872 | 1
320 | Classroom | 303 | 20 |  |  | 864 | 19 | 19 |  | 8 | 6912 | 2.6302 | 1 | 2.6302 | 1 | 2.6302 | 1
321 | Classroom | 85 | 5 |  |  | 864 | 19 | 5 |  | 8 | 6912 | 0.73785 | 1 | 0.73785 | 0 | 0.73785 | 0
322 | Classroom | 310 | 20 |  |  | 1152 | 26 | 20 |  | 8 | 9216 | 2.0182 | 1 | 2.0182 | 1 | 2.0182 | 1
323 | Classroom | 310 | 20 |  |  | 864 | 19 | 19 |  | 8 | 6912 | 2.691 | 1 | 2.691 | 1 | 2.691 | 1
324 | Classroom | 213 | 14 |  |  | 900 | 20 | 14 |  | 8 | 7200 | 1.775 | 1 | 1.775 | 1 | 1.775 | 1
325 | Classroom | 84 | 5 |  |  | 864 | 19 | 5 |  | 8 | 6912 | 0.72917 | 1 | 0.72917 | 0 | 0.72917 | 0
327 | Classroom |  | 0 | Yes | 20 | 1824 | 41 | 41 |  | 8 | 14592 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 13590 | 906 |  |  | 4350 | 98 | 98 |  | 8 | 34800 | 23.431 | 1.062 | 24.8846 | 4 | 24.8846 | 4
Sheet Last Modified: | 2021-03-18
School: | John Moffet Elementary School
Vendor: | Devine Brothers | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101A | Classroom | 97 | 6 |  |  | 360 | 8 | 6 | AHU | 8 | 2880 | 2.0208 | 1 | 2.0208 | 1 | 2.0208 | 1
104 | Classroom | 225 | 15 |  |  | 704 | 16 | 15 | Unit Ventilator | 8 | 5632 | 2.397 | 1 | 2.397 | 1 | 2.397 | 1
105 | Classroom | 205 | 13 |  |  | 575 | 13 | 13 | Unit Ventilator | 8 | 4600 | 2.6739 | 1 | 2.6739 | 1 | 2.6739 | 1
107 | Classroom | 271 | 18 |  |  | 805 | 18 | 18 | Unit Ventilator | 8 | 6440 | 2.5248 | 1 | 2.5248 | 1 | 2.5248 | 1
108 | Classroom | 327 | 21 |  |  | 782 | 17 | 17 | Unit Ventilator | 8 | 6256 | 3.1362 | 1 | 3.1362 | 1 | 3.1362 | 1
112 | Classroom | 524 | 34 |  |  | 896 | 20 | 20 | Unit Ventilator | 8 | 7168 | 4.3862 | 1 | 4.3862 | 2 | 4.3862 | 2
113 | Classroom | 293 | 19 |  |  | 928 | 21 | 19 | Unit Ventilator | 8 | 7424 | 2.368 | 1 | 2.368 | 1 | 2.368 | 1
114 | Classroom | 441 | 29 |  |  | 986 | 22 | 22 | Unit Ventilator | 8 | 7888 | 3.3545 | 1 | 3.3545 | 1 | 3.3545 | 1
115 | Classroom | 337 | 22 |  |  | 868 | 19 | 19 | Unit Ventilator | 8 | 6944 | 2.9119 | 1 | 2.9119 | 1 | 2.9119 | 1
119 | Nurse | 178 | 11 |  |  | 77 | 1 | 1 | AHU | 8 | 616 | 17.3377 | 1 | 17.3377 | 3 | 17.3377 | 3
201 | Classroom | 105 | 7 |  |  | 315 | 7 | 7 | Unit Ventilator | 8 | 2520 | 2.5 | 1 | 2.5 | 1 | 2.5 | 1
202 | Classroom | 745 | 49 |  |  | 891 | 20 | 20 | Unit Ventilator | 8 | 7128 | 6.271 | 1 | 6.271 | 2 | 6.271 | 2
203 | Classroom | 301 | 20 |  |  | 754 | 17 | 17 | Unit Ventilator | 8 | 6032 | 2.994 | 1 | 2.994 | 1 | 2.994 | 1
204 | Classroom | 357 | 23 |  |  | 754 | 17 | 17 | Unit Ventilator | 8 | 6032 | 3.5511 | 1 | 3.5511 | 1 | 3.5511 | 1
205 | Classroom | 267 | 17 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 3.0022 | 1 | 3.0022 | 1 | 3.0022 | 1
208 | Classroom | 183 | 12 |  |  | 924 | 21 | 12 | Unit Ventilator | 8 | 7392 | 1.4854 | 1 | 1.4854 | 1 | 1.4854 | 1
209 | Classroom | 542 | 36 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 6.0945 | 1 | 6.0945 | 2 | 6.0945 | 2
211 | Classroom | 543 | 36 |  |  | 648 | 14 | 14 | Unit Ventilator | 8 | 5184 | 6.2847 | 1 | 6.2847 | 2 | 6.2847 | 2
213 | Classroom | 114 | 7 |  |  | 352 | 8 | 7 | Unit Ventilator | 8 | 2816 | 2.429 | 1 | 2.429 | 1 | 2.429 | 1
214 | Classroom | 210 | 14 |  |  | 957 | 21 | 14 | Unit Ventilator | 8 | 7656 | 1.6458 | 1 | 1.6458 | 1 | 1.6458 | 1
215 | Classroom | 261 | 17 |  |  | 754 | 17 | 17 | Unit Ventilator | 8 | 6032 | 2.5962 | 1 | 2.5962 | 1 | 2.5962 | 1
216 | Classroom | 470 | 31 |  |  | 754 | 17 | 17 | Unit Ventilator | 8 | 6032 | 4.6751 | 1 | 4.6751 | 2 | 4.6751 | 2
217 | Classroom | 666 | 44 |  |  | 957 | 21 | 21 | Unit Ventilator | 8 | 7656 | 5.2194 | 1 | 5.2194 | 2 | 5.2194 | 2
218 | Classroom | 260 | 17 |  |  | 330 | 7 | 7 | Unit Ventilator | 8 | 2640 | 5.9091 | 1 | 5.9091 | 2 | 5.9091 | 2
219 | Classroom | 0 | 0 |  |  | 1100 | 25 | 0 | Unit Ventilator | 8 | 8800 | 0 | 1 | 0 | 0 | 0 | 0
221 | Classroom | 449 | 29 |  |  | 884 | 20 | 20 | Unit Ventilator | 8 | 7072 | 3.8094 | 1 | 3.8094 | 1 | 3.8094 | 1
223 | Classroom | 403 | 26 |  |  | 340 | 7 | 7 | AHU | 8 | 2720 | 8.8897 | 1 | 8.8897 | 2 | 8.8897 | 2
225 | Classroom | 266 | 17 |  |  | 858 | 19 | 17 | Unit Ventilator | 8 | 6864 | 2.3252 | 1 | 2.3252 | 1 | 2.3252 | 1
228A | Classroom | 60 | 4 |  |  | 252 | 5 | 4 | AHU | 8 | 2016 | 1.7857 | 1 | 1.7857 | 1 | 1.7857 | 1
229 | Classroom | 47 | 3 |  |  | 336 | 7 | 3 | AHU | 8 | 2688 | 1.0491 | 1 | 1.0491 | 1 | 1.0491 | 1
- | Auditorium | 773 | 51 |  |  | 2478 | 56 | 51 | AHU | 8 | 19824 | 2.3396 | 1 | 2.3396 | 1 | 2.3396 | 1
- | Faculty Lounge | 125 | 8 |  |  | 361 | 8 | 8 | Unit Ventilator | 8 | 2888 | 2.597 | 1 | 2.597 | 1 | 2.597 | 1
- | Library | 1025 | 68 |  |  | 1674 | 38 | 38 | AHU | 8 | 13392 | 4.5923 | 1 | 4.5923 | 2 | 4.5923 | 2
- | Office | 110 | 7 |  |  | 70 | 1 | 1 | AHU | 8 | 560 | 11.7857 | 1 | 11.7857 | 3 | 11.7857 | 3
- | Main Office | 87 | 5 |  |  | 496 | 11 | 5 | Unit Ventilator | 8 | 3968 | 1.3155 | 1 | 1.3155 | 1 | 1.3155 | 1
- | Principals Office | 140 | 9 |  |  | 294 | 6 | 6 | Unit Ventilator | 8 | 2352 | 3.5714 | 1 | 3.5714 | 1 | 3.5714 | 1
Sheet Last Modified: | 2021-04-26
School: | J. Hampton Moore Elementary School
| Mobile Classrooms | Main Building | Little School House
Vendor: | Devine | Main Retest | LSH Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Moore Main
- | Auditorium | 224 | 14 |  |  | 3015 | 68 | 14 | AHU | 8 | 24120 | 0.55721 | 1.062 | 0.59178 | 0 | 0.59178 | 0
- | Gym | 145 | 9 | Yes | 20 | 4500 | 102 | 102 | AHU | 8 | 36000 | 0.24167 | 1.062 | 0.25666 | 0 | 20.2567 | 3
101 | Classroom | 518 | 34 |  |  | 1055 | 23 | 23 | Univent | 8 | 8440 | 3.6825 | 1 | 3.6825 | 1 | 3.6825 | 1
102 | Classroom | 504 | 33 |  |  | 1055 | 23 | 23 | Univent | 8 | 8440 | 3.5829 | 1 | 3.5829 | 1 | 3.5829 | 1
103 | Classroom | 364 | 24 |  |  | 624 | 14 | 14 | Univent | 8 | 4992 | 4.375 | 1 | 4.375 | 2 | 4.375 | 2
104 | Classroom | 116 | 7 | Yes | 20 | 458 | 10 | 10 | Univent | 8 | 3664 | 1.8996 | 1 | 1.8996 | 1 | 21.8996 | 3
105 | Classroom | 408 | 27 |  |  | 1082 | 24 | 24 | Univent | 8 | 8656 | 2.8281 | 1 | 2.8281 | 1 | 2.8281 | 1
106 | Classroom | 237 | 15 | Yes | 20 | 951 | 21 | 21 | Univent | 8 | 7608 | 1.8691 | 1 | 1.8691 | 1 | 21.8691 | 3
107 | Classroom | 535 | 35 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 4.2192 | 1 | 4.2192 | 2 | 4.2192 | 2
108 | Classroom | 503 | 33 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 3.9669 | 1 | 3.9669 | 1 | 3.9669 | 1
109 | Classroom | 220 | 14 | Yes | 20 | 951 | 21 | 21 | Univent | 8 | 7608 | 1.735 | 1 | 1.735 | 1 | 21.735 | 3
110 | Classroom | 113 | 7 | Yes | 20 | 951 | 21 | 21 | Univent | 8 | 7608 | 0.89117 | 1 | 0.89117 | 0 | 20.8912 | 3
110A | Classroom | 237 | 15 |  |  | 951 | 21 | 15 | Univent | 8 | 7608 | 1.8691 | 1 | 1.8691 | 1 | 1.8691 | 1
112 | Classroom | 325 | 21 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 2.5631 | 1 | 2.5631 | 1 | 2.5631 | 1
113 | Classroom | 472 | 31 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 3.7224 | 1 | 3.7224 | 1 | 3.7224 | 1
114 | Classroom | 487 | 32 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 3.8407 | 1 | 3.8407 | 1 | 3.8407 | 1
115 | Classroom | 236 | 15 |  |  | 383 | 8 | 8 | Univent | 8 | 3064 | 4.6214 | 1 | 4.6214 | 2 | 4.6214 | 2
201 | Classroom | 480 | 32 |  |  | 976 | 22 | 22 | Univent | 8 | 7808 | 3.6885 | 1 | 3.6885 | 1 | 3.6885 | 1
202 | Classroom | 319 | 21 |  |  | 976 | 22 | 21 | Univent | 8 | 7808 | 2.4513 | 1 | 2.4513 | 1 | 2.4513 | 1
203 | Classroom | 251 | 16 | Yes | 20 | 951 | 21 | 21 | Univent | 8 | 7608 | 1.9795 | 1 | 1.9795 | 1 | 21.9795 | 3
203B | Classroom |  | 0 | Yes | 20 | 624 | 14 | 14 |  | 8 | 4992 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom | 291 | 19 | Yes | 20 | 951 | 21 | 21 | Univent | 8 | 7608 | 2.295 | 1 | 2.295 | 1 | 22.295 | 3
205A | Classroom | 261 | 17 | Yes | 20 | 452 | 10 | 10 | Univent | 8 | 3616 | 4.3308 | 1 | 4.3308 | 2 | 24.3308 | 4
205B | Classroom | 130 | 8 | Yes | 20 | 642 | 14 | 14 | Univent | 8 | 5136 | 1.5187 | 1 | 1.5187 | 1 | 21.5187 | 3
206 | Classroom | 326 | 21 |  |  | 970 | 22 | 21 | Univent | 8 | 7760 | 2.5206 | 1 | 2.5206 | 1 | 2.5206 | 1
207 | Classroom | 424 | 28 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 3.3438 | 1 | 3.3438 | 1 | 3.3438 | 1
207A | Classroom |  | 0 | Yes | 20 | 239 | 5 | 5 | N/A | 8 | 1912 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 527 | 35 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 4.1562 | 1 | 4.1562 | 2 | 4.1562 | 2
209 | Classroom | 399 | 26 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 3.1467 | 1 | 3.1467 | 1 | 3.1467 | 1
210A | Classroom | 108 | 7 | Yes | 20 | 458 | 10 | 10 | Univent | 8 | 3664 | 1.7686 | 1 | 1.7686 | 1 | 21.7686 | 3
210B | Classroom | 335 | 22 | Yes | 20 | 458 | 10 | 10 | Univent | 8 | 3664 | 5.4858 | 1 | 5.4858 | 2 | 25.4858 | 4
211 | Classroom | 433 | 28 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 3.4148 | 1 | 3.4148 | 1 | 3.4148 | 1
212 | Classroom | 244 | 16 | Yes | 20 | 951 | 21 | 21 | Univent | 8 | 7608 | 1.9243 | 1 | 1.9243 | 1 | 21.9243 | 3
213 | Classroom | 0 | 0 | Yes | 20 | 951 | 21 | 21 | Univent | 8 | 7608 | 0 | 1 | 0 | 0 | 20 | 3
214 | Classroom | 64 | 4 | Yes | 20 | 820 | 18 | 18 | Univent | 8 | 6560 | 0.58537 | 1 | 0.58537 | 0 | 20.5854 | 3
215 | Classroom | 454 | 30 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 3.5804 | 1 | 3.5804 | 1 | 3.5804 | 1
216 | Classroom | 444 | 29 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 3.5016 | 1 | 3.5016 | 1 | 3.5016 | 1
217 | Classroom | 520 | 34 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 4.1009 | 1 | 4.1009 | 2 | 4.1009 | 2
218 | Classroom | 347 | 23 |  |  | 951 | 21 | 21 | Univent | 8 | 7608 | 2.7366 | 1 | 2.7366 | 1 | 2.7366 | 1
219 | Counselor Office |  | 0 | Yes | 20 | 170 | 3 | 3 |  | 8 | 1360 | 0 | 1 | 0 | 0 | 20 | 3
- | Principals Office | 0 | 0 | Yes | 20 | 400 | 9 | 9 |  | 8 | 3200 | 0 | 1 | 0 | 0 | 20 | 3
Assistant Principal | Office |  | 0 | Yes | 20 | 172 | 3 | 3 |  | 8 | 1376 | 0 | 1 | 0 | 0 | 20 | 3
Teachers Lounge | Room |  | 0 | Yes | 20 | 170 | 3 | 3 |  | 8 | 1360 | 0 | 1 | 0 | 0 | 20 | 3
2nd Floor Copy Room | Room |  | 0 | Yes | 20 | 172 | 3 | 3 |  | 8 | 1376 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office | 0 | 0 | Yes | 20 | 800 | 18 | 18 | Univent | 8 | 6400 | 0 | 1 | 0 | 0 | 20 | 3
Moore LSH
- | Office | 224 | 14 |  |  | 200 | 4 | 4 | FCU | 8 | 1600 | 8.4 | 1 | 8.4 | 2 | 8.4 | 2
- | Kitchen | 145 | 9 |  |  | 624 | 14 | 9 | FCU | 8 | 4992 | 1.7428 | 1 | 1.7428 | 1 | 1.7428 | 1
- | Faculty Lounge | 130 | 8 | Yes | 20 | 200 | 4 | 4 | FCU | 8 | 1600 | 4.875 | 1 | 4.875 | 2 | 24.875 | 4
P101 | Classroom |  | 0 | Yes | 20 | 120 | 2 | 2 |  | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
P102 | Classroom |  | 0 | Yes | 20 | 120 | 2 | 2 |  | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
P110 | Classroom | 361 | 24 |  |  | 950 | 21 | 21 | Univent | 8 | 7600 | 2.85 | 1 | 2.85 | 1 | 2.85 | 1
P111 | Classroom | 593 | 39 |  |  | 950 | 21 | 21 | Univent | 8 | 7600 | 4.6816 | 1 | 4.6816 | 2 | 4.6816 | 2
P112 | Classroom | 379 | 25 |  |  | 950 | 21 | 21 | Univent | 8 | 7600 | 2.9921 | 1 | 2.9921 | 1 | 2.9921 | 1
P113 | Classroom | 463 | 30 |  |  | 950 | 21 | 21 | Univent | 8 | 7600 | 3.6553 | 1 | 3.6553 | 1 | 3.6553 | 1
P114 | Classroom | 747 | 49 |  |  | 950 | 21 | 21 | Univent | 8 | 7600 | 5.8974 | 1 | 5.8974 | 2 | 5.8974 | 2
P114 | Hallway | 130 | 8 |  |  | 780 | 17 | 8 | FCU | 8 | 6240 | 1.25 | 1 | 1.25 | 1 | 1.25 | 1
P115 | Classroom | 361 | 24 |  |  | 950 | 21 | 21 | Univent | 8 | 7600 | 2.85 | 1 | 2.85 | 1 | 2.85 | 1
P116 | Classroom | 491 | 32 |  |  | 950 | 21 | 21 | Univent | 8 | 7600 | 3.8763 | 1 | 3.8763 | 1 | 3.8763 | 1
P117 | Classroom | 430 | 28 |  |  | 950 | 21 | 21 | Univent | 8 | 7600 | 3.3947 | 1 | 3.3947 | 1 | 3.3947 | 1
P124 | Classroom | 999 | 66 |  |  | 950 | 21 | 21 | Univent | 8 | 7600 | 7.8868 | 1 | 7.8868 | 2 | 7.8868 | 2
P124 | Hallway | 80 | 5 |  |  | 1122 | 25 | 5 | FCU | 8 | 8976 | 0.53476 | 1 | 0.53476 | 0 | 0.53476 | 0
P125 | Classroom | 476 | 31 |  |  | 950 | 21 | 21 | Univent | 8 | 7600 | 3.7579 | 1 | 3.7579 | 1 | 3.7579 | 1
P126 | Classroom | 304 | 20 |  |  | 950 | 21 | 20 | Univent | 8 | 7600 | 2.4 | 1 | 2.4 | 1 | 2.4 | 1
P127 | Classroom | 1009 | 67 |  |  | 950 | 21 | 21 | Univent | 8 | 7600 | 7.9658 | 1 | 7.9658 | 2 | 7.9658 | 2
Moore Modular
A-1 | Classroom | 568 | 37 |  |  | 781 | 17 | 17 | Univent | 8 | 6248 | 5.4545 | 1 | 5.4545 | 2 | 5.4545 | 2
A-2 | Classroom | 453 | 30 |  |  | 781 | 17 | 17 | Univent | 8 | 6248 | 4.3502 | 1 | 4.3502 | 2 | 4.3502 | 2
A-3 | Classroom | 441 | 29 |  |  | 781 | 17 | 17 | Univent | 8 | 6248 | 4.235 | 1 | 4.235 | 2 | 4.235 | 2
A-4 | Classroom | 360 | 24 |  |  | 781 | 17 | 17 | Univent | 8 | 6248 | 3.4571 | 1 | 3.4571 | 1 | 3.4571 | 1
A-5 | Classroom | 214 | 14 | Yes | 20 | 781 | 17 | 17 | Univent | 8 | 6248 | 2.0551 | 1 | 2.0551 | 1 | 22.0551 | 3
A-6 | Classroom | 125 | 8 | Yes | 20 | 781 | 17 | 17 | Univent | 8 | 6248 | 1.2004 | 1 | 1.2004 | 1 | 21.2004 | 3
A-7 | Classroom | 465 | 31 |  |  | 781 | 17 | 17 | Univent | 8 | 6248 | 4.4654 | 1 | 4.4654 | 2 | 4.4654 | 2
A-8 | Classroom | 629 | 41 |  |  | 781 | 17 | 17 | Univent | 8 | 6248 | 6.0403 | 1 | 6.0403 | 2 | 6.0403 | 2
Sheet Last Modified: | 2021-04-12
School: | Robert Morris Elementary School
Vendor: | EMCOR Fluidics
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 192 | 12 | Yes | 20 | 1284 | 29 | 29 | Univent | 8 | 10272 | 1.1215 | 1 | 1.1215 | 1 | 21.1215 | 3
101 | Classroom | 171 | 11 | Yes | 20 | 1410 | 32 | 32 | Univent | 8 | 11280 | 0.90957 | 1 | 0.90957 | 0 | 20.9096 | 3
200 | Classroom | 185 | 12 | Yes | 20 | 858 | 19 | 19 | Univent | 8 | 6864 | 1.6171 | 1 | 1.6171 | 1 | 21.6171 | 3
201 | Classroom | 72 | 4 | Yes | 20 | 603 | 13 | 13 | Univent | 8 | 4824 | 0.89552 | 1 | 0.89552 | 0 | 20.8955 | 3
202 | Classroom | 218 | 14 |  |  | 849 | 19 | 14 | Univent | 8 | 6792 | 1.9258 | 1 | 1.9258 | 1 | 1.9258 | 1
203 | Classroom | 200 | 13 | Yes | 20 | 821 | 18 | 18 | Univent | 8 | 6568 | 1.827 | 1 | 1.827 | 1 | 21.827 | 3
204 | Classroom | 163 | 10 | Yes | 20 | 846 | 19 | 19 | Univent | 8 | 6768 | 1.445 | 1 | 1.445 | 1 | 21.445 | 3
206 | Classroom | 85 | 5 |  |  | 847 | 19 | 5 | Univent | 8 | 6776 | 0.75266 | 1 | 0.75266 | 0 | 0.75266 | 0
208 | Classroom | 152 | 10 |  |  | 830 | 18 | 10 | Univent | 8 | 6640 | 1.3735 | 1 | 1.3735 | 1 | 1.3735 | 1
210 | Classroom | 0 | 0 |  |  | 837 | 19 | 0 | Univent | 8 | 6696 | 0 | 1 | 0 | 0 | 0 | 0
212 | Lunch Room | 137 | 9 |  |  | 876 | 19 | 9 | Univent | 8 | 7008 | 1.1729 | 1 | 1.1729 | 1 | 1.1729 | 1
213 | Classroom | 74 | 4 |  |  | 875 | 19 | 4 | Univent | 8 | 7000 | 0.63429 | 1 | 0.63429 | 0 | 0.63429 | 0
214 | Classroom | 125 | 8 |  |  | 848 | 19 | 8 | Univent | 8 | 6784 | 1.1055 | 1 | 1.1055 | 1 | 1.1055 | 1
215 | Classroom | 286 | 19 |  |  | 840 | 19 | 19 | Univent | 8 | 6720 | 2.5536 | 1 | 2.5536 | 1 | 2.5536 | 1
216 | Classroom | 94 | 6 |  |  | 848 | 19 | 6 | Univent | 8 | 6784 | 0.83137 | 1 | 0.83137 | 0 | 0.83137 | 0
217 | Classroom | 114 | 7 | Yes | 20 | 463 | 10 | 10 | Univent | 8 | 3704 | 1.8467 | 1 | 1.8467 | 1 | 21.8467 | 3
218 | Classroom | 283 | 18 |  |  | 1037 | 23 | 18 | Univent | 8 | 8296 | 2.0468 | 1 | 2.0468 | 1 | 2.0468 | 1
219 | Kitchen | 261 | 17 |  |  | 1204 | 27 | 17 | Univent | 8 | 9632 | 1.6258 | 1 | 1.6258 | 1 | 1.6258 | 1
300 | Classroom | 86 | 5 | Yes | 20 | 856 | 19 | 19 | Univent | 8 | 6848 | 0.7535 | 1 | 0.7535 | 0 | 20.7535 | 3
301 | Classroom | 273 | 18 |  |  | 601 | 13 | 13 | Univent | 8 | 4808 | 3.4068 | 1 | 3.4068 | 1 | 3.4068 | 1
302 | Classroom | 225 | 15 |  |  | 848 | 19 | 15 | Univent | 8 | 6784 | 1.99 | 1 | 1.99 | 1 | 1.99 | 1
303 | Classroom | 266 | 17 |  |  | 818 | 18 | 17 | Univent | 8 | 6544 | 2.4389 | 1 | 2.4389 | 1 | 2.4389 | 1
304 | Classroom | 86 | 5 |  |  | 843 | 19 | 5 | Univent | 8 | 6744 | 0.76512 | 1 | 0.76512 | 0 | 0.76512 | 0
306 | Classroom | 169 | 11 |  |  | 849 | 19 | 11 | Univent | 8 | 6792 | 1.4929 | 1 | 1.4929 | 1 | 1.4929 | 1
308 | Classroom | 129 | 8 | Yes | 20 | 828 | 18 | 18 | Univent | 8 | 6624 | 1.1685 | 1 | 1.1685 | 1 | 21.1685 | 3
310/312/314 | Library | 734 | 48 |  |  | 2102 | 47 | 47 | Univent | 8 | 16816 | 2.6189 | 1 | 2.6189 | 1 | 2.6189 | 1
313 | Classroom | 264 | 17 |  |  | 975 | 22 | 17 | Univent | 8 | 7800 | 2.0308 | 1 | 2.0308 | 1 | 2.0308 | 1
315 | Classroom | 217 | 14 |  |  | 1220 | 27 | 14 | Univent | 8 | 9760 | 1.334 | 1 | 1.334 | 1 | 1.334 | 1
316 | Classroom | 139 | 9 |  |  | 845 | 19 | 9 | Univent | 8 | 6760 | 1.2337 | 1 | 1.2337 | 1 | 1.2337 | 1
317 | Classroom | 152 | 10 | Yes | 20 | 462 | 10 | 10 | Univent | 8 | 3696 | 2.4675 | 1 | 2.4675 | 1 | 22.4675 | 3
319 | Art Room | 0 | 0 | Yes | 20 | 1042 | 23 | 23 | Univent | 8 | 8336 | 0 | 1 | 0 | 0 | 20 | 3
400 | Classroom | 58 | 3 |  |  | 857 | 19 | 3 | Univent | 8 | 6856 | 0.50758 | 1 | 0.50758 | 0 | 0.50758 | 0
401 | Classroom | 121 | 8 | Yes | 20 | 602 | 13 | 13 | Univent | 8 | 4816 | 1.5075 | 1 | 1.5075 | 1 | 21.5075 | 3
402 | Classroom | 169 | 11 |  |  | 846 | 19 | 11 | Univent | 8 | 6768 | 1.4982 | 1 | 1.4982 | 1 | 1.4982 | 1
403 | Classroom | 498 | 33 |  |  | 817 | 18 | 18 | Univent | 8 | 6536 | 4.5716 | 1 | 4.5716 | 2 | 4.5716 | 2
404 | Classroom | 92 | 6 |  |  | 848 | 19 | 6 | Univent | 8 | 6784 | 0.81368 | 1 | 0.81368 | 0 | 0.81368 | 0
406 | Classroom | 60 | 4 |  |  | 845 | 19 | 4 | Univent | 8 | 6760 | 0.53254 | 1 | 0.53254 | 0 | 0.53254 | 0
408 | Classroom | 55 | 3 | Yes | 20 | 829 | 18 | 18 | Univent | 8 | 6632 | 0.49759 | 1 | 0.49759 | 0 | 20.4976 | 3
410 | Classroom | 0 | 0 |  |  | 849 | 19 | 0 | Univent | 8 | 6792 | 0 | 1 | 0 | 0 | 0 | 0
412 | Lunch Room | 106 | 7 |  |  | 858 | 19 | 7 | Univent | 8 | 6864 | 0.92657 | 1 | 0.92657 | 0 | 0.92657 | 0
413 | Classroom | 313 | 20 |  |  | 871 | 19 | 19 | Univent | 8 | 6968 | 2.6952 | 1 | 2.6952 | 1 | 2.6952 | 1
414 | Classroom | 291 | 19 |  |  | 847 | 19 | 19 | Univent | 8 | 6776 | 2.5767 | 1 | 2.5767 | 1 | 2.5767 | 1
415 | Classroom | 147 | 9 | Yes | 20 | 836 | 19 | 19 | Univent | 8 | 6688 | 1.3188 | 1 | 1.3188 | 1 | 21.3188 | 3
416 | Classroom | 106 | 7 | Yes | 20 | 847 | 19 | 19 | Univent | 8 | 6776 | 0.93861 | 1 | 0.93861 | 0 | 20.9386 | 3
417 | Faculty | 158 | 10 |  |  | 446 | 10 | 10 | Univent | 8 | 3568 | 2.657 | 1 | 2.657 | 1 | 2.657 | 1
418 | Classroom | 34 | 2 | Yes | 20 | 1044 | 23 | 23 | Univent | 8 | 8352 | 0.24425 | 1 | 0.24425 | 0 | 20.2443 | 3
419 | Music Room | 511 | 34 |  |  | 1040 | 23 | 23 | Univent | 8 | 8320 | 3.6851 | 1 | 3.6851 | 1 | 3.6851 | 1
- | Auditorium | 1066 | 71 |  |  | 5308 | 120 | 71 | Univent | 8 | 42464 | 1.5062 | 1.062 | 1.5997 | 1 | 1.5997 | 1
- | Counselor's Office | 70 | 4 |  |  | 474 | 10 | 4 | Univent | 8 | 3792 | 1.1076 | 1 | 1.1076 | 1 | 1.1076 | 1
- | Gymnasium | 1100 | 73 |  |  | 3688 | 83 | 73 | Univent | 8 | 29504 | 2.237 | 1.062 | 2.3758 | 1 | 2.3758 | 1
- | Nurse's Office |  | 0 | Yes | 20 | 261 | 5 | 5 | N/A | 8 | 2088 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 20 | 294 | 6 | 6 | N/A | 8 | 2352 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office | 387 | 25 |  |  | 1373 | 31 | 25 | Univent | 8 | 10984 | 2.114 | 1 | 2.114 | 1 | 2.114 | 1
Sheet Last Modified: | 2021-03-18
School: | Andrew Morrison Elementary School
Vendor: | EMCOR Fluidics | EMCOR Retest 1-15-21 | Retest 2-22-21
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
5 | Music Rm |  | 0 | Yes | 20 | 813 | 18 | 18 | House Fan | 8 | 6504 | 0 | 1 | 0 | 0 | 20 | 3
8 | Art Rm |  | 0 | Yes | 20 | 886 | 20 | 20 | House Fan | 8 | 7088 | 0 | 1 | 0 | 0 | 20 | 3
101A | Nurse |  | 0 | Yes | 20 | 376 | 8 | 8 | House Fan | 8 | 3008 | 0 | 1 | 0 | 0 | 20 | 3
101B | Counselor |  | 0 |  |  | 341 | 7 | 0 | House Fan | 8 | 2728 | 0 | 1 | 0 | 0 | 0 | 0
102 | Classroom |  | 0 | Yes | 20 | 701 | 15 | 15 | House Fan | 8 | 5608 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 734 | 16 | 16 | House Fan | 8 | 5872 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
106 | Lounge |  | 0 | Yes | 20 | 526 | 11 | 11 | House Fan | 8 | 4208 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom |  | 0 | Yes | 20 | 566 | 12 | 12 | House Fan | 8 | 4528 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 376 | 25 |  |  | 765 | 17 | 17 | Univent | 8 | 6120 | 3.6863 | 1 | 3.6863 | 1 | 3.6863 | 1
110 | Classroom | 427 | 28 |  |  | 792 | 18 | 18 | Univent | 8 | 6336 | 4.0436 | 1 | 4.0436 | 2 | 4.0436 | 2
111 | Classroom | 408 | 27 |  |  | 781 | 17 | 17 | Univent | 8 | 6248 | 3.9181 | 1 | 3.9181 | 1 | 3.9181 | 1
112 | Classroom | 469 | 31 |  |  | 792 | 18 | 18 | Univent | 8 | 6336 | 4.4413 | 1 | 4.4413 | 2 | 4.4413 | 2
113 | Classroom | 380 | 25 |  |  | 767 | 17 | 17 | Univent | 8 | 6136 | 3.7158 | 1 | 3.7158 | 1 | 3.7158 | 1
114 | Office / Classroom | 271 | 18 |  |  | 351 | 7 | 7 | Univent | 8 | 2808 | 5.7906 | 1 | 5.7906 | 2 | 5.7906 | 2
115 | Gym |  | 0 |  |  | 4693 | 106 | 0 | House Fan | 8 | 37544 | 0 | 1.062 | 0 | 0 | 0 | 0
200 | Office |  | 0 |  |  | 168 | 3 | 0 | House Fan | 8 | 1344 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom |  | 0 |  |  | 726 | 16 | 0 | House Fan | 8 | 5808 | 0 | 1 | 0 | 0 | 0 | 0
202 | Classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
203 | Classroom |  | 0 |  |  | 731 | 16 | 0 | House Fan | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
204 | Classroom |  | 0 |  |  | 718 | 16 | 0 | House Fan | 8 | 5744 | 0 | 1 | 0 | 0 | 0 | 0
204A | Office |  | 0 |  |  | 322 | 7 | 0 | House Fan | 8 | 2576 | 0 | 1 | 0 | 0 | 0 | 0
204B | Office |  | 0 | Yes | 20 | 150 | 3 | 3 | N/A | 8 | 1200 | 0 | 1 | 0 | 0 | 20 | 3
204C | Office |  | 0 |  |  | 84 | 1 | 0 | N/A | 8 | 672 | 0 | 1 | 0 | 0 | 0 | 0
205 | Classroom |  | 0 |  |  | 698 | 15 | 0 | House Fan | 8 | 5584 | 0 | 1 | 0 | 0 | 0 | 0
206 | Classroom |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom |  | 0 |  |  | 698 | 15 | 0 | House Fan | 8 | 5584 | 0 | 1 | 0 | 0 | 0 | 0
208 | Classroom |  | 0 |  |  | 643 | 14 | 0 | House Fan | 8 | 5144 | 0 | 1 | 0 | 0 | 0 | 0
212 | Classroom | 48 | 3 |  |  | 398 | 9 | 3 | Univent | 8 | 3184 | 0.90452 | 1 | 0.90452 | 0 | 0.90452 | 0
213 | Classroom | 194 | 12 |  |  | 742 | 16 | 12 | Univent | 8 | 5936 | 1.9609 | 1 | 1.9609 | 1 | 1.9609 | 1
214 | Classroom | 197 | 13 |  |  | 864 | 19 | 13 | Univent | 8 | 6912 | 1.7101 | 1 | 1.7101 | 1 | 1.7101 | 1
215 | Office | 0 | 0 |  |  | 100 | 2 | 0 | Univent | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
216 | Classroom | 411 | 27 |  |  | 762 | 17 | 17 | Univent | 8 | 6096 | 4.0453 | 1 | 4.0453 | 2 | 4.0453 | 2
217 | Classroom | 365 | 24 |  |  | 734 | 16 | 16 | Univent | 8 | 5872 | 3.7296 | 1 | 3.7296 | 1 | 3.7296 | 1
218 | Office / Classroom | 269 | 17 |  |  | 356 | 8 | 8 | Univent | 8 | 2848 | 5.6671 | 1 | 5.6671 | 2 | 5.6671 | 2
300 | Classroom |  | 0 |  |  | 644 | 14 | 0 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 0 | 0
301a | Office |  | 0 |  |  | 163 | 3 | 0 | House Fan | 8 | 1304 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom |  | 0 |  |  | 688 | 15 | 0 | House Fan | 8 | 5504 | 0 | 1 | 0 | 0 | 0 | 0
303 | Classroom |  | 0 |  |  | 736 | 16 | 0 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 0 | 0
304 | Classroom |  | 0 |  |  | 666 | 15 | 0 | House Fan | 8 | 5328 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom |  | 0 |  |  | 1085 | 24 | 0 | House Fan | 8 | 8680 | 0 | 1 | 0 | 0 | 0 | 0
306A | Library |  | 0 |  |  | 1166 | 26 | 0 | House Fan | 8 | 9328 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom |  | 0 |  |  | 687 | 15 | 0 | House Fan | 8 | 5496 | 0 | 1 | 0 | 0 | 0 | 0
308 | Classroom |  | 0 |  |  | 798 | 18 | 0 | House Fan | 8 | 6384 | 0 | 1 | 0 | 0 | 0 | 0
312 | Classroom | 224 | 14 |  |  | 1070 | 24 | 14 | Rooftop Unit | 8 | 8560 | 1.5701 | 1 | 1.5701 | 1 | 1.5701 | 1
313 | Classroom | 0 | 0 |  |  | 944 | 21 | 0 | Rooftop Unit | 8 | 7552 | 0 | 1 | 0 | 0 | 0 | 0
314 | Classroom | 332 | 22 |  |  | 1117 | 25 | 22 | Rooftop Unit | 8 | 8936 | 2.2292 | 1 | 2.2292 | 1 | 2.2292 | 1
314 | Office | 0 | 0 |  |  | 372 | 8 | 0 | Univent | 8 | 2976 | 0 | 1 | 0 | 0 | 0 | 0
314A | Office |  | 0 |  |  | 372 | 8 | 0 | House Fan | 8 | 2976 | 0 | 1 | 0 | 0 | 0 | 0
315A | Teacher's Lounge | 0 | 0 |  |  | 294 | 6 | 0 | Univent | 8 | 2352 | 0 | 1 | 0 | 0 | 0 | 0
316 | Office / Classroom | 130 | 8 |  |  | 356 | 8 | 8 | Rooftop Unit | 8 | 2848 | 2.7388 | 1 | 2.7388 | 1 | 2.7388 | 1
- | Auditorium |  | 0 |  |  | 3657 | 83 | 0 | House Fan | 8 | 29256 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Gym | 857 | 57 |  |  | 4693 | 106 | 57 | Univent | 8 | 37544 | 1.3696 | 1.062 | 1.4546 | 1 | 1.4546 | 1
- | Lunch Rm |  | 0 |  |  | 4331 | 98 | 0 | House Fan | 8 | 34648 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Main Office |  | 0 | Yes | 20 | 395 | 8 | 8 | House Fan | 8 | 3160 | 0 | 1 | 0 | 0 | 20 | 3
- | Principals Office |  | 0 | Yes | 20 | 269 | 6 | 6 | House Fan | 8 | 2152 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-23
School: | Thomas G. Morton Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 0 | 0 | Yes | 20 | 988 | 22 | 22 | Univent | 8 | 7904 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom | 0 | 0 | Yes | 20 | 875 | 19 | 19 | Univent | 8 | 7000 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom | 374 | 24 |  |  | 792 | 18 | 18 | Air Coil Unit | 8 | 6336 | 3.5417 | 1 | 3.5417 | 1 | 3.5417 | 1
104B | Storage | 77 | 5 |  |  | 84 | 1 | 1 | Univent | 8 | 672 | 6.875 | 1 | 6.875 | 2 | 6.875 | 2
108A | Nurse Office | 125 | 8 |  |  | 90 | 2 | 2 | Univent | 8 | 720 | 10.4167 | 1 | 10.4167 | 3 | 10.4167 | 3
108B | Audio | 40 | 2 |  |  | 224 | 5 | 2 | Univent | 8 | 1792 | 1.3393 | 1 | 1.3393 | 1 | 1.3393 | 1
108C | Examination | 36 | 2 |  |  | 234 | 5 | 2 | Univent | 8 | 1872 | 1.1538 | 1 | 1.1538 | 1 | 1.1538 | 1
110 | Classroom | 0 | 0 |  |  | 513 | 11 | 0 | Univent | 8 | 4104 | 0 | 1 | 0 | 0 | 0 | 0
111 | Classroom | 309 | 20 | Yes | 20 | 252 | 5 | 5 | Univent | 8 | 2016 | 9.1964 | 1 | 9.1964 | 2 | 29.1964 | 4
200 | Classroom | 0 | 0 | Yes | 20 | 1071 | 24 | 24 | Univent | 8 | 8568 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 20 | 754 | 17 | 17 | Univent | 8 | 6032 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 432 | 28 | Yes | 20 | 754 | 17 | 17 | Univent | 8 | 6032 | 4.2971 | 1 | 4.2971 | 2 | 24.2971 | 4
203 | Classroom | 475 | 31 |  |  | 8112 | 184 | 31 | Univent | 8 | 64896 | 0.43916 | 1.4912 | 0.65486 | 0 | 0.65486 | 0
204 | Classroom | 399 | 26 |  |  | 438 | 9 | 9 | Univent | 8 | 3504 | 6.8322 | 1 | 6.8322 | 2 | 6.8322 | 2
205 | Classroom | 0 | 0 | Yes | 20 | 1015 | 23 | 23 | Univent | 8 | 8120 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom | 0 | 0 | Yes | 20 | 1305 | 29 | 29 | Univent | 8 | 10440 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom | 0 | 0 | Yes | 20 | 1305 | 29 | 29 | Univent | 8 | 10440 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 329 | 21 | Yes | 20 | 1015 | 23 | 23 | Univent | 8 | 8120 | 2.431 | 1 | 2.431 | 1 | 22.431 | 3
209 | Classroom | 280 | 18 | Yes | 20 | 408 | 9 | 9 | Univent | 8 | 3264 | 5.1471 | 1 | 5.1471 | 2 | 25.1471 | 4
210 | Classroom | 0 | 0 | Yes | 20 | 725 | 16 | 16 | Univent | 8 | 5800 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom | 0 | 0 | Yes | 20 | 841 | 19 | 19 | Univent | 8 | 6728 | 0 | 1 | 0 | 0 | 20 | 3
212 | Classroom | 0 | 0 | Yes | 20 | 264 | 6 | 6 | Univent | 8 | 2112 | 0 | 1 | 0 | 0 | 20 | 3
213 | Classroom | 437 | 29 |  |  | 725 | 16 | 16 | Univent | 8 | 5800 | 4.5207 | 1 | 4.5207 | 2 | 4.5207 | 2
214A | Classroom | 94 | 6 |  |  | 190 | 4 | 4 | Univent | 8 | 1520 | 3.7105 | 1 | 3.7105 | 1 | 3.7105 | 1
214B | Classroom | 162 | 10 |  |  | 624 | 14 | 10 | Univent | 8 | 4992 | 1.9471 | 1 | 1.9471 | 1 | 1.9471 | 1
300 | Classroom | 309 | 20 |  |  | 780 | 17 | 17 | Univent | 8 | 6240 | 2.9712 | 1 | 2.9712 | 1 | 2.9712 | 1
301 | Classroom | 0 | 0 |  |  | 725 | 16 | 0 | Univent | 8 | 5800 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom | 685 | 45 |  |  | 240 | 5 | 5 | Univent | 8 | 1920 | 21.4062 | 1 | 21.4062 | 3 | 21.4062 | 3
303 | Classroom | 486 | 32 |  |  | 754 | 17 | 17 | Univent | 8 | 6032 | 4.8342 | 1 | 4.8342 | 2 | 4.8342 | 2
304 | Classroom | 448 | 29 | Yes | 20 | 725 | 16 | 16 | Univent | 8 | 5800 | 4.6345 | 1 | 4.6345 | 2 | 24.6345 | 4
305 | Classroom | 291 | 19 |  |  | 312 | 7 | 7 | Univent | 8 | 2496 | 6.9952 | 1 | 6.9952 | 2 | 6.9952 | 2
306 | Classroom | 483 | 32 | Yes | 20 | 754 | 17 | 17 | Univent | 8 | 6032 | 4.8044 | 1 | 4.8044 | 2 | 24.8044 | 4
307 | Classroom | 415 | 27 | Yes | 20 | 756 | 17 | 17 | Univent | 8 | 6048 | 4.1171 | 1 | 4.1171 | 2 | 24.1171 | 4
308 | Library | 1124 | 74 |  |  | 2975 | 67 | 67 | Univent | 8 | 23800 | 2.8336 | 1.062 | 3.0094 | 1 | 3.0094 | 1
308 | Library Office | 0 | 0 |  |  | 462 | 10 | 0 | Univent | 8 | 3696 | 0 | 1 | 0 | 0 | 0 | 0
309 | Classroom | 283 | 18 | Yes | 20 | 806 | 18 | 18 | Univent | 8 | 6448 | 2.6334 | 1 | 2.6334 | 1 | 22.6334 | 3
310 | Classroom | 628 | 41 |  |  | 700 | 15 | 15 | Univent | 8 | 5600 | 6.7286 | 1 | 6.7286 | 2 | 6.7286 | 2
311 | Classroom | 294 | 19 |  |  | 754 | 17 | 17 | Univent | 8 | 6032 | 2.9244 | 1 | 2.9244 | 1 | 2.9244 | 1
312 | Classroom | 349 | 23 |  |  | 754 | 17 | 17 | Univent | 8 | 6032 | 3.4715 | 1 | 3.4715 | 1 | 3.4715 | 1
313 | Classroom | 547 | 36 |  |  | 486 | 11 | 11 | Univent | 8 | 3888 | 8.4414 | 1 | 8.4414 | 2 | 8.4414 | 2
315 | Classroom | 544 | 36 |  |  | 754 | 17 | 17 | Univent | 8 | 6032 | 5.4111 | 1 | 5.4111 | 2 | 5.4111 | 2
316 | Classroom | 324 | 21 |  |  | 754 | 17 | 17 | Univent | 8 | 6032 | 3.2228 | 1 | 3.2228 | 1 | 3.2228 | 1
317 | Classroom | 431 | 28 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 3.7155 | 1 | 3.7155 | 1 | 3.7155 | 1
318 | Classroom | 305 | 20 |  |  | 312 | 7 | 7 | Univent | 8 | 2496 | 7.3317 | 1 | 7.3317 | 2 | 7.3317 | 2
319 | Classroom | 0 | 0 | Yes | 20 | 650 | 14 | 14 | Univent | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
320 | Classroom | 431 | 28 |  |  | 728 | 16 | 16 | Univent | 8 | 5824 | 4.4402 | 1 | 4.4402 | 2 | 4.4402 | 2
- | Auditorium | 5700 | 380 |  |  | 2646 | 60 | 60 | Air Coil Unit | 8 | 21168 | 16.1565 | 1.062 | 17.1587 | 3 | 17.1587 | 3
- | Cafeteria | 2196 | 146 | Yes | 20 | 2726 | 61 | 61 | Air Coil Unit | 8 | 21808 | 6.0418 | 1.062 | 6.4166 | 2 | 26.4166 | 4
- | Conference | 83 | 5 |  |  | 171 | 3 | 3 | Univent | 8 | 1368 | 3.6404 | 1 | 3.6404 | 1 | 3.6404 | 1
- | Counselors Office A | 87 | 5 |  |  | 99 | 2 | 2 | Univent | 8 | 792 | 6.5909 | 1 | 6.5909 | 2 | 6.5909 | 2
- | Counselors Office B | 91 | 6 |  |  | 128 | 2 | 2 | Univent | 8 | 1024 | 5.332 | 1 | 5.332 | 2 | 5.332 | 2
- | Counselors Office C | 148 | 9 |  |  | 100 | 2 | 2 | Univent | 8 | 800 | 11.1 | 1 | 11.1 | 3 | 11.1 | 3
- | Gym | 1927 | 128 |  |  | 4640 | 105 | 105 | Air Coil Unit | 8 | 37120 | 3.1148 | 1.062 | 3.308 | 1 | 3.308 | 1
- | Lounge | 311 | 20 |  |  | 351 | 7 | 7 | Univent | 8 | 2808 | 6.6453 | 1 | 6.6453 | 2 | 6.6453 | 2
- | Main Office | 285 | 19 |  |  | 380 | 8 | 8 | Univent | 8 | 3040 | 5.625 | 1 | 5.625 | 2 | 5.625 | 2
- | Copy Room | 53 | 3 |  |  | 60 | 1 | 1 | Univent | 8 | 480 | 6.625 | 1 | 6.625 | 2 | 6.625 | 2
- | Nurse | 83 | 5 |  |  | 123 | 2 | 2 | Univent | 8 | 984 | 5.061 | 1 | 5.061 | 2 | 5.061 | 2
- | Principal Office | 159 | 10 |  |  | 228 | 5 | 5 | Univent | 8 | 1824 | 5.2303 | 1 | 5.2303 | 2 | 5.2303 | 2
- | Vice Principal Office | 54 | 3 |  |  | 99 | 2 | 2 | Univent | 8 | 792 | 4.0909 | 1 | 4.0909 | 2 | 4.0909 | 2
Sheet Last Modified: | 2021-04-29
School: | Motivation High School KIPP Turner West Middle School
Vendor: | Capital
Vendor: | Devine | Devine Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
A-PreK Corridor | Corridor | 314 | 20 |  |  | 600 | 13 | 13 | Univent | 8 | 4800 | 3.925 | 1 | 3.925 | 1 | 3.925 | 1
A-PreK North Entrance-A | Corridor | 490 | 32 |  |  | 243 | 5 | 5 | Univent | 8 | 1944 | 15.1235 | 1 | 15.1235 | 3 | 15.1235 | 3
A-PreK North Entrance-B | Corridor | 548 | 36 |  |  | 480 | 10 | 10 | Univent | 8 | 3840 | 8.5625 | 1 | 8.5625 | 2 | 8.5625 | 2
A-PreK South Corridor | Corridor | 324 | 21 |  |  | 550 | 12 | 12 | Univent | 8 | 4400 | 4.4182 | 1 | 4.4182 | 2 | 4.4182 | 2
A-Wing Head Start Mech. Rm | Head Start PreK A169 & A170 | 349 | 23 |  |  | 1440 | 32 | 23 | Air Handling Unit | 8 | 11520 | 1.8177 | 1 | 1.8177 | 1 | 1.8177 | 1
A-Wing-Café Mech. Rm | 2nd & 3rd Flr. Staff Seminar Rms | 1734 | 115 |  |  |  | 0 | 0 | Air Handling Unit
A-Wing-Café Mech. Rm | 3rd Flr |  | 0 |  |  | 50 | 1 | 0 | Air Handling Unit | 8 | 400 | 0 | 1 | 0 | 0 | 0 | 0
A-Wing-Café Mech. Rm | 2nd Flr |  | 0 |  |  | 50 | 1 | 0 | Air Handling Unit | 8 | 400 | 0 | 1 | 0 | 0 | 0 | 0
A-Wing-Café Mech. Rm | Ground Flr. Administration | 351 | 23 |  |  |  | 0 | 0 | Air Handling Unit
A130 | Gym | 410 | 27 |  |  | 2552 | 58 | 27 | Heating Ventilation Unit | 8 | 20416 | 1.2049 | 1.062 | 1.2797 | 1 | 1.2797 | 1
A108 Locker Rm | A108 | 0 | 0 |  |  |  | 0 | 0 | Heating Ventilation Unit
A152 Locker Rm | A152 | 1340 | 89 |  |  | 690 | 15 | 15 | Heating Ventilation Unit | 8 | 5520 | 14.5652 | 1 | 14.5652 | 3 | 14.5652 | 3
A162 Storage | A154 Corrective Gym | 306 | 20 |  |  | 5192 | 118 | 20 | Heating Ventilation Unit | 8 | 41536 | 0.44203 | 1.062 | 0.46945 | 0 | 0.46945 | 0
A165 | Storage | 0 | 0 |  |  | 5192 | 118 | 0 | Heating Ventilation Unit | 8 | 41536 | 0 | 1.062 | 0 | 0 | 0 | 0
B-157 | B-155 Fitness Rm | 1593 | 106 |  |  | 1150 | 26 | 26 | Univent | 8 | 9200 | 10.3891 | 1 | 10.3891 | 3 | 10.3891 | 3
MER Rm B146 | B-Wing | 555 | 37 |  |  | 1012 | 23 | 23 | Air Handling Unit | 8 | 8096 | 4.1131 | 1 | 4.1131 | 2 | 4.1131 | 2
B-Wing B137 | B-139 A, B, C, D | 2003 | 133 |  |  | 4134 | 93 | 93 | Air Handling Unit | 8 | 33072 | 3.6339 | 1.062 | 3.8593 | 1 | 3.8593 | 1
B101 Cafeteria | B-Wing Roof | 320 | 21 |  |  | 9405 | 213 | 21 | Air Handling Unit | 8 | 75240 | 0.25518 | 1.4912 | 0.38052 | 0 | 0.38052 | 0
House Coord North 3rd & 2nd Flr | B-Wing Roof | 67 | 4 |  |  |  | 0 | 0 | Air Handling Unit
B318 | B-Wing Roof |  | 0 |  |  | 800 | 18 | 0 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
B218 | B-Wing Roof |  | 0 |  |  | 800 | 18 | 0 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
House Coord South 3rd & 2nd Flr | B-Wing Roof | 126 | 8 |  |  |  | 0 | 0 | Air Handling Unit
B306 | B-Wing Roof |  | 0 |  |  | 800 | 18 | 0 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
B206 | B-Wing Roof |  | 0 |  |  | 800 | 18 | 0 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
B325 IMC Library | B-Wing Roof | 7 | 0 |  |  | 851 | 19 | 0 | Air Handling Unit | 8 | 6808 | 0.061692 | 1 | 0.061692 | 0 | 0.061692 | 0
139A | Classroom |  | 0 |  |  | 880 | 20 | 0 |  | 8 | 7040 | 0 | 1 | 0 | 0 | 0 | 0
139B | Classroom |  | 0 |  |  | 987 | 22 | 0 |  | 8 | 7896 | 0 | 1 | 0 | 0 | 0 | 0
139C | Classroom |  | 0 |  |  | 884 | 20 | 0 |  | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
139D | Classroom |  | 0 |  |  | 1035 | 23 | 0 |  | 8 | 8280 | 0 | 1 | 0 | 0 | 0 | 0
151 | Classroom |  | 0 | Yes | 20 | 1824 | 41 | 41 |  | 8 | 14592 | 0 | 1 | 0 | 0 | 20 | 3
152 | Classroom |  | 0 | Yes | 20 | 1170 | 26 | 26 |  | 8 | 9360 | 0 | 1 | 0 | 0 | 20 | 3
B196 | Classroom | 376 | 25 |  |  | 567 | 12 | 12 | Univent | 8 | 4536 | 4.9735 | 1 | 4.9735 | 2 | 4.9735 | 2
B197 | Classroom | 755 | 50 |  |  | 962 | 21 | 21 | Univent | 8 | 7696 | 5.8862 | 1 | 5.8862 | 2 | 5.8862 | 2
B198 | Classroom | 739 | 49 |  |  | 792 | 18 | 18 | Univent | 8 | 6336 | 6.9981 | 1 | 6.9981 | 2 | 6.9981 | 2
B200 | Classroom | 1468 | 97 |  |  | 1564 | 35 | 35 | Univent | 8 | 12512 | 7.0396 | 1 | 7.0396 | 2 | 7.0396 | 2
B201 | Classroom | 673 | 44 |  |  | 850 | 19 | 19 | Univent | 8 | 6800 | 5.9382 | 1 | 5.9382 | 2 | 5.9382 | 2
B202 | Classroom | 172 | 11 |  |  | 748 | 17 | 11 | Univent | 8 | 5984 | 1.7246 | 1 | 1.7246 | 1 | 1.7246 | 1
B203 | Classroom | 673 | 44 |  |  | 748 | 17 | 17 | Univent | 8 | 5984 | 6.748 | 1 | 6.748 | 2 | 6.748 | 2
B204 | Classroom | 143 | 9 |  |  | 759 | 17 | 9 | Univent | 8 | 6072 | 1.413 | 1 | 1.413 | 1 | 1.413 | 1
B205 | Classroom | 555 | 37 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 5.7812 | 1 | 5.7812 | 2 | 5.7812 | 2
B207 | Classroom | 629 | 41 |  |  | 748 | 17 | 17 | Univent | 8 | 5984 | 6.3068 | 1 | 6.3068 | 2 | 6.3068 | 2
B208 | Classroom | 640 | 42 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 6.3241 | 1 | 6.3241 | 2 | 6.3241 | 2
B209 | Classroom | 108 | 7 |  |  | 816 | 18 | 7 | Univent | 8 | 6528 | 0.99265 | 1 | 0.99265 | 0 | 0.99265 | 0
B210 | Classroom | 630 | 42 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 6.5625 | 1 | 6.5625 | 2 | 6.5625 | 2
B211 | Classroom | 350 | 23 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 3.6458 | 1 | 3.6458 | 1 | 3.6458 | 1
B212 | Classroom | 538 | 35 |  |  | 1326 | 30 | 30 | Univent | 8 | 10608 | 3.043 | 1 | 3.043 | 1 | 3.043 | 1
B213 | Classroom | 244 | 16 |  |  | 759 | 17 | 16 | Univent | 8 | 6072 | 2.4111 | 1 | 2.4111 | 1 | 2.4111 | 1
B214 | Classroom | 0 | 0 |  |  | 759 | 17 | 0 | Univent | 8 | 6072 | 0 | 1 | 0 | 0 | 0 | 0
B215 | Classroom | 341 | 22 |  |  | 748 | 17 | 17 | Univent | 8 | 5984 | 3.4191 | 1 | 3.4191 | 1 | 3.4191 | 1
B216 | Classroom | 339 | 22 |  |  | 748 | 17 | 17 | Univent | 8 | 5984 | 3.3991 | 1 | 3.3991 | 1 | 3.3991 | 1
B217 | Classroom | 273 | 18 |  |  | 624 | 14 | 14 | Univent | 8 | 4992 | 3.2812 | 1 | 3.2812 | 1 | 3.2812 | 1
B219 | Classroom | 378 | 25 |  |  | 748 | 17 | 17 | Univent | 8 | 5984 | 3.7901 | 1 | 3.7901 | 1 | 3.7901 | 1
B220 | Classroom | 242 | 16 |  |  | 759 | 17 | 16 | Univent | 8 | 6072 | 2.3913 | 1 | 2.3913 | 1 | 2.3913 | 1
B221 | Classroom | 456 | 30 |  |  | 816 | 18 | 18 | Univent | 8 | 6528 | 4.1912 | 1 | 4.1912 | 2 | 4.1912 | 2
B222 | Classroom | 633 | 42 |  |  | 598 | 13 | 13 | Univent | 8 | 4784 | 7.939 | 1 | 7.939 | 2 | 7.939 | 2
B223 | Classroom | 642 | 42 |  |  | 690 | 15 | 15 | Univent | 8 | 5520 | 6.9783 | 1 | 6.9783 | 2 | 6.9783 | 2
B301 | Classroom | 200 | 13 |  |  | 850 | 19 | 13 | Univent | 8 | 6800 | 1.7647 | 1 | 1.7647 | 1 | 1.7647 | 1
B302 | Classroom | 129 | 8 |  |  | 748 | 17 | 8 | Univent | 8 | 5984 | 1.2934 | 1 | 1.2934 | 1 | 1.2934 | 1
B304 | Classroom | 630 | 42 |  |  | 1564 | 35 | 35 | Univent | 8 | 12512 | 3.0211 | 1 | 3.0211 | 1 | 3.0211 | 1
B305 | Classroom | 150 | 10 |  |  | 720 | 16 | 10 | Univent | 8 | 5760 | 1.5625 | 1 | 1.5625 | 1 | 1.5625 | 1
306 | Classroom |  | 0 | Yes | 20 | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
B307 | Classroom | 193 | 12 |  |  | 748 | 17 | 12 | Univent | 8 | 5984 | 1.9352 | 1 | 1.9352 | 1 | 1.9352 | 1
B308 | Classroom | 110 | 7 |  |  | 759 | 17 | 7 | Univent | 8 | 6072 | 1.087 | 1 | 1.087 | 1 | 1.087 | 1
B309 | Classroom | 186 | 12 |  |  | 816 | 18 | 12 | Univent | 8 | 6528 | 1.7096 | 1 | 1.7096 | 1 | 1.7096 | 1
B310 | Classroom | 196 | 13 |  |  | 720 | 16 | 13 | Univent | 8 | 5760 | 2.0417 | 1 | 2.0417 | 1 | 2.0417 | 1
B311 | Classroom | 222 | 14 |  |  | 720 | 16 | 14 | Univent | 8 | 5760 | 2.3125 | 1 | 2.3125 | 1 | 2.3125 | 1
B312 | Classroom | 691 | 46 |  |  | 1326 | 30 | 30 | Univent | 8 | 10608 | 3.9084 | 1 | 3.9084 | 1 | 3.9084 | 1
B313 | Classroom | 264 | 17 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 2.6087 | 1 | 2.6087 | 1 | 2.6087 | 1
B314 | Classroom | 436 | 29 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 4.3083 | 1 | 4.3083 | 2 | 4.3083 | 2
B315 | Classroom | 198 | 13 |  |  | 748 | 17 | 13 | Univent | 8 | 5984 | 1.9853 | 1 | 1.9853 | 1 | 1.9853 | 1
B316 | Classroom | 160 | 10 |  |  | 748 | 17 | 10 | Univent | 8 | 5984 | 1.6043 | 1 | 1.6043 | 1 | 1.6043 | 1
B317 | Classroom | 198 | 13 |  |  | 624 | 14 | 13 | Univent | 8 | 4992 | 2.3798 | 1 | 2.3798 | 1 | 2.3798 | 1
318 | Classroom |  | 0 | Yes | 20 | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
B319 | Classroom | 304 | 20 |  |  | 748 | 17 | 17 | Univent | 8 | 5984 | 3.0481 | 1 | 3.0481 | 1 | 3.0481 | 1
B320 | Classroom | 144 | 9 |  |  | 759 | 17 | 9 | Univent | 8 | 6072 | 1.4229 | 1 | 1.4229 | 1 | 1.4229 | 1
B321 | Classroom | 290 | 19 |  |  | 816 | 18 | 18 | Univent | 8 | 6528 | 2.6654 | 1 | 2.6654 | 1 | 2.6654 | 1
B322 | Classroom | 213 | 14 |  |  | 598 | 13 | 13 | Univent | 8 | 4784 | 2.6714 | 1 | 2.6714 | 1 | 2.6714 | 1
B323 | Classroom | 156 | 10 |  |  | 690 | 15 | 10 | Univent | 8 | 5520 | 1.6957 | 1 | 1.6957 | 1 | 1.6957 | 1
B324 | Classroom | 577 | 38 |  |  | 1435 | 32 | 32 | Univent | 8 | 11480 | 3.0157 | 1 | 3.0157 | 1 | 3.0157 | 1
Main Office | Main Office |  | 0 | Yes | 20 | 950 | 21 | 21 |  | 8 | 7600 | 0 | 1 | 0 | 0 | 20 | 3
Teachers Lounge | Lounge |  | 0 | Yes | 20 | 728 | 16 | 16 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 20 | 3
Nurse | Office |  | 0 | Yes | 20 | 910 | 20 | 20 |  | 8 | 7280 | 0 | 1 | 0 | 0 | 20 | 3
C-Wing | Auditorium | 346 | 23 | Yes | 20 | 1476 | 33 | 33 | Air Handling Unit | 8 | 11808 | 1.7581 | 1 | 1.7581 | 1 | 21.7581 | 3
Music Rm
C-Wing | Auditorium Comm. Rm. | 1811 | 120 |  |  | 7392 | 168 | 120 | Air Handling Unit | 8 | 59136 | 1.8375 | 1.4912 | 2.7399 | 1 | 2.7399 | 1
C-Wing | Auditorium/ Auditorium Stage | 3862 | 257 |  |  | 1890 | 42 | 42 | Air Handling Unit | 8 | 15120 | 15.3254 | 1 | 15.3254 | 3 | 15.3254 | 3
Head Start | B110 Learning Lab & B104 Student Store | 457 | 30 |  |  | 81 | 1 | 1 | Air Handling Unit | 8 | 648 | 42.3148 | 1 | 42.3148 | 4 | 42.3148 | 4
Mech Rm.
Sheet Last Modified: | 2021-05-03
School: | Luis Munoz – Marin Elementary School
Vendor: | Chadwick
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100B | CORRIDOR | 149 | 9 |  |  | 618 | 14 | 9 | Air Handling Unit | 8 | 4944 | 1.8083 | 1 | 1.8083 | 1 | 1.8083 | 1
100E | CORRIDOR | 115 | 7 |  |  | 1780 | 40 | 7 | Air Handling Unit | 8 | 14240 | 0.48455 | 1 | 0.48455 | 0 | 0.48455 | 0
100F | CORRIDOR | 250 | 16 |  |  | 1210 | 27 | 16 | Air Handling Unit | 8 | 9680 | 1.5496 | 1 | 1.5496 | 1 | 1.5496 | 1
100G | CORRIDOR | 142 | 9 |  |  | 1404 | 31 | 9 | Air Handling Unit | 8 | 11232 | 0.75855 | 1 | 0.75855 | 0 | 0.75855 | 0
100H | CORRIDOR |  | 0 |  |  | 1780 | 40 | 0 | Air Handling Unit | 8 | 14240 | 0 | 1 | 0 | 0 | 0 | 0
102 | Classroom | 193 | 12 |  |  | 792 | 18 | 12 | Air Handling Unit | 8 | 6336 | 1.8277 | 1 | 1.8277 | 1 | 1.8277 | 1
104 | Classroom | 225 | 15 | Yes | 20 | 805 | 18 | 18 | Air Handling Unit | 8 | 6440 | 2.0963 | 1 | 2.0963 | 1 | 22.0963 | 3
105 | Classroom | 195 | 13 | Yes | 20 | 713 | 16 | 16 | Air Handling Unit | 8 | 5704 | 2.0512 | 1 | 2.0512 | 1 | 22.0512 | 3
106 | Classroom | 213 | 14 | Yes | 20 | 713 | 16 | 16 | Air Handling Unit | 8 | 5704 | 2.2405 | 1 | 2.2405 | 1 | 22.2405 | 3
107 | Classroom | 170 | 11 | Yes | 20 | 682 | 15 | 15 | Air Handling Unit | 8 | 5456 | 1.8695 | 1 | 1.8695 | 1 | 21.8695 | 3
108 | Classroom | 202 | 13 | Yes | 20 | 682 | 15 | 15 | Air Handling Unit | 8 | 5456 | 2.2214 | 1 | 2.2214 | 1 | 22.2214 | 3
109 | Classroom | 227 | 15 |  |  | 682 | 15 | 15 | Air Handling Unit | 8 | 5456 | 2.4963 | 1 | 2.4963 | 1 | 2.4963 | 1
110 | Classroom | 212 | 14 | Yes | 20 | 682 | 15 | 15 | Air Handling Unit | 8 | 5456 | 2.3314 | 1 | 2.3314 | 1 | 22.3314 | 3
111 | Classroom | 469 | 31 |  |  | 700 | 15 | 15 | Air Handling Unit | 8 | 5600 | 5.025 | 1 | 5.025 | 2 | 5.025 | 2
115 | LOBBY | 648 | 43 |  |  | 1368 | 31 | 31 | Air Handling Unit | 8 | 10944 | 3.5526 | 1 | 3.5526 | 1 | 3.5526 | 1
116 | - | 215 | 14 |  |  | 609 | 13 | 13 | Air Handling Unit | 8 | 4872 | 2.6478 | 1 | 2.6478 | 1 | 2.6478 | 1
118 | - | 177 | 11 | Yes | 20 | 672 | 15 | 15 | Air Handling Unit | 8 | 5376 | 1.9754 | 1 | 1.9754 | 1 | 21.9754 | 3
120 | - | 188 | 12 | Yes | 20 | 768 | 17 | 17 | Air Handling Unit | 8 | 6144 | 1.8359 | 1 | 1.8359 | 1 | 21.8359 | 3
121 | HEALTH | 87 | 5 |  |  | 816 | 18 | 5 | Air Handling Unit | 8 | 6528 | 0.79963 | 1 | 0.79963 | 0 | 0.79963 | 0
124A | OFFICE | 19 | 1 |  |  | 120 | 2 | 1 | Air Handling Unit | 8 | 960 | 1.1875 | 1 | 1.1875 | 1 | 1.1875 | 1
125 | SPE. | 17 | 1 | Yes | 20 | 336 | 7 | 7 | Air Handling Unit | 8 | 2688 | 0.37946 | 1 | 0.37946 | 0 | 20.3795 | 3
125 | OCC | 51 | 3 |  |  | 272 | 6 | 3 | Air Handling Unit | 8 | 2176 | 1.4062 | 1 | 1.4062 | 1 | 1.4062 | 1
126 | FAM MGMT | 272 | 18 |  |  | 1215 | 27 | 18 | Air Handling Unit | 8 | 9720 | 1.679 | 1 | 1.679 | 1 | 1.679 | 1
127 | CLASSROOM | 56 | 3 |  |  | 670 | 15 | 3 | Air Handling Unit | 8 | 5360 | 0.62687 | 1 | 0.62687 | 0 | 0.62687 | 0
127B |  | 15 |  |  |  | 39 |  | 0 | Air Handling Unit | 8 | 312 |  | 1 | #VALUE! | #VALUE! | 2.8846
127C |  | 18 |  |  |  | 149 |  | 0 | Air Handling Unit | 8 | 1192 |  | 1 | #VALUE! | #VALUE! | 0.90604
160 | Classroom | 27 | 1 |  |  | 39 | 0 | 0 | Air Handling Unit | 8 | 312 | 5.1923 | 1 | 5.1923 | 2 | 5.1923 | 2
161 | Classroom | 33 | 2 |  |  | 375 | 8 | 2 | Air Handling Unit | 8 | 3000 | 0.66 | 1 | 0.66 | 0 | 0.66 | 0
162 | Classroom | 55 | 3 |  |  | 114 | 2 | 2 | Air Handling Unit | 8 | 912 | 3.6184 | 1 | 3.6184 | 1 | 3.6184 | 1
163 | Classroom | 62 | 4 |  |  | 114 | 2 | 2 | Air Handling Unit | 8 | 912 | 4.0789 | 1 | 4.0789 | 2 | 4.0789 | 2
164 | Classroom | 33 | 2 |  |  | 117 | 2 | 2 | Air Handling Unit | 8 | 936 | 2.1154 | 1 | 2.1154 | 1 | 2.1154 | 1
166 | Classroom | 23 | 1 |  |  | 102 | 2 | 1 | Air Handling Unit | 8 | 816 | 1.6912 | 1 | 1.6912 | 1 | 1.6912 | 1
168 | Classroom | 33 | 2 |  |  | 109 | 2 | 2 | Air Handling Unit | 8 | 872 | 2.2706 | 1 | 2.2706 | 1 | 2.2706 | 1
169 | Classroom | 23 | 1 |  |  | 81 | 1 | 1 | Air Handling Unit | 8 | 648 | 2.1296 | 1 | 2.1296 | 1 | 2.1296 | 1
170 | Classroom | 35 | 2 |  |  | 134 | 3 | 2 | Air Handling Unit | 8 | 1072 | 1.959 | 1 | 1.959 | 1 | 1.959 | 1
171 | OFFICE | 223 | 14 |  |  | 148 | 3 | 3 | Air Handling Unit | 8 | 1184 | 11.3007 | 1 | 11.3007 | 3 | 11.3007 | 3
172 | - | 58 | 3 |  |  | 148 | 3 | 3 | Air Handling Unit | 8 | 1184 | 2.9392 | 1 | 2.9392 | 1 | 2.9392 | 1
173 | PRINCIPAL | 87 | 5 |  |  | 304 | 6 | 5 | Air Handling Unit | 8 | 2432 | 2.1464 | 1 | 2.1464 | 1 | 2.1464 | 1
176 | - | 114 | 7 |  |  | 148 | 3 | 3 | Air Handling Unit | 8 | 1184 | 5.777 | 1 | 5.777 | 2 | 5.777 | 2
177 | - | 69 | 4 |  |  | 134 | 3 | 3 | Air Handling Unit | 8 | 1072 | 3.8619 | 1 | 3.8619 | 1 | 3.8619 | 1
180 | CONFR | 54 | 3 |  |  | 244 | 5 | 3 | Air Handling Unit | 8 | 1952 | 1.6598 | 1 | 1.6598 | 1 | 1.6598 | 1
181 | ASS PRINC | 100 | 6 |  |  | 188 | 4 | 4 | Air Handling Unit | 8 | 1504 | 3.9894 | 1 | 3.9894 | 1 | 3.9894 | 1
181A | OFFICE | 42 | 2 |  |  | 125 | 2 | 2 | Air Handling Unit | 8 | 1000 | 2.52 | 1 | 2.52 | 1 | 2.52 | 1
182 | - | 42 | 2 |  |  | 131 | 2 | 2 | Air Handling Unit | 8 | 1048 | 2.4046 | 1 | 2.4046 | 1 | 2.4046 | 1
183 | - | 42 | 2 |  |  | 97 | 2 | 2 | Air Handling Unit | 8 | 776 | 3.2474 | 1 | 3.2474 | 1 | 3.2474 | 1
200A | CORRIDOR | 160 | 10 |  |  | 1780 | 40 | 10 | Air Handling Unit | 8 | 14240 | 0.67416 | 1 | 0.67416 | 0 | 0.67416 | 0
200C | CORRIDOR | 148 | 9 |  |  | 1780 | 40 | 9 | Air Handling Unit | 8 | 14240 | 0.6236 | 1 | 0.6236 | 0 | 0.6236 | 0
200D | CORRIDOR | 240 | 16 |  |  | 1359 | 30 | 16 | Air Handling Unit | 8 | 10872 | 1.3245 | 1 | 1.3245 | 1 | 1.3245 | 1
200E | CORRIDOR | 100 | 6 |  |  | 1404 | 31 | 6 | Air Handling Unit | 8 | 11232 | 0.53419 | 1 | 0.53419 | 0 | 0.53419 | 0
200F | - | 156 | 10 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 11.7 | 1 | 11.7 | 3 | 11.7 | 3
201 | Classroom | 204 | 13 | Yes | 20 | 714 | 16 | 16 | Univent and Air Handling Unit | 8 | 5712 | 2.1429 | 1 | 2.1429 | 1 | 22.1429 | 3
202 | Classroom | 94 | 6 | Yes | 20 | 713 | 16 | 16 | Univent and Air Handling Unit | 8 | 5704 | 0.98878 | 1 | 0.98878 | 0 | 20.9888 | 3
203 | Classroom | 68 | 4 | Yes | 20 | 704 | 16 | 16 | Univent and Air Handling Unit | 8 | 5632 | 0.72443 | 1 | 0.72443 | 0 | 20.7244 | 3
204 | Classroom | 418 | 27 |  |  | 764 | 17 | 17 | Univent and Air Handling Unit | 8 | 6112 | 4.1034 | 1 | 4.1034 | 2 | 4.1034 | 2
205 | Classroom | 152 | 10 | Yes | 20 | 764 | 17 | 17 | Univent and Air Handling Unit | 8 | 6112 | 1.4921 | 1 | 1.4921 | 1 | 21.4921 | 3
206 | Classroom | 241 | 16 | Yes | 20 | 764 | 17 | 17 | Univent and Air Handling Unit | 8 | 6112 | 2.3658 | 1 | 2.3658 | 1 | 22.3658 | 3
207 | Classroom | 148 | 9 |  |  | 648 | 14 | 9 | Univent and Air Handling Unit | 8 | 5184 | 1.713 | 1 | 1.713 | 1 | 1.713 | 1
208 | IMC | 338 | 22 |  |  | 1757 | 39 | 22 | Air Handling Unit | 8 | 14056 | 1.4428 | 1 | 1.4428 | 1 | 1.4428 | 1
209 | Classroom | 272 | 18 |  |  | 648 | 14 | 14 | Univent and Air Handling Unit | 8 | 5184 | 3.1481 | 1 | 3.1481 | 1 | 3.1481 | 1
213 | Classroom | 155 | 10 |  |  | 764 | 17 | 10 | Univent and Air Handling Unit | 8 | 6112 | 1.5216 | 1 | 1.5216 | 1 | 1.5216 | 1
214 | Classroom | 140 | 9 |  |  | 118 | 2 | 2 | Univent | 8 | 944 | 8.8983 | 1 | 8.8983 | 2 | 8.8983 | 2
214 | IMC | 311 | 20 |  |  | 1405 | 31 | 20 | Air Handling Unit | 8 | 11240 | 1.6601 | 1 | 1.6601 | 1 | 1.6601 | 1
214A | WORK | 32 | 2 |  |  | 118 | 2 | 2 | Air Handling Unit | 8 | 944 | 2.0339 | 1 | 2.0339 | 1 | 2.0339 | 1
215 | Classroom | 232 | 15 | Yes | 20 | 840 | 19 | 19 | Univent and Air Handling Unit | 8 | 6720 | 2.0714 | 1 | 2.0714 | 1 | 22.0714 | 3
216A | OFFICE | 64 | 4 |  |  | 165 | 3 | 3 | Air Handling Unit | 8 | 1320 | 2.9091 | 1 | 2.9091 | 1 | 2.9091 | 1
217 | Classroom | 200 | 13 |  |  | 782 | 17 | 13 | Univent and Air Handling Unit | 8 | 6256 | 1.9182 | 1 | 1.9182 | 1 | 1.9182 | 1
218 | Classroom | 120 | 8 |  |  | 374 | 8 | 8 | Univent | 8 | 2992 | 2.4064 | 1 | 2.4064 | 1 | 2.4064 | 1
218B | STR. | 65 | 4 | Yes | 20 | 2255 | 51 | 51 | Air Handling Unit | 8 | 18040 | 0.21619 | 1 | 0.21619 | 0 | 20.2162 | 3
218S | Classroom | 71 | 4 |  |  | 241 | 5 | 4 | Air Handling Unit | 8 | 1928 | 2.2095 | 1 | 2.2095 | 1 | 2.2095 | 1
219 | Classroom | 153 | 10 | Yes | 20 | 7825 | 177 | 177 | Univent and Air Handling Unit | 8 | 62600 | 0.14665 | 1.4912 | 0.21867 | 0 | 20.2187 | 3
220 | Classroom | 117 | 7 | Yes | 20 | 648 | 14 | 14 | Univent and Air Handling Unit | 8 | 5184 | 1.3542 | 1 | 1.3542 | 1 | 21.3542 | 3
221 | Classroom | 253 | 16 | Yes | 20 | 764 | 17 | 17 | Univent and Air Handling Unit | 8 | 6112 | 2.4836 | 1 | 2.4836 | 1 | 22.4836 | 3
222 | OFFICE | 50 | 3 |  |  | 1105 | 25 | 3 | Air Handling Unit | 8 | 8840 | 0.33937 | 1 | 0.33937 | 0 | 0.33937 | 0
223 | Classroom | 188 | 12 | Yes | 20 | 690 | 15 | 15 | Univent and Air Handling Unit | 8 | 5520 | 2.0435 | 1 | 2.0435 | 1 | 22.0435 | 3
225 | Classroom | 73 | 4 | Yes | 20 | 870 | 19 | 19 | Univent | 8 | 6960 | 0.62931 | 1 | 0.62931 | 0 | 20.6293 | 3
225 | COMP. | 124 | 8 |  |  | 96 | 2 | 2 | Air Handling Unit | 8 | 768 | 9.6875 | 1 | 9.6875 | 2 | 9.6875 | 2
226 | TECH. | 94 | 6 | Yes | 20 | 906 | 20 | 20 | Air Handling Unit | 8 | 7248 | 0.77815 | 1 | 0.77815 | 0 | 20.7781 | 3
226 (right) | Classroom | 104 | 6 |  |  | 343 | 7 | 6 | Univent | 8 | 2744 | 2.2741 | 1 | 2.2741 | 1 | 2.2741 | 1
226(left) | Classroom | 191 | 12 |  |  | 104 | 2 | 2 | Univent | 8 | 832 | 13.774 | 1 | 13.774 | 3 | 13.774 | 3
226C | SHOP | 91 | 6 |  |  | 104 | 2 | 2 | Air Handling Unit | 8 | 832 | 6.5625 | 1 | 6.5625 | 2 | 6.5625 | 2
227 | Classroom | 150 | 10 |  |  | 660 | 15 | 10 | Univent and Air Handling Unit | 8 | 5280 | 1.7045 | 1 | 1.7045 | 1 | 1.7045 | 1
300b | Corridor | 191 | 12 |  |  | 1404 | 31 | 12 | Air Handling Unit | 8 | 11232 | 1.0203 | 1 | 1.0203 | 1 | 1.0203 | 1
300d | Corridor | 225 | 15 |  |  | 1359 | 30 | 15 | Air Handling Unit | 8 | 10872 | 1.2417 | 1 | 1.2417 | 1 | 1.2417 | 1
301 | Classroom | 224 | 14 | Yes | 20 | 714 | 16 | 16 | Univent and Air Handling Unit | 8 | 5712 | 2.3529 | 1 | 2.3529 | 1 | 22.3529 | 3
302 | Classroom | 229 | 15 | Yes | 20 | 757 | 17 | 17 | Univent and Air Handling Unit | 8 | 6056 | 2.2688 | 1 | 2.2688 | 1 | 22.2688 | 3
303 | Classroom | 188 | 12 | Yes | 20 | 704 | 16 | 16 | Univent and Air Handling Unit | 8 | 5632 | 2.0028 | 1 | 2.0028 | 1 | 22.0028 | 3
304 | Classroom | 194 | 12 | Yes | 20 | 757 | 17 | 17 | Univent and Air Handling Unit | 8 | 6056 | 1.9221 | 1 | 1.9221 | 1 | 21.9221 | 3
305 | Classroom | 232 | 15 | Yes | 20 | 704 | 16 | 16 | Univent and Air Handling Unit | 8 | 5632 | 2.4716 | 1 | 2.4716 | 1 | 22.4716 | 3
306 | Classroom | 243 | 16 | Yes | 20 | 757 | 17 | 17 | Univent and Air Handling Unit | 8 | 6056 | 2.4075 | 1 | 2.4075 | 1 | 22.4075 | 3
307 | Classroom | 139 | 9 | Yes | 20 | 648 | 14 | 14 | Univent and Air Handling Unit | 8 | 5184 | 1.6088 | 1 | 1.6088 | 1 | 21.6088 | 3
308 | Classroom | 86 | 5 |  |  | 734 | 16 | 5 | Univent and Air Handling Unit | 8 | 5872 | 0.87875 | 1 | 0.87875 | 0 | 0.87875 | 0
309 | Classroom | 120 | 8 | Yes | 20 | 648 | 14 | 14 | Univent and Air Handling Unit | 8 | 5184 | 1.3889 | 1 | 1.3889 | 1 | 21.3889 | 3
313 | Classroom | 156 | 10 | Yes | 20 | 1160 | 26 | 26 | Univent and Air Handling Unit | 8 | 9280 | 1.0086 | 1 | 1.0086 | 1 | 21.0086 | 3
314 | Classroom | 119 | 7 | Yes | 20 | 1163 | 26 | 26 | Univent and Air Handling Unit | 8 | 9304 | 0.76741 | 1 | 0.76741 | 0 | 20.7674 | 3
315 | Classroom | 107 | 7 | Yes | 20 | 713 | 16 | 16 | Univent and Air Handling Unit | 8 | 5704 | 1.1255 | 1 | 1.1255 | 1 | 21.1255 | 3
316 | Classroom | 49 | 3 | Yes | 20 | 782 | 17 | 17 | Univent and Air Handling Unit | 8 | 6256 | 0.46995 | 1 | 0.46995 | 0 | 20.4699 | 3
317 | Classroom | 99 | 6 | Yes | 20 | 782 | 17 | 17 | Univent and Air Handling Unit | 8 | 6256 | 0.94949 | 1 | 0.94949 | 0 | 20.9495 | 3
318 | Classroom | 118 | 7 | Yes | 20 | 684 | 15 | 15 | Univent and Air Handling Unit | 8 | 5472 | 1.2939 | 1 | 1.2939 | 1 | 21.2939 | 3
319 | Classroom | 358 | 23 |  |  | 782 | 17 | 17 | Univent and Air Handling Unit | 8 | 6256 | 3.4335 | 1 | 3.4335 | 1 | 3.4335 | 1
320 | Classroom | 252 | 16 |  |  | 648 | 14 | 14 | Univent and Air Handling Unit | 8 | 5184 | 2.9167 | 1 | 2.9167 | 1 | 2.9167 | 1
321 | Classroom | 454 | 30 |  |  | 648 | 14 | 14 | Univent and Air Handling Unit | 8 | 5184 | 5.2546 | 1 | 5.2546 | 2 | 5.2546 | 2
322 | OFFICE | 0 | 0 |  |  | 100 | 2 | 0 | Air Handling Unit | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
- | AUDITORIUM | 2082 | 138 |  |  | 2938 | 66 | 66 | Air Handling Unit | 8 | 23504 | 5.3148 | 1.062 | 5.6445 | 2 | 5.6445 | 2
- | CAFETERIA | 251 | 16 | Yes | 20 | 4402 | 100 | 100 | Air Handling Unit | 8 | 35216 | 0.42765 | 1.062 | 0.45418 | 0 | 20.4542 | 3
Sheet Last Modified: | 2021-04-29
School: | George W. Nebinger Elementary-Middle School
Vendor: | EMCOR Fluidics
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 | Yes | 20 | 44 | 1 | 1 | House Fan | 8 | 352 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 880 | 20 | 20 | House Fan | 8 | 7040 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 |  |  | 644 | 14 | 0 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 0 | 0
104 | Classroom |  | 0 |  |  | 644 | 14 | 0 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom |  | 0 | Yes | 20 | 644 | 14 | 14 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom |  | 0 | Yes | 20 | 644 | 14 | 14 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 644 | 14 | 14 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 | Yes | 20 | 899 | 20 | 20 | House Fan | 8 | 7192 | 0 | 1 | 0 | 0 | 20 | 3
204A | Classroom |  | 0 | Yes | 20 | 285 | 6 | 6 | House Fan | 8 | 2280 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 330 | 7 | 7 | House Fan | 8 | 2640 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 | Yes | 20 | 644 | 14 | 14 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom |  | 0 | Yes | 20 | 644 | 14 | 14 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom |  | 0 | Yes | 20 | 644 | 14 | 14 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
305A | Classroom |  | 0 |  |  | 450 | 10 | 0 | House Fan | 8 | 3600 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom |  | 0 | Yes | 20 | 644 | 14 | 14 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom |  | 0 | Yes | 20 | 750 | 17 | 17 | House Fan | 8 | 6000 | 0 | 1 | 0 | 0 | 20 | 3
401 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
402 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 |  |  | 2870 | 65 | 0 | House Fan | 8 | 22960 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Main Office |  | 0 | Yes | 20 | 330 | 7 | 7 | House Fan | 8 | 2640 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 20 | 247 | 5 | 5 | House Fan | 8 | 1976 | 0 | 1 | 0 | 0 | 20 | 3
- | Health Room |  | 0 | Yes | 20 | 99 | 2 | 2 | House Fan | 8 | 792 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-18
School: | Northeast High School
Vendor: | Capital Programs | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Devine Brothers Data
1 | Classroom | 591 | 39 |  |  | 705 | 16 | 16 | Unit Ventilator | 8 | 5640 | 6.2872 | 1 | 6.2872 | 2 | 6.2872 | 2
2 | Classroom | 520 | 34 |  |  | 619 | 14 | 14 | Unit Ventilator | 8 | 4952 | 6.3005 | 1 | 6.3005 | 2 | 6.3005 | 2
3 | Classroom | 546 | 36 |  |  | 759 | 17 | 17 | Unit Ventilator | 8 | 6072 | 5.3953 | 1 | 5.3953 | 2 | 5.3953 | 2
4 | Classroom | 545 | 36 |  |  | 749 | 17 | 17 | Unit Ventilator | 8 | 5992 | 5.4573 | 1 | 5.4573 | 2 | 5.4573 | 2
5 | Classroom | 586 | 39 |  |  | 807 | 18 | 18 | Unit Ventilator | 8 | 6456 | 5.4461 | 1 | 5.4461 | 2 | 5.4461 | 2
6 | Classroom | 564 | 37 |  |  | 782 | 17 | 17 | Unit Ventilator | 8 | 6256 | 5.4092 | 1 | 5.4092 | 2 | 5.4092 | 2
7 | Classroom | 572 | 38 |  |  | 761 | 17 | 17 | Unit Ventilator | 8 | 6088 | 5.6373 | 1 | 5.6373 | 2 | 5.6373 | 2
8 | Classroom | 539 | 35 |  |  | 775 | 17 | 17 | Unit Ventilator | 8 | 6200 | 5.2161 | 1 | 5.2161 | 2 | 5.2161 | 2
9 | Classroom | 280 | 18 |  |  | 762 | 17 | 17 | Unit Ventilator | 8 | 6096 | 2.7559 | 1 | 2.7559 | 1 | 2.7559 | 1
10 | Classroom | 271 | 18 |  |  | 749 | 17 | 17 | Unit Ventilator | 8 | 5992 | 2.7136 | 1 | 2.7136 | 1 | 2.7136 | 1
11 | Classroom | 337 | 22 |  |  | 770 | 17 | 17 | Unit Ventilator | 8 | 6160 | 3.2825 | 1 | 3.2825 | 1 | 3.2825 | 1
12 | Classroom | 633 | 42 |  |  | 1673 | 38 | 38 | Unit Ventilator | 8 | 13384 | 2.8377 | 1 | 2.8377 | 1 | 2.8377 | 1
13 | Classroom | 541 | 36 |  |  | 1744 | 39 | 36 | Unit Ventilator | 8 | 13952 | 2.3265 | 1 | 2.3265 | 1 | 2.3265 | 1
14 | Classroom | 334 | 22 |  |  | 1047 | 23 | 22 | Unit Ventilator | 8 | 8376 | 2.3926 | 1 | 2.3926 | 1 | 2.3926 | 1
15 | Classroom | 507 | 33 |  |  | 1526 | 34 | 33 | Unit Ventilator | 8 | 12208 | 2.4918 | 1 | 2.4918 | 1 | 2.4918 | 1
16A | Classroom | 238 | 15 |  |  | 731 | 16 | 15 | Unit Ventilator | 8 | 5848 | 2.4419 | 1 | 2.4419 | 1 | 2.4419 | 1
16B | Classroom | 264 | 17 |  |  | 885 | 20 | 17 | Unit Ventilator | 8 | 7080 | 2.2373 | 1 | 2.2373 | 1 | 2.2373 | 1
17A | Classroom | 380 | 25 |  |  | 661 | 15 | 15 | Unit Ventilator | 8 | 5288 | 4.3116 | 1 | 4.3116 | 2 | 4.3116 | 2
17B | Classroom | 419 | 27 |  |  | 853 | 19 | 19 | Unit Ventilator | 8 | 6824 | 3.6841 | 1 | 3.6841 | 1 | 3.6841 | 1
17C | Classroom | 259 | 17 |  |  | 1050 | 23 | 17 | Unit Ventilator | 8 | 8400 | 1.85 | 1 | 1.85 | 1 | 1.85 | 1
18B | Classroom | 0 | 0 |  |  | 962 | 21 | 0 | Unit Ventilator | 8 | 7696 | 0 | 1 | 0 | 0 | 0 | 0
18D | Classroom | 0 | 0 |  |  | 843 | 19 | 0 | Unit Ventilator | 8 | 6744 | 0 | 1 | 0 | 0 | 0 | 0
19B | Classroom | 374 | 24 |  |  | 862 | 19 | 19 | Unit Ventilator | 8 | 6896 | 3.2541 | 1 | 3.2541 | 1 | 3.2541 | 1
21 | Offices | 0 | 0 |  |  | 1233 | 28 | 0 | Vertical Fan Coil Unit | 8 | 9864 | 0 | 1 | 0 | 0 | 0 | 0
22 | Office | 230 | 15 |  |  | 172 | 3 | 3 | Unit Ventilator | 8 | 1376 | 10.0291 | 1 | 10.0291 | 3 | 10.0291 | 3
23 | Classroom | 260 | 17 |  |  | 741 | 16 | 16 | Unit Ventilator | 8 | 5928 | 2.6316 | 1 | 2.6316 | 1 | 2.6316 | 1
24 | Classroom | 129 | 8 |  |  | 370 | 8 | 8 | Unit Ventilator | 8 | 2960 | 2.6149 | 1 | 2.6149 | 1 | 2.6149 | 1
27 | Teacher's Lounge | 378 | 25 |  |  | 1205 | 27 | 25 | Unit Ventilator | 8 | 9640 | 2.3527 | 1 | 2.3527 | 1 | 2.3527 | 1
31 | Classroom | 0 | 0 |  |  | 562 | 12 | 0 | Unit Ventilator | 8 | 4496 | 0 | 1 | 0 | 0 | 0 | 0
32 | Classrm. Lab | 2251 | 150 |  |  | 824 | 18 | 18 | Unit Ventilator | 8 | 6592 | 20.4885 | 1 | 20.4885 | 3 | 20.4885 | 3
32A | Classrm. Lab | 0 | 0 |  |  | 435 | 9 | 0 | Unit Ventilator | 8 | 3480 | 0 | 1 | 0 | 0 | 0 | 0
34A | Office | 0 | 0 |  |  | 187 | 4 | 0 | Unit Ventilator | 8 | 1496 | 0 | 1 | 0 | 0 | 0 | 0
33 | Classroom | 499 | 33 |  |  | 571 | 12 | 12 | Unit Ventilator | 8 | 4568 | 6.5543 | 1 | 6.5543 | 2 | 6.5543 | 2
35 | Office | 0 | 0 |  |  | 459 | 10 | 0 | Unit Ventilator | 8 | 3672 | 0 | 1 | 0 | 0 | 0 | 0
105 | Offices | 517 | 34 |  |  | 519 | 11 | 11 | Unit Ventilator | 8 | 4152 | 7.4711 | 1 | 7.4711 | 2 | 7.4711 | 2
106 | Classroom | 748 | 49 |  |  | 1031 | 23 | 23 | Unit Ventilator | 8 | 8248 | 5.4413 | 1 | 5.4413 | 2 | 5.4413 | 2
108 | Classroom | 739 | 49 |  |  | 948 | 21 | 21 | Unit Ventilator | 8 | 7584 | 5.8465 | 1 | 5.8465 | 2 | 5.8465 | 2
109 | Classroom | 508 | 33 |  |  | 940 | 21 | 21 | Unit Ventilator | 8 | 7520 | 4.0532 | 1 | 4.0532 | 2 | 4.0532 | 2
110 | Library | 610 | 40 |  |  | 386 | 8 | 8 | Unit Ventilator | 8 | 3088 | 11.8523 | 1 | 11.8523 | 3 | 11.8523 | 3
111 | Classroom | 553 | 36 |  |  | 993 | 22 | 22 | Unit Ventilator | 8 | 7944 | 4.1767 | 1 | 4.1767 | 2 | 4.1767 | 2
112 | Classroom | 602 | 40 |  |  | 980 | 22 | 22 | Unit Ventilator | 8 | 7840 | 4.6071 | 1 | 4.6071 | 2 | 4.6071 | 2
113 | Classroom | 535 | 35 |  |  | 883 | 20 | 20 | Unit Ventilator | 8 | 7064 | 4.5442 | 1 | 4.5442 | 2 | 4.5442 | 2
114 | Classroom | 363 | 24 |  |  | 717 | 16 | 16 | Unit Ventilator | 8 | 5736 | 3.7971 | 1 | 3.7971 | 1 | 3.7971 | 1
115 | Room | 541 | 36 |  |  | 965 | 21 | 21 | Unit Ventilator | 8 | 7720 | 4.2047 | 1 | 4.2047 | 2 | 4.2047 | 2
116 | Classroom | 623 | 41 |  |  | 745 | 16 | 16 | Unit Ventilator | 8 | 5960 | 6.2718 | 1 | 6.2718 | 2 | 6.2718 | 2
117 | Classroom | 0 | 0 |  |  | 686 | 15 | 0 | Unit Ventilator | 8 | 5488 | 0 | 1 | 0 | 0 | 0 | 0
118 | Classroom | 543 | 36 |  |  | 842 | 19 | 19 | Unit Ventilator | 8 | 6736 | 4.8367 | 1 | 4.8367 | 2 | 4.8367 | 2
119 | Classroom | 436 | 29 |  |  | 766 | 17 | 17 | Unit Ventilator | 8 | 6128 | 4.2689 | 1 | 4.2689 | 2 | 4.2689 | 2
120 | Classroom | 370 | 24 |  |  | 741 | 16 | 16 | Unit Ventilator | 8 | 5928 | 3.7449 | 1 | 3.7449 | 1 | 3.7449 | 1
121 | Classroom | 370 | 24 |  |  | 767 | 17 | 17 | Unit Ventilator | 8 | 6136 | 3.618 | 1 | 3.618 | 1 | 3.618 | 1
122 | Classroom | 495 | 33 |  |  | 1571 | 35 | 33 | Unit Ventilator | 8 | 12568 | 2.3631 | 1 | 2.3631 | 1 | 2.3631 | 1
123 | Classroom | 403 | 26 |  |  | 738 | 16 | 16 | Unit Ventilator | 8 | 5904 | 4.0955 | 1 | 4.0955 | 2 | 4.0955 | 2
124 | Classroom | 458 | 30 |  |  | 1410 | 32 | 30 | Unit Ventilator | 8 | 11280 | 2.4362 | 1 | 2.4362 | 1 | 2.4362 | 1
125 | Classroom | 392 | 26 |  |  | 802 | 18 | 18 | Unit Ventilator | 8 | 6416 | 3.6658 | 1 | 3.6658 | 1 | 3.6658 | 1
126 | Classroom | 326 | 21 |  |  | 698 | 15 | 15 | Unit Ventilator | 8 | 5584 | 3.5029 | 1 | 3.5029 | 1 | 3.5029 | 1
127 | Classroom | 425 | 28 |  |  | 751 | 17 | 17 | Unit Ventilator | 8 | 6008 | 4.2443 | 1 | 4.2443 | 2 | 4.2443 | 2
130 | Classroom | 481 | 32 |  |  | 1091 | 24 | 24 | Unit Ventilator | 8 | 8728 | 3.3066 | 1 | 3.3066 | 1 | 3.3066 | 1
131 | Classroom | 409 | 27 |  |  | 713 | 16 | 16 | Unit Ventilator | 8 | 5704 | 4.3022 | 1 | 4.3022 | 2 | 4.3022 | 2
132 | Classroom | 726 | 48 |  |  | 1038 | 23 | 23 | Unit Ventilator | 8 | 8304 | 5.2457 | 1 | 5.2457 | 2 | 5.2457 | 2
133 | Classroom | 679 | 45 |  |  | 1627 | 36 | 36 | Unit Ventilator | 8 | 13016 | 3.13 | 1 | 3.13 | 1 | 3.13 | 1
133A | Office | 0 | 0 |  |  | 293 | 6 | 0 | Unit Ventilator | 8 | 2344 | 0 | 1 | 0 | 0 | 0 | 0
134 | Classroom | 181 | 12 |  |  | 402 | 9 | 9 | Unit Ventilator | 8 | 3216 | 3.3769 | 1 | 3.3769 | 1 | 3.3769 | 1
136 | Classroom | 712 | 47 |  |  | 1206 | 27 | 27 | Unit Ventilator | 8 | 9648 | 4.4279 | 1 | 4.4279 | 2 | 4.4279 | 2
137 | Classroom | 537 | 35 |  |  | 773 | 17 | 17 | Unit Ventilator | 8 | 6184 | 5.2102 | 1 | 5.2102 | 2 | 5.2102 | 2
138 | Classroom | 453 | 30 |  |  | 1240 | 28 | 28 | Unit Ventilator | 8 | 9920 | 2.7399 | 1 | 2.7399 | 1 | 2.7399 | 1
139 | Classroom | 601 | 40 |  |  | 798 | 18 | 18 | Unit Ventilator | 8 | 6384 | 5.6485 | 1 | 5.6485 | 2 | 5.6485 | 2
140 | Classroom | 356 | 23 |  |  | 694 | 15 | 15 | Unit Ventilator | 8 | 5552 | 3.8473 | 1 | 3.8473 | 1 | 3.8473 | 1
141 | Classroom | 510 | 34 |  |  | 773 | 17 | 17 | Unit Ventilator | 8 | 6184 | 4.9483 | 1 | 4.9483 | 2 | 4.9483 | 2
143 | Classroom | 368 | 24 |  |  | 778 | 17 | 17 | Unit Ventilator | 8 | 6224 | 3.5476 | 1 | 3.5476 | 1 | 3.5476 | 1
150 | Classroom | 118 | 7 |  |  | 845 | 19 | 7 | Unit Ventilator | 8 | 6760 | 1.0473 | 1 | 1.0473 | 1 | 1.0473 | 1
152 | Classroom | 127 | 8 |  |  | 881 | 20 | 8 | Unit Ventilator | 8 | 7048 | 1.0812 | 1 | 1.0812 | 1 | 1.0812 | 1
154 | Classroom | 0 | 0 |  |  | 874 | 19 | 0 | Unit Ventilator | 8 | 6992 | 0 | 1 | 0 | 0 | 0 | 0
156 | Classroom | 132 | 8 |  |  | 815 | 18 | 8 | Unit Ventilator | 8 | 6520 | 1.2147 | 1 | 1.2147 | 1 | 1.2147 | 1
158 | Classroom | 160 | 10 |  |  | 849 | 19 | 10 | Unit Ventilator | 8 | 6792 | 1.4134 | 1 | 1.4134 | 1 | 1.4134 | 1
160 | Classroom | 158 | 10 |  |  | 835 | 18 | 10 | Unit Ventilator | 8 | 6680 | 1.4192 | 1 | 1.4192 | 1 | 1.4192 | 1
162 | Classroom | 0 | 0 |  |  | 711 | 16 | 0 | Unit Ventilator | 8 | 5688 | 0 | 1 | 0 | 0 | 0 | 0
175 | Classroom | 480 | 32 |  |  | 1223 | 27 | 27 | Unit Ventilator | 8 | 9784 | 2.9436 | 1 | 2.9436 | 1 | 2.9436 | 1
200 | Classroom | 137 | 9 |  |  | 715 | 16 | 9 | Unit Ventilator | 8 | 5720 | 1.4371 | 1 | 1.4371 | 1 | 1.4371 | 1
201 | Classroom | 548 | 36 |  |  | 728 | 16 | 16 | Unit Ventilator | 8 | 5824 | 5.6456 | 1 | 5.6456 | 2 | 5.6456 | 2
202 | Classroom | 525 | 35 |  |  | 755 | 17 | 17 | Unit Ventilator | 8 | 6040 | 5.2152 | 1 | 5.2152 | 2 | 5.2152 | 2
203 | Classroom | 232 | 15 |  |  | 555 | 12 | 12 | Unit Ventilator | 8 | 4440 | 3.1351 | 1 | 3.1351 | 1 | 3.1351 | 1
203A | Classroom | 418 | 27 |  |  | 546 | 12 | 12 | Unit Ventilator | 8 | 4368 | 5.7418 | 1 | 5.7418 | 2 | 5.7418 | 2
204 | Classroom | 523 | 34 |  |  | 572 | 13 | 13 | Unit Ventilator | 8 | 4576 | 6.8575 | 1 | 6.8575 | 2 | 6.8575 | 2
205 | Classroom | 441 | 29 |  |  | 1073 | 24 | 24 | Unit Ventilator | 8 | 8584 | 3.0825 | 1 | 3.0825 | 1 | 3.0825 | 1
206 | Classroom | 463 | 30 |  |  | 677 | 15 | 15 | Unit Ventilator | 8 | 5416 | 5.1292 | 1 | 5.1292 | 2 | 5.1292 | 2
207 | Classroom | 790 | 52 |  |  | 651 | 14 | 14 | Unit Ventilator | 8 | 5208 | 9.1014 | 1 | 9.1014 | 2 | 9.1014 | 2
208 | Classroom | 704 | 46 |  |  | 724 | 16 | 16 | Unit Ventilator | 8 | 5792 | 7.2928 | 1 | 7.2928 | 2 | 7.2928 | 2
209 | Classroom | 769 | 51 |  |  | 1069 | 24 | 24 | Unit Ventilator | 8 | 8552 | 5.3952 | 1 | 5.3952 | 2 | 5.3952 | 2
210 | Classroom | 410 | 27 |  |  | 730 | 16 | 16 | Unit Ventilator | 8 | 5840 | 4.2123 | 1 | 4.2123 | 2 | 4.2123 | 2
211 | Classroom | 730 | 48 |  |  | 1069 | 24 | 24 | Unit Ventilator | 8 | 8552 | 5.1216 | 1 | 5.1216 | 2 | 5.1216 | 2
212 | Classroom | 504 | 33 |  |  | 662 | 15 | 15 | Unit Ventilator | 8 | 5296 | 5.71 | 1 | 5.71 | 2 | 5.71 | 2
213 | Classroom | 650 | 43 |  |  | 1100 | 25 | 25 | Unit Ventilator | 8 | 8800 | 4.4318 | 1 | 4.4318 | 2 | 4.4318 | 2
214 | Classroom | 522 | 34 |  |  | 713 | 16 | 16 | Unit Ventilator | 8 | 5704 | 5.4909 | 1 | 5.4909 | 2 | 5.4909 | 2
215 A&B | Offices | 842 | 56 |  |  | 410 | 9 | 9 | Unit Ventilator | 8 | 3280 | 15.4024 | 1 | 15.4024 | 3 | 15.4024 | 3
215 C&D | Offices | 833 | 55 |  |  | 410 | 9 | 9 | Unit Ventilator | 8 | 3280 | 15.2378 | 1 | 15.2378 | 3 | 15.2378 | 3
216 | Classroom | 552 | 36 |  |  | 678 | 15 | 15 | Unit Ventilator | 8 | 5424 | 6.1062 | 1 | 6.1062 | 2 | 6.1062 | 2
218 | Classroom | 527 | 35 |  |  | 677 | 15 | 15 | Unit Ventilator | 8 | 5416 | 5.8383 | 1 | 5.8383 | 2 | 5.8383 | 2
219A | Classroom | 313 | 20 |  |  | 607 | 13 | 13 | Unit Ventilator | 8 | 4856 | 3.8674 | 1 | 3.8674 | 1 | 3.8674 | 1
219B | Classroom | 322 | 21 |  |  | 446 | 10 | 10 | Unit Ventilator | 8 | 3568 | 5.4148 | 1 | 5.4148 | 2 | 5.4148 | 2
220 | Classroom | 534 | 35 |  |  | 662 | 15 | 15 | Unit Ventilator | 8 | 5296 | 6.0498 | 1 | 6.0498 | 2 | 6.0498 | 2
221A | Classroom | 307 | 20 |  |  | 717 | 16 | 16 | Unit Ventilator | 8 | 5736 | 3.2113 | 1 | 3.2113 | 1 | 3.2113 | 1
221B | Classroom | 334 | 22 |  |  | 391 | 8 | 8 | Unit Ventilator | 8 | 3128 | 6.4066 | 1 | 6.4066 | 2 | 6.4066 | 2
222 | Classroom | 547 | 36 |  |  | 792 | 18 | 18 | Unit Ventilator | 8 | 6336 | 5.1799 | 1 | 5.1799 | 2 | 5.1799 | 2
223A | Classroom | 267 | 17 |  |  | 598 | 13 | 13 | Unit Ventilator | 8 | 4784 | 3.3487 | 1 | 3.3487 | 1 | 3.3487 | 1
223C | Classroom | 426 | 28 |  |  | 373 | 8 | 8 | Unit Ventilator | 8 | 2984 | 8.5657 | 1 | 8.5657 | 2 | 8.5657 | 2
225 | Classroom | 708 | 47 |  |  | 1445 | 32 | 32 | Unit Ventilator | 8 | 11560 | 3.6747 | 1 | 3.6747 | 1 | 3.6747 | 1
227A | Classroom | 311 | 20 |  |  | 590 | 13 | 13 | Unit Ventilator | 8 | 4720 | 3.9534 | 1 | 3.9534 | 1 | 3.9534 | 1
227B | Classroom | 298 | 19 |  |  | 494 | 11 | 11 | Unit Ventilator | 8 | 3952 | 4.5243 | 1 | 4.5243 | 2 | 4.5243 | 2
228 | Classroom | 525 | 35 |  |  | 784 | 17 | 17 | Unit Ventilator | 8 | 6272 | 5.0223 | 1 | 5.0223 | 2 | 5.0223 | 2
229B | Classroom | 165 | 11 |  |  | 525 | 11 | 11 | Unit Ventilator | 8 | 4200 | 2.3571 | 1 | 2.3571 | 1 | 2.3571 | 1
229C | Classroom | 325 | 21 |  |  | 570 | 12 | 12 | Unit Ventilator | 8 | 4560 | 4.2763 | 1 | 4.2763 | 2 | 4.2763 | 2
230 | Classroom | 503 | 33 |  |  | 657 | 14 | 14 | Unit Ventilator | 8 | 5256 | 5.742 | 1 | 5.742 | 2 | 5.742 | 2
231 | Classroom | 562 | 37 |  |  | 751 | 17 | 17 | Unit Ventilator | 8 | 6008 | 5.6125 | 1 | 5.6125 | 2 | 5.6125 | 2
232 | Classroom | 592 | 39 |  |  | 691 | 15 | 15 | Unit Ventilator | 8 | 5528 | 6.4255 | 1 | 6.4255 | 2 | 6.4255 | 2
233 | Classroom | 557 | 37 |  |  | 705 | 16 | 16 | Unit Ventilator | 8 | 5640 | 5.9255 | 1 | 5.9255 | 2 | 5.9255 | 2
234 | Classroom | 532 | 35 |  |  | 703 | 15 | 15 | Unit Ventilator | 8 | 5624 | 5.6757 | 1 | 5.6757 | 2 | 5.6757 | 2
235 | Classroom | 458 | 30 |  |  | 704 | 16 | 16 | Unit Ventilator | 8 | 5632 | 4.8793 | 1 | 4.8793 | 2 | 4.8793 | 2
236 | Classroom | 405 | 27 |  |  | 701 | 15 | 15 | Unit Ventilator | 8 | 5608 | 4.3331 | 1 | 4.3331 | 2 | 4.3331 | 2
237 | Room | 148 | 9 |  |  | 384 | 8 | 8 | Unit Ventilator | 8 | 3072 | 2.8906 | 1 | 2.8906 | 1 | 2.8906 | 1
238 | Classroom | 389 | 25 |  |  | 675 | 15 | 15 | Unit Ventilator | 8 | 5400 | 4.3222 | 1 | 4.3222 | 2 | 4.3222 | 2
240 | Classroom | 411 | 27 |  |  | 685 | 15 | 15 | Unit Ventilator | 8 | 5480 | 4.5 | 1 | 4.5 | 2 | 4.5 | 2
242 | Classroom | 479 | 31 |  |  | 711 | 16 | 16 | Unit Ventilator | 8 | 5688 | 5.0527 | 1 | 5.0527 | 2 | 5.0527 | 2
244 | Classroom | 518 | 34 |  |  | 634 | 14 | 14 | Unit Ventilator | 8 | 5072 | 6.1278 | 1 | 6.1278 | 2 | 6.1278 | 2
1st Fl. Corridor | Corridor | 0 | 0 |  |  | 892 | 20 | 0 | Unit Ventilator | 8 | 7136 | 0 | 1 | 0 | 0 | 0 | 0
2nd Fl. Corr. | 2nd Fl. Corr. | 0 | 0 |  |  | 9100 | 206 | 0 | Unit Ventilator | 8 | 72800 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | Auditorium | 1799 | 119 |  |  | 12288 | 279 | 119 | Heating Ventilation Unit | 8 | 98304 | 1.098 | 1.4912 | 1.6373 | 1 | 1.6373 | 1
- | Band Room | 254 | 16 |  |  | 1028 | 23 | 16 | Heating Ventilation Unit | 8 | 8224 | 1.8531 | 1 | 1.8531 | 1 | 1.8531 | 1
Boys Gym #1 | Gym | 336 | 22 |  |  | 3701 | 84 | 22 | Heating Ventilation Unit | 8 | 29608 | 0.6809 | 1.062 | 0.72314 | 0 | 0.72314 | 0
Boys Gym #1 | Gym | 307 | 20 |  |  | 3701 | 84 | 20 | Heating Ventilation Unit | 8 | 29608 | 0.62213 | 1.062 | 0.66072 | 0 | 0.66072 | 0
Boys Gym #2 | Gym | 2587 | 172 |  |  | 3701 | 84 | 84 | Heating Ventilation Unit | 8 | 29608 | 5.2425 | 1.062 | 5.5677 | 2 | 5.5677 | 2
Boys Gym #2 | Gym | 1367 | 91 |  |  | 3701 | 84 | 84 | Heating Ventilation Unit | 8 | 29608 | 2.7702 | 1.062 | 2.942 | 1 | 2.942 | 1
Boys Lckr. Rm. | Locker Rm. | 1229 | 81 |  |  | 5966 | 135 | 81 | Heating Ventilation Unit | 8 | 47728 | 1.545 | 1.062 | 1.6408 | 1 | 1.6408 | 1
Cafeteria | Cafeteria | 1685 | 112 |  |  | 12073 | 274 | 112 | Heating Ventilation Unit | 8 | 96584 | 1.0468 | 1.4912 | 1.5609 | 1 | 1.5609 | 1
Girls Gym #1 | Gym | 317 | 21 |  |  | 3514 | 79 | 21 | Heating Ventilation Unit | 8 | 28112 | 0.67658 | 1.062 | 0.71855 | 0 | 0.71855 | 0
Girls Gym #1 | Gym | 397 | 26 |  |  | 3514 | 79 | 26 | Heating Ventilation Unit | 8 | 28112 | 0.84732 | 1.062 | 0.89989 | 0 | 0.89989 | 0
Girls Gym #2 | Gym | 187 | 12 |  |  | 3514 | 79 | 12 | Heating Ventilation Unit | 8 | 28112 | 0.39912 | 1.062 | 0.42388 | 0 | 0.42388 | 0
Girls Lckr. Rm. | Locker Rm. | 0 | 0 |  |  | 3920 | 89 | 0 | Heating Ventilation Unit | 8 | 31360 | 0 | 1.062 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  |  | 3443 | 78 | 0 | Unit Ventilator | 8 | 27544 | 0 | 1.062 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  |  | 3443 | 78 | 0 | Unit Ventilator | 8 | 27544 | 0 | 1.062 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  |  | 3443 | 78 | 0 | Unit Ventilator | 8 | 27544 | 0 | 1.062 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  |  | 3443 | 78 | 0 | Unit Ventilator | 8 | 27544 | 0 | 1.062 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  |  | 3443 | 78 | 0 | Unit Ventilator | 8 | 27544 | 0 | 1.062 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  |  | 3443 | 78 | 0 | Unit Ventilator | 8 | 27544 | 0 | 1.062 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  |  | 3443 | 78 | 0 | Unit Ventilator | 8 | 27544 | 0 | 1.062 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  |  | 3443 | 78 | 0 | Unit Ventilator | 8 | 27544 | 0 | 1.062 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  |  | 3443 | 78 | 0 | Unit Ventilator | 8 | 27544 | 0 | 1.062 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  |  | 3443 | 78 | 0 | Unit Ventilator | 8 | 27544 | 0 | 1.062 | 0 | 0 | 0 | 0
Grnd. Fl. Corridor | Corridor | 0 | 0 |  |  | 3443 | 78 | 0 | Unit Ventilator | 8 | 27544 | 0 | 1.062 | 0 | 0 | 0 | 0
Library | Library | 2751 | 183 |  |  | 1816 | 41 | 41 | Heating Ventilation Unit | 8 | 14528 | 11.3615 | 1 | 11.3615 | 3 | 11.3615 | 3
Library | Library | 453 | 30 |  |  | 454 | 10 | 10 | Unit Ventilator | 8 | 3632 | 7.4835 | 1 | 7.4835 | 2 | 7.4835 | 2
Library | Library | 525 | 35 |  |  | 454 | 10 | 10 | Unit Ventilator | 8 | 3632 | 8.6729 | 1 | 8.6729 | 2 | 8.6729 | 2
Library | Library | 509 | 33 |  |  | 454 | 10 | 10 | Unit Ventilator | 8 | 3632 | 8.4086 | 1 | 8.4086 | 2 | 8.4086 | 2
Library | Library | 477 | 31 |  |  | 454 | 10 | 10 | Unit Ventilator | 8 | 3632 | 7.88 | 1 | 7.88 | 2 | 7.88 | 2
Main office | Offices | 446 | 29 |  |  | 2450 | 55 | 29 | Unit Ventilator | 8 | 19600 | 1.3653 | 1 | 1.3653 | 1 | 1.3653 | 1
Stage | Stage | 235 | 15 |  |  | 1743 | 39 | 15 | Unit Ventilator | 8 | 13944 | 1.0112 | 1 | 1.0112 | 1 | 1.0112 | 1
Stage | Stage | 262 | 17 |  |  | 1743 | 39 | 17 | Unit Ventilator | 8 | 13944 | 1.1274 | 1 | 1.1274 | 1 | 1.1274 | 1
Sheet Last Modified: | 2021-04-29
School: | Olney Elementary School
Vendor: | Devine Main Building ABR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
101 | Classroom | 180 | 12 |  |  | 520 | 11 | 11 | AIr Handling Unit | 8 | 4160 | 2.5962 | 1 | 2.5962 | 1 | 2.5962 | 1
102 | Classroom | 122 | 8 |  |  | 520 | 11 | 8 | AIr Handling Unit | 8 | 4160 | 1.7596 | 1 | 1.7596 | 1 | 1.7596 | 1
103 | Classroom | 142 | 9 |  |  | 520 | 11 | 9 | AIr Handling Unit | 8 | 4160 | 2.0481 | 1 | 2.0481 | 1 | 2.0481 | 1
104 | Classroom | 527 | 35 |  |  | 520 | 11 | 11 | AIr Handling Unit | 8 | 4160 | 7.601 | 1 | 7.601 | 2 | 7.601 | 2
107 | Classroom | 63 | 4 |  |  | 667 | 15 | 4 | Univent | 8 | 5336 | 0.7084 | 1 | 0.7084 | 0 | 0.7084 | 0
108 | Classroom | 235 | 15 |  |  | 840 | 19 | 15 | Univent | 8 | 6720 | 2.0982 | 1 | 2.0982 | 1 | 2.0982 | 1
111 | Classroom | 88 | 5 |  |  | 378 | 8 | 5 | Univent | 8 | 3024 | 1.746 | 1 | 1.746 | 1 | 1.746 | 1
201 | Classroom | 289 | 19 |  |  | 682 | 15 | 15 | Univent | 8 | 5456 | 3.1782 | 1 | 3.1782 | 1 | 3.1782 | 1
203 | Classroom | 327 | 21 |  |  | 928 | 21 | 21 | Univent | 8 | 7424 | 2.6428 | 1 | 2.6428 | 1 | 2.6428 | 1
204 | Classroom | 286 | 19 |  |  | 756 | 17 | 17 | Univent | 8 | 6048 | 2.8373 | 1 | 2.8373 | 1 | 2.8373 | 1
205 | Classroom | 303 | 20 |  |  | 784 | 17 | 17 | Univent | 8 | 6272 | 2.8986 | 1 | 2.8986 | 1 | 2.8986 | 1
206 | Classroom | 296 | 19 |  |  | 812 | 18 | 18 | Univent | 8 | 6496 | 2.734 | 1 | 2.734 | 1 | 2.734 | 1
207 | Classroom | 309 | 20 |  |  | 594 | 13 | 13 | Univent | 8 | 4752 | 3.9015 | 1 | 3.9015 | 1 | 3.9015 | 1
208 | Classroom | 324 | 21 |  |  | 748 | 17 | 17 | Univent | 8 | 5984 | 3.2487 | 1 | 3.2487 | 1 | 3.2487 | 1
209 | Classroom | 282 | 18 |  |  | 1232 | 28 | 18 | Univent | 8 | 9856 | 1.7167 | 1 | 1.7167 | 1 | 1.7167 | 1
210 | Classroom | 327 | 21 |  |  | 330 | 7 | 7 | Univent | 8 | 2640 | 7.4318 | 1 | 7.4318 | 2 | 7.4318 | 2
211 | Classroom | 326 | 21 |  |  | 756 | 17 | 17 | Univent | 8 | 6048 | 3.2341 | 1 | 3.2341 | 1 | 3.2341 | 1
301 | Classroom | 0 | 0 |  |  | 682 | 15 | 0 | Univent | 8 | 5456 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom | 328 | 21 |  |  | 682 | 15 | 15 | Univent | 8 | 5456 | 3.607 | 1 | 3.607 | 1 | 3.607 | 1
303 | Classroom | 281 | 18 |  |  | 899 | 20 | 18 | Univent | 8 | 7192 | 2.3443 | 1 | 2.3443 | 1 | 2.3443 | 1
304 | Classroom | 280 | 18 |  |  | 729 | 16 | 16 | Univent | 8 | 5832 | 2.8807 | 1 | 2.8807 | 1 | 2.8807 | 1
305 | Classroom | 324 | 21 |  |  | 812 | 18 | 18 | Univent | 8 | 6496 | 2.9926 | 1 | 2.9926 | 1 | 2.9926 | 1
306 | Classroom | 285 | 19 |  |  | 783 | 17 | 17 | Univent | 8 | 6264 | 2.7299 | 1 | 2.7299 | 1 | 2.7299 | 1
307 | Classroom | 279 | 18 |  |  | 594 | 13 | 13 | Univent | 8 | 4752 | 3.5227 | 1 | 3.5227 | 1 | 3.5227 | 1
308 | Classroom | 291 | 19 |  |  | 782 | 17 | 17 | Univent | 8 | 6256 | 2.7909 | 1 | 2.7909 | 1 | 2.7909 | 1
309 | Classroom | 325 | 21 |  |  | 638 | 14 | 14 | Univent | 8 | 5104 | 3.8205 | 1 | 3.8205 | 1 | 3.8205 | 1
310 | Classroom | 328 | 21 |  |  | 638 | 14 | 14 | Univent | 8 | 5104 | 3.8558 | 1 | 3.8558 | 1 | 3.8558 | 1
311 | Classroom | 309 | 20 |  |  | 756 | 17 | 17 | Univent | 8 | 6048 | 3.0655 | 1 | 3.0655 | 1 | 3.0655 | 1
- | Main Office |  | 0 |  |  | 480 | 10 | 0 |  | 8 | 3840 | 0 | 1 | 0 | 0 | 0 | 0
- | Principal's Office | 173 | 11 |  |  | 396 | 9 | 9 | Univent | 8 | 3168 | 3.2765 | 1 | 3.2765 | 1 | 3.2765 | 1
- | Boys' Cafeteria |  | 0 | Yes | 20 | 1271 | 28 |  | Active Pure | 8 | 10168 | 0 | 1 | 0 | 0 | 20 | 3
- | Girls' Cafeteria |  | 0 | Yes | 20 | 943 | 21 |  | Active Pure | 8 | 7544 | 0 | 1 | 0 | 0 | 20 | 3
Annex
1 | Classroom |  | 0 | Yes | 20 | 684 | 15 | 15 |  | 8 | 5472 | 0 | 1 | 0 | 0 | 20 | 3
2 | Classroom |  | 0 | Yes | 20 | 1050 | 23 | 23 |  | 8 | 8400 | 0 | 1 | 0 | 0 | 20 | 3
3 | Classroom |  | 0 | Yes | 20 | 792 | 18 | 18 |  | 8 | 6336 | 0 | 1 | 0 | 0 | 20 | 3
4 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 |  | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
5 | Classroom |  | 0 | Yes | 20 | 1104 | 25 | 25 |  | 8 | 8832 | 0 | 1 | 0 | 0 | 20 | 3
6 | Classroom |  | 0 | Yes | 20 | 700 | 15 | 15 |  | 8 | 5600 | 0 | 1 | 0 | 0 | 20 | 3
7 | Classroom |  | 0 | Yes | 20 | 1050 | 23 | 23 |  | 8 | 8400 | 0 | 1 | 0 | 0 | 20 | 3
8 | Classroom |  | 0 | Yes | 20 | 816 | 18 | 18 |  | 8 | 6528 | 0 | 1 | 0 | 0 | 20 | 3
9 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 |  | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
10 | Classroom |  | 0 | Yes | 20 | 875 | 19 | 19 |  | 8 | 7000 | 0 | 1 | 0 | 0 | 20 | 3
- | Lobby |  | 0 | Yes | 20 | 180 | 4 | 4 |  | 8 | 1440 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office |  | 0 | Yes | 20 | 108 | 2 | 2 |  | 8 | 864 | 0 | 1 | 0 | 0 | 20 | 3
- | Asst Principal's Office |  | 0 | Yes | 20 | 89 | 2 | 2 |  | 8 | 712 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 | Yes | 20 | 4328 | 98 | 98 | Hydroxyl Unit | 8 | 34624 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Nurse Open area (Office D) and Early Lit |  | 0 | Yes | 20 | 547 | 12 | 12 |  | 8 | 4376 | 0 | 1 | 0 | 0 | 20 | 3
- | Conference room (medical waiting) |  | 0 | Yes | 20 | 141 | 3 | 3 |  | 8 | 1128 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-18
School: | One Bright Ray- Elmwood
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 313 | 20 |  |  |  | 0 | 0 | Air Handling Unit
102 | Classroom | 189 | 12 |  |  |  | 0 | 0 | Air Handling Unit
103 | Classroom | 249 | 16 |  |  |  | 0 | 0 | Air Handling Unit
104 | Classroom | 215 | 14 |  |  |  | 0 | 0 | Air Handling Unit
105 | Classroom | 250 | 16 |  |  |  | 0 | 0 | Air Handling Unit
105 | Principal's Office | 58 | 3 |  |  |  | 0 | 0 | Air Handling Unit
- | Dean of Students Office | 56 | 3 |  |  |  | 0 | 0 | Air Handling Unit
- | Faculty Lounge | 69 | 4 |  |  |  | 0 | 0 | Air Handling Unit
- | Foyer / Hallway | 147 | 9 |  |  |  | 0 | 0 | Air Handling Unit
- | Open Space / Classroom | 475 | 31 |  |  |  | 0 | 0 | Air Handling Unit
- | SW Office | 48 | 3 |  |  |  | 0 | 0 | Air Handling Unit
Sheet Last Modified: | 2021-04-30
School: | Overbrook Educational Center Elementary School
Vendor: | Goldner | Retest
School: | Overbrook Education Center Annex
Vendor: | EMCOR Fluidics
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
- | Boiler Room | 602 | 40 |  |  | 1496 | 34 | 34 | AHU | 8 | 11968 | 3.018 | 1 | 3.018 | 1 | 3.018 | 1
- | BE Office |  | 0 |  |  | 491 | 11 | 0 | AHU | 8 | 3928 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria | 233 | 15 | Yes | 20 | 1936 | 44 | 44 | AHU | 8 | 15488 | 0.90263 | 1 | 0.90263 | 0 | 20.9026 | 3
- | Corridor | 49 | 3 |  |  |  | 0 | 0 | AHU
- | Kitchen | 53 | 3 |  |  | 440 | 10 | 3 | AHU | 8 | 3520 | 0.90341 | 1 | 0.90341 | 0 | 0.90341 | 0
- | Music Room | 204 | 13 |  |  | 748 | 17 | 13 | AHU | 8 | 5984 | 2.0455 | 1 | 2.0455 | 1 | 2.0455 | 1
- | Computer Room | 79 | 5 |  |  | 176 | 4 | 4 | AHU | 8 | 1408 | 3.3665 | 1 | 3.3665 | 1 | 3.3665 | 1
- | 1st Flr Entryway | 42 | 2 |  |  | 396 | 9 | 2 | AHU | 8 | 3168 | 0.79545 | 1 | 0.79545 | 0 | 0.79545 | 0
- | Exam Office | 32 | 2 |  |  | 176 | 4 | 2 | AHU | 8 | 1408 | 1.3636 | 1 | 1.3636 | 1 | 1.3636 | 1
- | Gym Office | 28 | 1 |  |  | 132 | 3 | 1 | AHU | 8 | 1056 | 1.5909 | 1 | 1.5909 | 1 | 1.5909 | 1
- | Gym /Stage | 1257 | 83 |  |  | 2332 | 53 | 53 | AHU | 8 | 18656 | 4.0427 | 1 | 4.0427 | 2 | 4.0427 | 2
- | Gym Lobby | 109 | 7 |  |  |  | 0 | 0 | AHU
1st flr Hallway | Corridor | 20 | 1 |  |  |  | 0 | 0 | AHU
1st flr Lobby | Main Lobby | 71 | 4 |  |  | 396 | 9 | 4 | AHU | 8 | 3168 | 1.3447 | 1 | 1.3447 | 1 | 1.3447 | 1
1st flr Main Office | Administration | 65 | 4 |  |  | 220 | 5 | 4 | AHU | 8 | 1760 | 2.2159 | 1 | 2.2159 | 1 | 2.2159 | 1
1st flr Nurse's Office | Medical | 38 | 2 |  |  | 264 | 6 | 2 | AHU | 8 | 2112 | 1.0795 | 1 | 1.0795 | 1 | 1.0795 | 1
1st flr Office | Principal | 49 | 3 |  |  | 220 | 5 | 3 | AHU | 8 | 1760 | 1.6705 | 1 | 1.6705 | 1 | 1.6705 | 1
1st flr Office | Copy Room | 19 | 1 |  |  | 88 | 2 | 1 | AHU | 8 | 704 | 1.6193 | 1 | 1.6193 | 1 | 1.6193 | 1
1st flr Office | Conference Room | 47 | 3 |  |  | 176 | 4 | 3 | AHU | 8 | 1408 | 2.0028 | 1 | 2.0028 | 1 | 2.0028 | 1
201 | Faculty Lounge | 161 | 10 |  |  | 220 | 5 | 5 | AHU | 8 | 1760 | 5.4886 | 1 | 5.4886 | 2 | 5.4886 | 2
204 | Office | 171 | 11 | Yes | 20 | 176 | 4 | 4 | RTU | 8 | 1408 | 7.2869 | 1 | 7.2869 | 2 | 27.2869 | 4
206 | Classroom | 370 | 24 |  |  | 660 | 15 | 15 | Univent | 8 | 5280 | 4.2045 | 1 | 4.2045 | 2 | 4.2045 | 2
207 | Classroom | 353 | 23 |  |  | 748 | 17 | 17 | Univent | 8 | 5984 | 3.5394 | 1 | 3.5394 | 1 | 3.5394 | 1
208 | Classroom | 446 | 29 |  |  | 748 | 17 | 17 | Univent | 8 | 5984 | 4.4719 | 1 | 4.4719 | 2 | 4.4719 | 2
209 | Classroom | 475 | 31 |  |  | 572 | 13 | 13 | Univent | 8 | 4576 | 6.2281 | 1 | 6.2281 | 2 | 6.2281 | 2
210 | Classroom | 425 | 28 |  |  | 660 | 15 | 15 | Univent | 8 | 5280 | 4.8295 | 1 | 4.8295 | 2 | 4.8295 | 2
211 | Classroom (Life Skills) | 536 | 35 |  |  | 748 | 17 | 17 | Univent | 8 | 5984 | 5.3743 | 1 | 5.3743 | 2 | 5.3743 | 2
2nd flr Library | Library | 344 | 22 |  |  | 1496 | 34 | 22 | AHU | 8 | 11968 | 1.7246 | 1 | 1.7246 | 1 | 1.7246 | 1
2nd flr Art | Classroom | 74 | 4 |  |  | 924 | 21 | 4 | AHU | 8 | 7392 | 0.60065 | 1 | 0.60065 | 0 | 0.60065 | 0
2nd Flr Hallway | Corridor | 197 | 13 |  |  |  | 0 | 0 | AAON unit
2nd flr Science | Classroom | 84 | 5 |  |  | 836 | 19 | 5 | AHU | 8 | 6688 | 0.75359 | 1 | 0.75359 | 0 | 0.75359 | 0
301 | Classroom | 452 | 30 |  |  | 220 | 5 | 5 | RTU | 8 | 1760 | 15.4091 | 1 | 15.4091 | 3 | 15.4091 | 3
302 | Office | 284 | 18 |  |  | 176 | 4 | 4 | AHU | 8 | 1408 | 12.1023 | 1 | 12.1023 | 3 | 12.1023 | 3
304 | Classroom | 463 | 30 |  |  | 660 | 15 | 15 | Univent | 8 | 5280 | 5.2614 | 1 | 5.2614 | 2 | 5.2614 | 2
305 | Classroom | 517 | 34 |  |  | 748 | 17 | 17 | Univent | 8 | 5984 | 5.1838 | 1 | 5.1838 | 2 | 5.1838 | 2
306 | Classroom | 550 | 36 |  |  | 704 | 16 | 16 | Univent | 8 | 5632 | 5.8594 | 1 | 5.8594 | 2 | 5.8594 | 2
307 | Classroom | 596 | 39 |  |  | 572 | 13 | 13 | Univent | 8 | 4576 | 7.8147 | 1 | 7.8147 | 2 | 7.8147 | 2
308 | Classroom | 461 | 30 |  |  | 660 | 15 | 15 | Univent | 8 | 5280 | 5.2386 | 1 | 5.2386 | 2 | 5.2386 | 2
309 | Classroom | 1030 | 68 |  |  | 748 | 17 | 17 | Univent | 8 | 5984 | 10.3275 | 1 | 10.3275 | 3 | 10.3275 | 3
316 | Classroom |  | 0 | Yes | 20 | 695 | 15 | 15 |  | 8 | 5560 | 0 | 1 | 0 | 0 | 20 | 3
Annex Building
5 | Kitchen |  | 0 | Yes | 20 | 157 | 3 | 3 |  | 8 | 1256 | 0 | 1 | 0 | 0 | 20 | 3
6 | Office |  | 0 | Yes | 20 | 122 | 2 | 2 |  | 8 | 976 | 0 | 1 | 0 | 0 | 20 | 3
7 | Lobby |  | 0 |  |  | 890 | 20 | 0 |  | 8 | 7120 | 0 | 1 | 0 | 0 | 0 | 0
1 | Classroom |  | 0 | Yes | 20 | 1077 | 24 | 24 |  | 8 | 8616 | 0 | 1 | 0 | 0 | 20 | 3
2 | Classroom |  | 0 | Yes | 20 | 404 | 9 | 9 |  | 8 | 3232 | 0 | 1 | 0 | 0 | 20 | 3
25 | Classroom |  | 0 | Yes | 20 | 555 | 12 | 12 |  | 8 | 4440 | 0 | 1 | 0 | 0 | 20 | 3
24 | Office |  | 0 | Yes | 20 | 177 | 4 | 4 |  | 8 | 1416 | 0 | 1 | 0 | 0 | 20 | 3
22 | Classroom |  | 0 | Yes | 20 | 902 | 20 | 20 |  | 8 | 7216 | 0 | 1 | 0 | 0 | 20 | 3
21 | Classroom |  | 0 | Yes | 20 | 297 | 6 | 6 |  | 8 | 2376 | 0 | 1 | 0 | 0 | 20 | 3
31 | Classroom |  | 0 | Yes | 20 | 304 | 6 | 6 |  | 8 | 2432 | 0 | 1 | 0 | 0 | 20 | 3
32 | Classroom |  | 0 | Yes | 20 | 909 | 20 | 20 |  | 8 | 7272 | 0 | 1 | 0 | 0 | 20 | 3
34 | Classroom |  | 0 |  |  | 232 | 5 | 0 |  | 8 | 1856 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18
School: | Overbrook Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 825 | 55 |  |  | 720 | 16 | 16 | House fan | 8 | 5760 | 8.5938 | 1 | 8.5938 | 2 | 8.5938 | 2
2 | Classroom | 798 | 53 |  |  | 720 | 16 | 16 | House fan | 8 | 5760 | 8.3125 | 1 | 8.3125 | 2 | 8.3125 | 2
3 | Classroom | 872 | 58 |  |  | 720 | 16 | 16 | House fan | 8 | 5760 | 9.0833 | 1 | 9.0833 | 2 | 9.0833 | 2
4 | Classroom | 838 | 55 |  |  | 528 | 12 | 12 | House fan | 8 | 4224 | 11.9034 | 1 | 11.9034 | 3 | 11.9034 | 3
5 | Classroom | 579 | 38 |  |  | 720 | 16 | 16 | House fan | 8 | 5760 | 6.0312 | 1 | 6.0312 | 2 | 6.0312 | 2
6 | Classroom | 499 | 33 |  |  | 720 | 16 | 16 | House fan | 8 | 5760 | 5.1979 | 1 | 5.1979 | 2 | 5.1979 | 2
7 | Classroom | 816 | 54 |  |  | 768 | 17 | 17 | House fan | 8 | 6144 | 7.9688 | 1 | 7.9688 | 2 | 7.9688 | 2
8 | Classroom | 614 | 40 |  |  | 768 | 17 | 17 | House fan | 8 | 6144 | 5.9961 | 1 | 5.9961 | 2 | 5.9961 | 2
9 | Classroom | 788 | 52 |  |  | 768 | 17 | 17 | House fan | 8 | 6144 | 7.6953 | 1 | 7.6953 | 2 | 7.6953 | 2
12 | Classroom | 522 | 34 |  |  | 720 | 16 | 16 | House fan | 8 | 5760 | 5.4375 | 1 | 5.4375 | 2 | 5.4375 | 2
13 | Classroom | 581 | 38 |  |  | 720 | 16 | 16 | House fan | 8 | 5760 | 6.0521 | 1 | 6.0521 | 2 | 6.0521 | 2
14 | Classroom | 472 | 31 |  |  | 720 | 16 | 16 | House fan | 8 | 5760 | 4.9167 | 1 | 4.9167 | 2 | 4.9167 | 2
15 | Classroom | 412 | 27 |  |  | 720 | 16 | 16 | House fan | 8 | 5760 | 4.2917 | 1 | 4.2917 | 2 | 4.2917 | 2
16 | Classroom | 505 | 33 |  |  | 720 | 16 | 16 | House fan | 8 | 5760 | 5.2604 | 1 | 5.2604 | 2 | 5.2604 | 2
17 | Classroom | 524 | 34 |  |  | 720 | 16 | 16 | House fan | 8 | 5760 | 5.4583 | 1 | 5.4583 | 2 | 5.4583 | 2
18 | Classroom | 508 | 33 |  |  | 768 | 17 | 17 | House fan | 8 | 6144 | 4.9609 | 1 | 4.9609 | 2 | 4.9609 | 2
19 | Classroom | 654 | 43 |  |  | 768 | 17 | 17 | House fan | 8 | 6144 | 6.3867 | 1 | 6.3867 | 2 | 6.3867 | 2
20 | Classroom | 498 | 33 |  |  | 768 | 17 | 17 | House fan | 8 | 6144 | 4.8633 | 1 | 4.8633 | 2 | 4.8633 | 2
- | Boys Bathroom | 826 | 55 |  |  | 736 | 16 | 16 | House fan | 8 | 5888 | 8.4171 | 1 | 8.4171 | 2 | 8.4171 | 2
- | Cafeteria | 1236 | 82 |  |  | 1560 | 35 | 35 | House fan | 8 | 12480 | 5.9423 | 1 | 5.9423 | 2 | 5.9423 | 2
- | Faculty bathroom | 40 | 2 |  |  | 64 | 1 | 1 | House fan | 8 | 512 | 4.6875 | 1 | 4.6875 | 2 | 4.6875 | 2
- | Girls Bathroom | 445 | 29 |  |  | 340 | 7 | 7 | House fan | 8 | 2720 | 9.8162 | 1 | 9.8162 | 2 | 9.8162 | 2
Sheet Last Modified: | 2021-04-30
School: | Overbrook High School
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
10 | - |  | 0 |  |  | 1041 | 23 | 0 |  | 8 | 8328 | 0 | 1 | 0 | 0 | 0 | 0
11 | - |  | 0 |  |  | 1450 | 32 | 0 |  | 8 | 11600 | 0 | 1 | 0 | 0 | 0 | 0
100 | Classroom |  | 0 |  |  | 1409 | 32 | 0 |  | 8 | 11272 | 0 | 1 | 0 | 0 | 0 | 0
100A | Classroom |  | 0 | Yes | 20 | 435 | 9 | 9 |  | 8 | 3480 | 0 | 1 | 0 | 0 | 20 | 3
100B | Classroom |  | 0 | Yes | 20 | 479 | 10 | 10 |  | 8 | 3832 | 0 | 1 | 0 | 0 | 20 | 3
100C | Classroom |  | 0 | Yes | 20 | 1407 | 31 | 31 |  | 8 | 11256 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom |  | 0 | Yes | 20 | 832 | 18 | 18 |  | 8 | 6656 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 |  |  | 742 | 16 | 0 |  | 8 | 5936 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom |  | 0 |  |  | 692 | 15 | 0 |  | 8 | 5536 | 0 | 1 | 0 | 0 | 0 | 0
104 | Classroom |  | 0 |  |  | 649 | 14 | 0 |  | 8 | 5192 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom |  | 0 |  |  | 990 | 22 | 0 |  | 8 | 7920 | 0 | 1 | 0 | 0 | 0 | 0
105A | Classroom |  | 0 |  |  | 228 | 5 | 0 |  | 8 | 1824 | 0 | 1 | 0 | 0 | 0 | 0
106A | Classroom |  | 0 |  |  | 535 | 12 | 0 |  | 8 | 4280 | 0 | 1 | 0 | 0 | 0 | 0
160B | Classroom |  | 0 |  |  | 534 | 12 | 0 |  | 8 | 4272 | 0 | 1 | 0 | 0 | 0 | 0
107 | Classroom |  | 0 |  |  | 703 | 15 | 0 |  | 8 | 5624 | 0 | 1 | 0 | 0 | 0 | 0
108 | Classroom |  | 0 |  |  | 677 | 15 | 0 |  | 8 | 5416 | 0 | 1 | 0 | 0 | 0 | 0
109A | Classroom |  | 0 |  |  | 551 | 12 | 0 |  | 8 | 4408 | 0 | 1 | 0 | 0 | 0 | 0
109B | Classroom |  | 0 |  |  | 507 | 11 | 0 |  | 8 | 4056 | 0 | 1 | 0 | 0 | 0 | 0
110 | Classroom |  | 0 |  |  | 931 | 21 | 0 |  | 8 | 7448 | 0 | 1 | 0 | 0 | 0 | 0
117 | Classroom |  | 0 |  |  | 515 | 11 | 0 |  | 8 | 4120 | 0 | 1 | 0 | 0 | 0 | 0
118 | Classroom |  | 0 |  |  | 556 | 12 | 0 |  | 8 | 4448 | 0 | 1 | 0 | 0 | 0 | 0
119 | Classroom |  | 0 |  |  | 753 | 17 | 0 |  | 8 | 6024 | 0 | 1 | 0 | 0 | 0 | 0
120 | Classroom |  | 0 |  |  | 1026 | 23 | 0 |  | 8 | 8208 | 0 | 1 | 0 | 0 | 0 | 0
121 | Classroom |  | 0 |  |  | 1048 | 23 | 0 |  | 8 | 8384 | 0 | 1 | 0 | 0 | 0 | 0
200 | Classroom |  | 0 |  |  | 304 | 6 | 0 |  | 8 | 2432 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom |  | 0 |  |  | 496 | 11 | 0 |  | 8 | 3968 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom |  | 0 |  |  | 490 | 11 | 0 |  | 8 | 3920 | 0 | 1 | 0 | 0 | 0 | 0
202 | Classroom |  | 0 |  |  | 486 | 11 | 0 |  | 8 | 3888 | 0 | 1 | 0 | 0 | 0 | 0
204 | Classroom |  | 0 |  |  | 881 | 20 | 0 |  | 8 | 7048 | 0 | 1 | 0 | 0 | 0 | 0
205 | Classroom |  | 0 |  |  | 733 | 16 | 0 |  | 8 | 5864 | 0 | 1 | 0 | 0 | 0 | 0
206 | Classroom |  | 0 |  |  | 1003 | 22 | 0 |  | 8 | 8024 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom |  | 0 |  |  | 718 | 16 | 0 |  | 8 | 5744 | 0 | 1 | 0 | 0 | 0 | 0
209 | Classroom |  | 0 |  |  | 337 | 7 | 0 |  | 8 | 2696 | 0 | 1 | 0 | 0 | 0 | 0
210 | Classroom |  | 0 |  |  | 460 | 10 | 0 |  | 8 | 3680 | 0 | 1 | 0 | 0 | 0 | 0
211 | Classroom |  | 0 |  |  | 713 | 16 | 0 |  | 8 | 5704 | 0 | 1 | 0 | 0 | 0 | 0
212 | Classroom |  | 0 |  |  | 728 | 16 | 0 |  | 8 | 5824 | 0 | 1 | 0 | 0 | 0 | 0
213 | Classroom |  | 0 |  |  | 902 | 20 | 0 |  | 8 | 7216 | 0 | 1 | 0 | 0 | 0 | 0
214 | Classroom |  | 0 |  |  | 796 | 18 | 0 |  | 8 | 6368 | 0 | 1 | 0 | 0 | 0 | 0
215 | Classroom |  | 0 |  |  | 3413 | 77 | 0 |  | 8 | 27304 | 0 | 1.062 | 0 | 0 | 0 | 0
216 | Classroom |  | 0 |  |  | 850 | 19 | 0 |  | 8 | 6800 | 0 | 1 | 0 | 0 | 0 | 0
217 | Classroom |  | 0 |  |  | 712 | 16 | 0 |  | 8 | 5696 | 0 | 1 | 0 | 0 | 0 | 0
218 | Classroom |  | 0 |  |  | 700 | 15 | 0 |  | 8 | 5600 | 0 | 1 | 0 | 0 | 0 | 0
219 | Classroom |  | 0 |  |  | 719 | 16 | 0 |  | 8 | 5752 | 0 | 1 | 0 | 0 | 0 | 0
220 | Classroom |  | 0 |  |  | 359 | 8 | 0 |  | 8 | 2872 | 0 | 1 | 0 | 0 | 0 | 0
221 | Classroom |  | 0 |  |  | 877 | 19 | 0 |  | 8 | 7016 | 0 | 1 | 0 | 0 | 0 | 0
222 | Classroom |  | 0 |  |  | 877 | 19 | 0 |  | 8 | 7016 | 0 | 1 | 0 | 0 | 0 | 0
223 | Classroom |  | 0 |  |  | 729 | 16 | 0 |  | 8 | 5832 | 0 | 1 | 0 | 0 | 0 | 0
224 | Classroom |  | 0 |  |  | 731 | 16 | 0 |  | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
225 | Classroom |  | 0 |  |  | 694 | 15 | 0 |  | 8 | 5552 | 0 | 1 | 0 | 0 | 0 | 0
300 | Classroom |  | 0 |  |  | 747 | 16 | 0 |  | 8 | 5976 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom |  | 0 |  |  | 724 | 16 | 0 |  | 8 | 5792 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom |  | 0 |  |  | 737 | 16 | 0 |  | 8 | 5896 | 0 | 1 | 0 | 0 | 0 | 0
303 | Classroom |  | 0 |  |  | 907 | 20 | 0 |  | 8 | 7256 | 0 | 1 | 0 | 0 | 0 | 0
304 | Classroom |  | 0 |  |  | 941 | 21 | 0 |  | 8 | 7528 | 0 | 1 | 0 | 0 | 0 | 0
305 | Classroom |  | 0 |  |  | 724 | 16 | 0 |  | 8 | 5792 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom |  | 0 |  |  | 738 | 16 | 0 |  | 8 | 5904 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom |  | 0 |  |  | 739 | 16 | 0 |  | 8 | 5912 | 0 | 1 | 0 | 0 | 0 | 0
308 | Classroom |  | 0 |  |  | 834 | 18 | 0 |  | 8 | 6672 | 0 | 1 | 0 | 0 | 0 | 0
309 | Classroom |  | 0 |  |  | 733 | 16 | 0 |  | 8 | 5864 | 0 | 1 | 0 | 0 | 0 | 0
311 | Classroom |  | 0 |  |  | 721 | 16 | 0 |  | 8 | 5768 | 0 | 1 | 0 | 0 | 0 | 0
312 | Classroom |  | 0 |  |  | 704 | 16 | 0 |  | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
313 | Classroom |  | 0 |  |  | 491 | 11 | 0 |  | 8 | 3928 | 0 | 1 | 0 | 0 | 0 | 0
314 | Classroom |  | 0 |  |  | 669 | 15 | 0 |  | 8 | 5352 | 0 | 1 | 0 | 0 | 0 | 0
315 | Classroom |  | 0 |  |  | 673 | 15 | 0 |  | 8 | 5384 | 0 | 1 | 0 | 0 | 0 | 0
316 | Classroom |  | 0 | Yes | 20 | 762 | 17 | 17 |  | 8 | 6096 | 0 | 1 | 0 | 0 | 20 | 3
317 | Classroom |  | 0 | Yes | 20 | 917 | 20 | 20 |  | 8 | 7336 | 0 | 1 | 0 | 0 | 20 | 3
318 | Classroom |  | 0 |  |  | 669 | 15 | 0 |  | 8 | 5352 | 0 | 1 | 0 | 0 | 0 | 0
319 | Classroom |  | 0 |  |  | 681 | 15 | 0 |  | 8 | 5448 | 0 | 1 | 0 | 0 | 0 | 0
320 | Classroom |  | 0 |  |  | 724 | 16 | 0 |  | 8 | 5792 | 0 | 1 | 0 | 0 | 0 | 0
321 | Classroom |  | 0 |  |  | 712 | 16 | 0 |  | 8 | 5696 | 0 | 1 | 0 | 0 | 0 | 0
322 | Classroom |  | 0 |  |  | 499 | 11 | 0 |  | 8 | 3992 | 0 | 1 | 0 | 0 | 0 | 0
323 | Classroom |  | 0 |  |  | 437 | 9 | 0 |  | 8 | 3496 | 0 | 1 | 0 | 0 | 0 | 0
324 | Classroom |  | 0 |  |  | 801 | 18 | 0 |  | 8 | 6408 | 0 | 1 | 0 | 0 | 0 | 0
325 | Classroom |  | 0 |  |  | 936 | 21 | 0 |  | 8 | 7488 | 0 | 1 | 0 | 0 | 0 | 0
326 | Classroom |  | 0 |  |  | 690 | 15 | 0 |  | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
327 | Classroom |  | 0 |  |  | 191 | 4 | 0 |  | 8 | 1528 | 0 | 1 | 0 | 0 | 0 | 0
328 | Classroom |  | 0 |  |  | 683 | 15 | 0 |  | 8 | 5464 | 0 | 1 | 0 | 0 | 0 | 0
329 | Classroom |  | 0 |  |  | 711 | 16 | 0 |  | 8 | 5688 | 0 | 1 | 0 | 0 | 0 | 0
330 | Classroom |  | 0 |  |  | 690 | 15 | 0 |  | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
331 | Classroom |  | 0 |  |  | 204 | 4 | 0 |  | 8 | 1632 | 0 | 1 | 0 | 0 | 0 | 0
332 | Classroom |  | 0 |  |  | 687 | 15 | 0 |  | 8 | 5496 | 0 | 1 | 0 | 0 | 0 | 0
333 | Classroom |  | 0 |  |  | 720 | 16 | 0 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
334 | Classroom |  | 0 |  |  | 817 | 18 | 0 |  | 8 | 6536 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office |  | 0 |  |  | 1057 | 24 | 0 |  | 8 | 8456 | 0 | 1 | 0 | 0 | 0 | 0
- | Principal Office |  | 0 |  |  | 562 | 12 | 0 |  | 8 | 4496 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium Balcony |  | 0 |  |  | 1436 | 32 | 0 |  | 8 | 11488 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium |  | 0 |  |  | 8711 | 197 | 0 |  | 8 | 69688 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | Teachers Lounge |  | 0 |  |  | 310 | 7 | 0 |  | 8 | 2480 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria A |  | 0 |  |  | 2778 | 63 | 0 |  | 8 | 22224 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria B |  | 0 |  |  | 4516 | 102 | 0 |  | 8 | 36128 | 0 | 1.062 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29
School: | Academy @ Palumbo High School
Vendor: | EMCOR Fluidics
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
103 | Graphics Arts | 1248 | 83 |  |  | 1058 | 24 | 24 | Air Handling Unit | 8 | 8464 | 8.8469 | 1 | 8.8469 | 2 | 8.8469 | 2
104 | Fine Arts | 271 | 18 |  |  | 782 | 17 | 17 | Air Handling Unit | 8 | 6256 | 2.5991 | 1 | 2.5991 | 1 | 2.5991 | 1
118 | Conference Room | 1440 | 96 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 15.6522 | 1 | 15.6522 | 3 | 15.6522 | 3
129 | Main Office | 723 | 48 |  |  | 528 | 12 | 12 | Air Handling Unit | 8 | 4224 | 10.2699 | 1 | 10.2699 | 3 | 10.2699 | 3
132 | Mixed Choir | 736 | 49 |  |  | 966 | 21 | 21 | Air Handling Unit | 8 | 7728 | 5.7143 | 1 | 5.7143 | 2 | 5.7143 | 2
134 | Music Theory | 1170 | 78 |  |  | 946 | 21 | 21 | Air Handling Unit | 8 | 7568 | 9.2759 | 1 | 9.2759 | 2 | 9.2759 | 2
135 | Intro to Music | 1709 | 113 |  |  | 968 | 22 | 22 | Air Handling Unit | 8 | 7744 | 13.2412 | 1 | 13.2412 | 3 | 13.2412 | 3
136 | Music Equipment Storage | 609 | 40 |  |  | 396 | 9 | 9 | Air Handling Unit | 8 | 3168 | 11.5341 | 1 | 11.5341 | 3 | 11.5341 | 3
204 | Creative Writing | 843 | 56 |  |  | 660 | 15 | 15 | Air Handling Unit | 8 | 5280 | 9.5795 | 1 | 9.5795 | 2 | 9.5795 | 2
205 | Computer Lab | 653 | 43 |  |  | 768 | 17 | 17 | Air Handling Unit | 8 | 6144 | 6.377 | 1 | 6.377 | 2 | 6.377 | 2
206 | Environment Club | 713 | 47 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 7.75 | 1 | 7.75 | 2 | 7.75 | 2
207 | Language & Journalism | 1069 | 71 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 11.6196 | 1 | 11.6196 | 3 | 11.6196 | 3
212 | Visitor's Locker Room | 615 | 41 |  |  | 720 | 16 | 16 | Air Handling Unit | 8 | 5760 | 6.4062 | 1 | 6.4062 | 2 | 6.4062 | 2
221 | History | 618 | 41 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 6.7174 | 1 | 6.7174 | 2 | 6.7174 | 2
223 | Literature | 750 | 50 |  |  | 1104 | 25 | 25 | Air Handling Unit | 8 | 8832 | 5.0951 | 1 | 5.0951 | 2 | 5.0951 | 2
224 | English / History | 113 | 7 |  |  | 660 | 15 | 7 | Air Handling Unit | 8 | 5280 | 1.2841 | 1 | 1.2841 | 1 | 1.2841 | 1
231 | Office | 595 | 39 |  |  | 484 | 11 | 11 | Air Handling Unit | 8 | 3872 | 9.22 | 1 | 9.22 | 2 | 9.22 | 2
301 | Forensics / Algebra 2 | 604 | 40 |  |  | 528 | 12 | 12 | Air Handling Unit | 8 | 4224 | 8.5795 | 1 | 8.5795 | 2 | 8.5795 | 2
302 | Dean's Office | 1510 | 100 |  |  | 440 | 10 | 10 | Air Handling Unit | 8 | 3520 | 25.7386 | 1 | 25.7386 | 4 | 25.7386 | 4
305 | History | 257 | 17 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 2.7935 | 1 | 2.7935 | 1 | 2.7935 | 1
306 | Spanish | 554 | 36 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 6.0217 | 1 | 6.0217 | 2 | 6.0217 | 2
307 | American History | 282 | 18 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 3.0652 | 1 | 3.0652 | 1 | 3.0652 | 1
312 | Cardio & Weight Lifting | 615 | 41 |  |  | 720 | 16 | 16 | Air Handling Unit | 8 | 5760 | 6.4062 | 1 | 6.4062 | 2 | 6.4062 | 2
321 | Spanish | 666 | 44 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 7.2391 | 1 | 7.2391 | 2 | 7.2391 | 2
321 | History | 532 | 35 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 5.7826 | 1 | 5.7826 | 2 | 5.7826 | 2
322 | History | 1582 | 105 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 17.1957 | 1 | 17.1957 | 3 | 17.1957 | 3
323 | Spanish | 567 | 37 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 6.163 | 1 | 6.163 | 2 | 6.163 | 2
332 | Black History | 84 | 5 |  |  | 638 | 14 | 5 | Air Handling Unit | 8 | 5104 | 0.98746 | 1 | 0.98746 | 0 | 0.98746 | 0
333 | History | 1066 | 71 |  |  | 792 | 18 | 18 | Air Handling Unit | 8 | 6336 | 10.0947 | 1 | 10.0947 | 3 | 10.0947 | 3
334 | Psychologist | 0 | 0 |  |  | 567 | 12 | 0 | Air Handling Unit | 8 | 4536 | 0 | 1 | 0 | 0 | 0 | 0
336 | Spanish | 0 | 0 |  |  | 1058 | 24 | 0 | Air Handling Unit | 8 | 8464 | 0 | 1 | 0 | 0 | 0 | 0
403 | Physics Lab | 322 | 21 |  |  | 1056 | 24 | 21 | Air Handling Unit | 8 | 8448 | 2.2869 | 1 | 2.2869 | 1 | 2.2869 | 1
407 | Biology Lab | 587 | 39 |  |  | 1440 | 32 | 32 | Air Handling Unit | 8 | 11520 | 3.0573 | 1 | 3.0573 | 1 | 3.0573 | 1
411 | Chemistry | 651 | 43 |  |  | 720 | 16 | 16 | Air Handling Unit | 8 | 5760 | 6.7812 | 1 | 6.7812 | 2 | 6.7812 | 2
412 | Unknown | 668 | 44 |  |  | 720 | 16 | 16 | Air Handling Unit | 8 | 5760 | 6.9583 | 1 | 6.9583 | 2 | 6.9583 | 2
421 | Spanish | 117 | 7 |  |  | 690 | 15 | 7 | Air Handling Unit | 8 | 5520 | 1.2717 | 1 | 1.2717 | 1 | 1.2717 | 1
422 | Chinese | 965 | 64 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 10.4891 | 1 | 10.4891 | 3 | 10.4891 | 3
423 | English 1 | 628 | 41 |  |  | 690 | 15 | 15 | Air Handling Unit | 8 | 5520 | 6.8261 | 1 | 6.8261 | 2 | 6.8261 | 2
432 | Literature | 484 | 32 |  |  | 760 | 17 | 17 | Air Handling Unit | 8 | 6080 | 4.7763 | 1 | 4.7763 | 2 | 4.7763 | 2
433 | History | 142 | 9 |  |  | 760 | 17 | 9 | Air Handling Unit | 8 | 6080 | 1.4013 | 1 | 1.4013 | 1 | 1.4013 | 1
436 | Science | 769 | 51 |  |  | 1058 | 24 | 24 | Air Handling Unit | 8 | 8464 | 5.4513 | 1 | 5.4513 | 2 | 5.4513 | 2
437 | Geometry | 723 | 48 |  |  | 552 | 12 | 12 | Air Handling Unit | 8 | 4416 | 9.8234 | 1 | 9.8234 | 2 | 9.8234 | 2
501 | Algebra 2 | 677 | 45 |  |  | 768 | 17 | 17 | Air Handling Unit | 8 | 6144 | 6.6113 | 1 | 6.6113 | 2 | 6.6113 | 2
502 | Forensics / Algebra | 415 | 27 |  |  | 768 | 17 | 17 | Air Handling Unit | 8 | 6144 | 4.0527 | 1 | 4.0527 | 2 | 4.0527 | 2
503 | Statistics | 483 | 32 |  |  | 768 | 17 | 17 | Air Handling Unit | 8 | 6144 | 4.7168 | 1 | 4.7168 | 2 | 4.7168 | 2
504 | Algebra | 190 | 12 |  |  | 768 | 17 | 12 | Air Handling Unit | 8 | 6144 | 1.8555 | 1 | 1.8555 | 1 | 1.8555 | 1
506 | Algebra | 707 | 47 |  |  | 768 | 17 | 17 | Air Handling Unit | 8 | 6144 | 6.9043 | 1 | 6.9043 | 2 | 6.9043 | 2
507 | Computer Science | 420 | 28 |  |  | 768 | 17 | 17 | Air Handling Unit | 8 | 6144 | 4.1016 | 1 | 4.1016 | 2 | 4.1016 | 2
521 | Algebra | 190 | 12 |  |  | 690 | 15 | 12 | Air Handling Unit | 8 | 5520 | 2.0652 | 1 | 2.0652 | 1 | 2.0652 | 1
522 | Math | 2026 | 135 |  |  | 968 | 22 | 22 | Air Handling Unit | 8 | 7744 | 15.6973 | 1 | 15.6973 | 3 | 15.6973 | 3
524 | Algebra | 1222 | 81 |  |  | 770 | 17 | 17 | Air Handling Unit | 8 | 6160 | 11.9026 | 1 | 11.9026 | 3 | 11.9026 | 3
529 | Film | 493 | 32 |  |  | 660 | 15 | 15 | Air Handling Unit | 8 | 5280 | 5.6023 | 1 | 5.6023 | 2 | 5.6023 | 2
201A | Exercise | 323 | 21 |  |  | 23 | 0 | 0 | Air Handling Unit | 8 | 184 | 105.3261 | 1 | 105.3261 | 5 | 105.3261 | 5
201B | Exercise | 627 | 41 |  |  | 1771 | 40 | 40 | Air Handling Unit | 8 | 14168 | 2.6553 | 1 | 2.6553 | 1 | 2.6553 | 1
304A | Computer Lab | 571 | 38 |  |  | 500 | 11 | 11 | Air Handling Unit | 8 | 4000 | 8.565 | 1 | 8.565 | 2 | 8.565 | 2
304B | Computer Lab | 637 | 42 |  |  | 446 | 10 | 10 | Air Handling Unit | 8 | 3568 | 10.7119 | 1 | 10.7119 | 3 | 10.7119 | 3
329A | Admin. Office | 605 | 40 |  |  | 660 | 15 | 15 | Air Handling Unit | 8 | 5280 | 6.875 | 1 | 6.875 | 2 | 6.875 | 2
329B | Admin. Office | 196 | 13 |  |  | 660 | 15 | 13 | Air Handling Unit | 8 | 5280 | 2.2273 | 1 | 2.2273 | 1 | 2.2273 | 1
337A | Study Skills / AS | 860 | 57 |  |  | 337 | 7 | 7 | Air Handling Unit | 8 | 2696 | 19.1395 | 1 | 19.1395 | 3 | 19.1395 | 3
337B | Study Skills / AS | 975 | 65 |  |  | 552 | 12 | 12 | Air Handling Unit | 8 | 4416 | 13.2473 | 1 | 13.2473 | 3 | 13.2473 | 3
404A | Chemistry Lab | 230 | 15 |  |  | 720 | 16 | 15 | Air Handling Unit | 8 | 5760 | 2.3958 | 1 | 2.3958 | 1 | 2.3958 | 1
404B | Chemistry Lab | 2087 | 139 |  |  | 720 | 16 | 16 | Air Handling Unit | 8 | 5760 | 21.7396 | 1 | 21.7396 | 3 | 21.7396 | 3
409A | Office | 43 | 2 |  |  | 280 | 6 | 2 | Air Handling Unit | 8 | 2240 | 1.1518 | 1 | 1.1518 | 1 | 1.1518 | 1
409B | Office | 123 | 8 |  |  | 280 | 6 | 6 | Air Handling Unit | 8 | 2240 | 3.2946 | 1 | 3.2946 | 1 | 3.2946 | 1
429A | Robotics | 574 | 38 |  |  | 1320 | 30 | 30 | Air Handling Unit | 8 | 10560 | 3.2614 | 1 | 3.2614 | 1 | 3.2614 | 1
429B | Robotics | 652 | 43 |  |  | 429 | 9 | 9 | Air Handling Unit | 8 | 3432 | 11.3986 | 1 | 11.3986 | 3 | 11.3986 | 3
434A | Algebra | 541 | 36 |  |  | 434 | 9 | 9 | Air Handling Unit | 8 | 3472 | 9.3491 | 1 | 9.3491 | 2 | 9.3491 | 2
434B | Algebra | 276 | 18 |  |  | 1188 | 27 | 18 | Air Handling Unit | 8 | 9504 | 1.7424 | 1 | 1.7424 | 1 | 1.7424 | 1
B14 | Storage | 594 | 39 |  |  | 374 | 8 | 8 | Air Handling Unit | 8 | 2992 | 11.9118 | 1 | 11.9118 | 3 | 11.9118 | 3
B15 | Storage | 237 | 15 |  |  | 384 | 8 | 8 | Air Handling Unit | 8 | 3072 | 4.6289 | 1 | 4.6289 | 2 | 4.6289 | 2
B16 | Storage | 37 | 2 |  |  | 90 | 2 | 2 | Air Handling Unit | 8 | 720 | 3.0833 | 1 | 3.0833 | 1 | 3.0833 | 1
B17 | Storage | 326 | 21 |  |  | 364 | 8 | 8 | Air Handling Unit | 8 | 2912 | 6.717 | 1 | 6.717 | 2 | 6.717 | 2
B19 | Storage | 723 | 48 |  |  | 1013 | 23 | 23 | Air Handling Unit | 8 | 8104 | 5.3529 | 1 | 5.3529 | 2 | 5.3529 | 2
B24-A | Storage | 723 | 48 |  |  | 1013 | 23 | 23 | Air Handling Unit | 8 | 8104 | 5.3529 | 1 | 5.3529 | 2 | 5.3529 | 2
B24-B | Storage | 461 | 30 |  |  | 1013 | 23 | 23 | Air Handling Unit | 8 | 8104 | 3.4131 | 1 | 3.4131 | 1 | 3.4131 | 1
- | Auditorium | 16042 | 1069 |  |  | 12420 | 282 | 282 | Air Handling Unit | 8 | 99360 | 9.6872 | 1.4912 | 14.4451 | 3 | 14.4451 | 3
- | Gyms and Cafeteria | 7343 | 489 |  |  | 21078 | 479 | 479 | Air Handling Unit | 8 | 168624 | 2.6128 | 2.3523 | 6.1462 | 2 | 6.1462 | 2
- | Home Locker Room | 417 | 27 |  |  | 720 | 16 | 16 | Air Handling Unit | 8 | 5760 | 4.3438 | 1 | 4.3438 | 2 | 4.3438 | 2
- | Locker Room | 417 | 27 |  |  | 720 | 16 | 16 | Air Handling Unit | 8 | 5760 | 4.3438 | 1 | 4.3438 | 2 | 4.3438 | 2
- | Main Library | 1095 | 73 |  |  | 4608 | 104 | 73 | Air Handling Unit | 8 | 36864 | 1.7822 | 1.062 | 1.8928 | 1 | 1.8928 | 1
- | Library A | 1256 | 83 |  |  | 238 | 5 | 5 | Air Handling Unit | 8 | 1904 | 39.5798 | 1 | 39.5798 | 4 | 39.5798 | 4
- | Library B | 1078 | 71 |  |  | 238 | 5 | 5 | Air Handling Unit | 8 | 1904 | 33.9706 | 1 | 33.9706 | 4 | 33.9706 | 4
- | Library Storage | 917 | 61 |  |  | 288 | 6 | 6 | Air Handling Unit | 8 | 2304 | 23.8802 | 1 | 23.8802 | 3 | 23.8802 | 3
- | Men's Room | 50 | 3 |  |  | 252 | 5 | 3 | Air Handling Unit | 8 | 2016 | 1.4881 | 1 | 1.4881 | 1 | 1.4881 | 1
- | Ladies Room | 46 | 3 |  |  | 252 | 5 | 3 | Air Handling Unit | 8 | 2016 | 1.369 | 1 | 1.369 | 1 | 1.369 | 1
- | Safe Room | 1158 | 77 |  |  | 675 | 15 | 15 | Air Handling Unit | 8 | 5400 | 12.8667 | 1 | 12.8667 | 3 | 12.8667 | 3
B18 | Storage | 477 | 31 |  |  | 723 | 16 | 16 |  | 8 | 5784 | 4.9481 | 1 | 4.9481 | 2 | 4.9481 | 2
B20 | Storage | 461 | 30 |  |  | 1013 | 23 | 23 |  | 8 | 8104 | 3.4131 | 1 | 3.4131 | 1 | 3.4131 | 1
B21 | Storage | 736 | 49 |  |  | 966 | 21 | 21 |  | 8 | 7728 | 5.7143 | 1 | 5.7143 | 2 | 5.7143 | 2
B22 | Storage | 723 | 48 |  |  | 528 | 12 | 12 |  | 8 | 4224 | 10.2699 | 1 | 10.2699 | 3 | 10.2699 | 3
B23 | Storage | 323 | 21 |  |  | 23 | 0 | 0 |  | 8 | 184 | 105.3261 | 1 | 105.3261 | 5 | 105.3261 | 5
B24 | Storage | 627 | 41 |  |  | 1771 | 40 | 40 |  | 8 | 14168 | 2.6553 | 1 | 2.6553 | 1 | 2.6553 | 1
B25 | Storage | 843 | 56 |  |  | 660 | 15 | 15 |  | 8 | 5280 | 9.5795 | 1 | 9.5795 | 2 | 9.5795 | 2
B26 | Storage | 113 | 7 |  |  | 660 | 15 | 7 |  | 8 | 5280 | 1.2841 | 1 | 1.2841 | 1 | 1.2841 | 1
B27 | Storage | 595 | 39 |  |  | 484 | 11 | 11 |  | 8 | 3872 | 9.22 | 1 | 9.22 | 2 | 9.22 | 2
B28 | Storage | 604 | 40 |  |  | 528 | 12 | 12 |  | 8 | 4224 | 8.5795 | 1 | 8.5795 | 2 | 8.5795 | 2
B29 | Storage | 1510 | 100 |  |  | 440 | 10 | 10 |  | 8 | 3520 | 25.7386 | 1 | 25.7386 | 4 | 25.7386 | 4
B30 | Storage | 571 | 38 |  |  | 500 | 11 | 11 |  | 8 | 4000 | 8.565 | 1 | 8.565 | 2 | 8.565 | 2
B31 | Storage | 637 | 42 |  |  | 446 | 10 | 10 |  | 8 | 3568 | 10.7119 | 1 | 10.7119 | 3 | 10.7119 | 3
B32 | Storage | 666 | 44 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 7.2391 | 1 | 7.2391 | 2 | 7.2391 | 2
B33 | Storage | 567 | 37 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 6.163 | 1 | 6.163 | 2 | 6.163 | 2
B34 | Storage | 605 | 40 |  |  | 660 | 15 | 15 |  | 8 | 5280 | 6.875 | 1 | 6.875 | 2 | 6.875 | 2
B35 | Storage | 196 | 13 |  |  | 660 | 15 | 13 |  | 8 | 5280 | 2.2273 | 1 | 2.2273 | 1 | 2.2273 | 1
B36 | Storage | 84 | 5 |  |  | 638 | 14 | 5 |  | 8 | 5104 | 0.98746 | 1 | 0.98746 | 0 | 0.98746 | 0
B37 | Storage | 1066 | 71 |  |  | 792 | 18 | 18 |  | 8 | 6336 | 10.0947 | 1 | 10.0947 | 3 | 10.0947 | 3
B38 | Storage | 0 | 0 |  |  | 567 | 12 | 0 |  | 8 | 4536 | 0 | 1 | 0 | 0 | 0 | 0
B39 | Storage | 0 | 0 |  |  | 1058 | 24 | 0 |  | 8 | 8464 | 0 | 1 | 0 | 0 | 0 | 0
B40 | Storage | 860 | 57 |  |  | 337 | 7 | 7 |  | 8 | 2696 | 19.1395 | 1 | 19.1395 | 3 | 19.1395 | 3
B41 | Storage | 975 | 65 |  |  | 552 | 12 | 12 |  | 8 | 4416 | 13.2473 | 1 | 13.2473 | 3 | 13.2473 | 3
B42 | Storage | 322 | 21 |  |  | 1056 | 24 | 21 |  | 8 | 8448 | 2.2869 | 1 | 2.2869 | 1 | 2.2869 | 1
B43 | Storage | 230 | 15 |  |  | 720 | 16 | 15 |  | 8 | 5760 | 2.3958 | 1 | 2.3958 | 1 | 2.3958 | 1
B44 | Storage | 2087 | 139 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 21.7396 | 1 | 21.7396 | 3 | 21.7396 | 3
B45 | Storage | 628 | 41 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 6.8261 | 1 | 6.8261 | 2 | 6.8261 | 2
B46 | Storage | 574 | 38 |  |  | 1320 | 30 | 30 |  | 8 | 10560 | 3.2614 | 1 | 3.2614 | 1 | 3.2614 | 1
B47 | Storage | 652 | 43 |  |  | 429 | 9 | 9 |  | 8 | 3432 | 11.3986 | 1 | 11.3986 | 3 | 11.3986 | 3
B48 | Storage | 484 | 32 |  |  | 760 | 17 | 17 |  | 8 | 6080 | 4.7763 | 1 | 4.7763 | 2 | 4.7763 | 2
B49 | Storage | 142 | 9 |  |  | 760 | 17 | 9 |  | 8 | 6080 | 1.4013 | 1 | 1.4013 | 1 | 1.4013 | 1
B50 | Storage | 541 | 36 |  |  | 434 | 9 | 9 |  | 8 | 3472 | 9.3491 | 1 | 9.3491 | 2 | 9.3491 | 2
B51 | Storage | 276 | 18 |  |  | 1188 | 27 | 18 |  | 8 | 9504 | 1.7424 | 1 | 1.7424 | 1 | 1.7424 | 1
B52 | Storage | 769 | 51 |  |  | 1058 | 24 | 24 |  | 8 | 8464 | 5.4513 | 1 | 5.4513 | 2 | 5.4513 | 2
B53 | Storage | 723 | 48 |  |  | 552 | 12 | 12 |  | 8 | 4416 | 9.8234 | 1 | 9.8234 | 2 | 9.8234 | 2
B54 | Storage | 677 | 45 |  |  | 768 | 17 | 17 |  | 8 | 6144 | 6.6113 | 1 | 6.6113 | 2 | 6.6113 | 2
B55 | Storage | 415 | 27 |  |  | 768 | 17 | 17 |  | 8 | 6144 | 4.0527 | 1 | 4.0527 | 2 | 4.0527 | 2
B56 | Storage | 483 | 32 |  |  | 768 | 17 | 17 |  | 8 | 6144 | 4.7168 | 1 | 4.7168 | 2 | 4.7168 | 2
B57 | Storage | 1222 | 81 |  |  | 770 | 17 | 17 |  | 8 | 6160 | 11.9026 | 1 | 11.9026 | 3 | 11.9026 | 3
B58 | Storage | 493 | 32 |  |  | 660 | 15 | 15 |  | 8 | 5280 | 5.6023 | 1 | 5.6023 | 2 | 5.6023 | 2
B59 | Storage | 1158 | 77 |  |  |  | 0 | 0
B60 | Storage | 26166 | 1744 |  |  |  | 0 | 0
B61 | Storage | 594 | 39 |  |  | 374 | 8 | 8 |  | 8 | 2992 | 11.9118 | 1 | 11.9118 | 3 | 11.9118 | 3
B62 | Storage | 237 | 15 |  |  | 384 | 8 | 8 |  | 8 | 3072 | 4.6289 | 1 | 4.6289 | 2 | 4.6289 | 2
B63 | Storage | 37 | 2 |  |  | 90 | 2 | 2 |  | 8 | 720 | 3.0833 | 1 | 3.0833 | 1 | 3.0833 | 1
B64 | Storage | 1170 | 78 |  |  | 946 | 21 | 21 |  | 8 | 7568 | 9.2759 | 1 | 9.2759 | 2 | 9.2759 | 2
B65 | Storage | 1709 | 113 |  |  | 968 | 22 | 22 |  | 8 | 7744 | 13.2412 | 1 | 13.2412 | 3 | 13.2412 | 3
B66 | Storage | 609 | 40 |  |  | 396 | 9 | 9 |  | 8 | 3168 | 11.5341 | 1 | 11.5341 | 3 | 11.5341 | 3
B67 | Storage | 1248 | 83 |  |  | 1058 | 24 | 24 |  | 8 | 8464 | 8.8469 | 1 | 8.8469 | 2 | 8.8469 | 2
B68 | Storage | 271 | 18 |  |  | 782 | 17 | 17 |  | 8 | 6256 | 2.5991 | 1 | 2.5991 | 1 | 2.5991 | 1
B69 | Storage | 1440 | 96 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 15.6522 | 1 | 15.6522 | 3 | 15.6522 | 3
B70 | Storage | 653 | 43 |  |  | 768 | 17 | 17 |  | 8 | 6144 | 6.377 | 1 | 6.377 | 2 | 6.377 | 2
B71 | Storage | 713 | 47 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 7.75 | 1 | 7.75 | 2 | 7.75 | 2
B72 | Storage | 1069 | 71 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 11.6196 | 1 | 11.6196 | 3 | 11.6196 | 3
B73 | Storage | 615 | 41 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 6.4062 | 1 | 6.4062 | 2 | 6.4062 | 2
B74 | Storage | 417 | 27 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 4.3438 | 1 | 4.3438 | 2 | 4.3438 | 2
B75 | Storage | 618 | 41 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 6.7174 | 1 | 6.7174 | 2 | 6.7174 | 2
B76 | Storage | 750 | 50 |  |  | 1104 | 25 | 25 |  | 8 | 8832 | 5.0951 | 1 | 5.0951 | 2 | 5.0951 | 2
B77 | Storage | 257 | 17 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 2.7935 | 1 | 2.7935 | 1 | 2.7935 | 1
B78 | Storage | 554 | 36 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 6.0217 | 1 | 6.0217 | 2 | 6.0217 | 2
B79 | Storage | 282 | 18 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 3.0652 | 1 | 3.0652 | 1 | 3.0652 | 1
B80 | Storage | 615 | 41 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 6.4062 | 1 | 6.4062 | 2 | 6.4062 | 2
B81 | Storage | 532 | 35 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 5.7826 | 1 | 5.7826 | 2 | 5.7826 | 2
B82 | Storage | 1582 | 105 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 17.1957 | 1 | 17.1957 | 3 | 17.1957 | 3
B83 | Storage | 917 | 61 |  |  | N/A | 0 | 0
B84 | Storage | 1256 | 83 |  |  | N/A | 0 | 0
B85 | Storage | 1078 | 71 |  |  | N/A | 0 | 0
B86 | Storage | 587 | 39 |  |  | 1440 | 32 | 32 |  | 8 | 11520 | 3.0573 | 1 | 3.0573 | 1 | 3.0573 | 1
B87 | Storage | 651 | 43 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 6.7812 | 1 | 6.7812 | 2 | 6.7812 | 2
B88 | Storage | 668 | 44 |  |  | 720 | 16 | 16 |  | 8 | 5760 | 6.9583 | 1 | 6.9583 | 2 | 6.9583 | 2
B89 | Storage | 117 | 7 |  |  | 690 | 15 | 7 |  | 8 | 5520 | 1.2717 | 1 | 1.2717 | 1 | 1.2717 | 1
B90 | Storage | 965 | 64 |  |  | 690 | 15 | 15 |  | 8 | 5520 | 10.4891 | 1 | 10.4891 | 3 | 10.4891 | 3
B91 | Storage | 417 | 27 |  |  |  | 0 | 0
B92 | Storage | 190 | 12 |  |  | 768 | 17 | 12 |  | 8 | 6144 | 1.8555 | 1 | 1.8555 | 1 | 1.8555 | 1
B93 | Storage | 707 | 47 |  |  | 768 | 17 | 17 |  | 8 | 6144 | 6.9043 | 1 | 6.9043 | 2 | 6.9043 | 2
B94 | Storage | 420 | 28 |  |  | 768 | 17 | 17 |  | 8 | 6144 | 4.1016 | 1 | 4.1016 | 2 | 4.1016 | 2
B95 | Storage | 190 | 12 |  |  | 690 | 15 | 12 |  | 8 | 5520 | 2.0652 | 1 | 2.0652 | 1 | 2.0652 | 1
B96 | Storage | 2026 | 135 |  |  | 968 | 22 | 22 |  | 8 | 7744 | 15.6973 | 1 | 15.6973 | 3 | 15.6973 | 3
B97 | Storage | 16042 | 1069 |  |  | 12420 | 282 | 282 |  | 8 | 99360 | 9.6872 | 1.4912 | 14.4451 | 3 | 14.4451 | 3
B98 | Storage | 7343 | 489 |  |  | 21078 | 479 | 479 |  | 8 | 168624 | 2.6128 | 2.3523 | 6.1462 | 2 | 6.1462 | 2
B99 | Storage | 1095 | 73 |  |  | 4608 | 104 | 73 |  | 8 | 36864 | 1.7822 | 1.062 | 1.8928 | 1 | 1.8928 | 1
B100 | Storage | 43 | 2 |  |  | 280 | 6 | 2 |  | 8 | 2240 | 1.1518 | 1 | 1.1518 | 1 | 1.1518 | 1
B101 | Storage | 123 | 8 |  |  | 280 | 6 | 6 |  | 8 | 2240 | 3.2946 | 1 | 3.2946 | 1 | 3.2946 | 1
B102 | Storage | 50 | 3 |  |  | 252 | 5 | 3 |  | 8 | 2016 | 1.4881 | 1 | 1.4881 | 1 | 1.4881 | 1
B103 | Storage | 46 | 3 |  |  | 252 | 5 | 3 |  | 8 | 2016 | 1.369 | 1 | 1.369 | 1 | 1.369 | 1
Sheet Last Modified: | 2021-03-18
School: | Parkway Northwest High School former Hill, JE (Hill-Freedman)
Vendor: | Goldner | Goldner Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
108 | Room | 676 | 45 |  |  | 676 | 15 | 15 | Univent | 8 | 5408 | 7.5 | 1 | 7.5 | 2 | 7.5 | 2
109 | Room | 333 | 22 |  |  | 714 | 16 | 16 | Fan Coil Unit | 8 | 5712 | 3.4979 | 1 | 3.4979 | 1 | 3.4979 | 1
110 | Room | 168 | 11 |  |  | 1015 | 23 | 11 | Univent | 8 | 8120 | 1.2414 | 1 | 1.2414 | 1 | 1.2414 | 1
130 | Room | 564 | 37 |  |  | 630 | 14 | 14 | Univent | 8 | 5040 | 6.7143 | 1 | 6.7143 | 2 | 6.7143 | 2
131 | Room | 476 | 31 |  |  | 580 | 13 | 13 | Univent | 8 | 4640 | 6.1552 | 1 | 6.1552 | 2 | 6.1552 | 2
132 | Room | 528 | 35 |  |  | 580 | 13 | 13 | Univent | 8 | 4640 | 6.8276 | 1 | 6.8276 | 2 | 6.8276 | 2
133 | Room | 452 | 30 |  |  | 469 | 10 | 10 | Univent | 8 | 3752 | 7.2281 | 1 | 7.2281 | 2 | 7.2281 | 2
134 | Room | 496 | 33 |  |  | 1015 | 23 | 23 | Univent | 8 | 8120 | 3.665 | 1 | 3.665 | 1 | 3.665 | 1
135 | Room | 304 | 20 |  |  | 812 | 18 | 18 | Univent | 8 | 6496 | 2.8079 | 1 | 2.8079 | 1 | 2.8079 | 1
136 | Room | 424 | 28 |  |  | 424 | 9 | 9 | Univent | 8 | 3392 | 7.5 | 1 | 7.5 | 2 | 7.5 | 2
203 | Room | 409 | 27 |  |  | 600 | 13 | 13 | Univent | 8 | 4800 | 5.1125 | 1 | 5.1125 | 2 | 5.1125 | 2
204 | Room | 363 | 24 |  |  | 667 | 15 | 15 | Univent | 8 | 5336 | 4.0817 | 1 | 4.0817 | 2 | 4.0817 | 2
205 | Room | 376 | 25 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 3.9167 | 1 | 3.9167 | 1 | 3.9167 | 1
206 | Room | 350 | 23 |  |  | 810 | 18 | 18 | Univent | 8 | 6480 | 3.2407 | 1 | 3.2407 | 1 | 3.2407 | 1
207 | Room | 371 | 24 |  |  | 783 | 17 | 17 | Univent | 8 | 6264 | 3.5536 | 1 | 3.5536 | 1 | 3.5536 | 1
210 | Room | 482 | 32 |  |  | 1116 | 25 | 25 | Fan Coil Unit | 8 | 8928 | 3.2392 | 1 | 3.2392 | 1 | 3.2392 | 1
211 | Room | 329 | 21 |  |  | 957 | 21 | 21 | Univent | 8 | 7656 | 2.5784 | 1 | 2.5784 | 1 | 2.5784 | 1
221 | Room | 300 | 20 |  |  | 580 | 13 | 13 | Univent | 8 | 4640 | 3.8793 | 1 | 3.8793 | 1 | 3.8793 | 1
222 | Room | 75 | 5 |  |  | 580 | 13 | 5 | Univent | 8 | 4640 | 0.96983 | 1 | 0.96983 | 0 | 0.96983 | 0
223 | Room | 523 | 34 |  |  | 580 | 13 | 13 | Univent | 8 | 4640 | 6.7629 | 1 | 6.7629 | 2 | 6.7629 | 2
224 | Room | 717 | 47 |  |  | 580 | 13 | 13 | Univent | 8 | 4640 | 9.2716 | 1 | 9.2716 | 2 | 9.2716 | 2
225 | Room | 250 | 16 |  |  | 580 | 13 | 13 | Univent | 8 | 4640 | 3.2328 | 1 | 3.2328 | 1 | 3.2328 | 1
226 | Room | 163 | 10 |  |  | 580 | 13 | 10 | Univent | 8 | 4640 | 2.1078 | 1 | 2.1078 | 1 | 2.1078 | 1
- | Auditurium | 912 | 60 |  |  | 1050 | 23 | 23 | Univent | 8 | 8400 | 6.5143 | 1 | 6.5143 | 2 | 6.5143 | 2
- | Gym | 969 | 64 |  |  | 2460 | 55 | 55 | Univent | 8 | 19680 | 2.9543 | 1 | 2.9543 | 1 | 2.9543 | 1
- | Main Office | 0 | 0 |  |  | 399 | 9 | 0 |  | 8 | 3192 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30
School: | John M. Patterson Elementary School | House fan Abated
Vendor: | Devine Brothers Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom |  | 0 | Yes | 20 | 648 | 14 | 14 | House Fan | 8 | 5184 | 0 | 1 | 0 | 0 | 20 | 3
2 | Classroom |  | 0 | Yes | 20 | 648 | 14 | 14 | House Fan | 8 | 5184 | 0 | 1 | 0 | 0 | 20 | 3
3 | Classroom |  | 0 | Yes | 20 | 648 | 14 | 14 | House Fan | 8 | 5184 | 0 | 1 | 0 | 0 | 20 | 3
100 | Office | 0 | 0 |  |  | 143 | 3 | 0 | House Fan | 8 | 1144 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom | 659 | 43 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.0206 | 1 | 7.0206 | 2 | 7.0206 | 2
102 | Classroom | 568 | 37 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 6.9156 | 1 | 6.9156 | 2 | 6.9156 | 2
103 | Classroom | 403 | 26 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 4.9067 | 1 | 4.9067 | 2 | 4.9067 | 2
104 | Classroom | 663 | 44 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 8.0722 | 1 | 8.0722 | 2 | 8.0722 | 2
105 | Classroom | 518 | 34 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 6.3068 | 1 | 6.3068 | 2 | 6.3068 | 2
106 | Classroom | 639 | 42 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 7.78 | 1 | 7.78 | 2 | 7.78 | 2
107 | Classroom | 698 | 46 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 8.4984 | 1 | 8.4984 | 2 | 8.4984 | 2
108 | Classroom | 656 | 43 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.9886 | 1 | 6.9886 | 2 | 6.9886 | 2
109 | Classroom | 658 | 43 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.0099 | 1 | 7.0099 | 2 | 7.0099 | 2
110 | Classroom | 722 | 48 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.6918 | 1 | 7.6918 | 2 | 7.6918 | 2
200 | Classroom | 0 | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
200A | Counselor | 0 | 0 |  |  | 240 | 5 | 0 | House Fan | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom | 373 | 24 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 3.9737 | 1 | 3.9737 | 1 | 3.9737 | 1
202 | Classroom | 578 | 38 |  |  | 703 | 15 | 15 | House Fan | 8 | 5624 | 6.1664 | 1 | 6.1664 | 2 | 6.1664 | 2
203 | Classroom | 504 | 33 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 6.1364 | 1 | 6.1364 | 2 | 6.1364 | 2
204 | Classroom | 474 | 31 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 5.7711 | 1 | 5.7711 | 2 | 5.7711 | 2
205 | Classroom | 421 | 28 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 5.1258 | 1 | 5.1258 | 2 | 5.1258 | 2
206 | Classroom | 541 | 36 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 6.5869 | 1 | 6.5869 | 2 | 6.5869 | 2
207 | Classroom | 637 | 42 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 7.7557 | 1 | 7.7557 | 2 | 7.7557 | 2
208 | Classroom | 209 | 13 |  |  | 704 | 16 | 13 | House Fan | 8 | 5632 | 2.2266 | 1 | 2.2266 | 1 | 2.2266 | 1
209 | Classroom | 585 | 39 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.2322 | 1 | 6.2322 | 2 | 6.2322 | 2
210 | Classroom | 583 | 38 |  |  | 410 | 9 | 9 | House Fan | 8 | 3280 | 10.6646 | 1 | 10.6646 | 3 | 10.6646 | 3
300 | Classroom | 394 | 26 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 4.1974 | 1 | 4.1974 | 2 | 4.1974 | 2
301 | Classroom | 530 | 35 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 5.6463 | 1 | 5.6463 | 2 | 5.6463 | 2
302 | Classroom | 511 | 34 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 5.4439 | 1 | 5.4439 | 2 | 5.4439 | 2
303 | Classroom | 576 | 38 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.1364 | 1 | 6.1364 | 2 | 6.1364 | 2
304 | Classroom | 359 | 23 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 4.3709 | 1 | 4.3709 | 2 | 4.3709 | 2
305 | Classroom | 561 | 37 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 6.8304 | 1 | 6.8304 | 2 | 6.8304 | 2
306 | Classroom | 604 | 40 |  |  | 616 | 14 | 14 | House Fan | 8 | 4928 | 7.3539 | 1 | 7.3539 | 2 | 7.3539 | 2
307 | Classroom | 103 | 6 |  |  | 616 | 14 | 6 | House Fan | 8 | 4928 | 1.2541 | 1 | 1.2541 | 1 | 1.2541 | 1
308 | Classroom | 418 | 27 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 4.4531 | 1 | 4.4531 | 2 | 4.4531 | 2
309 | Classroom | 101 | 6 |  |  | 704 | 16 | 6 | House Fan | 8 | 5632 | 1.076 | 1 | 1.076 | 1 | 1.076 | 1
310 | Classroom | 429 | 28 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 4.5703 | 1 | 4.5703 | 2 | 4.5703 | 2
- | Auditorium | 5125 | 341 |  |  | 2880 | 65 | 65 | House Fan | 8 | 23040 | 13.3464 | 1.062 | 14.1743 | 3 | 14.1743 | 3
- | Admin Office | 0 | 0 | Yes | 20 | 88 | 2 | 2 | House Fan | 8 | 704 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 120 | 2 | 2 | House Fan | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
- | Book Room Storage | 0 | 0 |  |  | 230 | 5 | 0 | House Fan | 8 | 1840 | 0 | 1 | 0 | 0 | 0 | 0
- | Boiler Rm. | 22650 | 1510 |  |  | 1440 | 32 | 32 | House Fan | 8 | 11520 | 117.9688 | 1 | 117.9688 | 5 | 117.9688 | 5
- | Small Cafeteria | 689 | 45 |  |  | 1232 | 28 | 28 | House Fan | 8 | 9856 | 4.1944 | 1 | 4.1944 | 2 | 4.1944 | 2
- | Kitchen | 212 | 14 |  |  | 200 | 4 | 4 | House Fan | 8 | 1600 | 7.95 | 1 | 7.95 | 2 | 7.95 | 2
- | Gym/Cafeteria | 0 | 0 | Yes | 20 | 3762 | 85 | 85 | House Fan | 8 | 30096 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Storage | 574 | 38 |  |  |  | 0 | 0 | House Fan
- | Music | 375 | 25 |  |  | 560 | 12 | 12 | House Fan | 8 | 4480 | 5.0223 | 1 | 5.0223 | 2 | 5.0223 | 2
- | Nurse's Room | 0 | 0 | Yes | 20 | 336 | 7 | 7 | House Fan | 8 | 2688 | 0 | 1 | 0 | 0 | 20 | 3
- | Teacher's Lounge | 0 | 0 | Yes | 20 | 410 | 9 | 9 | House Fan | 8 | 3280 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-20
School: | Penn Alexander Elementary-Middle School
Vendor: | Devine Brothers | Part 2
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B24 | Classroom | 37 | 2 |  |  | 130 | 2 | 2 | Air Handling Unit | 8 | 1040 | 2.1346 | 1 | 2.1346 | 1 | 2.1346 | 1
B26 | Classroom | 120 | 8 |  |  | 216 | 4 | 4 | Air Handling Unit | 8 | 1728 | 4.1667 | 1 | 4.1667 | 2 | 4.1667 | 2
B28 | Classroom | 483 | 32 |  |  | 722 | 16 | 16 | Air Handling Unit | 8 | 5776 | 5.0173 | 1 | 5.0173 | 2 | 5.0173 | 2
106 | Classroom | 1065 | 71 |  |  | 806 | 18 | 18 | Air Handling Unit | 8 | 6448 | 9.91 | 1 | 9.91 | 2 | 9.91 | 2
108 | Classroom | 310 | 20 |  |  | 842 | 19 | 19 | Univent | 8 | 6736 | 2.7613 | 1 | 2.7613 | 1 | 2.7613 | 1
109 | Classroom | 311 | 20 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.0731 | 1 | 3.0731 | 1 | 3.0731 | 1
110 | Classroom | 305 | 20 |  |  | 693 | 15 | 15 | Univent | 8 | 5544 | 3.3009 | 1 | 3.3009 | 1 | 3.3009 | 1
113 | Classroom | 220 | 14 |  |  | 222 | 5 | 5 | Air Handling Unit | 8 | 1776 | 7.4324 | 1 | 7.4324 | 2 | 7.4324 | 2
117 | Classroom | 285 | 19 |  |  | 741 | 16 | 16 | Univent | 8 | 5928 | 2.8846 | 1 | 2.8846 | 1 | 2.8846 | 1
118 | Classroom | 329 | 21 |  |  | 759 | 17 | 17 | Univent | 8 | 6072 | 3.251 | 1 | 3.251 | 1 | 3.251 | 1
119 | Classroom | 315 | 21 |  |  | 683 | 15 | 15 | Univent | 8 | 5464 | 3.459 | 1 | 3.459 | 1 | 3.459 | 1
123 | Classroom | 0 | 0 |  |  | 150 | 3 | 0 | Air Handling Unit | 8 | 1200 | 0 | 1 | 0 | 0 | 0 | 0
125 | Classroom | 73 | 4 |  |  | 209 | 4 | 4 | Air Handling Unit | 8 | 1672 | 2.6196 | 1 | 2.6196 | 1 | 2.6196 | 1
126 | Classroom | 13 | 0 |  |  | 99 | 2 | 0 | Air Handling Unit | 8 | 792 | 0.98485 | 1 | 0.98485 | 0 | 0.98485 | 0
127 | Classroom | 14 | 0 |  |  | 99 | 2 | 0 | Air Handling Unit | 8 | 792 | 1.0606 | 1 | 1.0606 | 1 | 1.0606 | 1
128 | Classroom | 10 | 0 | Yes | 20 | 99 | 2 | 2 | Air Handling Unit | 8 | 792 | 0.75758 | 1 | 0.75758 | 0 | 20.7576 | 3
129 | Classroom | 84 | 5 | Yes | 20 | 291 | 6 | 6 | Air Handling Unit | 8 | 2328 | 2.1649 | 1 | 2.1649 | 1 | 22.1649 | 3
131 | Classroom | 302 | 20 |  |  | 694 | 15 | 15 | Univent | 8 | 5552 | 3.2637 | 1 | 3.2637 | 1 | 3.2637 | 1
133 | Classroom | 0 | 0 | Yes | 20 | 644 | 14 | 14 | Univent | 8 | 5152 | 0 | 1 | 0 | 0 | 20 | 3
134 | Classroom | 330 | 22 |  |  | 683 | 15 | 15 | Univent | 8 | 5464 | 3.6237 | 1 | 3.6237 | 1 | 3.6237 | 1
201 | Classroom | 491 | 32 |  |  | 875 | 19 | 19 | Air Handling Unit | 8 | 7000 | 4.2086 | 1 | 4.2086 | 2 | 4.2086 | 2
202 | Classroom | 74 | 4 |  |  | 324 | 7 | 4 | Air Handling Unit | 8 | 2592 | 1.713 | 1 | 1.713 | 1 | 1.713 | 1
208 | Classroom | 0 | 0 | Yes | 20 | 842 | 19 | 19 | Univent | 8 | 6736 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 | Yes | 20 | 759 | 17 | 17 | Univent | 8 | 6072 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom | 0 | 0 | Yes | 20 | 693 | 15 | 15 | Univent | 8 | 5544 | 0 | 1 | 0 | 0 | 20 | 3
213 | Classroom | 75 | 5 |  |  | 222 | 5 | 5 | Air Handling Unit | 8 | 1776 | 2.5338 | 1 | 2.5338 | 1 | 2.5338 | 1
217 | Classroom | 0 | 0 | Yes | 20 | 741 | 16 | 16 | Univent | 8 | 5928 | 0 | 1 | 0 | 0 | 20 | 3
218 | Classroom | 0 | 0 | Yes | 20 | 728 | 16 | 16 | Univent | 8 | 5824 | 0 | 1 | 0 | 0 | 20 | 3
219 | Classroom | 0 | 0 | Yes | 20 | 683 | 15 | 15 | Univent | 8 | 5464 | 0 | 1 | 0 | 0 | 20 | 3
220 | Classroom | 241 | 16 |  |  | 224 | 5 | 5 | Air Handling Unit | 8 | 1792 | 8.0692 | 1 | 8.0692 | 2 | 8.0692 | 2
221 | Classroom | 0 | 0 | Yes | 20 | 96 | 2 | 2 | Air Handling Unit | 8 | 768 | 0 | 1 | 0 | 0 | 20 | 3
222 | Classroom | 0 | 0 |  |  | 169 | 3 | 0 | Air Handling Unit | 8 | 1352 | 0 | 1 | 0 | 0 | 0 | 0
225 | Classroom | 0 | 0 | Yes | 20 | 209 | 4 | 4 | Air Handling Unit | 8 | 1672 | 0 | 1 | 0 | 0 | 20 | 3
227 | Classroom | 0 | 0 |  |  | 99 | 2 | 0 | Air Handling Unit | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
228 | Classroom | 0 | 0 |  |  | 154 | 3 | 0 | Air Handling Unit | 8 | 1232 | 0 | 1 | 0 | 0 | 0 | 0
229 | Classroom | 0 | 0 |  |  | 108 | 2 | 0 | Air Handling Unit | 8 | 864 | 0 | 1 | 0 | 0 | 0 | 0
230 | Classroom | 318 | 21 |  |  | 736 | 16 | 16 | Univent | 8 | 5888 | 3.2405 | 1 | 3.2405 | 1 | 3.2405 | 1
231 | Classroom | 301 | 20 |  |  | 840 | 19 | 19 | Univent | 8 | 6720 | 2.6875 | 1 | 2.6875 | 1 | 2.6875 | 1
233 | Classroom | 266 | 17 |  |  | 739 | 16 | 16 | Univent | 8 | 5912 | 2.6996 | 1 | 2.6996 | 1 | 2.6996 | 1
234 | Classroom | 328 | 21 |  |  | 671 | 15 | 15 | Univent | 8 | 5368 | 3.6662 | 1 | 3.6662 | 1 | 3.6662 | 1
301 | Classroom | 1176 | 78 |  |  | 1005 | 22 | 22 | Air Handling Unit | 8 | 8040 | 8.7761 | 1 | 8.7761 | 2 | 8.7761 | 2
302 | Classroom | 0 | 0 |  |  | 324 | 7 | 0 | Univent | 8 | 2592 | 0 | 1 | 0 | 0 | 0 | 0
308 | Classroom | 0 | 0 | Yes | 20 | 842 | 19 | 19 | Univent | 8 | 6736 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 | Yes | 20 | 713 | 16 | 16 | Univent | 8 | 5704 | 0 | 1 | 0 | 0 | 20 | 3
310 | Classroom | 0 | 0 | Yes | 20 | 693 | 15 | 15 | Univent | 8 | 5544 | 0 | 1 | 0 | 0 | 20 | 3
317 | Classroom | 0 | 0 | Yes | 20 | 741 | 16 | 16 | Univent | 8 | 5928 | 0 | 1 | 0 | 0 | 20 | 3
318 | Classroom | 0 | 0 | Yes | 20 | 759 | 17 | 17 | Univent | 8 | 6072 | 0 | 1 | 0 | 0 | 20 | 3
319 | Classroom | 0 | 0 | Yes | 20 | 683 | 15 | 15 | Univent | 8 | 5464 | 0 | 1 | 0 | 0 | 20 | 3
320 | Classroom | 0 | 0 |  |  | 320 | 7 | 0 | Air Handling Unit | 8 | 2560 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria | 7801 | 520 |  |  | 3766 | 85 | 85 | Air Handling Unit | 8 | 30128 | 15.5357 | 1.062 | 16.4995 | 3 | 16.4995 | 3
- | GYM | 1362 | 90 |  |  | 4271 | 97 | 90 | Air Handling Unit | 8 | 34168 | 2.3917 | 1.062 | 2.5401 | 1 | 2.5401 | 1
- | Library | 550 | 36 |  |  | 2658 | 60 | 36 | Air Handling Unit | 8 | 21264 | 1.5519 | 1.062 | 1.6482 | 1 | 1.6482 | 1
- | Main Office | 205 | 13 |  |  | 1063 | 24 | 13 | Air Handling Unit | 8 | 8504 | 1.4464 | 1 | 1.4464 | 1 | 1.4464 | 1
Sheet Last Modified: | 2021-04-28
School: | Penn Treaty High School
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | classroom |  | 0 | Yes | 20 | 624 | 14 | 14 | House Fan | 8 | 4992 | 0 | 1 | 0 | 0 | 20 | 3
102 | Administration |  | 0 | Yes | 20 | 336 | 7 | 7 | House Fan | 8 | 2688 | 0 | 1 | 0 | 0 | 20 | 3
102A | classroom |  | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
104 | classroom |  | 0 | Yes | 20 | 1539 | 34 | 34 | House Fan | 8 | 12312 | 0 | 1 | 0 | 0 | 20 | 3
105 | classroom |  | 0 | Yes | 20 | 594 | 13 | 13 | House Fan | 8 | 4752 | 0 | 1 | 0 | 0 | 20 | 3
106 | classroom |  | 0 | Yes | 20 | 864 | 19 | 19 | House Fan | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
107 | classroom |  | 0 | Yes | 20 | 920 | 20 | 20 | House Fan | 8 | 7360 | 0 | 1 | 0 | 0 | 20 | 3
108 | Administration |  | 0 | Yes | 20 | 780 | 17 | 17 | House Fan | 8 | 6240 | 0 | 1 | 0 | 0 | 20 | 3
109 | classroom |  | 0 | Yes | 20 | 864 | 19 | 19 | House Fan | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
110 | classroom |  | 0 | Yes | 20 | 672 | 15 | 15 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
110A | classroom |  | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
111 | classroom |  | 0 |  |  | 650 | 14 | 0 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 0 | 0
115 | Auditorium |  | 0 |  |  | 3594 | 81 | 0 | House Fan | 8 | 28752 | 0 | 1.062 | 0 | 0 | 0 | 0
H11A | Main office |  | 0 |  |  | 560 | 12 | 0 | House Fan | 8 | 4480 | 0 | 1 | 0 | 0 | 0 | 0
H11b | Main office |  | 0 |  |  | 576 | 13 | 0 | House Fan | 8 | 4608 | 0 | 1 | 0 | 0 | 0 | 0
H12 | Main office |  | 0 |  |  | 1150 | 26 | 0 | House Fan | 8 | 9200 | 0 | 1 | 0 | 0 | 0 | 0
H13 | Main office |  | 0 |  |  | 792 | 18 | 0 | House Fan | 8 | 6336 | 0 | 1 | 0 | 0 | 0 | 0
H13a | Main office |  | 0 |  |  | 312 | 7 | 0 | House Fan | 8 | 2496 | 0 | 1 | 0 | 0 | 0 | 0
H13b | Main office |  | 0 |  |  | 814 | 18 | 0 | House Fan | 8 | 6512 | 0 | 1 | 0 | 0 | 0 | 0
H13c | Main office |  | 0 |  |  | 275 | 6 | 0 | House Fan | 8 | 2200 | 0 | 1 | 0 | 0 | 0 | 0
H13d | Main office |  | 0 |  |  | 1150 | 26 | 0 | House Fan | 8 | 9200 | 0 | 1 | 0 | 0 | 0 | 0
201 | classroom |  | 0 |  |  | 650 | 14 | 0 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 0 | 0
202 | classroom |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
203 | classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
203A | classroom |  | 0 |  |  | 253 | 5 | 0 | House Fan | 8 | 2024 | 0 | 1 | 0 | 0 | 0 | 0
204 | classroom |  | 0 |  |  | 130 | 2 | 0 | House Fan | 8 | 1040 | 0 | 1 | 0 | 0 | 0 | 0
204A | classroom |  | 0 |  |  | 552 | 12 | 0 | House Fan | 8 | 4416 | 0 | 1 | 0 | 0 | 0 | 0
205 | Nurse |  | 0 | Yes | 20 | 325 | 7 | 7 | House Fan | 8 | 2600 | 0 | 1 | 0 | 0 | 20 | 3
207 | Main office |  | 0 | Yes | 20 | 667 | 15 | 15 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
207A | Speech |  | 0 | Yes | 20 | 70 | 1 | 1 | House Fan | 8 | 560 | 0 | 1 | 0 | 0 | 20 | 3
207B | Office |  | 0 |  |  | 120 | 2 | 0 | House Fan | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
207D | Principal Office |  | 0 | Yes | 20 | 300 | 6 | 6 | House Fan | 8 | 2400 | 0 | 1 | 0 | 0 | 20 | 3
207G | Conference Room |  | 0 | Yes | 20 | 144 | 3 | 3 | House Fan | 8 | 1152 | 0 | 1 | 0 | 0 | 20 | 3
208 | classroom |  | 0 |  |  | 1056 | 24 | 0 | House Fan | 8 | 8448 | 0 | 1 | 0 | 0 | 0 | 0
209 | classroom |  | 0 |  |  | 1032 | 23 | 0 | House Fan | 8 | 8256 | 0 | 1 | 0 | 0 | 0 | 0
210 | IMC |  | 0 | Yes | 20 | 2352 | 53 | 53 | House Fan | 8 | 18816 | 0 | 1 | 0 | 0 | 20 | 3
213 | classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
214 | classroom |  | 0 |  |  | 624 | 14 | 0 | House Fan | 8 | 4992 | 0 | 1 | 0 | 0 | 0 | 0
217 | Auditorium |  | 0 |  |  | 2304 | 52 | 0 | House Fan | 8 | 18432 | 0 | 1 | 0 | 0 | 0 | 0
301 | classroom |  | 0 |  |  | 650 | 14 | 0 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 0 | 0
301A | Administration |  | 0 |  |  | 375 | 8 | 0 | House Fan | 8 | 3000 | 0 | 1 | 0 | 0 | 0 | 0
303 | classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
303A | Admin |  | 0 |  |  | 275 | 6 | 0 | House Fan | 8 | 2200 | 0 | 1 | 0 | 0 | 0 | 0
304 | classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
305 | classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
305A | classroom |  | 0 |  |  | 912 | 20 | 0 | House Fan | 8 | 7296 | 0 | 1 | 0 | 0 | 0 | 0
307 | classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
308 | classroom |  | 0 |  |  | 672 | 15 | 0 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
309 | classroom |  | 0 |  |  | 744 | 16 | 0 | House Fan | 8 | 5952 | 0 | 1 | 0 | 0 | 0 | 0
310 | classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
311 | classroom |  | 0 |  |  | 720 | 16 | 0 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
312 | classroom |  | 0 |  |  | 720 | 16 | 0 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
313 | classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
314 | classroom |  | 0 |  |  | 624 | 14 | 0 | House Fan | 8 | 4992 | 0 | 1 | 0 | 0 | 0 | 0
315 | Admin |  | 0 |  |  | 238 | 5 | 0 | House Fan | 8 | 1904 | 0 | 1 | 0 | 0 | 0 | 0
316 | classroom |  | 0 |  |  | 696 | 15 | 0 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 0 | 0
317 | classroom |  | 0 |  |  | 672 | 15 | 0 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
401 | classroom |  | 0 |  |  | 624 | 14 | 0 | House Fan | 8 | 4992 | 0 | 1 | 0 | 0 | 0 | 0
402A | Admin |  | 0 |  |  | 828 | 18 | 0 | House Fan | 8 | 6624 | 0 | 1 | 0 | 0 | 0 | 0
402 | classroom |  | 0 |  |  | 322 | 7 | 0 | House Fan | 8 | 2576 | 0 | 1 | 0 | 0 | 0 | 0
403 | classroom |  | 0 |  |  | 1032 | 23 | 0 | House Fan | 8 | 8256 | 0 | 1 | 0 | 0 | 0 | 0
404 | classroom |  | 0 |  |  | 984 | 22 | 0 | House Fan | 8 | 7872 | 0 | 1 | 0 | 0 | 0 | 0
405 | classroom |  | 0 |  |  | 984 | 22 | 0 | House Fan | 8 | 7872 | 0 | 1 | 0 | 0 | 0 | 0
406 | classroom |  | 0 |  |  | 984 | 22 | 0 | House Fan | 8 | 7872 | 0 | 1 | 0 | 0 | 0 | 0
407 | classroom |  | 0 |  |  | 720 | 16 | 0 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
408 | classroom |  | 0 |  |  | 1008 | 22 | 0 | House Fan | 8 | 8064 | 0 | 1 | 0 | 0 | 0 | 0
409 | classroom |  | 0 |  |  | 1008 | 22 | 0 | House Fan | 8 | 8064 | 0 | 1 | 0 | 0 | 0 | 0
410 | classroom |  | 0 |  |  | 1008 | 22 | 0 | House Fan | 8 | 8064 | 0 | 1 | 0 | 0 | 0 | 0
412 | Admin |  | 0 |  |  | 506 | 11 | 0 | House Fan | 8 | 4048 | 0 | 1 | 0 | 0 | 0 | 0
412A | classroom |  | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
412b | classroom |  | 0 |  |  | 84 | 1 | 0 | House Fan | 8 | 672 | 0 | 1 | 0 | 0 | 0 | 0
412c | Admin |  | 0 |  |  | 484 | 11 | 0 | House Fan | 8 | 3872 | 0 | 1 | 0 | 0 | 0 | 0
413 | classroom |  | 0 |  |  | 720 | 16 | 0 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
414 | classroom |  | 0 |  |  | 650 | 14 | 0 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 0 | 0
415 | Cafe |  | 0 |  |  | 2200 | 50 | 0 | House Fan | 8 | 17600 | 0 | 1 | 0 | 0 | 0 | 0
417 | Kitchen |  | 0 | Yes | 20 | 455 | 10 | 10 | House Fan | 8 | 3640 | 0 | 1 | 0 | 0 | 20 | 3
417A | kitchen |  | 0 |  |  | 700 | 15 | 0 | House Fan | 8 | 5600 | 0 | 1 | 0 | 0 | 0 | 0
419 | Cafe |  | 0 |  |  | 2150 | 48 | 0 | House Fan | 8 | 17200 | 0 | 1 | 0 | 0 | 0 | 0
- | boys gym |  | 0 |  |  | 4725 | 107 | 0 | House Fan | 8 | 37800 | 0 | 1.062 | 0 | 0 | 0 | 0
- | girls gym |  | 0 |  |  | 4725 | 107 | 0 | House Fan | 8 | 37800 | 0 | 1.062 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-24
School: | Joseph Pennell Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | - | 0 | 0 | Yes | 20 | 1152 | 26 | 26 | Univent | 8 | 9216 | 0 | 1 | 0 | 0 | 20 | 3
2 | - | 0 | 0 | Yes | 20 | 1152 | 26 | 26 | Univent | 8 | 9216 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom | 0 | 0 |  |  | 288 | 6 | 0 | Air Handling Unit | 8 | 2304 | 0 | 1 | 0 | 0 | 0 | 0
102 | Classroom | 0 | 0 | Yes | 20 | 720 | 16 | 16 | Air Handling Unit | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom | 0 | 0 | Yes | 20 | 875 | 19 | 19 | Air Handling Unit | 8 | 7000 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom | 0 | 0 | Yes | 20 | 175 | 3 | 3 | Air Handling Unit | 8 | 1400 | 0 | 1 | 0 | 0 | 20 | 3
104A | Classroom | 0 | 0 |  |  | 375 | 8 | 0 | Air Handling Unit | 8 | 3000 | 0 | 1 | 0 | 0 | 0 | 0
104B | Classroom | 0 | 0 |  |  | 175 | 3 | 0 | Air Handling Unit | 8 | 1400 | 0 | 1 | 0 | 0 | 0 | 0
104C | Classroom | 0 | 0 |  |  | 125 | 2 | 0 | Air Handling Unit | 8 | 1000 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom | 0 | 0 |  |  | 900 | 20 | 0 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
106 | Classroom | 0 | 0 | Yes | 20 | 816 | 18 | 18 | Air Handling Unit | 8 | 6528 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom | 0 | 0 | Yes | 20 | 1025 | 23 | 23 | Air Handling Unit | 8 | 8200 | 0 | 1 | 0 | 0 | 20 | 3
110 | Classroom | 0 | 0 | Yes | 20 | 870 | 19 | 19 | Air Handling Unit | 8 | 6960 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 20 | 816 | 18 | 18 | Air Handling Unit | 8 | 6528 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 0 | 0 | Yes | 20 | 816 | 18 | 18 | Air Handling Unit | 8 | 6528 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom | 0 | 0 |  |  | 875 | 19 | 0 | Air Handling Unit | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
204 | Classroom | 0 | 0 |  |  | 875 | 19 | 0 | Air Handling Unit | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
205 | Classroom | 0 | 0 |  |  | 875 | 19 | 0 | Air Handling Unit | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
206 | Classroom | 0 | 0 |  |  | 875 | 19 | 0 | Air Handling Unit | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom | 0 | 0 | Yes | 20 | 816 | 18 | 18 | Air Handling Unit | 8 | 6528 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 20 | 984 | 22 | 22 | Air Handling Unit | 8 | 7872 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom | 0 | 0 |  |  | 870 | 19 | 0 | Air Handling Unit | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
210 | Classroom | 0 | 0 |  |  | 870 | 19 | 0 | Air Handling Unit | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
211 | Classroom | 0 | 0 |  |  | 870 | 19 | 0 | Air Handling Unit | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom | 0 | 0 |  |  | 816 | 18 | 0 | Air Handling Unit | 8 | 6528 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom | 0 | 0 |  |  | 816 | 18 | 0 | Air Handling Unit | 8 | 6528 | 0 | 1 | 0 | 0 | 0 | 0
303 | Classroom | 0 | 0 |  |  | 875 | 19 | 0 | Air Handling Unit | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
304 | Classroom | 0 | 0 |  |  | 875 | 19 | 0 | Air Handling Unit | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
305 | Classroom | 0 | 0 |  |  | 875 | 19 | 0 | Air Handling Unit | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom | 0 | 0 | Yes | 20 | 875 | 19 | 19 | Air Handling Unit | 8 | 7000 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 |  |  | 816 | 18 | 0 | Air Handling Unit | 8 | 6528 | 0 | 1 | 0 | 0 | 0 | 0
308 | Classroom | 0 | 0 | Yes | 20 | 910 | 20 | 20 | Air Handling Unit | 8 | 7280 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 |  |  | 870 | 19 | 0 | Air Handling Unit | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom | 0 | 0 |  |  | 870 | 19 | 0 | Air Handling Unit | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
311 | Classroom | 0 | 0 |  |  | 870 | 19 | 0 | Air Handling Unit | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
- | Basement Boys Room | 0 | 0 |  |  | 650 | 14 | 0 | Air Handling Unit | 8 | 5200 | 0 | 1 | 0 | 0 | 0 | 0
- | Basement Corridor | 0 | 0 |  |  | 352 | 8 | 0 | Air Handling Unit | 8 | 2816 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym | 0 | 0 | Yes | 20 | 5096 | 115 | 115 | Air Handling Unit | 8 | 40768 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Library | 0 | 0 |  |  | 1593 | 36 | 0 | Air Handling Unit | 8 | 12744 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurse | 0 | 0 | Yes | 20 | 384 | 8 | 8 | Air Handling Unit | 8 | 3072 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office |  | 0 |  |  | 384 | 8 | 0 |  | 8 | 3072 | 0 | 1 | 0 | 0 | 0 | 0
- | Office |  | 0 | Yes | 20 | 456 | 10 | 10 |  | 8 | 3648 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 20 | 234 | 5 | 5 |  | 8 | 1872 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-27
School: | Samuel Pennypacker Elementary-Middle School
Vendor: | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B2 | Classroom | 0 | 0 | Yes | 20 | 928 | 21 | 21 | House Fan | 8 | 7424 | 0 | 1 | 0 | 0 | 20 | 3
B3 | Classroom | 923 | 61 |  |  | 1160 | 26 | 26 | House Fan | 8 | 9280 | 5.9677 | 1 | 5.9677 | 2 | 5.9677 | 2
B4 | Classroom | 0 | 0 | Yes | 20 | 1260 | 28 | 28 | House Fan | 8 | 10080 | 0 | 1 | 0 | 0 | 20 | 3
B8 | Classroom | 488 | 32 |  |  | 576 | 13 | 13 | House Fan | 8 | 4608 | 6.3542 | 1 | 6.3542 | 2 | 6.3542 | 2
B9 | Classroom | 439 | 29 |  |  | 460 | 10 | 10 | House Fan | 8 | 3680 | 7.1576 | 1 | 7.1576 | 2 | 7.1576 | 2
B10 | Classroom | 425 | 28 |  |  | 576 | 13 | 13 | House Fan | 8 | 4608 | 5.5339 | 1 | 5.5339 | 2 | 5.5339 | 2
101 | Classroom | 545 | 36 |  |  | 1131 | 25 | 25 | House Fan | 8 | 9048 | 3.6141 | 1 | 3.6141 | 1 | 3.6141 | 1
102 | Classroom | 440 | 29 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 3.9239 | 1 | 3.9239 | 1 | 3.9239 | 1
103 | Classroom | 545 | 36 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 4.6983 | 1 | 4.6983 | 2 | 4.6983 | 2
104 | Classroom | 611 | 40 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 5.2672 | 1 | 5.2672 | 2 | 5.2672 | 2
105 | Classroom | 340 | 22 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 3.0321 | 1 | 3.0321 | 1 | 3.0321 | 1
106 | Classroom | 395 | 26 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 3.5226 | 1 | 3.5226 | 1 | 3.5226 | 1
107 | Classroom | 503 | 33 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 4.4857 | 1 | 4.4857 | 2 | 4.4857 | 2
108 | Classroom | 650 | 43 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 5.4227 | 1 | 5.4227 | 2 | 5.4227 | 2
109 | Classroom | 437 | 29 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 3.8971 | 1 | 3.8971 | 1 | 3.8971 | 1
110 | Classroom | 459 | 30 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 3.8293 | 1 | 3.8293 | 1 | 3.8293 | 1
201 | Classroom | 351 | 23 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 2.9283 | 1 | 2.9283 | 1 | 2.9283 | 1
202 | Classroom | 424 | 28 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 3.7812 | 1 | 3.7812 | 1 | 3.7812 | 1
203 | Classroom | 390 | 26 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 3.3621 | 1 | 3.3621 | 1 | 3.3621 | 1
204 | Classroom | 338 | 22 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 3.0143 | 1 | 3.0143 | 1 | 3.0143 | 1
205 | Classroom | 649 | 43 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 5.7878 | 1 | 5.7878 | 2 | 5.7878 | 2
208 | Classroom | 586 | 39 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 4.8888 | 1 | 4.8888 | 2 | 4.8888 | 2
209 | Classroom | 508 | 33 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 4.5303 | 1 | 4.5303 | 2 | 4.5303 | 2
210 | Classroom | 356 | 23 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 2.97 | 1 | 2.97 | 1 | 2.97 | 1
212 | Storage | 0 | 0 |  |  | 360 | 8 | 0 | House Fan | 8 | 2880 | 0 | 1 | 0 | 0 | 0 | 0
301 | Classroom | 382 | 25 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 3.1869 | 1 | 3.1869 | 1 | 3.1869 | 1
302 | Classroom | 653 | 43 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 5.8234 | 1 | 5.8234 | 2 | 5.8234 | 2
303 | Classroom | 355 | 23 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 3.0603 | 1 | 3.0603 | 1 | 3.0603 | 1
304 | Classroom | 407 | 27 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 3.6296 | 1 | 3.6296 | 1 | 3.6296 | 1
305 | Classroom | 583 | 38 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 5.1992 | 1 | 5.1992 | 2 | 5.1992 | 2
306 | Classroom | 554 | 36 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 4.7759 | 1 | 4.7759 | 2 | 4.7759 | 2
307 | Classroom | 513 | 34 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 4.5749 | 1 | 4.5749 | 2 | 4.5749 | 2
308 | Classroom | 515 | 34 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 4.2964 | 1 | 4.2964 | 2 | 4.2964 | 2
309 | Classroom | 676 | 45 |  |  | 841 | 19 | 19 | House Fan | 8 | 6728 | 6.0285 | 1 | 6.0285 | 2 | 6.0285 | 2
310 | Classroom | 422 | 28 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 3.5206 | 1 | 3.5206 | 1 | 3.5206 | 1
311 | Classroom | 550 | 36 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 5.7292 | 1 | 5.7292 | 2 | 5.7292 | 2
312 | Classroom | 0 | 0 | Yes | 20 | 138 | 3 | 3 | House Fan | 8 | 1104 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 1967 | 131 |  |  | 4272 | 97 | 97 | House Fan | 8 | 34176 | 3.4533 | 1.062 | 3.6675 | 1 | 3.6675 | 1
- | Counselor's Office | 0 | 0 | Yes | 20 | 386 | 8 | 8 | House Fan | 8 | 3088 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym/Café | 0 | 0 | Yes | 20 | 3608 | 82 | 82 | House Fan | 8 | 28864 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Nurse | 0 | 0 | Yes | 20 | 361 | 8 | 8 | House Fan | 8 | 2888 | 0 | 1 | 0 | 0 | 20 | 3
- | Library | 928 | 61 |  |  | 1620 | 36 | 36 | House Fan | 8 | 12960 | 4.2963 | 1 | 4.2963 | 2 | 4.2963 | 2
- | Main Office | 0 | 0 | Yes | 20 | 342 | 7 | 7 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 20 | 3
- | Principals Office | 0 | 0 | Yes | 20 | 346 | 7 | 7 | House Fan | 8 | 2768 | 0 | 1 | 0 | 0 | 20 | 3
- | Teacher's Lounge | 0 | 0 |  |  | 105 | 2 | 0 | House Fan | 8 | 840 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23
School: | Penrose Elementary School- Main Building
Main Exhaust Report
School: | Penrose Little School House
| Penrose LSH Exhaust Report | LSH Part 2 and Exhaust | LSH Part 3 and Exhaust
School: | TB Read – former Motivation High School Building
| TB Read Exhaust Report | TB Read Exhaust Retest
Vendor: | Chadwick
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Penrose Main Building
101 | Classroom | 373 | 24 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 3.1646 | 1 | 3.1646 | 1 | 3.1646 | 1
102 | Classroom | 387 | 25 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 3.2834 | 1 | 3.2834 | 1 | 3.2834 | 1
103 | Classroom | 359 | 23 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 3.0458 | 1 | 3.0458 | 1 | 3.0458 | 1
104 | Classroom | 505 | 33 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 4.2845 | 1 | 4.2845 | 2 | 4.2845 | 2
105 | Classroom | 469 | 31 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 3.9791 | 1 | 3.9791 | 1 | 3.9791 | 1
106 | office | 119 | 7 |  |  | 315 | 7 | 7 | Rooftop Unit | 8 | 2520 | 2.8333 | 1 | 2.8333 | 1 | 2.8333 | 1
106a | principal | 26 | 1 |  |  | 72 | 1 | 1 | Rooftop Unit | 8 | 576 | 2.7083 | 1 | 2.7083 | 1 | 2.7083 | 1
106b | council | 36 | 2 |  |  | 176 | 4 | 2 | Rooftop Unit | 8 | 1408 | 1.5341 | 1 | 1.5341 | 1 | 1.5341 | 1
107 | Classroom | 99 | 6 |  |  | 884 | 20 | 6 | Rooftop Unit | 8 | 7072 | 0.83993 | 1 | 0.83993 | 0 | 0.83993 | 0
111 | Classroom | 233 | 15 |  |  | 884 | 20 | 15 | Rooftop Unit | 8 | 7072 | 1.9768 | 1 | 1.9768 | 1 | 1.9768 | 1
113 | Classroom | 256 | 17 |  |  | 884 | 20 | 17 | Rooftop Unit | 8 | 7072 | 2.1719 | 1 | 2.1719 | 1 | 2.1719 | 1
115 | Classroom | 287 | 19 |  |  | 884 | 20 | 19 | Rooftop Unit | 8 | 7072 | 2.435 | 1 | 2.435 | 1 | 2.435 | 1
116 | cafe | 330 | 22 |  |  | 1794 | 40 | 22 | Rooftop Unit | 8 | 14352 | 1.3796 | 1 | 1.3796 | 1 | 1.3796 | 1
116 | Classroom | 387 | 25 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 3.2834 | 1 | 3.2834 | 1 | 3.2834 | 1
117 | Classroom | 337 | 22 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 2.8592 | 1 | 2.8592 | 1 | 2.8592 | 1
118 | Classroom | 306 | 20 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 2.5962 | 1 | 2.5962 | 1 | 2.5962 | 1
119 | Classroom | 297 | 19 |  |  | 884 | 20 | 19 | Rooftop Unit | 8 | 7072 | 2.5198 | 1 | 2.5198 | 1 | 2.5198 | 1
121 | Classroom | 291 | 19 |  |  | 884 | 20 | 19 | Rooftop Unit | 8 | 7072 | 2.4689 | 1 | 2.4689 | 1 | 2.4689 | 1
201 | Classroom | 704 | 46 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 5.9729 | 1 | 5.9729 | 2 | 5.9729 | 2
202 | Classroom | 475 | 31 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 4.03 | 1 | 4.03 | 2 | 4.03 | 2
203 | Classroom | 697 | 46 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 5.9135 | 1 | 5.9135 | 2 | 5.9135 | 2
204 | Classroom | 457 | 30 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 3.8773 | 1 | 3.8773 | 1 | 3.8773 | 1
205 | Classroom | 292 | 19 |  |  | 884 | 20 | 19 | Rooftop Unit | 8 | 7072 | 2.4774 | 1 | 2.4774 | 1 | 2.4774 | 1
206 | Classroom | 399 | 26 |  |  | 496 | 11 | 11 | Rooftop Unit | 8 | 3968 | 6.0333 | 1 | 6.0333 | 2 | 6.0333 | 2
207 | Classroom | 574 | 38 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 4.8699 | 1 | 4.8699 | 2 | 4.8699 | 2
211 | Classroom | 423 | 28 |  |  | 884 | 20 | 20 | Rooftop Unit | 8 | 7072 | 3.5888 | 1 | 3.5888 | 1 | 3.5888 | 1
213 | Classroom | 159 | 10 |  |  | 884 | 20 | 10 | Rooftop Unit | 8 | 7072 | 1.349 | 1 | 1.349 | 1 | 1.349 | 1
214 | Classroom | 202 | 13 |  |  | 884 | 20 | 13 | Rooftop Unit | 8 | 7072 | 1.7138 | 1 | 1.7138 | 1 | 1.7138 | 1
215 | Classroom | 208 | 13 |  |  | 884 | 20 | 13 | Rooftop Unit | 8 | 7072 | 1.7647 | 1 | 1.7647 | 1 | 1.7647 | 1
216 | Classroom | 144 | 9 |  |  | 884 | 20 | 9 | Rooftop Unit | 8 | 7072 | 1.2217 | 1 | 1.2217 | 1 | 1.2217 | 1
217 | Classroom | 142 | 9 |  |  | 884 | 20 | 9 | Rooftop Unit | 8 | 7072 | 1.2048 | 1 | 1.2048 | 1 | 1.2048 | 1
218 | Classroom | 153 | 10 |  |  | 1768 | 40 | 10 | Rooftop Unit | 8 | 14144 | 0.64904 | 1 | 0.64904 | 0 | 0.64904 | 0
219 | Classroom | 131 | 8 |  |  | 884 | 20 | 8 | Rooftop Unit | 8 | 7072 | 1.1114 | 1 | 1.1114 | 1 | 1.1114 | 1
221 | Classroom | 151 | 10 |  |  | 884 | 20 | 10 | Rooftop Unit | 8 | 7072 | 1.2811 | 1 | 1.2811 | 1 | 1.2811 | 1
Penrose Little School House
1 | Classroom | 289 | 19 |  |  | 978 | 22 | 19 | Blower Coil Unit | 8 | 7824 | 2.2163 | 1 | 2.2163 | 1 | 2.2163 | 1
2 | Classroom | 340 | 22 |  |  | 978 | 22 | 22 | Blower Coil Unit | 8 | 7824 | 2.6074 | 1 | 2.6074 | 1 | 2.6074 | 1
3 | Classroom | 289 | 19 |  |  | 978 | 22 | 19 | Blower Coil Unit | 8 | 7824 | 2.2163 | 1 | 2.2163 | 1 | 2.2163 | 1
4 | Classroom | 340 | 22 |  |  | 978 | 22 | 22 | Blower Coil Unit | 8 | 7824 | 2.6074 | 1 | 2.6074 | 1 | 2.6074 | 1
5 | Classroom | 350 | 23 |  |  | 978 | 22 | 22 | Blower Coil Unit | 8 | 7824 | 2.684 | 1 | 2.684 | 1 | 2.684 | 1
6 | Classroom | 374 | 24 |  |  | 978 | 22 | 22 | Blower Coil Unit | 8 | 7824 | 2.8681 | 1 | 2.8681 | 1 | 2.8681 | 1
7 | Classroom | 374 | 24 |  |  | 978 | 22 | 22 | Blower Coil Unit | 8 | 7824 | 2.8681 | 1 | 2.8681 | 1 | 2.8681 | 1
8 | Classroom | 493 | 32 |  |  | 978 | 22 | 22 | Blower Coil Unit | 8 | 7824 | 3.7807 | 1 | 3.7807 | 1 | 3.7807 | 1
9 | Classroom | 311 | 20 |  |  | 978 | 22 | 20 | Blower Coil Unit | 8 | 7824 | 2.385 | 1 | 2.385 | 1 | 2.385 | 1
10 | Classroom | 493 | 32 |  |  | 978 | 22 | 22 | Blower Coil Unit | 8 | 7824 | 3.7807 | 1 | 3.7807 | 1 | 3.7807 | 1
11 | Classroom | 311 | 20 |  |  | 978 | 22 | 20 | Blower Coil Unit | 8 | 7824 | 2.385 | 1 | 2.385 | 1 | 2.385 | 1
- | multipurpose | 2960 | 197 |  |  | 2067 | 46 | 46 | Blower Coil Unit | 8 | 16536 | 10.7402 | 1 | 10.7402 | 3 | 10.7402 | 3
- | Corridor | 58 | 3 |  |  | 684 | 15 | 3 | Blower Coil Unit | 8 | 5472 | 0.63596 | 1 | 0.63596 | 0 | 0.63596 | 0
- | Boy's Restroom | 59 | 3 |  |  | 200 | 4 | 3 | Blower Coil Unit | 8 | 1600 | 2.2125 | 1 | 2.2125 | 1 | 2.2125 | 1
- | Girl's Rest Room | 64 | 4 |  |  | 200 | 4 | 4 | Blower Coil Unit | 8 | 1600 | 2.4 | 1 | 2.4 | 1 | 2.4 | 1
- | General Office |  | 0 |  |  | 146 | 3 | 0 | Blower Coil Unit | 8 | 1168 | 0 | 1 | 0 | 0 | 0 | 0
- | Principal's Office |  | 0 |  |  | 72 | 1 | 0 | Blower Coil Unit | 8 | 576 | 0 | 1 | 0 | 0 | 0 | 0
- | Psychiastrist's Office |  | 0 |  |  | 72 | 1 | 0 | Blower Coil Unit | 8 | 576 | 0 | 1 | 0 | 0 | 0 | 0
TB Read
101 | Classroom | 324 | 21 |  |  | 792 | 18 | 18 | Heating Ventilation Unit | 8 | 6336 | 3.0682 | 1 | 3.0682 | 1 | 3.0682 | 1
102 | Classroom | 101 | 6 | Yes | 20 | 792 | 18 | 18 | Heating Ventilation Unit | 8 | 6336 | 0.95644 | 1 | 0.95644 | 0 | 20.9564 | 3
103 | Classroom | 492 | 32 |  |  | 792 | 18 | 18 | Heating Ventilation Unit | 8 | 6336 | 4.6591 | 1 | 4.6591 | 2 | 4.6591 | 2
104 | Classroom | 584 | 38 |  |  | 792 | 18 | 18 | Heating Ventilation Unit | 8 | 6336 | 5.5303 | 1 | 5.5303 | 2 | 5.5303 | 2
105 | Classroom | 400 | 26 |  |  | 792 | 18 | 18 | Heating Ventilation Unit | 8 | 6336 | 3.7879 | 1 | 3.7879 | 1 | 3.7879 | 1
201 | Classroom | 443 | 29 |  |  | 792 | 18 | 18 | Heating Ventilation Unit | 8 | 6336 | 4.1951 | 1 | 4.1951 | 2 | 4.1951 | 2
202 | Classroom | 1636 | 109 |  |  | 792 | 18 | 18 | Heating Ventilation Unit | 8 | 6336 | 15.4924 | 1 | 15.4924 | 3 | 15.4924 | 3
203 | Classroom | 717 | 47 |  |  | 792 | 18 | 18 | Heating Ventilation Unit | 8 | 6336 | 6.7898 | 1 | 6.7898 | 2 | 6.7898 | 2
204 | Classroom | 948 | 63 |  |  | 792 | 18 | 18 | Heating Ventilation Unit | 8 | 6336 | 8.9773 | 1 | 8.9773 | 2 | 8.9773 | 2
205 | Classroom | 397 | 26 |  |  | 792 | 18 | 18 | Heating Ventilation Unit | 8 | 6336 | 3.7595 | 1 | 3.7595 | 1 | 3.7595 | 1
14 | Computer Lab | 473 | 31 |  |  | 792 | 18 | 18 | Heating Ventilation Unit | 8 | 6336 | 4.4792 | 1 | 4.4792 | 2 | 4.4792 | 2
- | Corridor #1 | 795 | 53 |  |  | 1298 | 29 | 29 | Heating Ventilation Unit | 8 | 10384 | 4.5936 | 1 | 4.5936 | 2 | 4.5936 | 2
- | Corridor #2 | 413 | 27 |  |  | 1600 | 36 | 27 | Heating Ventilation Unit | 8 | 12800 | 1.9359 | 1 | 1.9359 | 1 | 1.9359 | 1
- | GYM | 7270 | 484 |  |  | 8969 | 203 | 203 | Heating Ventilation Unit | 8 | 71752 | 6.0793 | 1.4912 | 9.0652 | 2 | 9.0652 | 2
- | Library | 442 | 29 |  |  | 874 | 19 | 19 | Heating Ventilation Unit | 8 | 6992 | 3.7929 | 1 | 3.7929 | 1 | 3.7929 | 1
Sheet Last Modified: | 2021-05-03
School: | Philadelphia Learning Academy North/ Camelot Academy East/ Crossroads Academy at Hunting Park (former CEP Hunting Park) Alternative School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
3 | Room (Split Level South) | 25 | 1 |  |  | 86 | 1 | 1 | Rooftop Unit | 8 | 688 | 2.1802 | 1 | 2.1802 | 1 | 2.1802 | 1
5 | Room (Split Level South) | 141 | 9 |  |  | 396 | 9 | 9 | Rooftop Unit | 8 | 3168 | 2.6705 | 1 | 2.6705 | 1 | 2.6705 | 1
005A | Room (Split Level South) | 20 | 1 |  |  | 87 | 1 | 1 | Rooftop Unit | 8 | 696 | 1.7241 | 1 | 1.7241 | 1 | 1.7241 | 1
6 | Room | 27 | 1 |  |  | 83 | 1 | 1 | Rooftop Unit | 8 | 664 | 2.4398 | 1 | 2.4398 | 1 | 2.4398 | 1
006A | Room | 14 | 0 |  |  | 80 | 1 | 0 | Rooftop Unit | 8 | 640 | 1.3125 | 1 | 1.3125 | 1 | 1.3125 | 1
006B | Room | 13 | 0 |  |  | 79 | 1 | 0 | Rooftop Unit | 8 | 632 | 1.2342 | 1 | 1.2342 | 1 | 1.2342 | 1
10 | Room | 7 | 0 |  |  | 84 | 1 | 0 | Rooftop Unit | 8 | 672 | 0.625 | 1 | 0.625 | 0 | 0.625 | 0
010A | Room | 53 | 3 |  |  | 80 | 1 | 1 | Rooftop Unit | 8 | 640 | 4.9688 | 1 | 4.9688 | 2 | 4.9688 | 2
103 | Room | 20 | 1 |  |  | 87 | 1 | 1 | Rooftop Unit | 8 | 696 | 1.7241 | 1 | 1.7241 | 1 | 1.7241 | 1
104 | Room | 19 | 1 |  |  | 85 | 1 | 1 | Rooftop Unit | 8 | 680 | 1.6765 | 1 | 1.6765 | 1 | 1.6765 | 1
105 | Room | 27 | 1 |  |  | 81 | 1 | 1 | Rooftop Unit | 8 | 648 | 2.5 | 1 | 2.5 | 1 | 2.5 | 1
106 | Room | 22 | 1 |  |  | 83 | 1 | 1 | Rooftop Unit | 8 | 664 | 1.988 | 1 | 1.988 | 1 | 1.988 | 1
108 | Room | 14 | 0 |  |  | 89 | 2 | 0 | Rooftop Unit | 8 | 712 | 1.1798 | 1 | 1.1798 | 1 | 1.1798 | 1
109 | Room | 13 | 0 |  |  | 92 | 2 | 0 | Rooftop Unit | 8 | 736 | 1.0598 | 1 | 1.0598 | 1 | 1.0598 | 1
110 | Room | 15 | 0 |  |  | 269 | 6 | 0 | Rooftop Unit | 8 | 2152 | 0.41822 | 1 | 0.41822 | 0 | 0.41822 | 0
113 | Room (Split Level South) | 56 | 3 |  |  | 134 | 3 | 3 | Rooftop Unit | 8 | 1072 | 3.1343 | 1 | 3.1343 | 1 | 3.1343 | 1
114 | Room (Split Level South) | 26 | 1 |  |  | 136 | 3 | 1 | Rooftop Unit | 8 | 1088 | 1.4338 | 1 | 1.4338 | 1 | 1.4338 | 1
115 | Room (Split Level South) | 41 | 2 |  |  | 139 | 3 | 2 | Rooftop Unit | 8 | 1112 | 2.2122 | 1 | 2.2122 | 1 | 2.2122 | 1
116 | Room (Split Level South) | 25 | 1 |  |  | 139 | 3 | 1 | Rooftop Unit | 8 | 1112 | 1.3489 | 1 | 1.3489 | 1 | 1.3489 | 1
117 | Room (Split Level South) | 80 | 5 |  |  | 355 | 8 | 5 | Rooftop Unit | 8 | 2840 | 1.6901 | 1 | 1.6901 | 1 | 1.6901 | 1
120 | Admin Office | -231 | -15 |  |  | 92 | 2 | -15 | Rooftop Unit | 8 | 736 | 18.8315 | 1 | 18.8315 | 3 | 18.8315 | 3
121 | Admin Office | 145 | 9 |  |  | 396 | 9 | 9 | Rooftop Unit | 8 | 3168 | 2.7462 | 1 | 2.7462 | 1 | 2.7462 | 1
122 | Admin Office | 208 | 13 |  |  | 94 | 2 | 2 | Rooftop Unit | 8 | 752 | 16.5957 | 1 | 16.5957 | 3 | 16.5957 | 3
123 | Admin Office | 97 | 6 |  |  | 92 | 2 | 2 | Rooftop Unit | 8 | 736 | 7.9076 | 1 | 7.9076 | 2 | 7.9076 | 2
124 | Admin Office | -65 | -4 |  |  | 92 | 2 | -4 | Rooftop Unit | 8 | 736 | 5.2989 | 1 | 5.2989 | 2 | 5.2989 | 2
126 | Admin Office | 57 | 3 |  |  | 139 | 3 | 3 | Rooftop Unit | 8 | 1112 | 3.0755 | 1 | 3.0755 | 1 | 3.0755 | 1
127 | Admin Office | -417 | -27 |  |  | 95 | 2 | -27 | Rooftop Unit | 8 | 760 | 32.9211 | 1 | 32.9211 | 4 | 32.9211 | 4
129 | Admin Office | -65 | -4 |  |  | 355 | 8 | -4 | Rooftop Unit | 8 | 2840 | 1.3732 | 1 | 1.3732 | 1 | 1.3732 | 1
130 | Admin Office | -52 | -3 | Yes | 20 | 140 | 3 | 3 | Rooftop Unit | 8 | 1120 | 2.7857 | 1 | 2.7857 | 1 | 17.2143 | 3
133 | Admin Office | 104 | 6 |  |  | 266 | 6 | 6 | Rooftop Unit | 8 | 2128 | 2.9323 | 1 | 2.9323 | 1 | 2.9323 | 1
133A | Admin Office | 322 | 21 |  |  | 927 | 21 | 21 | Rooftop Unit | 8 | 7416 | 2.6052 | 1 | 2.6052 | 1 | 2.6052 | 1
133B | Admin Office | 316 | 21 |  |  | 927 | 21 | 21 | Rooftop Unit | 8 | 7416 | 2.5566 | 1 | 2.5566 | 1 | 2.5566 | 1
134 | Media Room | 195 | 13 |  |  | 1769 | 40 | 13 | Rooftop Unit | 8 | 14152 | 0.82674 | 1 | 0.82674 | 0 | 0.82674 | 0
135 | Admin Office | 253 | 16 |  |  | 709 | 16 | 16 | Rooftop Unit | 8 | 5672 | 2.6763 | 1 | 2.6763 | 1 | 2.6763 | 1
136 | Media Room | 465 | 31 |  |  | 407 | 9 | 9 | Rooftop Unit | 8 | 3256 | 8.5688 | 1 | 8.5688 | 2 | 8.5688 | 2
142 | Admin Office | 339 | 22 |  |  | 225 | 5 | 5 | Rooftop Unit | 8 | 1800 | 11.3 | 1 | 11.3 | 3 | 11.3 | 3
147 | AEP Office | 146 | 9 |  |  | 413 | 9 | 9 | Rooftop Unit | 8 | 3304 | 2.6513 | 1 | 2.6513 | 1 | 2.6513 | 1
148 | AEP Office | -245 | -16 |  |  | 92 | 2 | -16 | Rooftop Unit | 8 | 736 | 19.9728 | 1 | 19.9728 | 3 | 19.9728 | 3
149 | AEP Office | -104 | -6 |  |  | 94 | 2 | -6 | Rooftop Unit | 8 | 752 | 8.2979 | 1 | 8.2979 | 2 | 8.2979 | 2
150 | AEP Office | -38 | -2 |  |  | 136 | 3 | -2 | Rooftop Unit | 8 | 1088 | 2.0956 | 1 | 2.0956 | 1 | 2.0956 | 1
151 | AEP Office | 178 | 11 |  |  | 179 | 4 | 4 | Rooftop Unit | 8 | 1432 | 7.4581 | 1 | 7.4581 | 2 | 7.4581 | 2
152 | AEP Office | 10 | 0 |  |  | 91 | 2 | 0 | Rooftop Unit | 8 | 728 | 0.82418 | 1 | 0.82418 | 0 | 0.82418 | 0
153 | AEP Office | 36 | 2 |  |  | 92 | 2 | 2 | Rooftop Unit | 8 | 736 | 2.9348 | 1 | 2.9348 | 1 | 2.9348 | 1
154 | AEP Office | 69 | 4 |  |  | 96 | 2 | 2 | Rooftop Unit | 8 | 768 | 5.3906 | 1 | 5.3906 | 2 | 5.3906 | 2
155 | AEP Office | 179 | 11 |  |  | 184 | 4 | 4 | Rooftop Unit | 8 | 1472 | 7.2962 | 1 | 7.2962 | 2 | 7.2962 | 2
156 | AEP Office | -34 | -2 |  |  | 80 | 1 | -2 | Rooftop Unit | 8 | 640 | 3.1875 | 1 | 3.1875 | 1 | 3.1875 | 1
157 | AEP Office | 70 | 4 |  |  | 79 | 1 | 1 | Rooftop Unit | 8 | 632 | 6.6456 | 1 | 6.6456 | 2 | 6.6456 | 2
158 | AEP Office | 119 | 7 |  |  | 85 | 1 | 1 | Rooftop Unit | 8 | 680 | 10.5 | 1 | 10.5 | 3 | 10.5 | 3
159 | AEP Office | 21 | 1 |  |  | 84 | 1 | 1 | Rooftop Unit | 8 | 672 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
160 | AEP Office | 184 | 12 |  |  | 142 | 3 | 3 | Rooftop Unit | 8 | 1136 | 9.7183 | 1 | 9.7183 | 2 | 9.7183 | 2
161 | Library Office | -59 | -3 |  |  | 91 | 2 | -3 | Rooftop Unit | 8 | 728 | 4.8626 | 1 | 4.8626 | 2 | 4.8626 | 2
162 | Library Office | -99 | -6 |  |  | 269 | 6 | -6 | Rooftop Unit | 8 | 2152 | 2.7602 | 1 | 2.7602 | 1 | 2.7602 | 1
164 | Main Library | 980 | 65 |  |  | 973 | 22 | 22 | Rooftop Unit | 8 | 7784 | 7.554 | 1 | 7.554 | 2 | 7.554 | 2
174 | Office | -270 | -18 |  |  | 83 | 1 | -18 | Rooftop Unit | 8 | 664 | 24.3976 | 1 | 24.3976 | 4 | 24.3976 | 4
175 | Office | 80 | 5 |  |  | 82 | 1 | 1 | Rooftop Unit | 8 | 656 | 7.3171 | 1 | 7.3171 | 2 | 7.3171 | 2
180 | Office | 87 | 5 |  |  | 93 | 2 | 2 | Rooftop Unit | 8 | 744 | 7.0161 | 1 | 7.0161 | 2 | 7.0161 | 2
181 | Office | -31 | -2 |  |  | 92 | 2 | -2 | Rooftop Unit | 8 | 736 | 2.5272 | 1 | 2.5272 | 1 | 2.5272 | 1
182 | Office | 166 | 11 |  |  | 92 | 2 | 2 | Rooftop Unit | 8 | 736 | 13.5326 | 1 | 13.5326 | 3 | 13.5326 | 3
184 | Office | 122 | 8 |  |  | 93 | 2 | 2 | Rooftop Unit | 8 | 744 | 9.8387 | 1 | 9.8387 | 2 | 9.8387 | 2
185 | Office | 27 | 1 |  |  | 92 | 2 | 1 | Rooftop Unit | 8 | 736 | 2.2011 | 1 | 2.2011 | 1 | 2.2011 | 1
186A | Office | -272 | -18 |  |  | 449 | 10 | -18 | Rooftop Unit | 8 | 3592 | 4.5434 | 1 | 4.5434 | 2 | 4.5434 | 2
186B | Office | -47 | -3 |  |  | 449 | 10 | -3 | Rooftop Unit | 8 | 3592 | 0.78508 | 1 | 0.78508 | 0 | 0.78508 | 0
187 | Office | -182 | -12 |  |  | 94 | 2 | -12 | Rooftop Unit | 8 | 752 | 14.5213 | 1 | 14.5213 | 3 | 14.5213 | 3
188 | Office | 100 | 6 |  |  | 92 | 2 | 2 | Rooftop Unit | 8 | 736 | 8.1522 | 1 | 8.1522 | 2 | 8.1522 | 2
189 | Office | 78 | 5 |  |  | 227 | 5 | 5 | Rooftop Unit | 8 | 1816 | 2.5771 | 1 | 2.5771 | 1 | 2.5771 | 1
192 | Office | -269 | -17 |  |  | 72 | 1 | -17 | Rooftop Unit | 8 | 576 | 28.0208 | 1 | 28.0208 | 4 | 28.0208 | 4
193 | Office | 283 | 18 |  |  | 82 | 1 | 1 | Rooftop Unit | 8 | 656 | 25.8841 | 1 | 25.8841 | 4 | 25.8841 | 4
194 | Office | 106 | 7 |  |  | 48 | 1 | 1 | Rooftop Unit | 8 | 384 | 16.5625 | 1 | 16.5625 | 3 | 16.5625 | 3
195 | Office | 78 | 5 |  |  | 232 | 5 | 5 | Rooftop Unit | 8 | 1856 | 2.5216 | 1 | 2.5216 | 1 | 2.5216 | 1
196 | Classroom | 190 | 12 |  |  | 528 | 12 | 12 | Rooftop Unit | 8 | 4224 | 2.6989 | 1 | 2.6989 | 1 | 2.6989 | 1
201 | Classroom | 248 | 16 |  |  | 712 | 16 | 16 | Rooftop Unit | 8 | 5696 | 2.6124 | 1 | 2.6124 | 1 | 2.6124 | 1
204 | Electrical Closet | 13 | 0 |  |  | 80 | 1 | 0 | Rooftop Unit | 8 | 640 | 1.2188 | 1 | 1.2188 | 1 | 1.2188 | 1
205 | IT Room | -3 | 0 |  |  | 84 | 1 | 0 | Rooftop Unit | 8 | 672 | 0.26786 | 1 | 0.26786 | 0 | 0.26786 | 0
207 | Closet | 0 | 0 |  |  | 136 | 3 | 0 | Rooftop Unit | 8 | 1088 | 0 | 1 | 0 | 0 | 0 | 0
210 | Office | -127 | -8 |  |  | 96 | 2 | -8 | Rooftop Unit | 8 | 768 | 9.9219 | 1 | 9.9219 | 2 | 9.9219 | 2
211 | Office | -20 | -1 |  |  | 94 | 2 | -1 | Rooftop Unit | 8 | 752 | 1.5957 | 1 | 1.5957 | 1 | 1.5957 | 1
212 | Office | 0 | 0 |  |  | 96 | 2 | 0 | Rooftop Unit | 8 | 768 | 0 | 1 | 0 | 0 | 0 | 0
213 | Room |  | 0 | Yes | 20 | 880 | 20 | 20 |  | 8 | 7040 | 0 | 1 | 0 | 0 | 20 | 3
213A | Office | 63 | 4 |  |  | 180 | 4 | 4 | Rooftop Unit | 8 | 1440 | 2.625 | 1 | 2.625 | 1 | 2.625 | 1
213B | Office | 284 | 18 |  |  | 792 | 18 | 18 | Rooftop Unit | 8 | 6336 | 2.6894 | 1 | 2.6894 | 1 | 2.6894 | 1
214 | Office | -12 | 0 |  |  | 89 | 2 | 0 | Rooftop Unit | 8 | 712 | 1.0112 | 1 | 1.0112 | 1 | 1.0112 | 1
215 | Office | 0 | 0 |  |  | 92 | 2 | 0 | Rooftop Unit | 8 | 736 | 0 | 1 | 0 | 0 | 0 | 0
217 | Office | -31 | -2 |  |  | 96 | 2 | -2 | Rooftop Unit | 8 | 768 | 2.4219 | 1 | 2.4219 | 1 | 2.4219 | 1
218 | Office | -23 | -1 |  |  | 86 | 1 | -1 | Rooftop Unit | 8 | 688 | 2.0058 | 1 | 2.0058 | 1 | 2.0058 | 1
219 | Office | 0 | 0 |  |  | 93 | 2 | 0 | Rooftop Unit | 8 | 744 | 0 | 1 | 0 | 0 | 0 | 0
221 | IT Room | 13 | 0 |  |  | 52 | 1 | 0 | Rooftop Unit | 8 | 416 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
222 | Electrical Closet | 195 | 13 |  |  | 94 | 2 | 2 | Rooftop Unit | 8 | 752 | 15.5585 | 1 | 15.5585 | 3 | 15.5585 | 3
223 | Closet | 0 | 0 |  |  | 55 | 1 | 0 | Rooftop Unit | 8 | 440 | 0 | 1 | 0 | 0 | 0 | 0
303 | Room (Split Level South) | 45 | 2 |  |  | 86 | 1 | 1 | Rooftop Unit | 8 | 688 | 3.9244 | 1 | 3.9244 | 1 | 3.9244 | 1
304 | Room (Split Level South) | 124 | 8 |  |  | 231 | 5 | 5 | Rooftop Unit | 8 | 1848 | 4.026 | 1 | 4.026 | 2 | 4.026 | 2
307 | Room (Split Level South) | 118 | 7 |  |  | 312 | 7 | 7 | Rooftop Unit | 8 | 2496 | 2.8365 | 1 | 2.8365 | 1 | 2.8365 | 1
311 | Room (Split Level South) | 13 | 0 |  |  | 136 | 3 | 0 | Rooftop Unit | 8 | 1088 | 0.71691 | 1 | 0.71691 | 0 | 0.71691 | 0
311A | Room (Split Level South) | 20 | 1 |  |  | 63 | 1 | 1 | Rooftop Unit | 8 | 504 | 2.381 | 1 | 2.381 | 1 | 2.381 | 1
311B | Room (Split Level South) | 12 | 0 |  |  | 86 | 1 | 0 | Rooftop Unit | 8 | 688 | 1.0465 | 1 | 1.0465 | 1 | 1.0465 | 1
313 | Room | 20 | 1 |  |  | 98 | 2 | 1 | Rooftop Unit | 8 | 784 | 1.5306 | 1 | 1.5306 | 1 | 1.5306 | 1
314 | Room | 21 | 1 |  |  | 85 | 1 | 1 | Rooftop Unit | 8 | 680 | 1.8529 | 1 | 1.8529 | 1 | 1.8529 | 1
316 | Room | 62 | 4 |  |  | 449 | 10 | 4 | Rooftop Unit | 8 | 3592 | 1.0356 | 1 | 1.0356 | 1 | 1.0356 | 1
320 | Room | 19 | 1 |  |  | 87 | 1 | 1 | Rooftop Unit | 8 | 696 | 1.6379 | 1 | 1.6379 | 1 | 1.6379 | 1
321 | Room | 16 | 1 |  |  | 89 | 2 | 1 | Rooftop Unit | 8 | 712 | 1.3483 | 1 | 1.3483 | 1 | 1.3483 | 1
322 | Room | 17 | 1 |  |  | 87 | 1 | 1 | Rooftop Unit | 8 | 696 | 1.4655 | 1 | 1.4655 | 1 | 1.4655 | 1
H01 | Room (Split Level South) | 34 | 2 |  |  | 89 | 2 | 2 | Rooftop Unit | 8 | 712 | 2.8652 | 1 | 2.8652 | 1 | 2.8652 | 1
H01 | Room | 15 | 0 |  |  | 72 | 1 | 0 | Rooftop Unit | 8 | 576 | 1.5625 | 1 | 1.5625 | 1 | 1.5625 | 1
H21 | Room (Split Level South) | 159 | 10 |  |  | 446 | 10 | 10 | Rooftop Unit | 8 | 3568 | 2.6738 | 1 | 2.6738 | 1 | 2.6738 | 1
H21 | Room | 7 | 0 |  |  | 52 | 1 | 0 | Rooftop Unit | 8 | 416 | 1.0096 | 1 | 1.0096 | 1 | 1.0096 | 1
L4/L5 | Room | 84 | 5 |  |  | 225 | 5 | 5 | Rooftop Unit | 8 | 1800 | 2.8 | 1 | 2.8 | 1 | 2.8 | 1
A1 | Classroom | 594 | 39 | Yes | 20 | 794 | 18 | 18 | Rooftop Unit | 8 | 6352 | 5.6108 | 1 | 5.6108 | 2 | 25.6108 | 4
A2 | Classroom | 876 | 58 |  |  | 793 | 18 | 18 | Rooftop Unit | 8 | 6344 | 8.285 | 1 | 8.285 | 2 | 8.285 | 2
A3 | Classroom | 219 | 14 |  |  | 795 | 18 | 14 | Rooftop Unit | 8 | 6360 | 2.066 | 1 | 2.066 | 1 | 2.066 | 1
A4 | Classroom | 905 | 60 |  |  | 796 | 18 | 18 | Rooftop Unit | 8 | 6368 | 8.527 | 1 | 8.527 | 2 | 8.527 | 2
B1 | Classroom | 430 | 28 |  |  | 793 | 18 | 18 | Rooftop Unit | 8 | 6344 | 4.0668 | 1 | 4.0668 | 2 | 4.0668 | 2
B2 | Classroom | 1048 | 69 |  |  | 792 | 18 | 18 | Rooftop Unit | 8 | 6336 | 9.9242 | 1 | 9.9242 | 2 | 9.9242 | 2
B3 | Classroom | 84 | 5 |  |  | 794 | 18 | 5 | Rooftop Unit | 8 | 6352 | 0.79345 | 1 | 0.79345 | 0 | 0.79345 | 0
B4 | Classroom | 769 | 51 |  |  | 794 | 18 | 18 | Rooftop Unit | 8 | 6352 | 7.2639 | 1 | 7.2639 | 2 | 7.2639 | 2
C1 | Classroom | 551 | 36 |  |  | 797 | 18 | 18 | Rooftop Unit | 8 | 6376 | 5.1851 | 1 | 5.1851 | 2 | 5.1851 | 2
C2 | Classroom | 927 | 61 |  |  | 795 | 18 | 18 | Rooftop Unit | 8 | 6360 | 8.7453 | 1 | 8.7453 | 2 | 8.7453 | 2
C3 | Classroom | 115 | 7 |  |  | 794 | 18 | 7 | Rooftop Unit | 8 | 6352 | 1.0863 | 1 | 1.0863 | 1 | 1.0863 | 1
C4 | Classroom | 70 | 4 |  |  | 795 | 18 | 4 | Rooftop Unit | 8 | 6360 | 0.66038 | 1 | 0.66038 | 0 | 0.66038 | 0
D1 | Classroom | 587 | 39 |  |  | 797 | 18 | 18 | Rooftop Unit | 8 | 6376 | 5.5238 | 1 | 5.5238 | 2 | 5.5238 | 2
D2 | Classroom | 935 | 62 |  |  | 795 | 18 | 18 | Rooftop Unit | 8 | 6360 | 8.8208 | 1 | 8.8208 | 2 | 8.8208 | 2
D3 | Classroom | 14 | 0 |  |  | 793 | 18 | 0 | Rooftop Unit | 8 | 6344 | 0.13241 | 1 | 0.13241 | 0 | 0.13241 | 0
D4 | Classroom | 617 | 41 |  |  | 796 | 18 | 18 | Rooftop Unit | 8 | 6368 | 5.8134 | 1 | 5.8134 | 2 | 5.8134 | 2
E1 | Classroom | 312 | 20 | Yes | 20 | 794 | 18 | 18 | Rooftop Unit | 8 | 6352 | 2.9471 | 1 | 2.9471 | 1 | 22.9471 | 3
E2 | Classroom | 752 | 50 | Yes | 20 | 796 | 18 | 18 | Rooftop Unit | 8 | 6368 | 7.0854 | 1 | 7.0854 | 2 | 27.0854 | 4
E3 | Classroom | 269 | 17 |  |  | 793 | 18 | 17 | Rooftop Unit | 8 | 6344 | 2.5441 | 1 | 2.5441 | 1 | 2.5441 | 1
E4 | Classroom | 715 | 47 | Yes | 20 | 795 | 18 | 18 | Rooftop Unit | 8 | 6360 | 6.7453 | 1 | 6.7453 | 2 | 26.7453 | 4
G1 | Classroom | 66 | 4 | Yes | 20 | 794 | 18 | 18 | Rooftop Unit | 8 | 6352 | 0.62343 | 1 | 0.62343 | 0 | 20.6234 | 3
G2 | Classroom | 857 | 57 | Yes | 20 | 796 | 18 | 18 | Rooftop Unit | 8 | 6368 | 8.0747 | 1 | 8.0747 | 2 | 28.0747 | 4
G3 | Classroom | 197 | 13 | Yes | 20 | 793 | 18 | 18 | Rooftop Unit | 8 | 6344 | 1.8632 | 1 | 1.8632 | 1 | 21.8632 | 3
G4 | Classroom | 813 | 54 | Yes | 20 | 797 | 18 | 18 | Rooftop Unit | 8 | 6376 | 7.6506 | 1 | 7.6506 | 2 | 27.6506 | 4
Gym | Recreational Area 1 | 442 | 29 |  |  | 1276 | 29 | 29 | Rooftop Unit | 8 | 10208 | 2.598 | 1 | 2.598 | 1 | 2.598 | 1
Gym | Gym Cafeteria | 306 | 20 |  |  | 886 | 20 | 20 | Rooftop Unit | 8 | 7088 | 2.5903 | 1 | 2.5903 | 1 | 2.5903 | 1
Gym | Recreational Area 1 | 630 | 42 |  |  | 1848 | 42 | 42 | Rooftop Unit | 8 | 14784 | 2.5568 | 1 | 2.5568 | 1 | 2.5568 | 1
Gym | Gym 2A | 716 | 47 |  |  | 9196 | 209 | 47 | Rooftop Unit | 8 | 73568 | 0.58395 | 1.4912 | 0.87076 | 0 | 0.87076 | 0
Gym | Gym 2B | 601 | 40 |  |  | 9196 | 209 | 40 | Rooftop Unit | 8 | 73568 | 0.49016 | 1.4912 | 0.7309 | 0 | 0.7309 | 0
Gym | Vestibule | 0 | 0 |  |  | 176 | 4 | 0 | Rooftop Unit | 8 | 1408 | 0 | 1 | 0 | 0 | 0 | 0
H1 | Classroom | 807 | 53 |  |  | 796 | 18 | 18 | Rooftop Unit | 8 | 6368 | 7.6036 | 1 | 7.6036 | 2 | 7.6036 | 2
H17 | Hallway | 91 | 6 |  |  | 264 | 6 | 6 | Rooftop Unit | 8 | 2112 | 2.5852 | 1 | 2.5852 | 1 | 2.5852 | 1
H2 | Classroom | 706 | 47 |  |  | 794 | 18 | 18 | Rooftop Unit | 8 | 6352 | 6.6688 | 1 | 6.6688 | 2 | 6.6688 | 2
H3 | Classroom | -660 | -44 |  |  | 793 | 18 | -44 | Rooftop Unit | 8 | 6344 | 6.2421 | 1 | 6.2421 | 2 | 6.2421 | 2
H4 | Classroom | 11 | 0 |  |  | 795 | 18 | 0 | Rooftop Unit | 8 | 6360 | 0.10377 | 1 | 0.10377 | 0 | 0.10377 | 0
Hallway | Hallway (Split Level South) | 48 | 3 |  |  | 136 | 3 | 3 | Rooftop Unit | 8 | 1088 | 2.6471 | 1 | 2.6471 | 1 | 2.6471 | 1
Hunter | Office | 229 | 15 |  |  | 664 | 15 | 15 | Rooftop Unit | 8 | 5312 | 2.5866 | 1 | 2.5866 | 1 | 2.5866 | 1
Hunting Park | Lobby | 1738 | 115 |  |  | 5069 | 115 | 115 | Rooftop Unit | 8 | 40552 | 2.5715 | 1.062 | 2.731 | 1 | 2.731 | 1
J | Hallway | 0 | 0 |  |  | 616 | 14 | 0 | Rooftop Unit | 8 | 4928 | 0 | 1 | 0 | 0 | 0 | 0
J1 | Classroom | -493 | -32 | Yes | 20 | 529 | 12 | 12 | Rooftop Unit | 8 | 4232 | 6.9896 | 1 | 6.9896 | 2 | 13.0104 | 3
J2 | Classroom | 381 | 25 |  |  | 792 | 18 | 18 | Rooftop Unit | 8 | 6336 | 3.608 | 1 | 3.608 | 1 | 3.608 | 1
J3 | Classroom | 493 | 32 |  |  | 528 | 12 | 12 | Rooftop Unit | 8 | 4224 | 7.0028 | 1 | 7.0028 | 2 | 7.0028 | 2
J4 | Classroom | 1208 | 80 |  |  | 528 | 12 | 12 | Rooftop Unit | 8 | 4224 | 17.1591 | 1 | 17.1591 | 3 | 17.1591 | 3
K | Hallway | 0 | 0 |  |  | 616 | 14 | 0 | Rooftop Unit | 8 | 4928 | 0 | 1 | 0 | 0 | 0 | 0
K1 | Classroom | 189 | 12 |  |  | 792 | 18 | 12 | Rooftop Unit | 8 | 6336 | 1.7898 | 1 | 1.7898 | 1 | 1.7898 | 1
K2 | Classroom | 682 | 45 |  |  | 794 | 18 | 18 | Rooftop Unit | 8 | 6352 | 6.4421 | 1 | 6.4421 | 2 | 6.4421 | 2
K3 | Classroom | 130 | 8 | Yes | 20 | 796 | 18 | 18 | Rooftop Unit | 8 | 6368 | 1.2249 | 1 | 1.2249 | 1 | 21.2249 | 3
K4 | Classroom | 617 | 41 |  |  | 797 | 18 | 18 | Rooftop Unit | 8 | 6376 | 5.8061 | 1 | 5.8061 | 2 | 5.8061 | 2
Kitchen | Kitchen | 1953 | 130 |  |  | 880 | 20 | 20 | Rooftop Unit | 8 | 7040 | 16.6449 | 1 | 16.6449 | 3 | 16.6449 | 3
Kitchen | Lounge | -3 | 0 |  |  | 73 | 1 | 0 | Rooftop Unit | 8 | 584 | 0.30822 | 1 | 0.30822 | 0 | 0.30822 | 0
L | Hallway | 0 | 0 |  |  | 704 | 16 | 0 | Rooftop Unit | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
L1 | Classroom | 79 | 5 | Yes | 20 | 794 | 18 | 18 | Rooftop Unit | 8 | 6352 | 0.74622 | 1 | 0.74622 | 0 | 20.7462 | 3
L2 | Classroom | 636 | 42 |  |  | 793 | 18 | 18 | Rooftop Unit | 8 | 6344 | 6.0151 | 1 | 6.0151 | 2 | 6.0151 | 2
L3 | Classroom | 109 | 7 | Yes | 20 | 792 | 18 | 18 | Rooftop Unit | 8 | 6336 | 1.0322 | 1 | 1.0322 | 1 | 21.0322 | 3
L4 | Classroom | 707 | 47 |  |  | 797 | 18 | 18 | Rooftop Unit | 8 | 6376 | 6.6531 | 1 | 6.6531 | 2 | 6.6531 | 2
Lobby | Main Lobby North | 147 | 9 |  |  | 410 | 9 | 9 | Rooftop Unit | 8 | 3280 | 2.689 | 1 | 2.689 | 1 | 2.689 | 1
M | Hallway | 0 | 0 |  |  | 704 | 16 | 0 | Rooftop Unit | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
M1 | Classroom | 226 | 15 |  |  | 794 | 18 | 15 | Rooftop Unit | 8 | 6352 | 2.1348 | 1 | 2.1348 | 1 | 2.1348 | 1
M2 | Classroom | 855 | 57 |  |  | 796 | 18 | 18 | Rooftop Unit | 8 | 6368 | 8.0559 | 1 | 8.0559 | 2 | 8.0559 | 2
M3 | Classroom | 17 | 1 |  |  | 793 | 18 | 1 | Rooftop Unit | 8 | 6344 | 0.16078 | 1 | 0.16078 | 0 | 0.16078 | 0
M4 | Classroom | 684 | 45 |  |  | 795 | 18 | 18 | Rooftop Unit | 8 | 6360 | 6.4528 | 1 | 6.4528 | 2 | 6.4528 | 2
Men's Bathroom | Men's Bathroom | 0 | 0 |  |  | 132 | 3 | 0 | Rooftop Unit | 8 | 1056 | 0 | 1 | 0 | 0 | 0 | 0
MS0S1 | Office | 432 | 28 |  |  | 528 | 12 | 12 | Rooftop Unit | 8 | 4224 | 6.1364 | 1 | 6.1364 | 2 | 6.1364 | 2
MS0S2 | Office | 1153 | 76 |  |  | 880 | 20 | 20 | Rooftop Unit | 8 | 7040 | 9.8267 | 1 | 9.8267 | 2 | 9.8267 | 2
MS2 | MS2 (Woodshop) | 480 | 32 |  |  | 1408 | 32 | 32 | Rooftop Unit | 8 | 11264 | 2.5568 | 1 | 2.5568 | 1 | 2.5568 | 1
MS2 | MS2 (Woodshop) | 768 | 51 |  |  | 1408 | 32 | 32 | Rooftop Unit | 8 | 11264 | 4.0909 | 1 | 4.0909 | 2 | 4.0909 | 2
MS6 | Office | 107 | 7 |  |  | 176 | 4 | 4 | Rooftop Unit | 8 | 1408 | 4.5597 | 1 | 4.5597 | 2 | 4.5597 | 2
MS7 | Office | 0 | 0 |  |  | 132 | 3 | 0 | Rooftop Unit | 8 | 1056 | 0 | 1 | 0 | 0 | 0 | 0
N1 | Classroom | 612 | 40 |  |  | 794 | 18 | 18 | Rooftop Unit | 8 | 6352 | 5.7809 | 1 | 5.7809 | 2 | 5.7809 | 2
N2 | Classroom (with office) | 100 | 6 |  |  | 796 | 18 | 6 | Rooftop Unit | 8 | 6368 | 0.94221 | 1 | 0.94221 | 0 | 0.94221 | 0
N3 | Classroom (with office) | 1490 | 99 |  |  | 795 | 18 | 18 | Rooftop Unit | 8 | 6360 | 14.0566 | 1 | 14.0566 | 3 | 14.0566 | 3
N4 | Classroom | 781 | 52 |  |  | 796 | 18 | 18 | Rooftop Unit | 8 | 6368 | 7.3587 | 1 | 7.3587 | 2 | 7.3587 | 2
Office | Office | 12 | 0 |  |  | 132 | 3 | 0 | Rooftop Unit | 8 | 1056 | 0.68182 | 1 | 0.68182 | 0 | 0.68182 | 0
S11 | AEP Office | -244 | -16 |  |  | 396 | 9 | -16 | Rooftop Unit | 8 | 3168 | 4.6212 | 1 | 4.6212 | 2 | 4.6212 | 2
- | Staff Lounge | 243 | 16 |  |  | 528 | 12 | 12 | Rooftop Unit | 8 | 4224 | 3.4517 | 1 | 3.4517 | 1 | 3.4517 | 1
- | Women's Bathroom | 0 | 0 |  |  | 132 | 3 | 0 | Rooftop Unit | 8 | 1056 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23
School: | Robert B. Pollock Elementary School
Vendor: | EMCORE Fluidics | Retest Report
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 313 | 20 |  |  | 945 | 21 | 20 | Perimeter Heater | 8 | 7560 | 2.4841 | 1 | 2.4841 | 1 | 2.4841 | 1
2 | Classroom | 385 | 25 |  |  | 945 | 21 | 21 | Perimeter Heater | 8 | 7560 | 3.0556 | 1 | 3.0556 | 1 | 3.0556 | 1
3 | Classroom | 141 | 9 | Yes | 20 | 945 | 21 | 21 | Perimeter Heater | 8 | 7560 | 1.119 | 1 | 1.119 | 1 | 21.119 | 3
4 | Classroom | 406 | 27 |  |  | 945 | 21 | 21 | Perimeter Heater | 8 | 7560 | 3.2222 | 1 | 3.2222 | 1 | 3.2222 | 1
5 | Classroom | 222 | 14 | Yes | 20 | 945 | 21 | 21 | Perimeter Heater | 8 | 7560 | 1.7619 | 1 | 1.7619 | 1 | 21.7619 | 3
6 | Classroom | 278 | 18 |  |  | 720 | 16 | 16 | Perimeter Heater | 8 | 5760 | 2.8958 | 1 | 2.8958 | 1 | 2.8958 | 1
7 | Classroom | 270 | 18 |  |  | 945 | 21 | 18 | Perimeter Heater | 8 | 7560 | 2.1429 | 1 | 2.1429 | 1 | 2.1429 | 1
8 | Classroom | 329 | 21 |  |  | 945 | 21 | 21 | Perimeter Heater | 8 | 7560 | 2.6111 | 1 | 2.6111 | 1 | 2.6111 | 1
9 | Classroom | 301 | 20 |  |  | 945 | 21 | 20 | Perimeter Heater | 8 | 7560 | 2.3889 | 1 | 2.3889 | 1 | 2.3889 | 1
10 | Classroom | 482 | 32 |  |  | 945 | 21 | 21 | Perimeter Heater | 8 | 7560 | 3.8254 | 1 | 3.8254 | 1 | 3.8254 | 1
11 | Classroom | 0 | 0 | Yes | 20 | 945 | 21 | 21 | Perimeter Heater | 8 | 7560 | 0 | 1 | 0 | 0 | 20 | 3
12 | Classroom | 369 | 24 |  |  | 945 | 21 | 21 | Perimeter Heater | 8 | 7560 | 2.9286 | 1 | 2.9286 | 1 | 2.9286 | 1
13 | Classroom | 282 | 18 |  |  | 945 | 21 | 18 | Perimeter Heater | 8 | 7560 | 2.2381 | 1 | 2.2381 | 1 | 2.2381 | 1
14 | Classroom | 338 | 22 |  |  | 945 | 21 | 21 | Perimeter Heater | 8 | 7560 | 2.6825 | 1 | 2.6825 | 1 | 2.6825 | 1
15 | Classroom | 275 | 18 |  |  | 945 | 21 | 18 | Perimeter Heater | 8 | 7560 | 2.1825 | 1 | 2.1825 | 1 | 2.1825 | 1
16 | Classroom | 311 | 20 |  |  | 840 | 19 | 19 | Perimeter Heater | 8 | 6720 | 2.7768 | 1 | 2.7768 | 1 | 2.7768 | 1
17 | Classroom | 294 | 19 |  |  | 945 | 21 | 19 | Perimeter Heater | 8 | 7560 | 2.3333 | 1 | 2.3333 | 1 | 2.3333 | 1
101 | Classroom | 505 | 33 |  |  | 1450 | 32 | 32 | Perimeter Heater | 8 | 11600 | 2.6121 | 1 | 2.6121 | 1 | 2.6121 | 1
102 | Classroom | 280 | 18 |  |  | 945 | 21 | 18 | Perimeter Heater | 8 | 7560 | 2.2222 | 1 | 2.2222 | 1 | 2.2222 | 1
103 | Classroom | 305 | 20 |  |  | 945 | 21 | 20 | Perimeter Heater | 8 | 7560 | 2.4206 | 1 | 2.4206 | 1 | 2.4206 | 1
104 | Classroom | 277 | 18 |  |  | 945 | 21 | 18 | Perimeter Heater | 8 | 7560 | 2.1984 | 1 | 2.1984 | 1 | 2.1984 | 1
105 | Classroom | 273 | 18 |  |  | 945 | 21 | 18 | Perimeter Heater | 8 | 7560 | 2.1667 | 1 | 2.1667 | 1 | 2.1667 | 1
106 | Classroom | 707 | 47 |  |  | 945 | 21 | 21 | Perimeter Heater | 8 | 7560 | 5.6111 | 1 | 5.6111 | 2 | 5.6111 | 2
107 | Classroom |  | 0 | Yes | 20 | 945 | 21 | 21 |  | 8 | 7560 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom | 315 | 21 |  |  | 594 | 13 | 13 | Perimeter Heater | 8 | 4752 | 3.9773 | 1 | 3.9773 | 1 | 3.9773 | 1
110 | Classroom | 301 | 20 | Yes | 20 | 945 | 21 | 21 | Perimeter Heater | 8 | 7560 | 2.3889 | 1 | 2.3889 | 1 | 22.3889 | 3
111 | Classroom | 276 | 18 |  |  | 480 | 10 | 10 | Perimeter Heater | 8 | 3840 | 4.3125 | 1 | 4.3125 | 2 | 4.3125 | 2
112 | Classroom | 276 | 18 |  |  | 945 | 21 | 18 | Perimeter Heater | 8 | 7560 | 2.1905 | 1 | 2.1905 | 1 | 2.1905 | 1
113 | Classroom | 272 | 18 |  |  | 945 | 21 | 18 | Perimeter Heater | 8 | 7560 | 2.1587 | 1 | 2.1587 | 1 | 2.1587 | 1
114 | Classroom | 277 | 18 |  |  | 945 | 21 | 18 | Perimeter Heater | 8 | 7560 | 2.1984 | 1 | 2.1984 | 1 | 2.1984 | 1
115 | Classroom | 275 | 18 |  |  | 945 | 21 | 18 | Perimeter Heater | 8 | 7560 | 2.1825 | 1 | 2.1825 | 1 | 2.1825 | 1
116 | Classroom | 289 | 19 |  |  | 945 | 21 | 19 | Perimeter Heater | 8 | 7560 | 2.2937 | 1 | 2.2937 | 1 | 2.2937 | 1
117A | Classroom | 579 | 38 |  |  | 1890 | 42 | 38 | Perimeter Heater | 8 | 15120 | 2.2976 | 1 | 2.2976 | 1 | 2.2976 | 1
118 | Classroom | 323 | 21 |  |  | 945 | 21 | 21 | Perimeter Heater | 8 | 7560 | 2.5635 | 1 | 2.5635 | 1 | 2.5635 | 1
- | Main Office |  | 0 | Yes | 20 | 674 | 15 | 15 |  | 8 | 5392 | 0 | 1 | 0 | 0 | 20 | 3
- | Principals Office |  | 0 | Yes | 20 | 96 | 2 | 2 |  | 8 | 768 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses Office |  | 0 | Yes | 20 | 96 | 2 | 2 |  | 8 | 768 | 0 | 1 | 0 | 0 | 20 | 3
- | Office |  | 0 | Yes | 20 | 108 | 2 | 2 |  | 8 | 864 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 5528 | 368 |  |  | 4240 | 96 | 96 | Air Handling Unit | 8 | 33920 | 9.7783 | 1.062 | 10.3849 | 3 | 10.3849 | 3
- | Cafeteria | 5093 | 339 |  |  | 4032 | 91 | 91 | Air Handling Unit | 8 | 32256 | 9.4736 | 1.062 | 10.0613 | 3 | 10.0613 | 3
- | Confrence Room | 275 | 18 |  |  | 374 | 8 | 8 | Perimeter Heater | 8 | 2992 | 5.5147 | 1 | 5.5147 | 2 | 5.5147 | 2
- | Gym | 3930 | 262 |  |  | 3901 | 88 | 88 | Air Handling Unit | 8 | 31208 | 7.5558 | 1.062 | 8.0245 | 2 | 8.0245 | 2
- | Kindergarten Classroom | 438 | 29 |  |  | 1450 | 32 | 29 | Perimeter Heater | 8 | 11600 | 2.2655 | 1 | 2.2655 | 1 | 2.2655 | 1
- | First Flr Office | 0 | 0 |  |  | 674 | 15 | 0 | Perimeter Heater | 8 | 5392 | 0 | 1 | 0 | 0 | 0 | 0
- | P1 Bungalow Building | 527 | 35 |  |  | 1248 | 28 | 28 | Perimeter Heater | 8 | 9984 | 3.1671 | 1 | 3.1671 | 1 | 3.1671 | 1
- | P2 Bungalow Building | 298 | 19 |  |  | 806 | 18 | 18 | Perimeter Heater | 8 | 6448 | 2.773 | 1 | 2.773 | 1 | 2.773 | 1
- | P3 Bungalow Building | 385 | 25 |  |  | 1040 | 23 | 23 | Perimeter Heater | 8 | 8320 | 2.7764 | 1 | 2.7764 | 1 | 2.7764 | 1
Sheet Last Modified: | 2021-04-21
School: | Potter Thomas Promise Academy Elementary School
Vendor: | Goldner | Retest
Devine 2nd Retest 2-15-21
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 322 | 21 |  |  | 1350 | 30 | 21 | Univent | 8 | 10800 | 1.7889 | 1 | 1.7889 | 1 | 1.7889 | 1
102 | Classroom | 387 | 25 |  |  | 1590 | 36 | 25 | Univent | 8 | 12720 | 1.8255 | 1 | 1.8255 | 1 | 1.8255 | 1
103 | Classroom | 374 | 24 |  |  | 1590 | 36 | 24 | Univent | 8 | 12720 | 1.7642 | 1 | 1.7642 | 1 | 1.7642 | 1
104 | Classroom | 817 | 54 |  |  | 1590 | 36 | 36 | Univent | 8 | 12720 | 3.8538 | 1 | 3.8538 | 1 | 3.8538 | 1
105 | Classroom | 296 | 19 |  |  | 1024 | 23 | 19 | Univent | 8 | 8192 | 2.168 | 1 | 2.168 | 1 | 2.168 | 1
106 | Music Room | 216 | 14 |  |  | 754 | 17 | 14 | Univent | 8 | 6032 | 2.1485 | 1 | 2.1485 | 1 | 2.1485 | 1
106 | Computer Lab | 149 | 9 | Yes | 20 | 1989 | 45 | 45 | Univent | 8 | 15912 | 0.56184 | 1 | 0.56184 | 0 | 20.5618 | 3
201 | Classroom | 245 | 16 |  |  | 812 | 18 | 16 | Univent | 8 | 6496 | 2.2629 | 1 | 2.2629 | 1 | 2.2629 | 1
202 | Classroom | 275 | 18 |  |  | 870 | 19 | 18 | Univent | 8 | 6960 | 2.3707 | 1 | 2.3707 | 1 | 2.3707 | 1
203 | Classroom | 329 | 21 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 2.8362 | 1 | 2.8362 | 1 | 2.8362 | 1
204 | Classroom | 350 | 23 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 3.0172 | 1 | 3.0172 | 1 | 3.0172 | 1
205 | Classroom | 356 | 23 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 3.069 | 1 | 3.069 | 1 | 3.069 | 1
206 | Classroom | 338 | 22 |  |  | 783 | 17 | 17 | Univent | 8 | 6264 | 3.2375 | 1 | 3.2375 | 1 | 3.2375 | 1
207 | Classroom | 469 | 31 |  |  | 841 | 19 | 19 | Univent | 8 | 6728 | 4.1825 | 1 | 4.1825 | 2 | 4.1825 | 2
208 | Classroom | 397 | 26 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 3.4224 | 1 | 3.4224 | 1 | 3.4224 | 1
209 | Classroom | 257 | 17 |  |  | 870 | 19 | 17 | Univent | 8 | 6960 | 2.2155 | 1 | 2.2155 | 1 | 2.2155 | 1
210 | Classroom | 368 | 24 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 3.1724 | 1 | 3.1724 | 1 | 3.1724 | 1
211 | Classroom | 348 | 23 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 3 | 1 | 3 | 1 | 3 | 1
212 | Classroom | 291 | 19 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 2.5086 | 1 | 2.5086 | 1 | 2.5086 | 1
213 | Classroom | 280 | 18 |  |  | 870 | 19 | 18 | Univent | 8 | 6960 | 2.4138 | 1 | 2.4138 | 1 | 2.4138 | 1
214 | Classroom | 319 | 21 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 2.75 | 1 | 2.75 | 1 | 2.75 | 1
215 | Classroom | 297 | 19 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 2.5603 | 1 | 2.5603 | 1 | 2.5603 | 1
216 | Classroom | 286 | 19 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 2.4655 | 1 | 2.4655 | 1 | 2.4655 | 1
217 | Classroom | 392 | 26 |  |  | 896 | 20 | 20 | Univent | 8 | 7168 | 3.2812 | 1 | 3.2812 | 1 | 3.2812 | 1
218 | Classroom | 296 | 19 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 2.5517 | 1 | 2.5517 | 1 | 2.5517 | 1
219 | Classroom | 307 | 20 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 2.6466 | 1 | 2.6466 | 1 | 2.6466 | 1
220 | Classroom | 235 | 15 |  |  | 870 | 19 | 15 | Univent | 8 | 6960 | 2.0259 | 1 | 2.0259 | 1 | 2.0259 | 1
221 | Classroom | 293 | 19 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 2.5259 | 1 | 2.5259 | 1 | 2.5259 | 1
222 | Classroom | 312 | 20 |  |  | 783 | 17 | 17 | Univent | 8 | 6264 | 2.9885 | 1 | 2.9885 | 1 | 2.9885 | 1
223 | Classroom | 238 | 15 |  |  | 870 | 19 | 15 | Univent | 8 | 6960 | 2.0517 | 1 | 2.0517 | 1 | 2.0517 | 1
224 | Classroom | 300 | 20 |  |  | 870 | 19 | 19 | Univent | 8 | 6960 | 2.5862 | 1 | 2.5862 | 1 | 2.5862 | 1
226 | Classroom | 365 | 24 |  |  | 942 | 21 | 21 | Univent | 8 | 7536 | 2.9061 | 1 | 2.9061 | 1 | 2.9061 | 1
226A | - |  | 0 | Yes | 20 | 269 | 6 | 6 |  | 8 | 2152 | 0 | 1 | 0 | 0 | 20 | 3
228 | Classroom | 364 | 24 |  |  | 942 | 21 | 21 | Univent | 8 | 7536 | 2.8981 | 1 | 2.8981 | 1 | 2.8981 | 1
228A | - |  | 0 | Yes | 20 | 269 | 6 | 6 |  | 8 | 2152 | 0 | 1 | 0 | 0 | 20 | 3
- | Art room | 642 | 42 |  |  | 1800 | 40 | 40 | Univent | 8 | 14400 | 2.675 | 1 | 2.675 | 1 | 2.675 | 1
| Art Room B |  | 0 |  |  | 260 | 5 | 0 |  | 8 | 2080 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria/Theatre | 0 | 0 | Yes | 20 | 5280 | 120 | 120 | Air Handling Unit | 8 | 42240 | 0 | 1.062 | 0 | 0 | 20 | 3
| ESOL Suite |  | 0 | Yes | 20 | 119 | 2 | 2 |  | 8 | 952 | 0 | 1 | 0 | 0 | 20 | 3
- | Community Room | 239 | 15 |  |  | 839 | 19 | 15 | Univent | 8 | 6712 | 2.1365 | 1 | 2.1365 | 1 | 2.1365 | 1
- | Gym | 0 | 0 |  |  | 5016 | 114 | 0 | Air Handling Unit | 8 | 40128 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Gym Offices | 0 | 0 | Yes | 20 | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 0 | 1 | 0 | 0 | 20 | 3
- | Kitchen | 273 | 18 |  |  | 1332 | 30 | 18 | Air Handling Unit | 8 | 10656 | 1.5372 | 1 | 1.5372 | 1 | 1.5372 | 1
- | Library | 5562 | 370 |  |  | 1944 | 44 | 44 | Air Handling Unit | 8 | 15552 | 21.4583 | 1 | 21.4583 | 3 | 21.4583 | 3
Counselor | Office |  | 0 | Yes | 20 | 261 | 5 | 5 |  | 8 | 2088 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office | 1418 | 94 |  |  | 1800 | 40 | 40 | Air Handling Unit | 8 | 14400 | 5.9083 | 1 | 5.9083 | 2 | 5.9083 | 2
- | Faculty lounge |  | 0 |  |  | 840 | 19 | 0 |  | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-29
School: | Powel/SLAMS Elementary School
Vendor: | Capital Retest 3-31-2021
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Report Classroom ID / Area ID Number | Posted Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) |  | Active Pure Unit Installed | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room
26 | 26 | Electrical room |  | 0 |  |  | 502 | 11 | 0
21 | 21 | Lockers | 98 | 6 |  |  | 114 | 2 | 2
23 | 23 | Lockers | 101 | 6 |  |  | 149 | 3 | 3
17 | 17 | Storage | 203 | 13 |  |  | 330 | 7 | 7
18 | 18 | Workshop | 362 | 24 |  |  | 305 | 6 | 6
103 | 101 | Cafeteria | 3580 | 238 |  |  | 3579 | 81 | 81
104 | - | Corridor | 498 | 33 |  |  | 977 | 22 | 22
105 | 100 | Waiting Area | 241 | 16 |  |  | 404 | 9 | 9
112 | 100A | Conselor's Office | 15 | 1 |  |  | 104 | 2 | 1
113 | 100G | Office | 16 | 1 |  |  | 123 | 2 | 1
114 | 100B | Dean's Office | 16 | 1 |  |  | 104 | 2 | 1
115 | 100F | Records | 14 | 0 |  |  | 101 | 2 | 0
115 | - | Open Office Space | 29 | 1 |  |  | 332 | 7 | 1
116 | 100C | Principal's Office | 30 | 2 |  |  | 166 | 3 | 2
118 | 100D | Conference Room | 67 | 4 |  |  | 186 | 4 | 4
119 | 101F | Kitchen Storage | 36 | 2 |  |  | 152 | 3 | 2
121 | 101E | Kitchen | 535 | 35 |  |  | 841 | 19 | 19
123 | - | Servery | 270 | 18 |  |  | 486 | 11 | 11
124 | 101B | Office | 33 | 2 |  |  | 91 | 2 | 2
126 | - | Corridor | 251 | 16 |  |  | 2146 | 48 | 16
127 | 102 | Kindergarten Classroom | 314 | 20 |  |  | 1023 | 23 | 20
128 | 103 | Classroom | 302 | 20 |  |  | 853 | 19 | 19
129 | 104 | Kindergarten Classroom | 317 | 21 |  |  | 1022 | 23 | 21
130 | 105 | Classroom | 318 | 21 |  |  | 851 | 19 | 19
131 | 106 | Kindergarten Classroom | 321 | 21 |  |  | 1022 | 23 | 21
132 | 107 | Classroom | 322 | 21 |  |  | 853 | 19 | 19
133 | 108 | Special Education Classroom | 147 | 9 |  |  | 378 | 8 | 8
134 | 109 | Classroom | 314 | 20 |  |  | 853 | 19 | 19
135 | 110 | Classroom | 326 | 21 |  |  | 852 | 19 | 19
136 | 111 | Classroom | 322 | 21 |  |  | 853 | 19 | 19
137 | 112 | Classroom | 323 | 21 |  |  | 842 | 19 | 19
138 | 113 | Classroom | 310 | 20 |  |  | 842 | 19 | 19
139 | 114 | Classroom | 317 | 21 |  |  | 844 | 19 | 19
140 | 115 | Classroom | 318 | 21 |  |  | 844 | 19 | 19
141 | 116 | Classroom | 325 | 21 |  |  | 851 | 19 | 19
142 | 117 | Classroom | 313 | 20 |  |  | 853 | 19 | 19
143 | 118 | Special Education Classroom | 151 | 10 |  |  | 388 | 8 | 8
145 | 119 | Library | 546 | 36 |  |  | 1712 | 38 | 36
146 | 119B | Conference Room | 32 | 2 |  |  | 261 | 5 | 2
147 | 119A | Work Room | 19 | 1 |  |  | 270 | 6 | 1
148 | 120/121 | Art Classroom | 379 | 25 |  |  | 956 | 21 | 21
149 | 120A | Art Storage Room | 50 | 3 |  |  | 61 | 1 | 1
150 | 121/123 | Music Classroom | 200 | 13 |  |  | 1083 | 24 | 13
152 | 123A | Music Studio | 53 | 3 |  |  | 237 | 5 | 3
161 | - | Lobby | 208 | 13 |  |  | 475 | 10 | 10
162 | 122 | Gym | 4453 | 296 |  |  | 5236 | 119 | 119
163 | 125A | Office | 55 | 3 |  |  | 161 | 3 | 3
164 | 125B | Storage | 35 | 2 |  |  | 141 | 3 | 2
167 | - | Small Group | 1288 | 85 |  |  | 963 | 21 | 21
168 | - | Open Space/Corridor | 196 | 13 |  |  | 324 | 7 | 7
201 | - | Corridor | 472 | 31 |  |  | 563 | 12 | 12
212 | 200A | Conselor's Office | 22 | 1 |  |  | 104 | 2 | 1
214 | 200B | Principal's Office | 33 | 2 |  |  | 166 | 3 | 2
216 | 200C | Conference Room | 65 | 4 |  |  | 189 | 4 | 4
217 | 200D | Small Meeting Room | 20 | 1 |  |  | 96 | 2 | 1
218 | 200E | Small Meeting Room | 20 | 1 |  |  | 96 | 2 | 1
219 | 200F | Records | 8 | 0 |  |  | 180 | 4 | 0
202 | 201 | Nurse's Suite | 23 | 1 |  |  | 221 | 5 | 1
203 | 201D | Exam Room | 12 | 0 |  |  | 81 | 1 | 0
204 | 201A | Exam Room | 13 | 0 |  |  | 102 | 2 | 0
205 | 200 | Waiting Area | 161 | 10 |  |  | 359 | 8 | 8
213 | 201E | Building Storage | 44 | 2 |  |  | 494 | 11 | 2
215 | - | Open Office | 121 | 8 |  |  | 1263 | 28 | 8
220 | - | Corridor | 11 | 0 |  |  | 266 | 6 | 0
221 | 201H | Faculty Lounge | 126 | 8 |  |  | 419 | 9 | 8
226 | - | Corridor | 233 | 15 |  |  | 3096 | 70 | 15
227 | 202 | Classroom | 421 | 28 |  |  | 858 | 19 | 19
228 | 203 | Classroom | 446 | 29 |  |  | 860 | 19 | 19
229 | 204 | Classroom | 427 | 28 |  |  | 856 | 19 | 19
230 | 205 | Classroom | 416 | 27 |  |  | 858 | 19 | 19
231 | 206 | Classroom | 426 | 28 |  |  | 858 | 19 | 19
232 | 207 | Classroom | 417 | 27 |  |  | 860 | 19 | 19
233 | 208 | Special Education Classroom | 195 | 13 |  |  | 377 | 8 | 8
234 | 209 | Classroom | 438 | 29 |  |  | 860 | 19 | 19
235 | 210 | Art Classroom | 494 | 32 |  |  | 1235 | 28 | 28
237 | 210A | Storage | 18 | 1 |  |  | 48 | 1 | 1
239 | 210B | Storage | 33 | 2 |  |  | 113 | 2 | 2
236 | 211 | Classroom | 435 | 29 |  |  | 860 | 19 | 19
241 | 212 | Classroom | 450 | 30 |  |  | 852 | 19 | 19
238 | 213 | Classroom | 425 | 28 |  |  | 851 | 19 | 19
243 | 214 | Classroom | 447 | 29 |  |  | 859 | 19 | 19
240 | 215 | Classroom | 456 | 30 |  |  | 852 | 19 | 19
244 | 216 | Small Group Classroom | 119 | 7 |  |  | 388 | 8 | 7
242 | 217 | Pre-Eng. Classroom | 417 | 27 |  |  | 860 | 19 | 19
245 | 219 | Makerspace | 677 | 45 |  |  | 165 | 3 | 3
248 | 220 | Science Classroom | 1385 | 92 |  |  | 1289 | 29 | 29
249 | 220B | Prep Room | 739 | 49 |  |  | 403 | 9 | 9
250 | 221 | Classroom | 1356 | 90 |  |  | 1285 | 29 | 29
256 | 221C | Storage | 0 | 0 |  |  | 50 | 1 | 0
253 | 221C | Room | 489 | 32 |  |  | 632 | 14 | 14
254 | 225 | Office | 50 | 3 |  |  | 173 | 3 | 3
266 | - | West Hallway | 208 | 13 |  |  | 779 | 17 | 13
Sheet Last Modified: | 2021-03-31
School: | Anna B. Pratt Elementary School
Vendor: | Capital | Devine ABR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
106 | Classroom / Swing Space | 597 | 39 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 4.7837 | 1 | 4.7837 | 2 | 4.7837 | 2
109 | Classroom | 651 | 43 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 5.2163 | 1 | 5.2163 | 2 | 5.2163 | 2
110 | Classroom | 327 | 21 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 2.6202 | 1 | 2.6202 | 1 | 2.6202 | 1
111 | Classroom | 320 | 21 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 2.5641 | 1 | 2.5641 | 1 | 2.5641 | 1
112 | Classroom | 393 | 26 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 3.149 | 1 | 3.149 | 1 | 3.149 | 1
113 | Special Education | 453 | 30 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 3.6298 | 1 | 3.6298 | 1 | 3.6298 | 1
114 | Classroom | 442 | 29 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 3.5417 | 1 | 3.5417 | 1 | 3.5417 | 1
201 | Classroom / Swing Space | 473 | 31 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 3.7901 | 1 | 3.7901 | 1 | 3.7901 | 1
200 / 202 | Library | 776 | 51 |  |  | 1848 | 42 | 42 | Univent | 8 | 14784 | 3.1494 | 1 | 3.1494 | 1 | 3.1494 | 1
208 | Classroom | 367 | 24 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 2.9407 | 1 | 2.9407 | 1 | 2.9407 | 1
209 | Classroom | 489 | 32 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 3.9183 | 1 | 3.9183 | 1 | 3.9183 | 1
210 | Technology Classroom | 422 | 28 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 3.3814 | 1 | 3.3814 | 1 | 3.3814 | 1
211 | Classroom | 313 | 20 |  |  | 936 | 21 | 20 | Univent | 8 | 7488 | 2.508 | 1 | 2.508 | 1 | 2.508 | 1
212 | Classroom | 526 | 35 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 4.2147 | 1 | 4.2147 | 2 | 4.2147 | 2
213 | Classroom | 468 | 31 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 3.75 | 1 | 3.75 | 1 | 3.75 | 1
214 | Data Room | 433 | 28 |  |  | 399 | 9 | 9 | Univent | 8 | 3192 | 8.1391 | 1 | 8.1391 | 2 | 8.1391 | 2
301 | Music Room | 327 | 21 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 2.6202 | 1 | 2.6202 | 1 | 2.6202 | 1
302 | Classroom | 311 | 20 |  |  | 936 | 21 | 20 | Univent | 8 | 7488 | 2.492 | 1 | 2.492 | 1 | 2.492 | 1
308 | Classroom | 386 | 25 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 3.0929 | 1 | 3.0929 | 1 | 3.0929 | 1
309 | Special Education | 459 | 30 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 3.6779 | 1 | 3.6779 | 1 | 3.6779 | 1
310 | Special Education | 447 | 29 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 3.5817 | 1 | 3.5817 | 1 | 3.5817 | 1
311 | Classroom | 430 | 28 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 3.4455 | 1 | 3.4455 | 1 | 3.4455 | 1
312 | Classroom | 615 | 41 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 4.9279 | 1 | 4.9279 | 2 | 4.9279 | 2
313 | Classroom | 330 | 22 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 2.6442 | 1 | 2.6442 | 1 | 2.6442 | 1
314 | Classroom | 522 | 34 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 4.1827 | 1 | 4.1827 | 2 | 4.1827 | 2
315 | Staff Room | 361 | 24 |  |  | 399 | 9 | 9 | Univent | 8 | 3192 | 6.7857 | 1 | 6.7857 | 2 | 6.7857 | 2
- | Main Office |  | 0 | Yes | 20 | 352 | 8 | 8 |  | 8 | 2816 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 228 | 5 | 5 |  | 8 | 1824 | 0 | 1 | 0 | 0 | 20 | 3
- | AS Office |  | 0 | Yes | 20 | 192 | 4 | 4 |  | 8 | 1536 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses Office |  | 0 | Yes | 20 | 156 | 3 | 3 |  | 8 | 1248 | 0 | 1 | 0 | 0 | 20 | 3
- | Climate Office |  | 0 | Yes | 20 | 156 | 3 | 3 |  | 8 | 1248 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselors Office |  | 0 | Yes | 20 | 156 | 3 | 3 |  | 8 | 1248 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-23
School: | Prince Hall Elementary School
Vendor: | Devine Brothers | Retest | Gymnasium
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
1 | Classroom | 380 | 25 |  |  | 1200 | 27 | 25 | Univent | 8 | 9600 | 2.375 | 1 | 2.375 | 1 | 2.375 | 1
2 | Classroom | 321 | 21 |  |  | 1200 | 27 | 21 | Univent | 8 | 9600 | 2.0063 | 1 | 2.0063 | 1 | 2.0063 | 1
3 | Classroom | 387 | 25 |  |  | 1200 | 27 | 25 | Univent | 8 | 9600 | 2.4188 | 1 | 2.4188 | 1 | 2.4188 | 1
4 | Classroom | 304 | 20 |  |  | 1200 | 27 | 20 | Univent | 8 | 9600 | 1.9 | 1 | 1.9 | 1 | 1.9 | 1
5 | Classroom | 313 | 20 |  |  | 900 | 20 | 20 | Univent | 8 | 7200 | 2.6083 | 1 | 2.6083 | 1 | 2.6083 | 1
6 | Classroom | 268 | 17 | Yes | 20 | 900 | 20 | 20 | Univent | 8 | 7200 | 2.2333 | 1 | 2.2333 | 1 | 22.2333 | 3
7 | Classroom | 351 | 23 |  |  | 836 | 19 | 19 | Univent | 8 | 6688 | 3.1489 | 1 | 3.1489 | 1 | 3.1489 | 1
8 | Classroom | 334 | 22 |  |  | 874 | 19 | 19 | Univent | 8 | 6992 | 2.8661 | 1 | 2.8661 | 1 | 2.8661 | 1
9 | Classroom | 235 | 15 | Yes | 20 | 1050 | 23 | 23 | Univent | 8 | 8400 | 1.6786 | 1 | 1.6786 | 1 | 21.6786 | 3
10 | Classroom | 375 | 25 |  |  | 888 | 20 | 20 | Univent | 8 | 7104 | 3.1672 | 1 | 3.1672 | 1 | 3.1672 | 1
11 | Classroom | 242 | 16 | Yes | 20 | 1066 | 24 | 24 | Univent | 8 | 8528 | 1.7026 | 1 | 1.7026 | 1 | 21.7026 | 3
12 | Classroom | 234 | 15 | Yes | 20 | 1134 | 25 | 25 | Univent | 8 | 9072 | 1.5476 | 1 | 1.5476 | 1 | 21.5476 | 3
13 | Classroom | 227 | 15 | Yes | 20 | 1100 | 25 | 25 | Univent | 8 | 8800 | 1.5477 | 1 | 1.5477 | 1 | 21.5477 | 3
103 | Classroom | 601 | 40 |  |  | 1280 | 29 | 29 | Univent | 8 | 10240 | 3.5215 | 1 | 3.5215 | 1 | 3.5215 | 1
104 | Classroom | 696 | 46 |  |  | 1280 | 29 | 29 | Univent | 8 | 10240 | 4.0781 | 1 | 4.0781 | 2 | 4.0781 | 2
105 | Classroom | 664 | 44 |  |  | 1360 | 30 | 30 | Univent | 8 | 10880 | 3.6618 | 1 | 3.6618 | 1 | 3.6618 | 1
106 | Classroom | 739 | 49 |  |  | 1280 | 29 | 29 | Univent | 8 | 10240 | 4.3301 | 1 | 4.3301 | 2 | 4.3301 | 2
112 | Classroom |  | 0 | Yes | 20 | 1360 | 30 | 30 |  | 8 | 10880 | 0 | 1 | 0 | 0 | 20 | 3
116 | Classroom | 279 | 18 |  |  | 400 | 9 | 9 | Univent | 8 | 3200 | 5.2313 | 1 | 5.2313 | 2 | 5.2313 | 2
117 | Classroom | 322 | 21 |  |  | 700 | 15 | 15 | Univent | 8 | 5600 | 3.45 | 1 | 3.45 | 1 | 3.45 | 1
201 | Classroom | 418 | 27 |  |  | 1200 | 27 | 27 | Univent | 8 | 9600 | 2.6125 | 1 | 2.6125 | 1 | 2.6125 | 1
202 | Classroom | 292 | 19 | Yes | 20 | 1200 | 27 | 27 | Univent | 8 | 9600 | 1.825 | 1 | 1.825 | 1 | 21.825 | 3
203 | Classroom | 311 | 20 |  |  | 1200 | 27 | 20 | Univent | 8 | 9600 | 1.9438 | 1 | 1.9438 | 1 | 1.9438 | 1
204 | Classroom | 259 | 17 | Yes | 20 | 1200 | 27 | 27 | Univent | 8 | 9600 | 1.6187 | 1 | 1.6187 | 1 | 21.6187 | 3
205 | Classroom | 377 | 25 |  |  | 900 | 20 | 20 | Univent | 8 | 7200 | 3.1417 | 1 | 3.1417 | 1 | 3.1417 | 1
206 | Classroom | 338 | 22 |  |  | 900 | 20 | 20 | Univent | 8 | 7200 | 2.8167 | 1 | 2.8167 | 1 | 2.8167 | 1
207 | Classroom | 238 | 15 |  |  | 836 | 19 | 15 | Univent | 8 | 6688 | 2.1352 | 1 | 2.1352 | 1 | 2.1352 | 1
208 | Classroom | 312 | 20 |  |  | 874 | 19 | 19 | Univent | 8 | 6992 | 2.6773 | 1 | 2.6773 | 1 | 2.6773 | 1
209 | Classroom | 244 | 16 | Yes | 20 | 1050 | 23 | 23 | Univent | 8 | 8400 | 1.7429 | 1 | 1.7429 | 1 | 21.7429 | 3
210 | Classroom | 240 | 16 |  |  | 888 | 20 | 16 | Univent | 8 | 7104 | 2.027 | 1 | 2.027 | 1 | 2.027 | 1
211 | Classroom | 263 | 17 |  |  | 1066 | 24 | 17 | Univent | 8 | 8528 | 1.8504 | 1 | 1.8504 | 1 | 1.8504 | 1
212 | Classroom | 332 | 22 |  |  | 1170 | 26 | 22 | Univent | 8 | 9360 | 2.1282 | 1 | 2.1282 | 1 | 2.1282 | 1
213 | Classroom | 614 | 40 |  |  | 988 | 22 | 22 | Univent | 8 | 7904 | 4.6609 | 1 | 4.6609 | 2 | 4.6609 | 2
- | AUDITORIUM | 1185 | 79 |  |  | 3363 | 76 | 76 | Air Handling Unit | 8 | 26904 | 2.6427 | 1.062 | 2.8067 | 1 | 2.8067 | 1
- | Admin. Main Office | 56 | 3 |  |  | 255 | 5 | 3 | Univent | 8 | 2040 | 1.6471 | 1 | 1.6471 | 1 | 1.6471 | 1
- | Admin. Office | 28 | 1 |  |  | 126 | 2 | 1 | Univent | 8 | 1008 | 1.6667 | 1 | 1.6667 | 1 | 1.6667 | 1
- | Main Office | 301 | 20 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 3.1354 | 1 | 3.1354 | 1 | 3.1354 | 1
- | Principal's Office |  | 0 | Yes | 20 | 255 | 5 | 5 |  | 8 | 2040 | 0 | 1 | 0 | 0 | 20 | 3
- | Copy Room Office | 16 | 1 |  |  | 98 | 2 | 1 | Univent | 8 | 784 | 1.2245 | 1 | 1.2245 | 1 | 1.2245 | 1
- | Counselor's Office | 107 | 7 |  |  | 416 | 9 | 7 | Univent | 8 | 3328 | 1.9291 | 1 | 1.9291 | 1 | 1.9291 | 1
- | Computer Room Classroom | 380 | 25 |  |  | 1600 | 36 | 25 | Univent | 8 | 12800 | 1.7812 | 1 | 1.7812 | 1 | 1.7812 | 1
- | IMC Classroom | 1021 | 68 |  |  | 4335 | 98 | 68 | Univent | 8 | 34680 | 1.7664 | 1.062 | 1.876 | 1 | 1.876 | 1
- | Gym | 0 | 0 |  |  | 4800 | 109 | 0 | Air Handling Unit | 8 | 38400 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Gym Locker Rooms | 335 | 22 |  |  | 403 | 9 | 9 | Air Handling Unit | 8 | 3224 | 6.2345 | 1 | 6.2345 | 2 | 6.2345 | 2
- | Main Entrance | 68 | 4 |  |  | 150 | 3 | 3 | Univent | 8 | 1200 | 3.4 | 1 | 3.4 | 1 | 3.4 | 1
- | Multi-Purpose/Cafe | 2016 | 134 |  |  | 2760 | 62 | 62 | Air Handling Unit | 8 | 22080 | 5.4783 | 1.062 | 5.8181 | 2 | 5.8181 | 2
- | Nurse's Office 1 | 50 | 3 |  |  | 90 | 2 | 2 | Univent | 8 | 720 | 4.1667 | 1 | 4.1667 | 2 | 4.1667 | 2
- | Nurse's Office 2 | 40 | 2 |  |  | 110 | 2 | 2 | Univent | 8 | 880 | 2.7273 | 1 | 2.7273 | 1 | 2.7273 | 1
- | Nurse's Office | 71 | 4 | Yes | 20 | 160 | 3 | 3 | Univent | 8 | 1280 | 3.3281 | 1 | 3.3281 | 1 | 23.3281 | 3
Sheet Last Modified: | 2021-03-18
School: | A. Philip Randolph Career and Technical High School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
20 | Classroom | 1172 | 78 |  |  |  | 0 | 0 | Air Coil Unit
21 | Classroom | 1124 | 74 |  |  | 600 | 13 | 13 | Air Coil Unit | 8 | 4800 | 14.05 | 1 | 14.05 | 3 | 14.05 | 3
23 | Classroom | 1177 | 78 |  |  | 720 | 16 | 16 | Air Coil Unit | 8 | 5760 | 12.2604 | 1 | 12.2604 | 3 | 12.2604 | 3
24 | Classroom | 889 | 59 |  |  | 792 | 18 | 18 | Air Coil Unit | 8 | 6336 | 8.4186 | 1 | 8.4186 | 2 | 8.4186 | 2
36 | Classroom | 93 | 6 |  |  |  | 0 | 0 | Rooftop Unit
37 | Classroom | 176 | 11 |  |  | 704 | 16 | 11 | Rooftop Unit | 8 | 5632 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
38 | DENTAL SHOP | 236 | 15 |  |  | 1596 | 36 | 15 | Rooftop Unit | 8 | 12768 | 1.109 | 1 | 1.109 | 1 | 1.109 | 1
38 | DENTAL IMAGE ROOM | 8 | 0 |  |  |  | 0 | 0 | Rooftop Unit
38 | DENTAL X-RAY ROOM | 12 | 0 |  |  |  | 0 | 0 | Rooftop Unit
39 | Classroom | 73 | 4 |  |  |  | 0 | 0 | Rooftop Unit
50 | Art Room | 694 | 46 |  |  | 1008 | 22 | 22 | Air Coil Unit | 8 | 8064 | 5.1637 | 1 | 5.1637 | 2 | 5.1637 | 2
51 | Classroom | 199 | 13 |  |  | 510 | 11 | 11 | Air Coil Unit | 8 | 4080 | 2.9265 | 1 | 2.9265 | 1 | 2.9265 | 1
52 | Classroom | 435 | 29 |  |  | 420 | 9 | 9 | Air Coil Unit | 8 | 3360 | 7.7679 | 1 | 7.7679 | 2 | 7.7679 | 2
53 | Classroom | 483 | 32 |  |  | 612 | 13 | 13 | Air Coil Unit | 8 | 4896 | 5.9191 | 1 | 5.9191 | 2 | 5.9191 | 2
54 | Classroom | 784 | 52 |  |  | 798 | 18 | 18 | Air Coil Unit | 8 | 6384 | 7.3684 | 1 | 7.3684 | 2 | 7.3684 | 2
55 | Classroom | 149 | 9 |  |  | 660 | 15 | 9 | Air Coil Unit | 8 | 5280 | 1.6932 | 1 | 1.6932 | 1 | 1.6932 | 1
56 | Classroom | 570 | 38 |  |  | 1190 | 27 | 27 | Air Coil Unit | 8 | 9520 | 3.5924 | 1 | 3.5924 | 1 | 3.5924 | 1
57 | Classroom | 505 | 33 |  |  | 522 | 11 | 11 | Air Coil Unit | 8 | 4176 | 7.2557 | 1 | 7.2557 | 2 | 7.2557 | 2
71 | Room | 262 | 17 |  |  | 480 | 10 | 10 | Air Coil Unit | 8 | 3840 | 4.0938 | 1 | 4.0938 | 2 | 4.0938 | 2
72 | Room | 289 | 19 |  |  | 510 | 11 | 11 | Air Coil Unit | 8 | 4080 | 4.25 | 1 | 4.25 | 2 | 4.25 | 2
73 | Classroom | 0 | 0 |  |  | 616 | 14 | 0 | Air Coil Unit | 8 | 4928 | 0 | 1 | 0 | 0 | 0 | 0
74 | Room | 0 | 0 |  |  | 572 | 13 | 0 | Air Coil Unit | 8 | 4576 | 0 | 1 | 0 | 0 | 0 | 0
75 | Classroom | 0 | 0 |  |  | 660 | 15 | 0 | Air Coil Unit | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
76 | Classroom | 0 | 0 |  |  | 600 | 13 | 0 | Air Coil Unit | 8 | 4800 | 0 | 1 | 0 | 0 | 0 | 0
94 | Room | 88 | 5 |  |  | 72 | 1 | 1 | Air Coil Unit | 8 | 576 | 9.1667 | 1 | 9.1667 | 2 | 9.1667 | 2
100 | Classroom | 197 | 13 |  |  | 396 | 9 | 9 | Air Coil Unit | 8 | 3168 | 3.7311 | 1 | 3.7311 | 1 | 3.7311 | 1
- | Automotive | 80 | 5 |  |  |  | 0 | 0 | Air Coil Unit
- | AV storage | 96 | 6 |  |  |  | 0 | 0 | Air Coil Unit
- | BEHAVIORAL THERAPIST OFFICE | 26 | 1 |  |  |  | 0 | 0 | Rooftop Unit
- | Boys Bathroom | 0 | 0 |  |  |  | 0 | 0 | Air Coil Unit
- | Break Room | 168 | 11 |  |  |  | 0 | 0 | Air Coil Unit
- | CAFETERIA | 2027 | 135 |  |  | 3828 | 87 | 87 | Rooftop Unit | 8 | 30624 | 3.9714 | 1.062 | 4.2178 | 2 | 4.2178 | 2
- | Cafeteria | 2027 | 135 |  |  | 704 | 16 | 16 | Air Coil Unit | 8 | 5632 | 21.5945 | 1 | 21.5945 | 3 | 21.5945 | 3
- | Classrooms | 392 | 26 |  |  | 600 | 13 | 13 | Air Coil Unit | 8 | 4800 | 4.9 | 1 | 4.9 | 2 | 4.9 | 2
- | Classrooms | 5734 | 382 |  |  | 720 | 16 | 16 | Air Coil Unit | 8 | 5760 | 59.7292 | 1 | 59.7292 | 5 | 59.7292 | 5
- | Classrooms | 4521 | 301 |  |  | 792 | 18 | 18 | Air Coil Unit | 8 | 6336 | 42.8125 | 1 | 42.8125 | 4 | 42.8125 | 4
- | Classrooms | 0 | 0 |  |  | 572 | 13 | 0 | Air Coil Unit | 8 | 4576 | 0 | 1 | 0 | 0 | 0 | 0
- | COUNSELORS OFFICE | 19 | 1 |  |  |  | 0 | 0 | Rooftop Unit
- | Engineers Office | 238 | 15 |  |  |  | 0 | 0 | Air Coil Unit
- | Girls Bathroom | 0 | 0 |  |  | 200 | 4 | 0 | Air Coil Unit | 8 | 1600 | 0 | 1 | 0 | 0 | 0 | 0
- | Hallway | 245 | 16 |  |  |  | 0 | 0 | Air Coil Unit
- | IMC side area | 657 | 43 |  |  |  | 0 | 0 | Air Coil Unit
- | IMC area | 118 | 7 |  |  | 1664 | 37 | 7 | Air Coil Unit | 8 | 13312 | 0.53185 | 1 | 0.53185 | 0 | 0.53185 | 0
- | INSPECTORS OFFICE | 0 | 0 |  |  |  | 0 | 0 | Rooftop Unit
- | IT ROOM | 40 | 2 |  |  |  | 0 | 0 | Rooftop Unit
- | kitchen | 1766 | 117 |  |  | 722 | 16 | 16 | Air Coil Unit | 8 | 5776 | 18.3449 | 1 | 18.3449 | 3 | 18.3449 | 3
- | Kitchen | 3575 | 238 |  |  | 722 | 16 | 16 | Air Coil Unit | 8 | 5776 | 37.1364 | 1 | 37.1364 | 4 | 37.1364 | 4
- | Kitchen Dining | 93 | 6 |  |  | 252 | 5 | 5 | Air Coil Unit | 8 | 2016 | 2.7679 | 1 | 2.7679 | 1 | 2.7679 | 1
- | Library | 29 | 1 |  |  | 1664 | 37 | 1 | Air Coil Unit | 8 | 13312 | 0.13071 | 1 | 0.13071 | 0 | 0.13071 | 0
- | MAIL ROOM | 50 | 3 |  |  | 384 | 8 | 3 | Rooftop Unit | 8 | 3072 | 0.97656 | 1 | 0.97656 | 0 | 0.97656 | 0
- | MAIN OFFICE | 113 | 7 |  |  | 134 | 3 | 3 | Rooftop Unit | 8 | 1072 | 6.3246 | 1 | 6.3246 | 2 | 6.3246 | 2
- | CONFERENCE ROOM | 23 | 1 |  |  | 247 | 5 | 1 | Rooftop Unit | 8 | 1976 | 0.69838 | 1 | 0.69838 | 0 | 0.69838 | 0
Main office, classrooms | Main office, classrooms | 1328 | 88 |  |  | 285 | 6 | 6 | Air Coil Unit | 8 | 2280 | 34.9474 | 1 | 34.9474 | 4 | 34.9474 | 4
- | Ms. SMALLEY OFFICE | 7 | 0 |  |  | 120 | 2 | 0 | Rooftop Unit | 8 | 960 | 0.4375 | 1 | 0.4375 | 0 | 0.4375 | 0
- | NURSES OFFICE | 156 | 10 |  |  | 196 | 4 | 4 | Rooftop Unit | 8 | 1568 | 5.9694 | 1 | 5.9694 | 2 | 5.9694 | 2
- | office next to electrical room | 136 | 9 |  |  | 140 | 3 | 3 | Air Coil Unit | 8 | 1120 | 7.2857 | 1 | 7.2857 | 2 | 7.2857 | 2
office diffuser s1 | office | 223 | 14 |  |  | 140 | 3 | 3 | Air Coil Unit | 8 | 1120 | 11.9464 | 1 | 11.9464 | 3 | 11.9464 | 3
- | kitchen office | 21 | 1 |  |  | 320 | 7 | 1 | Air Coil Unit | 8 | 2560 | 0.49219 | 1 | 0.49219 | 0 | 0.49219 | 0
- | VP office | 0 | 0 |  |  | 130 | 2 | 0 | Air Coil Unit | 8 | 1040 | 0 | 1 | 0 | 0 | 0 | 0
office Diffuser S6 | office | 0 | 0 |  |  | 192 | 4 | 0 | Air Coil Unit | 8 | 1536 | 0 | 1 | 0 | 0 | 0 | 0
office Diffuser S1 | office | 0 | 0 |  |  | 320 | 7 | 0 | Air Coil Unit | 8 | 2560 | 0 | 1 | 0 | 0 | 0 | 0
office diffuser s18 | office | 78 | 5 |  |  | 120 | 2 | 2 | Air Coil Unit | 8 | 960 | 4.875 | 1 | 4.875 | 2 | 4.875 | 2
office diffuser s17 | office | 84 | 5 |  |  | 308 | 7 | 5 | Air Coil Unit | 8 | 2464 | 2.0455 | 1 | 2.0455 | 1 | 2.0455 | 1
office diffuser s16 | office | 108 | 7 |  |  | 280 | 6 | 6 | Air Coil Unit | 8 | 2240 | 2.8929 | 1 | 2.8929 | 1 | 2.8929 | 1
OFFICE IN BACK OF MAIN OFFICE | OFFICE IN BACK OF MAIN OFFICE | 0 | 0 |  |  | 110 | 2 | 0 | Rooftop Unit | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
OFFICE NEXT TO RM 39 | OFFICE NEXT TO RM 39 | 23 | 1 |  |  | 216 | 4 | 1 | Rooftop Unit | 8 | 1728 | 0.79861 | 1 | 0.79861 | 0 | 0.79861 | 0
- | Paint shop | 0 | 0 |  |  | 320 | 7 | 0 | H2-7 | 8 | 2560 | 0 | 1 | 0 | 0 | 0 | 0
- | Paint shop | 0 | 0 |  |  |  | 0 | 0 | H2-8
PRINCIPLE OFFICE | PRINCIPLE OFFICE | 49 | 3 |  |  | 16 | 0 | 0 | Rooftop Unit | 8 | 128 | 22.9688 | 1 | 22.9688 | 3 | 22.9688 | 3
security | office diffuser s4 | 180 | 12 |  |  |  | 0 | 0 | Air Coil Unit
- | Shop area | 408 | 27 |  |  |  | 0 | 0 | H2-5
- | Shop area | 1346 | 89 |  |  |  | 0 | 0 | H1-4
- | Shop area | 591 | 39 |  |  |  | 0 | 0 | H1-3
- | Shop area | 450 | 30 |  |  |  | 0 | 0 | H4-14
- | Shop area | 0 | 0 |  |  |  | 0 | 0 | H4-13
- | Shop area | 0 | 0 |  |  |  | 0 | 0 | H4-12
- | Shop area | 0 | 0 |  |  |  | 0 | 0 | H3-10
- | Shop area | 0 | 0 |  |  |  | 0 | 0 | H3-11
- | Shop Classrooms | 2065 | 137 |  |  |  | 0 | 0 | Air Coil Unit
- | SPEECH THERAPIST NEXT TO PRINCIPLE OFFICE | 60 | 4 |  |  |  | 0 | 0 | Rooftop Unit
- | SPEECH THERAPIST OFFICE | 20 | 1 |  |  |  | 0 | 0 | Rooftop Unit
storage diffuser s11 | storage | 53 | 3 |  |  |  | 0 | 0 | Air Coil Unit
storage diffuser s10 | storage | 192 | 12 |  |  |  | 0 | 0 | Air Coil Unit
storage diffuser s9 | storage | 170 | 11 |  |  |  | 0 | 0 | Air Coil Unit
storage diffuser s2 | storage | 120 | 8 |  |  |  | 0 | 0 | Air Coil Unit
storage diffuser s1 | storage | 115 | 7 |  |  |  | 0 | 0 | Air Coil Unit
storage diffuser S19 | storage | 0 | 0 |  |  |  | 0 | 0 | Air Coil Unit
storage diffuser S17 | storage | 0 | 0 |  |  |  | 0 | 0 | Air Coil Unit
storage diffuser S16 | storage | 0 | 0 |  |  |  | 0 | 0 | Air Coil Unit
Storage Diffuser S5 | Storage | 0 | 0 |  |  |  | 0 | 0 | Air Coil Unit
storage diffuser s6 | storage | 76 | 5 |  |  |  | 0 | 0 | Air Coil Unit
storage diffuser s4 | storage | 64 | 4 |  |  |  | 0 | 0 | Air Coil Unit
- | STORAGE ROOM IN MAIN OFFICE | 16 | 1 |  |  |  | 0 | 0 | Rooftop Unit
teacher lounge diffuser S19 | teachers lounge | 37 | 2 |  |  | 572 | 13 | 2 | Air Coil Unit | 8 | 4576 | 0.48514 | 1 | 0.48514 | 0 | 0.48514 | 0
- | TOM MCLAUGHLIN OFFICE | 29 | 1 |  |  | 572 | 13 | 1 | Rooftop Unit | 8 | 4576 | 0.38024 | 1 | 0.38024 | 0 | 0.38024 | 0
- | vending machine shop | 0 | 0 |  |  |  | 0 | 0 | H1-1
- | welding shop | 0 | 0 |  |  |  | 0 | 0 | H2-9
Sheet Last Modified: | 2021-04-07
School: | Rhawnhurst Elementary School
Vendor: | Devine | Part 2 | Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 301 | 20 |  |  | 1485 | 33 | 20 | Univent | 8 | 11880 | 1.5202 | 1 | 1.5202 | 1 | 1.5202 | 1
101 | Classroom | 341 | 22 |  |  | 1056 | 24 | 22 | Univent | 8 | 8448 | 2.4219 | 1 | 2.4219 | 1 | 2.4219 | 1
102 | Classroom | 296 | 19 |  |  | 1056 | 24 | 19 | Univent | 8 | 8448 | 2.1023 | 1 | 2.1023 | 1 | 2.1023 | 1
102B | Office |  | 0 | Yes | 20 | 110 | 2 | 2 | Univent | 8 | 880 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom | 297 | 19 |  |  | 1056 | 24 | 19 | Univent | 8 | 8448 | 2.1094 | 1 | 2.1094 | 1 | 2.1094 | 1
104 | Classroom | 335 | 22 |  |  | 1056 | 24 | 22 | Univent | 8 | 8448 | 2.3793 | 1 | 2.3793 | 1 | 2.3793 | 1
105 | Classroom | 307 | 20 |  |  | 1073 | 24 | 20 | Univent | 8 | 8584 | 2.1459 | 1 | 2.1459 | 1 | 2.1459 | 1
106 | Classroom | 624 | 41 |  |  | 1020 | 23 | 23 | Univent | 8 | 8160 | 4.5882 | 1 | 4.5882 | 2 | 4.5882 | 2
107 | Classroom | 321 | 21 |  |  | 1056 | 24 | 21 | Univent | 8 | 8448 | 2.2798 | 1 | 2.2798 | 1 | 2.2798 | 1
108 | Classroom | 313 | 20 |  |  | 1056 | 24 | 20 | Univent | 8 | 8448 | 2.223 | 1 | 2.223 | 1 | 2.223 | 1
109 | Classroom | 302 | 20 |  |  | 1056 | 24 | 20 | Univent | 8 | 8448 | 2.1449 | 1 | 2.1449 | 1 | 2.1449 | 1
110 | Classroom | 301 | 20 |  |  | 1056 | 24 | 20 | Univent | 8 | 8448 | 2.1378 | 1 | 2.1378 | 1 | 2.1378 | 1
200 | Classroom | 520 | 34 |  |  | 1056 | 24 | 24 | Univent | 8 | 8448 | 3.6932 | 1 | 3.6932 | 1 | 3.6932 | 1
201 | Classroom | 259 | 17 |  |  | 1056 | 24 | 17 | Univent | 8 | 8448 | 1.8395 | 1 | 1.8395 | 1 | 1.8395 | 1
202 | Classroom | 306 | 20 |  |  | 1056 | 24 | 20 | Univent | 8 | 8448 | 2.1733 | 1 | 2.1733 | 1 | 2.1733 | 1
203 | Classroom | 586 | 39 |  |  | 1056 | 24 | 24 | Univent | 8 | 8448 | 4.1619 | 1 | 4.1619 | 2 | 4.1619 | 2
203A | Office |  | 0 | Yes | 20 | 275 | 6 | 6 | Univent | 8 | 2200 | 0 | 1 | 0 | 0 | 20 | 3
203B | Office |  | 0 | Yes | 20 | 198 | 4 | 4 | Univent | 8 | 1584 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom | 452 | 30 |  |  | 1056 | 24 | 24 | Univent | 8 | 8448 | 3.2102 | 1 | 3.2102 | 1 | 3.2102 | 1
Annex 301 | Classroom | 246 | 16 |  |  | 792 | 18 | 16 | Univent | 8 | 6336 | 2.3295 | 1 | 2.3295 | 1 | 2.3295 | 1
Annex 302 | Classroom | 291 | 19 |  |  | 792 | 18 | 18 | Univent | 8 | 6336 | 2.7557 | 1 | 2.7557 | 1 | 2.7557 | 1
Annex 303 | Classroom | 303 | 20 |  |  | 792 | 18 | 18 | Univent | 8 | 6336 | 2.8693 | 1 | 2.8693 | 1 | 2.8693 | 1
Annex 304 | Classroom | 198 | 13 | Yes | 20 | 792 | 18 | 18 | Univent | 8 | 6336 | 1.875 | 1 | 1.875 | 1 | 21.875 | 3
Annex 305 | Classroom | 248 | 16 |  |  | 792 | 18 | 16 | Univent | 8 | 6336 | 2.3485 | 1 | 2.3485 | 1 | 2.3485 | 1
Annex 306 | Classroom | 216 | 14 | Yes | 20 | 792 | 18 | 18 | Univent | 8 | 6336 | 2.0455 | 1 | 2.0455 | 1 | 22.0455 | 3
- | Main Office |  | 0 | Yes | 20 | 240 | 5 | 5 | Univent | 8 | 1920 | 0 | 1 | 0 | 0 | 20 | 3
Principal | Office |  | 0 | Yes | 20 | 264 | 6 | 6 | Univent | 8 | 2112 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses Office |  | 0 | Yes | 20 | 460 | 10 | 10 | Univent | 8 | 3680 | 0 | 1 | 0 | 0 | 20 | 3
- | Special Education Office |  | 0 | Yes | 20 | 360 | 8 | 8 | Univent | 8 | 2880 | 0 | 1 | 0 | 0 | 20 | 3
- | Counselor Office |  | 0 | Yes | 20 | 241 | 5 | 5 | Univent | 8 | 1928 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 2049 | 136 |  |  | 3431 | 77 | 77 | Air Handling Unit | 8 | 27448 | 4.479 | 1.062 | 4.7569 | 2 | 4.7569 | 2
- | Cafeteria | 362 | 24 |  |  | 2814 | 63 | 24 | Univent | 8 | 22512 | 0.96482 | 1.062 | 1.0247 | 1 | 1.0247 | 1
- | Gym | 116 | 7 |  |  | 3969 | 90 | 7 | Air Handling Unit | 8 | 31752 | 0.2192 | 1.062 | 0.2328 | 0 | 0.2328 | 0
- | Library | 140 | 9 | Yes | 20 | 1134 | 25 | 25 | Univent | 8 | 9072 | 0.92593 | 1 | 0.92593 | 0 | 20.9259 | 3
- | Trailer | 286 | 19 |  |  | 649 | 14 | 14 | Air Handling Unit | 8 | 5192 | 3.3051 | 1 | 3.3051 | 1 | 3.3051 | 1
A1 | Annex | 75 | 5 |  |  | 792 | 18 | 5 | Univent | 8 | 6336 | 0.71023 | 1 | 0.71023 | 0 | 0.71023 | 0
A2 | Annex | 95 | 6 |  |  | 792 | 18 | 6 | Univent | 8 | 6336 | 0.89962 | 1 | 0.89962 | 0 | 0.89962 | 0
A3 | Annex | 54 | 3 |  |  | 792 | 18 | 3 | Univent | 8 | 6336 | 0.51136 | 1 | 0.51136 | 0 | 0.51136 | 0
A4 | Annex | 62 | 4 |  |  | 792 | 18 | 4 | Univent | 8 | 6336 | 0.58712 | 1 | 0.58712 | 0 | 0.58712 | 0
A5 | Annex | 63 | 4 |  |  | 792 | 18 | 4 | Univent | 8 | 6336 | 0.59659 | 1 | 0.59659 | 0 | 0.59659 | 0
A6 | Annex | 70 | 4 |  |  | 792 | 18 | 4 | Univent | 8 | 6336 | 0.66288 | 1 | 0.66288 | 0 | 0.66288 | 0
Sheet Last Modified: | 2021-04-15
School: | James Rhoads Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 122 | 8 |  |  | 552 | 12 | 8 | Univent | 8 | 4416 | 1.6576 | 1 | 1.6576 | 1 | 1.6576 | 1
102 | Classroom | 87 | 5 | Yes | 20 | 968 | 22 | 22 | Univent | 8 | 7744 | 0.67407 | 1 | 0.67407 | 0 | 20.6741 | 3
104 | Classroom | 136 | 9 | Yes | 20 | 968 | 22 | 22 | Univent | 8 | 7744 | 1.0537 | 1 | 1.0537 | 1 | 21.0537 | 3
200 | Classroom | 0 | 0 |  |  | 805 | 18 | 0 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom | 190 | 12 | Yes | 20 | 805 | 18 | 18 | Univent | 8 | 6440 | 1.7702 | 1 | 1.7702 | 1 | 21.7702 | 3
202 | Classroom | 237 | 15 |  |  | 805 | 18 | 15 | Univent | 8 | 6440 | 2.2081 | 1 | 2.2081 | 1 | 2.2081 | 1
203 | Classroom | 212 | 14 | Yes | 20 | 805 | 18 | 18 | Univent | 8 | 6440 | 1.9752 | 1 | 1.9752 | 1 | 21.9752 | 3
204 | Classroom | 0 | 0 | Yes | 20 | 805 | 18 | 18 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom | 162 | 10 | Yes | 20 | 805 | 18 | 18 | Univent | 8 | 6440 | 1.5093 | 1 | 1.5093 | 1 | 21.5093 | 3
206 | Classroom | 201 | 13 | Yes | 20 | 805 | 18 | 18 | Univent | 8 | 6440 | 1.8727 | 1 | 1.8727 | 1 | 21.8727 | 3
207 | Classroom | 0 | 0 |  |  | 805 | 18 | 0 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
208 | Classroom | 236 | 15 |  |  | 805 | 18 | 15 | Univent | 8 | 6440 | 2.1988 | 1 | 2.1988 | 1 | 2.1988 | 1
209 | Classroom | 174 | 11 | Yes | 20 | 805 | 18 | 18 | Univent | 8 | 6440 | 1.6211 | 1 | 1.6211 | 1 | 21.6211 | 3
210 | Classroom | 212 | 14 |  |  | 805 | 18 | 14 | Univent | 8 | 6440 | 1.9752 | 1 | 1.9752 | 1 | 1.9752 | 1
300 | Classroom | 318 | 21 |  |  | 805 | 18 | 18 | Univent | 8 | 6440 | 2.9627 | 1 | 2.9627 | 1 | 2.9627 | 1
301 | Classroom | 202 | 13 |  |  | 805 | 18 | 13 | Univent | 8 | 6440 | 1.882 | 1 | 1.882 | 1 | 1.882 | 1
302 | Classroom | 197 | 13 |  |  | 805 | 18 | 13 | Univent | 8 | 6440 | 1.8354 | 1 | 1.8354 | 1 | 1.8354 | 1
303 | Classroom | 300 | 20 |  |  | 805 | 18 | 18 | Univent | 8 | 6440 | 2.795 | 1 | 2.795 | 1 | 2.795 | 1
304 | Classroom | 203 | 13 |  |  | 805 | 18 | 13 | Univent | 8 | 6440 | 1.8913 | 1 | 1.8913 | 1 | 1.8913 | 1
305 | Classroom | 205 | 13 |  |  | 805 | 18 | 13 | Univent | 8 | 6440 | 1.9099 | 1 | 1.9099 | 1 | 1.9099 | 1
306 | Classroom | 169 | 11 |  |  | 805 | 18 | 11 | Univent | 8 | 6440 | 1.5745 | 1 | 1.5745 | 1 | 1.5745 | 1
307 | Classroom | 233 | 15 |  |  | 805 | 18 | 15 | Univent | 8 | 6440 | 2.1708 | 1 | 2.1708 | 1 | 2.1708 | 1
308 | Classroom | 201 | 13 |  |  | 805 | 18 | 13 | Univent | 8 | 6440 | 1.8727 | 1 | 1.8727 | 1 | 1.8727 | 1
309 | Classroom | 174 | 11 |  |  | 805 | 18 | 11 | Univent | 8 | 6440 | 1.6211 | 1 | 1.6211 | 1 | 1.6211 | 1
310 | Classroom | 342 | 22 |  |  | 805 | 18 | 18 | Univent | 8 | 6440 | 3.1863 | 1 | 3.1863 | 1 | 3.1863 | 1
400 | Classroom | 0 | 0 |  |  | 805 | 18 | 0 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
401 | Classroom | 0 | 0 |  |  | 805 | 18 | 0 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
402 | Classroom | 0 | 0 |  |  | 805 | 18 | 0 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
403 | Classroom | 0 | 0 |  |  | 805 | 18 | 0 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
404 | Classroom | 0 | 0 | Yes | 20 | 805 | 18 | 18 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
405 | Classroom | 0 | 0 | Yes | 20 | 805 | 18 | 18 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
406 | Classroom | 0 | 0 | Yes | 20 | 805 | 18 | 18 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
407 | Classroom | 0 | 0 | Yes | 20 | 805 | 18 | 18 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
408 | Classroom | 0 | 0 |  |  | 805 | 18 | 0 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
409 | Classroom | 0 | 0 | Yes | 20 | 805 | 18 | 18 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 20 | 3
410 | Classroom | 0 | 0 |  |  | 805 | 18 | 0 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office |  | 0 | Yes | 20 | 616 | 14 | 14 |  | 8 | 4928 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 300 | 6 | 6 |  | 8 | 2400 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office |  | 0 | Yes | 20 | 120 | 2 | 2 |  | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 0 | 0 |  |  | 1800 | 40 | 0 | Air Handling Unit | 8 | 14400 | 0 | 1 | 0 | 0 | 0 | 0
- | Café/Gym | 0 | 0 |  |  | 6480 | 147 | 0 | Air Handling Unit | 8 | 51840 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | IMC | 0 | 0 |  |  | 897 | 20 | 0 | Univent | 8 | 7176 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-08
School: | E. Washington Rhodes Elementary School
Vendor: | Goldner | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | 1ST/2ND FLR A&B POD AREAS | 0 | 0 |  |  | 1829 | 41 | 0 | Air Handling Unit | 8 | 14632 | 0 | 1 | 0 | 0 | 0 | 0
- | 1ST/2ND FLR C&D POD AREAS | 0 | 0 |  |  | 1829 | 41 | 0 | Air Handling Unit | 8 | 14632 | 0 | 1 | 0 | 0 | 0 | 0
A1 | CLASSROOM | 365 | 24 |  |  | 850 | 19 | 19 | Univent | 8 | 6800 | 3.2206 | 1 | 3.2206 | 1 | 3.2206 | 1
A2 | CLASSROOM | 326 | 21 |  |  | 850 | 19 | 19 | Univent | 8 | 6800 | 2.8765 | 1 | 2.8765 | 1 | 2.8765 | 1
A3 | CLASSROOM | 0 | 0 |  |  | 850 | 19 | 0 | Univent | 8 | 6800 | 0 | 1 | 0 | 0 | 0 | 0
A4 | CLASSROOM | 0 | 0 |  |  | 1085 | 24 | 0 | Univent | 8 | 8680 | 0 | 1 | 0 | 0 | 0 | 0
A5 | CLASSROOM | 289 | 19 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 3.0104 | 1 | 3.0104 | 1 | 3.0104 | 1
A6 | CLASSROOM | 308 | 20 |  |  | 890 | 20 | 20 | Univent | 8 | 7120 | 2.5955 | 1 | 2.5955 | 1 | 2.5955 | 1
A7 | CLASSROOM | 0 | 0 |  |  | 0 | 0 | 0 | Univent | 8 | 0 | #DIV/0! | 1 | #DIV/0! | #DIV/0! | #DIV/0!
A101 | CLASSROOM | 283 | 18 |  |  | 850 | 19 | 18 | Univent | 8 | 6800 | 2.4971 | 1 | 2.4971 | 1 | 2.4971 | 1
A102 | CLASSROOM | 369 | 24 |  |  | 850 | 19 | 19 | Univent | 8 | 6800 | 3.2559 | 1 | 3.2559 | 1 | 3.2559 | 1
A103 | CLASSROOM | 279 | 18 |  |  | 816 | 18 | 18 | Univent | 8 | 6528 | 2.5643 | 1 | 2.5643 | 1 | 2.5643 | 1
A104 | CLASSROOM | 238 | 15 |  |  | 1120 | 25 | 15 | Univent | 8 | 8960 | 1.5938 | 1 | 1.5938 | 1 | 1.5938 | 1
A105 | CLASSROOM | 296 | 19 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 2.9839 | 1 | 2.9839 | 1 | 2.9839 | 1
A106 | CLASSROOM | 227 | 15 |  |  | 1100 | 25 | 15 | Univent | 8 | 8800 | 1.5477 | 1 | 1.5477 | 1 | 1.5477 | 1
B1 | CLASSROOM | 275 | 18 |  |  | 850 | 19 | 18 | Univent | 8 | 6800 | 2.4265 | 1 | 2.4265 | 1 | 2.4265 | 1
B2 | CLASSROOM | 308 | 20 |  |  | 850 | 19 | 19 | Univent | 8 | 6800 | 2.7176 | 1 | 2.7176 | 1 | 2.7176 | 1
B3 | CLASSROOM | 338 | 22 |  |  | 850 | 19 | 19 | Univent | 8 | 6800 | 2.9824 | 1 | 2.9824 | 1 | 2.9824 | 1
B4 | CLASSROOM | 300 | 20 |  |  | 1085 | 24 | 20 | Univent | 8 | 8680 | 2.0737 | 1 | 2.0737 | 1 | 2.0737 | 1
B5 | CLASSROOM | 233 | 15 |  |  | 720 | 16 | 15 | Univent | 8 | 5760 | 2.4271 | 1 | 2.4271 | 1 | 2.4271 | 1
B6 | CLASSROOM | 296 | 19 |  |  | 890 | 20 | 19 | Univent | 8 | 7120 | 2.4944 | 1 | 2.4944 | 1 | 2.4944 | 1
B101 | CLASSROOM | 237 | 15 |  |  | 850 | 19 | 15 | Univent | 8 | 6800 | 2.0912 | 1 | 2.0912 | 1 | 2.0912 | 1
B102 | CLASSROOM | 325 | 21 |  |  | 850 | 19 | 19 | Univent | 8 | 6800 | 2.8676 | 1 | 2.8676 | 1 | 2.8676 | 1
B103 | CLASSROOM | 275 | 18 |  |  | 816 | 18 | 18 | Univent | 8 | 6528 | 2.5276 | 1 | 2.5276 | 1 | 2.5276 | 1
B104 | CLASSROOM | 307 | 20 |  |  | 1120 | 25 | 20 | Univent | 8 | 8960 | 2.0558 | 1 | 2.0558 | 1 | 2.0558 | 1
B105 | CLASSROOM | 301 | 20 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 3.0343 | 1 | 3.0343 | 1 | 3.0343 | 1
B106 | CLASSROOM | 297 | 19 |  |  | 1100 | 25 | 19 | Univent | 8 | 8800 | 2.025 | 1 | 2.025 | 1 | 2.025 | 1
C1 | CLASSROOM | 297 | 19 |  |  | 850 | 19 | 19 | Univent | 8 | 6800 | 2.6206 | 1 | 2.6206 | 1 | 2.6206 | 1
C2 | CLASSROOM | 0 | 0 | Yes | 20 | 850 | 19 | 19 | Univent | 8 | 6800 | 0 | 1 | 0 | 0 | 20 | 3
C3 | CLASSROOM | 0 | 0 | Yes | 20 | 850 | 19 | 19 | Univent | 8 | 6800 | 0 | 1 | 0 | 0 | 20 | 3
C4 | CLASSROOM | 367 | 24 |  |  | 1085 | 24 | 24 | Univent | 8 | 8680 | 2.5369 | 1 | 2.5369 | 1 | 2.5369 | 1
C5 | CLASSROOM | 368 | 24 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 3.8333 | 1 | 3.8333 | 1 | 3.8333 | 1
C6 | CLASSROOM | 333 | 22 |  |  | 890 | 20 | 20 | Univent | 8 | 7120 | 2.8062 | 1 | 2.8062 | 1 | 2.8062 | 1
C7 | CLASSROOM | 293 | 19 |  |  | 0 | 0 | 0 | Univent | 8 | 0 | #DIV/0! | 1 | #DIV/0! | #DIV/0! | #DIV/0!
C101 | CLASSROOM | 253 | 16 |  |  | 850 | 19 | 16 | Univent | 8 | 6800 | 2.2324 | 1 | 2.2324 | 1 | 2.2324 | 1
C102 | CLASSROOM | 404 | 26 |  |  | 850 | 19 | 19 | Univent | 8 | 6800 | 3.5647 | 1 | 3.5647 | 1 | 3.5647 | 1
C103 | CLASSROOM | 230 | 15 |  |  | 816 | 18 | 15 | Univent | 8 | 6528 | 2.114 | 1 | 2.114 | 1 | 2.114 | 1
C104 | CLASSROOM | 353 | 23 |  |  | 1120 | 25 | 23 | Univent | 8 | 8960 | 2.3638 | 1 | 2.3638 | 1 | 2.3638 | 1
C105 | CLASSROOM | 290 | 19 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 2.9234 | 1 | 2.9234 | 1 | 2.9234 | 1
C106 | CLASSROOM | 241 | 16 |  |  | 1100 | 25 | 16 | Univent | 8 | 8800 | 1.6432 | 1 | 1.6432 | 1 | 1.6432 | 1
D1 | CLASSROOM | 274 | 18 |  |  | 850 | 19 | 18 | Univent | 8 | 6800 | 2.4176 | 1 | 2.4176 | 1 | 2.4176 | 1
D2 | CLASSROOM | 449 | 29 |  |  | 850 | 19 | 19 | Univent | 8 | 6800 | 3.9618 | 1 | 3.9618 | 1 | 3.9618 | 1
D3 | CLASSROOM | 314 | 20 |  |  | 850 | 19 | 19 | Univent | 8 | 6800 | 2.7706 | 1 | 2.7706 | 1 | 2.7706 | 1
D4 | CLASSROOM | 293 | 19 |  |  | 1085 | 24 | 19 | Univent | 8 | 8680 | 2.0253 | 1 | 2.0253 | 1 | 2.0253 | 1
D5 | CLASSROOM | 273 | 18 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 2.8438 | 1 | 2.8438 | 1 | 2.8438 | 1
D6 | CLASSROOM | 405 | 27 |  |  | 890 | 20 | 20 | Univent | 8 | 7120 | 3.4129 | 1 | 3.4129 | 1 | 3.4129 | 1
D101 | CLASSROOM | 283 | 18 |  |  | 850 | 19 | 18 | Univent | 8 | 6800 | 2.4971 | 1 | 2.4971 | 1 | 2.4971 | 1
D102 | CLASSROOM | 304 | 20 |  |  | 850 | 19 | 19 | Univent | 8 | 6800 | 2.6824 | 1 | 2.6824 | 1 | 2.6824 | 1
D103 | CLASSROOM | 326 | 21 |  |  | 816 | 18 | 18 | Univent | 8 | 6528 | 2.9963 | 1 | 2.9963 | 1 | 2.9963 | 1
D104 | CLASSROOM | 244 | 16 |  |  | 1120 | 25 | 16 | Univent | 8 | 8960 | 1.6339 | 1 | 1.6339 | 1 | 1.6339 | 1
D105 | CLASSROOM | 235 | 15 |  |  | 744 | 16 | 15 | Univent | 8 | 5952 | 2.369 | 1 | 2.369 | 1 | 2.369 | 1
D106 | CLASSROOM | 0 | 0 |  |  | 1100 | 25 | 0 | Univent | 8 | 8800 | 0 | 1 | 0 | 0 | 0 | 0
D200 | MUSIC CLASSROOM 2 | 729 | 48 |  |  | 1600 | 36 | 36 | Univent | 8 | 12800 | 3.4172 | 1 | 3.4172 | 1 | 3.4172 | 1
D205 | MUSIC CLASSROOM 1 | 620 | 41 |  |  | 1600 | 36 | 36 | Univent | 8 | 12800 | 2.9062 | 1 | 2.9062 | 1 | 2.9062 | 1
E12 | SCIENCE CLASSROOM | 0 | 0 |  |  | 1232 | 28 | 0 | Univent | 8 | 9856 | 0 | 1 | 0 | 0 | 0 | 0
E-147 | BREAK ROOM, OFFICE AREA | 0 | 0 |  |  | 120 | 2 | 0 | Univent | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
E-148 | VICE PRINCIPAL OFFICE | 0 | 0 |  |  | 120 | 2 | 0 | Univent | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
E-149 | CONFERENCE AREA | 47 | 3 |  |  | 260 | 5 | 3 | Univent | 8 | 2080 | 1.3558 | 1 | 1.3558 | 1 | 1.3558 | 1
E-150 | PRINCIPAL OFFICE | 36 | 2 |  |  | 225 | 5 | 2 | Univent | 8 | 1800 | 1.2 | 1 | 1.2 | 1 | 1.2 | 1
E204 | EARLY CHILDROOM ED CLASSROOM | 0 | 0 |  |  |  | 0 | 0 | Univent
E205 | CREATIVE WRITING CLASSROOM (LEFT) | 577 | 38 |  |  |  | 0 | 0 | Univent
E207 | COMPUTER LAB | 3 | 0 |  |  | 2070 | 47 | 0 | Univent | 8 | 16560 | 0.01087 | 1 | 0.01087 | 0 | 0.01087 | 0
- | GIRLS GYM | 0 | 0 |  |  | 4897 | 111 | 0 | Air Handling Unit | 8 | 39176 | 0 | 1.062 | 0 | 0 | 0 | 0
- | BOYS GYM | 0 | 0 |  |  | 4897 | 111 | 0 | Air Handling Unit | 8 | 39176 | 0 | 1.062 | 0 | 0 | 0 | 0
- | IMC - LIBRARY | 0 | 0 |  |  | 3985 | 90 | 0 | Air Handling Unit | 8 | 31880 | 0 | 1.062 | 0 | 0 | 0 | 0
- | INDUSTRIAL ART (WOODSHOP) | 0 | 0 |  |  | 1564 | 35 | 0 | Air Handling Unit | 8 | 12512 | 0 | 1 | 0 | 0 | 0 | 0
- | SWIMMING POOL | 0 | 0 |  |  | 10200 | 231 | 0 | Air Handling Unit | 8 | 81600 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | ADMIN + HEALTH OFFICE | 0 | 0 |  |  | 130 | 2 | 0 | Air Handling Unit | 8 | 1040 | 0 | 1 | 0 | 0 | 0 | 0
- | ART STUDIOS | 0 | 0 |  |  | 3860 | 87 | 0 | Air Handling Unit | 8 | 30880 | 0 | 1.062 | 0 | 0 | 0 | 0
- | AUDITORIUM + STAGE | 0 | 0 |  |  | 12450 | 282 | 0 | Air Handling Unit | 8 | 99600 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | CLASSROOM (YMCA 2) | 0 | 0 |  |  | 704 | 16 | 0 | Air Handling Unit | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
- | CLASSROOM (YMCA OST1) | 0 | 0 |  |  | 544 | 12 | 0 | Air Handling Unit | 8 | 4352 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-05
School: | Richmond Elementary School
Vendor: | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
3 | - |  | 0 |  |  | 1000 | 22 | 0 | Radiators/House fan | 8 | 8000 | 0 | 1 | 0 | 0 | 0 | 0
8 | - |  | 0 |  |  | 1200 | 27 | 0 | Radiators/House fan | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom |  | 0 | Yes | 20 | 759 | 17 | 17 | Radiators/House fan | 8 | 6072 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 759 | 17 | 17 | Radiators/House fan | 8 | 6072 | 0 | 1 | 0 | 0 | 20 | 3
102A | Nurse |  | 0 | Yes | 20 | 216 | 4 | 4 | Radiators/House fan | 8 | 1728 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 812 | 18 | 18 | Radiators/House fan | 8 | 6496 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom |  | 0 | Yes | 20 | 812 | 18 | 18 | Radiators/House fan | 8 | 6496 | 0 | 1 | 0 | 0 | 20 | 3
105 | Main Office |  | 0 | Yes | 20 | 416 | 9 | 9 | Radiators/House fan | 8 | 3328 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom |  | 0 | Yes | 20 | 762 | 17 | 17 | Radiators/House fan | 8 | 6096 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 | Yes | 20 | 742 | 16 | 16 | Radiators/House fan | 8 | 5936 | 0 | 1 | 0 | 0 | 20 | 3
108 | Faculty Lounge |  | 0 |  |  | 440 | 10 | 0 | Radiators/House fan | 8 | 3520 | 0 | 1 | 0 | 0 | 0 | 0
109 | Classroom |  | 0 | Yes | 20 | 1180 | 26 | 26 | Radiators/House fan | 8 | 9440 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 759 | 17 | 17 | Radiators/House fan | 8 | 6072 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 759 | 17 | 17 | Radiators/House fan | 8 | 6072 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 960 | 21 | 21 | Radiators/House fan | 8 | 7680 | 0 | 1 | 0 | 0 | 20 | 3
203A | Counselor Office |  | 0 |  |  | 167 | 3 | 0 | Radiators/House fan | 8 | 1336 | 0 | 1 | 0 | 0 | 0 | 0
204 | Classroom |  | 0 | Yes | 20 | 960 | 21 | 21 | Radiators/House fan | 8 | 7680 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 896 | 20 | 20 | Radiators/House fan | 8 | 7168 | 0 | 1 | 0 | 0 | 20 | 3
206 | - |  | 0 |  |  | 896 | 20 | 0 | Radiators/House fan | 8 | 7168 | 0 | 1 | 0 | 0 | 0 | 0
207 | - |  | 0 | Yes | 20 | 792 | 18 | 18 | Radiators/House fan | 8 | 6336 | 0 | 1 | 0 | 0 | 20 | 3
208 | - |  | 0 |  |  | 792 | 18 | 0 | Radiators/House fan | 8 | 6336 | 0 | 1 | 0 | 0 | 0 | 0
209 | - |  | 0 | Yes | 20 | 841 | 19 | 19 | Radiators/House fan | 8 | 6728 | 0 | 1 | 0 | 0 | 20 | 3
210 | - |  | 0 |  |  | 202 | 4 | 0 | Radiators/House fan | 8 | 1616 | 0 | 1 | 0 | 0 | 0 | 0
301 | - |  | 0 |  |  | 792 | 18 | 0 | Radiators/House fan | 8 | 6336 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom |  | 0 |  |  | 792 | 18 | 0 | Radiators/House fan | 8 | 6336 | 0 | 1 | 0 | 0 | 0 | 0
303 | - |  | 0 |  |  | 840 | 19 | 0 | Radiators/House fan | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
303A | - |  | 0 |  |  | 390 | 8 | 0 | Radiators/House fan | 8 | 3120 | 0 | 1 | 0 | 0 | 0 | 0
304 | - |  | 0 |  |  | 900 | 20 | 0 | Radiators/House fan | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
305 | - |  | 0 |  |  | 840 | 19 | 0 | Radiators/House fan | 8 | 6720 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom |  | 0 |  |  | 870 | 19 | 0 | Radiators/House fan | 8 | 6960 | 0 | 1 | 0 | 0 | 0 | 0
307 | - |  | 0 |  |  | 850 | 19 | 0 | Radiators/House fan | 8 | 6800 | 0 | 1 | 0 | 0 | 0 | 0
308 | - |  | 0 |  |  | 850 | 19 | 0 | Radiators/House fan | 8 | 6800 | 0 | 1 | 0 | 0 | 0 | 0
309 | - |  | 0 |  |  | 900 | 20 | 0 | Radiators/House fan | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
310 | - |  | 0 |  |  | 202 | 4 | 0 | Radiators/House fan | 8 | 1616 | 0 | 1 | 0 | 0 | 0 | 0
- | Principal's Office |  | 0 |  |  | 448 | 10 | 0 | Radiators/House fan | 8 | 3584 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym |  | 0 |  |  | 2760 | 62 | 0 | Heating Ventalation Unit | 8 | 22080 | 0 | 1.062 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-01
School: | Rivera (Bright Futures) Early Childhood Center
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Basement | Cafeteria | 1016 | 67 |  |  | 4000 | 90 | 67 | Air Handling Unit | 8 | 32000 | 1.905 | 1.062 | 2.0232 | 1 | 2.0232 | 1
Basement | VVT's in the small Building | 138 | 9 |  |  | 247 | 5 | 5 | Air Handling Unit | 8 | 1976 | 4.1903 | 1 | 4.1903 | 2 | 4.1903 | 2
2nd floor | Common area vvt's(tall Building) | 131 | 8 |  |  | 247 | 5 | 5 | Air Handling Unit | 8 | 1976 | 3.9777 | 1 | 3.9777 | 1 | 3.9777 | 1
4th for upper building | Zoned AH for 5 zone floor | 0 | 0 |  |  | 247 | 5 | 0 | Air Handling Unit | 8 | 1976 | 0 | 1 | 0 | 0 | 0 | 0
5th floor upper building | Zoned AH for 6 zone floor | 1 | 0 |  |  | 247 | 5 | 0 | Air Handling Unit | 8 | 1976 | 0.030364 | 1 | 0.030364 | 0 | 0.030364 | 0
- | Zone1( group learning room) | 0 | 0 |  |  | 135 | 3 | 0 | Air Handling Unit | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
- | Zone2 | 0 | 0 |  |  | 135 | 3 | 0 | Air Handling Unit | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
- | Zone3 | 0 | 0 |  |  | 135 | 3 | 0 | Air Handling Unit | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
- | Zone4 | 0 | 0 |  |  | 135 | 3 | 0 | Air Handling Unit | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
- | Zone5 | 0 | 0 |  |  | 135 | 3 | 0 | Air Handling Unit | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
- | Zone6 | 0 | 0 |  |  | 135 | 3 | 0 | Air Handling Unit | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
Zone1 | Group learning open area 1 | 804 | 53 |  |  | 280 | 6 | 6 | Air Handling Unit | 8 | 2240 | 21.5357 | 1 | 21.5357 | 3 | 21.5357 | 3
Zone 1 | Group learning open area 2 | 0 | 0 |  |  | 270 | 6 | 0 | Air Handling Unit | 8 | 2160 | 0 | 1 | 0 | 0 | 0 | 0
Zone 1 | Group learning office | 0 | 0 |  |  | 276 | 6 | 0 | Air Handling Unit | 8 | 2208 | 0 | 1 | 0 | 0 | 0 | 0
Zone 1 | Large storage | 0 | 0 |  |  | 112 | 2 | 0 | Air Handling Unit | 8 | 896 | 0 | 1 | 0 | 0 | 0 | 0
Zone 1 | Small storage | 21 | 1 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 1.9688 | 1 | 1.9688 | 1 | 1.9688 | 1
Zone 2 | Office 1 | 85 | 5 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 7.9688 | 1 | 7.9688 | 2 | 7.9688 | 2
Zone 2 | Office 2 | 72 | 4 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 6.75 | 1 | 6.75 | 2 | 6.75 | 2
Zone 2 | Office 3 | 37 | 2 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 3.4688 | 1 | 3.4688 | 1 | 3.4688 | 1
Zone 2 | Spare room | 83 | 5 |  |  | 85 | 1 | 1 | Air Handling Unit | 8 | 680 | 7.3235 | 1 | 7.3235 | 2 | 7.3235 | 2
Zone 2 | Hallway | 0 | 0 |  |  | 110 | 2 | 0 | Air Handling Unit | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
Zone 2 | Copy room | 38 | 2 |  |  | 84 | 1 | 1 | Air Handling Unit | 8 | 672 | 3.3929 | 1 | 3.3929 | 1 | 3.3929 | 1
Zone 3 | Conference room vent 1 | 314 | 20 |  |  | 1344 | 30 | 20 | Air Handling Unit | 8 | 10752 | 1.7522 | 1 | 1.7522 | 1 | 1.7522 | 1
Zone 3 | Conference room vent 2 | 0 | 0 |  |  | 1344 | 30 | 0 | Air Handling Unit | 8 | 10752 | 0 | 1 | 0 | 0 | 0 | 0
Zone 3 | Conference room vent 3 | 0 | 0 |  |  | 1344 | 30 | 0 | Air Handling Unit | 8 | 10752 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Admin open area 1 | 307 | 20 |  |  | 182 | 4 | 4 | Air Handling Unit | 8 | 1456 | 12.6511 | 1 | 12.6511 | 3 | 12.6511 | 3
Zone 4 | Admin open area 2 | 0 | 0 |  |  | 182 | 4 | 0 | Air Handling Unit | 8 | 1456 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | copy room | 57 | 3 |  |  | 84 | 1 | 1 | Air Handling Unit | 8 | 672 | 5.0893 | 1 | 5.0893 | 2 | 5.0893 | 2
Zone 4 | elevator hallway | 0 | 0 |  |  | 144 | 3 | 0 | Air Handling Unit | 8 | 1152 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | admin waiting area | 0 | 0 |  |  | 380 | 8 | 0 | Air Handling Unit | 8 | 3040 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Vacant office 1 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Vacant office 2 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Supply Room | 0 | 0 |  |  | 110 | 2 | 0 | Air Handling Unit | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
Zone 5 | Office 1 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 5 | Office 2 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 5 | Zone 5 meeting Room 1 | 42 | 2 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 3.9375 | 1 | 3.9375 | 1 | 3.9375 | 1
Zone 5 | Zone 5 meeting Room 2 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 6 | Storage | 110 | 7 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 10.3125 | 1 | 10.3125 | 3 | 10.3125 | 3
Zone 6 | Office 1 | 272 | 18 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 25.5 | 1 | 25.5 | 4 | 25.5 | 4
Zone 6 | Office 2 | 121 | 8 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 11.3438 | 1 | 11.3438 | 3 | 11.3438 | 3
Zone 6 | Office 3 | 115 | 7 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 10.7812 | 1 | 10.7812 | 3 | 10.7812 | 3
Zone 6 | Office 4 | 198 | 13 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 18.5625 | 1 | 18.5625 | 3 | 18.5625 | 3
Zone 6 | Office 5 | 147 | 9 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 13.7812 | 1 | 13.7812 | 3 | 13.7812 | 3
- | Zone 1 | 0 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Zone 2 | 0 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Zone 3 | 0 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Zone 4 | 0 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Zone 5 | 0 | 0 |  |  |  | 0 | 0 | Air Handling Unit
Zone 1 | Group learning area. Diffuser 1 | 91 | 6 |  |  |  | 0 | 0 | Air Handling Unit
Zone 1 | Group learning area. Diffuser 2 | 0 | 0 |  |  |  | 0 | 0 | Air Handling Unit
Zone 1 | Group learning area. Diffuser 3 | 0 | 0 |  |  |  | 0 | 0 | Air Handling Unit
Zone 1 | Group learning area. Diffuser 4 | 0 | 0 |  |  |  | 0 | 0 | Air Handling Unit
Zone 1 | Group learning area. Diffuser 5 | 0 | 0 |  |  |  | 0 | 0 | Air Handling Unit
Zone 1 | Office 1 | 18 | 1 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 1.6875 | 1 | 1.6875 | 1 | 1.6875 | 1
Zone 1 | Office 2 | 19 | 1 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 1.7812 | 1 | 1.7812 | 1 | 1.7812 | 1
Zone 1 | Office 3 | 12 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 1.125 | 1 | 1.125 | 1 | 1.125 | 1
Zone 2 | Elevator lobby | 0 | 0 |  |  | 144 | 3 | 0 | Air Handling Unit | 8 | 1152 | 0 | 1 | 0 | 0 | 0 | 0
Zone 2 | Reception diffuser 1 | 34 | 2 |  |  |  | 0 | 0 | Air Handling Unit
Zone 2 | Reception diffuser 2 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 2 | Office 1 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 2 | Office 2 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 3 | Office 1 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 3 | Office 2 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 3 | Office 3 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 3 | Kitchen 1 | 0 | 0 |  |  | 214 | 4 | 0 | Air Handling Unit | 8 | 1712 | 0 | 1 | 0 | 0 | 0 | 0
Zone 3 | Kitchen 2 | 0 | 0 |  |  | 214 | 4 | 0 | Air Handling Unit | 8 | 1712 | 0 | 1 | 0 | 0 | 0 | 0
Zone 3 | Hallway 1 | 0 | 0 |  |  | 276 | 6 | 0 | Air Handling Unit | 8 | 2208 | 0 | 1 | 0 | 0 | 0 | 0
Zone 3 | Hallway 2 | 0 | 0 |  |  | 168 | 3 | 0 | Air Handling Unit | 8 | 1344 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Office 411 | 0 | 0 |  |  | 75 | 1 | 0 | Air Handling Unit | 8 | 600 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Office 2 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Office 3 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Storage 415 | 0 | 0 |  |  | 39 | 0 | 0 | Air Handling Unit | 8 | 312 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Hallway | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Assistant Superintendent | 0 | 0 |  |  | 460 | 10 | 0 | Air Handling Unit | 8 | 3680 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Assistant Superintendent | 0 | 0 |  |  | 460 | 10 | 0 | Air Handling Unit | 8 | 3680 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Assistant Superintendent | 0 | 0 |  |  | 460 | 10 | 0 | Air Handling Unit | 8 | 3680 | 0 | 1 | 0 | 0 | 0 | 0
Zone 4 | Storage 408 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 5 | Office 403 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 5 | Office 403 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 5 | Office 404 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 5 | Office | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 5 | Office | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 5 | Conference room 406 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 5 | Conference room 406 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Zone 5 | Office 407 | 0 | 0 |  |  | 142 | 3 | 0 | Air Handling Unit | 8 | 1136 | 0 | 1 | 0 | 0 | 0 | 0
Zone 5 | Office 409 | 0 | 0 |  |  | 80 | 1 | 0 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
3rd floor. VVT#11 | Commons area total | 50 | 3 |  |  | 247 | 5 | 3 | Air Handling Unit | 8 | 1976 | 1.5182 | 1 | 1.5182 | 1 | 1.5182 | 1
- | Elevator hall | 9 | 0 |  |  | 400 | 9 | 0 | Air Handling Unit | 8 | 3200 | 0.16875 | 1 | 0.16875 | 0 | 0.16875 | 0
- | Elevator hall | 0 | 0 |  |  | 602 | 13 | 0 | Air Handling Unit | 8 | 4816 | 0 | 1 | 0 | 0 | 0 | 0
- | Commons Area Diffuser | 11 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Diffuser | 11 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Diffuser | 11 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Diffuser | 12 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Office | 2 | 0 |  |  |  | 0 | 0 | Air Handling Unit
2nd floor. VVT#8 | Commons Are Total | 58 | 3 |  |  | 247 | 5 | 3 | Air Handling Unit | 8 | 1976 | 1.7611 | 1 | 1.7611 | 1 | 1.7611 | 1
- | Elevator hall | 2 | 0 |  |  | 400 | 9 | 0 | Air Handling Unit | 8 | 3200 | 0.0375 | 1 | 0.0375 | 0 | 0.0375 | 0
- | Commons Area Diffuser | 14 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Diffuser | 14 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Diffuser | 12 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Commons Area Diffuser | 8 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Commons area office | 3 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Class bathroom | 3 | 0 |  |  | 75 | 1 | 0 | Air Handling Unit | 8 | 600 | 0.3 | 1 | 0.3 | 0 | 0.3 | 0
- | Staff Bathroom | 2 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Elevator hall | 2 | 0 |  |  |  | 0 | 0 | Air Handling Unit
1st floor VVT#4 | 1st floor Commons Area Total | 46 | 3 |  |  | 247 | 5 | 3 | Air Handling Unit | 8 | 1976 | 1.3968 | 1 | 1.3968 | 1 | 1.3968 | 1
- | elevator hall | 14 | 0 |  |  | 480 | 10 | 0 | Air Handling Unit | 8 | 3840 | 0.21875 | 1 | 0.21875 | 0 | 0.21875 | 0
- | elevator hall | 7 | 0 |  |  | 700 | 15 | 0 | Air Handling Unit | 8 | 5600 | 0.075 | 1 | 0.075 | 0 | 0.075 | 0
- | Commons area diffuser | 7 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Commons area diffuser | 8 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Commons area diffuser | 2 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Commons area diffuser | 4 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Commons area office | 3 | 0 |  |  | 126 | 2 | 0 | Air Handling Unit | 8 | 1008 | 0.17857 | 1 | 0.17857 | 0 | 0.17857 | 0
- | Class bathroom | 0 | 0 |  |  | 75 | 1 | 0 | Air Handling Unit | 8 | 600 | 0 | 1 | 0 | 0 | 0 | 0
- | Staff bathroom | 2 | 0 |  |  | 48 | 1 | 0 | Air Handling Unit | 8 | 384 | 0.3125 | 1 | 0.3125 | 0 | 0.3125 | 0
Room110 | Classroom | 400 | 26 |  |  | 900 | 20 | 20 | Univent | 8 | 7200 | 3.3333 | 1 | 3.3333 | 1 | 3.3333 | 1
Room 111 | Classroom | 335 | 22 |  |  | 900 | 20 | 20 | Univent | 8 | 7200 | 2.7917 | 1 | 2.7917 | 1 | 2.7917 | 1
Room 112 | Classroom | 410 | 27 |  |  | 900 | 20 | 20 | Univent | 8 | 7200 | 3.4167 | 1 | 3.4167 | 1 | 3.4167 | 1
Room 113 | Classroom | 375 | 25 |  |  | 900 | 20 | 20 | Univent | 8 | 7200 | 3.125 | 1 | 3.125 | 1 | 3.125 | 1
205A | Office space | 290 | 19 |  |  | 480 | 10 | 10 | Univent | 8 | 3840 | 4.5312 | 1 | 4.5312 | 2 | 4.5312 | 2
205B | Office space | 484 | 32 |  |  | 613 | 13 | 13 | Univent | 8 | 4904 | 5.9217 | 1 | 5.9217 | 2 | 5.9217 | 2
Room 212 | Classroom | 259 | 17 |  |  | 900 | 20 | 17 | Univent | 8 | 7200 | 2.1583 | 1 | 2.1583 | 1 | 2.1583 | 1
Room 213 | Classroom | 502 | 33 |  |  | 900 | 20 | 20 | Univent | 8 | 7200 | 4.1833 | 1 | 4.1833 | 2 | 4.1833 | 2
Room 214 | Classroom | 277 | 18 |  |  | 900 | 20 | 18 | Univent | 8 | 7200 | 2.3083 | 1 | 2.3083 | 1 | 2.3083 | 1
Room 215 | Classroom | 544 | 36 |  |  | 900 | 20 | 20 | Univent | 8 | 7200 | 4.5333 | 1 | 4.5333 | 2 | 4.5333 | 2
Room303 | Office space | 482 | 32 |  |  | 1414 | 32 | 32 | Univent | 8 | 11312 | 2.5566 | 1 | 2.5566 | 1 | 2.5566 | 1
Room 303B | Office space | 256 | 17 |  |  | 360 | 8 | 8 | Univent | 8 | 2880 | 5.3333 | 1 | 5.3333 | 2 | 5.3333 | 2
Room 309 | Classroom | 517 | 34 |  |  | 1110 | 25 | 25 | Univent | 8 | 8880 | 3.4932 | 1 | 3.4932 | 1 | 3.4932 | 1
Room 310 | Classroom | 290 | 19 |  |  | 900 | 20 | 19 | Univent | 8 | 7200 | 2.4167 | 1 | 2.4167 | 1 | 2.4167 | 1
Room 311 | Classroom | 326 | 21 |  |  | 900 | 20 | 20 | Univent | 8 | 7200 | 2.7167 | 1 | 2.7167 | 1 | 2.7167 | 1
Room 312 | Classroom | 394 | 26 |  |  | 900 | 20 | 20 | Univent | 8 | 7200 | 3.2833 | 1 | 3.2833 | 1 | 3.2833 | 1
VVT 9 | Total | 10 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Office | 3 | 0 |  |  | 144 | 3 | 0 | Air Handling Unit | 8 | 1152 | 0.15625 | 1 | 0.15625 | 0 | 0.15625 | 0
- | Office | 4 | 0 |  |  | 144 | 3 | 0 | Air Handling Unit | 8 | 1152 | 0.20833 | 1 | 0.20833 | 0 | 0.20833 | 0
- | Hallway | 4 | 0 |  |  | 688 | 15 | 0 | Air Handling Unit | 8 | 5504 | 0.043605 | 1 | 0.043605 | 0 | 0.043605 | 0
VVT 10 | Total | 43 | 2 |  |  | 688 | 15 | 2 | Air Handling Unit | 8 | 5504 | 0.46875 | 1 | 0.46875 | 0 | 0.46875 | 0
- | Teachers Lounge | 16 | 1 |  |  | 390 | 8 | 1 | Air Handling Unit | 8 | 3120 | 0.30769 | 1 | 0.30769 | 0 | 0.30769 | 0
- | Bathroom | 4 | 0 |  |  | 48 | 1 | 0 | Air Handling Unit | 8 | 384 | 0.625 | 1 | 0.625 | 0 | 0.625 | 0
- | Women's Room | 8 | 0 |  |  | 112 | 2 | 0 | Air Handling Unit | 8 | 896 | 0.53571 | 1 | 0.53571 | 0 | 0.53571 | 0
- | Men's Room | 3 | 0 |  |  | 112 | 2 | 0 | Air Handling Unit | 8 | 896 | 0.20089 | 1 | 0.20089 | 0 | 0.20089 | 0
- | Hallway | 11 | 0 |  |  | 688 | 15 | 0 | Air Handling Unit | 8 | 5504 | 0.11991 | 1 | 0.11991 | 0 | 0.11991 | 0
VVT 6 | Total | 18 | 1 |  |  |  | 0 | 0 | Air Handling Unit
- | office | 6 | 0 |  |  | 100 | 2 | 0 | Air Handling Unit | 8 | 800 | 0.45 | 1 | 0.45 | 0 | 0.45 | 0
- | Office | 5 | 0 |  |  | 100 | 2 | 0 | Air Handling Unit | 8 | 800 | 0.375 | 1 | 0.375 | 0 | 0.375 | 0
- | Office | 5 | 0 |  |  | 100 | 2 | 0 | Air Handling Unit | 8 | 800 | 0.375 | 1 | 0.375 | 0 | 0.375 | 0
- | Hallway | 2 | 0 |  |  | 688 | 15 | 0 | Air Handling Unit | 8 | 5504 | 0.021802 | 1 | 0.021802 | 0 | 0.021802 | 0
VVT 7 | Total | 32 | 2 |  |  |  | 0 | 0 | Air Handling Unit
- | Men's room | 7 | 0 |  |  | 112 | 2 | 0 | Air Handling Unit | 8 | 896 | 0.46875 | 1 | 0.46875 | 0 | 0.46875 | 0
- | Women's room | 11 | 0 |  |  | 112 | 2 | 0 | Air Handling Unit | 8 | 896 | 0.73661 | 1 | 0.73661 | 0 | 0.73661 | 0
- | Staff bathroom | 4 | 0 |  |  | 52 | 1 | 0 | Air Handling Unit | 8 | 416 | 0.57692 | 1 | 0.57692 | 0 | 0.57692 | 0
- | Hallway | 4 | 0 |  |  | 688 | 15 | 0 | Air Handling Unit | 8 | 5504 | 0.043605 | 1 | 0.043605 | 0 | 0.043605 | 0
- | Hallway | 4 | 0 |  |  | 688 | 15 | 0 | Air Handling Unit | 8 | 5504 | 0.043605 | 1 | 0.043605 | 0 | 0.043605 | 0
VVT1 | Total | 29 | 1 |  |  |  | 0 | 0 | Air Handling Unit
- | kitchen | 6 | 0 |  |  | 288 | 6 | 0 | Air Handling Unit | 8 | 2304 | 0.15625 | 1 | 0.15625 | 0 | 0.15625 | 0
- | Storage | 4 | 0 |  |  | 450 | 10 | 0 | Air Handling Unit | 8 | 3600 | 0.066667 | 1 | 0.066667 | 0 | 0.066667 | 0
- | Men's room | 4 | 0 |  |  | 77 | 1 | 0 | Air Handling Unit | 8 | 616 | 0.38961 | 1 | 0.38961 | 0 | 0.38961 | 0
- | Women's room | 6 | 0 |  |  | 77 | 1 | 0 | Air Handling Unit | 8 | 616 | 0.58442 | 1 | 0.58442 | 0 | 0.58442 | 0
- | Unisex bathroom | 3 | 0 |  |  | 77 | 1 | 0 | Air Handling Unit | 8 | 616 | 0.29221 | 1 | 0.29221 | 0 | 0.29221 | 0
VVT 3 | Total | 0 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | storage | 0 | 0 |  |  | 328 | 7 | 0 | Air Handling Unit | 8 | 2624 | 0 | 1 | 0 | 0 | 0 | 0
- | storage | 0 | 0 |  |  | 450 | 10 | 0 | Air Handling Unit | 8 | 3600 | 0 | 1 | 0 | 0 | 0 | 0
- | storage | 0 | 0 |  |  | 250 | 5 | 0 | Air Handling Unit | 8 | 2000 | 0 | 1 | 0 | 0 | 0 | 0
- | storage | 0 | 0 |  |  | 175 | 3 | 0 | Air Handling Unit | 8 | 1400 | 0 | 1 | 0 | 0 | 0 | 0
VVT 5 | Total | 41 | 2 |  |  |  | 0 | 0 | Air Handling Unit
- | hallway | 7 | 0 |  |  | 425 | 9 | 0 | Air Handling Unit | 8 | 3400 | 0.12353 | 1 | 0.12353 | 0 | 0.12353 | 0
- | Lobby | 11 | 0 |  |  | 375 | 8 | 0 | Air Handling Unit | 8 | 3000 | 0.22 | 1 | 0.22 | 0 | 0.22 | 0
- | Guard office | 8 | 0 |  |  | 120 | 2 | 0 | Air Handling Unit | 8 | 960 | 0.5 | 1 | 0.5 | 0 | 0.5 | 0
- | Staff lockers | 4 | 0 |  |  | 450 | 10 | 0 | Air Handling Unit | 8 | 3600 | 0.066667 | 1 | 0.066667 | 0 | 0.066667 | 0
- | Hallway | 4 | 0 |  |  | 800 | 18 | 0 | Air Handling Unit | 8 | 6400 | 0.0375 | 1 | 0.0375 | 0 | 0.0375 | 0
- | Hallway | 8 | 0 |  |  | 168 | 3 | 0 | Air Handling Unit | 8 | 1344 | 0.35714 | 1 | 0.35714 | 0 | 0.35714 | 0
Sheet Last Modified: | 2021-03-18
School: | Paul Robeson High School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B-2 | Classroom | 0 | 0 |  |  | 1073 | 24 | 0 | Fan Coil Unit | 8 | 8584 | 0 | 1 | 0 | 0 | 0 | 0
100 | Classroom | 380 | 25 |  |  | 940 | 21 | 21 | Univent | 8 | 7520 | 3.0319 | 1 | 3.0319 | 1 | 3.0319 | 1
106 | Classroom | 470 | 31 |  |  | 840 | 19 | 19 | Univent | 8 | 6720 | 4.1964 | 1 | 4.1964 | 2 | 4.1964 | 2
108 | Classroom | 11 | 0 |  |  | 828 | 18 | 0 | Univent | 8 | 6624 | 0.099638 | 1 | 0.099638 | 0 | 0.099638 | 0
200 | Classroom | 89 | 5 |  |  | 696 | 15 | 5 | Univent | 8 | 5568 | 0.95905 | 1 | 0.95905 | 0 | 0.95905 | 0
202 | Classroom | 231 | 15 |  |  | 696 | 15 | 15 | Univent | 8 | 5568 | 2.4892 | 1 | 2.4892 | 1 | 2.4892 | 1
204 | Classroom | 301 | 20 |  |  | 696 | 15 | 15 | Univent | 8 | 5568 | 3.2435 | 1 | 3.2435 | 1 | 3.2435 | 1
205 | Classroom | 304 | 20 |  |  | 672 | 15 | 15 | Univent | 8 | 5376 | 3.3929 | 1 | 3.3929 | 1 | 3.3929 | 1
206 | Classroom | 200 | 13 |  |  | 696 | 15 | 13 | Univent | 8 | 5568 | 2.1552 | 1 | 2.1552 | 1 | 2.1552 | 1
207 | Classroom | 191 | 12 |  |  | 696 | 15 | 12 | Univent | 8 | 5568 | 2.0582 | 1 | 2.0582 | 1 | 2.0582 | 1
208 | Classroom | 125 | 8 |  |  | 696 | 15 | 8 | Univent | 8 | 5568 | 1.347 | 1 | 1.347 | 1 | 1.347 | 1
209 | Classroom | 178 | 11 |  |  | 384 | 8 | 8 | Univent | 8 | 3072 | 3.4766 | 1 | 3.4766 | 1 | 3.4766 | 1
210 | Classroom | 200 | 13 |  |  | 690 | 15 | 13 | Univent | 8 | 5520 | 2.1739 | 1 | 2.1739 | 1 | 2.1739 | 1
211 | Classroom | 262 | 17 |  |  | 851 | 19 | 17 | Univent | 8 | 6808 | 2.309 | 1 | 2.309 | 1 | 2.309 | 1
212 | Classroom | 280 | 18 |  |  | 875 | 19 | 18 | Univent | 8 | 7000 | 2.4 | 1 | 2.4 | 1 | 2.4 | 1
213 | Classroom | 0 | 0 |  |  | 875 | 19 | 0 | Univent | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
- | AUDITORIUM | 0 | 0 |  |  | 2793 | 63 | 0 | Air Handling Unit | 8 | 22344 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria | 862 | 57 |  |  | 2343 | 53 | 53 | Univent | 8 | 18744 | 2.7593 | 1 | 2.7593 | 1 | 2.7593 | 1
- | GYM | 812 | 54 |  |  | 3478 | 79 | 54 | Air Handling Unit | 8 | 27824 | 1.751 | 1.062 | 1.8596 | 1 | 1.8596 | 1
- | MAIN OFFICE | 0 | 0 |  |  | 552 | 12 | 0 | Univent | 8 | 4416 | 0 | 1 | 0 | 0 | 0 | 0
- | Student Lounge | 64 | 4 |  |  | 552 | 12 | 4 | Univent | 8 | 4416 | 0.86957 | 1 | 0.86957 | 0 | 0.86957 | 0
Sheet Last Modified: | 2021-05-03
School: | Roosevelt Elementary School
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 | Yes | 20 | 1035 | 23 | 23 | House Fan | 8 | 8280 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 1012 | 23 | 23 | House Fan | 8 | 8096 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 650 | 14 | 14 | House Fan | 8 | 5200 | 0 | 1 | 0 | 0 | 20 | 3
104 | Main Office |  | 0 | Yes | 20 | 1225 | 27 | 27 | House Fan | 8 | 9800 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 | House Fan | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
106 & 106a | Classroom |  | 0 | Yes | 20 | 1298 | 29 | 29 | House Fan | 8 | 10384 | 0 | 1 | 0 | 0 | 20 | 3
107 | Parent Liason |  | 0 | Yes | 20 | 550 | 12 | 12 | House Fan | 8 | 4400 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom |  | 0 | Yes | 20 | 814 | 18 | 18 | House Fan | 8 | 6512 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom |  | 0 | Yes | 20 | 1104 | 25 | 25 | House Fan | 8 | 8832 | 0 | 1 | 0 | 0 | 20 | 3
110 | Classroom |  | 0 | Yes | 20 | 960 | 21 | 21 | House Fan | 8 | 7680 | 0 | 1 | 0 | 0 | 20 | 3
- | Lunchroom A |  | 0 | Yes | 20 | 2881 | 65 | 65 | House Fan | 8 | 23048 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Lunchroom B |  | 0 | Yes | 20 | 2898 | 65 | 65 | House Fan | 8 | 23184 | 0 | 1.062 | 0 | 0 | 20 | 3
200A | Counselor |  | 0 | Yes | 20 | 342 | 7 | 7 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 20 | 3
200B | Counselor |  | 0 |  |  | 342 | 7 | 0 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 0 | 0
200C | Counselor |  | 0 | Yes | 20 | 342 | 7 | 7 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 638 | 14 | 14 | House Fan | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 748 | 17 | 17 | House Fan | 8 | 5984 | 0 | 1 | 0 | 0 | 20 | 3
205 | IMC |  | 0 | Yes | 20 | 1320 | 30 | 30 | House Fan | 8 | 10560 | 0 | 1 | 0 | 0 | 20 | 3
206A | Counselor |  | 0 | Yes | 20 | 140 | 3 | 3 | House Fan | 8 | 1120 | 0 | 1 | 0 | 0 | 20 | 3
206B | Counselor |  | 0 | Yes | 20 | 116 | 2 | 2 | House Fan | 8 | 928 | 0 | 1 | 0 | 0 | 20 | 3
206C | Counselor |  | 0 | Yes | 20 | 115 | 2 | 2 | House Fan | 8 | 920 | 0 | 1 | 0 | 0 | 20 | 3
206D | Counselor |  | 0 | Yes | 20 | 142 | 3 | 3 | House Fan | 8 | 1136 | 0 | 1 | 0 | 0 | 20 | 3
206E | Counselor |  | 0 | Yes | 20 | 126 | 2 | 2 | House Fan | 8 | 1008 | 0 | 1 | 0 | 0 | 20 | 3
207A | Room |  | 0 | Yes | 20 | 108 | 2 | 2 | House Fan | 8 | 864 | 0 | 1 | 0 | 0 | 20 | 3
207B | Room |  | 0 |  |  | 145 | 3 | 0 | House Fan | 8 | 1160 | 0 | 1 | 0 | 0 | 0 | 0
207C | Room |  | 0 | Yes | 20 | 108 | 2 | 2 | House Fan | 8 | 864 | 0 | 1 | 0 | 0 | 20 | 3
207D | Room |  | 0 |  |  | 103 | 2 | 0 | House Fan | 8 | 824 | 0 | 1 | 0 | 0 | 0 | 0
207E | Room |  | 0 | Yes | 20 | 132 | 3 | 3 | House Fan | 8 | 1056 | 0 | 1 | 0 | 0 | 20 | 3
208 | Art Room |  | 0 | Yes | 20 | 1152 | 26 | 26 | House Fan | 8 | 9216 | 0 | 1 | 0 | 0 | 20 | 3
209 | Faculty Lounge |  | 0 | Yes | 20 | 696 | 15 | 15 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 629 | 14 | 14 | House Fan | 8 | 5032 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Suite |  | 0 | Yes | 20 | 552 | 12 | 12 | House Fan | 8 | 4416 | 0 | 1 | 0 | 0 | 20 | 3
210 | Science Lab |  | 0 | Yes | 20 | 700 | 15 | 15 | House Fan | 8 | 5600 | 0 | 1 | 0 | 0 | 20 | 3
211 | Music |  | 0 | Yes | 20 | 858 | 19 | 19 | House Fan | 8 | 6864 | 0 | 1 | 0 | 0 | 20 | 3
212 | Classroom |  | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
213 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
214 | Classroom |  | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
215 | Classroom |  | 0 | Yes | 20 | 572 | 13 | 13 | House Fan | 8 | 4576 | 0 | 1 | 0 | 0 | 20 | 3
216 | Classroom |  | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
217 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
218 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
219 | Classroom |  | 0 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
220 | Classroom |  | 0 |  |  | 704 | 16 | 0 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
221A | Classroom |  | 0 | Yes | 20 | 342 | 7 | 7 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 20 | 3
221B | Classroom |  | 0 |  |  | 342 | 7 | 0 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 0 | 0
221C | Classroom |  | 0 |  |  | 342 | 7 | 0 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 0 | 0
222 | Classroom |  | 0 |  |  | 336 | 7 | 0 | House Fan | 8 | 2688 | 0 | 1 | 0 | 0 | 0 | 0
300A | Counselor // Storage |  | 0 |  |  | 342 | 7 | 0 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 0 | 0
300B | Counselor // Storage |  | 0 |  |  | 342 | 7 | 0 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 0 | 0
300C | Counselor // Storage |  | 0 |  |  | 342 | 7 | 0 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 0 | 0
301 | Vice Principals Office |  | 0 | Yes | 20 | 629 | 14 | 14 | House Fan | 8 | 5032 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom |  | 0 | Yes | 20 | 735 | 16 | 16 | House Fan | 8 | 5880 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom |  | 0 | Yes | 20 | 789 | 17 | 17 | House Fan | 8 | 6312 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom |  | 0 | Yes | 20 | 734 | 16 | 16 | House Fan | 8 | 5872 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom |  | 0 | Yes | 20 | 789 | 17 | 17 | House Fan | 8 | 6312 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom |  | 0 |  |  | 1170 | 26 | 0 | House Fan | 8 | 9360 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom |  | 0 | Yes | 20 | 936 | 21 | 21 | House Fan | 8 | 7488 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom |  | 0 | Yes | 20 | 735 | 16 | 16 | House Fan | 8 | 5880 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom |  | 0 |  |  | 952 | 21 | 0 | House Fan | 8 | 7616 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom |  | 0 | Yes | 20 | 840 | 19 | 19 | House Fan | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
311 | Classroom |  | 0 |  |  | 836 | 19 | 0 | House Fan | 8 | 6688 | 0 | 1 | 0 | 0 | 0 | 0
312 | Classroom |  | 0 |  |  | 792 | 18 | 0 | House Fan | 8 | 6336 | 0 | 1 | 0 | 0 | 0 | 0
313 | Classroom |  | 0 |  |  | 920 | 20 | 0 | House Fan | 8 | 7360 | 0 | 1 | 0 | 0 | 0 | 0
314 | Classroom |  | 0 |  |  | 713 | 16 | 0 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 0 | 0
315 | Classroom |  | 0 |  |  | 667 | 15 | 0 | House Fan | 8 | 5336 | 0 | 1 | 0 | 0 | 0 | 0
316 | Classroom |  | 0 |  |  | 713 | 16 | 0 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 0 | 0
317 | Classroom |  | 0 |  |  | 638 | 14 | 0 | House Fan | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
318 | Classroom |  | 0 |  |  | 868 | 19 | 0 | House Fan | 8 | 6944 | 0 | 1 | 0 | 0 | 0 | 0
319 | Classroom |  | 0 | Yes | 20 | 868 | 19 | 19 | House Fan | 8 | 6944 | 0 | 1 | 0 | 0 | 20 | 3
320 | Classroom |  | 0 | Yes | 20 | 868 | 19 | 19 | House Fan | 8 | 6944 | 0 | 1 | 0 | 0 | 20 | 3
324A | Counselor, School Police |  | 0 |  |  | 342 | 7 | 0 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 0 | 0
324B | Counselor, School Police |  | 0 |  |  | 342 | 7 | 0 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 0 | 0
324C | Counselor, School Police |  | 0 |  |  | 342 | 7 | 0 | House Fan | 8 | 2736 | 0 | 1 | 0 | 0 | 0 | 0
322 | Classroom |  | 0 | Yes | 20 | 868 | 19 | 19 | House Fan | 8 | 6944 | 0 | 1 | 0 | 0 | 20 | 3
321 | Classroom |  | 0 | Yes | 20 | 861 | 19 | 19 | House Fan | 8 | 6888 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-26
School: | William Rowen Elementary School
Vendor: | EMCOR | EMCOR Part 2 | Devine
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Auditorium | 0 | 0 |  |  | 4256 | 96 | 0 | House Fan | 8 | 34048 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria/Gym | 0 | 0 | Yes | 20 | 5220 | 118 | 118 | Univent | 8 | 41760 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Library | 328 | 21 |  |  | 1456 | 33 | 21 | Univent | 8 | 11648 | 1.6896 | 1 | 1.6896 | 1 | 1.6896 | 1
101 | Classroom | 457 | 30 |  |  | 1128 | 25 | 25 | Univent | 8 | 9024 | 3.0386 | 1 | 3.0386 | 1 | 3.0386 | 1
102 | Classroom | 545 | 36 |  |  | 1128 | 25 | 25 | Univent | 8 | 9024 | 3.6237 | 1 | 3.6237 | 1 | 3.6237 | 1
103 | Classroom | 42 | 2 | Yes | 20 | 266 | 6 | 6 | Univent | 8 | 2128 | 1.1842 | 1 | 1.1842 | 1 | 21.1842 | 3
104 | Classroom | 0 | 0 | Yes | 20 | 816 | 18 | 18 | Univent | 8 | 6528 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom | 304 | 20 |  |  | 816 | 18 | 18 | Univent | 8 | 6528 | 2.7941 | 1 | 2.7941 | 1 | 2.7941 | 1
106 | Classroom | 0 | 0 | Yes | 20 | 816 | 18 | 18 | Univent | 8 | 6528 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom | 299 | 19 |  |  | 816 | 18 | 18 | Univent | 8 | 6528 | 2.7482 | 1 | 2.7482 | 1 | 2.7482 | 1
108 | Classroom | 0 | 0 | Yes | 20 | 720 | 16 | 16 | Univent | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 234 | 15 |  |  | 720 | 16 | 15 | Univent | 8 | 5760 | 2.4375 | 1 | 2.4375 | 1 | 2.4375 | 1
110 | Classroom | 399 | 26 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 4.1562 | 1 | 4.1562 | 2 | 4.1562 | 2
111 | Classroom | 440 | 29 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 4.5833 | 1 | 4.5833 | 2 | 4.5833 | 2
112 | Classroom | 68 | 4 |  |  | 720 | 16 | 4 | Univent | 8 | 5760 | 0.70833 | 1 | 0.70833 | 0 | 0.70833 | 0
113 | Classroom | 235 | 15 |  |  | 720 | 16 | 15 | Univent | 8 | 5760 | 2.4479 | 1 | 2.4479 | 1 | 2.4479 | 1
- | Nurse's Office | 235 | 15 |  |  | 192 | 4 | 4 | Univent | 8 | 1536 | 9.1797 | 1 | 9.1797 | 2 | 9.1797 | 2
201 | Classroom | 373 | 24 |  |  | 920 | 20 | 20 | Univent | 8 | 7360 | 3.0408 | 1 | 3.0408 | 1 | 3.0408 | 1
202 | Classroom | 396 | 26 |  |  | 920 | 20 | 20 | Univent | 8 | 7360 | 3.2283 | 1 | 3.2283 | 1 | 3.2283 | 1
203 | Classroom | 307 | 20 |  |  | 442 | 10 | 10 | Univent | 8 | 3536 | 5.2093 | 1 | 5.2093 | 2 | 5.2093 | 2
204 | Classroom | 299 | 19 |  |  | 384 | 8 | 8 | Univent | 8 | 3072 | 5.8398 | 1 | 5.8398 | 2 | 5.8398 | 2
205 | Classroom | 309 | 20 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 3.2188 | 1 | 3.2188 | 1 | 3.2188 | 1
206 | Classroom | 230 | 15 |  |  | 720 | 16 | 15 | Univent | 8 | 5760 | 2.3958 | 1 | 2.3958 | 1 | 2.3958 | 1
207 | Classroom | 327 | 21 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 3.4062 | 1 | 3.4062 | 1 | 3.4062 | 1
208 | Classroom | 272 | 18 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 2.8333 | 1 | 2.8333 | 1 | 2.8333 | 1
209 | Classroom | 324 | 21 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 3.375 | 1 | 3.375 | 1 | 3.375 | 1
210 | Classroom | 276 | 18 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 2.875 | 1 | 2.875 | 1 | 2.875 | 1
211 | Classroom | 336 | 22 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 3.5 | 1 | 3.5 | 1 | 3.5 | 1
212 | Classroom | 272 | 18 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 2.8333 | 1 | 2.8333 | 1 | 2.8333 | 1
213 | Classroom | 284 | 18 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 2.9583 | 1 | 2.9583 | 1 | 2.9583 | 1
214 | Classroom | 271 | 18 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 2.8229 | 1 | 2.8229 | 1 | 2.8229 | 1
215 | Classroom | 280 | 18 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 2.9167 | 1 | 2.9167 | 1 | 2.9167 | 1
216 | Classroom | 300 | 20 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 3.0242 | 1 | 3.0242 | 1 | 3.0242 | 1
- | Main Office |  | 0 | Yes | 20 | 552 | 12 | 12 |  | 8 | 4416 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal |  | 0 | Yes | 20 | 270 | 6 | 6 |  | 8 | 2160 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-23
School: | Roxborough High School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
114 | Classroom | 0 | 0 |  |  | 857 | 19 | 0 | Univent | 8 | 6856 | 0 | 1 | 0 | 0 | 0 | 0
115 | Classroom | 30 | 2 |  |  | 870 | 19 | 2 | Univent | 8 | 6960 | 0.25862 | 1 | 0.25862 | 0 | 0.25862 | 0
116 | Classroom | 45 | 3 |  |  | 690 | 15 | 3 | Univent | 8 | 5520 | 0.48913 | 1 | 0.48913 | 0 | 0.48913 | 0
117 | Weight Room | 30 | 2 |  |  | 814 | 18 | 2 | Univent | 8 | 6512 | 0.27641 | 1 | 0.27641 | 0 | 0.27641 | 0
118 | Classroom | 55 | 3 |  |  | 702 | 15 | 3 | Univent | 8 | 5616 | 0.58761 | 1 | 0.58761 | 0 | 0.58761 | 0
119 | Classroom | 270 | 18 |  |  | 877 | 19 | 18 | Univent | 8 | 7016 | 2.309 | 1 | 2.309 | 1 | 2.309 | 1
120 | Classroom | 85 | 5 |  |  | 694 | 15 | 5 | Univent | 8 | 5552 | 0.91859 | 1 | 0.91859 | 0 | 0.91859 | 0
121 | Classroom | 40 | 2 |  |  | 1207 | 27 | 2 | Univent | 8 | 9656 | 0.24855 | 1 | 0.24855 | 0 | 0.24855 | 0
124A-1 | Classroom | 55 | 3 |  |  | 621 | 14 | 3 | Univent | 8 | 4968 | 0.66425 | 1 | 0.66425 | 0 | 0.66425 | 0
124B-1 | Classroom | 30 | 2 |  |  | 672 | 15 | 2 | Univent | 8 | 5376 | 0.33482 | 1 | 0.33482 | 0 | 0.33482 | 0
126 | Classroom | 0 | 0 |  |  | 1841 | 41 | 0 | Univent | 8 | 14728 | 0 | 1 | 0 | 0 | 0 | 0
128 | Classroom | 50 | 3 |  |  | 1501 | 34 | 3 | Univent | 8 | 12008 | 0.24983 | 1 | 0.24983 | 0 | 0.24983 | 0
203 | Classroom |  | 0 | Yes | 20 | 682 | 15 | 15 |  | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 682 | 15 | 15 |  | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
215 | Classroom | 0 | 0 |  |  | 829 | 18 | 0 | Univent | 8 | 6632 | 0 | 1 | 0 | 0 | 0 | 0
216 | Classroom | 50 | 3 |  |  | 834 | 18 | 3 | Univent | 8 | 6672 | 0.44964 | 1 | 0.44964 | 0 | 0.44964 | 0
217 | Classroom | 0 | 0 |  |  | 686 | 15 | 0 | Univent | 8 | 5488 | 0 | 1 | 0 | 0 | 0 | 0
218 | Classroom | 0 | 0 |  |  | 724 | 16 | 0 | Univent | 8 | 5792 | 0 | 1 | 0 | 0 | 0 | 0
219 | Classroom | 55 | 3 |  |  | 842 | 19 | 3 | Univent | 8 | 6736 | 0.4899 | 1 | 0.4899 | 0 | 0.4899 | 0
220 | Classroom | 60 | 4 |  |  | 616 | 14 | 4 | Univent | 8 | 4928 | 0.73052 | 1 | 0.73052 | 0 | 0.73052 | 0
221 | Classroom | 35 | 2 |  |  | 845 | 19 | 2 | Univent | 8 | 6760 | 0.31065 | 1 | 0.31065 | 0 | 0.31065 | 0
223 | Classroom | 55 | 3 |  |  | 1072 | 24 | 3 | Univent | 8 | 8576 | 0.38479 | 1 | 0.38479 | 0 | 0.38479 | 0
224 | Classroom | 55 | 3 |  |  | 1010 | 22 | 3 | Univent | 8 | 8080 | 0.40842 | 1 | 0.40842 | 0 | 0.40842 | 0
235 | Classroom |  | 0 | Yes | 20 | 839 | 19 | 19 |  | 8 | 6712 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom |  | 0 | Yes | 20 | 997 | 22 | 22 |  | 8 | 7976 | 0 | 1 | 0 | 0 | 20 | 3
312 | Classroom |  | 0 | Yes | 20 | 1071 | 24 | 24 |  | 8 | 8568 | 0 | 1 | 0 | 0 | 20 | 3
319 | Classroom | 40 | 2 |  |  | 644 | 14 | 2 | Univent | 8 | 5152 | 0.46584 | 1 | 0.46584 | 0 | 0.46584 | 0
320 | Classroom | 40 | 2 |  |  | 721 | 16 | 2 | Univent | 8 | 5768 | 0.41609 | 1 | 0.41609 | 0 | 0.41609 | 0
321 | Classroom | 55 | 3 |  |  | 924 | 21 | 3 | Univent | 8 | 7392 | 0.44643 | 1 | 0.44643 | 0 | 0.44643 | 0
322 | Classroom | 30 | 2 |  |  | 723 | 16 | 2 | Univent | 8 | 5784 | 0.3112 | 1 | 0.3112 | 0 | 0.3112 | 0
323 | Classroom | 60 | 4 |  |  | 777 | 17 | 4 | Univent | 8 | 6216 | 0.57915 | 1 | 0.57915 | 0 | 0.57915 | 0
324 | Classroom | 55 | 3 |  |  | 942 | 21 | 3 | Univent | 8 | 7536 | 0.4379 | 1 | 0.4379 | 0 | 0.4379 | 0
325 | Classroom | 45 | 3 | Yes | 20 | 325 | 7 | 7 | Univent | 8 | 2600 | 1.0385 | 1 | 1.0385 | 1 | 21.0385 | 3
326 | Classroom | 55 | 3 |  |  | 1000 | 22 | 3 | Univent | 8 | 8000 | 0.4125 | 1 | 0.4125 | 0 | 0.4125 | 0
- | Gymnasium | 740 | 49 |  |  | 11475 | 260 | 49 | Air Handling Unit | 8 | 91800 | 0.48366 | 1.4912 | 0.72121 | 0 | 0.72121 | 0
- | Library | 2335 | 155 |  |  | 2622 | 59 | 59 | Air Handling Unit | 8 | 20976 | 6.6791 | 1.062 | 7.0934 | 2 | 7.0934 | 2
East Office | Office | 75 | 5 |  |  |  | 0 | 0
West Office | Office | 110 | 7 |  |  |  | 0 | 0 | Air Handling Unit
- | Alumni Room | 255 | 17 |  |  | 377 | 8 | 8 | Air Handling Unit | 8 | 3016 | 5.0729 | 1 | 5.0729 | 2 | 5.0729 | 2
- | Computer Lab | 1285 | 85 |  |  | 870 | 19 | 19 | Air Handling Unit | 8 | 6960 | 11.0776 | 1 | 11.0776 | 3 | 11.0776 | 3
Sheet Last Modified: | 2021-03-18
School: | Arts Academy @ Benjamin Rush High School
Vendor: | Goldner | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
103 | Lab Classroom | 465 | 31 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 4.6624 | 1 | 4.6624 | 2 | 4.6624 | 2
103 | Lab Classroom | 465 | 31 |  |  |  | 0 | 0 | Univent & Air Handling Unit
104 | GraphicArts Classroom | 928 | 61 |  |  | 1840 | 41 | 41 | Univent & Air Handling Unit | 8 | 14720 | 3.7826 | 1 | 3.7826 | 1 | 3.7826 | 1
104 | Graphic Arts Classroom | 946 | 63 |  |  |  | 0 | 0 | Univent & Air Handling Unit
105 | IMC Classroom | 2959 | 197 |  |  |  | 0 | 0 | Air Handling Unit
105D | Student Property Office | 281 | 18 |  |  |  | 0 | 0 | Air Handling Unit
105E | IMC Copy Office | 960 | 64 |  |  |  | 0 | 0 | Air Handling Unit
105F | Cart Storage | 368 | 24 |  |  |  | 0 | 0 | Air Handling Unit
105G | Tech Equip Office | 255 | 17 |  |  |  | 0 | 0 | Air Handling Unit
105H | IMC Office | 201 | 13 |  |  |  | 0 | 0 | Air Handling Unit
105J | IMC Storage room | 252 | 16 |  |  |  | 0 | 0 | Air Handling Unit
105K | IMC Conference Rm | 312 | 20 |  |  |  | 0 | 0 | Air Handling Unit
106 | Art Studio Classroom | 1326 | 88 |  |  | 1020 | 23 | 23 | Air Handling Unit | 8 | 8160 | 9.75 | 1 | 9.75 | 2 | 9.75 | 2
107 | storage room | 275 | 18 |  |  | 280 | 6 | 6 | Air Handling Unit | 8 | 2240 | 7.3661 | 1 | 7.3661 | 2 | 7.3661 | 2
122 | Art Studio Classroom | 1689 | 112 |  |  | 1496 | 34 | 34 | Air Handling Unit | 8 | 11968 | 8.4676 | 1 | 8.4676 | 2 | 8.4676 | 2
123 | Production Studio Classroom | 2228 | 148 |  |  | 1254 | 28 | 28 | Air Handling Unit | 8 | 10032 | 13.3254 | 1 | 13.3254 | 3 | 13.3254 | 3
126A | Boys Locker Room | 0 | 0 |  |  |  | 0 | 0
127A | Girls Locker Room | 0 | 0 |  |  |  | 0 | 0
129 | Production Booth Classroom | 842 | 56 |  |  | 264 | 6 | 6 | Air Handling Unit | 8 | 2112 | 23.9205 | 1 | 23.9205 | 3 | 23.9205 | 3
131A | Changing Room Classroom | 238 | 15 |  |  | 72 | 1 | 1 | Air Handling Unit | 8 | 576 | 24.7917 | 1 | 24.7917 | 4 | 24.7917 | 4
131B | Changing Room Classroom | 175 | 11 |  |  | 192 | 4 | 4 | Air Handling Unit | 8 | 1536 | 6.8359 | 1 | 6.8359 | 2 | 6.8359 | 2
133 | Storage Room | 428 | 28 |  |  | 580 | 13 | 13 | Air Handling Unit | 8 | 4640 | 5.5345 | 1 | 5.5345 | 2 | 5.5345 | 2
134 | Music Classroom | 1076 | 71 |  |  | 748 | 17 | 17 | Air Handling Unit | 8 | 5984 | 10.7888 | 1 | 10.7888 | 3 | 10.7888 | 3
135 | Music Classroom | 1097 | 73 |  |  | 748 | 17 | 17 | Air Handling Unit | 8 | 5984 | 10.9993 | 1 | 10.9993 | 3 | 10.9993 | 3
136 | Practice Classroom | 113 | 7 |  |  | 36 | 0 | 0 | Air Handling Unit | 8 | 288 | 23.5417 | 1 | 23.5417 | 3 | 23.5417 | 3
137 | Practice Classroom | 116 | 7 |  |  | 36 | 0 | 0 | Air Handling Unit | 8 | 288 | 24.1667 | 1 | 24.1667 | 4 | 24.1667 | 4
138 | Library | 88 | 5 |  |  |  | 0 | 0 | Air Handling Unit
140 | Vocal Music Classroom | 3597 | 239 |  |  |  | 0 | 0 | Air Handling Unit
141 | Scene Shop Classroom | 994 | 66 |  |  |  | 0 | 0 | Univent & Air Handling Unit
142 | Vocal Theory Classroom | 347 | 23 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 3.4793 | 1 | 3.4793 | 1 | 3.4793 | 1
143 | Music Theory Classroom | 963 | 64 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 9.6557 | 1 | 9.6557 | 2 | 9.6557 | 2
144 | Music Tech Lab Classroom | 699 | 46 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 7.0087 | 1 | 7.0087 | 2 | 7.0087 | 2
145A | Clerical Office | 362 | 24 |  |  | 720 | 16 | 16 | Air Handling Unit | 8 | 5760 | 3.7708 | 1 | 3.7708 | 1 | 3.7708 | 1
145B | Roster Office | 161 | 10 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 15.0938 | 1 | 15.0938 | 3 | 15.0938 | 3
145D | Copier Office | 219 | 14 |  |  | 75 | 1 | 1 | Air Handling Unit | 8 | 600 | 21.9 | 1 | 21.9 | 3 | 21.9 | 3
145E | Conference Office | 341 | 22 |  |  | 128 | 2 | 2 | Air Handling Unit | 8 | 1024 | 19.9805 | 1 | 19.9805 | 3 | 19.9805 | 3
145F | Principal Office | 328 | 21 |  |  | 247 | 5 | 5 | Air Handling Unit | 8 | 1976 | 9.9595 | 1 | 9.9595 | 2 | 9.9595 | 2
145J | Asset Princ.Office | 114 | 7 |  |  | 272 | 6 | 6 | Air Handling Unit | 8 | 2176 | 3.1434 | 1 | 3.1434 | 1 | 3.1434 | 1
145K | Asset Princ.Office | 67 | 4 |  |  | 180 | 4 | 4 | Air Handling Unit | 8 | 1440 | 2.7917 | 1 | 2.7917 | 1 | 2.7917 | 1
146A | Clinic Office | 45 | 3 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 2.8125 | 1 | 2.8125 | 1 | 2.8125 | 1
146B | ClinicWaitingoffice | 506 | 33 |  |  | 221 | 5 | 5 | Air Handling Unit | 8 | 1768 | 17.1719 | 1 | 17.1719 | 3 | 17.1719 | 3
146D | Exam Room | 328 | 21 |  |  | 60 | 1 | 1 | Air Handling Unit | 8 | 480 | 41 | 1 | 41 | 4 | 41 | 4
147 | Counselor Waiting Area | 450 | 30 |  |  | 288 | 6 | 6 | Air Handling Unit | 8 | 2304 | 11.7188 | 1 | 11.7188 | 3 | 11.7188 | 3
147B | Counselor Office | 149 | 9 |  |  | 221 | 5 | 5 | Air Handling Unit | 8 | 1768 | 5.0566 | 1 | 5.0566 | 2 | 5.0566 | 2
147D | Counselor's Office | 283 | 18 |  |  | 60 | 1 | 1 | Air Handling Unit | 8 | 480 | 35.375 | 1 | 35.375 | 4 | 35.375 | 4
147E | Counselor Office | 157 | 10 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 9.8125 | 1 | 9.8125 | 2 | 9.8125 | 2
147F | Counselor Conference Office | 311 | 20 |  |  | 169 | 3 | 3 | Air Handling Unit | 8 | 1352 | 13.8018 | 1 | 13.8018 | 3 | 13.8018 | 3
147G | Counselor's Office | 383 | 25 |  |  | 180 | 4 | 4 | Air Handling Unit | 8 | 1440 | 15.9583 | 1 | 15.9583 | 3 | 15.9583 | 3
148A | Camera office | 565 | 37 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 35.3125 | 1 | 35.3125 | 4 | 35.3125 | 4
148B | Storage Room | 121 | 8 |  |  |  | 0 | 0 | Air Handling Unit
148C | Records Office | 118 | 7 |  |  |  | 0 | 0 | Air Handling Unit
148D | Security Office | 125 | 8 |  |  |  | 0 | 0 | Air Handling Unit
148E | Operations Office | 372 | 24 |  |  |  | 0 | 0 | Air Handling Unit
200 | General Classroom | 649 | 43 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 6.5074 | 1 | 6.5074 | 2 | 6.5074 | 2
201 | General Classroom | 532 | 35 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 5.3342 | 1 | 5.3342 | 2 | 5.3342 | 2
202 | General Classroom | 692 | 46 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 6.9385 | 1 | 6.9385 | 2 | 6.9385 | 2
204 | General Classroom | 447 | 29 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 4.482 | 1 | 4.482 | 2 | 4.482 | 2
205 | General Classroom | 566 | 37 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 5.6751 | 1 | 5.6751 | 2 | 5.6751 | 2
209 | Social Ed. Classroom | 779 | 51 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 7.8108 | 1 | 7.8108 | 2 | 7.8108 | 2
210 | General Classroom | 662 | 44 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 6.6377 | 1 | 6.6377 | 2 | 6.6377 | 2
211 | General Classroom | 562 | 37 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 5.635 | 1 | 5.635 | 2 | 5.635 | 2
212 | General Classroom | 423 | 28 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 4.2413 | 1 | 4.2413 | 2 | 4.2413 | 2
213 | General Classroom | 597 | 39 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 5.986 | 1 | 5.986 | 2 | 5.986 | 2
214 | General Classroom | 868 | 57 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 8.7032 | 1 | 8.7032 | 2 | 8.7032 | 2
215 | General Classroom | 442 | 29 |  |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
216 | Physical Science Classroom | 970 | 64 |  |  | 1344 | 30 | 30 | Fan Coil Unit & Air Handling Unit | 8 | 10752 | 5.4129 | 1 | 5.4129 | 2 | 5.4129 | 2
217 | Prep Classroom | 299 | 19 |  |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
219 | Physics Classroom | 630 | 42 |  |  | 1344 | 30 | 30 | Fan Coil Unit & Air Handling Unit | 8 | 10752 | 3.5156 | 1 | 3.5156 | 1 | 3.5156 | 1
220 | Storage room | 418 | 27 |  |  |  | 0 | 0 | Air Handling Unit
221 | General Classroom | 324 | 21 |  |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
221B | Storage Room | 135 | 9 |  |  |  | 0 | 0 | Air Handling Unit
221C | Storage Room | 130 | 8 |  |  |  | 0 | 0 | Air Handling Unit
222 | Biology Classroom | 633 | 42 |  |  | 1764 | 40 | 40 | Fan Coil Unit & Air Handling Unit | 8 | 14112 | 2.6913 | 1 | 2.6913 | 1 | 2.6913 | 1
223 | Prep Classroom | 322 | 21 |  |  | 312 | 7 | 7 | Fan Coil Unit & Air Handling Unit | 8 | 2496 | 7.7404 | 1 | 7.7404 | 2 | 7.7404 | 2
224 | Chemistry Classroom | 616 | 41 |  |  | 1716 | 39 | 39 | Fan Coil Unit & Air Handling Unit | 8 | 13728 | 2.6923 | 1 | 2.6923 | 1 | 2.6923 | 1
224A | Storage Room | 135 | 9 |  |  |  | 0 | 0 | Air Handling Unit
225 | Instructional Room | 483 | 32 |  |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
234 | Lab Classroom | 1107 | 73 |  |  | 850 | 19 | 19 | Fan Coil Unit & Air Handling Unit | 8 | 6800 | 9.7676 | 1 | 9.7676 | 2 | 9.7676 | 2
235 | Lab Classroom | 595 | 39 |  |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
235 | Lab Classroom | 465 | 31 |  |  |  | 0 | 0 | Univent & Air Handling Unit
236 | Multipurpose Classroom | 636 | 42 |  |  | 1156 | 26 | 26 | Fan Coil Unit & Air Handling Unit | 8 | 9248 | 4.1263 | 1 | 4.1263 | 2 | 4.1263 | 2
237 | Foreign Language Classroom | 613 | 40 |  |  | 1156 | 26 | 26 | Fan Coil Unit & Air Handling Unit | 8 | 9248 | 3.9771 | 1 | 3.9771 | 1 | 3.9771 | 1
240 | Commercial Art Classroom | 845 | 56 |  |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
241 | General Classroom | 664 | 44 |  |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
242 | Instructional Room | 551 | 36 |  |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
243 | General Classroom | 518 | 34 |  |  |  | 0 | 0 | Fan Coil Unit & Air Handling Unit
244 | General Classroom | 737 | 49 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 7.3897 | 1 | 7.3897 | 2 | 7.3897 | 2
245 | General Classroom | 586 | 39 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 5.8757 | 1 | 5.8757 | 2 | 5.8757 | 2
246 | General Classroom | 719 | 47 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 7.2092 | 1 | 7.2092 | 2 | 7.2092 | 2
247 | General Classroom | 705 | 47 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 7.0689 | 1 | 7.0689 | 2 | 7.0689 | 2
248 | General Classroom | 909 | 60 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 9.1143 | 1 | 9.1143 | 2 | 9.1143 | 2
249 | General Classroom | 779 | 51 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 7.8108 | 1 | 7.8108 | 2 | 7.8108 | 2
251 | General Classroom | 671 | 44 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 6.7279 | 1 | 6.7279 | 2 | 6.7279 | 2
252 | General Classroom | 876 | 58 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 8.7834 | 1 | 8.7834 | 2 | 8.7834 | 2
253 | General Classroom | 608 | 40 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 6.0963 | 1 | 6.0963 | 2 | 6.0963 | 2
254 | General Classroom | 633 | 42 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 6.3469 | 1 | 6.3469 | 2 | 6.3469 | 2
255 | General Classroom | 738 | 49 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 7.3997 | 1 | 7.3997 | 2 | 7.3997 | 2
256 | General Classroom | 684 | 45 |  |  | 748 | 17 | 17 | Univent & Air Handling Unit | 8 | 5984 | 6.8583 | 1 | 6.8583 | 2 | 6.8583 | 2
- | Auditorium | 18527 | 1235 |  |  |  | 0 | 0 | Air Handling Unit
- | Cafeteria | 10458 | 697 |  |  |  | 0 | 0 | Air Handling Unit
- | Studios Area and Assoc. Corridors, fresh air vent in rooms | 18369 | 1224 |  |  |  | 0 | 0 | Air Handling Unit
- | Instrumental Music Area | 14678 | 978 |  |  |  | 0 | 0 | Air Handling Unit
- | Gym | 8904 | 593 |  |  |  | 0 | 0 | Air Handling Unit
- | ICM Classroom Area | 11044 | 736 |  |  |  | 0 | 0 | Air Handling Unit
Sheet Last Modified: | 2021-04-27
School: | Walter Biddle Saul High School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
A1 | A1 | 732 | 48 |  |  | 864 | 19 | 19 | Air Handling Unit | 8 | 6912 | 6.3542 | 1 | 6.3542 | 2 | 6.3542 | 2
A1/A2 | Storage | 288 | 19 |  |  | 255 | 5 | 5 | Air Handling Unit | 8 | 2040 | 8.4706 | 1 | 8.4706 | 2 | 8.4706 | 2
A2 | A2 | 703 | 46 |  |  | 864 | 19 | 19 | Air Handling Unit | 8 | 6912 | 6.1024 | 1 | 6.1024 | 2 | 6.1024 | 2
A3 | A3 | 395 | 26 |  |  | 792 | 18 | 18 | Univent | 8 | 6336 | 3.7405 | 1 | 3.7405 | 1 | 3.7405 | 1
A5 | A5 | 1123 | 74 |  |  | 740 | 16 | 16 | Univent | 8 | 5920 | 11.3818 | 1 | 11.3818 | 3 | 11.3818 | 3
A21 | A21 | 0 | 0 |  |  | 570 | 12 | 0 | Air Handling Unit | 8 | 4560 | 0 | 1 | 0 | 0 | 0 | 0
A22 | A22 | 487 | 32 |  |  | 620 | 14 | 14 | Univent | 8 | 4960 | 5.8911 | 1 | 5.8911 | 2 | 5.8911 | 2
A23 | A23 | 699 | 46 |  |  | 888 | 20 | 20 | Univent | 8 | 7104 | 5.9037 | 1 | 5.9037 | 2 | 5.9037 | 2
A24 | A24 | 1147 | 76 |  |  | 888 | 20 | 20 | Univent | 8 | 7104 | 9.6875 | 1 | 9.6875 | 2 | 9.6875 | 2
A25 | A25 | 878 | 58 |  |  | 888 | 20 | 20 | Univent | 8 | 7104 | 7.4155 | 1 | 7.4155 | 2 | 7.4155 | 2
A26 | A26 | 449 | 29 |  |  | 888 | 20 | 20 | Univent | 8 | 7104 | 3.7922 | 1 | 3.7922 | 1 | 3.7922 | 1
A29 | A29 |  | 0 | Yes | 20 | 864 | 19 | 19 |  | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
1 | 1 | 240 | 16 |  |  | 864 | 19 | 19 | Univent | 8 | 6912 | 2.0833 | 1 | 2.0833 | 1 | 2.0833 | 1
2 | 2 | 70 | 4 |  |  | 551 | 12 | 12 | Univent | 8 | 4408 | 0.95281 | 1 | 0.95281 | 0 | 0.95281 | 0
3 | 3 | 900 | 60 |  |  | 1134 | 25 | 25 | Univent | 8 | 9072 | 5.9524 | 1 | 5.9524 | 2 | 5.9524 | 2
4 | 4 | 0 | 0 |  |  | 896 | 20 | 0 | Univent | 8 | 7168 | 0 | 1 | 0 | 0 | 0 | 0
100 | 100 | 215 | 14 |  |  | 620 | 14 | 14 | Univent | 8 | 4960 | 2.6008 | 1 | 2.6008 | 1 | 2.6008 | 1
102 | 102 | 342 | 22 |  |  | 620 | 14 | 14 | Univent | 8 | 4960 | 4.1371 | 1 | 4.1371 | 2 | 4.1371 | 2
103 | 103 | 206 | 13 |  |  | 780 | 17 | 17 | Univent | 8 | 6240 | 1.9808 | 1 | 1.9808 | 1 | 1.9808 | 1
104 | 104 | 265 | 17 |  |  | 640 | 14 | 14 | Univent | 8 | 5120 | 3.1055 | 1 | 3.1055 | 1 | 3.1055 | 1
200 | 200 | 258 | 17 |  |  | 620 | 14 | 14 | Univent | 8 | 4960 | 3.121 | 1 | 3.121 | 1 | 3.121 | 1
201 | 201 | 244 | 16 |  |  | 620 | 14 | 14 | Univent | 8 | 4960 | 2.9516 | 1 | 2.9516 | 1 | 2.9516 | 1
202 | 202 | 251 | 16 |  |  | 620 | 14 | 14 | Univent | 8 | 4960 | 3.0363 | 1 | 3.0363 | 1 | 3.0363 | 1
203 | 203 | 173 | 11 |  |  | 620 | 14 | 14 | Univent | 8 | 4960 | 2.0927 | 1 | 2.0927 | 1 | 2.0927 | 1
204 | 204 | 226 | 15 |  |  | 620 | 14 | 14 | Univent | 8 | 4960 | 2.7339 | 1 | 2.7339 | 1 | 2.7339 | 1
205 | 205 | 468 | 31 |  |  | 660 | 15 | 15 | Univent | 8 | 5280 | 5.3182 | 1 | 5.3182 | 2 | 5.3182 | 2
206 | 206 | 560 | 37 |  |  | 110 | 2 | 2 | Univent | 8 | 880 | 38.1818 | 1 | 38.1818 | 4 | 38.1818 | 4
208 | 208 | 232 | 15 |  |  | 600 | 13 | 13 | Univent | 8 | 4800 | 2.9 | 1 | 2.9 | 1 | 2.9 | 1
210 | 210 | 244 | 16 |  |  | 465 | 10 | 10 | Univent | 8 | 3720 | 3.9355 | 1 | 3.9355 | 1 | 3.9355 | 1
Food Science | Laboratory |  | 0 |  |  | 560 | 12 | 12 |  | 8 | 4480 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurse | 316 | 21 |  |  | 260 | 5 | 5 | Univent | 8 | 2080 | 9.1154 | 1 | 9.1154 | 2 | 9.1154 | 2
- | Staff Lounge | 0 | 0 |  |  | 384 | 8 | 0 | Univent | 8 | 3072 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-05-03
School: | William L. Sayre High School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 518 | 34 |  |  | 720 | 16 | 16 | Univent | 8 | 5760 | 5.3958 | 1 | 5.3958 | 2 | 5.3958 | 2
102 | Lounge | 229 | 15 |  |  | 408 | 9 | 9 | Univent | 8 | 3264 | 4.2096 | 1 | 4.2096 | 2 | 4.2096 | 2
103 | Music | 327 | 21 |  |  | 1260 | 28 | 28 | Univent | 8 | 10080 | 1.9464 | 1 | 1.9464 | 1 | 1.9464 | 1
104 | Office | 0 | 0 |  |  | 360 | 8 | 0 | Univent | 8 | 2880 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom | 375 | 25 |  |  | 1504 | 34 | 34 | Univent | 8 | 12032 | 1.87 | 1 | 1.87 | 1 | 1.87 | 1
106 | Classroom | 389 | 25 |  |  | 768 | 17 | 17 | Univent | 8 | 6144 | 3.7988 | 1 | 3.7988 | 1 | 3.7988 | 1
107 | Classroom | 517 | 34 |  |  | 1408 | 32 | 32 | Univent | 8 | 11264 | 2.7539 | 1 | 2.7539 | 1 | 2.7539 | 1
108 | Classroom | 0 | 0 |  |  | 768 | 17 | 0 | Univent | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
109 | Classroom | 0 | 0 | Yes | 20 | 1120 | 25 | 25 | Univent | 8 | 8960 | 0 | 1 | 0 | 0 | 20 | 3
110 | Classroom | 351 | 23 |  |  | 768 | 17 | 17 | Univent | 8 | 6144 | 3.4277 | 1 | 3.4277 | 1 | 3.4277 | 1
111 | Classroom | 638 | 42 |  |  | 1363 | 30 | 30 | Univent | 8 | 10904 | 3.5106 | 1 | 3.5106 | 1 | 3.5106 | 1
115 | Classroom | 369 | 24 |  |  | 896 | 20 | 20 | Univent | 8 | 7168 | 3.0887 | 1 | 3.0887 | 1 | 3.0887 | 1
117 | Classroom | 0 | 0 | Yes | 20 | 756 | 17 | 17 | Univent | 8 | 6048 | 0 | 1 | 0 | 0 | 20 | 3
119 | Classroom | 192 | 12 |  |  | 868 | 19 | 19 | Univent | 8 | 6944 | 1.659 | 1 | 1.659 | 1 | 1.659 | 1
131 | Classroom | 402 | 26 |  |  | 729 | 16 | 16 | Univent | 8 | 5832 | 4.1358 | 1 | 4.1358 | 2 | 4.1358 | 2
133 | Office | 357 | 23 |  |  | 288 | 6 | 6 | Univent | 8 | 2304 | 9.2969 | 1 | 9.2969 | 2 | 9.2969 | 2
135 | Boy's Infirmary | 287 | 19 |  |  | 132 | 3 | 3 | Univent | 8 | 1056 | 16.3068 | 1 | 16.3068 | 3 | 16.3068 | 3
137 | Girl's Infirmary | 142 | 9 |  |  | 285 | 6 | 6 | Univent | 8 | 2280 | 3.7368 | 1 | 3.7368 | 1 | 3.7368 | 1
139 | Classroom | 202 | 13 |  |  | 1024 | 23 | 23 | Univent | 8 | 8192 | 1.4795 | 1 | 1.4795 | 1 | 1.4795 | 1
141 | Classroom | 384 | 25 |  |  | 1188 | 27 | 27 | Univent | 8 | 9504 | 2.4242 | 1 | 2.4242 | 1 | 2.4242 | 1
200 | Youth Court | 693 | 46 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 6.9859 | 1 | 6.9859 | 2 | 6.9859 | 2
200 | Classroom | 410 | 27 |  |  | 592 | 13 | 13 | Univent | 8 | 4736 | 5.1943 | 1 | 5.1943 | 2 | 5.1943 | 2
203 | Classroom | 808 | 53 |  |  | 1504 | 34 | 34 | Univent | 8 | 12032 | 4.0293 | 1 | 4.0293 | 2 | 4.0293 | 2
204 | Classroom | 294 | 19 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 2.9637 | 1 | 2.9637 | 1 | 2.9637 | 1
205 | Classroom | 762 | 50 |  |  | 1504 | 34 | 34 | Univent | 8 | 12032 | 3.7999 | 1 | 3.7999 | 1 | 3.7999 | 1
206 | Classroom | 473 | 31 |  |  | 696 | 15 | 15 | Univent | 8 | 5568 | 5.097 | 1 | 5.097 | 2 | 5.097 | 2
207 | Classroom | 702 | 46 |  |  | 1280 | 29 | 29 | Univent | 8 | 10240 | 4.1133 | 1 | 4.1133 | 2 | 4.1133 | 2
208 | Classroom | 548 | 36 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 5.5242 | 1 | 5.5242 | 2 | 5.5242 | 2
210 | Classroom | 246 | 16 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 2.4798 | 1 | 2.4798 | 1 | 2.4798 | 1
211 | Classroom | 835 | 55 |  |  | 1344 | 30 | 30 | Univent | 8 | 10752 | 4.6596 | 1 | 4.6596 | 2 | 4.6596 | 2
212 | Classroom | 367 | 24 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 3.6996 | 1 | 3.6996 | 1 | 3.6996 | 1
215 | Classroom | 0 | 0 |  |  | 621 | 14 | 0 | Univent | 8 | 4968 | 0 | 1 | 0 | 0 | 0 | 0
216 | Classroom | 731 | 48 |  |  | 864 | 19 | 19 | Univent | 8 | 6912 | 6.3455 | 1 | 6.3455 | 2 | 6.3455 | 2
217 | Classroom | 81 | 5 |  |  | 990 | 22 | 22 | Univent | 8 | 7920 | 0.61364 | 1 | 0.61364 | 0 | 0.61364 | 0
219 | Classroom | 0 | 0 |  |  | 1008 | 22 | 0 | Univent | 8 | 8064 | 0 | 1 | 0 | 0 | 0 | 0
220 | Classroom | 301 | 20 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 3.0343 | 1 | 3.0343 | 1 | 3.0343 | 1
221 | Classroom | 92 | 6 |  |  | 987 | 22 | 22 | Univent | 8 | 7896 | 0.69909 | 1 | 0.69909 | 0 | 0.69909 | 0
222 | Classroom | 623 | 41 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 6.2802 | 1 | 6.2802 | 2 | 6.2802 | 2
223 | Classroom | 0 | 0 |  |  | 902 | 20 | 0 | Univent | 8 | 7216 | 0 | 1 | 0 | 0 | 0 | 0
224 | Classroom | 419 | 27 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 4.2238 | 1 | 4.2238 | 2 | 4.2238 | 2
225 | Classroom | 264 | 17 |  |  | 725 | 16 | 16 | Univent | 8 | 5800 | 2.731 | 1 | 2.731 | 1 | 2.731 | 1
226 | Classroom | 0 | 0 |  |  | 744 | 16 | 0 | Univent | 8 | 5952 | 0 | 1 | 0 | 0 | 0 | 0
228 | Classroom | 202 | 13 |  |  | 840 | 19 | 19 | Univent | 8 | 6720 | 1.8036 | 1 | 1.8036 | 1 | 1.8036 | 1
229 | Classroom | 401 | 26 |  |  | 1458 | 33 | 33 | Univent | 8 | 11664 | 2.0628 | 1 | 2.0628 | 1 | 2.0628 | 1
230 | Classroom | 797 | 53 |  |  | 792 | 18 | 18 | Univent | 8 | 6336 | 7.5473 | 1 | 7.5473 | 2 | 7.5473 | 2
231 | Classroom | 509 | 33 |  |  | 999 | 22 | 22 | Univent | 8 | 7992 | 3.8213 | 1 | 3.8213 | 1 | 3.8213 | 1
232 | Classroom | 1571 | 104 |  |  | 960 | 21 | 21 | Univent | 8 | 7680 | 12.2734 | 1 | 12.2734 | 3 | 12.2734 | 3
234 | Classroom | 1041 | 69 |  |  | 816 | 18 | 18 | Univent | 8 | 6528 | 9.568 | 1 | 9.568 | 2 | 9.568 | 2
235 | Classroom | 778 | 51 |  |  | 1400 | 31 | 31 | Univent | 8 | 11200 | 4.1679 | 1 | 4.1679 | 2 | 4.1679 | 2
236 | Classroom | 809 | 53 |  |  | 744 | 16 | 16 | Univent | 8 | 5952 | 8.1552 | 1 | 8.1552 | 2 | 8.1552 | 2
240 | Classroom | 683 | 45 |  |  | 696 | 15 | 15 | Univent | 8 | 5568 | 7.3599 | 1 | 7.3599 | 2 | 7.3599 | 2
242 | Classroom | 274 | 18 |  |  | 912 | 20 | 20 | Univent | 8 | 7296 | 2.2533 | 1 | 2.2533 | 1 | 2.2533 | 1
244 | Classroom | 0 | 0 |  |  | 768 | 17 | 0 | Univent | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
246 | Classroom | 415 | 27 |  |  | 936 | 21 | 21 | Univent | 8 | 7488 | 3.3253 | 1 | 3.3253 | 1 | 3.3253 | 1
248 | Classroom | 0 | 0 |  |  | 666 | 15 | 0 | Univent | 8 | 5328 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium | 0 | 0 |  |  | 10250 | 232 | 0 | House Fan | 8 | 82000 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 |  |  | 10540 | 239 | 0 | House Fan | 8 | 84320 | 0 | 1.4912 | 0 | 0 | 0 | 0
- | Counseling Office | 234 | 15 |  |  | 187 | 4 | 4 | Univent | 8 | 1496 | 9.385 | 1 | 9.385 | 2 | 9.385 | 2
- | Girls Gym | 0 | 0 | Yes | 20 | 7630 | 173 | 173 | House Fan | 8 | 61040 | 0 | 1.4912 | 0 | 0 | 20 | 3
- | Boys Gym | 0 | 0 | Yes | 20 | 7630 | 173 | 173 | House Fan | 8 | 61040 | 0 | 1.4912 | 0 | 0 | 20 | 3
- | Handball Court | 0 | 0 |  |  | 800 | 18 | 0 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
- | Library | 0 | 0 |  |  | 3432 | 78 | 0 | Univent | 8 | 27456 | 0 | 1.062 | 0 | 0 | 0 | 0
- | IMC Computer | 0 | 0 |  |  | 744 | 16 | 0 | Univent | 8 | 5952 | 0 | 1 | 0 | 0 | 0 | 0
- | Kitchen Cooler room | 0 | 0 |  |  | 182 | 4 | 0 | Univent | 8 | 1456 | 0 | 1 | 0 | 0 | 0 | 0
- | Locker room | 0 | 0 |  |  | 180 | 4 | 0 | Air Handling Unit & Univent | 8 | 1440 | 0 | 1 | 0 | 0 | 0 | 0
- | Boys Locker Rm | 0 | 0 |  |  | 7470 | 169 | 0 | Whole House | 8 | 59760 | 0 | 1.4912 | 0 | 0 | 0 | 0
Return Air Fan & Air Handling Unit
- | Girls Locker Rm | 0 | 0 |  |  | 7470 | 169 | 0 | Whole House | 8 | 59760 | 0 | 1.4912 | 0 | 0 | 0 | 0
Return Air Fan & Air Handling Unit
- | Main Office | 153 | 10 |  |  | 1128 | 25 | 25 | Univent | 8 | 9024 | 1.0173 | 1 | 1.0173 | 1 | 1.0173 | 1
- | Office | 0 | 0 |  |  | 198 | 4 | 0 | Univent | 8 | 1584 | 0 | 1 | 0 | 0 | 0 | 0
- | Rec Room | 0 | 0 |  |  | 9780 | 222 | 0 | House Fan | 8 | 78240 | 0 | 1.4912 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18
School: | High School of the Future
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Auditorium | 4278 | 285 |  |  | 4935 | 112 | 112 | Air Handling Unit | 8 | 39480 | 6.5015 | 1.062 | 6.9048 | 2 | 6.9048 | 2
10 | Mens Room | 139 | 9 |  |  | 205 | 4 | 4 | Air Handling Unit | 8 | 1640 | 5.0854 | 1 | 5.0854 | 2 | 5.0854 | 2
12 | Womens Room | 88 | 5 |  |  | 215 | 4 | 4 | Air Handling Unit | 8 | 1720 | 3.0698 | 1 | 3.0698 | 1 | 3.0698 | 1
14 | Storage | 26 | 1 |  |  | 275 | 6 | 6 | Air Handling Unit | 8 | 2200 | 0.70909 | 1 | 0.70909 | 0 | 0.70909 | 0
16 | IDF | 15 | 1 |  |  | 165 | 3 | 3 | Air Handling Unit | 8 | 1320 | 0.68182 | 1 | 0.68182 | 0 | 0.68182 | 0
17 | Electrical room | 40 | 2 |  |  | 75 | 1 | 1 | Air Handling Unit | 8 | 600 | 4 | 1 | 4 | 1 | 4 | 1
19 | Music Library | 30 | 2 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
21 | Instrument stroage | 96 | 6 |  |  | 370 | 8 | 8 | Air Handling Unit | 8 | 2960 | 1.9459 | 1 | 1.9459 | 1 | 1.9459 | 1
22 | Uniform Room | 49 | 3 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 3.675 | 1 | 3.675 | 1 | 3.675 | 1
23 | Practice room | 41 | 2 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 3.075 | 1 | 3.075 | 1 | 3.075 | 1
24 | Practice room | 42 | 2 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 3.15 | 1 | 3.15 | 1 | 3.15 | 1
25 | Practice room | 43 | 2 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 3.225 | 1 | 3.225 | 1 | 3.225 | 1
26 | Vocal Music Room | 184 | 12 |  |  | 1400 | 31 | 31 | Air Handling Unit | 8 | 11200 | 0.98571 | 1 | 0.98571 | 0 | 0.98571 | 0
27 | Practice Room | 27 | 1 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 2.025 | 1 | 2.025 | 1 | 2.025 | 1
28 | Practice Room | 36 | 2 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 2.7 | 1 | 2.7 | 1 | 2.7 | 1
29 | Practice Room | 41 | 2 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 3.075 | 1 | 3.075 | 1 | 3.075 | 1
30 | Dressing Room | 45 | 3 |  |  | 1300 | 29 | 29 | Air Handling Unit | 8 | 10400 | 0.25962 | 1 | 0.25962 | 0 | 0.25962 | 0
31 | Music Intrrument room | 966 | 64 |  |  | 1800 | 40 | 40 | Air Handling Unit | 8 | 14400 | 4.025 | 1 | 4.025 | 2 | 4.025 | 2
32 | Dressing Room | 104 | 6 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.86667 | 1 | 0.86667 | 0 | 0.86667 | 0
33 | Dressing Room | 45 | 3 |  |  | 300 | 6 | 6 | Air Handling Unit | 8 | 2400 | 1.125 | 1 | 1.125 | 1 | 1.125 | 1
34 | Scene shop | 537 | 35 |  |  | 1200 | 27 | 27 | Air Handling Unit | 8 | 9600 | 3.3563 | 1 | 3.3563 | 1 | 3.3563 | 1
58 | Kitchen |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
101 | Vestibule | 102 | 6 |  |  | 555 | 12 | 12 | Air Handling Unit | 8 | 4440 | 1.3784 | 1 | 1.3784 | 1 | 1.3784 | 1
103 | Camera Room | 49 | 3 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 3.675 | 1 | 3.675 | 1 | 3.675 | 1
104 | Security Room | 59 | 3 |  |  | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 2.2125 | 1 | 2.2125 | 1 | 2.2125 | 1
105 | Corridor |  | 0 |  |  | 50 | 1 | 1 | Air Handling Unit | 8 | 400 | 0 | 1 | 0 | 0 | 0 | 0
106 | Electric room | 63 | 4 |  |  | 135 | 3 | 3 | Air Handling Unit | 8 | 1080 | 3.5 | 1 | 3.5 | 1 | 3.5 | 1
107 | Equipment room | 55 | 3 |  |  | 205 | 4 | 4 | Air Handling Unit | 8 | 1640 | 2.0122 | 1 | 2.0122 | 1 | 2.0122 | 1
110 | waiting room | 101 | 6 |  |  | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 3.7875 | 1 | 3.7875 | 1 | 3.7875 | 1
112 | clerical office | 315 | 21 |  |  | 635 | 14 | 14 | Air Handling Unit | 8 | 5080 | 3.7205 | 1 | 3.7205 | 1 | 3.7205 | 1
113 | work/ conf room | 97 | 6 |  |  | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 3.6375 | 1 | 3.6375 | 1 | 3.6375 | 1
114 | Admin conf room | 81 | 5 |  |  | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 3.0375 | 1 | 3.0375 | 1 | 3.0375 | 1
115 | Principal office | 80 | 5 |  |  | 255 | 5 | 5 | Air Handling Unit | 8 | 2040 | 2.3529 | 1 | 2.3529 | 1 | 2.3529 | 1
115A | Principal bathroom | 8 | 0 |  |  | 60 | 1 | 1 | Air Handling Unit | 8 | 480 | 1 | 1 | 1 | 0 | 1 | 0
117 | Operations office | 24 | 1 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1
118 | vault room | 25 | 1 |  |  | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 0.9375 | 1 | 0.9375 | 0 | 0.9375 | 0
119 | supply room | 12 | 0 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 0.75 | 1 | 0.75 | 0 | 0.75 | 0
121 | Nurse | 38 | 2 |  |  | 95 | 2 | 2 | Air Handling Unit | 8 | 760 | 3 | 1 | 3 | 1 | 3 | 1
121 | Waiting room | 17 | 1 |  |  | 95 | 2 | 2 | Air Handling Unit | 8 | 760 | 1.3421 | 1 | 1.3421 | 1 | 1.3421 | 1
123 | Nurse office | 14 | 0 |  |  |  | 0 | 0 | Air Handling Unit
125 | Exam room B | 14 | 0 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 1.05 | 1 | 1.05 | 1 | 1.05 | 1
125 | Exam room A | 13 | 0 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 0.975 | 1 | 0.975 | 0 | 0.975 | 0
130 | Parent volunteer room | 13 | 0 |  |  | 480 | 10 | 10 | Air Handling Unit | 8 | 3840 | 0.20312 | 1 | 0.20312 | 0 | 0.20312 | 0
130 | Parent volunteer room | 13 | 0 |  |  | 480 | 10 | 10 | Air Handling Unit | 8 | 3840 | 0.20312 | 1 | 0.20312 | 0 | 0.20312 | 0
131 | Plasma screen room | 9 | 0 |  |  | 45 | 1 | 1 | Air Handling Unit | 8 | 360 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1
131 | Janitor closet |  | 0 |  |  | 30 | 0 | 0 | Air Handling Unit | 8 | 240 | 0 | 1 | 0 | 0 | 0 | 0
132 | Womens room | 25 | 1 |  |  | 220 | 5 | 5 | Air Handling Unit | 8 | 1760 | 0.85227 | 1 | 0.85227 | 0 | 0.85227 | 0
132 | Womens Room | 20 | 1 |  |  | 220 | 5 | 5 | Air Handling Unit | 8 | 1760 | 0.68182 | 1 | 0.68182 | 0 | 0.68182 | 0
132 | Womens room |  | 0 |  |  | 220 | 5 | 5 | Air Handling Unit | 8 | 1760 | 0 | 1 | 0 | 0 | 0 | 0
132 | Womens room |  | 0 |  |  | 220 | 5 | 5 | Air Handling Unit | 8 | 1760 | 0 | 1 | 0 | 0 | 0 | 0
133 | Mens room | 49 | 3 |  |  | 245 | 5 | 5 | Air Handling Unit | 8 | 1960 | 1.5 | 1 | 1.5 | 1 | 1.5 | 1
133 | Mens room | 38 | 2 |  |  | 245 | 5 | 5 | Air Handling Unit | 8 | 1960 | 1.1633 | 1 | 1.1633 | 1 | 1.1633 | 1
135 | Mens Room |  | 0 |  |  | 245 | 5 | 5 | Air Handling Unit | 8 | 1960 | 0 | 1 | 0 | 0 | 0 | 0
135 | Mens Room |  | 0 |  |  | 245 | 5 | 5 | Air Handling Unit | 8 | 1960 | 0 | 1 | 0 | 0 | 0 | 0
139 | Mens locker | 14 | 0 |  |  | 375 | 8 | 8 | Air Handling Unit | 8 | 3000 | 0.28 | 1 | 0.28 | 0 | 0.28 | 0
139 | Mens Locker | 14 | 0 |  |  | 375 | 8 | 8 | Air Handling Unit | 8 | 3000 | 0.28 | 1 | 0.28 | 0 | 0.28 | 0
139 | Mens Locker | 15 | 1 |  |  | 375 | 8 | 8 | Air Handling Unit | 8 | 3000 | 0.3 | 1 | 0.3 | 0 | 0.3 | 0
139 | Mens Locker | 15 | 1 |  |  | 375 | 8 | 8 | Air Handling Unit | 8 | 3000 | 0.3 | 1 | 0.3 | 0 | 0.3 | 0
139 | Mens Locker room |  | 0 |  |  | 375 | 8 | 8 | Air Handling Unit | 8 | 3000 | 0 | 1 | 0 | 0 | 0 | 0
139 | Mens locaker room |  | 0 |  |  | 375 | 8 | 8 | Air Handling Unit | 8 | 3000 | 0 | 1 | 0 | 0 | 0 | 0
140 | office | 48 | 3 |  |  | 300 | 6 | 6 | Air Handling Unit | 8 | 2400 | 1.2 | 1 | 1.2 | 1 | 1.2 | 1
140 | office |  | 0 |  |  | 300 | 6 | 6 | Air Handling Unit | 8 | 2400 | 0 | 1 | 0 | 0 | 0 | 0
141 | toilet room | 9 | 0 |  |  | 90 | 2 | 2 | Air Handling Unit | 8 | 720 | 0.75 | 1 | 0.75 | 0 | 0.75 | 0
141 | toilet room |  | 0 |  |  | 90 | 2 | 2 | Air Handling Unit | 8 | 720 | 0 | 1 | 0 | 0 | 0 | 0
142 | Training room | 20 | 1 |  |  | 375 | 8 | 8 | Air Handling Unit | 8 | 3000 | 0.4 | 1 | 0.4 | 0 | 0.4 | 0
142 | Training room | 22 | 1 |  |  | 375 | 8 | 8 | Air Handling Unit | 8 | 3000 | 0.44 | 1 | 0.44 | 0 | 0.44 | 0
142 | training room |  | 0 |  |  | 375 | 8 | 8 | Air Handling Unit | 8 | 3000 | 0 | 1 | 0 | 0 | 0 | 0
143 | Womens Locker | 14 | 0 |  |  | 750 | 17 | 14 | Air Handling Unit | 8 | 6000 | 0.14 | 1 | 0.14 | 0 | 0.14 | 0
143 | Womens Locker | 14 | 0 |  |  | 750 | 17 | 14 | Air Handling Unit | 8 | 6000 | 0.14 | 1 | 0.14 | 0 | 0.14 | 0
143 | Womens Locker | 15 | 1 |  |  | 750 | 17 | 15 | Air Handling Unit | 8 | 6000 | 0.15 | 1 | 0.15 | 0 | 0.15 | 0
143 | Womens LOcker | 16 | 1 |  |  | 750 | 17 | 16 | Air Handling Unit | 8 | 6000 | 0.16 | 1 | 0.16 | 0 | 0.16 | 0
143 | Womens locker room |  | 0 |  |  | 750 | 17 | 17 | Air Handling Unit | 8 | 6000 | 0 | 1 | 0 | 0 | 0 | 0
143 | Womens locker room |  | 0 |  |  | 750 | 17 | 17 | Air Handling Unit | 8 | 6000 | 0 | 1 | 0 | 0 | 0 | 0
144 | Office | 44 | 2 |  |  | 300 | 6 | 6 | Air Handling Unit | 8 | 2400 | 1.1 | 1 | 1.1 | 1 | 1.1 | 1
144 | office |  | 0 |  |  | 300 | 6 | 6 | Air Handling Unit | 8 | 2400 | 0 | 1 | 0 | 0 | 0 | 0
145 | Toilet Room | 9 | 0 |  |  | 65 | 1 | 1 | Air Handling Unit | 8 | 520 | 1.0385 | 1 | 1.0385 | 1 | 1.0385 | 1
145 | toilet room |  | 0 |  |  | 65 | 1 | 1 | Air Handling Unit | 8 | 520 | 0 | 1 | 0 | 0 | 0 | 0
146 | Corridor | 6 | 0 |  |  | 150 | 3 | 3 | Air Handling Unit | 8 | 1200 | 0.3 | 1 | 0.3 | 0 | 0.3 | 0
146 | corridor |  | 0 |  |  | 150 | 3 | 3 | Air Handling Unit | 8 | 1200 | 0 | 1 | 0 | 0 | 0 | 0
147 | Fitness center | 44 | 2 |  |  | 1545 | 35 | 35 | Air Handling Unit | 8 | 12360 | 0.21359 | 1 | 0.21359 | 0 | 0.21359 | 0
147 | Fitness center | 62 | 4 |  |  | 1545 | 35 | 35 | Air Handling Unit | 8 | 12360 | 0.30097 | 1 | 0.30097 | 0 | 0.30097 | 0
147 | Fitness center | 47 | 3 |  |  | 1545 | 35 | 35 | Air Handling Unit | 8 | 12360 | 0.22816 | 1 | 0.22816 | 0 | 0.22816 | 0
147 | Fitness center |  | 0 |  |  | 1545 | 35 | 35 | Air Handling Unit | 8 | 12360 | 0 | 1 | 0 | 0 | 0 | 0
147 | Fitness center |  | 0 |  |  | 1545 | 35 | 35 | Air Handling Unit | 8 | 12360 | 0 | 1 | 0 | 0 | 0 | 0
147 | Fitness center |  | 0 |  |  | 1545 | 35 | 35 | Air Handling Unit | 8 | 12360 | 0 | 1 | 0 | 0 | 0 | 0
148 | Visitor locker room | 39 | 2 |  |  | 485 | 11 | 11 | Air Handling Unit | 8 | 3880 | 0.60309 | 1 | 0.60309 | 0 | 0.60309 | 0
148 | Visitor locker room | 44 | 2 |  |  | 485 | 11 | 11 | Air Handling Unit | 8 | 3880 | 0.68041 | 1 | 0.68041 | 0 | 0.68041 | 0
148 | visitor locaker room |  | 0 |  |  | 485 | 11 | 11 | Air Handling Unit | 8 | 3880 | 0 | 1 | 0 | 0 | 0 | 0
148 | Visitor locaker room |  | 0 |  |  | 485 | 11 | 11 | Air Handling Unit | 8 | 3880 | 0 | 1 | 0 | 0 | 0 | 0
148 | visitor locker room |  | 0 |  |  | 485 | 11 | 11 | Air Handling Unit | 8 | 3880 | 0 | 1 | 0 | 0 | 0 | 0
149 | IDF | 15 | 1 |  |  | 50 | 1 | 1 | Air Handling Unit | 8 | 400 | 2.25 | 1 | 2.25 | 1 | 2.25 | 1
149 | IDF |  | 0 |  |  | 50 | 1 | 1 | Air Handling Unit | 8 | 400 | 0 | 1 | 0 | 0 | 0 | 0
150 | work shop |  | 0 |  |  | 155 | 3 | 3 | Air Handling Unit | 8 | 1240 | 0 | 1 | 0 | 0 | 0 | 0
151 | Custodial office |  | 0 |  |  | 155 | 3 | 3 | Air Handling Unit | 8 | 1240 | 0 | 1 | 0 | 0 | 0 | 0
152 | Corridor | 34 | 2 |  |  | 2055 | 46 | 34 | Air Handling Unit | 8 | 16440 | 0.12409 | 1 | 0.12409 | 0 | 0.12409 | 0
152 | Corridor | 28 | 1 |  |  | 2055 | 46 | 28 | Air Handling Unit | 8 | 16440 | 0.10219 | 1 | 0.10219 | 0 | 0.10219 | 0
152 | Corridor | 28 | 1 |  |  | 2055 | 46 | 28 | Air Handling Unit | 8 | 16440 | 0.10219 | 1 | 0.10219 | 0 | 0.10219 | 0
155 | Corridor |  | 0 |  |  | 145 | 3 | 3 | Air Handling Unit | 8 | 1160 | 0 | 1 | 0 | 0 | 0 | 0
156 | Locker room |  | 0 |  |  | 60 | 1 | 1 | Air Handling Unit | 8 | 480 | 0 | 1 | 0 | 0 | 0 | 0
158 | Kitchen |  | 0 |  |  | 1485 | 33 | 33 | Air Handling Unit | 8 | 11880 | 0 | 1 | 0 | 0 | 0 | 0
158 | Kitchen |  | 0 |  |  | 1485 | 33 | 33 | Air Handling Unit | 8 | 11880 | 0 | 1 | 0 | 0 | 0 | 0
158 | Kitchen |  | 0 |  |  | 1485 | 33 | 33 | Air Handling Unit | 8 | 11880 | 0 | 1 | 0 | 0 | 0 | 0
158 | Kitchen |  | 0 |  |  | 1485 | 33 | 33 | Air Handling Unit | 8 | 11880 | 0 | 1 | 0 | 0 | 0 | 0
158 | Kitchen |  | 0 |  |  | 1485 | 33 | 33 | Air Handling Unit | 8 | 11880 | 0 | 1 | 0 | 0 | 0 | 0
158 | Kitchen |  | 0 |  |  | 1485 | 33 | 33 | Air Handling Unit | 8 | 11880 | 0 | 1 | 0 | 0 | 0 | 0
158 | Kitchen |  | 0 |  |  | 1485 | 33 | 33 | Air Handling Unit | 8 | 11880 | 0 | 1 | 0 | 0 | 0 | 0
158 | Kitchen |  | 0 |  |  | 1485 | 33 | 33 | Air Handling Unit | 8 | 11880 | 0 | 1 | 0 | 0 | 0 | 0
158 | Kitchen |  | 0 |  |  | 1485 | 33 | 33 | Air Handling Unit | 8 | 11880 | 0 | 1 | 0 | 0 | 0 | 0
158 | Dishwashing |  | 0 |  |  | 390 | 8 | 8 | Air Handling Unit | 8 | 3120 | 0 | 1 | 0 | 0 | 0 | 0
158 | Kitchen |  | 0 |  |  | 1485 | 33 | 33 | Air Handling Unit | 8 | 11880 | 0 | 1 | 0 | 0 | 0 | 0
160 | Dishwashing |  | 0 |  |  | 390 | 8 | 8 | Air Handling Unit | 8 | 3120 | 0 | 1 | 0 | 0 | 0 | 0
161 | Serving |  | 0 |  |  | 695 | 15 | 15 | Air Handling Unit | 8 | 5560 | 0 | 1 | 0 | 0 | 0 | 0
161 | Serving |  | 0 |  |  | 695 | 15 | 15 | Air Handling Unit | 8 | 5560 | 0 | 1 | 0 | 0 | 0 | 0
161 | Serving |  | 0 |  |  | 695 | 15 | 15 | Air Handling Unit | 8 | 5560 | 0 | 1 | 0 | 0 | 0 | 0
162 | Kitchen office |  | 0 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
163 | Cafeteria |  | 0 |  |  | 7850 | 178 | 178 | Air Handling Unit | 8 | 62800 | 0 | 1.4912 | 0 | 0 | 0 | 0
164 | Faculty dining |  | 0 |  |  | 610 | 13 | 13 | Air Handling Unit | 8 | 4880 | 0 | 1 | 0 | 0 | 0 | 0
164 | Faculty dining |  | 0 |  |  | 610 | 13 | 13 | Air Handling Unit | 8 | 4880 | 0 | 1 | 0 | 0 | 0 | 0
166 | Mens Room | 71 | 4 |  |  | 220 | 5 | 5 | Air Handling Unit | 8 | 1760 | 2.4205 | 1 | 2.4205 | 1 | 2.4205 | 1
167 | Womens Room | 50 | 3 |  |  | 245 | 5 | 5 | Air Handling Unit | 8 | 1960 | 1.5306 | 1 | 1.5306 | 1 | 1.5306 | 1
170 | Special Education | 24 | 1 |  |  | 1205 | 27 | 24 | Air Handling Unit | 8 | 9640 | 0.14938 | 1 | 0.14938 | 0 | 0.14938 | 0
170 | Special Education | 21 | 1 |  |  | 1205 | 27 | 21 | Air Handling Unit | 8 | 9640 | 0.13071 | 1 | 0.13071 | 0 | 0.13071 | 0
170 | Special Education | 31 | 2 |  |  | 1205 | 27 | 27 | Air Handling Unit | 8 | 9640 | 0.19295 | 1 | 0.19295 | 0 | 0.19295 | 0
170 | Special Education | 30 | 2 |  |  | 1205 | 27 | 27 | Air Handling Unit | 8 | 9640 | 0.18672 | 1 | 0.18672 | 0 | 0.18672 | 0
173 | Driver education lab | 70 | 4 |  |  | 1200 | 27 | 27 | Air Handling Unit | 8 | 9600 | 0.4375 | 1 | 0.4375 | 0 | 0.4375 | 0
173 | Driver education lab | 70 | 4 |  |  | 1200 | 27 | 27 | Air Handling Unit | 8 | 9600 | 0.4375 | 1 | 0.4375 | 0 | 0.4375 | 0
173 | Driver education lab | 69 | 4 |  |  | 1200 | 27 | 27 | Air Handling Unit | 8 | 9600 | 0.43125 | 1 | 0.43125 | 0 | 0.43125 | 0
173 | Driver education lab | 65 | 4 |  |  | 1200 | 27 | 27 | Air Handling Unit | 8 | 9600 | 0.40625 | 1 | 0.40625 | 0 | 0.40625 | 0
174 | Science Prep | 59 | 3 |  |  | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 2.2125 | 1 | 2.2125 | 1 | 2.2125 | 1
175 | Science Lab | 55 | 3 |  |  | 1505 | 34 | 34 | Air Handling Unit | 8 | 12040 | 0.27409 | 1 | 0.27409 | 0 | 0.27409 | 0
175 | Science LAB | 54 | 3 |  |  | 1505 | 34 | 34 | Air Handling Unit | 8 | 12040 | 0.2691 | 1 | 0.2691 | 0 | 0.2691 | 0
175 | science lab | 47 | 3 |  |  | 1505 | 34 | 34 | Air Handling Unit | 8 | 12040 | 0.23422 | 1 | 0.23422 | 0 | 0.23422 | 0
175 | science lab | 41 | 2 |  |  | 1505 | 34 | 34 | Air Handling Unit | 8 | 12040 | 0.20432 | 1 | 0.20432 | 0 | 0.20432 | 0
175 | science lab | 59 | 3 |  |  | 1505 | 34 | 34 | Air Handling Unit | 8 | 12040 | 0.29402 | 1 | 0.29402 | 0 | 0.29402 | 0
175 | science lab | 63 | 4 |  |  | 1505 | 34 | 34 | Air Handling Unit | 8 | 12040 | 0.31395 | 1 | 0.31395 | 0 | 0.31395 | 0
177 | table storage | 0 | 0 |  |  | 610 | 13 | 0 | Air Handling Unit | 8 | 4880 | 0 | 1 | 0 | 0 | 0 | 0
177 | table storage | 0 | 0 |  |  | 610 | 13 | 0 | Air Handling Unit | 8 | 4880 | 0 | 1 | 0 | 0 | 0 | 0
178 | teacher storage | 0 | 0 |  |  | 125 | 2 | 0 | Air Handling Unit | 8 | 1000 | 0 | 1 | 0 | 0 | 0 | 0
179 | services room | 0 | 0 |  |  | 160 | 3 | 0 | Air Handling Unit | 8 | 1280 | 0 | 1 | 0 | 0 | 0 | 0
180 | IDF closet | 0 | 0 |  |  | 155 | 3 | 0 | Air Handling Unit | 8 | 1240 | 0 | 1 | 0 | 0 | 0 | 0
181 | School store | 0 | 0 |  |  | 200 | 4 | 0 | Air Handling Unit | 8 | 1600 | 0 | 1 | 0 | 0 | 0 | 0
183 | Computer lab |  | 0 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
183 | Computer lab | 374 | 24 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 3.1167 | 1 | 3.1167 | 1 | 3.1167 | 1
183 | Computer lab | 362 | 24 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 3.0167 | 1 | 3.0167 | 1 | 3.0167 | 1
183 | Computer lab | 477 | 31 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 3.975 | 1 | 3.975 | 1 | 3.975 | 1
183 | Computer lab | 477 | 31 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 3.975 | 1 | 3.975 | 1 | 3.975 | 1
184 | Interactive learning center | 667 | 44 |  |  | 2800 | 63 | 63 | Air Handling Unit | 8 | 22400 | 1.7866 | 1.062 | 1.8974 | 1 | 1.8974 | 1
184 | Interactive learning center | 473 | 31 |  |  | 2800 | 63 | 63 | Air Handling Unit | 8 | 22400 | 1.267 | 1.062 | 1.3456 | 1 | 1.3456 | 1
184 | Interactive learning center | 570 | 38 |  |  | 2800 | 63 | 63 | Air Handling Unit | 8 | 22400 | 1.5268 | 1.062 | 1.6215 | 1 | 1.6215 | 1
184 | Interactive learning center | 536 | 35 |  |  | 2800 | 63 | 63 | Air Handling Unit | 8 | 22400 | 1.4357 | 1.062 | 1.5248 | 1 | 1.5248 | 1
184 | Interactive learning center | 417 | 27 |  |  | 2800 | 63 | 63 | Air Handling Unit | 8 | 22400 | 1.117 | 1.062 | 1.1863 | 1 | 1.1863 | 1
185 | Individual reading | 37 | 2 |  |  | 390 | 8 | 8 | Air Handling Unit | 8 | 3120 | 0.71154 | 1 | 0.71154 | 0 | 0.71154 | 0
185 | Individual reading | 32 | 2 |  |  | 390 | 8 | 8 | Air Handling Unit | 8 | 3120 | 0.61538 | 1 | 0.61538 | 0 | 0.61538 | 0
185 | Individual reading | 27 | 1 |  |  | 390 | 8 | 8 | Air Handling Unit | 8 | 3120 | 0.51923 | 1 | 0.51923 | 0 | 0.51923 | 0
185 | Individual reading | 31 | 2 |  |  | 390 | 8 | 8 | Air Handling Unit | 8 | 3120 | 0.59615 | 1 | 0.59615 | 0 | 0.59615 | 0
186 | Literacy Nook | 35 | 2 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.29167 | 1 | 0.29167 | 0 | 0.29167 | 0
186 | Literacy Nook | 28 | 1 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.23333 | 1 | 0.23333 | 0 | 0.23333 | 0
186 | Literacy Nook | 20 | 1 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.16667 | 1 | 0.16667 | 0 | 0.16667 | 0
186 | Literacy Nook | 20 | 1 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.16667 | 1 | 0.16667 | 0 | 0.16667 | 0
186 | Literacy Nook | 20 | 1 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.16667 | 1 | 0.16667 | 0 | 0.16667 | 0
186 | Literacy Nook | 20 | 1 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.16667 | 1 | 0.16667 | 0 | 0.16667 | 0
186 | Literacy Nook | 30 | 2 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.25 | 1 | 0.25 | 0 | 0.25 | 0
186 | Literacy Nook | 14 | 0 |  |  | 900 | 20 | 14 | Air Handling Unit | 8 | 7200 | 0.11667 | 1 | 0.11667 | 0 | 0.11667 | 0
187 | Copy Room | 111 | 7 |  |  | 250 | 5 | 5 | Air Handling Unit | 8 | 2000 | 3.33 | 1 | 3.33 | 1 | 3.33 | 1
187 | Copy Room | 86 | 5 |  |  | 250 | 5 | 5 | Air Handling Unit | 8 | 2000 | 2.58 | 1 | 2.58 | 1 | 2.58 | 1
188 | Conference room | 87 | 5 |  |  | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 3.2625 | 1 | 3.2625 | 1 | 3.2625 | 1
188 | Conferenceroom | 90 | 6 |  |  | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 3.375 | 1 | 3.375 | 1 | 3.375 | 1
189 | Visitor room | 165 | 11 |  |  | 605 | 13 | 13 | Air Handling Unit | 8 | 4840 | 2.0455 | 1 | 2.0455 | 1 | 2.0455 | 1
189 | Visitor room | 202 | 13 |  |  | 605 | 13 | 13 | Air Handling Unit | 8 | 4840 | 2.5041 | 1 | 2.5041 | 1 | 2.5041 | 1
189 | Visitor room | 177 | 11 |  |  | 605 | 13 | 13 | Air Handling Unit | 8 | 4840 | 2.1942 | 1 | 2.1942 | 1 | 2.1942 | 1
190 | ILC office | 120 | 8 |  |  | 135 | 3 | 3 | Air Handling Unit | 8 | 1080 | 6.6667 | 1 | 6.6667 | 2 | 6.6667 | 2
191 | storage | 112 | 7 |  |  | 170 | 3 | 3 | Air Handling Unit | 8 | 1360 | 4.9412 | 1 | 4.9412 | 2 | 4.9412 | 2
192 |  | 1210 | [5 empty] | 1210 | Air Handling Unit
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
192 | School street |  | 0 |  |  | 9910 | 225 | 225 | Air Handling Unit | 8 | 79280 | 0 | 1.4912 | 0 | 0 | 0 | 0
201 | Computer tech |  | 0 |  |  | 1200 | 27 | 27 | Air Handling Unit | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
201 | Computer tech |  | 0 |  |  | 1200 | 27 | 27 | Air Handling Unit | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
201 | Computer tech |  | 0 |  |  | 1200 | 27 | 27 | Air Handling Unit | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
203 | Teachers Copy center |  | 0 |  |  | 300 | 6 | 6 | Air Handling Unit | 8 | 2400 | 0 | 1 | 0 | 0 | 0 | 0
204 | IT Web Design |  | 0 |  |  | 1190 | 27 | 27 | Air Handling Unit | 8 | 9520 | 0 | 1 | 0 | 0 | 0 | 0
204 | IT Web Design |  | 0 |  |  | 1190 | 27 | 27 | Air Handling Unit | 8 | 9520 | 0 | 1 | 0 | 0 | 0 | 0
204 | IT Web Design |  | 0 |  |  | 1190 | 27 | 27 | Air Handling Unit | 8 | 9520 | 0 | 1 | 0 | 0 | 0 | 0
204 | IT Web Design |  | 0 |  |  | 1190 | 27 | 27 | Air Handling Unit | 8 | 9520 | 0 | 1 | 0 | 0 | 0 | 0
204 | IT Web Design |  | 0 |  |  | 1190 | 27 | 27 | Air Handling Unit | 8 | 9520 | 0 | 1 | 0 | 0 | 0 | 0
204 | IT Web Design |  | 0 |  |  | 1190 | 27 | 27 | Air Handling Unit | 8 | 9520 | 0 | 1 | 0 | 0 | 0 | 0
205 | Storage |  | 0 |  |  | 150 | 3 | 3 | Air Handling Unit | 8 | 1200 | 0 | 1 | 0 | 0 | 0 | 0
207 | Clerical |  | 0 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
207 | Clerical |  | 0 |  |  | 100 | 2 | 2 | Air Handling Unit | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
208 | Office |  | 0 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
209 | Roster Room |  | 0 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
210 | [5 empty] | 200 |  | 0 | Air Handling Unit | 8 | 1600 |  | 1 | #VALUE! | #VALUE! | 0
211 | [5 empty] | 200 |  | 0 | Air Handling Unit | 8 | 1600 |  | 1 | #VALUE! | #VALUE! | 0
212 | Staff Room |  | 0 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
213 | Staff Room |  | 0 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
214 | Assistant Principle office |  | 0 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
215 | [5 empty] | 120 |  | 0 | Air Handling Unit | 8 | 960 |  | 1 | #VALUE! | #VALUE! | 0
216 | Rest Room |  | 0 |  |  | 50 | 1 | 1 | Air Handling Unit | 8 | 400 | 0 | 1 | 0 | 0 | 0 | 0
217 | Records |  | 0 |  |  | 300 | 6 | 6 | Air Handling Unit | 8 | 2400 | 0 | 1 | 0 | 0 | 0 | 0
218 | [5 empty] | 120 |  | 0 | Air Handling Unit | 8 | 960 |  | 1 | #VALUE! | #VALUE! | 0
219 | PE Director |  | 0 |  |  | 150 | 3 | 3 | Air Handling Unit | 8 | 1200 | 0 | 1 | 0 | 0 | 0 | 0
220 | [5 empty] | 150 |  | 0 | Air Handling Unit | 8 | 1200 |  | 1 | #VALUE! | #VALUE! | 0
221 | [5 empty] | 120 |  | 0 | Air Handling Unit | 8 | 960 |  | 1 | #VALUE! | #VALUE! | 0
222 | [5 empty] | 120 |  | 0 | Air Handling Unit | 8 | 960 |  | 1 | #VALUE! | #VALUE! | 0
223 | Counselor office |  | 0 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
224 | Success center |  | 0 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
224 | Success center |  | 0 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
224 | Success center |  | 0 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
224 | Success center |  | 0 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
225 | [5 empty] | 450 |  | 0 | Air Handling Unit | 8 | 3600 |  | 1 | #VALUE! | #VALUE! | 0
225 | [5 empty] | 450 |  | 0 | Air Handling Unit | 8 | 3600 |  | 1 | #VALUE! | #VALUE! | 0
226 | Computer flex lab |  | 0 |  |  | 1200 | 27 | 27 | Air Handling Unit | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
226 | Computer flex lab |  | 0 |  |  | 1200 | 27 | 27 | Air Handling Unit | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
226 | Computer flex lab |  | 0 |  |  | 1200 | 27 | 27 | Air Handling Unit | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
226 | Computer flex lab |  | 0 |  |  | 1200 | 27 | 27 | Air Handling Unit | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
227 | General classroom |  | 0 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
227 | General Classroom |  | 0 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
227 | General Classroom |  | 0 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
227 | General Classroom |  | 0 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
228 | Art Storage |  | 0 |  |  | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 0 | 1 | 0 | 0 | 0 | 0
229 | [7 empty] | 0 | Air Handling Unit
230 | Art room |  | 0 |  |  | 1800 | 40 | 40 | Air Handling Unit | 8 | 14400 | 0 | 1 | 0 | 0 | 0 | 0
230 | Art room |  | 0 |  |  | 1800 | 40 | 40 | Air Handling Unit | 8 | 14400 | 0 | 1 | 0 | 0 | 0 | 0
230 | Art room |  | 0 |  |  | 1800 | 40 | 40 | Air Handling Unit | 8 | 14400 | 0 | 1 | 0 | 0 | 0 | 0
230 | Art room |  | 0 |  |  | 1800 | 40 | 40 | Air Handling Unit | 8 | 14400 | 0 | 1 | 0 | 0 | 0 | 0
230 | Art room |  | 0 |  |  | 1800 | 40 | 40 | Air Handling Unit | 8 | 14400 | 0 | 1 | 0 | 0 | 0 | 0
230 | Art room |  | 0 |  |  | 1800 | 40 | 40 | Air Handling Unit | 8 | 14400 | 0 | 1 | 0 | 0 | 0 | 0
231A | [7 empty] | 0 | Air Handling Unit
231A | [7 empty] | 0 | Air Handling Unit
231B | Special education |  | 0 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
231B | Special education |  | 0 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
237 | Mens Room | 57 | 3 |  |  | 250 | 5 | 5 | Air Handling Unit | 8 | 2000 | 1.71 | 1 | 1.71 | 1 | 1.71 | 1
240 | Womens Room | 76 | 5 |  |  | 255 | 5 | 5 | Air Handling Unit | 8 | 2040 | 2.2353 | 1 | 2.2353 | 1 | 2.2353 | 1
241 | Storage | 0 | 0 |  |  | 900 | 20 | 0 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
241 | Storage | 0 | 0 |  |  | 900 | 20 | 0 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
241 | Storage | 0 | 0 |  |  | 900 | 20 | 0 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
241 | Storage | 0 | 0 |  |  | 900 | 20 | 0 | Air Handling Unit | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
242 | chemistry classroom | 53 | 3 |  |  | 1500 | 34 | 34 | Air Handling Unit | 8 | 12000 | 0.265 | 1 | 0.265 | 0 | 0.265 | 0
242 | chemistry classroom | 47 | 3 |  |  | 1500 | 34 | 34 | Air Handling Unit | 8 | 12000 | 0.235 | 1 | 0.235 | 0 | 0.235 | 0
242 | chemistry classroom | 51 | 3 |  |  | 1500 | 34 | 34 | Air Handling Unit | 8 | 12000 | 0.255 | 1 | 0.255 | 0 | 0.255 | 0
242 | chemistry classroom | 56 | 3 |  |  | 1500 | 34 | 34 | Air Handling Unit | 8 | 12000 | 0.28 | 1 | 0.28 | 0 | 0.28 | 0
242 | chemistry classroom | 56 | 3 |  |  | 1500 | 34 | 34 | Air Handling Unit | 8 | 12000 | 0.28 | 1 | 0.28 | 0 | 0.28 | 0
242 | chemistry classroom | 41 | 2 |  |  | 1500 | 34 | 34 | Air Handling Unit | 8 | 12000 | 0.205 | 1 | 0.205 | 0 | 0.205 | 0
243 | Storage | 84 | 5 |  |  | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 3.15 | 1 | 3.15 | 1 | 3.15 | 1
244 | Planning | 72 | 4 |  |  | 290 | 6 | 6 | Air Handling Unit | 8 | 2320 | 1.8621 | 1 | 1.8621 | 1 | 1.8621 | 1
245 | Biology class | 97 | 6 |  |  | 245 | 5 | 5 | Air Handling Unit | 8 | 1960 | 2.9694 | 1 | 2.9694 | 1 | 2.9694 | 1
245 | Biology class | 97 | 6 |  |  | 1290 | 29 | 29 | Air Handling Unit | 8 | 10320 | 0.56395 | 1 | 0.56395 | 0 | 0.56395 | 0
245 | Biology class | 78 | 5 |  |  | 1290 | 29 | 29 | Air Handling Unit | 8 | 10320 | 0.45349 | 1 | 0.45349 | 0 | 0.45349 | 0
245 | Biology class | 83 | 5 |  |  | 1290 | 29 | 29 | Air Handling Unit | 8 | 10320 | 0.48256 | 1 | 0.48256 | 0 | 0.48256 | 0
245 | Biology class | 93 | 6 |  |  | 1290 | 29 | 29 | Air Handling Unit | 8 | 10320 | 0.5407 | 1 | 0.5407 | 0 | 0.5407 | 0
245 | Biology class | 51 | 3 |  |  | 1290 | 29 | 29 | Air Handling Unit | 8 | 10320 | 0.29651 | 1 | 0.29651 | 0 | 0.29651 | 0
246 | General classroom | 67 | 4 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.55833 | 1 | 0.55833 | 0 | 0.55833 | 0
246 | General classroom | 50 | 3 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.41667 | 1 | 0.41667 | 0 | 0.41667 | 0
246 | General classroom | 66 | 4 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.55 | 1 | 0.55 | 0 | 0.55 | 0
246 | General classroom | 63 | 4 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.525 | 1 | 0.525 | 0 | 0.525 | 0
247 | General classroom | 68 | 4 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.56667 | 1 | 0.56667 | 0 | 0.56667 | 0
247 | General classroom | 72 | 4 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.6 | 1 | 0.6 | 0 | 0.6 | 0
247 | General classroom | 69 | 4 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.575 | 1 | 0.575 | 0 | 0.575 | 0
247 | General classroom | 81 | 5 |  |  | 900 | 20 | 20 | Air Handling Unit | 8 | 7200 | 0.675 | 1 | 0.675 | 0 | 0.675 | 0
248 | N/A | 107 | 7 |  |  | 135 | 3 | 3 | Air Handling Unit | 8 | 1080 | 5.9444 | 1 | 5.9444 | 2 | 5.9444 | 2
249 | General classroom | 59 | 3 |  |  | 745 | 16 | 16 | Air Handling Unit | 8 | 5960 | 0.59396 | 1 | 0.59396 | 0 | 0.59396 | 0
249 | General classroom | 62 | 4 |  |  | 745 | 16 | 16 | Air Handling Unit | 8 | 5960 | 0.62416 | 1 | 0.62416 | 0 | 0.62416 | 0
249 | General classroom | 90 | 6 |  |  | 745 | 16 | 16 | Air Handling Unit | 8 | 5960 | 0.90604 | 1 | 0.90604 | 0 | 0.90604 | 0
249 | General classroom | 77 | 5 |  |  | 745 | 16 | 16 | Air Handling Unit | 8 | 5960 | 0.77517 | 1 | 0.77517 | 0 | 0.77517 | 0
250 | General classroom | 68 | 4 |  |  | 795 | 18 | 18 | Air Handling Unit | 8 | 6360 | 0.64151 | 1 | 0.64151 | 0 | 0.64151 | 0
250 | General classroom | 60 | 4 |  |  | 795 | 18 | 18 | Air Handling Unit | 8 | 6360 | 0.56604 | 1 | 0.56604 | 0 | 0.56604 | 0
250 | General classroom | 80 | 5 |  |  | 795 | 18 | 18 | Air Handling Unit | 8 | 6360 | 0.75472 | 1 | 0.75472 | 0 | 0.75472 | 0
250 | General classroom | 83 | 5 |  |  | 795 | 18 | 18 | Air Handling Unit | 8 | 6360 | 0.78302 | 1 | 0.78302 | 0 | 0.78302 | 0
251 | N/A | 173 | 11 |  |  |  | 0 | 0 | Air Handling Unit
252 | General classroom | 57 | 3 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0.53438 | 1 | 0.53438 | 0 | 0.53438 | 0
252 | General classroom | 56 | 3 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0.525 | 1 | 0.525 | 0 | 0.525 | 0
252 | General classroom | 88 | 5 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0.825 | 1 | 0.825 | 0 | 0.825 | 0
252 | General classroom | 79 | 5 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0.74062 | 1 | 0.74062 | 0 | 0.74062 | 0
253 | Corridor | 26 | 1 |  |  | 6010 | 136 | 26 | Air Handling Unit | 8 | 48080 | 0.032446 | 1.062 | 0.034459 | 0 | 0.034459 | 0
253 | Corridor | 25 | 1 |  |  | 6010 | 136 | 25 | Air Handling Unit | 8 | 48080 | 0.031198 | 1.062 | 0.033133 | 0 | 0.033133 | 0
253 | Corridor | 28 | 1 |  |  | 6010 | 136 | 28 | Air Handling Unit | 8 | 48080 | 0.034942 | 1.062 | 0.037109 | 0 | 0.037109 | 0
254 | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
254 | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
254 | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
254 | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
254 | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
301 | General classroom |  | 0 |  |  | 825 | 18 | 18 | Air Handling Unit | 8 | 6600 | 0 | 1 | 0 | 0 | 0 | 0
301 | General classroom |  | 0 |  |  | 825 | 18 | 18 | Air Handling Unit | 8 | 6600 | 0 | 1 | 0 | 0 | 0 | 0
301 | General classroom |  | 0 |  |  | 825 | 18 | 18 | Air Handling Unit | 8 | 6600 | 0 | 1 | 0 | 0 | 0 | 0
301 | General classroom |  | 0 |  |  | 825 | 18 | 18 | Air Handling Unit | 8 | 6600 | 0 | 1 | 0 | 0 | 0 | 0
302 | SPR |  | 0 |  |  | 135 | 3 | 3 | Air Handling Unit | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
303 | General classroom |  | 0 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0 | 1 | 0 | 0 | 0 | 0
305 | SPR |  | 0 |  |  | 135 | 3 | 3 | Air Handling Unit | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
307 | Multi purpose classroom |  | 0 |  |  | 1500 | 34 | 34 | Air Handling Unit | 8 | 12000 | 0 | 1 | 0 | 0 | 0 | 0
307 | Multi purpose classroom |  | 0 |  |  | 1500 | 34 | 34 | Air Handling Unit | 8 | 12000 | 0 | 1 | 0 | 0 | 0 | 0
307 | Multi purpose classroom |  | 0 |  |  | 1500 | 34 | 34 | Air Handling Unit | 8 | 12000 | 0 | 1 | 0 | 0 | 0 | 0
307 | Multi purpose classroom |  | 0 |  |  | 1500 | 34 | 34 | Air Handling Unit | 8 | 12000 | 0 | 1 | 0 | 0 | 0 | 0
307 | Multi purpose classroom |  | 0 |  |  | 1500 | 34 | 34 | Air Handling Unit | 8 | 12000 | 0 | 1 | 0 | 0 | 0 | 0
307 | Multi purpose classroom |  | 0 |  |  | 1500 | 34 | 34 | Air Handling Unit | 8 | 12000 | 0 | 1 | 0 | 0 | 0 | 0
308 | Teacher storage |  | 0 |  |  | 90 | 2 | 2 | Air Handling Unit | 8 | 720 | 0 | 1 | 0 | 0 | 0 | 0
309 | Resource room |  | 0 |  |  | 645 | 14 | 14 | Air Handling Unit | 8 | 5160 | 0 | 1 | 0 | 0 | 0 | 0
309 | Resource room |  | 0 |  |  | 645 | 14 | 14 | Air Handling Unit | 8 | 5160 | 0 | 1 | 0 | 0 | 0 | 0
309 | Resource room |  | 0 |  |  | 645 | 14 | 14 | Air Handling Unit | 8 | 5160 | 0 | 1 | 0 | 0 | 0 | 0
309 | Resource room |  | 0 |  |  | 645 | 14 | 14 | Air Handling Unit | 8 | 5160 | 0 | 1 | 0 | 0 | 0 | 0
315 | Electrical room | 27 | 1 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 1.6875 | 1 | 1.6875 | 1 | 1.6875 | 1
316 | IDF closet | 29 | 1 |  |  | 170 | 3 | 3 | Air Handling Unit | 8 | 1360 | 1.2794 | 1 | 1.2794 | 1 | 1.2794 | 1
317 | Deans Office | 32 | 2 |  |  | 140 | 3 | 3 | Air Handling Unit | 8 | 1120 | 1.7143 | 1 | 1.7143 | 1 | 1.7143 | 1
318 | Mens room | 107 | 7 |  |  | 245 | 5 | 5 | Air Handling Unit | 8 | 1960 | 3.2755 | 1 | 3.2755 | 1 | 3.2755 | 1
321 | Womens Room | 110 | 7 |  |  | 250 | 5 | 5 | Air Handling Unit | 8 | 2000 | 3.3 | 1 | 3.3 | 1 | 3.3 | 1
322 | General classroom | 102 | 6 |  |  | 815 | 18 | 18 | Air Handling Unit | 8 | 6520 | 0.93865 | 1 | 0.93865 | 0 | 0.93865 | 0
322 | General classroom | 105 | 7 |  |  | 815 | 18 | 18 | Air Handling Unit | 8 | 6520 | 0.96626 | 1 | 0.96626 | 0 | 0.96626 | 0
322 | General classroom | 65 | 4 |  |  | 815 | 18 | 18 | Air Handling Unit | 8 | 6520 | 0.59816 | 1 | 0.59816 | 0 | 0.59816 | 0
322 | General classroom | 73 | 4 |  |  | 815 | 18 | 18 | Air Handling Unit | 8 | 6520 | 0.67178 | 1 | 0.67178 | 0 | 0.67178 | 0
323 | Physics classroom | 0 | 0 |  |  | 1575 | 35 | 0 | Air Handling Unit | 8 | 12600 | 0 | 1 | 0 | 0 | 0 | 0
323 | Physics classroom | 0 | 0 |  |  | 1575 | 35 | 0 | Air Handling Unit | 8 | 12600 | 0 | 1 | 0 | 0 | 0 | 0
323 | Physics classroom | 0 | 0 |  |  | 1575 | 35 | 0 | Air Handling Unit | 8 | 12600 | 0 | 1 | 0 | 0 | 0 | 0
323 | Physics classroom | 0 | 0 |  |  | 1575 | 35 | 0 | Air Handling Unit | 8 | 12600 | 0 | 1 | 0 | 0 | 0 | 0
323 | Physics classroom | 0 | 0 |  |  | 1575 | 35 | 0 | Air Handling Unit | 8 | 12600 | 0 | 1 | 0 | 0 | 0 | 0
323 | Physics classroom | 0 | 0 |  |  | 1575 | 35 | 0 | Air Handling Unit | 8 | 12600 | 0 | 1 | 0 | 0 | 0 | 0
324 | Science Prep | 54 | 3 |  |  | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 2.025 | 1 | 2.025 | 1 | 2.025 | 1
324 | Science Prep | 53 | 3 |  |  | 200 | 4 | 4 | Air Handling Unit | 8 | 1600 | 1.9875 | 1 | 1.9875 | 1 | 1.9875 | 1
325 | Physics classroom | 16 | 1 |  |  | 1505 | 34 | 16 | Air Handling Unit | 8 | 12040 | 0.079734 | 1 | 0.079734 | 0 | 0.079734 | 0
325 | Physics classroom | 116 | 7 |  |  | 1505 | 34 | 34 | Air Handling Unit | 8 | 12040 | 0.57807 | 1 | 0.57807 | 0 | 0.57807 | 0
325 | Physics classroom | 14 | 0 |  |  | 1505 | 34 | 14 | Air Handling Unit | 8 | 12040 | 0.069767 | 1 | 0.069767 | 0 | 0.069767 | 0
325 | Physics classroom | 13 | 0 |  |  | 1505 | 34 | 13 | Air Handling Unit | 8 | 12040 | 0.064784 | 1 | 0.064784 | 0 | 0.064784 | 0
325 | Physics classroom | 13 | 0 |  |  | 1505 | 34 | 13 | Air Handling Unit | 8 | 12040 | 0.064784 | 1 | 0.064784 | 0 | 0.064784 | 0
325 | Physics classroom | 14 | 0 |  |  | 1505 | 34 | 14 | Air Handling Unit | 8 | 12040 | 0.069767 | 1 | 0.069767 | 0 | 0.069767 | 0
326 | General classroom | 86 | 5 |  |  | 825 | 18 | 18 | Air Handling Unit | 8 | 6600 | 0.78182 | 1 | 0.78182 | 0 | 0.78182 | 0
326 | General classroom | 85 | 5 |  |  | 825 | 18 | 18 | Air Handling Unit | 8 | 6600 | 0.77273 | 1 | 0.77273 | 0 | 0.77273 | 0
326 | General classroom | 99 | 6 |  |  | 825 | 18 | 18 | Air Handling Unit | 8 | 6600 | 0.9 | 1 | 0.9 | 0 | 0.9 | 0
326 | General classroom | 47 | 3 |  |  | 825 | 18 | 18 | Air Handling Unit | 8 | 6600 | 0.42727 | 1 | 0.42727 | 0 | 0.42727 | 0
327 | General classroom | 64 | 4 |  |  | 795 | 18 | 18 | Air Handling Unit | 8 | 6360 | 0.60377 | 1 | 0.60377 | 0 | 0.60377 | 0
327 | General classroom | 58 | 3 |  |  | 795 | 18 | 18 | Air Handling Unit | 8 | 6360 | 0.54717 | 1 | 0.54717 | 0 | 0.54717 | 0
327 | General classroom | 62 | 4 |  |  | 795 | 18 | 18 | Air Handling Unit | 8 | 6360 | 0.58491 | 1 | 0.58491 | 0 | 0.58491 | 0
327 | General classroom | 43 | 2 |  |  | 795 | 18 | 18 | Air Handling Unit | 8 | 6360 | 0.40566 | 1 | 0.40566 | 0 | 0.40566 | 0
328 | N/A | 159 | 10 |  |  | 135 | 3 | 3 | Air Handling Unit | 8 | 1080 | 8.8333 | 1 | 8.8333 | 2 | 8.8333 | 2
329 | General classroom | 64 | 4 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0.6 | 1 | 0.6 | 0 | 0.6 | 0
329 | General classroom | 59 | 3 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0.55312 | 1 | 0.55312 | 0 | 0.55312 | 0
329 | General classroom | 65 | 4 |  |  | 135 | 3 | 3 | Air Handling Unit | 8 | 1080 | 3.6111 | 1 | 3.6111 | 1 | 3.6111 | 1
329 | General classroom | 68 | 4 |  |  | 800 | 18 | 18 | Air Handling Unit | 8 | 6400 | 0.6375 | 1 | 0.6375 | 0 | 0.6375 | 0
330 | General classroom | 70 | 4 |  |  | 795 | 18 | 18 | Air Handling Unit | 8 | 6360 | 0.66038 | 1 | 0.66038 | 0 | 0.66038 | 0
330 | General classroom | 64 | 4 |  |  | 795 | 18 | 18 | Air Handling Unit | 8 | 6360 | 0.60377 | 1 | 0.60377 | 0 | 0.60377 | 0
330 | General classroom | 74 | 4 |  |  | 795 | 18 | 18 | Air Handling Unit | 8 | 6360 | 0.69811 | 1 | 0.69811 | 0 | 0.69811 | 0
330 | General classroom | 81 | 5 |  |  | 795 | 18 | 18 | Air Handling Unit | 8 | 6360 | 0.76415 | 1 | 0.76415 | 0 | 0.76415 | 0
331 | General classroom | 62 | 4 |  |  | 135 | 3 | 3 | Air Handling Unit | 8 | 1080 | 3.4444 | 1 | 3.4444 | 1 | 3.4444 | 1
331 | General classroom | 69 | 4 |  |  | 135 | 3 | 3 | Air Handling Unit | 8 | 1080 | 3.8333 | 1 | 3.8333 | 1 | 3.8333 | 1
331 | General classroom | 73 | 4 |  |  | 135 | 3 | 3 | Air Handling Unit | 8 | 1080 | 4.0556 | 1 | 4.0556 | 2 | 4.0556 | 2
331 | General classroom | 73 | 4 |  |  | 135 | 3 | 3 | Air Handling Unit | 8 | 1080 | 4.0556 | 1 | 4.0556 | 2 | 4.0556 | 2
333 | Corridor | 79 | 5 |  |  | 5535 | 125 | 79 | Air Handling Unit | 8 | 44280 | 0.10705 | 1.062 | 0.11369 | 0 | 0.11369 | 0
333 | Corridor | 66 | 4 |  |  | 5535 | 125 | 66 | Air Handling Unit | 8 | 44280 | 0.089431 | 1.062 | 0.094979 | 0 | 0.094979 | 0
333 | Corridor | 81 | 5 |  |  | 5535 | 125 | 81 | Air Handling Unit | 8 | 44280 | 0.10976 | 1.062 | 0.11656 | 0 | 0.11656 | 0
360 | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
360 | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
360 | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Corridor | 9 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Vending machines |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Corridor | 28 | 1 |  |  |  | 0 | 0 | Air Handling Unit
- | Corridor | 11 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Kitchen storage |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Gymnasium | 5058 | 337 |  |  |  | 0 | 0 | Air Handling Unit
- | Storage |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Fitness center |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Fitness center |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
Sheet Last Modified: | 2021-04-22
School: | George W. Sharswood Elementary School | House fan Abated
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Building Engineer | 0 | 0 |  |  | 1288 | 29 | 0 | House Fan | 8 | 10304 | 0 | 1 | 0 | 0 | 0 | 0
- | Cafeteria | 0 | 0 | Yes | 20 | 2000 | 45 | 45 | House Fan | 8 | 16000 | 0 | 1 | 0 | 0 | 20 | 3
- | Kitchen Storage | 0 | 0 |  |  | 121 | 2 | 0 | House Fan | 8 | 968 | 0 | 1 | 0 | 0 | 0 | 0
- | Art Room | 1817 | 121 |  |  | 1242 | 28 | 28 | House Fan | 8 | 9936 | 10.9722 | 1 | 10.9722 | 3 | 10.9722 | 3
B9A & B9B | Classroom | 2017 | 134 |  |  | 1242 | 28 | 28 | House Fan | 8 | 9936 | 12.18 | 1 | 12.18 | 3 | 12.18 | 3
- | Gym | 2219 | 147 |  |  | 2160 | 49 | 49 | House Fan | 8 | 17280 | 7.7049 | 1 | 7.7049 | 2 | 7.7049 | 2
- | Main Office | 0 | 0 | Yes | 20 | 552 | 12 | 12 | House Fan | 8 | 4416 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office | 0 | 0 | Yes | 20 | 550 | 12 | 12 | House Fan | 8 | 4400 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Exam | 0 | 0 | Yes | 20 | 299 | 6 | 6 | House Fan | 8 | 2392 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office | 0 | 0 | Yes | 20 | 288 | 6 | 6 | House Fan | 8 | 2304 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom | 1018 | 67 |  |  | 550 | 12 | 12 | House Fan | 8 | 4400 | 13.8818 | 1 | 13.8818 | 3 | 13.8818 | 3
102 | Classroom | 932 | 62 |  |  | 550 | 12 | 12 | House Fan | 8 | 4400 | 12.7091 | 1 | 12.7091 | 3 | 12.7091 | 3
103 | Classroom | 484 | 32 |  |  | 550 | 12 | 12 | House Fan | 8 | 4400 | 6.6 | 1 | 6.6 | 2 | 6.6 | 2
104 | Classroom |  | 0 | Yes | 20 | 276 | 6 | 6 | House Fan | 8 | 2208 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom | 0 | 0 | Yes | 20 | 840 | 19 | 19 | House Fan | 8 | 6720 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom | 0 | 0 | Yes | 20 | 728 | 16 | 16 | House Fan | 8 | 5824 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom | 0 | 0 | Yes | 20 | 728 | 16 | 16 | House Fan | 8 | 5824 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 20 | 728 | 16 | 16 | House Fan | 8 | 5824 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 0 | 0 | Yes | 20 | 713 | 16 | 16 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 20 | 3
114 | Classroom | 0 | 0 | Yes | 20 | 748 | 17 | 17 | House Fan | 8 | 5984 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 0 | 0 |  |  | 2350 | 53 | 0 | House Fan | 8 | 18800 | 0 | 1 | 0 | 0 | 0 | 0
216 | Music Rm | 0 | 0 | Yes | 20 | 1500 | 34 | 34 | House Fan | 8 | 12000 | 0 | 1 | 0 | 0 | 20 | 3
- | Teacher's Lounge | 0 | 0 |  |  | 440 | 10 | 0 | House Fan | 8 | 3520 | 0 | 1 | 0 | 0 | 0 | 0
217 | Classroom | 0 | 0 | Yes | 20 | 644 | 14 | 14 | House Fan | 8 | 5152 | 0 | 1 | 0 | 0 | 20 | 3
219 | Classroom | 0 | 0 | Yes | 20 | 744 | 16 | 16 | House Fan | 8 | 5952 | 0 | 1 | 0 | 0 | 20 | 3
223 | Classroom | 0 | 0 | Yes | 20 | 713 | 16 | 16 | House Fan | 8 | 5704 | 0 | 1 | 0 | 0 | 20 | 3
224 | Classroom | 0 | 0 | Yes | 20 | 684 | 15 | 15 | House Fan | 8 | 5472 | 0 | 1 | 0 | 0 | 20 | 3
225 | Classroom | 695 | 46 |  |  | 684 | 15 | 15 | House Fan | 8 | 5472 | 7.6206 | 1 | 7.6206 | 2 | 7.6206 | 2
226 | Classroom | 881 | 58 |  |  | 684 | 15 | 15 | House Fan | 8 | 5472 | 9.6601 | 1 | 9.6601 | 2 | 9.6601 | 2
227 | Classroom | 429 | 28 |  |  | 684 | 15 | 15 | House Fan | 8 | 5472 | 4.7039 | 1 | 4.7039 | 2 | 4.7039 | 2
228 | Classroom | 0 | 0 | Yes | 20 | 682 | 15 | 15 | House Fan | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
329 | Classroom | 281 | 18 |  |  | 696 | 15 | 15 | House Fan | 8 | 5568 | 3.028 | 1 | 3.028 | 1 | 3.028 | 1
329A | Office | 0 | 0 | Yes | 20 | 120 | 2 | 2 | House Fan | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
330 | Classroom | 811 | 54 |  |  | 696 | 15 | 15 | House Fan | 8 | 5568 | 8.7392 | 1 | 8.7392 | 2 | 8.7392 | 2
331 | Classroom | 276 | 18 |  |  | 696 | 15 | 15 | House Fan | 8 | 5568 | 2.9741 | 1 | 2.9741 | 1 | 2.9741 | 1
332 | Classroom | 0 | 0 | Yes | 20 | 576 | 13 | 13 | House Fan | 8 | 4608 | 0 | 1 | 0 | 0 | 20 | 3
333 | Classroom | 0 | 0 | Yes | 20 | 775 | 17 | 17 | House Fan | 8 | 6200 | 0 | 1 | 0 | 0 | 20 | 3
334 | Classroom | 0 | 0 | Yes | 20 | 783 | 17 | 17 | House Fan | 8 | 6264 | 0 | 1 | 0 | 0 | 20 | 3
335 | Classroom | 0 | 0 | Yes | 20 | 783 | 17 | 17 | House Fan | 8 | 6264 | 0 | 1 | 0 | 0 | 20 | 3
336 | Classroom | 0 | 0 | Yes | 20 | 783 | 17 | 17 | House Fan | 8 | 6264 | 0 | 1 | 0 | 0 | 20 | 3
337 | Classroom | 0 | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
338 | Classroom | 0 | 0 | Yes | 20 | 552 | 12 | 12 | House Fan | 8 | 4416 | 0 | 1 | 0 | 0 | 20 | 3
339 | Classroom | 368 | 24 |  |  | 672 | 15 | 15 | House Fan | 8 | 5376 | 4.1071 | 1 | 4.1071 | 2 | 4.1071 | 2
340 | Classroom | 326 | 21 |  |  | 576 | 13 | 13 | House Fan | 8 | 4608 | 4.2448 | 1 | 4.2448 | 2 | 4.2448 | 2
341 | Classroom | 156 | 10 |  |  | 576 | 13 | 10 | House Fan | 8 | 4608 | 2.0312 | 1 | 2.0312 | 1 | 2.0312 | 1
341A | Classroom | 0 | 0 |  |  | 120 | 2 | 0 | House Fan | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
342A | Classroom | 0 | 0 |  |  | 288 | 6 | 0 | House Fan | 8 | 2304 | 0 | 1 | 0 | 0 | 0 | 0
342B | Classroom | 0 | 0 | Yes | 20 | 432 | 9 | 9 | House Fan | 8 | 3456 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-26
School: | Shawmont Elementary-Middle School
Vendor: | EMCOR Fluidics | Retest | 2nd Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | CLASS | 0 | 0 | Yes | 20 | 1033 | 23 | 23 | Univent | 8 | 8264 | 0 | 1 | 0 | 0 | 20 | 3
103 | CLASS | 323 | 21 |  |  | 687 | 15 | 15 | Univent | 8 | 5496 | 3.5262 | 1 | 3.5262 | 1 | 3.5262 | 1
104 | CLASS | 337 | 22 |  |  | 568 | 12 | 12 | Univent | 8 | 4544 | 4.4498 | 1 | 4.4498 | 2 | 4.4498 | 2
105 | Office | 0 | 0 | Yes | 20 | 359 | 8 | 8 |  | 8 | 2872 | 0 | 1 | 0 | 0 | 20 | 3
106 | CLASS | 336 | 22 |  |  | 687 | 15 | 15 | Univent | 8 | 5496 | 3.6681 | 1 | 3.6681 | 1 | 3.6681 | 1
107 | CLASS | 327 | 21 |  |  | 705 | 16 | 16 | Univent | 8 | 5640 | 3.4787 | 1 | 3.4787 | 1 | 3.4787 | 1
108 | CLASS | 308 | 20 |  |  | 750 | 17 | 17 | Univent | 8 | 6000 | 3.08 | 1 | 3.08 | 1 | 3.08 | 1
201 | CLASS | 312 | 20 |  |  | 670 | 15 | 15 | Univent | 8 | 5360 | 3.4925 | 1 | 3.4925 | 1 | 3.4925 | 1
202 | CLASS | 323 | 21 |  |  | 536 | 12 | 12 | Univent | 8 | 4288 | 4.5196 | 1 | 4.5196 | 2 | 4.5196 | 2
203 | CLASS | 372 | 24 |  |  | 794 | 18 | 18 | Univent | 8 | 6352 | 3.5139 | 1 | 3.5139 | 1 | 3.5139 | 1
204 | CLASS | 273 | 18 |  |  | 794 | 18 | 18 | Univent | 8 | 6352 | 2.5787 | 1 | 2.5787 | 1 | 2.5787 | 1
205 | Therapy | 340 | 22 |  |  | 370 | 8 | 8 | Univent | 8 | 2960 | 6.8919 | 1 | 6.8919 | 2 | 6.8919 | 2
206 | CLASS | 325 | 21 |  |  | 670 | 15 | 15 | Univent | 8 | 5360 | 3.6381 | 1 | 3.6381 | 1 | 3.6381 | 1
207 | CLASS | 222 | 14 | Yes | 20 | 675 | 15 | 15 | Univent | 8 | 5400 | 2.4667 | 1 | 2.4667 | 1 | 22.4667 | 3
208 | CLASS | 272 | 18 |  |  | 675 | 15 | 15 | Univent | 8 | 5400 | 3.0222 | 1 | 3.0222 | 1 | 3.0222 | 1
209 | CLASS | 252 | 16 |  |  | 670 | 15 | 15 | Univent | 8 | 5360 | 2.8209 | 1 | 2.8209 | 1 | 2.8209 | 1
300 | CLASS | 281 | 18 |  |  | 503 | 11 | 11 | Univent | 8 | 4024 | 4.1899 | 1 | 4.1899 | 2 | 4.1899 | 2
301 | CLASS | 312 | 20 |  |  | 690 | 15 | 15 | Univent | 8 | 5520 | 3.3913 | 1 | 3.3913 | 1 | 3.3913 | 1
302 | CLASS | 287 | 19 |  |  | 704 | 16 | 16 | Univent | 8 | 5632 | 3.0575 | 1 | 3.0575 | 1 | 3.0575 | 1
303 | CLASS | 276 | 18 |  |  | 695 | 15 | 15 | Univent | 8 | 5560 | 2.9784 | 1 | 2.9784 | 1 | 2.9784 | 1
304 | CLASS | 371 | 24 |  |  | 797 | 18 | 18 | Univent | 8 | 6376 | 3.4912 | 1 | 3.4912 | 1 | 3.4912 | 1
305 | Office | 96 | 6 | Yes | 20 | 448 | 10 | 10 | Univent | 8 | 3584 | 1.6071 | 1 | 1.6071 | 1 | 21.6071 | 3
305-A | Classroom | 313 | 20 |  |  | 814 | 18 | 18 | Univent | 8 | 6512 | 2.8839 | 1 | 2.8839 | 1 | 2.8839 | 1
306 | CLASS | 296 | 19 |  |  | 675 | 15 | 15 | Univent | 8 | 5400 | 3.2889 | 1 | 3.2889 | 1 | 3.2889 | 1
307 | CLASS | 279 | 18 |  |  | 675 | 15 | 15 | Univent | 8 | 5400 | 3.1 | 1 | 3.1 | 1 | 3.1 | 1
308 | CLASS | 0 | 0 | Yes | 20 | 695 | 15 | 15 | Univent | 8 | 5560 | 0 | 1 | 0 | 0 | 20 | 3
309 | CLASS | 370 | 24 |  |  | 690 | 15 | 15 | Univent | 8 | 5520 | 4.0217 | 1 | 4.0217 | 2 | 4.0217 | 2
310 | CLASS | 275 | 18 | Yes | 20 | 1103 | 25 | 25 | Univent | 8 | 8824 | 1.8699 | 1 | 1.8699 | 1 | 21.8699 | 3
311 | CLASS | 292 | 19 |  |  | 935 | 21 | 19 | Univent | 8 | 7480 | 2.3422 | 1 | 2.3422 | 1 | 2.3422 | 1
312 | CLASS | 0 | 0 | Yes | 20 | 1039 | 23 | 23 | Univent | 8 | 8312 | 0 | 1 | 0 | 0 | 20 | 3
313 | CLASS | 0 | 0 | Yes | 20 | 1036 | 23 | 23 | Univent | 8 | 8288 | 0 | 1 | 0 | 0 | 20 | 3
314 | CLASS | 433 | 28 |  |  | 1012 | 23 | 23 | Univent | 8 | 8096 | 3.209 | 1 | 3.209 | 1 | 3.209 | 1
315 | CLASS | 388 | 25 |  |  | 1184 | 26 | 25 | Univent | 8 | 9472 | 2.4578 | 1 | 2.4578 | 1 | 2.4578 | 1
- | AUDITORIUM | 1331 | 88 |  |  | 3193 | 72 | 72 | Air Handling Unit | 8 | 25544 | 3.1264 | 1.062 | 3.3203 | 1 | 3.3203 | 1
- | BAND RM | 0 | 0 | Yes | 20 | 934 | 21 | 21 | Univent | 8 | 7472 | 0 | 1 | 0 | 0 | 20 | 3
- | COMPUTER LAB | 0 | 0 | Yes | 20 | 1103 | 25 | 25 | Univent | 8 | 8824 | 0 | 1 | 0 | 0 | 20 | 3
- | GYM | 5749 | 383 | Yes | 20 | 2610 | 59 | 59 | Air Handling Unit | 8 | 20880 | 16.5201 | 1.062 | 17.5449 | 3 | 37.5449 | 4
- | LIBRARY | 750 | 50 |  |  | 1804 | 41 | 41 | Univent | 8 | 14432 | 3.1181 | 1 | 3.1181 | 1 | 3.1181 | 1
B-1 | Strings Room | 343 | 22 |  |  | 641 | 14 | 14 | Univent | 8 | 5128 | 4.0133 | 1 | 4.0133 | 2 | 4.0133 | 2
B-2 | Music Room | 0 | 0 | Yes | 20 | 518 | 11 | 11 | Univent | 8 | 4144 | 0 | 1 | 0 | 0 | 20 | 3
B-3 | Band Room | 396 | 26 |  |  | 153 | 3 | 3 | Univent | 8 | 1224 | 19.4118 | 1 | 19.4118 | 3 | 19.4118 | 3
B-4 | Band Room | 281 | 18 |  |  | 940 | 21 | 18 | Univent | 8 | 7520 | 2.242 | 1 | 2.242 | 1 | 2.242 | 1
B-6 | Classroom | 395 | 26 |  |  | 803 | 18 | 18 | Univent | 8 | 6424 | 3.6893 | 1 | 3.6893 | 1 | 3.6893 | 1
- | Cafeteria | 1132 | 75 |  |  | 4090 | 92 | 75 | Univent | 8 | 32720 | 2.0758 | 1.062 | 2.2046 | 1 | 2.2046 | 1
- | Staff Lounge | 0 | 0 | Yes | 20 | 364 | 8 | 8 | Univent | 8 | 2912 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse |  | 0 | Yes | 20 | 287 | 6 | 6 |  | 8 | 2296 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 20 | 210 | 4 | 4 |  | 8 | 1680 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 379 | 8 | 8 |  | 8 | 3032 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-06
School: | Isaac A. Sheppard Elementary School
Vendor: | EMCOR Fluidics | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 661 | 44 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 6.4551 | 1 | 6.4551 | 2 | 6.4551 | 2
101 | Classroom | 894 | 59 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 9.8314 | 1 | 9.8314 | 2 | 9.8314 | 2
102 | Classroom | 910 | 60 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 10.0073 | 1 | 10.0073 | 3 | 10.0073 | 3
103 | Classroom | 578 | 38 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 6.3563 | 1 | 6.3563 | 2 | 6.3563 | 2
200 | Classroom | 665 | 44 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.0845 | 1 | 7.0845 | 2 | 7.0845 | 2
201 | Classroom | 595 | 39 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.3388 | 1 | 6.3388 | 2 | 6.3388 | 2
202 | Classroom | 1004 | 66 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 11.0411 | 1 | 11.0411 | 3 | 11.0411 | 3
203 | Classroom | 951 | 63 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 10.4582 | 1 | 10.4582 | 3 | 10.4582 | 3
204 | Classroom | 949 | 63 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 10.4362 | 1 | 10.4362 | 3 | 10.4362 | 3
205 | Classroom | 661 | 44 |  |  | 682 | 15 | 15 | House Fan | 8 | 5456 | 7.2691 | 1 | 7.2691 | 2 | 7.2691 | 2
206 | Classroom | 844 | 56 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 8.9915 | 1 | 8.9915 | 2 | 8.9915 | 2
300 | Classroom | 840 | 56 |  |  | 875 | 19 | 19 | House Fan | 8 | 7000 | 7.2 | 1 | 7.2 | 2 | 7.2 | 2
301 | Classroom | 717 | 47 |  |  | 875 | 19 | 19 | House Fan | 8 | 7000 | 6.1457 | 1 | 6.1457 | 2 | 6.1457 | 2
302 | Classroom | 963 | 64 |  |  | 836 | 19 | 19 | House Fan | 8 | 6688 | 8.6394 | 1 | 8.6394 | 2 | 8.6394 | 2
303 | Classroom | 762 | 50 |  |  | 836 | 19 | 19 | House Fan | 8 | 6688 | 6.8361 | 1 | 6.8361 | 2 | 6.8361 | 2
304 | Classroom | 998 | 66 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 10.6321 | 1 | 10.6321 | 3 | 10.6321 | 3
305 | Classroom | 847 | 56 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 9.0234 | 1 | 9.0234 | 2 | 9.0234 | 2
306 | Classroom | 636 | 42 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.7756 | 1 | 6.7756 | 2 | 6.7756 | 2
- | Auditorium | 1843 | 122 |  |  | 1176 | 26 | 26 | House Fan | 8 | 9408 | 11.7538 | 1 | 11.7538 | 3 | 11.7538 | 3
Main Office | Office |  | 0 | Yes | 20 | 255 | 5 | 5 | Air Purifier | 8 | 2040 | 0 | 1 | 0 | 0 | 20 | 3
Nurse Office | Office |  | 0 | Yes | 20 | 122 | 2 | 2 | Air Purifier | 8 | 976 | 0 | 1 | 0 | 0 | 20 | 3
Principal Office | Office |  | 0 | Yes | 20 | 183 | 4 | 4 | Air Purifier | 8 | 1464 | 0 | 1 | 0 | 0 | 20 | 3
- | Library | 1317 | 87 |  |  | 851 | 19 | 19 | House Fan | 8 | 6808 | 11.6069 | 1 | 11.6069 | 3 | 11.6069 | 3
- | Lunch Room/Cafeteria | 1498 | 99 |  |  | 1311 | 29 | 29 | House Fan | 8 | 10488 | 8.5698 | 1 | 8.5698 | 2 | 8.5698 | 2
- | Server Room | 0 | 0 |  |  | 0 | 0 | 0 | Minisplit Air Handling Unit | 8 | 0 | #DIV/0! | 1 | #DIV/0! | #DIV/0! | #DIV/0!
Sheet Last Modified: | 2021-04-07
School: | Philip Sheridan Elementary School
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Room | 0 | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
102 | Room | 1116 | 74 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 10.8984 | 1 | 10.8984 | 3 | 10.8984 | 3
103 | Room | 921 | 61 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 8.9941 | 1 | 8.9941 | 2 | 8.9941 | 2
104 | Room | 749 | 49 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 7.8021 | 1 | 7.8021 | 2 | 7.8021 | 2
105 | Room | 693 | 46 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 7.2188 | 1 | 7.2188 | 2 | 7.2188 | 2
106 | Classroom | 1006 | 67 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 9.8242 | 1 | 9.8242 | 2 | 9.8242 | 2
107 | Classroom | 0 | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom | 0 | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom | 861 | 57 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 8.4082 | 1 | 8.4082 | 2 | 8.4082 | 2
110 | Classroom | 376 | 25 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 3.6719 | 1 | 3.6719 | 1 | 3.6719 | 1
Main Office | Office |  | 0 | Yes | 20 | 448 | 10 | 10 | House Fan | 8 | 3584 | 0 | 1 | 0 | 0 | 20 | 3
110 | Principal office | 597 | 39 |  |  | 216 | 4 | 4 | House Fan | 8 | 1728 | 20.7292 | 1 | 20.7292 | 3 | 20.7292 | 3
111 | Nurse | 0 | 0 | Yes | 20 | 312 | 7 | 7 | House Fan | 8 | 2496 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 0 | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 877 | 58 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 8.5645 | 1 | 8.5645 | 2 | 8.5645 | 2
203 | Classroom | 981 | 65 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 10.2188 | 1 | 10.2188 | 3 | 10.2188 | 3
204 | Classroom | 760 | 50 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 7.9167 | 1 | 7.9167 | 2 | 7.9167 | 2
205 | Classroom | 737 | 49 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 7.6771 | 1 | 7.6771 | 2 | 7.6771 | 2
206 | Classroom | 999 | 66 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 9.7559 | 1 | 9.7559 | 2 | 9.7559 | 2
207 | Classroom | 0 | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom | 0 | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom | 1162 | 77 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 11.3477 | 1 | 11.3477 | 3 | 11.3477 | 3
209.5 | Office |  | 0 | Yes | 20 | 220 | 5 | 5 | House Fan | 8 | 1760 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom | 926 | 61 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 9.043 | 1 | 9.043 | 2 | 9.043 | 2
210.5 | Office |  | 0 |  |  | 220 | 5 | 0 | House Fan | 8 | 1760 | 0 | 1 | 0 | 0 | 0 | 0
211 | Classroom | 0 | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom | 1253 | 83 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 12.2363 | 1 | 12.2363 | 3 | 12.2363 | 3
303 | Classroom | 1038 | 69 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 10.8125 | 1 | 10.8125 | 3 | 10.8125 | 3
304 | Classroom | 746 | 49 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 7.7708 | 1 | 7.7708 | 2 | 7.7708 | 2
305 | Classroom | 811 | 54 |  |  | 720 | 16 | 16 | House Fan | 8 | 5760 | 8.4479 | 1 | 8.4479 | 2 | 8.4479 | 2
306 | Classroom | 1007 | 67 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 9.834 | 1 | 9.834 | 2 | 9.834 | 2
307 | Classroom | 0 | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
308 | Classroom | 0 | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
309 | Classroom | 894 | 59 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 8.7305 | 1 | 8.7305 | 2 | 8.7305 | 2
310 | Classroom | 1334 | 88 |  |  | 768 | 17 | 17 | House Fan | 8 | 6144 | 13.0273 | 1 | 13.0273 | 3 | 13.0273 | 3
311 | Classroom | 0 | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
- | Basement East Side |  | 0 |  |  | 567 | 12 | 0 | House Fan | 8 | 4536 | 0 | 1 | 0 | 0 | 0 | 0
- | Basement West Side |  | 0 |  |  | 567 | 12 | 0 | House Fan | 8 | 4536 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-19
School: | SLA @ Beeber
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom |  | 0 |  |  | 1200 | 27 | 0 |  | 8 | 9600 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom |  | 0 |  |  | 1150 | 26 | 0 |  | 8 | 9200 | 0 | 1 | 0 | 0 | 0 | 0
102 | Classroom |  | 0 |  |  | 925 | 21 | 0 |  | 8 | 7400 | 0 | 1 | 0 | 0 | 0 | 0
102A | Classroom |  | 0 |  |  | 720 | 16 | 0 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom |  | 0 |  |  | 1636 | 37 | 0 |  | 8 | 13088 | 0 | 1 | 0 | 0 | 0 | 0
104 | Classroom |  | 0 |  |  | 875 | 19 | 0 |  | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom |  | 0 |  |  | 909 | 20 | 0 |  | 8 | 7272 | 0 | 1 | 0 | 0 | 0 | 0
106 | Classroom |  | 0 | Yes | 20 | 966 | 21 | 21 |  | 8 | 7728 | 0 | 1 | 0 | 0 | 20 | 3
106A | Classroom |  | 0 | Yes | 20 | 610 | 13 | 13 |  | 8 | 4880 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 |  |  | 912 | 20 | 0 |  | 8 | 7296 | 0 | 1 | 0 | 0 | 0 | 0
107A | Classroom |  | 0 |  |  | 720 | 16 | 0 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
107B | Classroom |  | 0 |  |  | 360 | 8 | 0 |  | 8 | 2880 | 0 | 1 | 0 | 0 | 0 | 0
108 | Classroom |  | 0 |  |  | 912 | 20 | 0 |  | 8 | 7296 | 0 | 1 | 0 | 0 | 0 | 0
109 | Classroom |  | 0 |  |  | 700 | 15 | 0 |  | 8 | 5600 | 0 | 1 | 0 | 0 | 0 | 0
200 | Classroom |  | 0 | Yes | 20 | 638 | 14 | 14 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
201 | Office |  | 0 | Yes | 20 | 187 | 4 | 4 |  | 8 | 1496 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 1128 | 25 | 25 |  | 8 | 9024 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 |  |  | 1128 | 25 | 0 |  | 8 | 9024 | 0 | 1 | 0 | 0 | 0 | 0
203A | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
203B | Classroom |  | 0 | Yes | 20 | 360 | 8 | 8 |  | 8 | 2880 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 | Yes | 20 | 664 | 15 | 15 |  | 8 | 5312 | 0 | 1 | 0 | 0 | 20 | 3
204A | Nurse office |  | 0 |  |  | 187 | 4 | 0 |  | 8 | 1496 | 0 | 1 | 0 | 0 | 0 | 0
205 | Office |  | 0 | Yes | 20 | 360 | 8 | 8 |  | 8 | 2880 | 0 | 1 | 0 | 0 | 20 | 3
206-208 | Office |  | 0 |  |  | 996 | 22 | 0 |  | 8 | 7968 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office |  | 0 | Yes | 20 | 335 | 7 | 7 |  | 8 | 2680 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 |  |  | 660 | 15 | 0 |  | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
Secretary | Office |  | 0 | Yes | 20 |  | 0 | 0
Conference Room | Conference Room |  | 0 | Yes | 20 |  | 0 | 0
Cafeteria | Cafeteria |  | 0 |  |  | 7014 | 159 | 0 |  | 8 | 56112 | 0 | 1.4912 | 0 | 0 | 0 | 0
209-210 | Library |  | 0 | Yes | 20 | 1872 | 42 | 42 |  | 8 | 14976 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom |  | 0 |  |  | 984 | 22 | 0 |  | 8 | 7872 | 0 | 1 | 0 | 0 | 0 | 0
212 | Classroom |  | 0 |  |  | 720 | 16 | 0 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 0 | 0
213-214 | Classroom |  | 0 |  |  | 1518 | 34 | 0 |  | 8 | 12144 | 0 | 1 | 0 | 0 | 0 | 0
214A-B | Classroom |  | 0 |  |  | 1021 | 23 | 0 |  | 8 | 8168 | 0 | 1 | 0 | 0 | 0 | 0
215 | Office |  | 0 |  |  | 187 | 4 | 0 |  | 8 | 1496 | 0 | 1 | 0 | 0 | 0 | 0
216 | Classroom |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
217 | Classroom |  | 0 |  |  | 816 | 18 | 0 |  | 8 | 6528 | 0 | 1 | 0 | 0 | 0 | 0
218 | Classroom |  | 0 | Yes | 20 | 744 | 16 | 16 |  | 8 | 5952 | 0 | 1 | 0 | 0 | 20 | 3
219 | Classroom |  | 0 | Yes | 20 | 768 | 17 | 17 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
220 | Classroom |  | 0 | Yes | 20 | 768 | 17 | 17 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
221 | Classroom |  | 0 | Yes | 20 | 768 | 17 | 17 |  | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
222 | Classroom |  | 0 | Yes | 20 | 816 | 18 | 18 |  | 8 | 6528 | 0 | 1 | 0 | 0 | 20 | 3
223 | Classroom |  | 0 | Yes | 20 |  | 0 | 0
224 | Classroom |  | 0 | Yes | 20 |  | 0 | 0
316 | Office |  | 0 |  |  | 187 | 4 | 0 |  | 8 | 1496 | 0 | 1 | 0 | 0 | 0 | 0
317 | Classroom |  | 0 |  |  | 665 | 15 | 0 |  | 8 | 5320 | 0 | 1 | 0 | 0 | 0 | 0
318 | Classroom |  | 0 |  |  | 836 | 19 | 0 |  | 8 | 6688 | 0 | 1 | 0 | 0 | 0 | 0
319-320 | Classroom |  | 0 |  |  | 1488 | 33 | 0 |  | 8 | 11904 | 0 | 1 | 0 | 0 | 0 | 0
321 | Classroom |  | 0 |  |  | 749 | 17 | 0 |  | 8 | 5992 | 0 | 1 | 0 | 0 | 0 | 0
322 | Classroom |  | 0 |  |  | 766 | 17 | 0 |  | 8 | 6128 | 0 | 1 | 0 | 0 | 0 | 0
323 | Classroom |  | 0 |  |  | 808 | 18 | 0 |  | 8 | 6464 | 0 | 1 | 0 | 0 | 0 | 0
324 | Classroom |  | 0 |  |  | 668 | 15 | 0 |  | 8 | 5344 | 0 | 1 | 0 | 0 | 0 | 0
300 | Office |  | 0 |  |  | 187 | 4 | 0 |  | 8 | 1496 | 0 | 1 | 0 | 0 | 0 | 0
301-303 | Classroom |  | 0 | Yes | 20 | 2072 | 47 | 47 |  | 8 | 16576 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
303A-B | Classroom |  | 0 | Yes | 20 | 1072 | 24 | 24 |  | 8 | 8576 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom |  | 0 | Yes | 20 | 1009 | 22 | 22 |  | 8 | 8072 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom |  | 0 |  |  | 989 | 22 | 0 |  | 8 | 7912 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom |  | 0 |  |  | 1001 | 22 | 0 |  | 8 | 8008 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom |  | 0 |  |  | 1361 | 30 | 0 |  | 8 | 10888 | 0 | 1 | 0 | 0 | 0 | 0
308 | Office |  | 0 |  |  | 200 | 4 | 0 |  | 8 | 1600 | 0 | 1 | 0 | 0 | 0 | 0
309-310 | Classroom |  | 0 | Yes | 20 | 2085 | 47 | 47 |  | 8 | 16680 | 0 | 1 | 0 | 0 | 20 | 3
311 | Office |  | 0 | Yes | 20 | 651 | 14 | 14 |  | 8 | 5208 | 0 | 1 | 0 | 0 | 20 | 3
312 | Office |  | 0 |  |  | 300 | 6 | 0 |  | 8 | 2400 | 0 | 1 | 0 | 0 | 0 | 0
313-315 | Classroom |  | 0 |  |  | 2227 | 50 | 0 |  | 8 | 17816 | 0 | 1 | 0 | 0 | 0 | 0
314A | Classroom |  | 0 |  |  | 1126 | 25 | 0 |  | 8 | 9008 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-23
School: | Solis-Cohen Elementary School
Vendor: | Chadwick | Main Exhaust | Main Exhaust Part 2
School: | Solis-Cohen Elementary School- Little School House
Vendor: | Chadwick | Chadwick Part 2 | Chadwick Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Solis-Cohen Main Building
- | Main Office |  | 0 |  |  | 120 | 2 | 0 | N/A | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
1 | classroom |  | 0 |  |  | 914 | 20 | 0 | N/A | 8 | 7312 | 0 | 1 | 0 | 0 | 0 | 0
2 | classroom |  | 0 |  |  | 914 | 20 | 0 | N/A | 8 | 7312 | 0 | 1 | 0 | 0 | 0 | 0
3 | Classroom |  | 0 |  |  | 914 | 20 | 0 | N/A | 8 | 7312 | 0 | 1 | 0 | 0 | 0 | 0
4 | classroom |  | 0 |  |  | 914 | 20 | 0 | N/A | 8 | 7312 | 0 | 1 | 0 | 0 | 0 | 0
5 | classroom |  | 0 |  |  | 914 | 20 | 0 | N/A | 8 | 7312 | 0 | 1 | 0 | 0 | 0 | 0
6 | classroom |  | 0 |  |  | 731 | 16 | 0 | N/A | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
7 | classroom |  | 0 |  |  | 731 | 16 | 0 | N/A | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
8 | classroom |  | 0 |  |  | 731 | 16 | 0 | N/A | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
9 | classroom |  | 0 |  |  | 731 | 16 | 0 | N/A | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
9A | classroom |  | 0 |  |  | 731 | 16 | 0 | N/A | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
10 | classroom |  | 0 |  |  | 731 | 16 | 0 | N/A | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
11 | classroom |  | 0 |  |  | 731 | 16 | 0 | N/A | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
12 | classroom |  | 0 |  |  | 731 | 16 | 0 | N/A | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
13 | classroom |  | 0 |  |  | 731 | 16 | 0 | N/A | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
14 | classroom |  | 0 |  |  | 731 | 16 | 0 | N/A | 8 | 5848 | 0 | 1 | 0 | 0 | 0 | 0
26 | Classroom |  | 0 |  |  | 914 | 20 | 0 | N/A | 8 | 7312 | 0 | 1 | 0 | 0 | 0 | 0
27 | Classroom |  | 0 |  |  | 914 | 20 | 0 | N/A | 8 | 7312 | 0 | 1 | 0 | 0 | 0 | 0
- | Esol Room |  | 0 |  |  | 806 | 18 | 0 | N/A | 8 | 6448 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurses Office |  | 0 |  |  | 1116 | 25 | 0 | N/A | 8 | 8928 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym |  | 0 |  |  | 5355 | 121 | 0 | N/A | 8 | 42840 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria |  | 0 |  |  | 2660 | 60 | 0 | N/A | 8 | 21280 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Auditorium |  | 0 |  |  | 5036 | 114 | 0 | N/A | 8 | 40288 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Counselors Office A |  | 0 |  |  | 352 | 8 | 0 | N/A | 8 | 2816 | 0 | 1 | 0 | 0 | 0 | 0
- | Counselors Office B |  | 0 |  |  | 352 | 8 | 0 | N/A | 8 | 2816 | 0 | 1 | 0 | 0 | 0 | 0
Solis-Cohen LSH
100B | Lobby | 88 | 5 |  |  | 196 | 4 | 4 | Air Handling Unit | 8 | 1568 | 3.3673 | 1 | 3.3673 | 1 | 3.3673 | 1
101A | Reception Office | 30 | 2 |  |  | 256 | 5 | 2 | Air Handling Unit | 8 | 2048 | 0.87891 | 1 | 0.87891 | 0 | 0.87891 | 0
101B | Clerical Office | 56 | 3 |  |  | 336 | 7 | 3 | Air Handling Unit | 8 | 2688 | 1.25 | 1 | 1.25 | 1 | 1.25 | 1
101C | Asst. Principals Office | 32 | 2 |  |  | 598 | 13 | 2 | Air Handling Unit | 8 | 4784 | 0.40134 | 1 | 0.40134 | 0 | 0.40134 | 0
101D | Nurses Office | 32 | 2 |  |  | 256 | 5 | 2 | Air Handling Unit | 8 | 2048 | 0.9375 | 1 | 0.9375 | 0 | 0.9375 | 0
102 | Classroom | 287 | 19 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 2.5087 | 1 | 2.5087 | 1 | 2.5087 | 1
103 | Classroom | 276 | 18 |  |  | 858 | 19 | 18 | Univent | 8 | 6864 | 2.4126 | 1 | 2.4126 | 1 | 2.4126 | 1
104 | Classroom | 276 | 18 |  |  | 858 | 19 | 18 | Univent | 8 | 6864 | 2.4126 | 1 | 2.4126 | 1 | 2.4126 | 1
105 | Classroom | 292 | 19 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 2.5524 | 1 | 2.5524 | 1 | 2.5524 | 1
106 | Classroom | 280 | 18 |  |  | 858 | 19 | 18 | Univent | 8 | 6864 | 2.4476 | 1 | 2.4476 | 1 | 2.4476 | 1
107 | Classroom | 274 | 18 |  |  | 858 | 19 | 18 | Univent | 8 | 6864 | 2.3951 | 1 | 2.3951 | 1 | 2.3951 | 1
108 | Classroom | 275 | 18 |  |  | 858 | 19 | 18 | Univent | 8 | 6864 | 2.4038 | 1 | 2.4038 | 1 | 2.4038 | 1
110 | Faculty Dining | 45 | 3 |  |  | 640 | 14 | 3 | Air Handling Unit | 8 | 5120 | 0.52734 | 1 | 0.52734 | 0 | 0.52734 | 0
121 | Classroom | 282 | 18 |  |  | 1092 | 24 | 18 | Univent | 8 | 8736 | 1.9368 | 1 | 1.9368 | 1 | 1.9368 | 1
122 | Classroom | 289 | 19 |  |  | 1092 | 24 | 19 | Univent | 8 | 8736 | 1.9849 | 1 | 1.9849 | 1 | 1.9849 | 1
123 | Classroom | 290 | 19 |  |  | 1092 | 24 | 19 | Univent | 8 | 8736 | 1.9918 | 1 | 1.9918 | 1 | 1.9918 | 1
124 | Classroom | 292 | 19 |  |  | 1092 | 24 | 19 | Univent | 8 | 8736 | 2.0055 | 1 | 2.0055 | 1 | 2.0055 | 1
125 | Classroom | 320 | 21 |  |  | 598 | 13 | 13 | Univent | 8 | 4784 | 4.0134 | 1 | 4.0134 | 2 | 4.0134 | 2
126 | Classroom | 287 | 19 |  |  | 1092 | 24 | 19 | Univent | 8 | 8736 | 1.9712 | 1 | 1.9712 | 1 | 1.9712 | 1
- | Lunch Room |  | 0 | Yes | 20 | 2160 | 49 | 49 | Air Handling Unit | 8 | 17280 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-30
School: | South Philly HS
Vendor: | Meehan (Auditoriums) | EMCOR (School) | Chadwick Retest
Vendor: | EMCOR (Gym) | EMCOR Retest 2 | EMCOR Retest 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Pre Engineering Shop Class A | 0 | 0 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
- | Pre Engineering Shop Class B | 281 | 18 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
- | Computer Lab | 296 | 19 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
004A | Engineering Tech. | 308 | 20 |  |  | 1716 | 39 | 20 | Nesbitt Unit Ventilator | 8 | 13728 | 1.3462 | 1 | 1.3462 | 1 | 1.3462 | 1
004B | Engineering Tech. | 0 | 0 |  |  | 880 | 20 | 0 | Nesbitt Unit Ventilator | 8 | 7040 | 0 | 1 | 0 | 0 | 0 | 0
004C | Engineering Tech. | 313 | 20 |  |  | 2640 | 60 | 20 | Nesbitt Unit Ventilator | 8 | 21120 | 0.8892 | 1.062 | 0.94437 | 0 | 0.94437 | 0
- | Cafeteria | 7225 | 481 |  |  | 11200 | 254 | 254 | Nesbitt Unit Ventilator | 8 | 89600 | 4.8382 | 1.4912 | 7.2145 | 2 | 7.2145 | 2
- | Cafeteria | 5887 | 392 |  |  |  | 0 | 0 | Air Handling Unit
- | Culinary Kitchen Hood MAU | 0 | 0 |  |  |  | 0 | 0 | Make-up Air Unit
- | Cafeteria Kitchen Hood | 4929 | 328 |  |  |  | 0 | 0 | Cafeteria Kitchen Hood
005A | Room | 0 | 0 |  |  | 2204 | 50 | 0 | Nesbitt Unit Ventilator | 8 | 17632 | 0 | 1 | 0 | 0 | 0 | 0
005B | Room | 0 | 0 |  |  | 984 | 22 | 0 | Nesbitt Unit Ventilator | 8 | 7872 | 0 | 1 | 0 | 0 | 0 | 0
- | General Office A | 461 | 30 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
- | General Office B | 394 | 26 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
100 | Room | 384 | 25 |  |  | 1100 | 25 | 25 | Nesbitt Unit Ventilator | 8 | 8800 | 2.6182 | 1 | 2.6182 | 1 | 2.6182 | 1
101 | Room | 345 | 23 |  |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5520 | 3.75 | 1 | 3.75 | 1 | 3.75 | 1
104 | Room | 276 | 18 |  |  | 620 | 14 | 14 | Nesbitt Unit Ventilator | 8 | 4960 | 3.3387 | 1 | 3.3387 | 1 | 3.3387 | 1
105A | Room | 0 | 0 |  |  | 2709 | 61 | 0 | Nesbitt Unit Ventilator | 8 | 21672 | 0 | 1.062 | 0 | 0 | 0 | 0
105B | Room | 207 | 13 |  |  | 260 | 5 | 5 | Nesbitt Unit Ventilator | 8 | 2080 | 5.9712 | 1 | 5.9712 | 2 | 5.9712 | 2
106 | Room | 400 | 26 |  |  | 667 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5336 | 4.4978 | 1 | 4.4978 | 2 | 4.4978 | 2
108A | Room | 0 | 0 |  |  | 2280 | 51 | 0 | Nesbitt Unit Ventilator | 8 | 18240 | 0 | 1 | 0 | 0 | 0 | 0
108B | Room | 386 | 25 |  |  | 528 | 12 | 12 | Nesbitt Unit Ventilator | 8 | 4224 | 5.483 | 1 | 5.483 | 2 | 5.483 | 2
108C | Room | 417 | 27 |  |  | 276 | 6 | 6 | Nesbitt Unit Ventilator | 8 | 2208 | 11.3315 | 1 | 11.3315 | 3 | 11.3315 | 3
109 | Room | 0 | 0 |  |  | 812 | 18 | 0 | Nesbitt Unit Ventilator | 8 | 6496 | 0 | 1 | 0 | 0 | 0 | 0
- | Studio 1 | 308 | 20 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
- | Studio 2 | 419 | 27 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
- | Community Closet | 352 | 23 |  |  | 899 | 20 | 20 | Nesbitt Unit Ventilator | 8 | 7192 | 2.9366 | 1 | 2.9366 | 1 | 2.9366 | 1
200 | Room | 371 | 24 |  |  | 840 | 19 | 19 |  | 8 | 6720 | 3.3125 | 1 | 3.3125 | 1 | 3.3125 | 1
201 | Room | 363 | 24 |  |  | 1008 | 22 | 22 | Nesbitt Unit Ventilator | 8 | 8064 | 2.7009 | 1 | 2.7009 | 1 | 2.7009 | 1
202 | Room | 465 | 31 |  |  | 1247 | 28 | 28 | Nesbitt Unit Ventilator | 8 | 9976 | 2.7967 | 1 | 2.7967 | 1 | 2.7967 | 1
203 | Room | 278 | 18 |  |  | 579 | 13 | 13 | Nesbitt Unit Ventilator | 8 | 4632 | 3.601 | 1 | 3.601 | 1 | 3.601 | 1
204 | Room | 549 | 36 |  |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5520 | 5.9674 | 1 | 5.9674 | 2 | 5.9674 | 2
205A | Room | 0 | 0 |  |  | 86.25 | 1 | 0 | Nesbitt Unit Ventilator | 8 | 690 | 0 | 1 | 0 | 0 | 0 | 0
205B | Room | 415 | 27 |  |  | 150 | 3 | 3 | Nesbitt Unit Ventilator | 8 | 1200 | 20.75 | 1 | 20.75 | 3 | 20.75 | 3
206 | Room | 479 | 31 |  |  | 705 | 16 | 16 | Nesbitt Unit Ventilator | 8 | 5640 | 5.0957 | 1 | 5.0957 | 2 | 5.0957 | 2
207 | Room | 426 | 28 |  |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5520 | 4.6304 | 1 | 4.6304 | 2 | 4.6304 | 2
208 | Room | 373 | 24 |  |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5520 | 4.0543 | 1 | 4.0543 | 2 | 4.0543 | 2
209 | Room | 419 | 27 |  |  | 242 | 5 | 5 | Nesbitt Unit Ventilator | 8 | 1936 | 12.9855 | 1 | 12.9855 | 3 | 12.9855 | 3
210 | Room | 297 | 19 |  |  | 900 | 20 | 19 | Nesbitt Unit Ventilator | 8 | 7200 | 2.475 | 1 | 2.475 | 1 | 2.475 | 1
211 | Room | 320 | 21 |  |  | 690 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5520 | 3.4783 | 1 | 3.4783 | 1 | 3.4783 | 1
214A | Music Room | 350 | 23 |  |  | 2142 | 48 | 23 | Nesbitt Unit Ventilator | 8 | 17136 | 1.2255 | 1 | 1.2255 | 1 | 1.2255 | 1
214B | Music Room | 323 | 21 |  |  | 170 | 3 | 3 | Nesbitt Unit Ventilator | 8 | 1360 | 14.25 | 1 | 14.25 | 3 | 14.25 | 3
217A | Room | 382 | 25 |  |  | 2560 | 58 | 25 | Nesbitt Unit Ventilator | 8 | 20480 | 1.1191 | 1.062 | 1.1886 | 1 | 1.1886 | 1
217B | Room | 411 | 27 |  |  | 1312 | 29 | 27 | Nesbitt Unit Ventilator | 8 | 10496 | 2.3495 | 1 | 2.3495 | 1 | 2.3495 | 1
219A | Room | 367 | 24 |  |  | 899 | 20 | 20 | Nesbitt Unit Ventilator | 8 | 7192 | 3.0617 | 1 | 3.0617 | 1 | 3.0617 | 1
220 | Room | 380 | 25 |  |  | 667 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5336 | 4.2729 | 1 | 4.2729 | 2 | 4.2729 | 2
221A | Room | 320 | 21 |  |  | 1984 | 45 | 21 | Nesbitt Unit Ventilator | 8 | 15872 | 1.2097 | 1 | 1.2097 | 1 | 1.2097 | 1
221B | Room | 279 | 18 |  |  | 127.5 | 2 | 2 | Nesbitt Unit Ventilator | 8 | 1020 | 16.4118 | 1 | 16.4118 | 3 | 16.4118 | 3
222A | Room | 329 | 21 |  |  | 1705 | 38 | 21 | Nesbitt Unit Ventilator | 8 | 13640 | 1.4472 | 1 | 1.4472 | 1 | 1.4472 | 1
222B | Room | 286 | 19 |  |  | 110.5 | 2 | 2 | Nesbitt Unit Ventilator | 8 | 884 | 19.4118 | 1 | 19.4118 | 3 | 19.4118 | 3
223A | Room | 259 | 17 |  |  | 1519 | 34 | 17 | Nesbitt Unit Ventilator | 8 | 12152 | 1.2788 | 1 | 1.2788 | 1 | 1.2788 | 1
223B | Room | 217 | 14 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
- | Culinary Arts A | 0 | 0 |  |  | 130.5 | 2 | 0 | Nesbitt Unit Ventilator | 8 | 1044 | 0 | 1 | 0 | 0 | 0 | 0
- | Culinary Arts B | 0 | 0 |  |  | 215 | 4 | 0 | Nesbitt Unit Ventilator | 8 | 1720 | 0 | 1 | 0 | 0 | 0 | 0
300A | Room | 0 | 0 |  |  | 112 | 2 | 0 | Nesbitt Unit Ventilator | 8 | 896 | 0 | 1 | 0 | 0 | 0 | 0
300B | Room | 367 | 24 |  |  | 149 | 3 | 3 | Nesbitt Unit Ventilator | 8 | 1192 | 18.4732 | 1 | 18.4732 | 3 | 18.4732 | 3
301 | Room | 416 | 27 |  |  | 1207 | 27 | 27 | Nesbitt Unit Ventilator | 8 | 9656 | 2.5849 | 1 | 2.5849 | 1 | 2.5849 | 1
302 | Room | 393 | 26 |  |  | 1167 | 26 | 26 | Nesbitt Unit Ventilator | 8 | 9336 | 2.5257 | 1 | 2.5257 | 1 | 2.5257 | 1
303 | Room | 338 | 22 |  |  | 875 | 19 | 19 | Nesbitt Unit Ventilator | 8 | 7000 | 2.8971 | 1 | 2.8971 | 1 | 2.8971 | 1
304A | Room | 413 | 27 |  |  | 193 | 4 | 4 | Nesbitt Unit Ventilator | 8 | 1544 | 16.0492 | 1 | 16.0492 | 3 | 16.0492 | 3
304B | Room | 427 | 28 |  |  | 1027 | 23 | 23 | Nesbitt Unit Ventilator | 8 | 8216 | 3.1183 | 1 | 3.1183 | 1 | 3.1183 | 1
305A | Room | 371 | 24 |  |  | 259 | 5 | 5 | Nesbitt Unit Ventilator | 8 | 2072 | 10.7432 | 1 | 10.7432 | 3 | 10.7432 | 3
305B | Room | 365 | 24 |  |  | 140 | 3 | 3 | Nesbitt Unit Ventilator | 8 | 1120 | 19.5536 | 1 | 19.5536 | 3 | 19.5536 | 3
306A | Room | 358 | 23 |  |  | 193 | 4 | 4 | Nesbitt Unit Ventilator | 8 | 1544 | 13.9119 | 1 | 13.9119 | 3 | 13.9119 | 3
306B | Room | 310 | 20 |  |  | 948 | 21 | 20 | Nesbitt Unit Ventilator | 8 | 7584 | 2.4525 | 1 | 2.4525 | 1 | 2.4525 | 1
307A | Room | 298 | 19 |  |  | 959 | 21 | 19 | Nesbitt Unit Ventilator | 8 | 7672 | 2.3306 | 1 | 2.3306 | 1 | 2.3306 | 1
308 | Library A | 322 | 21 |  |  | 6124 | 139 | 21 | Nesbitt Unit Ventilator | 8 | 48992 | 0.39435 | 1.062 | 0.41881 | 0 | 0.41881 | 0
308 | Library B | 429 | 28 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
308 | Library C | 381 | 25 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
308 | Library Office | 361 | 24 |  |  | 84 | 1 | 1 | Nesbitt Unit Ventilator | 8 | 672 | 32.2321 | 1 | 32.2321 | 4 | 32.2321 | 4
308 | Library Archive Room | 0 | 0 |  |  | 360 | 8 | 0 | Nesbitt Unit Ventilator | 8 | 2880 | 0 | 1 | 0 | 0 | 0 | 0
311A | Room | 347 | 23 |  |  | 973 | 22 | 22 | Nesbitt Unit Ventilator | 8 | 7784 | 2.6747 | 1 | 2.6747 | 1 | 2.6747 | 1
311B | Room | 374 | 24 |  |  | 1054 | 23 | 23 | Nesbitt Unit Ventilator | 8 | 8432 | 2.6613 | 1 | 2.6613 | 1 | 2.6613 | 1
313B | Room | 0 | 0 |  |  | 526 | 11 | 0 | Nesbitt Unit Ventilator | 8 | 4208 | 0 | 1 | 0 | 0 | 0 | 0
316 | Room | 686 | 45 |  |  | 722 | 16 | 16 | Nesbitt Unit Ventilator | 8 | 5776 | 7.126 | 1 | 7.126 | 2 | 7.126 | 2
400A | Room | 314 | 20 |  |  | 203 | 4 | 4 | Nesbitt Unit Ventilator | 8 | 1624 | 11.601 | 1 | 11.601 | 3 | 11.601 | 3
400B | Room | 208 | 13 |  |  | 1092 | 24 | 13 | Nesbitt Unit Ventilator | 8 | 8736 | 1.4286 | 1 | 1.4286 | 1 | 1.4286 | 1
401A | Room | 342 | 22 |  |  | 878 | 19 | 19 | Nesbitt Unit Ventilator | 8 | 7024 | 2.9214 | 1 | 2.9214 | 1 | 2.9214 | 1
401B | Room | 318 | 21 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
402A | Room | 0 | 0 |  |  | 894 | 20 | 0 | Nesbitt Unit Ventilator | 8 | 7152 | 0 | 1 | 0 | 0 | 0 | 0
402B | Room | 296 | 19 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
403A | Room | 0 | 0 |  |  | 994 | 22 | 0 | Nesbitt Unit Ventilator | 8 | 7952 | 0 | 1 | 0 | 0 | 0 | 0
403B | Room | 307 | 20 |  |  | 458 | 10 | 10 |  | 8 | 3664 | 5.0273 | 1 | 5.0273 | 2 | 5.0273 | 2
404A | Room | 0 | 0 |  |  | 952 | 21 | 0 | Nesbitt Unit Ventilator | 8 | 7616 | 0 | 1 | 0 | 0 | 0 | 0
404B | Room | 297 | 19 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
405A | Room | 306 | 20 |  |  | 893 | 20 | 20 | Nesbitt Unit Ventilator | 8 | 7144 | 2.57 | 1 | 2.57 | 1 | 2.57 | 1
405B | Room | 0 | 0 |  |  |  | 0 | 0 | Nesbitt Unit Ventilator
406 | Room | 339 | 22 |  |  | 708 | 16 | 16 | Nesbitt Unit Ventilator | 8 | 5664 | 3.5911 | 1 | 3.5911 | 1 | 3.5911 | 1
407 | Room | 298 | 19 |  |  | 715 | 16 | 16 | Nesbitt Unit Ventilator | 8 | 5720 | 3.1259 | 1 | 3.1259 | 1 | 3.1259 | 1
408 | Room | 321 | 21 |  |  | 708 | 16 | 16 | Nesbitt Unit Ventilator | 8 | 5664 | 3.4004 | 1 | 3.4004 | 1 | 3.4004 | 1
409 | Room | 278 | 18 |  |  | 675 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5400 | 3.0889 | 1 | 3.0889 | 1 | 3.0889 | 1
410 | Room | 288 | 19 |  |  | 694 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5552 | 3.1124 | 1 | 3.1124 | 1 | 3.1124 | 1
411 | Room | 333 | 22 |  |  | 707 | 16 | 16 | Nesbitt Unit Ventilator | 8 | 5656 | 3.5325 | 1 | 3.5325 | 1 | 3.5325 | 1
412 | Room | 276 | 18 |  |  | 701 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5608 | 2.9529 | 1 | 2.9529 | 1 | 2.9529 | 1
412A | Room | 222 | 14 |  |  | 471 | 10 | 10 | Nesbitt Unit Ventilator | 8 | 3768 | 3.535 | 1 | 3.535 | 1 | 3.535 | 1
413 | Room | 284 | 18 |  |  | 711 | 16 | 16 | Nesbitt Unit Ventilator | 8 | 5688 | 2.9958 | 1 | 2.9958 | 1 | 2.9958 | 1
414 | Room | 0 | 0 |  |  | 580 | 13 | 0 | Nesbitt Unit Ventilator | 8 | 4640 | 0 | 1 | 0 | 0 | 0 | 0
415 | Room | 416 | 27 |  |  | 691 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5528 | 4.5152 | 1 | 4.5152 | 2 | 4.5152 | 2
416 | Room | 337 | 22 |  |  | 660 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5280 | 3.8295 | 1 | 3.8295 | 1 | 3.8295 | 1
417 | Room | 349 | 23 |  |  | 694 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5552 | 3.7716 | 1 | 3.7716 | 1 | 3.7716 | 1
418 | Room | 343 | 22 |  |  | 698 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5584 | 3.6855 | 1 | 3.6855 | 1 | 3.6855 | 1
418A | Room | 277 | 18 |  |  | 341 | 7 | 7 | Nesbitt Unit Ventilator | 8 | 2728 | 6.0924 | 1 | 6.0924 | 2 | 6.0924 | 2
419A | Room | 0 | 0 |  |  | 1126 | 25 | 0 | Nesbitt Unit Ventilator | 8 | 9008 | 0 | 1 | 0 | 0 | 0 | 0
419B | Room | 0 | 0 |  |  | 135 | 3 | 0 | Nesbitt Unit Ventilator | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
420A | Room | 322 | 21 |  |  | 1082 | 24 | 21 | Nesbitt Unit Ventilator | 8 | 8656 | 2.232 | 1 | 2.232 | 1 | 2.232 | 1
420B | Room | 337 | 22 |  |  | 85 | 1 | 1 | Nesbitt Unit Ventilator | 8 | 680 | 29.7353 | 1 | 29.7353 | 4 | 29.7353 | 4
421 | Room | 328 | 21 |  |  | 673 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5384 | 3.6553 | 1 | 3.6553 | 1 | 3.6553 | 1
422 | Room | 343 | 22 |  |  | 673 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5384 | 3.8224 | 1 | 3.8224 | 1 | 3.8224 | 1
423 | Room | 322 | 21 |  |  | 673 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5384 | 3.5884 | 1 | 3.5884 | 1 | 3.5884 | 1
424 | Room | 272 | 18 |  |  | 705 | 16 | 16 | Nesbitt Unit Ventilator | 8 | 5640 | 2.8936 | 1 | 2.8936 | 1 | 2.8936 | 1
425 | Room | 310 | 20 |  |  | 706 | 16 | 16 | Nesbitt Unit Ventilator | 8 | 5648 | 3.2932 | 1 | 3.2932 | 1 | 3.2932 | 1
426 | Room | 285 | 19 |  |  | 681 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5448 | 3.1388 | 1 | 3.1388 | 1 | 3.1388 | 1
427 | Room | 295 | 19 |  |  | 670 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5360 | 3.3022 | 1 | 3.3022 | 1 | 3.3022 | 1
428 | Room | 400 | 26 |  |  | 681 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5448 | 4.4053 | 1 | 4.4053 | 2 | 4.4053 | 2
429 | Room | 309 | 20 |  |  | 716 | 16 | 16 | Nesbitt Unit Ventilator | 8 | 5728 | 3.2367 | 1 | 3.2367 | 1 | 3.2367 | 1
432 | Room | 972 | 64 |  |  | 664 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5312 | 10.9789 | 1 | 10.9789 | 3 | 10.9789 | 3
433 | Room | 401 | 26 |  |  | 705 | 16 | 16 | Nesbitt Unit Ventilator | 8 | 5640 | 4.266 | 1 | 4.266 | 2 | 4.266 | 2
434 | Room | 544 | 36 |  |  | 677 | 15 | 15 | Nesbitt Unit Ventilator | 8 | 5416 | 6.0266 | 1 | 6.0266 | 2 | 6.0266 | 2
435 | Room | 503 | 33 |  |  | 705 | 16 | 16 | Nesbitt Unit Ventilator | 8 | 5640 | 5.3511 | 1 | 5.3511 | 2 | 5.3511 | 2
500 | Classroom | 0 | 0 |  |  | 937 | 21 | 0 | Nesbitt Unit Ventilator | 8 | 7496 | 0 | 1 | 0 | 0 | 0 | 0
500A | Classroom | 0 | 0 |  |  | 36 | 0 | 0 | Univent | 8 | 288 | 0 | 1 | 0 | 0 | 0 | 0
500B | Classroom | 158 | 10 |  |  |  | 0 | 0 | Univent
501 A | Classroom | 0 | 0 |  |  | 845 | 19 | 0 | Univent | 8 | 6760 | 0 | 1 | 0 | 0 | 0 | 0
501 B | Classroom | 351 | 23 |  |  |  | 0 | 0 | Univent
502 A | Classroom | 208 | 13 |  |  | 969 | 22 | 13 | Univent | 8 | 7752 | 1.6099 | 1 | 1.6099 | 1 | 1.6099 | 1
502 B | Classroom | 266 | 17 |  |  |  | 0 | 0 | Univent
503 A | Classroom | 157 | 10 |  |  | 1035 | 23 | 10 | Univent | 8 | 8280 | 1.1377 | 1 | 1.1377 | 1 | 1.1377 | 1
503 B | Classroom | 67 | 4 |  |  | 200 | 4 | 4 | Univent | 8 | 1600 | 2.5125 | 1 | 2.5125 | 1 | 2.5125 | 1
504 A | Classroom | 330 | 22 |  |  | 982 | 22 | 22 | Univent | 8 | 7856 | 2.5204 | 1 | 2.5204 | 1 | 2.5204 | 1
504 B | Classroom | 160 | 10 |  |  |  | 0 | 0 | Univent
505 A | Classroom |  | 0 |  |  | 942 | 21 | 0 | Univent | 8 | 7536 | 0 | 1 | 0 | 0 | 0 | 0
505 B | Classroom |  | 0 |  |  |  | 0 | 0 | Univent
506 | Classroom | 320 | 21 |  |  | 690 | 15 | 15 | Univent | 8 | 5520 | 3.4783 | 1 | 3.4783 | 1 | 3.4783 | 1
507 | Classroom | 212 | 14 |  |  | 690 | 15 | 14 | Univent | 8 | 5520 | 2.3043 | 1 | 2.3043 | 1 | 2.3043 | 1
508 | Classroom | 0 | 0 |  |  | 690 | 15 | 0 | Univent | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
509 | Classroom | 192 | 12 |  |  | 690 | 15 | 12 | Univent | 8 | 5520 | 2.087 | 1 | 2.087 | 1 | 2.087 | 1
510 A | Classroom | 183 | 12 |  |  | 990 | 22 | 12 | Univent | 8 | 7920 | 1.3864 | 1 | 1.3864 | 1 | 1.3864 | 1
510 B | Classroom | 353 | 23 |  |  | 102 | 2 | 2 | Univent | 8 | 816 | 25.9559 | 1 | 25.9559 | 4 | 25.9559 | 4
511 | Classroom | 286 | 19 |  |  | 690 | 15 | 15 | Univent | 8 | 5520 | 3.1087 | 1 | 3.1087 | 1 | 3.1087 | 1
512 | Classroom | 159 | 10 |  |  | 690 | 15 | 10 | Univent | 8 | 5520 | 1.7283 | 1 | 1.7283 | 1 | 1.7283 | 1
513 | Classroom | 183 | 12 |  |  | 690 | 15 | 12 | Univent | 8 | 5520 | 1.9891 | 1 | 1.9891 | 1 | 1.9891 | 1
514 | Classroom | 182 | 12 |  |  | 690 | 15 | 12 | Univent | 8 | 5520 | 1.9783 | 1 | 1.9783 | 1 | 1.9783 | 1
515 | Classroom | 205 | 13 |  |  | 690 | 15 | 13 | Univent | 8 | 5520 | 2.2283 | 1 | 2.2283 | 1 | 2.2283 | 1
516 | Classroom | 65 | 4 |  |  | 713 | 16 | 4 | Univent | 8 | 5704 | 0.68373 | 1 | 0.68373 | 0 | 0.68373 | 0
517 | Classroom | 334 | 22 |  |  | 552 | 12 | 12 | Univent | 8 | 4416 | 4.538 | 1 | 4.538 | 2 | 4.538 | 2
518 | Classroom | 0 | 0 |  |  | 713 | 16 | 0 | Univent | 8 | 5704 | 0 | 1 | 0 | 0 | 0 | 0
519 | Classroom | 177 | 11 |  |  | 616 | 14 | 11 | Univent | 8 | 4928 | 2.155 | 1 | 2.155 | 1 | 2.155 | 1
520 | Classroom | 196 | 13 |  |  | 616 | 14 | 13 | Univent | 8 | 4928 | 2.3864 | 1 | 2.3864 | 1 | 2.3864 | 1
521 | Classroom | 155 | 10 |  |  | 616 | 14 | 10 | Univent | 8 | 4928 | 1.8872 | 1 | 1.8872 | 1 | 1.8872 | 1
522 | Classroom | 0 | 0 |  |  | 616 | 14 | 0 | Univent | 8 | 4928 | 0 | 1 | 0 | 0 | 0 | 0
523 | Classroom | 153 | 10 |  |  | 705 | 16 | 10 | Univent | 8 | 5640 | 1.6277 | 1 | 1.6277 | 1 | 1.6277 | 1
524 | Classroom | 63 | 4 |  |  | 690 | 15 | 4 | Univent | 8 | 5520 | 0.68478 | 1 | 0.68478 | 0 | 0.68478 | 0
525 | Classroom | 76 | 5 |  |  | 690 | 15 | 5 | Univent | 8 | 5520 | 0.82609 | 1 | 0.82609 | 0 | 0.82609 | 0
526 | Classroom | 0 | 0 |  |  | 690 | 15 | 0 | Univent | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
527 | Classroom | 167 | 11 |  |  | 690 | 15 | 11 | Univent | 8 | 5520 | 1.8152 | 1 | 1.8152 | 1 | 1.8152 | 1
528 | Classroom | 223 | 14 |  |  | 690 | 15 | 14 | Univent | 8 | 5520 | 2.4239 | 1 | 2.4239 | 1 | 2.4239 | 1
529 | Classroom | 0 | 0 |  |  | 690 | 15 | 0 | Univent | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
530 | Classroom | 0 | 0 |  |  | 690 | 15 | 0 | Univent | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
531 | Classroom | 4 | 0 |  |  | 690 | 15 | 0 | Univent | 8 | 5520 | 0.043478 | 1 | 0.043478 | 0 | 0.043478 | 0
532 | Classroom | 0 | 0 |  |  | 705 | 16 | 0 | Univent | 8 | 5640 | 0 | 1 | 0 | 0 | 0 | 0
533 | Classroom | 163 | 10 |  |  | 705 | 16 | 10 | Univent | 8 | 5640 | 1.734 | 1 | 1.734 | 1 | 1.734 | 1
534 | Classroom | 0 | 0 |  |  | 705 | 16 | 0 | Univent | 8 | 5640 | 0 | 1 | 0 | 0 | 0 | 0
535 | Classroom | 380 | 25 |  |  | 705 | 16 | 16 | Univent | 8 | 5640 | 4.0426 | 1 | 4.0426 | 2 | 4.0426 | 2
- | Auditorium | 10918 | 727 |  |  | 11536 | 262 | 262 | Nesbitt Unit Ventilator | 8 | 92288 | 7.0982 | 1.4912 | 10.5846 | 3 | 10.5846 | 3
- | Gym | 24019 | 1601 |  |  | 20384 | 463 | 463 | Air Handling Unit | 8 | 163072 | 8.8374 | 2.3523 | 20.7887 | 3 | 20.7887 | 3
Sheet Last Modified: | 2021-05-03
School: | Southwark Elementary School
Vendor: | Devine | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B4 | Office | 0 | 0 | Yes | 20 | 952 | 21 | 21 | House Fan | 8 | 7616 | 0 | 1 | 0 | 0 | 20 | 3
B5 | Music Room | 1241 | 82 |  |  | 1800 | 40 | 40 | House Fan | 8 | 14400 | 5.1708 | 1 | 5.1708 | 2 | 5.1708 | 2
B20 | Basement | 584 | 38 |  |  | 960 | 21 | 21 | House Fan | 8 | 7680 | 4.5625 | 1 | 4.5625 | 2 | 4.5625 | 2
B21 | Basement | 515 | 34 |  |  | 1728 | 39 | 34 | House Fan | 8 | 13824 | 2.2352 | 1 | 2.2352 | 1 | 2.2352 | 1
102 | First Floor | 532 | 35 |  |  | 528 | 12 | 12 | House Fan | 8 | 4224 | 7.5568 | 1 | 7.5568 | 2 | 7.5568 | 2
103 | First Floor | 268 | 17 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 3.0455 | 1 | 3.0455 | 1 | 3.0455 | 1
107 | First Floor | 739 | 49 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.8729 | 1 | 7.8729 | 2 | 7.8729 | 2
112 | Classroom | 579 | 38 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 5.026 | 1 | 5.026 | 2 | 5.026 | 2
113 | First Floor | 679 | 45 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 7.2337 | 1 | 7.2337 | 2 | 7.2337 | 2
114 | Classroom | 716 | 47 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 6.2153 | 1 | 6.2153 | 2 | 6.2153 | 2
115 | First Floor | 417 | 27 |  |  | 792 | 18 | 18 | House Fan | 8 | 6336 | 3.9489 | 1 | 3.9489 | 1 | 3.9489 | 1
116 | Classroom | 575 | 38 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 4.9913 | 1 | 4.9913 | 2 | 4.9913 | 2
117 | Classroom |  | 0 | Yes | 20 | 414 | 9 | 9 | House Fan | 8 | 3312 | 0 | 1 | 0 | 0 | 20 | 3
201 | Second Floor | 772 | 51 |  |  | 748 | 17 | 17 | House Fan | 8 | 5984 | 7.7406 | 1 | 7.7406 | 2 | 7.7406 | 2
202 | Classroom | 486 | 32 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 4.2188 | 1 | 4.2188 | 2 | 4.2188 | 2
203 | Classroom | 297 | 19 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 3.1641 | 1 | 3.1641 | 1 | 3.1641 | 1
204 | Library |  | 0 | Yes | 20 | 696 | 15 | 15 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
205 | Library |  | 0 | Yes | 20 | 696 | 15 | 15 | House Fan | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
206 | Second Floor | 615 | 41 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.5518 | 1 | 6.5518 | 2 | 6.5518 | 2
207 | Classroom | 633 | 42 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 5.4948 | 1 | 5.4948 | 2 | 5.4948 | 2
208 | Second Floor | 332 | 22 |  |  | 792 | 18 | 18 | House Fan | 8 | 6336 | 3.1439 | 1 | 3.1439 | 1 | 3.1439 | 1
209 | Classroom | 990 | 66 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 8.5938 | 1 | 8.5938 | 2 | 8.5938 | 2
210 | Second Floor | 236 | 15 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 2.6818 | 1 | 2.6818 | 1 | 2.6818 | 1
211 | Classroom |  | 0 | Yes | 20 | 792 | 18 | 18 | House Fan | 8 | 6336 | 0 | 1 | 0 | 0 | 20 | 3
212 | Classroom | 1033 | 68 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 8.967 | 1 | 8.967 | 2 | 8.967 | 2
213 | Second Floor | 675 | 45 |  |  | 792 | 18 | 18 | House Fan | 8 | 6336 | 6.392 | 1 | 6.392 | 2 | 6.392 | 2
214 | Classroom | 453 | 30 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 3.9323 | 1 | 3.9323 | 1 | 3.9323 | 1
215 | Second Floor | 532 | 35 |  |  | 748 | 17 | 17 | House Fan | 8 | 5984 | 5.3342 | 1 | 5.3342 | 2 | 5.3342 | 2
216 | Classroom | 562 | 37 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 4.8785 | 1 | 4.8785 | 2 | 4.8785 | 2
217 | Room |  | 0 | Yes | 20 | 272 | 6 | 6 | House Fan | 8 | 2176 | 0 | 1 | 0 | 0 | 20 | 3
300 | Classroom |  | 0 | Yes | 20 | 480 | 10 | 10 | House Fan | 8 | 3840 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 | Yes | 20 | 800 | 18 | 18 | House Fan | 8 | 6400 | 0 | 1 | 0 | 0 | 20 | 3
302 | Third Floor | 415 | 27 |  |  | 748 | 17 | 17 | House Fan | 8 | 5984 | 4.1611 | 1 | 4.1611 | 2 | 4.1611 | 2
303 | Classroom | 291 | 19 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 2.526 | 1 | 2.526 | 1 | 2.526 | 1
304 | Room |  | 0 | Yes | 20 | 336 | 7 | 7 | House Fan | 8 | 2688 | 0 | 1 | 0 | 0 | 20 | 3
305 | Third Floor | 589 | 39 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.2749 | 1 | 6.2749 | 2 | 6.2749 | 2
306 | Classroom | 276 | 18 |  |  | 864 | 19 | 18 | House Fan | 8 | 6912 | 2.3958 | 1 | 2.3958 | 1 | 2.3958 | 1
307 | Classroom |  | 0 | Yes | 20 | 480 | 10 | 10 | House Fan | 8 | 3840 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
309 | Third Floor | 98 | 6 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 1.044 | 1 | 1.044 | 1 | 21.044 | 3
310 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
311 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
312 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
313 | Third Floor | 66 | 4 | Yes | 20 | 704 | 16 | 16 | House Fan | 8 | 5632 | 0.70312 | 1 | 0.70312 | 0 | 20.7031 | 3
314 | Classroom |  | 0 | Yes | 20 | 800 | 18 | 18 | House Fan | 8 | 6400 | 0 | 1 | 0 | 0 | 20 | 3
315 | Classroom | 214 | 14 | Yes | 20 | 864 | 19 | 19 | House Fan | 8 | 6912 | 1.8576 | 1 | 1.8576 | 1 | 21.8576 | 3
316 | Classroom |  | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium | 1586 | 105 |  |  | 1584 | 36 | 36 | House Fan | 8 | 12672 | 7.5095 | 1 | 7.5095 | 2 | 7.5095 | 2
- | Boy's Bathroom | 541 | 36 |  |  | 792 | 18 | 18 | House Fan | 8 | 6336 | 5.1231 | 1 | 5.1231 | 2 | 5.1231 | 2
- | Girl's Bathroom | 582 | 38 |  |  | 704 | 16 | 16 | House Fan | 8 | 5632 | 6.2003 | 1 | 6.2003 | 2 | 6.2003 | 2
- | Music Room | 1241 | 82 |  |  | 1496 | 34 | 34 | House Fan | 8 | 11968 | 6.2216 | 1 | 6.2216 | 2 | 6.2216 | 2
- | Nurses | 1184 | 78 |  |  | 150 | 3 | 3 | House Fan | 8 | 1200 | 59.2 | 1 | 59.2 | 5 | 59.2 | 5
- | Gym | 1915 | 127 |  |  | 1560 | 35 | 35 | House Fan | 8 | 12480 | 9.2067 | 1 | 9.2067 | 2 | 9.2067 | 2
- | Main Office | 0 | 0 | Yes | 20 | 416 | 9 | 9 | House Fan | 8 | 3328 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 20 | 294 | 6 | 6 | House Fan | 8 | 2352 | 0 | 1 | 0 | 0 | 20 | 3
- | Cafeteria |  | 0 | Yes | 20 | 1890 | 42 | 42 | House Fan | 8 | 15120 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-26
School: | Spring Garden
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 | Yes | 20 | 475 | 10 | 10 |  | 8 | 3800 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 494 | 11 | 11 |  | 8 | 3952 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 | Yes | 20 | 494 | 11 | 11 |  | 8 | 3952 | 0 | 1 | 0 | 0 | 20 | 3
104A | storage |  | 0 |  |  | 50 | 1 | 0 |  | 8 | 400 | 0 | 1 | 0 | 0 | 0 | 0
104B | office |  | 0 | Yes | 20 | 80 | 1 | 1 |  | 8 | 640 | 0 | 1 | 0 | 0 | 20 | 3
104C | office |  | 0 | Yes | 20 | 110 | 2 | 2 |  | 8 | 880 | 0 | 1 | 0 | 0 | 20 | 3
104D | office |  | 0 | Yes | 20 | 99 | 2 | 2 |  | 8 | 792 | 0 | 1 | 0 | 0 | 20 | 3
105A | Classroom |  | 0 | Yes | 20 | 483 | 10 | 10 |  | 8 | 3864 | 0 | 1 | 0 | 0 | 20 | 3
105B | Classroom |  | 0 | Yes | 20 | 420 | 9 | 9 |  | 8 | 3360 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 494 | 11 | 11 |  | 8 | 3952 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 494 | 11 | 11 |  | 8 | 3952 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 494 | 11 | 11 |  | 8 | 3952 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 | Yes | 20 | 494 | 11 | 11 |  | 8 | 3952 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 494 | 11 | 11 |  | 8 | 3952 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 | Yes | 20 | 483 | 10 | 10 |  | 8 | 3864 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom |  | 0 | Yes | 20 | 572 | 13 | 13 |  | 8 | 4576 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 | Yes | 20 | 741 | 16 | 16 |  | 8 | 5928 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom |  | 0 | Yes | 20 | 532 | 12 | 12 |  | 8 | 4256 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom |  | 0 | Yes | 20 | 578 | 13 | 13 |  | 8 | 4624 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 |  | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom |  | 0 | Yes | 20 | 494 | 11 | 11 |  | 8 | 3952 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom |  | 0 | Yes | 20 | 608 | 13 | 13 |  | 8 | 4864 | 0 | 1 | 0 | 0 | 20 | 3
308 | IMC |  | 0 | Yes | 20 | 874 | 19 | 19 |  | 8 | 6992 | 0 | 1 | 0 | 0 | 20 | 3
310 | Classroom |  | 0 | Yes | 20 | 380 | 8 | 8 |  | 8 | 3040 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium |  | 0 | Yes | 20 | 2265 | 51 | 51 |  | 8 | 18120 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 | Yes | 20 | 1800 | 40 | 40 |  | 8 | 14400 | 0 | 1 | 0 | 0 | 20 | 3
- | Lunchroom |  | 0 | Yes | 20 | 1520 | 34 | 34 |  | 8 | 12160 | 0 | 1 | 0 | 0 | 20 | 3
- | Main office |  | 0 | Yes | 20 | 231 | 5 | 5 |  | 8 | 1848 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses Office |  | 0 | Yes | 20 | 189 | 4 | 4 |  | 8 | 1512 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office |  | 0 | Yes | 20 | 210 | 4 | 4 |  | 8 | 1680 | 0 | 1 | 0 | 0 | 20 | 3
- | Staff lounge |  | 0 | Yes | 20 | 168 | 3 | 3 |  | 8 | 1344 | 0 | 1 | 0 | 0 | 20 | 3
- | Teachers lounge |  | 0 | Yes | 20 | 195 | 4 | 4 |  | 8 | 1560 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-19
School: | Gilbert Spruance Elementary School
Vendor: | EMCOR
School: | Gilbert Spruance Little School House
Vendor: | EMCOR | Chadwick
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Spruance Main Building
100 | Room | 108 | 7 |  |  | 728 | 16 | 7 | Unit Ventilator | 8 | 5824 | 1.1126 | 1 | 1.1126 | 1 | 1.1126 | 1
101 & 101B | Room | 208 | 13 |  |  | 1180 | 26 | 13 | Unit Ventilator | 8 | 9440 | 1.322 | 1 | 1.322 | 1 | 1.322 | 1
102 | Room | 112 | 7 |  |  | 756 | 17 | 7 | Unit Ventilator | 8 | 6048 | 1.1111 | 1 | 1.1111 | 1 | 1.1111 | 1
Outside 102 | Hallway | 0 | 0 |  |  | 370 | 8 | 0 | Unit Ventilator | 8 | 2960 | 0 | 1 | 0 | 0 | 0 | 0
103 | Room | 188 | 12 |  |  | 756 | 17 | 12 | Unit Ventilator | 8 | 6048 | 1.8651 | 1 | 1.8651 | 1 | 1.8651 | 1
104 | Room | 101 | 6 |  |  | 756 | 17 | 6 | Unit Ventilator | 8 | 6048 | 1.002 | 1 | 1.002 | 1 | 1.002 | 1
105 | Room | 83 | 5 |  |  | 756 | 17 | 5 | Unit Ventilator | 8 | 6048 | 0.82341 | 1 | 0.82341 | 0 | 0.82341 | 0
106 | Room | 106 | 7 |  |  | 756 | 17 | 7 | Unit Ventilator | 8 | 6048 | 1.0516 | 1 | 1.0516 | 1 | 1.0516 | 1
107 | Room | 119 | 7 | Yes | 20 | 756 | 17 | 17 | Unit Ventilator | 8 | 6048 | 1.1806 | 1 | 1.1806 | 1 | 21.1806 | 3
108 | Room | 115 | 7 |  |  | 756 | 17 | 7 | Unit Ventilator | 8 | 6048 | 1.1409 | 1 | 1.1409 | 1 | 1.1409 | 1
109 | Room | 160 | 10 |  |  | 756 | 17 | 10 | Unit Ventilator | 8 | 6048 | 1.5873 | 1 | 1.5873 | 1 | 1.5873 | 1
110 | Room | 97 | 6 |  |  | 756 | 17 | 6 | Unit Ventilator | 8 | 6048 | 0.9623 | 1 | 0.9623 | 0 | 0.9623 | 0
111 | Room | 145 | 9 |  |  | 996 | 22 | 9 | Unit Ventilator | 8 | 7968 | 1.0919 | 1 | 1.0919 | 1 | 1.0919 | 1
112 | Room | 208 | 13 |  |  | 996 | 22 | 13 | Unit Ventilator | 8 | 7968 | 1.5663 | 1 | 1.5663 | 1 | 1.5663 | 1
113 | Room | 110 | 7 |  |  | 996 | 22 | 7 | Unit Ventilator | 8 | 7968 | 0.82831 | 1 | 0.82831 | 0 | 0.82831 | 0
Outside of 113 | Hallway | 0 | 0 |  |  | 3700 | 84 | 0 | Unit Ventilator | 8 | 29600 | 0 | 1.062 | 0 | 0 | 0 | 0
114 | Room | 240 | 16 |  |  | 996 | 22 | 16 | Unit Ventilator | 8 | 7968 | 1.8072 | 1 | 1.8072 | 1 | 1.8072 | 1
115 | Room | 150 | 10 |  |  | 996 | 22 | 10 | Unit Ventilator | 8 | 7968 | 1.1295 | 1 | 1.1295 | 1 | 1.1295 | 1
116 | Room | 334 | 22 |  |  | 719 | 16 | 16 | Unit Ventilator | 8 | 5752 | 3.484 | 1 | 3.484 | 1 | 3.484 | 1
117 | Room | 240 | 16 |  |  | 736 | 16 | 16 | Unit Ventilator | 8 | 5888 | 2.4457 | 1 | 2.4457 | 1 | 2.4457 | 1
118 | Room | 145 | 9 |  |  | 1075 | 24 | 9 | Unit Ventilator | 8 | 8600 | 1.0116 | 1 | 1.0116 | 1 | 1.0116 | 1
118A | Room | 183 | 12 |  |  | 486 | 11 | 11 | Unit Ventilator | 8 | 3888 | 2.8241 | 1 | 2.8241 | 1 | 2.8241 | 1
119 | Room | 241 | 16 |  |  | 736 | 16 | 16 | Unit Ventilator | 8 | 5888 | 2.4558 | 1 | 2.4558 | 1 | 2.4558 | 1
120 | Room | 225 | 15 |  |  | 1062 | 24 | 15 | Unit Ventilator | 8 | 8496 | 1.589 | 1 | 1.589 | 1 | 1.589 | 1
122 | Room | 248 | 16 |  |  | 851 | 19 | 16 | Unit Ventilator | 8 | 6808 | 2.1857 | 1 | 2.1857 | 1 | 2.1857 | 1
124 | Room | 58 | 3 | Yes | 20 | 756 | 17 | 17 | Unit Ventilator | 8 | 6048 | 0.5754 | 1 | 0.5754 | 0 | 20.5754 | 3
- | Auditorium/Gym | 0 | 0 |  |  | 4620 | 105 | 0 | Unit Ventilator | 8 | 36960 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Adjustment Room | 73 | 4 |  |  | 435 | 9 | 4 | Unit Ventilator | 8 | 3480 | 1.2586 | 1 | 1.2586 | 1 | 1.2586 | 1
200 | Room | 148 | 9 |  |  | 756 | 17 | 9 | Unit Ventilator | 8 | 6048 | 1.4683 | 1 | 1.4683 | 1 | 1.4683 | 1
201 | Room | 136 | 9 |  |  | 756 | 17 | 9 | Unit Ventilator | 8 | 6048 | 1.3492 | 1 | 1.3492 | 1 | 1.3492 | 1
202 | Room | 179 | 11 |  |  | 690 | 15 | 11 | Unit Ventilator | 8 | 5520 | 1.9457 | 1 | 1.9457 | 1 | 1.9457 | 1
Outside of 202 | Hallway | 0 | 0 |  |  | 3700 | 84 | 0 | Unit Ventilator | 8 | 29600 | 0 | 1.062 | 0 | 0 | 0 | 0
203 | Room | 134 | 8 |  |  | 756 | 17 | 8 | Unit Ventilator | 8 | 6048 | 1.3294 | 1 | 1.3294 | 1 | 1.3294 | 1
204 | Room | 114 | 7 |  |  | 756 | 17 | 7 | Unit Ventilator | 8 | 6048 | 1.131 | 1 | 1.131 | 1 | 1.131 | 1
205 | Room | 97 | 6 |  |  | 756 | 17 | 6 | Unit Ventilator | 8 | 6048 | 0.9623 | 1 | 0.9623 | 0 | 0.9623 | 0
206 | Room | 83 | 5 |  |  | 756 | 17 | 5 | Unit Ventilator | 8 | 6048 | 0.82341 | 1 | 0.82341 | 0 | 0.82341 | 0
207 | Room | 102 | 6 |  |  | 756 | 17 | 6 | Unit Ventilator | 8 | 6048 | 1.0119 | 1 | 1.0119 | 1 | 1.0119 | 1
208 | Room | 139 | 9 |  |  | 756 | 17 | 9 | Unit Ventilator | 8 | 6048 | 1.379 | 1 | 1.379 | 1 | 1.379 | 1
209 | Room | 121 | 8 |  |  | 756 | 17 | 8 | Unit Ventilator | 8 | 6048 | 1.2004 | 1 | 1.2004 | 1 | 1.2004 | 1
210 | Room | 90 | 6 |  |  | 756 | 17 | 6 | Unit Ventilator | 8 | 6048 | 0.89286 | 1 | 0.89286 | 0 | 0.89286 | 0
211 | Room | 199 | 13 |  |  | 756 | 17 | 13 | Unit Ventilator | 8 | 6048 | 1.9742 | 1 | 1.9742 | 1 | 1.9742 | 1
212 | Room | 134 | 8 |  |  | 756 | 17 | 8 | Unit Ventilator | 8 | 6048 | 1.3294 | 1 | 1.3294 | 1 | 1.3294 | 1
213A | Room | 103 | 6 |  |  | 420 | 9 | 6 | Unit Ventilator | 8 | 3360 | 1.8393 | 1 | 1.8393 | 1 | 1.8393 | 1
Outside of Room 213A | Hallway | 0 | 0 |  |  | 756 | 17 | 0 | Unit Ventilator | 8 | 6048 | 0 | 1 | 0 | 0 | 0 | 0
213B | Room | 267 | 17 |  |  | 548 | 12 | 12 | Unit Ventilator | 8 | 4384 | 3.6542 | 1 | 3.6542 | 1 | 3.6542 | 1
214 | Room | 114 | 7 |  |  | 755 | 17 | 7 | Unit Ventilator | 8 | 6040 | 1.1325 | 1 | 1.1325 | 1 | 1.1325 | 1
214A | Room | 0 | 0 |  |  | 756 | 17 | 0 | Unit Ventilator | 8 | 6048 | 0 | 1 | 0 | 0 | 0 | 0
215 | Room | 53 | 3 |  |  | 756 | 17 | 3 | Unit Ventilator | 8 | 6048 | 0.52579 | 1 | 0.52579 | 0 | 0.52579 | 0
216 | Room | 122 | 8 |  |  | 756 | 17 | 8 | Unit Ventilator | 8 | 6048 | 1.2103 | 1 | 1.2103 | 1 | 1.2103 | 1
217 | Room | 83 | 5 |  |  | 756 | 17 | 5 | Unit Ventilator | 8 | 6048 | 0.82341 | 1 | 0.82341 | 0 | 0.82341 | 0
Outside of Room 217 | Hallway | 0 | 0 |  |  | 1850 | 42 | 0 | Unit Ventilator | 8 | 14800 | 0 | 1 | 0 | 0 | 0 | 0
218 | Room | 139 | 9 |  |  | 718 | 16 | 9 | Unit Ventilator | 8 | 5744 | 1.4519 | 1 | 1.4519 | 1 | 1.4519 | 1
220 | Room | 131 | 8 |  |  | 724 | 16 | 8 | Unit Ventilator | 8 | 5792 | 1.357 | 1 | 1.357 | 1 | 1.357 | 1
- | Cafeteria | 263 | 17 | Yes | 20 | 4550 | 103 | 103 | Unit Ventilator | 8 | 36400 | 0.43352 | 1.062 | 0.46041 | 0 | 20.4604 | 3
- | Main Office | 315 | 21 |  |  | 456 | 10 | 10 |  | 8 | 3648 | 5.1809 | 1 | 5.1809 | 2 | 5.1809 | 2
- | Principal | 240 | 16 |  |  | 241 | 5 | 5 |  | 8 | 1928 | 7.4689 | 1 | 7.4689 | 2 | 7.4689 | 2
- | Nurse | 374 | 24 |  |  | 374 | 8 | 8 |  | 8 | 2992 | 7.5 | 1 | 7.5 | 2 | 7.5 | 2
- | Main Entrance Lobby | 1498 | 99 |  |  | 1498 | 34 | 34 | Unit Ventilator | 8 | 11984 | 7.5 | 1 | 7.5 | 2 | 7.5 | 2
Little School House
1 | Room | 1072 | 71 |  |  | 1056 | 24 | 24 | Air Handling Unit | 8 | 8448 | 7.6136 | 1 | 7.6136 | 2 | 7.6136 | 2
2 | Room | 938 | 62 |  |  | 1056 | 24 | 24 | Air Handling Unit | 8 | 8448 | 6.6619 | 1 | 6.6619 | 2 | 6.6619 | 2
3 | Room | 741 | 49 |  |  | 1056 | 24 | 24 | Air Handling Unit | 8 | 8448 | 5.2628 | 1 | 5.2628 | 2 | 5.2628 | 2
4 | Room | 1188 | 79 |  |  | 1056 | 24 | 24 | Air Handling Unit | 8 | 8448 | 8.4375 | 1 | 8.4375 | 2 | 8.4375 | 2
5 | Room | 682 | 45 |  |  | 1056 | 24 | 24 | Air Handling Unit | 8 | 8448 | 4.8438 | 1 | 4.8438 | 2 | 4.8438 | 2
6 | Room | 713 | 47 |  |  | 1056 | 24 | 24 | Air Handling Unit | 8 | 8448 | 5.0639 | 1 | 5.0639 | 2 | 5.0639 | 2
7 | Room | 554 | 36 |  |  | 1056 | 24 | 24 | Air Handling Unit | 8 | 8448 | 3.9347 | 1 | 3.9347 | 1 | 3.9347 | 1
8 | Room | 690 | 46 |  |  | 1056 | 24 | 24 | Air Handling Unit | 8 | 8448 | 4.9006 | 1 | 4.9006 | 2 | 4.9006 | 2
9 | Room | 1558 | 103 |  |  | 1056 | 24 | 24 | Air Handling Unit | 8 | 8448 | 11.0653 | 1 | 11.0653 | 3 | 11.0653 | 3
10 | Room | 853 | 56 |  |  | 1056 | 24 | 24 | Air Handling Unit | 8 | 8448 | 6.0582 | 1 | 6.0582 | 2 | 6.0582 | 2
11 | Room | 1512 | 100 |  |  | 1056 | 24 | 24 | Air Handling Unit | 8 | 8448 | 10.7386 | 1 | 10.7386 | 3 | 10.7386 | 3
12 | Room | 946 | 63 |  |  | 1056 | 24 | 24 | Air Handling Unit | 8 | 8448 | 6.7188 | 1 | 6.7188 | 2 | 6.7188 | 2
- | CLI Office | 159 | 10 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 9.9375 | 1 | 9.9375 | 2 | 9.9375 | 2
- | Entrance/Lobby | 0 | 0 |  |  | 210 | 4 | 0 | Air Handling Unit | 8 | 1680 | 0 | 1 | 0 | 0 | 0 | 0
- | Hallway | 0 | 0 |  |  | 1950 | 44 | 0 | Air Handling Unit | 8 | 15600 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office | 165 | 11 |  |  | 315 | 7 | 7 | Air Handling Unit | 8 | 2520 | 3.9286 | 1 | 3.9286 | 1 | 3.9286 | 1
- | Office | 158 | 10 |  |  | 126 | 2 | 2 | Air Handling Unit | 8 | 1008 | 9.4048 | 1 | 9.4048 | 2 | 9.4048 | 2
- | Storage | 0 | 0 |  |  | 215 | 4 | 0 | Air Handling Unit | 8 | 1720 | 0 | 1 | 0 | 0 | 0 | 0
- | Teachers Lounge | 331 | 22 |  |  | 72 | 1 | 1 | Air Handling Unit | 8 | 576 | 34.4792 | 1 | 34.4792 | 4 | 34.4792 | 4
- | Therapy Room | 0 | 0 |  |  | 72 | 1 | 0 | Air Handling Unit | 8 | 576 | 0 | 1 | 0 | 0 | 0 | 0
- | Girl's RR | 0 | 0 |  |  | 272 | 6 | 0 | Air Handling Unit | 8 | 2176 | 0 | 1 | 0 | 0 | 0 | 0
- | Boy's RR | 0 | 0 |  |  | 272 | 6 | 0 | Air Handling Unit | 8 | 2176 | 0 | 1 | 0 | 0 | 0 | 0
- | Men's RR | 0 | 0 |  |  | 77 | 1 | 0 | Air Handling Unit | 8 | 616 | 0 | 1 | 0 | 0 | 0 | 0
- | Women's RR | 0 | 0 |  |  | 131 | 2 | 0 | Air Handling Unit | 8 | 1048 | 0 | 1 | 0 | 0 | 0 | 0
- | Multi-purpose Room | 2808 | 187 |  |  | 1998 | 45 | 45 | Fan Coil Unit | 8 | 15984 | 10.5405 | 1 | 10.5405 | 3 | 10.5405 | 3
Sheet Last Modified: | 2021-04-29
School: | Edwin M. Stanton Elementary School
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Main Office | 0 | 0 | Yes | 20 | 375 | 8 | 8 | House Fan | 8 | 3000 | 0 | 1 | 0 | 0 | 20 | 3
101 | Classroom | 829 | 55 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 7.1466 | 1 | 7.1466 | 2 | 7.1466 | 2
102 | Classroom | 598 | 39 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 5.1552 | 1 | 5.1552 | 2 | 5.1552 | 2
103 | Classroom | 630 | 42 |  |  | 899 | 20 | 20 | House Fan | 8 | 7192 | 5.2558 | 1 | 5.2558 | 2 | 5.2558 | 2
104 | Classroom | 635 | 42 |  |  | 864 | 19 | 19 | House Fan | 8 | 6912 | 5.5122 | 1 | 5.5122 | 2 | 5.5122 | 2
105 | Classroom | 639 | 42 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 5.5086 | 1 | 5.5086 | 2 | 5.5086 | 2
106 | Classroom | 764 | 50 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 6.5862 | 1 | 6.5862 | 2 | 6.5862 | 2
107 | Classroom | 836 | 55 |  |  | 1450 | 32 | 32 | House Fan | 8 | 11600 | 4.3241 | 1 | 4.3241 | 2 | 4.3241 | 2
201 | Classroom | 697 | 46 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 6.0086 | 1 | 6.0086 | 2 | 6.0086 | 2
202 | Classroom | 500 | 33 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 4.3103 | 1 | 4.3103 | 2 | 4.3103 | 2
203 | Classroom | 526 | 35 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 4.5345 | 1 | 4.5345 | 2 | 4.5345 | 2
204 | Classroom | 527 | 35 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 4.5431 | 1 | 4.5431 | 2 | 4.5431 | 2
205 | Library | 907 | 60 |  |  | 1363 | 30 | 30 | House Fan | 8 | 10904 | 4.9908 | 1 | 4.9908 | 2 | 4.9908 | 2
206 | Classroom | 531 | 35 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 4.5776 | 1 | 4.5776 | 2 | 4.5776 | 2
207 | Classroom | 706 | 47 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 6.0862 | 1 | 6.0862 | 2 | 6.0862 | 2
208 | Classroom | 806 | 53 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 6.9483 | 1 | 6.9483 | 2 | 6.9483 | 2
301 | Gym | 61 | 4 |  |  | 870 | 19 | 4 | House Fan | 8 | 6960 | 0.52586 | 1 | 0.52586 | 0 | 0.52586 | 0
302 | Gym | 432 | 28 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 3.7241 | 1 | 3.7241 | 1 | 3.7241 | 1
302 | Classroom | 560 | 37 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 4.8276 | 1 | 4.8276 | 2 | 4.8276 | 2
304 | Classroom | 715 | 47 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 6.1638 | 1 | 6.1638 | 2 | 6.1638 | 2
305 | Classroom | 833 | 55 |  |  | 1316 | 29 | 29 | House Fan | 8 | 10528 | 4.7473 | 1 | 4.7473 | 2 | 4.7473 | 2
306 | Classroom | 525 | 35 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 4.5259 | 1 | 4.5259 | 2 | 4.5259 | 2
307 | Classroom | 988 | 65 |  |  | 870 | 19 | 19 | House Fan | 8 | 6960 | 8.5172 | 1 | 8.5172 | 2 | 8.5172 | 2
308 | Classroom | 230 | 15 |  |  | 870 | 19 | 15 | House Fan | 8 | 6960 | 1.9828 | 1 | 1.9828 | 1 | 1.9828 | 1
Counselor | Office |  | 0 | Yes | 20 | 240 | 5 | 5 | House Fan | 8 | 1920 | 0 | 1 | 0 | 0 | 20 | 3
- | Cafeteria | 0 | 0 | Yes | 20 | 2400 | 54 | 54 | House Fan | 8 | 19200 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Office | 0 | 0 | Yes | 20 | 200 | 4 | 4 | House Fan | 8 | 1600 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal Office | 0 | 0 | Yes | 20 | 256 | 5 | 5 | House Fan | 8 | 2048 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-15
School: | Allen M. Stearne Elementary School
Vendor: | EMCOR | EMCOR Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | classroom | 529 | 35 |  |  | 730 | 16 | 16 | Perimeter Heater | 8 | 5840 | 5.4349 | 1 | 5.4349 | 2 | 5.4349 | 2
100A | First Floor | 30 | 2 |  |  | 222 | 5 | 2 | Perimeter Heater | 8 | 1776 | 1.0135 | 1 | 1.0135 | 1 | 1.0135 | 1
101 | classroom | 316 | 21 |  |  | 1197 | 27 | 21 | Perimeter Heater | 8 | 9576 | 1.9799 | 1 | 1.9799 | 1 | 1.9799 | 1
102 | classroom | 452 | 30 |  |  | 753 | 17 | 17 | Perimeter Heater | 8 | 6024 | 4.502 | 1 | 4.502 | 2 | 4.502 | 2
102A | First Floor | 284 | 18 |  |  | 401 | 9 | 9 | Perimeter Heater | 8 | 3208 | 5.3117 | 1 | 5.3117 | 2 | 5.3117 | 2
103 | classroom | 569 | 37 |  |  | 1175 | 26 | 26 | Perimeter Heater | 8 | 9400 | 3.6319 | 1 | 3.6319 | 1 | 3.6319 | 1
104 | classroom | 224 | 14 |  |  | 716 | 16 | 14 | Perimeter Heater | 8 | 5728 | 2.3464 | 1 | 2.3464 | 1 | 2.3464 | 1
105 | Classroom |  | 0 |  |  | 319 | 7 | 0 | Perimeter Heater | 8 | 2552 | 0 | 1 | 0 | 0 | 0 | 0
106 | classroom | 189 | 12 |  |  | 730 | 16 | 12 | Perimeter Heater | 8 | 5840 | 1.9418 | 1 | 1.9418 | 1 | 1.9418 | 1
108A | First Floor | 276 | 18 |  |  | 810 | 18 | 18 | Perimeter Heater | 8 | 6480 | 2.5556 | 1 | 2.5556 | 1 | 2.5556 | 1
108B | First Floor | 59 | 3 |  |  | 129 | 2 | 2 | Perimeter Heater | 8 | 1032 | 3.4302 | 1 | 3.4302 | 1 | 3.4302 | 1
108C | First Floor | 109 | 7 |  |  | 146 | 3 | 3 | Perimeter Heater | 8 | 1168 | 5.5993 | 1 | 5.5993 | 2 | 5.5993 | 2
108D | First Floor | 54 | 3 |  |  | 86 | 1 | 1 | Perimeter Heater | 8 | 688 | 4.7093 | 1 | 4.7093 | 2 | 4.7093 | 2
108E | First Floor | 87 | 5 |  |  | 75 | 1 | 1 | Perimeter Heater | 8 | 600 | 8.7 | 1 | 8.7 | 2 | 8.7 | 2
108F | First Floor | 62 | 4 |  |  | 94 | 2 | 2 | Perimeter Heater | 8 | 752 | 4.9468 | 1 | 4.9468 | 2 | 4.9468 | 2
200 | classroom | 274 | 18 |  |  | 740 | 16 | 16 | Perimeter Heater | 8 | 5920 | 2.777 | 1 | 2.777 | 1 | 2.777 | 1
201 | classroom | 322 | 21 |  |  | 717 | 16 | 16 | Perimeter Heater | 8 | 5736 | 3.3682 | 1 | 3.3682 | 1 | 3.3682 | 1
202 | classroom | 313 | 20 |  |  | 705 | 16 | 16 | Perimeter Heater | 8 | 5640 | 3.3298 | 1 | 3.3298 | 1 | 3.3298 | 1
203 | classroom | 337 | 22 |  |  | 739 | 16 | 16 | Perimeter Heater | 8 | 5912 | 3.4202 | 1 | 3.4202 | 1 | 3.4202 | 1
204 | classroom | 329 | 21 |  |  | 737 | 16 | 16 | Perimeter Heater | 8 | 5896 | 3.348 | 1 | 3.348 | 1 | 3.348 | 1
205 | classroom | 325 | 21 |  |  | 756 | 17 | 17 | Perimeter Heater | 8 | 6048 | 3.2242 | 1 | 3.2242 | 1 | 3.2242 | 1
206 | classroom | 334 | 22 |  |  | 745 | 16 | 16 | Perimeter Heater | 8 | 5960 | 3.3624 | 1 | 3.3624 | 1 | 3.3624 | 1
207 | classroom | 0 | 0 | Yes | 20 | 386 | 8 | 8 | Perimeter Heater | 8 | 3088 | 0 | 1 | 0 | 0 | 20 | 3
208 | classroom | 328 | 21 |  |  | 882 | 20 | 20 | Perimeter Heater | 8 | 7056 | 2.7891 | 1 | 2.7891 | 1 | 2.7891 | 1
209 | classroom | 109 | 7 | Yes | 20 | 639 | 14 | 14 | Perimeter Heater | 8 | 5112 | 1.2793 | 1 | 1.2793 | 1 | 21.2793 | 3
209A | classroom | 80 | 5 |  |  | 152 | 3 | 3 | Perimeter Heater | 8 | 1216 | 3.9474 | 1 | 3.9474 | 1 | 3.9474 | 1
209B | classroom | 0 | 0 |  |  | 125 | 2 | 0 | Perimeter Heater | 8 | 1000 | 0 | 1 | 0 | 0 | 0 | 0
210 | classroom | 549 | 36 |  |  | 1185 | 26 | 26 | Perimeter Heater | 8 | 9480 | 3.4747 | 1 | 3.4747 | 1 | 3.4747 | 1
211 | classroom | 845 | 56 |  |  | 728 | 16 | 16 | Perimeter Heater | 8 | 5824 | 8.7054 | 1 | 8.7054 | 2 | 8.7054 | 2
212 | classroom | 116 | 7 |  |  | 434 | 9 | 7 | Perimeter Heater | 8 | 3472 | 2.0046 | 1 | 2.0046 | 1 | 2.0046 | 1
213 | classroom | 131 | 8 |  |  | 224 | 5 | 5 | Perimeter Heater | 8 | 1792 | 4.3862 | 1 | 4.3862 | 2 | 4.3862 | 2
300 | classroom | 532 | 35 |  |  | 763 | 17 | 17 | Perimeter Heater | 8 | 6104 | 5.2294 | 1 | 5.2294 | 2 | 5.2294 | 2
300A | classroom | 395 | 26 |  |  | 224 | 5 | 5 | Perimeter Heater | 8 | 1792 | 13.2254 | 1 | 13.2254 | 3 | 13.2254 | 3
301 | classroom | 350 | 23 |  |  | 755 | 17 | 17 | Perimeter Heater | 8 | 6040 | 3.4768 | 1 | 3.4768 | 1 | 3.4768 | 1
302 | classroom | 289 | 19 |  |  | 746 | 16 | 16 | Perimeter Heater | 8 | 5968 | 2.9055 | 1 | 2.9055 | 1 | 2.9055 | 1
303 | classroom | 447 | 29 |  |  | 722 | 16 | 16 | Perimeter Heater | 8 | 5776 | 4.6434 | 1 | 4.6434 | 2 | 4.6434 | 2
304 | classroom | 434 | 28 |  |  | 745 | 16 | 16 | Perimeter Heater | 8 | 5960 | 4.3691 | 1 | 4.3691 | 2 | 4.3691 | 2
305 | classroom | 360 | 24 |  |  | 747 | 16 | 16 | Perimeter Heater | 8 | 5976 | 3.6145 | 1 | 3.6145 | 1 | 3.6145 | 1
306 | classroom | 534 | 35 |  |  | 715 | 16 | 16 | Perimeter Heater | 8 | 5720 | 5.6014 | 1 | 5.6014 | 2 | 5.6014 | 2
307 | Classroom |  | 0 |  |  | 790 | 17 | 0 | Perimeter Heater | 8 | 6320 | 0 | 1 | 0 | 0 | 0 | 0
308 | classroom | 278 | 18 |  |  | 717 | 16 | 16 | Perimeter Heater | 8 | 5736 | 2.9079 | 1 | 2.9079 | 1 | 2.9079 | 1
- | Auditorium | 0 | 0 |  |  | 2919 | 66 | 0 | AHU | 8 | 23352 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Cafeteria/Gym | 0 | 0 | Yes | 20 | 3719 | 84 | 84 | AHU | 8 | 29752 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Dean's Office (Temple) | 72 | 4 |  |  | 106 | 2 | 2 | Perimter Heater | 8 | 848 | 5.0943 | 1 | 5.0943 | 2 | 5.0943 | 2
- | Health Office | 274 | 18 |  |  | 294 | 6 | 6 | Perimter Heater | 8 | 2352 | 6.9898 | 1 | 6.9898 | 2 | 6.9898 | 2
- | Office | 300 | 20 |  |  | 984 | 22 | 20 | Perimter Heater | 8 | 7872 | 2.2866 | 1 | 2.2866 | 1 | 2.2866 | 1
- | Principal | 187 | 12 |  |  | 321 | 7 | 7 | Perimter Heater | 8 | 2568 | 4.3692 | 1 | 4.3692 | 2 | 4.3692 | 2
Sheet Last Modified: | 2021-04-27
School: | Edward Steel Elementary School
Vendor: | EMCORE Fluidics | Exhaust Report
| 2-15-2021 Retest | 2-22-21 Retest | 4-12-21 Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Storeroom | 0 | 0 | Yes | 20 | 323 | 7 | 7 | Air Coil Unit | 8 | 2584 | 0 | 1 | 0 | 0 | 20 | 3
101A - C | Office | 0 | 0 | Yes | 20 | 356 | 8 | 8 | Air Coil Unit | 8 | 2848 | 0 | 1 | 0 | 0 | 20 | 3
102 | Main Office- open office | 0 | 0 | Yes | 20 | 512 | 11 | 11 | Air Coil Unit | 8 | 4096 | 0 | 1 | 0 | 0 | 20 | 3
102 | Main Office- admin ofc | 0 | 0 |  |  | 121 | 2 | 0 | Air Coil Unit | 8 | 968 | 0 | 1 | 0 | 0 | 0 | 0
102 | Main Office- asst principals ofc | 0 | 0 | Yes | 20 | 121 | 2 | 2 | Air Coil Unit | 8 | 968 | 0 | 1 | 0 | 0 | 20 | 3
102 | Main Office- principals ofc | 0 | 0 | Yes | 20 | 143 | 3 | 3 | Air Coil Unit | 8 | 1144 | 0 | 1 | 0 | 0 | 20 | 3
102 | Main Office- conf rm | 0 | 0 | Yes | 20 | 204 | 4 | 4 | Air Coil Unit | 8 | 1632 | 0 | 1 | 0 | 0 | 20 | 3
103 | Lounge | 0 | 0 | Yes | 20 | 676 | 15 | 15 | Air Coil Unit | 8 | 5408 | 0 | 1 | 0 | 0 | 20 | 3
104 | counselors ofc | 0 | 0 | Yes | 20 | 385 | 8 | 8 | Air Coil Unit | 8 | 3080 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom | 46 | 3 | Yes | 20 | 660 | 15 | 15 | Air Handling Unit | 8 | 5280 | 0.52273 | 1 | 0.52273 | 0 | 20.5227 | 3
106 | data room | 0 | 0 | Yes | 20 | 1364 | 31 | 31 | Air Coil Unit | 8 | 10912 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom | 363 | 24 | Yes | 20 | 1364 | 31 | 31 | Air Handling Unit | 8 | 10912 | 1.996 | 1 | 1.996 | 1 | 21.996 | 3
109 | Classroom | 257 | 17 | Yes | 20 | 1364 | 31 | 31 | Air Handling Unit | 8 | 10912 | 1.4131 | 1 | 1.4131 | 1 | 21.4131 | 3
110 | nurse str | 0 | 0 | Yes | 20 | 886 | 20 | 20 | Air Coil Unit | 8 | 7088 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse Waiting Area |  | 0 | Yes | 20 | 208 | 4 | 4 |  | 8 | 1664 | 0 | 1 | 0 | 0 | 20 | 3
111 | Classroom | 450 | 30 | Yes | 20 | 1364 | 31 | 31 | Air Handling Unit | 8 | 10912 | 2.4743 | 1 | 2.4743 | 1 | 22.4743 | 3
113 | Classroom | 338 | 22 | Yes | 20 | 1364 | 31 | 31 | Air Handling Unit | 8 | 10912 | 1.8585 | 1 | 1.8585 | 1 | 21.8585 | 3
- | AUDITORIUM | 475 | 31 | Yes | 20 | 2482 | 56 | 56 | Air Coil Unit | 8 | 19856 | 1.4353 | 1 | 1.4353 | 1 | 21.4353 | 3
- | CAFETERIA | 0 | 0 | Yes | 20 | 3478 | 79 | 79 | Air Coil Unit | 8 | 27824 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Cafeteria Office |  | 0 | Yes | 20 | 300 | 6 | 6 |  | 8 | 2400 | 0 | 1 | 0 | 0 | 20 | 3
- | IMC | 2021 | 134 |  |  | 3283 | 74 | 74 | Air Coil Unit | 8 | 26264 | 4.617 | 1.062 | 4.9034 | 2 | 4.9034 | 2
201 | Classroom | 163 | 10 | Yes | 20 | 1330 | 30 | 30 | Air Handling Unit | 8 | 10640 | 0.91917 | 1 | 0.91917 | 0 | 20.9192 | 3
202 | Classroom | 250 | 16 | Yes | 20 | 1330 | 30 | 30 | Air Handling Unit | 8 | 10640 | 1.4098 | 1 | 1.4098 | 1 | 21.4098 | 3
203 | Classroom | 188 | 12 | Yes | 20 | 1147 | 26 | 26 | Air Handling Unit | 8 | 9176 | 1.2293 | 1 | 1.2293 | 1 | 21.2293 | 3
204 | Classroom | 0 | 0 | Yes | 20 | 1147 | 26 | 26 | Air Coil Unit | 8 | 9176 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom | 194 | 12 | Yes | 20 | 1147 | 26 | 26 | Air Handling Unit | 8 | 9176 | 1.2685 | 1 | 1.2685 | 1 | 21.2685 | 3
206 | Classroom | 0 | 0 | Yes | 20 | 1147 | 26 | 26 | Air Coil Unit | 8 | 9176 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom | 144 | 9 | Yes | 20 | 1147 | 26 | 26 | Air Handling Unit | 8 | 9176 | 0.94159 | 1 | 0.94159 | 0 | 20.9416 | 3
208 | Classroom | 0 | 0 | Yes | 20 | 1147 | 26 | 26 | Air Coil Unit | 8 | 9176 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom | 186 | 12 | Yes | 20 | 1147 | 26 | 26 | Air Handling Unit | 8 | 9176 | 1.2162 | 1 | 1.2162 | 1 | 21.2162 | 3
210 | Classroom | 196 | 13 | Yes | 20 | 1147 | 26 | 26 | Air Coil Unit | 8 | 9176 | 1.2816 | 1 | 1.2816 | 1 | 21.2816 | 3
211 | Classroom | 0 | 0 | Yes | 20 | 1147 | 26 | 26 | Air Coil Unit | 8 | 9176 | 0 | 1 | 0 | 0 | 20 | 3
212 | Classroom | 287 | 19 | Yes | 20 | 1130 | 25 | 25 | Air Coil Unit | 8 | 9040 | 1.9049 | 1 | 1.9049 | 1 | 21.9049 | 3
213 | Classroom | 0 | 0 | Yes | 20 | 870 | 19 | 19 | Air Coil Unit | 8 | 6960 | 0 | 1 | 0 | 0 | 20 | 3
214 | Classroom |  | 0 | Yes | 20 | 870 | 19 | 19 | Air Coil Unit | 8 | 6960 | 0 | 1 | 0 | 0 | 20 | 3
215 | Office | 0 | 0 | Yes | 20 | 345 | 7 | 7 | Air Coil Unit | 8 | 2760 | 0 | 1 | 0 | 0 | 20 | 3
216 | Classroom | 0 | 0 | Yes | 20 | 588 | 13 | 13 | Air Coil Unit | 8 | 4704 | 0 | 1 | 0 | 0 | 20 | 3
219 | Classroom |  | 0 | Yes | 20 | 462 | 10 | 10 | Air Coil Unit | 8 | 3696 | 0 | 1 | 0 | 0 | 20 | 3
220 | team office | 0 | 0 | Yes | 20 | 462 | 10 | 10 | Air Coil Unit | 8 | 3696 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 0 | 0 | Yes | 20 | 1330 | 30 | 30 | Air Coil Unit | 8 | 10640 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom | 0 | 0 | Yes | 20 | 1330 | 30 | 30 | Air Coil Unit | 8 | 10640 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom | 0 | 0 | Yes | 20 | 1147 | 26 | 26 | Air Coil Unit | 8 | 9176 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom | 0 | 0 | Yes | 20 | 1147 | 26 | 26 | Air Coil Unit | 8 | 9176 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom | 0 | 0 | Yes | 20 | 1147 | 26 | 26 | Air Coil Unit | 8 | 9176 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom | 0 | 0 | Yes | 20 | 1147 | 26 | 26 | Air Coil Unit | 8 | 9176 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom | 0 | 0 | Yes | 20 | 1147 | 26 | 26 | Air Coil Unit | 8 | 9176 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom | 0 | 0 | Yes | 20 | 1147 | 26 | 26 | Air Coil Unit | 8 | 9176 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom | 0 | 0 | Yes | 20 | 1155 | 26 | 26 | Air Coil Unit | 8 | 9240 | 0 | 1 | 0 | 0 | 20 | 3
310 | Classroom | 0 | 0 | Yes | 20 | 1147 | 26 | 26 | Air Coil Unit | 8 | 9176 | 0 | 1 | 0 | 0 | 20 | 3
311 | Classroom | 0 | 0 | Yes | 20 | 1330 | 30 | 30 | Air Coil Unit | 8 | 10640 | 0 | 1 | 0 | 0 | 20 | 3
312 | Classroom | 482 | 32 |  |  | 1330 | 30 | 30 | Air Coil Unit | 8 | 10640 | 2.718 | 1 | 2.718 | 1 | 2.718 | 1
313 | Classroom | 0 | 0 | Yes | 20 | 870 | 19 | 19 | Air Coil Unit | 8 | 6960 | 0 | 1 | 0 | 0 | 20 | 3
314 | Classroom | 0 | 0 | Yes | 20 | 870 | 19 | 19 | Air Coil Unit | 8 | 6960 | 0 | 1 | 0 | 0 | 20 | 3
315 | Staff Lounge |  | 0 | Yes | 20 | 330 | 7 | 7 | Air Coil Unit | 8 | 2640 | 0 | 1 | 0 | 0 | 20 | 3
319 | Classroom |  | 0 | Yes | 20 | 462 | 10 | 10 | Air Coil Unit | 8 | 3696 | 0 | 1 | 0 | 0 | 20 | 3
320 | team office |  | 0 | Yes | 20 | 462 | 10 | 10 | Air Coil Unit | 8 | 3696 | 0 | 1 | 0 | 0 | 20 | 3
- | imc office | 105 | 7 | Yes | 20 | 3283 | 74 | 74 | Air Coil Unit | 8 | 26264 | 0.23987 | 1.062 | 0.25475 | 0 | 20.2548 | 3
- | imc storage | 70 | 4 |  |  | 255 | 5 | 4 | Air Coil Unit | 8 | 2040 | 2.0588 | 1 | 2.0588 | 1 | 2.0588 | 1
- | material production | 210 | 14 | Yes | 20 | 625 | 14 | 14 | Air Coil Unit | 8 | 5000 | 2.52 | 1 | 2.52 | 1 | 22.52 | 3
- | open library | 1180 | 78 |  |  | 3360 | 76 | 76 | Air Coil Unit | 8 | 26880 | 2.6339 | 1.062 | 2.7973 | 1 | 2.7973 | 1
- | Gym Office |  | 0 | Yes | 20 | 168 | 3 | 3 |  | 8 | 1344 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym | 7824 | 521 |  |  | 4860 | 110 | 110 |  | 8 | 38880 | 12.0741 | 1.062 | 12.8231 | 3 | 12.8231 | 3
Sheet Last Modified: | 2021-03-18
School: | Parkway Center City Middle College @ Stoddart Fleisher
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | kitchen |  | 0 |  |  | 837 | 19 | 0 |  | 8 | 6696 | 0 | 1 | 0 | 0 | 0 | 0
- | lunchroom |  | 0 |  |  | 3822 | 86 | 0 |  | 8 | 30576 | 0 | 1.062 | 0 | 0 | 0 | 0
- | art room |  | 0 |  |  | 782 | 17 | 0 |  | 8 | 6256 | 0 | 1 | 0 | 0 | 0 | 0
506 | art room |  | 0 |  |  | 851 | 19 | 0 |  | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
505B | office |  | 0 |  |  | 528 | 12 | 0 |  | 8 | 4224 | 0 | 1 | 0 | 0 | 0 | 0
505 | classroom |  | 0 |  |  | 1078 | 24 | 0 |  | 8 | 8624 | 0 | 1 | 0 | 0 | 0 | 0
504 | classroom |  | 0 |  |  | 1144 | 26 | 0 |  | 8 | 9152 | 0 | 1 | 0 | 0 | 0 | 0
503A | office |  | 0 |  |  | 96 | 2 | 0 |  | 8 | 768 | 0 | 1 | 0 | 0 | 0 | 0
503B | shop |  | 0 |  |  | 252 | 5 | 0 |  | 8 | 2016 | 0 | 1 | 0 | 0 | 0 | 0
- | teacher's lounge |  | 0 |  |  | 621 | 14 | 0 |  | 8 | 4968 | 0 | 1 | 0 | 0 | 0 | 0
502 | classroom |  | 0 |  |  | 552 | 12 | 0 |  | 8 | 4416 | 0 | 1 | 0 | 0 | 0 | 0
501 | classroom |  | 0 |  |  | 640 | 14 | 0 |  | 8 | 5120 | 0 | 1 | 0 | 0 | 0 | 0
411 | classroom |  | 0 |  |  | 770 | 17 | 0 |  | 8 | 6160 | 0 | 1 | 0 | 0 | 0 | 0
410 | classroom |  | 0 |  |  | 805 | 18 | 0 |  | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
409 | classroom |  | 0 |  |  | 713 | 16 | 0 |  | 8 | 5704 | 0 | 1 | 0 | 0 | 0 | 0
408 | classroom |  | 0 |  |  | 716 | 16 | 0 |  | 8 | 5728 | 0 | 1 | 0 | 0 | 0 | 0
407 | classroom |  | 0 |  |  | 748 | 17 | 0 |  | 8 | 5984 | 0 | 1 | 0 | 0 | 0 | 0
406 | classroom |  | 0 |  |  | 704 | 16 | 0 |  | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
405B | counselor |  | 0 |  |  | 135 | 3 | 0 |  | 8 | 1080 | 0 | 1 | 0 | 0 | 0 | 0
405A | VP office |  | 0 |  |  | 506 | 11 | 0 |  | 8 | 4048 | 0 | 1 | 0 | 0 | 0 | 0
404 | classroom |  | 0 |  |  | 644 | 14 | 0 |  | 8 | 5152 | 0 | 1 | 0 | 0 | 0 | 0
403 | classroom |  | 0 |  |  | 621 | 14 | 0 |  | 8 | 4968 | 0 | 1 | 0 | 0 | 0 | 0
402 | classroom |  | 0 |  |  | 598 | 13 | 0 |  | 8 | 4784 | 0 | 1 | 0 | 0 | 0 | 0
401 | classroom |  | 0 |  |  | 640 | 14 | 0 |  | 8 | 5120 | 0 | 1 | 0 | 0 | 0 | 0
310 | classroom |  | 0 |  |  | 704 | 16 | 0 |  | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
309 | weight room |  | 0 |  |  | 920 | 20 | 0 |  | 8 | 7360 | 0 | 1 | 0 | 0 | 0 | 0
308 | classroom |  | 0 |  |  | 897 | 20 | 0 |  | 8 | 7176 | 0 | 1 | 0 | 0 | 0 | 0
307 | classroom |  | 0 |  |  | 858 | 19 | 0 |  | 8 | 6864 | 0 | 1 | 0 | 0 | 0 | 0
306 | storage room |  | 0 |  |  | 682 | 15 | 0 |  | 8 | 5456 | 0 | 1 | 0 | 0 | 0 | 0
305 | classroom |  | 0 |  |  | 660 | 15 | 0 |  | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
304 | classroom |  | 0 |  |  | 726 | 16 | 0 |  | 8 | 5808 | 0 | 1 | 0 | 0 | 0 | 0
303A | office |  | 0 |  |  | 161 | 3 | 0 |  | 8 | 1288 | 0 | 1 | 0 | 0 | 0 | 0
303 | classroom |  | 0 |  |  | 713 | 16 | 0 |  | 8 | 5704 | 0 | 1 | 0 | 0 | 0 | 0
302 | classroom |  | 0 |  |  | 682 | 15 | 0 |  | 8 | 5456 | 0 | 1 | 0 | 0 | 0 | 0
301A | computer office |  | 0 |  |  | 184 | 4 | 0 |  | 8 | 1472 | 0 | 1 | 0 | 0 | 0 | 0
301 | classroom |  | 0 |  |  | 640 | 14 | 0 |  | 8 | 5120 | 0 | 1 | 0 | 0 | 0 | 0
- | Boys locker room |  | 0 |  |  | 360 | 8 | 0 |  | 8 | 2880 | 0 | 1 | 0 | 0 | 0 | 0
- | Gym |  | 0 |  |  | 3300 | 75 | 0 |  | 8 | 26400 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Girls Locker room |  | 0 |  |  | 324 | 7 | 0 |  | 8 | 2592 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurses office |  | 0 |  |  | 240 | 5 | 0 |  | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
- | Exam Room |  | 0 |  |  | 150 | 3 | 0 |  | 8 | 1200 | 0 | 1 | 0 | 0 | 0 | 0
208 | classroom |  | 0 |  |  | 598 | 13 | 0 |  | 8 | 4784 | 0 | 1 | 0 | 0 | 0 | 0
207 | classroom |  | 0 |  |  | 598 | 13 | 0 |  | 8 | 4784 | 0 | 1 | 0 | 0 | 0 | 0
206 | classroom |  | 0 |  |  | 644 | 14 | 0 |  | 8 | 5152 | 0 | 1 | 0 | 0 | 0 | 0
205 | Library |  | 0 |  |  | 1081 | 24 | 0 |  | 8 | 8648 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office Area |  | 0 |  |  | 285 | 6 | 0 |  | 8 | 2280 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office Waiting area |  | 0 |  |  | 150 | 3 | 0 |  | 8 | 1200 | 0 | 1 | 0 | 0 | 0 | 0
- | Principal's office |  | 0 |  |  | 280 | 6 | 0 |  | 8 | 2240 | 0 | 1 | 0 | 0 | 0 | 0
204 | classroom |  | 0 |  |  | 616 | 14 | 0 |  | 8 | 4928 | 0 | 1 | 0 | 0 | 0 | 0
203 | classroom |  | 0 |  |  | 621 | 14 | 0 |  | 8 | 4968 | 0 | 1 | 0 | 0 | 0 | 0
202 | classroom |  | 0 |  |  | 598 | 13 | 0 |  | 8 | 4784 | 0 | 1 | 0 | 0 | 0 | 0
201 | counselor's Sitting area |  | 0 |  |  | 200 | 4 | 0 |  | 8 | 1600 | 0 | 1 | 0 | 0 | 0 | 0
201A | counselor's A |  | 0 |  |  | 96 | 2 | 0 |  | 8 | 768 | 0 | 1 | 0 | 0 | 0 | 0
201B | counselor's B |  | 0 |  |  | 132 | 3 | 0 |  | 8 | 1056 | 0 | 1 | 0 | 0 | 0 | 0
201C | counselor's C |  | 0 |  |  | 121 | 2 | 0 |  | 8 | 968 | 0 | 1 | 0 | 0 | 0 | 0
201D | counsel's D |  | 0 |  |  | 121 | 2 | 0 |  | 8 | 968 | 0 | 1 | 0 | 0 | 0 | 0
105 | conferance room |  | 0 |  |  | 598 | 13 | 0 |  | 8 | 4784 | 0 | 1 | 0 | 0 | 0 | 0
104A | classroom |  | 0 |  |  | 247 | 5 | 0 |  | 8 | 1976 | 0 | 1 | 0 | 0 | 0 | 0
104B | office |  | 0 |  |  | 117 | 2 | 0 |  | 8 | 936 | 0 | 1 | 0 | 0 | 0 | 0
104C | office |  | 0 |  |  | 112 | 2 | 0 |  | 8 | 896 | 0 | 1 | 0 | 0 | 0 | 0
104D | office |  | 0 |  |  | 90 | 2 | 0 |  | 8 | 720 | 0 | 1 | 0 | 0 | 0 | 0
104E | office |  | 0 |  |  | 99 | 2 | 0 |  | 8 | 792 | 0 | 1 | 0 | 0 | 0 | 0
- | Regional office |  | 0 |  |  | No Access | 0 | 0
- | Data room |  | 0 |  |  | 484 | 11 | 0 |  | 8 | 3872 | 0 | 1 | 0 | 0 | 0 | 0
102A | classroom |  | 0 |  |  | 693 | 15 | 0 |  | 8 | 5544 | 0 | 1 | 0 | 0 | 0 | 0
102C | office |  | 0 |  |  | 195 | 4 | 0 |  | 8 | 1560 | 0 | 1 | 0 | 0 | 0 | 0
102E | classroom |  | 0 |  |  | 513 | 11 | 0 |  | 8 | 4104 | 0 | 1 | 0 | 0 | 0 | 0
102D | office |  | 0 |  |  | 635 | 14 | 0 |  | 8 | 5080 | 0 | 1 | 0 | 0 | 0 | 0
102B | office |  | 0 |  |  | 195 | 4 | 0 |  | 8 | 1560 | 0 | 1 | 0 | 0 | 0 | 0
101 | counselor |  | 0 |  |  | 306 | 6 | 0 |  | 8 | 2448 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium |  | 0 |  |  | 4539 | 103 | 0 |  | 8 | 36312 | 0 | 1.062 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18
School: | Strawberry Mansion High School
School: | Leslie P. Hill Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Strawberry Mansion
101 | Music Rm. | 0 | 0 |  |  | 1288 | 29 | 0 | Heating Unit Ventilator | 8 | 10304 | 0 | 1 | 0 | 0 | 0 | 0
102 | Classroom | 542 | 36 |  |  | 768 | 17 | 17 | Univent | 8 | 6144 | 5.293 | 1 | 5.293 | 2 | 5.293 | 2
103 | Music Rm. | 78 | 5 |  |  | 1288 | 29 | 5 | Heating Unit Ventilator | 8 | 10304 | 0.45419 | 1 | 0.45419 | 0 | 0.45419 | 0
104 | Classroom | 427 | 28 |  |  | 888 | 20 | 20 | Univent | 8 | 7104 | 3.6064 | 1 | 3.6064 | 1 | 3.6064 | 1
108 | Classroom | 0 | 0 |  |  | 888 | 20 | 0 | Univent | 8 | 7104 | 0 | 1 | 0 | 0 | 0 | 0
109A & 109B | Classroom | 620 | 41 |  |  | 1288 | 29 | 29 | Heating Unit Ventilator | 8 | 10304 | 3.6102 | 1 | 3.6102 | 1 | 3.6102 | 1
110 | Classroom | 695 | 46 |  |  | 888 | 20 | 20 | Univent | 8 | 7104 | 5.8699 | 1 | 5.8699 | 2 | 5.8699 | 2
111 | Classroom | 444 | 29 |  |  | 288 | 6 | 6 | Univent | 8 | 2304 | 11.5625 | 1 | 11.5625 | 3 | 11.5625 | 3
112 | Classroom | 0 | 0 |  |  | 888 | 20 | 0 | Univent | 8 | 7104 | 0 | 1 | 0 | 0 | 0 | 0
200 | Classroom | 0 | 0 |  |  | 1056 | 24 | 0 | Univent | 8 | 8448 | 0 | 1 | 0 | 0 | 0 | 0
201 | Classroom | 416 | 27 |  |  | 805 | 18 | 18 | Univent | 8 | 6440 | 3.8758 | 1 | 3.8758 | 1 | 3.8758 | 1
202 | Classroom | 357 | 23 |  |  | 1152 | 26 | 23 | Univent | 8 | 9216 | 2.3242 | 1 | 2.3242 | 1 | 2.3242 | 1
203 | Classroom | 607 | 40 |  |  | 782 | 17 | 17 | Univent | 8 | 6256 | 5.8216 | 1 | 5.8216 | 2 | 5.8216 | 2
206 | Classroom | 0 | 0 |  |  | 805 | 18 | 0 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
207 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
208 | Classroom | 512 | 34 |  |  | 1104 | 25 | 25 | Univent | 8 | 8832 | 3.4783 | 1 | 3.4783 | 1 | 3.4783 | 1
209 | Computer Lab | 859 | 57 |  |  | 1012 | 23 | 23 | Air Handling Unit | 8 | 8096 | 6.3661 | 1 | 6.3661 | 2 | 6.3661 | 2
212 | Classroom | 382 | 25 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 3.3666 | 1 | 3.3666 | 1 | 3.3666 | 1
214 | Classroom | 301 | 20 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 2.6528 | 1 | 2.6528 | 1 | 2.6528 | 1
216 | Classroom | 350 | 23 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 3.0846 | 1 | 3.0846 | 1 | 3.0846 | 1
217 | Classroom | 516 | 34 |  |  | 1012 | 23 | 23 | Univent | 8 | 8096 | 3.8241 | 1 | 3.8241 | 1 | 3.8241 | 1
219 | Classroom | 0 | 0 |  |  | 960 | 21 | 0 | Univent | 8 | 7680 | 0 | 1 | 0 | 0 | 0 | 0
220 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
222 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
224 | Classroom | 0 | 0 |  |  | 782 | 17 | 0 | Univent | 8 | 6256 | 0 | 1 | 0 | 0 | 0 | 0
300 | Classroom | 464 | 30 |  |  | 782 | 17 | 17 | Univent | 8 | 6256 | 4.4501 | 1 | 4.4501 | 2 | 4.4501 | 2
301 | Classroom | 0 | 0 |  |  | 805 | 18 | 0 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom | 401 | 26 |  |  | 782 | 17 | 17 | Univent | 8 | 6256 | 3.8459 | 1 | 3.8459 | 1 | 3.8459 | 1
303 | Classroom | 0 | 0 |  |  | 805 | 18 | 0 | Univent | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
304 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom | 442 | 29 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 3.8954 | 1 | 3.8954 | 1 | 3.8954 | 1
308 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
309 | Classroom | 335 | 22 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 2.9524 | 1 | 2.9524 | 1 | 2.9524 | 1
310 | Classroom | 430 | 28 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 3.7897 | 1 | 3.7897 | 1 | 3.7897 | 1
311 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
312 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
314 | Classroom | 446 | 29 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 3.9307 | 1 | 3.9307 | 1 | 3.9307 | 1
315 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
316 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
317 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
319 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
320 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
322 | Classroom | 459 | 30 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 4.0452 | 1 | 4.0452 | 2 | 4.0452 | 2
323 | Classroom | 601 | 40 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 5.2967 | 1 | 5.2967 | 2 | 5.2967 | 2
324 | Classroom | 466 | 31 |  |  | 782 | 17 | 17 | Univent | 8 | 6256 | 4.4693 | 1 | 4.4693 | 2 | 4.4693 | 2
325 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
400A&B | Classroom | 0 | 0 |  |  | 598 | 13 | 0 | Univent | 8 | 4784 | 0 | 1 | 0 | 0 | 0 | 0
401A | Classroom | 488 | 32 |  |  | 345 | 7 | 7 | Univent | 8 | 2760 | 10.6087 | 1 | 10.6087 | 3 | 10.6087 | 3
402 | Classroom | 465 | 31 |  |  | 1288 | 29 | 29 | Univent | 8 | 10304 | 2.7077 | 1 | 2.7077 | 1 | 2.7077 | 1
403 | Classroom | 250 | 16 |  |  | 299 | 6 | 6 | Univent | 8 | 2392 | 6.2709 | 1 | 6.2709 | 2 | 6.2709 | 2
404 | Classroom | 434 | 28 |  |  | 1196 | 27 | 27 | Univent | 8 | 9568 | 2.7216 | 1 | 2.7216 | 1 | 2.7216 | 1
405 | Classroom | 503 | 33 |  |  | 987 | 22 | 22 | Univent | 8 | 7896 | 3.8222 | 1 | 3.8222 | 1 | 3.8222 | 1
406 | Classroom | 239 | 15 |  |  | 666 | 15 | 15 | Univent | 8 | 5328 | 2.6914 | 1 | 2.6914 | 1 | 2.6914 | 1
407 | Classroom | 236 | 15 |  |  | 375 | 8 | 8 | Univent | 8 | 3000 | 4.72 | 1 | 4.72 | 2 | 4.72 | 2
408 | Classroom | 456 | 30 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 4.0188 | 1 | 4.0188 | 2 | 4.0188 | 2
409 | Classroom | 0 | 0 |  |  | 1288 | 29 | 0 | Univent | 8 | 10304 | 0 | 1 | 0 | 0 | 0 | 0
410 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
412 | Classroom | 431 | 28 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 3.7985 | 1 | 3.7985 | 1 | 3.7985 | 1
413 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
414 | Classroom | 467 | 31 |  |  | 851 | 19 | 19 | Univent | 8 | 6808 | 4.1157 | 1 | 4.1157 | 2 | 4.1157 | 2
415 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
417 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
418 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
420 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
421 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
422 | Classroom | 0 | 0 |  |  | 782 | 17 | 0 | Univent | 8 | 6256 | 0 | 1 | 0 | 0 | 0 | 0
423 | Classroom | 0 | 0 |  |  | 851 | 19 | 0 | Univent | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
500 | Classroom | 280 | 18 |  |  | 800 | 18 | 18 | Univent | 8 | 6400 | 2.625 | 1 | 2.625 | 1 | 2.625 | 1
500B | Classroom | 264 | 17 |  |  | 375 | 8 | 8 | Univent | 8 | 3000 | 5.28 | 1 | 5.28 | 2 | 5.28 | 2
502 | Classroom | 442 | 29 |  |  | 300 | 6 | 6 | Univent | 8 | 2400 | 11.05 | 1 | 11.05 | 3 | 11.05 | 3
505 | Classroom | 0 | 0 |  |  | 1300 | 29 | 0 | Univent | 8 | 10400 | 0 | 1 | 0 | 0 | 0 | 0
506 | Classroom | 0 | 0 |  |  | 925 | 21 | 0 | Univent | 8 | 7400 | 0 | 1 | 0 | 0 | 0 | 0
507 | Classroom | 0 | 0 |  |  | 425 | 9 | 0 | Univent | 8 | 3400 | 0 | 1 | 0 | 0 | 0 | 0
508 | Classroom | 487 | 32 |  |  | 1250 | 28 | 28 | Univent | 8 | 10000 | 2.922 | 1 | 2.922 | 1 | 2.922 | 1
509 | Classroom | 0 | 0 |  |  | 1100 | 25 | 0 | Univent | 8 | 8800 | 0 | 1 | 0 | 0 | 0 | 0
513 | Classroom | 489 | 32 |  |  | 325 | 7 | 7 | Univent | 8 | 2600 | 11.2846 | 1 | 11.2846 | 3 | 11.2846 | 3
516 | Classroom | 0 | 0 |  |  | 1327 | 30 | 0 | Univent | 8 | 10616 | 0 | 1 | 0 | 0 | 0 | 0
517 | Classroom | 0 | 0 |  |  | 1162 | 26 | 0 | Univent | 8 | 9296 | 0 | 1 | 0 | 0 | 0 | 0
518 | Classroom | 0 | 0 |  |  | 1375 | 31 | 0 | Univent | 8 | 11000 | 0 | 1 | 0 | 0 | 0 | 0
519 | Classroom | 292 | 19 |  |  | 570 | 12 | 12 | Univent | 8 | 4560 | 3.8421 | 1 | 3.8421 | 1 | 3.8421 | 1
520 | Classroom | 683 | 45 |  |  | 1447 | 32 | 32 | Univent | 8 | 11576 | 3.5401 | 1 | 3.5401 | 1 | 3.5401 | 1
522 | Classroom | 0 | 0 |  |  | 1471 | 33 | 0 | Univent | 8 | 11768 | 0 | 1 | 0 | 0 | 0 | 0
- | Library | 1247 | 83 |  |  | 1863 | 42 | 42 | Air Handling Unit | 8 | 14904 | 5.0201 | 1 | 5.0201 | 2 | 5.0201 | 2
- | Culinary Arts area | 1077 | 71 |  |  | 6536 | 148 | 71 | Air Handling Unit | 8 | 52288 | 1.2358 | 1.4912 | 1.8428 | 1 | 1.8428 | 1
- | Book Strg. Rm. Security office | 0 | 0 |  |  | 1733 | 39 | 0 | Air Handling Unit | 8 | 13864 | 0 | 1 | 0 | 0 | 0 | 0
- | DOS office | 0 | 0 |  |  |  | 0 | 0 | Univent
- | EST office | 513 | 34 |  |  |  | 0 | 0 | Univent
| Serves unknown | 0 | 0 |  |  |  | 0 | 0 | Heating Unit Ventilator
- | Auditorium | 7054 | 470 |  |  | 9936 | 225 | 225 | Heating Unit Ventilator | 8 | 79488 | 5.3246 | 1.4912 | 7.9398 | 2 | 7.9398 | 2
- | Cafeteria | 1912 | 127 |  |  | 10725 | 243 | 127 | Heating Unit Ventilator | 8 | 85800 | 1.3371 | 1.4912 | 1.9938 | 1 | 1.9938 | 1
- | Aud. Stage | 2999 | 199 |  |  | 2668 | 60 | 60 | Heating Unit Ventilator | 8 | 21344 | 8.4305 | 1.062 | 8.9535 | 2 | 8.9535 | 2
- | Unknown location and what it serves |  | 0 |  |  |  | 0 | 0 | Heating Unit Ventilator
- | Maintenance office, Lobby | 317 | 21 |  |  |  | 0 | 0 | Heating Unit Ventilator
- | Girls Locker Room | 1759 | 117 |  |  |  | 0 | 0 | Heating Unit Ventilator
- | Girls Gym | 885 | 59 |  |  | 5808 | 132 | 59 | Heating Unit Ventilator | 8 | 46464 | 1.1428 | 1.062 | 1.2137 | 1 | 1.2137 | 1
- | Boys Locker Room | 126 | 8 |  |  |  | 0 | 0 | Heating Unit Ventilator
- | Boys Gym | 6081 | 405 |  |  | 5808 | 132 | 132 | Heating Unit Ventilator | 8 | 46464 | 7.8525 | 1.062 | 8.3397 | 2 | 8.3397 | 2
- | Unknown location and what it serves |  | 0 |  |  |  | 0 | 0 | Heating Unit Ventilator
- | Music Prac. Rms. & Office | 607 | 40 |  |  |  | 0 | 0 | Heating Unit Ventilator
- | Nurses area, Admin areas | 796 | 53 |  |  |  | 0 | 0 | Heating Unit Ventilator
- | Unknown |  | 0 |  |  |  | 0 | 0 | Heating Unit Ventilator
- | Unknown |  | 0 |  |  |  | 0 | 0 | Heating Unit Ventilator
LP Hill Building
1 | Office | 0 | 0 |  |  | 870.365 | 19 | 0 | Vertical ACU | 8 | 6962.92 | 0 | 1 | 0 | 0 | 0 | 0
4 | Office | 0 | 0 |  |  | 409.462 | 9 | 0 | Vertical Air Coil Unit and Univent | 8 | 3275.696 | 0 | 1 | 0 | 0 | 0 | 0
5 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Vertical Air Coil Unit and Univent
7 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Vertical Air Coil Unit and Univent
7 | Conference Rm. | 0 | 0 |  |  | 1111.66 | 25 | 0 | Vertical Air Coil Unit and Univent | 8 | 8893.28 | 0 | 1 | 0 | 0 | 0 | 0
10 | Storage Room | 0 | 0 |  |  | 454.88 | 10 | 0 | Vertical Air Coil Unit | 8 | 3639.04 | 0 | 1 | 0 | 0 | 0 | 0
12 | Truency Court | 0 | 0 |  |  | 988.792 | 22 | 0 | Vertical Air Coil Unit | 8 | 7910.336 | 0 | 1 | 0 | 0 | 0 | 0
14 | Truency Court | 0 | 0 |  |  | 715.596 | 16 | 0 | Univent | 8 | 5724.768 | 0 | 1 | 0 | 0 | 0 | 0
15 | General Room | 0 | 0 |  |  | 734.479 | 16 | 0 | Vertical Air Coil Unit and Univent | 8 | 5875.832 | 0 | 1 | 0 | 0 | 0 | 0
100 | Classroom | 0 | 0 |  |  | 982.127 | 22 | 0 | Vertical Air Coil Unit and Univent | 8 | 7857.016 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom | 0 | 0 |  |  | 1041.52 | 23 | 0 | Vertical Air Coil Unit and Univent | 8 | 8332.16 | 0 | 1 | 0 | 0 | 0 | 0
102 | Classroom | 0 | 0 |  |  | 973.903 | 22 | 0 | Univent | 8 | 7791.224 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom | 0 | 0 |  |  | 1054.8 | 23 | 0 | Vertical Air Coil Unit and Univent | 8 | 8438.4 | 0 | 1 | 0 | 0 | 0 | 0
104 | Classroom | 0 | 0 |  |  | 1022.271 | 23 | 0 | Univent | 8 | 8178.168 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom | 0 | 0 |  |  | 875 | 19 | 0 | Univent | 8 | 7000 | 0 | 1 | 0 | 0 | 0 | 0
106 | Classroom | 160 | 10 |  |  | 933.66 | 21 | 10 | Univent | 8 | 7469.28 | 1.2853 | 1 | 1.2853 | 1 | 1.2853 | 1
107 | Classroom | 15 | 1 |  |  | 1492.29 | 33 | 1 | Univent | 8 | 11938.32 | 0.075387 | 1 | 0.075387 | 0 | 0.075387 | 0
108 | Classroom | 224 | 14 |  |  | 1492.29 | 33 | 14 | Univent | 8 | 11938.32 | 1.1258 | 1 | 1.1258 | 1 | 1.1258 | 1
200 | Office | 0 | 0 |  |  | 917.724 | 20 | 0 | Univent | 8 | 7341.792 | 0 | 1 | 0 | 0 | 0 | 0
202 | Office | 294 | 19 |  |  | 1034 | 23 | 19 | Univent | 8 | 8272 | 2.1325 | 1 | 2.1325 | 1 | 2.1325 | 1
203 | Office | 0 | 0 |  |  | 833.94 | 18 | 0 | Univent | 8 | 6671.52 | 0 | 1 | 0 | 0 | 0 | 0
204 | Office | 50 | 3 |  |  | 1034 | 23 | 3 | Univent | 8 | 8272 | 0.36267 | 1 | 0.36267 | 0 | 0.36267 | 0
205 | Office | 0 | 0 |  |  | 1033.59 | 23 | 0 | Univent | 8 | 8268.72 | 0 | 1 | 0 | 0 | 0 | 0
206 | Office | 0 | 0 |  |  | 951.5 | 21 | 0 | Univent | 8 | 7612 | 0 | 1 | 0 | 0 | 0 | 0
207 | Office | 31 | 2 |  |  | 1033.59 | 23 | 2 | Univent | 8 | 8268.72 | 0.22494 | 1 | 0.22494 | 0 | 0.22494 | 0
209 | Office | 119 | 7 |  |  | 1031.06 | 23 | 7 | Univent | 8 | 8248.48 | 0.86561 | 1 | 0.86561 | 0 | 0.86561 | 0
210 | Office | 0 | 0 |  |  | 1009.73 | 22 | 0 | Univent | 8 | 8077.84 | 0 | 1 | 0 | 0 | 0 | 0
212 | Office | 169 | 11 |  |  | 882.972 | 20 | 11 | Univent | 8 | 7063.776 | 1.4355 | 1 | 1.4355 | 1 | 1.4355 | 1
213 | Office | 0 | 0 |  |  | 940.62 | 21 | 0 | Univent | 8 | 7524.96 | 0 | 1 | 0 | 0 | 0 | 0
214 | Waiting area | 0 | 0 |  |  | 912.502 | 20 | 0 | Univent | 8 | 7300.016 | 0 | 1 | 0 | 0 | 0 | 0
215 | Waiting area | 0 | 0 |  |  | 1025.81 | 23 | 0 | Univent | 8 | 8206.48 | 0 | 1 | 0 | 0 | 0 | 0
300 | Classroom | 216 | 14 |  |  | 922.898 | 20 | 14 | Univent | 8 | 7383.184 | 1.7553 | 1 | 1.7553 | 1 | 1.7553 | 1
301 | Classroom | 0 | 0 |  |  | 921.33 | 20 | 0 | Univent | 8 | 7370.64 | 0 | 1 | 0 | 0 | 0 | 0
302 | Classroom | 0 | 0 |  |  | 1010.47 | 22 | 0 | Univent | 8 | 8083.76 | 0 | 1 | 0 | 0 | 0 | 0
303 | Classroom | 0 | 0 |  |  | 912.38 | 20 | 0 | Univent | 8 | 7299.04 | 0 | 1 | 0 | 0 | 0 | 0
304 | Classroom | 0 | 0 |  |  | 986.631 | 22 | 0 | Univent | 8 | 7893.048 | 0 | 1 | 0 | 0 | 0 | 0
305 | Classroom | 25 | 1 |  |  | 618.57 | 14 | 1 | Univent | 8 | 4948.56 | 0.30312 | 1 | 0.30312 | 0 | 0.30312 | 0
306 | Classroom | 0 | 0 |  |  | 932.119 | 21 | 0 | Univent | 8 | 7456.952 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
309 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
310 | Classroom | 280 | 18 |  |  | 1009.5 | 22 | 18 | Univent | 8 | 8076 | 2.0802 | 1 | 2.0802 | 1 | 2.0802 | 1
312 | Classroom | 0 | 0 |  |  | 992.166 | 22 | 0 | Univent | 8 | 7937.328 | 0 | 1 | 0 | 0 | 0 | 0
313 | Classroom | 0 | 0 |  |  | 978.97 | 22 | 0 | Univent | 8 | 7831.76 | 0 | 1 | 0 | 0 | 0 | 0
314 | Classroom | 0 | 0 |  |  | 911.255 | 20 | 0 | Univent | 8 | 7290.04 | 0 | 1 | 0 | 0 | 0 | 0
315 | Classroom |  | 0 |  |  | 863.91 | 19 | 0 | Univent | 8 | 6911.28 | 0 | 1 | 0 | 0 | 0 | 0
400 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
401 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
402 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
403 | Classroom | 194 | 12 |  |  |  | 0 | 0 | Univent
404 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
405 | Classroom | 92 | 6 |  |  |  | 0 | 0 | Univent
406 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
407 | Classroom | 131 | 8 |  |  |  | 0 | 0 | Univent
409 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
410 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
411/413 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
412 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
414 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
415 | Classroom | 0 | 0 |  |  |  | 0 | 0 | Univent
- | Faculty Rm. | 0 | 0 |  |  |  | 0 | 0 | Univent
- | Main office | 0 | 0 |  |  | 1107.41 | 25 | 0 | Univent | 8 | 8859.28 | 0 | 1 | 0 | 0 | 0 | 0
- | Princ. Office | 682 | 45 |  |  | 355.756 | 8 | 8 | Univent | 8 | 2846.048 | 14.3778 | 1 | 14.3778 | 3 | 14.3778 | 3
Sheet Last Modified: | 2021-04-27
School: | James J. Sullivan Elementary School
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B7 | Classroom |  | 0 | Yes | 20 | 610 | 13 | 13 | House Fan | 8 | 4880 | 0 | 1 | 0 | 0 | 20 | 3
B2 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
- | Library |  | 0 | Yes | 20 | 968 | 22 | 22 | House Fan | 8 | 7744 | 0 | 1 | 0 | 0 | 20 | 3
B9 | Classroom |  | 0 |  |  | 506 | 11 | 0 | House Fan | 8 | 4048 | 0 | 1 | 0 | 0 | 0 | 0
- | Kitchen |  | 0 |  |  | 704 | 16 | 0 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom |  | 0 | Yes | 20 | 920 | 20 | 20 | House Fan | 8 | 7360 | 0 | 1 | 0 | 0 | 20 | 3
102 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom |  | 0 |  |  | 736 | 16 | 0 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 0 | 0
104 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
105 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 | Yes | 20 | 275 | 6 | 6 |  | 8 | 2200 | 0 | 1 | 0 | 0 | 20 | 3
107a | office |  | 0 | Yes | 20 | 115 | 2 | 2 | House Fan | 8 | 920 | 0 | 1 | 0 | 0 | 20 | 3
107b | office |  | 0 | Yes | 20 | 115 | 2 | 2 | House Fan | 8 | 920 | 0 | 1 | 0 | 0 | 20 | 3
107c | office |  | 0 | Yes | 20 | 115 | 2 | 2 | House Fan | 8 | 920 | 0 | 1 | 0 | 0 | 20 | 3
108 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
110 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
- | Main Office |  | 0 | Yes | 20 | 336 | 7 | 7 | House Fan | 8 | 2688 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 20 | 210 | 4 | 4 | House Fan | 8 | 1680 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
206 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom |  | 0 | Yes | 20 | 192 | 4 | 4 | House Fan | 8 | 1536 | 0 | 1 | 0 | 0 | 20 | 3
214 | Classroom |  | 0 | Yes | 20 | 384 | 8 | 8 | House Fan | 8 | 3072 | 0 | 1 | 0 | 0 | 20 | 3
215 | Office |  | 0 | Yes | 20 | 195 | 4 | 4 | House Fan | 8 | 1560 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurses Office |  | 0 | Yes | 20 | 264 | 6 | 6 | House Fan | 8 | 2112 | 0 | 1 | 0 | 0 | 20 | 3
300 | Classroom |  | 0 | Yes | 20 | 720 | 16 | 16 | House Fan | 8 | 5760 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
306 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom |  | 0 | Yes | 20 | 690 | 15 | 15 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
307B | Classroom |  | 0 | Yes | 20 | 119 | 2 | 2 |  | 8 | 952 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
309 | Computer Room |  | 0 |  |  | 690 | 15 | 0 | House Fan | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 | House Fan | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
311 | Office |  | 0 | Yes | 20 | 192 | 4 | 4 | House Fan | 8 | 1536 | 0 | 1 | 0 | 0 | 20 | 3
- | Cafe/Gym |  | 0 | Yes | 20 | 3432 | 78 | 78 | Hydroxyl Unit | 8 | 27456 | 0 | 1.062 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-27
School: | Parkway West High School @ Sulzberger
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | - |  | 0 |  |  | 483 | 10 | 0 |  | 8 | 3864 | 0 | 1 | 0 | 0 | 0 | 0
101 | - |  | 0 |  |  | 575 | 13 | 0 |  | 8 | 4600 | 0 | 1 | 0 | 0 | 0 | 0
102 | - |  | 0 |  |  | 851 | 19 | 0 |  | 8 | 6808 | 0 | 1 | 0 | 0 | 0 | 0
106 | - |  | 0 |  |  | 920 | 20 | 0 |  | 8 | 7360 | 0 | 1 | 0 | 0 | 0 | 0
107 | - |  | 0 | Yes | 20 | 943 | 21 | 21 |  | 8 | 7544 | 0 | 1 | 0 | 0 | 20 | 3
108 | - |  | 0 | Yes | 20 | 874 | 19 | 19 |  | 8 | 6992 | 0 | 1 | 0 | 0 | 20 | 3
109 | - |  | 0 |  |  | 920 | 20 | 0 |  | 8 | 7360 | 0 | 1 | 0 | 0 | 0 | 0
201 | - |  | 0 |  |  | 682 | 15 | 0 |  | 8 | 5456 | 0 | 1 | 0 | 0 | 0 | 0
202 | - |  | 0 |  |  | 660 | 15 | 0 |  | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
203 | - |  | 0 | Yes | 20 | 528 | 12 | 12 |  | 8 | 4224 | 0 | 1 | 0 | 0 | 20 | 3
203A | - |  | 0 | Yes | 20 | 660 | 15 | 15 |  | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
204 | Nurses Office |  | 0 | Yes | 20 | 460 | 10 | 10 |  | 8 | 3680 | 0 | 1 | 0 | 0 | 20 | 3
205 | - |  | 0 | Yes | 20 | 660 | 15 | 15 |  | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
206 | Counselors Office |  | 0 | Yes | 20 | 690 | 15 | 15 |  | 8 | 5520 | 0 | 1 | 0 | 0 | 20 | 3
Principal | Office |  | 0 | Yes | 20 | 322 | 7 | 7 |  | 8 | 2576 | 0 | 1 | 0 | 0 | 20 | 3
208 | Main Office |  | 0 | Yes | 20 | 825 | 18 | 18 |  | 8 | 6600 | 0 | 1 | 0 | 0 | 20 | 3
210 | - |  | 0 |  |  | 836 | 19 | 0 |  | 8 | 6688 | 0 | 1 | 0 | 0 | 0 | 0
211 | - |  | 0 | Yes | 20 | 864 | 19 | 19 |  | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
212 | - |  | 0 | Yes | 20 | 660 | 15 | 15 |  | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
212A | - |  | 0 | Yes | 20 | 660 | 15 | 15 |  | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
213 | - |  | 0 | Yes | 20 | 682 | 15 | 15 |  | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
215 | - |  | 0 |  |  | 816 | 18 | 0 |  | 8 | 6528 | 0 | 1 | 0 | 0 | 0 | 0
216 | - |  | 0 | Yes | 20 | 748 | 17 | 17 |  | 8 | 5984 | 0 | 1 | 0 | 0 | 20 | 3
217 | - |  | 0 | Yes | 20 | 736 | 16 | 16 |  | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
218 | - |  | 0 | Yes | 20 | 704 | 16 | 16 |  | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
219 | - |  | 0 | Yes | 20 | 704 | 16 | 16 |  | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
220 | - |  | 0 | Yes | 20 | 704 | 16 | 16 |  | 8 | 5632 | 0 | 1 | 0 | 0 | 20 | 3
221 | - |  | 0 |  |  | 805 | 18 | 0 |  | 8 | 6440 | 0 | 1 | 0 | 0 | 0 | 0
222 | - |  | 0 |  |  | 690 | 15 | 0 |  | 8 | 5520 | 0 | 1 | 0 | 0 | 0 | 0
301-302 | - |  | 0 | Yes | 20 | 1012 | 23 | 23 |  | 8 | 8096 | 0 | 1 | 0 | 0 | 20 | 3
303 | - |  | 0 | Yes | 20 | 1176 | 26 | 26 |  | 8 | 9408 | 0 | 1 | 0 | 0 | 20 | 3
304 | - |  | 0 | Yes | 20 | 966 | 21 | 21 |  | 8 | 7728 | 0 | 1 | 0 | 0 | 20 | 3
305 | - |  | 0 |  |  | 858 | 19 | 0 |  | 8 | 6864 | 0 | 1 | 0 | 0 | 0 | 0
306 | - |  | 0 | Yes | 20 | 770 | 17 | 17 |  | 8 | 6160 | 0 | 1 | 0 | 0 | 20 | 3
307 | - |  | 0 |  |  | 770 | 17 | 0 |  | 8 | 6160 | 0 | 1 | 0 | 0 | 0 | 0
308 | - |  | 0 | Yes | 20 | 900 | 20 | 20 |  | 8 | 7200 | 0 | 1 | 0 | 0 | 20 | 3
309 | - |  | 0 |  |  | 880 | 20 | 0 |  | 8 | 7040 | 0 | 1 | 0 | 0 | 0 | 0
310 | - |  | 0 |  |  | 880 | 20 | 0 |  | 8 | 7040 | 0 | 1 | 0 | 0 | 0 | 0
311 | - |  | 0 |  |  | 924 | 21 | 0 |  | 8 | 7392 | 0 | 1 | 0 | 0 | 0 | 0
312 | - |  | 0 | Yes | 20 | 682 | 15 | 15 |  | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
313 | - |  | 0 | Yes | 20 | 660 | 15 | 15 |  | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
314 | - |  | 0 | Yes | 20 | 682 | 15 | 15 |  | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
315 | - |  | 0 |  |  | 330 | 7 | 0 |  | 8 | 2640 | 0 | 1 | 0 | 0 | 0 | 0
316 | - |  | 0 | Yes | 20 | 660 | 15 | 15 |  | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
317 | - |  | 0 |  |  | 748 | 17 | 0 |  | 8 | 5984 | 0 | 1 | 0 | 0 | 0 | 0
318 | - |  | 0 | Yes | 20 | 736 | 16 | 16 |  | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
319 | - |  | 0 | Yes | 20 | 616 | 14 | 14 |  | 8 | 4928 | 0 | 1 | 0 | 0 | 20 | 3
320 | - |  | 0 | Yes | 20 | 616 | 14 | 14 |  | 8 | 4928 | 0 | 1 | 0 | 0 | 20 | 3
321 | - |  | 0 |  |  | 704 | 16 | 0 |  | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
322 | - |  | 0 | Yes | 20 | 748 | 17 | 17 |  | 8 | 5984 | 0 | 1 | 0 | 0 | 20 | 3
323 | - |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
- | 3rd Flr. Computer Lab |  | 0 |  |  | 1035 | 23 | 0 |  | 8 | 8280 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium |  | 0 |  |  | 3390 | 77 | 0 |  | 8 | 27120 | 0 | 1.062 | 0 | 0 | 0 | 0
- | North Caf. |  | 0 |  |  | 2680 | 60 | 0 |  | 8 | 21440 | 0 | 1.062 | 0 | 0 | 0 | 0
- | South Caf. |  | 0 | Yes | 20 | 2720 | 61 | 61 |  | 8 | 21760 | 0 | 1.062 | 0 | 0 | 20 | 3
- | South Gym |  | 0 |  |  | 4186 | 95 | 0 |  | 8 | 33488 | 0 | 1.062 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30
School: | Swenson Arts & Technology High School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
49 | Classroom |  | 0 | Yes | 20 | 308 | 7 | 7 |  | 8 | 2464 | 0 | 1 | 0 | 0 | 20 | 3
50 | Classroom |  | 0 |  |  | 308 | 7 | 0 |  | 8 | 2464 | 0 | 1 | 0 | 0 | 0 | 0
51 | Classroom |  | 0 | Yes | 20 | 308 | 7 | 7 |  | 8 | 2464 | 0 | 1 | 0 | 0 | 20 | 3
53 | Classroom |  | 0 | Yes | 20 | 616 | 14 | 14 |  | 8 | 4928 | 0 | 1 | 0 | 0 | 20 | 3
4 | Classroom |  | 0 | Yes | 20 | 532 | 12 | 12 |  | 8 | 4256 | 0 | 1 | 0 | 0 | 20 | 3
5 | Classroom |  | 0 | Yes | 20 | 528 | 12 | 12 |  | 8 | 4224 | 0 | 1 | 0 | 0 | 20 | 3
6 | Classroom |  | 0 |  |  | 132 | 3 | 0 |  | 8 | 1056 | 0 | 1 | 0 | 0 | 0 | 0
100 | Classroom | 242 | 16 |  |  | 1278 | 29 | 16 | Rooftop Unit | 8 | 10224 | 1.4202 | 1 | 1.4202 | 1 | 1.4202 | 1
101 | Classroom | 143 | 9 |  |  | 228 | 5 | 5 | Rooftop Unit | 8 | 1824 | 4.7039 | 1 | 4.7039 | 2 | 4.7039 | 2
102 | Classroom | 76 | 5 |  |  | 149 | 3 | 3 | Rooftop Unit | 8 | 1192 | 3.8255 | 1 | 3.8255 | 1 | 3.8255 | 1
103 | Classroom | 82 | 5 |  |  | 151 | 3 | 3 | Rooftop Unit | 8 | 1208 | 4.0728 | 1 | 4.0728 | 2 | 4.0728 | 2
104 | Classroom | 116 | 7 |  |  | 144 | 3 | 3 | Rooftop Unit | 8 | 1152 | 6.0417 | 1 | 6.0417 | 2 | 6.0417 | 2
105 | Classroom | 40 | 2 |  |  | 110 | 2 | 2 | Rooftop Unit | 8 | 880 | 2.7273 | 1 | 2.7273 | 1 | 2.7273 | 1
105 | Classroom | 55 | 3 |  |  | 200 | 4 | 3 | Rooftop Unit | 8 | 1600 | 2.0625 | 1 | 2.0625 | 1 | 2.0625 | 1
106 | Classroom | 75 | 5 |  |  | 178 | 4 | 4 | Rooftop Unit | 8 | 1424 | 3.1601 | 1 | 3.1601 | 1 | 3.1601 | 1
109 | Classroom | 93 | 6 |  |  | 306 | 6 | 6 | Rooftop Unit | 8 | 2448 | 2.2794 | 1 | 2.2794 | 1 | 2.2794 | 1
110 | Classroom | 70 | 4 |  |  | 159 | 3 | 3 | Rooftop Unit | 8 | 1272 | 3.3019 | 1 | 3.3019 | 1 | 3.3019 | 1
111 | Classroom | 42 | 2 |  |  | 146 | 3 | 2 | Rooftop Unit | 8 | 1168 | 2.1575 | 1 | 2.1575 | 1 | 2.1575 | 1
112 | Classroom | 24 | 1 |  |  | 100 | 2 | 1 | Rooftop Unit | 8 | 800 | 1.8 | 1 | 1.8 | 1 | 1.8 | 1
113 | Classroom | 21 | 1 | Yes | 20 | 105 | 2 | 2 | Rooftop Unit | 8 | 840 | 1.5 | 1 | 1.5 | 1 | 21.5 | 3
114 | Classroom | 135 | 9 |  |  | 602 | 13 | 9 | Rooftop Unit | 8 | 4816 | 1.6819 | 1 | 1.6819 | 1 | 1.6819 | 1
128 | Classroom | 612 | 40 |  |  | 1275 | 28 | 28 | Rooftop Unit | 8 | 10200 | 3.6 | 1 | 3.6 | 1 | 3.6 | 1
129 | Classroom | 39 | 2 |  |  | 144 | 3 | 2 | Rooftop Unit | 8 | 1152 | 2.0312 | 1 | 2.0312 | 1 | 2.0312 | 1
130 | Classroom | 536 | 35 |  |  | 960 | 21 | 21 | Rooftop Unit | 8 | 7680 | 4.1875 | 1 | 4.1875 | 2 | 4.1875 | 2
138 | Classroom | 305 | 20 | Yes | 20 | 1125 | 25 | 25 | Rooftop Unit | 8 | 9000 | 2.0333 | 1 | 2.0333 | 1 | 22.0333 | 3
140 | Classroom | 675 | 45 |  |  | 1085 | 24 | 24 | Rooftop Unit | 8 | 8680 | 4.6659 | 1 | 4.6659 | 2 | 4.6659 | 2
144 | Classroom | 1497 | 99 |  |  | 1734 | 39 | 39 | Rooftop Unit | 8 | 13872 | 6.4749 | 1 | 6.4749 | 2 | 6.4749 | 2
146 | Classroom | 650 | 43 |  |  | 700 | 15 | 15 | Rooftop Unit | 8 | 5600 | 6.9643 | 1 | 6.9643 | 2 | 6.9643 | 2
150 | Classroom | 618 | 41 |  |  | 308 | 7 | 7 | Rooftop Unit | 8 | 2464 | 15.0487 | 1 | 15.0487 | 3 | 15.0487 | 3
164 | Classroom | 305 | 20 |  |  | 899 | 20 | 20 | Rooftop Unit | 8 | 7192 | 2.5445 | 1 | 2.5445 | 1 | 2.5445 | 1
170 | Classroom | 188 | 12 |  |  | 351 | 7 | 7 | Rooftop Unit | 8 | 2808 | 4.0171 | 1 | 4.0171 | 2 | 4.0171 | 2
171 | Classroom | 526 | 35 |  |  | 1461 | 33 | 33 | Rooftop Unit | 8 | 11688 | 2.7002 | 1 | 2.7002 | 1 | 2.7002 | 1
172 | Classroom |  | 0 | Yes | 20 | 126 | 2 | 2 |  | 8 | 1008 | 0 | 1 | 0 | 0 | 20 | 3
176 | Classroom |  | 0 | Yes | 20 | 452 | 10 | 10 |  | 8 | 3616 | 0 | 1 | 0 | 0 | 20 | 3
180 | Classroom | 93 | 6 |  |  | 209 | 4 | 4 | Rooftop Unit | 8 | 1672 | 3.3373 | 1 | 3.3373 | 1 | 3.3373 | 1
182 | Classroom | 251 | 16 | Yes | 20 | 1059 | 24 | 24 | Rooftop Unit | 8 | 8472 | 1.7776 | 1 | 1.7776 | 1 | 21.7776 | 3
184 | Classroom | 228 | 15 | Yes | 20 | 1628 | 37 | 37 | Rooftop Unit | 8 | 13024 | 1.0504 | 1 | 1.0504 | 1 | 21.0504 | 3
195 | Classroom | 439 | 29 |  |  | 1566 | 35 | 29 | Rooftop Unit | 8 | 12528 | 2.1025 | 1 | 2.1025 | 1 | 2.1025 | 1
196 | Classroom | 68 | 4 |  |  | 272 | 6 | 4 | Rooftop Unit | 8 | 2176 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
200 | Classroom | 344 | 22 |  |  | 1624 | 36 | 22 | Rooftop Unit | 8 | 12992 | 1.5887 | 1 | 1.5887 | 1 | 1.5887 | 1
201 & 201A | Classroom | 211 | 14 | Yes | 20 | 660 | 15 | 15 | Rooftop Unit | 8 | 5280 | 2.3977 | 1 | 2.3977 | 1 | 22.3977 | 3
202 | Classroom | 181 | 12 | Yes | 20 | 836 | 19 | 19 | Rooftop Unit | 8 | 6688 | 1.6238 | 1 | 1.6238 | 1 | 21.6238 | 3
203 | Classroom | 190 | 12 |  |  | 760 | 17 | 12 | Rooftop Unit | 8 | 6080 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
204 | Classroom |  | 0 | Yes | 20 | 1584 | 36 | 36 | Rooftop Unit | 8 | 12672 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom | 328 | 21 | Yes | 20 | 1925 | 43 | 43 | Rooftop Unit | 8 | 15400 | 1.2779 | 1 | 1.2779 | 1 | 21.2779 | 3
207 | Classroom | 994 | 66 |  |  | 2300 | 52 | 52 | Rooftop Unit | 8 | 18400 | 3.2413 | 1 | 3.2413 | 1 | 3.2413 | 1
210 | Classroom | 1278 | 85 |  |  | 1020 | 23 | 23 | Rooftop Unit | 8 | 8160 | 9.3971 | 1 | 9.3971 | 2 | 9.3971 | 2
213 | Classroom |  | 0 | Yes | 20 | 748 | 17 | 17 | Rooftop Unit | 8 | 5984 | 0 | 1 | 0 | 0 | 20 | 3
214 | Classroom |  | 0 | Yes | 20 | 126 | 2 | 2 |  | 8 | 1008 | 0 | 1 | 0 | 0 | 20 | 3
216 | Classroom | 410 | 27 |  |  | 1597 | 36 | 27 | Rooftop Unit | 8 | 12776 | 1.9255 | 1 | 1.9255 | 1 | 1.9255 | 1
216 | Classroom | 1578 | 105 |  |  | 1597 | 36 | 36 | Rooftop Unit | 8 | 12776 | 7.4108 | 1 | 7.4108 | 2 | 7.4108 | 2
227 | Classroom | 225 | 15 | Yes | 20 | 840 | 19 | 19 | Rooftop Unit | 8 | 6720 | 2.0089 | 1 | 2.0089 | 1 | 22.0089 | 3
228 | Classroom | 135 | 9 | Yes | 20 | 930 | 21 | 21 | Rooftop Unit | 8 | 7440 | 1.0887 | 1 | 1.0887 | 1 | 21.0887 | 3
229 | Classroom | 174 | 11 | Yes | 20 | 1008 | 22 | 22 | Rooftop Unit | 8 | 8064 | 1.2946 | 1 | 1.2946 | 1 | 21.2946 | 3
230/231 | Classroom | 87 | 5 | Yes | 20 | 522 | 11 | 11 | Rooftop Unit | 8 | 4176 | 1.25 | 1 | 1.25 | 1 | 21.25 | 3
231 | Classroom | 43 | 2 |  |  | 100 | 2 | 2 | Rooftop Unit | 8 | 800 | 3.225 | 1 | 3.225 | 1 | 3.225 | 1
232 | Classroom |  | 0 | Yes | 20 | 968 | 22 | 22 |  | 8 | 7744 | 0 | 1 | 0 | 0 | 20 | 3
232B | Classroom | 46 | 3 | Yes | 20 | 348 | 7 | 7 | Rooftop Unit | 8 | 2784 | 0.99138 | 1 | 0.99138 | 0 | 20.9914 | 3
234 | Classroom | 192 | 12 | Yes | 20 | 900 | 20 | 20 | Rooftop Unit | 8 | 7200 | 1.6 | 1 | 1.6 | 1 | 21.6 | 3
236 | Classroom | 293 | 19 |  |  | 1240 | 28 | 19 | Rooftop Unit | 8 | 9920 | 1.7722 | 1 | 1.7722 | 1 | 1.7722 | 1
237 | Classroom | 186 | 12 | Yes | 20 | 969 | 22 | 22 | Rooftop Unit | 8 | 7752 | 1.4396 | 1 | 1.4396 | 1 | 21.4396 | 3
238 | Classroom | 442 | 29 |  |  | 888 | 20 | 20 | Rooftop Unit | 8 | 7104 | 3.7331 | 1 | 3.7331 | 1 | 3.7331 | 1
245 | Classroom | 281 | 18 |  |  | 675 | 15 | 15 | Rooftop Unit | 8 | 5400 | 3.1222 | 1 | 3.1222 | 1 | 3.1222 | 1
247 | Classroom | 140 | 9 |  |  | 448 | 10 | 9 | Rooftop Unit | 8 | 3584 | 2.3438 | 1 | 2.3438 | 1 | 2.3438 | 1
249 & 249 A-B | Classroom | 520 | 34 |  |  | 414 | 9 | 9 | Rooftop Unit | 8 | 3312 | 9.4203 | 1 | 9.4203 | 2 | 9.4203 | 2
250 | Classroom | 303 | 20 |  |  | 900 | 20 | 20 | Rooftop Unit | 8 | 7200 | 2.525 | 1 | 2.525 | 1 | 2.525 | 1
253 | Classroom | 655 | 43 |  |  | 186 | 4 | 4 | Rooftop Unit | 8 | 1488 | 26.4113 | 1 | 26.4113 | 4 | 26.4113 | 4
257 | Classroom | 341 | 22 |  |  | 756 | 17 | 17 | Rooftop Unit | 8 | 6048 | 3.3829 | 1 | 3.3829 | 1 | 3.3829 | 1
258 | Classroom | 357 | 23 |  |  | 1050 | 23 | 23 | Rooftop Unit | 8 | 8400 | 2.55 | 1 | 2.55 | 1 | 2.55 | 1
259 | Classroom | 242 | 16 |  |  | 1225 | 27 | 16 | Rooftop Unit | 8 | 9800 | 1.4816 | 1 | 1.4816 | 1 | 1.4816 | 1
260 and 260 A-C | Classroom | 579 | 38 |  |  | 561 | 12 | 12 | Rooftop Unit | 8 | 4488 | 7.7406 | 1 | 7.7406 | 2 | 7.7406 | 2
261 | Classroom | 375 | 25 |  |  | 1050 | 23 | 23 | Rooftop Unit | 8 | 8400 | 2.6786 | 1 | 2.6786 | 1 | 2.6786 | 1
262 | Classroom | 678 | 45 |  |  | 2373 | 53 | 45 | Rooftop Unit | 8 | 18984 | 2.1429 | 1 | 2.1429 | 1 | 2.1429 | 1
263 | Classroom |  | 0 | Yes | 20 | 2373 | 53 | 53 |  | 8 | 18984 | 0 | 1 | 0 | 0 | 20 | 3
264 | Classroom | 333 | 22 |  |  | 870 | 19 | 19 | Rooftop Unit | 8 | 6960 | 2.8707 | 1 | 2.8707 | 1 | 2.8707 | 1
265 | Classroom | 307 | 20 |  |  | 928 | 21 | 20 | Rooftop Unit | 8 | 7424 | 2.4811 | 1 | 2.4811 | 1 | 2.4811 | 1
1750b | Room | 108 | 7 |  |  | 374 | 8 | 7 | Rooftop Unit | 8 | 2992 | 2.1658 | 1 | 2.1658 | 1 | 2.1658 | 1
1775A | - |  | 0 | Yes | 20 | 528 | 12 | 12 |  | 8 | 4224 | 0 | 1 | 0 | 0 | 20 | 3
- | Baking Room | 525 | 34 |  |  | 1981 | 45 | 34 | Rooftop Unit | 8 | 15848 | 1.9876 | 1 | 1.9876 | 1 | 1.9876 | 1
- | Dark Room | 59 | 3 |  |  | 104 | 2 | 2 | Rooftop Unit | 8 | 832 | 4.2548 | 1 | 4.2548 | 2 | 4.2548 | 2
- | Corridor | 109 | 7 |  |  | 355 | 8 | 7 | Rooftop Unit | 8 | 2840 | 2.3028 | 1 | 2.3028 | 1 | 2.3028 | 1
- | Hallway | 640 | 42 |  |  | 730 | 16 | 16 | Rooftop Unit | 8 | 5840 | 6.5753 | 1 | 6.5753 | 2 | 6.5753 | 2
- | Corridor | 54 | 3 |  |  | 162 | 3 | 3 | Rooftop Unit | 8 | 1296 | 2.5 | 1 | 2.5 | 1 | 2.5 | 1
- | Corridor | 53 | 3 |  |  | 152 | 3 | 3 | Rooftop Unit | 8 | 1216 | 2.6151 | 1 | 2.6151 | 1 | 2.6151 | 1
- | Corridor | 167 | 11 |  |  | 286 | 6 | 6 | Rooftop Unit | 8 | 2288 | 4.3794 | 1 | 4.3794 | 2 | 4.3794 | 2
- | Corridor | 70 | 4 |  |  | 344 | 7 | 4 | Rooftop Unit | 8 | 2752 | 1.5262 | 1 | 1.5262 | 1 | 1.5262 | 1
- | Hallway Diffuser s31 | 25 | 1 |  |  | 258 | 5 | 1 | Rooftop Unit | 8 | 2064 | 0.72674 | 1 | 0.72674 | 0 | 0.72674 | 0
- | Kitchen | 1391 | 92 |  |  | 205 | 4 | 4 | Rooftop Unit | 8 | 1640 | 50.8902 | 1 | 50.8902 | 5 | 50.8902 | 5
- | Nurse's Office/Medical | 165 | 11 |  |  | 591 | 13 | 11 | Rooftop Unit | 8 | 4728 | 2.0939 | 1 | 2.0939 | 1 | 2.0939 | 1
- | Office | 35 | 2 |  |  | 287 | 6 | 2 | Rooftop Unit | 8 | 2296 | 0.91463 | 1 | 0.91463 | 0 | 0.91463 | 0
- | Office | 77 | 5 |  |  | 1435 | 32 | 5 | Rooftop Unit | 8 | 11480 | 0.40244 | 1 | 0.40244 | 0 | 0.40244 | 0
- | Office | 54 | 3 |  |  | 157 | 3 | 3 | Rooftop Unit | 8 | 1256 | 2.5796 | 1 | 2.5796 | 1 | 2.5796 | 1
- | Office | 598 | 39 |  |  | 94 | 2 | 2 | Rooftop Unit | 8 | 752 | 47.7128 | 1 | 47.7128 | 4 | 47.7128 | 4
- | Classroom | 313 | 20 |  |  | 1769 | 40 | 20 | Rooftop Unit | 8 | 14152 | 1.327 | 1 | 1.327 | 1 | 1.327 | 1
S1 | Classroom | 309 | 20 |  |  | 336 | 7 | 7 | Rooftop Unit | 8 | 2688 | 6.8973 | 1 | 6.8973 | 2 | 6.8973 | 2
S2 | Classroom | 318 | 21 |  |  | 336 | 7 | 7 | Rooftop Unit | 8 | 2688 | 7.0982 | 1 | 7.0982 | 2 | 7.0982 | 2
S3 | Classroom | 52 | 3 |  |  | 336 | 7 | 3 | Rooftop Unit | 8 | 2688 | 1.1607 | 1 | 1.1607 | 1 | 1.1607 | 1
S3 | Office | 232 | 15 |  |  | 306 | 6 | 6 | Rooftop Unit | 8 | 2448 | 5.6863 | 1 | 5.6863 | 2 | 5.6863 | 2
S4 | Office | 14 | 0 |  |  | 20 | 0 | 0 | Rooftop Unit | 8 | 160 | 5.25 | 1 | 5.25 | 2 | 5.25 | 2
S5 | Storage | 33 | 2 |  |  | 270 | 6 | 2 | Rooftop Unit | 8 | 2160 | 0.91667 | 1 | 0.91667 | 0 | 0.91667 | 0
S6 | School Police | 207 | 13 |  |  | 515 | 11 | 11 | Rooftop Unit | 8 | 4120 | 3.0146 | 1 | 3.0146 | 1 | 3.0146 | 1
S8 | Classroom | 104 | 6 |  |  | 560 | 12 | 6 | Rooftop Unit | 8 | 4480 | 1.3929 | 1 | 1.3929 | 1 | 1.3929 | 1
- | School Store | 386 | 25 |  |  | 455 | 10 | 10 | Rooftop Unit | 8 | 3640 | 6.3626 | 1 | 6.3626 | 2 | 6.3626 | 2
- | Second Floor Hallway | 95 | 6 |  |  | 1846 | 41 | 6 | Rooftop Unit | 8 | 14768 | 0.38597 | 1 | 0.38597 | 0 | 0.38597 | 0
- | Storage | 33 | 2 |  |  | 590 | 13 | 2 | Rooftop Unit | 8 | 4720 | 0.41949 | 1 | 0.41949 | 0 | 0.41949 | 0
- | Storage | 107 | 7 |  |  | 35 | 0 | 0 | Rooftop Unit | 8 | 280 | 22.9286 | 1 | 22.9286 | 3 | 22.9286 | 3
- | Storage | 73 | 4 |  |  | 134 | 3 | 3 | Rooftop Unit | 8 | 1072 | 4.0858 | 1 | 4.0858 | 2 | 4.0858 | 2
- | Storage | 44 | 2 |  |  | 94 | 2 | 2 | Rooftop Unit | 8 | 752 | 3.5106 | 1 | 3.5106 | 1 | 3.5106 | 1
- | Storage | 45 | 3 |  |  | 91 | 2 | 2 | Rooftop Unit | 8 | 728 | 3.7088 | 1 | 3.7088 | 1 | 3.7088 | 1
- | Storage/Closet | 237 | 15 |  |  | 50 | 1 | 1 | Rooftop Unit | 8 | 400 | 35.55 | 1 | 35.55 | 4 | 35.55 | 4
Sheet Last Modified: | 2021-04-23
School: | John H. Taggart Elementary-Middle School
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
102-A | Classroom |  | 0 |  |  | 372 | 8 | 0 |  | 8 | 2976 | 0 | 1 | 0 | 0 | 0 | 0
102-B | Classroom |  | 0 |  |  | 230 | 5 | 0 |  | 8 | 1840 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom |  | 0 |  |  | 506 | 11 | 0 |  | 8 | 4048 | 0 | 1 | 0 | 0 | 0 | 0
104 | Classroom |  | 0 | Yes | 20 | 594 | 13 | 13 |  | 8 | 4752 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 | Yes | 20 | 682 | 15 | 15 |  | 8 | 5456 | 0 | 1 | 0 | 0 | 20 | 3
108 | Nurse's Office |  | 0 | Yes | 20 | 176 | 4 | 4 |  | 8 | 1408 | 0 | 1 | 0 | 0 | 20 | 3
- | 2nd Floor Dean of Student's Office |  | 0 |  |  | 144 | 3 | 0 |  | 8 | 1152 | 0 | 1 | 0 | 0 | 0 | 0
200 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 |  |  | 136 | 3 | 0 |  | 8 | 1088 | 0 | 1 | 0 | 0 | 0 | 0
204 | Computer Lab |  | 0 | Yes | 20 | 924 | 21 | 21 |  | 8 | 7392 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom |  | 0 |  |  | 414 | 9 | 0 |  | 8 | 3312 | 0 | 1 | 0 | 0 | 0 | 0
206 | Classroom |  | 0 | Yes | 20 | 736 | 16 | 16 |  | 8 | 5888 | 0 | 1 | 0 | 0 | 20 | 3
207 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
208 | Classroom |  | 0 | Yes | 20 | 638 | 14 | 14 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
209 | Classroom |  | 0 | Yes | 20 | 638 | 14 | 14 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
- | 3rd Floor Men's Room |  | 0 |  |  | 56 | 1 | 0 |  | 8 | 448 | 0 | 1 | 0 | 0 | 0 | 0
300 | Classroom |  | 0 | Yes | 20 | 638 | 14 | 14 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
303 | Classroom |  | 0 | Yes | 20 | 616 | 14 | 14 |  | 8 | 4928 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom |  | 0 | Yes | 20 | 594 | 13 | 13 |  | 8 | 4752 | 0 | 1 | 0 | 0 | 20 | 3
305-306 | Library |  | 0 | Yes | 20 | 1320 | 30 | 30 |  | 8 | 10560 | 0 | 1 | 0 | 0 | 20 | 3
307 | Classroom |  | 0 | Yes | 20 | 638 | 14 | 14 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
308 | Classroom |  | 0 | Yes | 20 | 660 | 15 | 15 |  | 8 | 5280 | 0 | 1 | 0 | 0 | 20 | 3
309 | Classroom |  | 0 |  |  | 638 | 14 | 0 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 0 | 0
400 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
401 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
402 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
403 | Classroom |  | 0 | Yes | 20 | 638 | 14 | 14 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
404 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
405 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
406 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
407 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
408 | Classroom |  | 0 | Yes | 20 | 638 | 14 | 14 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
409 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 |  | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
410 | Classroom |  | 0 | Yes | 20 | 638 | 14 | 14 |  | 8 | 5104 | 0 | 1 | 0 | 0 | 20 | 3
500 | Classroom |  | 0 | Yes | 20 | 132 | 3 | 3 |  | 8 | 1056 | 0 | 1 | 0 | 0 | 20 | 3
- | Gym |  | 0 | Yes | 20 | 3555 | 80 | 80 | Hydroxyl Unit | 8 | 28440 | 0 | 1.062 | 0 | 0 | 20 | 3
- | Building Engineer's Office |  | 0 |  |  | 286 | 6 | 0 |  | 8 | 2288 | 0 | 1 | 0 | 0 | 0 | 0
- | Main Office |  | 0 | Yes | 20 | 286 | 6 | 6 |  | 8 | 2288 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 20 | 154 | 3 | 3 |  | 8 | 1232 | 0 | 1 | 0 | 0 | 20 | 3
- | Teacher's Lounge |  | 0 |  |  | 322 | 7 | 0 |  | 8 | 2576 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-18
School: | Bayard Taylor Elementary School
Vendor: | EMCOR Main Building Test 10-29-20
Vendor: | Devine Main Building Retest 2-7-21
School: | Bayard Taylor Annex (Our Lady of Pompeii)
Vendor: | EMCOR | EMCOR Retest 2-18-21
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Taylor Main Building
B1 | Classroom | 210 | 14 |  |  | 780 | 17 | 14 | Univent | 8 | 6240 | 2.0192 | 1 | 2.0192 | 1 | 2.0192 | 1
B1B and B1B North & South. | B1 and B1 North & South. | 325 | 21 |  |  | 760 | 17 | 17 | Univent | 8 | 6080 | 3.2072 | 1 | 3.2072 | 1 | 3.2072 | 1
B2A & B2B | Classroom | 0 | 0 |  |  | 600 | 13 | 0 | Univent | 8 | 4800 | 0 | 1 | 0 | 0 | 0 | 0
B4 | Classroom | 299 | 19 |  |  | 1444 | 32 | 19 | Univent | 8 | 11552 | 1.553 | 1 | 1.553 | 1 | 1.553 | 1
B5 | Classroom | 316 | 21 |  |  | 1410 | 32 | 21 | Univent | 8 | 11280 | 1.6809 | 1 | 1.6809 | 1 | 1.6809 | 1
101 | Classroom | 362 | 24 |  |  | 1159 | 26 | 24 | Univent | 8 | 9272 | 2.3425 | 1 | 2.3425 | 1 | 2.3425 | 1
102 | Classroom |  | 0 | Yes | 20 | 1148 | 26 | 26 | Univent | 8 | 9184 | 0 | 1 | 0 | 0 | 20 | 3
103 | Classroom | 328 | 21 |  |  | 1149 | 26 | 21 | Univent | 8 | 9192 | 2.141 | 1 | 2.141 | 1 | 2.141 | 1
104 | Classroom | 387 | 25 |  |  | 1107 | 25 | 25 | Univent | 8 | 8856 | 2.622 | 1 | 2.622 | 1 | 2.622 | 1
105 | Classroom | 387 | 25 |  |  | 1394 | 31 | 25 | Univent | 8 | 11152 | 2.0821 | 1 | 2.0821 | 1 | 2.0821 | 1
201 | Classroom | 342 | 22 |  |  | 1101 | 25 | 22 | Univent | 8 | 8808 | 2.3297 | 1 | 2.3297 | 1 | 2.3297 | 1
202 | Classroom | 423 | 28 |  |  | 1097 | 24 | 24 | Univent | 8 | 8776 | 2.892 | 1 | 2.892 | 1 | 2.892 | 1
203 | Classroom |  | 0 | Yes | 20 | 1163 | 26 | 26 | Univent | 8 | 9304 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom | 444 | 29 |  |  | 1099 | 24 | 24 | Univent | 8 | 8792 | 3.03 | 1 | 3.03 | 1 | 3.03 | 1
205 | Classroom | 470 | 31 |  |  | 1098 | 24 | 24 | Univent | 8 | 8784 | 3.2104 | 1 | 3.2104 | 1 | 3.2104 | 1
206 | Classroom | 408 | 27 |  |  | 1052 | 23 | 23 | Univent | 8 | 8416 | 2.9087 | 1 | 2.9087 | 1 | 2.9087 | 1
301 | Classroom |  | 0 | Yes | 20 | 1066 | 24 | 24 | Univent | 8 | 8528 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom | 299 | 19 |  |  | 1065 | 24 | 19 | Univent | 8 | 8520 | 2.1056 | 1 | 2.1056 | 1 | 2.1056 | 1
303 | Classroom | 317 | 21 |  |  | 1127 | 25 | 21 | Univent | 8 | 9016 | 2.1096 | 1 | 2.1096 | 1 | 2.1096 | 1
304 | Classroom | 344 | 22 |  |  | 1133 | 25 | 22 | Univent | 8 | 9064 | 2.2771 | 1 | 2.2771 | 1 | 2.2771 | 1
305 | Classroom | 73 | 4 | Yes | 20 | 1109 | 25 | 25 | Univent | 8 | 8872 | 0.49369 | 1 | 0.49369 | 0 | 20.4937 | 3
306 | Classroom | 483 | 32 |  |  | 1107 | 25 | 25 | Univent | 8 | 8856 | 3.2724 | 1 | 3.2724 | 1 | 3.2724 | 1
- | IMC Library | 353 | 23 |  |  | 1641 | 37 | 23 | Univent | 8 | 13128 | 1.6133 | 1 | 1.6133 | 1 | 1.6133 | 1
- | Music Classroom | 162 | 10 |  |  | 780 | 17 | 10 | Univent | 8 | 6240 | 1.5577 | 1 | 1.5577 | 1 | 1.5577 | 1
- | Main Office | 303 | 20 |  |  | 889 | 20 | 20 | Univent | 8 | 7112 | 2.5562 | 1 | 2.5562 | 1 | 2.5562 | 1
- | Principal | 359 | 23 |  |  | 479 | 10 | 10 | Univent | 8 | 3832 | 5.6211 | 1 | 5.6211 | 2 | 5.6211 | 2
- | Lounge | 232 | 15 |  |  | 300 | 6 | 6 | Univent | 8 | 2400 | 5.8 | 1 | 5.8 | 2 | 5.8 | 2
- | Nurse | 148 | 9 |  |  | 300 | 6 | 6 | Univent | 8 | 2400 | 3.7 | 1 | 3.7 | 1 | 3.7 | 1
- | Art Classroom | 123 | 8 |  |  | 1107 | 25 | 8 | Univent | 8 | 8856 | 0.83333 | 1 | 0.83333 | 0 | 0.83333 | 0
Taylor Annex
222 | Classroom |  | 0 |  |  | 750 | 17 | 0 | N/A | 8 | 6000 | 0 | 1 | 0 | 0 | 0 | 0
223 | Classroom |  | 0 |  |  | 625 | 14 | 0 | N/A | 8 | 5000 | 0 | 1 | 0 | 0 | 0 | 0
224 | Classroom |  | 0 |  |  | 675 | 15 | 0 | N/A | 8 | 5400 | 0 | 1 | 0 | 0 | 0 | 0
231 | Classroom |  | 0 |  |  | 700 | 15 | 0 | N/A | 8 | 5600 | 0 | 1 | 0 | 0 | 0 | 0
331 | Classroom |  | 0 |  |  | 700 | 15 | 0 | N/A | 8 | 5600 | 0 | 1 | 0 | 0 | 0 | 0
332 | Classroom |  | 0 |  |  | 750 | 17 | 0 | N/A | 8 | 6000 | 0 | 1 | 0 | 0 | 0 | 0
333 | Classroom |  | 0 |  |  | 675 | 15 | 0 | N/A | 8 | 5400 | 0 | 1 | 0 | 0 | 0 | 0
334 | Classroom |  | 0 |  |  | 625 | 14 | 0 | N/A | 8 | 5000 | 0 | 1 | 0 | 0 | 0 | 0
- | Auditorium/Gym/Ca |  | 0 |  |  | 2516 | 57 | 0 | N/A | 8 | 20128 | 0 | 1.062 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30
School: | Tilden Middle School
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom |  | 0 |  |  | 576 | 13 | 0 | House Fan | 8 | 4608 | 0 | 1 | 0 | 0 | 0 | 0
101 | Classroom |  | 0 |  |  | 624 | 14 | 0 | House Fan | 8 | 4992 | 0 | 1 | 0 | 0 | 0 | 0
103 | Classroom |  | 0 | Yes | 20 | 960 | 21 | 21 | House Fan | 8 | 7680 | 0 | 1 | 0 | 0 | 20 | 3
104 | Classroom |  | 0 |  |  | 1248 | 28 | 0 | House Fan | 8 | 9984 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom |  | 0 | Yes | 20 | 1248 | 28 | 28 | House Fan | 8 | 9984 | 0 | 1 | 0 | 0 | 20 | 3
106 | Classroom |  | 0 | Yes | 20 | 864 | 19 | 19 | House Fan | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom |  | 0 | Yes | 20 | 792 | 18 | 18 | House Fan | 8 | 6336 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom |  | 0 | Yes | 20 | 792 | 18 | 18 | House Fan | 8 | 6336 | 0 | 1 | 0 | 0 | 20 | 3
109A | Classroom |  | 0 |  |  | 704 | 16 | 0 | House Fan | 8 | 5632 | 0 | 1 | 0 | 0 | 0 | 0
110 | Classroom |  | 0 | Yes | 20 | 616 | 14 | 14 | House Fan | 8 | 4928 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom |  | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
203 | Classroom |  | 0 | Yes | 20 | 672 | 15 | 15 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
203A | Classroom |  | 0 | Yes | 20 | 1056 | 24 | 24 | House Fan | 8 | 8448 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom |  | 0 | Yes | 20 | 672 | 15 | 15 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
205 | Nurse's office |  | 0 | Yes | 20 | 384 | 8 | 8 | House Fan | 8 | 3072 | 0 | 1 | 0 | 0 | 20 | 3
207A | Principal's Office |  | 0 | Yes | 20 | 560 | 12 | 12 | House Fan | 8 | 4480 | 0 | 1 | 0 | 0 | 20 | 3
207C | Counselor's Suite |  | 0 |  |  | 120 | 2 | 0 | House Fan | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
207D | Counselor's Suite |  | 0 | Yes | 20 | 120 | 2 | 2 | House Fan | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
207F | Counselor's Suite |  | 0 | Yes | 20 | 120 | 2 | 2 | House Fan | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
207G | Counselor's Suite |  | 0 | Yes | 20 | 120 | 2 | 2 | House Fan | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
207H | Counselor's Suite |  | 0 |  |  | 120 | 2 | 0 | House Fan | 8 | 960 | 0 | 1 | 0 | 0 | 0 | 0
208 | Main Office |  | 0 | Yes | 20 | 560 | 12 | 12 | House Fan | 8 | 4480 | 0 | 1 | 0 | 0 | 20 | 3
209 | IMC |  | 0 | Yes | 20 | 1728 | 39 | 39 | House Fan | 8 | 13824 | 0 | 1 | 0 | 0 | 20 | 3
211 | Classroom |  | 0 | Yes | 20 | 968 | 22 | 22 | House Fan | 8 | 7744 | 0 | 1 | 0 | 0 | 20 | 3
212 | Classroom |  | 0 | Yes | 20 | 1152 | 26 | 26 | House Fan | 8 | 9216 | 0 | 1 | 0 | 0 | 20 | 3
213 | Classroom |  | 0 |  |  | 616 | 14 | 0 | House Fan | 8 | 4928 | 0 | 1 | 0 | 0 | 0 | 0
214 | Classroom |  | 0 | Yes | 20 | 672 | 15 | 15 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
214A | Classroom |  | 0 | Yes | 20 | 864 | 19 | 19 | House Fan | 8 | 6912 | 0 | 1 | 0 | 0 | 20 | 3
215 | Classroom |  | 0 | Yes | 20 | 576 | 13 | 13 | House Fan | 8 | 4608 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom |  | 0 |  |  | 576 | 13 | 0 | House Fan | 8 | 4608 | 0 | 1 | 0 | 0 | 0 | 0
302 | Carson Valley |  | 0 |  |  | 288 | 6 | 0 | House Fan | 8 | 2304 | 0 | 1 | 0 | 0 | 0 | 0
303 | Classroom |  | 0 | Yes | 20 | 672 | 15 | 15 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
303A | Classroom |  | 0 | Yes | 20 | 672 | 15 | 15 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
304 | Classroom |  | 0 | Yes | 20 | 672 | 15 | 15 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
305 | Classroom |  | 0 |  |  | 672 | 15 | 0 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
306 | Classroom |  | 0 |  |  | 616 | 14 | 0 | House Fan | 8 | 4928 | 0 | 1 | 0 | 0 | 0 | 0
307 | Classroom |  | 0 |  |  | 672 | 15 | 0 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
308 | Classroom |  | 0 |  |  | 672 | 15 | 0 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom |  | 0 |  |  | 480 | 10 | 0 | House Fan | 8 | 3840 | 0 | 1 | 0 | 0 | 0 | 0
311 | Classroom |  | 0 |  |  | 768 | 17 | 0 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
312 | Classroom |  | 0 |  |  | 672 | 15 | 0 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
313 | Classroom |  | 0 |  |  | 672 | 15 | 0 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
314 | Classroom |  | 0 |  |  | 672 | 15 | 0 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 0 | 0
315 | Dean of Students |  | 0 | Yes | 20 | 216 | 4 | 4 | House Fan | 8 | 1728 | 0 | 1 | 0 | 0 | 20 | 3
316 | Classroom |  | 0 | Yes | 20 | 768 | 17 | 17 | House Fan | 8 | 6144 | 0 | 1 | 0 | 0 | 20 | 3
318 | Classroom |  | 0 |  |  | 792 | 18 | 0 | House Fan | 8 | 6336 | 0 | 1 | 0 | 0 | 0 | 0
319 | Classroom |  | 0 |  |  | 832 | 18 | 0 | House Fan | 8 | 6656 | 0 | 1 | 0 | 0 | 0 | 0
401 | Classroom |  | 0 | Yes | 20 | 625 | 14 | 14 | House Fan | 8 | 5000 | 0 | 1 | 0 | 0 | 20 | 3
403A | Faculty Lounge |  | 0 | Yes | 20 | 792 | 18 | 18 | House Fan | 8 | 6336 | 0 | 1 | 0 | 0 | 20 | 3
404 | Classroom |  | 0 | Yes | 20 | 1056 | 24 | 24 | House Fan | 8 | 8448 | 0 | 1 | 0 | 0 | 20 | 3
404A | Classroom |  | 0 | Yes | 20 | 120 | 2 | 2 | House Fan | 8 | 960 | 0 | 1 | 0 | 0 | 20 | 3
405 | Classroom |  | 0 | Yes | 20 | 1056 | 24 | 24 | House Fan | 8 | 8448 | 0 | 1 | 0 | 0 | 20 | 3
406 | Classroom |  | 0 | Yes | 20 | 1056 | 24 | 24 | House Fan | 8 | 8448 | 0 | 1 | 0 | 0 | 20 | 3
407 | Classroom |  | 0 | Yes | 20 | 1056 | 24 | 24 | House Fan | 8 | 8448 | 0 | 1 | 0 | 0 | 20 | 3
408 | Classroom |  | 0 | Yes | 20 | 792 | 18 | 18 | House Fan | 8 | 6336 | 0 | 1 | 0 | 0 | 20 | 3
410B | Staff Conference |  | 0 | Yes | 20 | 1232 | 28 | 28 | House Fan | 8 | 9856 | 0 | 1 | 0 | 0 | 20 | 3
411 | Classroom |  | 0 | Yes | 20 | 769 | 17 | 17 | House Fan | 8 | 6152 | 0 | 1 | 0 | 0 | 20 | 3
412 | Classroom |  | 0 | Yes | 20 | 968 | 22 | 22 | House Fan | 8 | 7744 | 0 | 1 | 0 | 0 | 20 | 3
414 | Classroom |  | 0 | Yes | 20 | 968 | 22 | 22 | House Fan | 8 | 7744 | 0 | 1 | 0 | 0 | 20 | 3
415 | Classroom |  | 0 | Yes | 20 | 672 | 15 | 15 | House Fan | 8 | 5376 | 0 | 1 | 0 | 0 | 20 | 3
416 | Classroom |  | 0 | Yes | 20 | 392 | 8 | 8 | House Fan | 8 | 3136 | 0 | 1 | 0 | 0 | 20 | 3
- | Cafeteria |  | 0 | Yes | 20 | 5150 | 117 | 117 | House Fan | 8 | 41200 | 0 | 1.062 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-30
School: | Trinidad Center
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
- | Adult Restroom | 13 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Assistant Director's Office | 16 | 1 |  |  |  | 0 | 0 | Air Handling Unit
- | Boy's Restroom | 16 | 1 |  |  |  | 0 | 0 | Air Handling Unit
- | Computer Room | 31 | 2 |  |  |  | 0 | 0 | Air Handling Unit
- | Corridor |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Front Entrance | 34 | 2 |  |  |  | 0 | 0 | Air Handling Unit
- | Girl's Restroom | 18 | 1 |  |  |  | 0 | 0 | Air Handling Unit
- | Gym |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Hallway |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Head Receptionist's Office | 21 | 1 |  |  |  | 0 | 0 | Air Handling Unit
- | Kitchen | 50 | 3 |  |  |  | 0 | 0 | Air Handling Unit
- | Library |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Main Corridor (Hallway) | 0 | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Maintenance Office | 22 | 1 |  |  |  | 0 | 0 | Air Handling Unit
- | Rear Entrance | 19 | 1 |  |  |  | 0 | 0 | Air Handling Unit
1 | Classroom | 101 | 6 | Yes | 20 | 610 | 13 | 13 | Air Handling Unit | 8 | 4880 | 1.2418 | 1 | 1.2418 | 1 | 21.2418 | 3
2 | Classroom | 95 | 6 | Yes | 20 | 610 | 13 | 13 | Air Handling Unit | 8 | 4880 | 1.168 | 1 | 1.168 | 1 | 21.168 | 3
3 | Classroom | 100 | 6 | Yes | 20 | 575 | 13 | 13 | Air Handling Unit | 8 | 4600 | 1.3043 | 1 | 1.3043 | 1 | 21.3043 | 3
4 | Classroom | 112 | 7 | Yes | 20 | 575 | 13 | 13 | Air Handling Unit | 8 | 4600 | 1.4609 | 1 | 1.4609 | 1 | 21.4609 | 3
5 | Classroom | 132 | 8 |  |  | 590 | 13 | 8 | Air Handling Unit | 8 | 4720 | 1.678 | 1 | 1.678 | 1 | 1.678 | 1
6 | Classroom |  | 0 | Yes | 20 | 629 | 14 | 14 | Air Handling Unit | 8 | 5032 | 0 | 1 | 0 | 0 | 20 | 3
7 | Storage |  | 0 | Yes | 20 | 609 | 13 | 13 | Air Handling Unit | 8 | 4872 | 0 | 1 | 0 | 0 | 20 | 3
8 | Storage |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
9 | Storage |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
10 | Roof Access |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
- | Stairway |  | 0 |  |  |  | 0 | 0 | Air Handling Unit
Sheet Last Modified: | 2021-03-18
School: | The U School at Ferguson
Vendor: | EMCOR Fluidics
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
B10 | Classroom | 0 | 0 |  |  | 886 | 20 | 0 | Unit Ventilator | 8 | 7088 | 0 | 1 | 0 | 0 | 0 | 0
B11 | Classroom | 0 | 0 |  |  | 886 | 20 | 0 | Unit Ventilator | 8 | 7088 | 0 | 1 | 0 | 0 | 0 | 0
B12 | Classroom | 0 | 0 |  |  | 886 | 20 | 0 | Unit Ventilator | 8 | 7088 | 0 | 1 | 0 | 0 | 0 | 0
110 | Classroom | 0 | 0 |  |  | 886 | 20 | 0 | Unit Ventilator | 8 | 7088 | 0 | 1 | 0 | 0 | 0 | 0
111 | Classroom | 0 | 0 |  |  | 886 | 20 | 0 | Unit Ventilator | 8 | 7088 | 0 | 1 | 0 | 0 | 0 | 0
112 | Classroom | 0 | 0 |  |  | 886 | 20 | 0 | Unit Ventilator | 8 | 7088 | 0 | 1 | 0 | 0 | 0 | 0
113 | Classroom | 0 | 0 |  |  | 884 | 20 | 0 | Unit Ventilator | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
114 | Classroom | 0 | 0 |  |  | 884 | 20 | 0 | Unit Ventilator | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
115 | Classroom | 0 | 0 |  |  | 884 | 20 | 0 | Unit Ventilator | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
210 | Classroom | 0 | 0 |  |  | 886 | 20 | 0 | Unit Ventilator | 8 | 7088 | 0 | 1 | 0 | 0 | 0 | 0
211 | Classroom | 0 | 0 |  |  | 886 | 20 | 0 | Unit Ventilator | 8 | 7088 | 0 | 1 | 0 | 0 | 0 | 0
212 | Classroom | 0 | 0 |  |  | 886 | 20 | 0 | Unit Ventilator | 8 | 7088 | 0 | 1 | 0 | 0 | 0 | 0
213 | Classroom | 0 | 0 |  |  | 884 | 20 | 0 | Unit Ventilator | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
214 | Classroom | 0 | 0 |  |  | 884 | 20 | 0 | Unit Ventilator | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
215 | Classroom | 0 | 0 |  |  | 884 | 20 | 0 | Unit Ventilator | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom | 0 | 0 |  |  | 886 | 20 | 0 | Unit Ventilator | 8 | 7088 | 0 | 1 | 0 | 0 | 0 | 0
311 | Classroom | 0 | 0 |  |  | 886 | 20 | 0 | Unit Ventilator | 8 | 7088 | 0 | 1 | 0 | 0 | 0 | 0
312 | Classroom | 0 | 0 |  |  | 886 | 20 | 0 | Unit Ventilator | 8 | 7088 | 0 | 1 | 0 | 0 | 0 | 0
313 | Classroom | 0 | 0 |  |  | 884 | 20 | 0 | Unit Ventilator | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
314 | Classroom | 0 | 0 |  |  | 442 | 10 | 0 | Unit Ventilator | 8 | 3536 | 0 | 1 | 0 | 0 | 0 | 0
315 | Classroom | 0 | 0 |  |  | 884 | 20 | 0 | Unit Ventilator | 8 | 7072 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-06
School: | Vare-Washington Elementary School
Vendor: | EMCOR Fluidics | EMCOR Retest | Devine Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | classroom | 478 | 31 |  |  | 1040 | 23 | 23 | Unit Ventilator | 8 | 8320 | 3.4471 | 1 | 3.4471 | 1 | 3.4471 | 1
102 | classroom | 251 | 16 | Yes | 20 | 936 | 21 | 21 | Unit Ventilator | 8 | 7488 | 2.0112 | 1 | 2.0112 | 1 | 22.0112 | 3
103 | classroom | 267 | 17 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.5673 | 1 | 2.5673 | 1 | 2.5673 | 1
104 | classroom | 331 | 22 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 3.1827 | 1 | 3.1827 | 1 | 3.1827 | 1
105 | classroom | 297 | 19 |  |  | 936 | 21 | 19 | Unit Ventilator | 8 | 7488 | 2.3798 | 1 | 2.3798 | 1 | 2.3798 | 1
106 | classroom | 390 | 26 |  |  | 1040 | 23 | 23 | Unit Ventilator | 8 | 8320 | 2.8125 | 1 | 2.8125 | 1 | 2.8125 | 1
107 | classroom | 210 | 14 | Yes | 20 | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.0192 | 1 | 2.0192 | 1 | 22.0192 | 3
108 | classroom | 319 | 21 |  |  | 767 | 17 | 17 | Unit Ventilator | 8 | 6136 | 3.1193 | 1 | 3.1193 | 1 | 3.1193 | 1
109 | classroom | 313 | 20 |  |  | 767 | 17 | 17 | Unit Ventilator | 8 | 6136 | 3.0606 | 1 | 3.0606 | 1 | 3.0606 | 1
110 | classroom | 594 | 39 |  |  | 1482 | 33 | 33 | Unit Ventilator | 8 | 11856 | 3.0061 | 1 | 3.0061 | 1 | 3.0061 | 1
201 | Counselor | 380 | 25 |  |  | 684 | 15 | 15 | Unit Ventilator | 8 | 5472 | 4.1667 | 1 | 4.1667 | 2 | 4.1667 | 2
202 | classroom | 326 | 21 |  |  | 832 | 18 | 18 | Unit Ventilator | 8 | 6656 | 2.9387 | 1 | 2.9387 | 1 | 2.9387 | 1
203 | 4-6 Autistic Supp. | 316 | 21 |  |  | 832 | 18 | 18 | Unit Ventilator | 8 | 6656 | 2.8486 | 1 | 2.8486 | 1 | 2.8486 | 1
204 | classroom | 310 | 20 |  |  | 832 | 18 | 18 | Unit Ventilator | 8 | 6656 | 2.7945 | 1 | 2.7945 | 1 | 2.7945 | 1
205 | K-2 Autistic Supp. | 210 | 14 | Yes | 20 | 832 | 18 | 18 | Unit Ventilator | 8 | 6656 | 1.893 | 1 | 1.893 | 1 | 21.893 | 3
206 | classroom | 417 | 27 |  |  | 832 | 18 | 18 | Unit Ventilator | 8 | 6656 | 3.759 | 1 | 3.759 | 1 | 3.759 | 1
207 | classroom | 227 | 15 |  |  | 832 | 18 | 15 | Unit Ventilator | 8 | 6656 | 2.0463 | 1 | 2.0463 | 1 | 2.0463 | 1
208A | 3-4 Autistic Supp. | 293 | 19 |  |  | 832 | 18 | 18 | Unit Ventilator | 8 | 6656 | 2.6412 | 1 | 2.6412 | 1 | 2.6412 | 1
208B | K-2 Emotional Support | 297 | 19 |  |  | 725 | 16 | 16 | Unit Ventilator | 8 | 5800 | 3.0724 | 1 | 3.0724 | 1 | 3.0724 | 1
210 | ESOL | 234 | 15 |  |  | 575 | 13 | 13 | Unit Ventilator | 8 | 4600 | 3.0522 | 1 | 3.0522 | 1 | 3.0522 | 1
211 | ESOL/SBTL | 251 | 16 |  |  | 628 | 14 | 14 | Unit Ventilator | 8 | 5024 | 2.9976 | 1 | 2.9976 | 1 | 2.9976 | 1
213 | classroom | 405 | 27 |  |  | 1092 | 24 | 24 | Unit Ventilator | 8 | 8736 | 2.7816 | 1 | 2.7816 | 1 | 2.7816 | 1
214 | classroom | 322 | 21 |  |  | 468 | 10 | 10 | Unit Ventilator | 8 | 3744 | 5.1603 | 1 | 5.1603 | 2 | 5.1603 | 2
301 | classroom | 258 | 17 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.4808 | 1 | 2.4808 | 1 | 2.4808 | 1
302 | classroom | 291 | 19 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.7981 | 1 | 2.7981 | 1 | 2.7981 | 1
303 | classroom | 217 | 14 | Yes | 20 | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.0865 | 1 | 2.0865 | 1 | 22.0865 | 3
304 | classroom | 234 | 15 |  |  | 780 | 17 | 15 | Unit Ventilator | 8 | 6240 | 2.25 | 1 | 2.25 | 1 | 2.25 | 1
305 | classroom | 287 | 19 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.7596 | 1 | 2.7596 | 1 | 2.7596 | 1
306 | classroom | 323 | 21 |  |  | 690 | 15 | 15 | Unit Ventilator | 8 | 5520 | 3.5109 | 1 | 3.5109 | 1 | 3.5109 | 1
307 | classroom | 217 | 14 | Yes | 20 | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 2.0865 | 1 | 2.0865 | 1 | 22.0865 | 3
308 | classroom | 269 | 17 |  |  | 988 | 22 | 17 | Unit Ventilator | 8 | 7904 | 2.042 | 1 | 2.042 | 1 | 2.042 | 1
309 | Psychologist / Climate Liaison | 185 | 12 |  |  | 598 | 13 | 12 | Unit Ventilator | 8 | 4784 | 2.3202 | 1 | 2.3202 | 1 | 2.3202 | 1
310 | Math Interventionist | 211 | 14 |  |  | 624 | 14 | 14 | Unit Ventilator | 8 | 4992 | 2.5361 | 1 | 2.5361 | 1 | 2.5361 | 1
311 | classroom | 189 | 12 | Yes | 20 | 624 | 14 | 14 | Unit Ventilator | 8 | 4992 | 2.2716 | 1 | 2.2716 | 1 | 22.2716 | 3
312A | classroom | 295 | 19 |  |  | 1014 | 23 | 19 | Unit Ventilator | 8 | 8112 | 2.182 | 1 | 2.182 | 1 | 2.182 | 1
313 | classroom | 166 | 11 |  |  | 494 | 11 | 11 | Unit Ventilator | 8 | 3952 | 2.5202 | 1 | 2.5202 | 1 | 2.5202 | 1
- | Gym | 305 | 20 |  |  | 4352 | 98 | 20 | Unit Ventilator | 8 | 34816 | 0.52562 | 1.062 | 0.55823 | 0 | 0.55823 | 0
- | Library | 208 | 13 |  |  | 578 | 13 | 13 | Unit Ventilator | 8 | 4624 | 2.699 | 1 | 2.699 | 1 | 2.699 | 1
- | Lunch Room | 146 | 9 | Yes | 20 | 1292 | 29 | 29 | Unit Ventilator | 8 | 10336 | 0.84752 | 1 | 0.84752 | 0 | 20.8475 | 3
- | Music | 748 | 49 |  |  | 1098 | 24 | 24 | Unit Ventilator | 8 | 8784 | 5.1093 | 1 | 5.1093 | 2 | 5.1093 | 2
- | Main Office |  | 0 | Yes | 20 | 396 | 9 | 9 | Active Pure Unit | 8 | 3168 | 0 | 1 | 0 | 0 | 20 | 3
- | Princpal's Office |  | 0 | Yes | 20 | 350 | 7 | 7 | Active Pure Unit | 8 | 2800 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse's Office |  | 0 | Yes | 20 | 264 | 6 | 6 | Active Pure Unit | 8 | 2112 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-12
School: | EH Vare
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
109 | - |  | 0 |  |  |  | 0 | 0
110 | - |  | 0 |  |  |  | 0 | 0
Sheet Last Modified: | 2021-04-21
School: | General Louis Wagner Middle School
Vendor: | EMCOR Fluidics | Exhaust Report
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101A | classroom | 312 | 20 |  |  | 552 | 12 | 12 | Air Handling Unit | 8 | 4416 | 4.2391 | 1 | 4.2391 | 2 | 4.2391 | 2
101B | classroom | 376 | 25 |  |  | 506 | 11 | 11 | Air Handling Unit | 8 | 4048 | 5.5731 | 1 | 5.5731 | 2 | 5.5731 | 2
102 | classroom | 644 | 42 |  |  | 888 | 20 | 20 | Air Handling Unit | 8 | 7104 | 5.4392 | 1 | 5.4392 | 2 | 5.4392 | 2
103A | classroom | 1312 | 87 |  |  | 1344 | 30 | 30 | Air Handling Unit | 8 | 10752 | 7.3214 | 1 | 7.3214 | 2 | 7.3214 | 2
105 | classroom | 527 | 35 |  |  | 878 | 19 | 19 | Air Handling Unit | 8 | 7024 | 4.5017 | 1 | 4.5017 | 2 | 4.5017 | 2
106 | classroom | 713 | 47 |  |  | 883 | 20 | 20 | Air Handling Unit | 8 | 7064 | 6.0561 | 1 | 6.0561 | 2 | 6.0561 | 2
107 | classroom | 635 | 42 |  |  | 705 | 16 | 16 | Air Handling Unit | 8 | 5640 | 6.7553 | 1 | 6.7553 | 2 | 6.7553 | 2
108 | classroom | 586 | 39 |  |  | 916 | 20 | 20 | Air Handling Unit | 8 | 7328 | 4.798 | 1 | 4.798 | 2 | 4.798 | 2
111 | classroom | 536 | 35 |  |  | 360 | 8 | 8 | Air Handling Unit | 8 | 2880 | 11.1667 | 1 | 11.1667 | 3 | 11.1667 | 3
112 | classroom | 585 | 39 |  |  | 720 | 16 | 16 | Air Handling Unit | 8 | 5760 | 6.0938 | 1 | 6.0938 | 2 | 6.0938 | 2
201 | classroom | 973 | 64 |  |  | 711 | 16 | 16 | Air Handling Unit | 8 | 5688 | 10.2637 | 1 | 10.2637 | 3 | 10.2637 | 3
202 | classroom | 907 | 60 |  |  | 677 | 15 | 15 | Air Handling Unit | 8 | 5416 | 10.048 | 1 | 10.048 | 3 | 10.048 | 3
203 | classroom | 306 | 20 |  |  | 697 | 15 | 15 | Air Handling Unit | 8 | 5576 | 3.2927 | 1 | 3.2927 | 1 | 3.2927 | 1
204 | classroom | 600 | 40 |  |  | 657 | 14 | 14 | Air Handling Unit | 8 | 5256 | 6.8493 | 1 | 6.8493 | 2 | 6.8493 | 2
205A | Counselor Office | 597 | 39 |  |  | 306 | 6 | 6 | Air Handling Unit | 8 | 2448 | 14.6324 | 1 | 14.6324 | 3 | 14.6324 | 3
205B | Counselor Office | 690 | 46 |  |  | 306 | 6 | 6 | Air Handling Unit | 8 | 2448 | 16.9118 | 1 | 16.9118 | 3 | 16.9118 | 3
209A | classroom | 496 | 33 |  |  | 2064 | 46 | 33 | Air Handling Unit | 8 | 16512 | 1.8023 | 1 | 1.8023 | 1 | 1.8023 | 1
209B | classroom | 763 | 50 |  |  | 336 | 7 | 7 | Air Handling Unit | 8 | 2688 | 17.0312 | 1 | 17.0312 | 3 | 17.0312 | 3
209C | classroom | 995 | 66 |  |  | 336 | 7 | 7 | Air Handling Unit | 8 | 2688 | 22.2098 | 1 | 22.2098 | 3 | 22.2098 | 3
212 | classroom | 1030 | 68 |  |  | 859 | 19 | 19 | Air Handling Unit | 8 | 6872 | 8.993 | 1 | 8.993 | 2 | 8.993 | 2
213 | classroom | 870 | 58 |  |  | 656 | 14 | 14 | Air Handling Unit | 8 | 5248 | 9.9466 | 1 | 9.9466 | 2 | 9.9466 | 2
214 | classroom | 446 | 29 |  |  | 714 | 16 | 16 | Air Handling Unit | 8 | 5712 | 4.6849 | 1 | 4.6849 | 2 | 4.6849 | 2
215 | classroom | 240 | 16 |  |  | 659 | 14 | 14 | Air Handling Unit | 8 | 5272 | 2.7314 | 1 | 2.7314 | 1 | 2.7314 | 1
216 | classroom | 2170 | 144 |  |  | 777 | 17 | 17 | Air Handling Unit | 8 | 6216 | 20.9459 | 1 | 20.9459 | 3 | 20.9459 | 3
217 | classroom | 1626 | 108 |  |  | 743 | 16 | 16 | Air Handling Unit | 8 | 5944 | 16.4132 | 1 | 16.4132 | 3 | 16.4132 | 3
218 | classroom | 197 | 13 |  |  | 645 | 14 | 13 | Air Handling Unit | 8 | 5160 | 2.2907 | 1 | 2.2907 | 1 | 2.2907 | 1
219 | classroom | 1463 | 97 |  |  | 643 | 14 | 14 | Air Handling Unit | 8 | 5144 | 17.0645 | 1 | 17.0645 | 3 | 17.0645 | 3
220 | classroom | 731 | 48 |  |  | 563 | 12 | 12 | Air Handling Unit | 8 | 4504 | 9.738 | 1 | 9.738 | 2 | 9.738 | 2
221 | classroom | 1653 | 110 |  |  | 779 | 17 | 17 | Air Handling Unit | 8 | 6232 | 15.9146 | 1 | 15.9146 | 3 | 15.9146 | 3
222 | classroom | 667 | 44 |  |  | 670 | 15 | 15 | Air Handling Unit | 8 | 5360 | 7.4664 | 1 | 7.4664 | 2 | 7.4664 | 2
225 | Dean | 272 | 18 |  |  | 348 | 7 | 7 | Air Handling Unit | 8 | 2784 | 5.8621 | 1 | 5.8621 | 2 | 5.8621 | 2
226 | classroom | 671 | 44 |  |  | 654 | 14 | 14 | Air Handling Unit | 8 | 5232 | 7.695 | 1 | 7.695 | 2 | 7.695 | 2
301 | classroom | 1282 | 85 |  |  | 714 | 16 | 16 | Air Handling Unit | 8 | 5712 | 13.4664 | 1 | 13.4664 | 3 | 13.4664 | 3
302 | classroom | 2224 | 148 |  |  | 670 | 15 | 15 | Air Handling Unit | 8 | 5360 | 24.8955 | 1 | 24.8955 | 4 | 24.8955 | 4
303 | classroom | 2929 | 195 |  |  | 671 | 15 | 15 | Air Handling Unit | 8 | 5368 | 32.7385 | 1 | 32.7385 | 4 | 32.7385 | 4
304A | classroom | 1335 | 89 |  |  | 984 | 22 | 22 | Air Handling Unit | 8 | 7872 | 10.1753 | 1 | 10.1753 | 3 | 10.1753 | 3
305 | classroom | 3981 | 265 |  |  | 956 | 21 | 21 | Air Handling Unit | 8 | 7648 | 31.2317 | 1 | 31.2317 | 4 | 31.2317 | 4
306 | classroom | 3461 | 230 |  |  | 783 | 17 | 17 | Air Handling Unit | 8 | 6264 | 33.1513 | 1 | 33.1513 | 4 | 33.1513 | 4
307 | classroom | 996 | 66 |  |  | 912 | 20 | 20 | Air Handling Unit | 8 | 7296 | 8.1908 | 1 | 8.1908 | 2 | 8.1908 | 2
308 | classroom | 1202 | 80 |  |  | 928 | 21 | 21 | Air Handling Unit | 8 | 7424 | 9.7144 | 1 | 9.7144 | 2 | 9.7144 | 2
309 | classroom | 2171 | 144 |  |  | 847 | 19 | 19 | Air Handling Unit | 8 | 6776 | 19.2237 | 1 | 19.2237 | 3 | 19.2237 | 3
310 | classroom | 2047 | 136 |  |  | 881 | 20 | 20 | Air Handling Unit | 8 | 7048 | 17.4262 | 1 | 17.4262 | 3 | 17.4262 | 3
311A | classroom | 990 | 66 |  |  | 929 | 21 | 21 | Air Handling Unit | 8 | 7432 | 7.9925 | 1 | 7.9925 | 2 | 7.9925 | 2
312 | classroom | 211 | 14 |  |  | 716 | 16 | 14 | Air Handling Unit | 8 | 5728 | 2.2102 | 1 | 2.2102 | 1 | 2.2102 | 1
313 | classroom | 868 | 57 |  |  | 672 | 15 | 15 | Air Handling Unit | 8 | 5376 | 9.6875 | 1 | 9.6875 | 2 | 9.6875 | 2
314 | classroom | 350 | 23 |  |  | 719 | 16 | 16 | Air Handling Unit | 8 | 5752 | 3.6509 | 1 | 3.6509 | 1 | 3.6509 | 1
315 | classroom | 83 | 5 |  |  | 662 | 15 | 5 | Air Handling Unit | 8 | 5296 | 0.94033 | 1 | 0.94033 | 0 | 0.94033 | 0
316 | classroom | 1078 | 71 |  |  | 778 | 17 | 17 | Air Handling Unit | 8 | 6224 | 10.392 | 1 | 10.392 | 3 | 10.392 | 3
317 | classroom | 1382 | 92 |  |  | 604 | 13 | 13 | Air Handling Unit | 8 | 4832 | 17.1606 | 1 | 17.1606 | 3 | 17.1606 | 3
318 | classroom | 1811 | 120 |  |  | 610 | 13 | 13 | Air Handling Unit | 8 | 4880 | 22.2664 | 1 | 22.2664 | 3 | 22.2664 | 3
319 | classroom | 3185 | 212 |  |  | 644 | 14 | 14 | Air Handling Unit | 8 | 5152 | 37.0924 | 1 | 37.0924 | 4 | 37.0924 | 4
320 | classroom | 4504 | 300 |  |  | 738 | 16 | 16 | Air Handling Unit | 8 | 5904 | 45.7724 | 1 | 45.7724 | 4 | 45.7724 | 4
321 | classroom | 3538 | 235 |  |  | 786 | 17 | 17 | Air Handling Unit | 8 | 6288 | 33.7595 | 1 | 33.7595 | 4 | 33.7595 | 4
322 | classroom | 82 | 5 |  |  | 660 | 15 | 5 | Air Handling Unit | 8 | 5280 | 0.93182 | 1 | 0.93182 | 0 | 0.93182 | 0
323 | classroom | 1074 | 71 |  |  | 324 | 7 | 7 | Air Handling Unit | 8 | 2592 | 24.8611 | 1 | 24.8611 | 4 | 24.8611 | 4
324 | classroom | 909 | 60 |  |  | 659 | 14 | 14 | Air Handling Unit | 8 | 5272 | 10.3452 | 1 | 10.3452 | 3 | 10.3452 | 3
325 | classroom | 1021 | 68 |  |  | 346 | 7 | 7 | Air Handling Unit | 8 | 2768 | 22.1315 | 1 | 22.1315 | 3 | 22.1315 | 3
326 | classroom | 481 | 32 |  |  | 659 | 14 | 14 | Air Handling Unit | 8 | 5272 | 5.4742 | 1 | 5.4742 | 2 | 5.4742 | 2
326 | Counselor Office | 513 | 34 |  |  | 306 | 6 | 6 | Air Handling Unit | 8 | 2448 | 12.5735 | 1 | 12.5735 | 3 | 12.5735 | 3
- | Auditorium | 0 | 0 |  |  | 5460 | 124 | 0 | Air Handling Unit | 8 | 43680 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Boy's Gym | 14624 | 974 |  |  | 4350 | 98 | 98 | Air Handling Unit | 8 | 34800 | 25.2138 | 1.062 | 26.7779 | 4 | 26.7779 | 4
- | Cafeteria | 498 | 33 |  |  | 408 | 9 | 9 | Air Handling Unit | 8 | 3264 | 9.1544 | 1 | 9.1544 | 2 | 9.1544 | 2
- | Computer Lab | 446 | 29 |  |  | 657 | 14 | 14 | Air Handling Unit | 8 | 5256 | 5.0913 | 1 | 5.0913 | 2 | 5.0913 | 2
- | Conf. Room | 884 | 58 |  |  | 336 | 7 | 7 | Air Handling Unit | 8 | 2688 | 19.7321 | 1 | 19.7321 | 3 | 19.7321 | 3
- | Kitchen | 5749 | 383 |  |  | 816 | 18 | 18 | Air Handling Unit | 8 | 6528 | 52.8401 | 1 | 52.8401 | 5 | 52.8401 | 5
- | Kitchen- Freezer/Cooler Condenser Fan | 0 | 0 |  |  | 144 | 3 | 0 | Air Handling Unit | 8 | 1152 | 0 | 1 | 0 | 0 | 0 | 0
- | Lunch Room | 175 | 11 |  |  | 2040 | 46 | 11 | Air Handling Unit | 8 | 16320 | 0.64338 | 1 | 0.64338 | 0 | 0.64338 | 0
- | Main Office | 632 | 42 |  |  | 531 | 12 | 12 | Air Handling Unit | 8 | 4248 | 8.9266 | 1 | 8.9266 | 2 | 8.9266 | 2
Principal | Office |  | 0 | Yes | 20 | 259 | 5 | 5 |  | 8 | 2072 | 0 | 1 | 0 | 0 | 20 | 3
Nurse | Office |  | 0 | Yes | 20 | 249 | 5 | 5 |  | 8 | 1992 | 0 | 1 | 0 | 0 | 20 | 3
- | MEDIA LAB A | 304 | 20 |  |  | 60 | 1 | 1 | Air Handling Unit | 8 | 480 | 38 | 1 | 38 | 4 | 38 | 4
- | MEDIA LAB B | 564 | 37 |  |  | 60 | 1 | 1 | Air Handling Unit | 8 | 480 | 70.5 | 1 | 70.5 | 5 | 70.5 | 5
- | Staff Lounge | 421 | 28 |  |  | 657 | 14 | 14 | Air Handling Unit | 8 | 5256 | 4.8059 | 1 | 4.8059 | 2 | 4.8059 | 2
- | VP Office | 1325 | 88 |  |  | 232 | 5 | 5 | Air Handling Unit | 8 | 1856 | 42.8341 | 1 | 42.8341 | 4 | 42.8341 | 4
- | Gym- Weight Room A | 1230 | 82 |  |  | 181 | 4 | 4 | Air Handling Unit | 8 | 1448 | 50.9669 | 1 | 50.9669 | 5 | 50.9669 | 5
- | Gym- Weight Room B | 1164 | 77 |  |  | 181 | 4 | 4 | Air Handling Unit | 8 | 1448 | 48.232 | 1 | 48.232 | 4 | 48.232 | 4
Sheet Last Modified: | 2021-04-26
School: | Laura W. Waring Elementary School
Vendor: | EMCOR Fluidics | EMCOR Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 188 | 12 | Yes | 20 | 430 | 9 | 9 | Nesbitt Unit Ventilator | 8 | 3440 | 3.2791 | 1 | 3.2791 | 1 | 23.2791 | 3
102 | Classroom | 118 | 7 | Yes | 20 | 872 | 19 | 19 | Nesbitt Unit Ventilator | 8 | 6976 | 1.0149 | 1 | 1.0149 | 1 | 21.0149 | 3
103 | Classroom | 150 | 10 | Yes | 20 | 872 | 19 | 19 | Nesbitt Unit Ventilator | 8 | 6976 | 1.2901 | 1 | 1.2901 | 1 | 21.2901 | 3
105 | Classroom | 180 | 12 | Yes | 20 | 789 | 17 | 17 | Nesbitt Unit Ventilator | 8 | 6312 | 1.711 | 1 | 1.711 | 1 | 21.711 | 3
106 | Classroom | 171 | 11 | Yes | 20 | 850 | 19 | 19 | Nesbitt Unit Ventilator | 8 | 6800 | 1.5088 | 1 | 1.5088 | 1 | 21.5088 | 3
107 | Classroom | 226 | 15 |  |  | 850 | 19 | 15 | Nesbitt Unit Ventilator | 8 | 6800 | 1.9941 | 1 | 1.9941 | 1 | 1.9941 | 1
108 | Classroom | 165 | 11 | Yes | 20 | 750 | 17 | 17 | Nesbitt Unit Ventilator | 8 | 6000 | 1.65 | 1 | 1.65 | 1 | 21.65 | 3
200 | Counselor's Room | 0 | 0 |  |  | 300 | 6 | 0 | Nesbitt Unit Ventilator | 8 | 2400 | 0 | 1 | 0 | 0 | 0 | 0
201 | Computer Room | 0 | 0 | Yes | 20 | 925 | 21 | 21 | Nesbitt Unit Ventilator | 8 | 7400 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 87 | 5 | Yes | 20 | 888 | 20 | 20 | Nesbitt Unit Ventilator | 8 | 7104 | 0.7348 | 1 | 0.7348 | 0 | 20.7348 | 3
203 | Classroom | 274 | 18 |  |  | 888 | 20 | 18 | Nesbitt Unit Ventilator | 8 | 7104 | 2.3142 | 1 | 2.3142 | 1 | 2.3142 | 1
204 | Classroom | 276 | 18 |  |  | 888 | 20 | 18 | Nesbitt Unit Ventilator | 8 | 7104 | 2.3311 | 1 | 2.3311 | 1 | 2.3311 | 1
205 | Classroom | 311 | 20 |  |  | 850 | 19 | 19 | Nesbitt Unit Ventilator | 8 | 6800 | 2.7441 | 1 | 2.7441 | 1 | 2.7441 | 1
206 | Classroom | 193 | 12 | Yes | 20 | 850 | 19 | 19 | Nesbitt Unit Ventilator | 8 | 6800 | 1.7029 | 1 | 1.7029 | 1 | 21.7029 | 3
207 | Classroom | 152 | 10 | Yes | 20 | 850 | 19 | 19 | Nesbitt Unit Ventilator | 8 | 6800 | 1.3412 | 1 | 1.3412 | 1 | 21.3412 | 3
208 | Classroom | 209 | 13 | Yes | 20 | 750 | 17 | 17 | Nesbitt Unit Ventilator | 8 | 6000 | 2.09 | 1 | 2.09 | 1 | 22.09 | 3
300 | Classroom | 0 | 0 | Yes | 20 | 888 | 20 | 20 | Nesbitt Unit Ventilator | 8 | 7104 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 212 | 14 | Yes | 20 | 888 | 20 | 20 | Nesbitt Unit Ventilator | 8 | 7104 | 1.7905 | 1 | 1.7905 | 1 | 21.7905 | 3
302 | Classroom | 105 | 7 | Yes | 20 | 888 | 20 | 20 | Nesbitt Unit Ventilator | 8 | 7104 | 0.88682 | 1 | 0.88682 | 0 | 20.8868 | 3
303 | Classroom | 133 | 8 | Yes | 20 | 888 | 20 | 20 | Nesbitt Unit Ventilator | 8 | 7104 | 1.1233 | 1 | 1.1233 | 1 | 21.1233 | 3
304 | Classroom | 255 | 17 |  |  | 888 | 20 | 17 | Nesbitt Unit Ventilator | 8 | 7104 | 2.1537 | 1 | 2.1537 | 1 | 2.1537 | 1
305 | Classroom | 93 | 6 | Yes | 20 | 888 | 20 | 20 | Nesbitt Unit Ventilator | 8 | 7104 | 0.78547 | 1 | 0.78547 | 0 | 20.7855 | 3
306/307 | Classroom | 266 | 17 |  |  | 1850 | 42 | 17 | Nesbitt Unit Ventilator | 8 | 14800 | 1.0784 | 1 | 1.0784 | 1 | 1.0784 | 1
308 | Classroom | 220 | 14 | Yes | 20 | 896 | 20 | 20 | Nesbitt Unit Ventilator | 8 | 7168 | 1.8415 | 1 | 1.8415 | 1 | 21.8415 | 3
311 | Dining Room | 120 | 8 |  |  | 242 | 5 | 5 | Nesbitt Unit Ventilator | 8 | 1936 | 3.719 | 1 | 3.719 | 1 | 3.719 | 1
- | Cafeteria | 0 | 0 |  |  | 3477 | 79 | 0 | Nesbitt Unit Ventilator | 8 | 27816 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Vestibule left of office | 0 | 0 |  |  | 96 | 2 | 0 | Nesbitt Unit Ventilator | 8 | 768 | 0 | 1 | 0 | 0 | 0 | 0
- | Nurse |  | 0 |  |  | 231 | 5 | 0 | Nesbitt Unit Ventilator | 8 | 1848 | 0 | 1 | 0 | 0 | 0 | 0
- | Faculty Lounge | 57 | 3 |  |  | 228 | 5 | 3 | Nesbitt Unit Ventilator | 8 | 1824 | 1.875 | 1 | 1.875 | 1 | 1.875 | 1
- | Health Office | 0 | 0 | Yes | 20 | 231 | 5 | 5 | Nesbitt Unit Ventilator | 8 | 1848 | 0 | 1 | 0 | 0 | 20 | 3
- | Multi-Purpose Room | 457 | 30 |  |  | 1820 | 41 | 30 | Nesbitt Unit Ventilator | 8 | 14560 | 1.8832 | 1 | 1.8832 | 1 | 1.8832 | 1
- | Main Office | 0 | 0 | Yes | 20 | 378 | 8 | 8 | Nesbitt Unit Ventilator | 8 | 3024 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office | 69 | 4 | Yes | 20 | 381 | 8 | 8 | Nesbitt Unit Ventilator | 8 | 3048 | 1.3583 | 1 | 1.3583 | 1 | 21.3583 | 3
Sheet Last Modified: | 2021-04-30
School: | George Washington High School
Vendor: | EMCOR | Meehan (Auditorium)
School: | George Washington High School Annex
Vendor:
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Main Building
1 | - | 370 | 24 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.6133 | 1 | 3.6133 | 1 | 3.6133 | 1
2 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
3 | - | 0 | 0 |  |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
4 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
5 | - | 0 | 0 |  |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
6 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
7 | - | 348 | 23 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.3984 | 1 | 3.3984 | 1 | 3.3984 | 1
8 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
9 | - | 412 | 27 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 4.0234 | 1 | 4.0234 | 2 | 4.0234 | 2
10 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
11 | - | 451 | 30 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 4.4043 | 1 | 4.4043 | 2 | 4.4043 | 2
12 | - | 0 | 0 |  |  | 775 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6200 | 0 | 1 | 0 | 0 | 0 | 0
13 | - | 414 | 27 |  |  | 1209 | 27 | 27 | Carrier / Perimeter Heater | 8 | 9672 | 2.5682 | 1 | 2.5682 | 1 | 2.5682 | 1
14 | - | 374 | 24 |  |  | 1209 | 27 | 24 | Carrier / Perimeter Heater | 8 | 9672 | 2.3201 | 1 | 2.3201 | 1 | 2.3201 | 1
15 | - | 403 | 26 |  |  | 1209 | 27 | 26 | Carrier / Perimeter Heater | 8 | 9672 | 2.5 | 1 | 2.5 | 1 | 2.5 | 1
16 | - | 849 | 56 |  |  | 1911 | 43 | 43 | Carrier / Perimeter Heater | 8 | 15288 | 3.332 | 1 | 3.332 | 1 | 3.332 | 1
17 | - | 0 | 0 |  |  | 1240 | 28 | 0 | Carrier / Perimeter Heater | 8 | 9920 | 0 | 1 | 0 | 0 | 0 | 0
18 | - | 763 | 50 |  |  | 1911 | 43 | 43 | Carrier / Perimeter Heater | 8 | 15288 | 2.9945 | 1 | 2.9945 | 1 | 2.9945 | 1
19 | - | 0 | 0 |  |  | 1302 | 29 | 0 | Carrier / Perimeter Heater | 8 | 10416 | 0 | 1 | 0 | 0 | 0 | 0
20 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
21 | - | 451 | 30 |  |  | 1240 | 28 | 28 | Carrier / Perimeter Heater | 8 | 9920 | 2.7278 | 1 | 2.7278 | 1 | 2.7278 | 1
22 | - | 421 | 28 |  |  | 1209 | 27 | 27 | Carrier / Perimeter Heater | 8 | 9672 | 2.6117 | 1 | 2.6117 | 1 | 2.6117 | 1
23 | - | 0 | 0 |  |  | 1240 | 28 | 0 | Carrier / Perimeter Heater | 8 | 9920 | 0 | 1 | 0 | 0 | 0 | 0
24 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
25 | - | 419 | 27 |  |  | 912 | 20 | 20 | Carrier / Perimeter Heater | 8 | 7296 | 3.4457 | 1 | 3.4457 | 1 | 3.4457 | 1
26 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
27 | - | 0 | 0 |  |  | 912 | 20 | 0 | Carrier / Perimeter Heater | 8 | 7296 | 0 | 1 | 0 | 0 | 0 | 0
28 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
29 | - | 355 | 23 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.4668 | 1 | 3.4668 | 1 | 3.4668 | 1
30 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
31 | - | 413 | 27 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 4.0332 | 1 | 4.0332 | 2 | 4.0332 | 2
32 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
33 | - | 338 | 22 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.3008 | 1 | 3.3008 | 1 | 3.3008 | 1
34 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
35 | - | 0 | 0 |  |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
36 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
37 | - | 0 | 0 |  |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
38 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
39 | - | 403 | 26 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.9355 | 1 | 3.9355 | 1 | 3.9355 | 1
100 | - | 334 | 22 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.2617 | 1 | 3.2617 | 1 | 3.2617 | 1
102 | - | 335 | 22 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.2715 | 1 | 3.2715 | 1 | 3.2715 | 1
104 | Health Room |  | 0 |  |  | 1488 | 33 | 0 |  | 8 | 11904 | 0 | 1 | 0 | 0 | 0 | 0
107 | - | 495 | 33 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
108 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
109 | - | 357 | 23 |  |  | 744 | 16 | 16 | Carrier / Perimeter Heater | 8 | 5952 | 3.5988 | 1 | 3.5988 | 1 | 3.5988 | 1
110 | - | 413 | 27 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
111 | - | 370 | 24 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.6133 | 1 | 3.6133 | 1 | 3.6133 | 1
112 | - | 398 | 26 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.8867 | 1 | 3.8867 | 1 | 3.8867 | 1
113 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
114 | - | 427 | 28 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 4.1699 | 1 | 4.1699 | 2 | 4.1699 | 2
115 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
116 | - | 368 | 24 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.5938 | 1 | 3.5938 | 1 | 3.5938 | 1
117 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
118 | - | 0 | 0 |  |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
119 | - | 368 | 24 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
120 | - | 0 | 0 |  |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
121 | - | 381 | 25 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.7207 | 1 | 3.7207 | 1 | 3.7207 | 1
122 | - | 408 | 27 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 3.8636 | 1 | 3.8636 | 1 | 3.8636 | 1
123 | - | 465 | 31 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 4.541 | 1 | 4.541 | 2 | 4.541 | 2
124 | - | 436 | 29 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 4.2578 | 1 | 4.2578 | 2 | 4.2578 | 2
125 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
126 | - | 336 | 22 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.2812 | 1 | 3.2812 | 1 | 3.2812 | 1
127 | - | 416 | 27 |  |  | 1102 | 25 | 25 | Carrier / Perimeter Heater | 8 | 8816 | 2.8312 | 1 | 2.8312 | 1 | 2.8312 | 1
128 | - | 0 | 0 |  |  | 1280 | 29 | 0 | Carrier / Perimeter Heater | 8 | 10240 | 0 | 1 | 0 | 0 | 0 | 0
129 | - | 366 | 24 |  |  | 1073 | 24 | 24 | Carrier / Perimeter Heater | 8 | 8584 | 2.5582 | 1 | 2.5582 | 1 | 2.5582 | 1
130 | - | 0 | 0 |  |  | 1280 | 29 | 0 | Carrier / Perimeter Heater | 8 | 10240 | 0 | 1 | 0 | 0 | 0 | 0
131 | - | 388 | 25 |  |  | 1160 | 26 | 25 | Carrier / Perimeter Heater | 8 | 9280 | 2.5086 | 1 | 2.5086 | 1 | 2.5086 | 1
132 | - | 610 | 40 |  |  | 1092 | 24 | 24 | Carrier / Perimeter Heater | 8 | 8736 | 4.1896 | 1 | 4.1896 | 2 | 4.1896 | 2
133 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
134 | - | 732 | 48 |  |  | 1092 | 24 | 24 | Carrier / Perimeter Heater | 8 | 8736 | 5.0275 | 1 | 5.0275 | 2 | 5.0275 | 2
135 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
136 | - | 325 | 21 |  |  | 1092 | 24 | 21 | Carrier / Perimeter Heater | 8 | 8736 | 2.2321 | 1 | 2.2321 | 1 | 2.2321 | 1
137 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
138 | - | 408 | 27 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
139 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
140 | - | 424 | 28 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
141 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
142 | - | 865 | 57 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
143 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
144 | - | 308 | 20 |  |  | 832 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6656 | 2.7764 | 1 | 2.7764 | 1 | 2.7764 | 1
145 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
146 | - | 0 | 0 |  |  | 775 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6200 | 0 | 1 | 0 | 0 | 0 | 0
147 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
148 | - | 242 | 16 |  |  | 775 | 17 | 16 | Carrier / Perimeter Heater | 8 | 6200 | 2.3419 | 1 | 2.3419 | 1 | 2.3419 | 1
149 -155 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
156 | - | 926 | 61 |  |  | 814 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6512 | 8.5319 | 1 | 8.5319 | 2 | 8.5319 | 2
157 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
158 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
159 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
160 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
161 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
162 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
164 | - | 695 | 46 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
200 | - | 485 | 32 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 4.7363 | 1 | 4.7363 | 2 | 4.7363 | 2
201 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
202 | - | 417 | 27 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 4.0723 | 1 | 4.0723 | 2 | 4.0723 | 2
203 | - | 397 | 26 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.877 | 1 | 3.877 | 1 | 3.877 | 1
204 | - | 337 | 22 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 3.291 | 1 | 3.291 | 1 | 3.291 | 1
205 | - | 0 | 0 |  |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
206 | - | 424 | 28 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
207 | - | 0 | 0 |  |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
208 | - | 536 | 35 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 5.2344 | 1 | 5.2344 | 2 | 5.2344 | 2
209 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
210 | - | 575 | 38 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 5.6152 | 1 | 5.6152 | 2 | 5.6152 | 2
211 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
212 | - | 514 | 34 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 5.0195 | 1 | 5.0195 | 2 | 5.0195 | 2
213 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
214 | - | 0 | 0 |  |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
215 | - | 547 | 36 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 5.3418 | 1 | 5.3418 | 2 | 5.3418 | 2
216 | - | 519 | 34 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 5.0684 | 1 | 5.0684 | 2 | 5.0684 | 2
217 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
218 | - | 521 | 34 |  |  | 1536 | 34 | 34 | Carrier / Perimeter Heater | 8 | 12288 | 2.5439 | 1 | 2.5439 | 1 | 2.5439 | 1
219 | - | 0 | 0 |  |  | 1536 | 34 | 0 | Carrier / Perimeter Heater | 8 | 12288 | 0 | 1 | 0 | 0 | 0 | 0
220 | - | 0 | 0 |  |  | 1536 | 34 | 0 | Carrier / Perimeter Heater | 8 | 12288 | 0 | 1 | 0 | 0 | 0 | 0
221 | - | 0 | 0 |  |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
222 | - | 569 | 37 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 5.5566 | 1 | 5.5566 | 2 | 5.5566 | 2
223 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
224 | - | 533 | 35 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.0473 | 1 | 5.0473 | 2 | 5.0473 | 2
225 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
226 | - | 536 | 35 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.0758 | 1 | 5.0758 | 2 | 5.0758 | 2
227 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
228 | - | 543 | 36 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.142 | 1 | 5.142 | 2 | 5.142 | 2
229 | - | 508 | 33 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 4.8106 | 1 | 4.8106 | 2 | 4.8106 | 2
230 | - | 563 | 37 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.3314 | 1 | 5.3314 | 2 | 5.3314 | 2
231 | - | 492 | 32 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 4.6591 | 1 | 4.6591 | 2 | 4.6591 | 2
232 | - | 563 | 37 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.3314 | 1 | 5.3314 | 2 | 5.3314 | 2
233 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
234 | - | 539 | 35 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.1042 | 1 | 5.1042 | 2 | 5.1042 | 2
235 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
236 | - | 544 | 36 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.1515 | 1 | 5.1515 | 2 | 5.1515 | 2
237 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
238 | - | 399 | 26 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 3.7784 | 1 | 3.7784 | 1 | 3.7784 | 1
239 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
240 | - | 0 | 0 |  |  | 768 | 17 | 0 | Carrier / Perimeter Heater | 8 | 6144 | 0 | 1 | 0 | 0 | 0 | 0
241 | - | 344 | 22 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 3.2576 | 1 | 3.2576 | 1 | 3.2576 | 1
242 | - | 450 | 30 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 4.3945 | 1 | 4.3945 | 2 | 4.3945 | 2
243 | - | 455 | 30 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 4.3087 | 1 | 4.3087 | 2 | 4.3087 | 2
244 | - | 428 | 28 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 4.053 | 1 | 4.053 | 2 | 4.053 | 2
245 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
246 | - | 423 | 28 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 4.0057 | 1 | 4.0057 | 2 | 4.0057 | 2
300 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
301 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
302 | - | 542 | 36 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.1326 | 1 | 5.1326 | 2 | 5.1326 | 2
303 | - | 539 | 35 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.1042 | 1 | 5.1042 | 2 | 5.1042 | 2
304 | - | 591 | 39 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.5966 | 1 | 5.5966 | 2 | 5.5966 | 2
305 | - | 556 | 37 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.2652 | 1 | 5.2652 | 2 | 5.2652 | 2
306 | - | 561 | 37 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.3125 | 1 | 5.3125 | 2 | 5.3125 | 2
307 | - | 592 | 39 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.6061 | 1 | 5.6061 | 2 | 5.6061 | 2
308 | - | 263 | 17 |  |  | 792 | 18 | 17 | Carrier / Perimeter Heater | 8 | 6336 | 2.4905 | 1 | 2.4905 | 1 | 2.4905 | 1
309 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
310 | - | 602 | 40 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.7008 | 1 | 5.7008 | 2 | 5.7008 | 2
311 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
312 | - | 599 | 39 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.6723 | 1 | 5.6723 | 2 | 5.6723 | 2
313 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
314 | - | 539 | 35 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.1042 | 1 | 5.1042 | 2 | 5.1042 | 2
315 | - | 530 | 35 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.0189 | 1 | 5.0189 | 2 | 5.0189 | 2
316 | - | 557 | 37 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.2746 | 1 | 5.2746 | 2 | 5.2746 | 2
317 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
318 | - | 580 | 38 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 5.6641 | 1 | 5.6641 | 2 | 5.6641 | 2
319 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
320 | - | 610 | 40 |  |  | 768 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6144 | 5.957 | 1 | 5.957 | 2 | 5.957 | 2
321 | - | 551 | 36 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.2178 | 1 | 5.2178 | 2 | 5.2178 | 2
322 | - | 554 | 36 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.2462 | 1 | 5.2462 | 2 | 5.2462 | 2
323 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
324 | - | 591 | 39 |  |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 8 | 7680 | 4.6172 | 1 | 4.6172 | 2 | 4.6172 | 2
325 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
326 | - | 533 | 35 |  |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 8 | 7680 | 4.1641 | 1 | 4.1641 | 2 | 4.1641 | 2
327 | - | 554 | 36 |  |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 8 | 7680 | 4.3281 | 1 | 4.3281 | 2 | 4.3281 | 2
328 | - | 561 | 37 |  |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 8 | 7680 | 4.3828 | 1 | 4.3828 | 2 | 4.3828 | 2
329 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
330 | - | 572 | 38 |  |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 8 | 7680 | 4.4688 | 1 | 4.4688 | 2 | 4.4688 | 2
331 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
332 | - | 576 | 38 |  |  | 792 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6336 | 5.4545 | 1 | 5.4545 | 2 | 5.4545 | 2
333 | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
334 | - | 506 | 33 |  |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 8 | 7680 | 3.9531 | 1 | 3.9531 | 1 | 3.9531 | 1
335 | - | 605 | 40 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
336 | - | 559 | 37 |  |  | 960 | 21 | 21 | Carrier / Perimeter Heater | 8 | 7680 | 4.3672 | 1 | 4.3672 | 2 | 4.3672 | 2
337 | - | 0 | 0 |  |  | 792 | 18 | 0 | Carrier / Perimeter Heater | 8 | 6336 | 0 | 1 | 0 | 0 | 0 | 0
338 | - | 0 | 0 |  |  | 792 | 18 | 0 | Carrier / Perimeter Heater | 8 | 6336 | 0 | 1 | 0 | 0 | 0 | 0
339 | - | 0 | 0 |  |  | 792 | 18 | 0 | Carrier / Perimeter Heater | 8 | 6336 | 0 | 1 | 0 | 0 | 0 | 0
Gymnasium | Gymnasium |  | 0 |  |  |  | 0 | 0
Auditorium | Auditorium | 17891 | 1192 |  |  | 10800 | 245 | 245 | Air Handling Unit | 8 | 86400 | 12.4243 | 1.4912 | 18.5266 | 3 | 18.5266 | 3
- | Beacon Left | 311 | 20 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
- | Beacon Right | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
- | Cafeteria | 17015 | 1134 |  |  |  | 0 | 0 | Air Handling Unit
Center | - | 438 | 29 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
Dean's Office | - | 437 | 29 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
Library Left | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
Main Office | - | 394 | 26 |  |  | 2332 | 53 | 26 | Carrier / Perimeter Heater | 8 | 18656 | 1.2672 | 1 | 1.2672 | 1 | 1.2672 | 1
Principle | - | 0 | 0 |  |  | 615 | 13 | 0 | Carrier / Perimeter Heater | 8 | 4920 | 0 | 1 | 0 | 0 | 0 | 0
Right | - | 0 | 0 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
- | Roster | 426 | 28 |  |  |  | 0 | 0 | Carrier / Perimeter Heater
- | Staff Cafeteria | 1328 | 88 |  |  |  | 0 | 0 | Make-up Air Unit
- | Student Cafeteria | 8507 | 567 |  |  | 12000 | 272 | 272 | Make-up Air Unit | 8 | 96000 | 5.3169 | 1.4912 | 7.9283 | 2 | 7.9283 | 2
Annex
408 Annex | Classroom |  | 0 | Yes | 20 | 858 | 19 | 19 | Air Handling Unit | 8 | 6864 | 0 | 1 | 0 | 0 | 20 | 3
409 Annex | Classroom |  | 0 | Yes | 20 | 858 | 19 | 19 | Air Handling Unit | 8 | 6864 | 0 | 1 | 0 | 0 | 20 | 3
410 Annex | Classroom |  | 0 | Yes | 20 | 858 | 19 | 19 | Air Handling Unit | 8 | 6864 | 0 | 1 | 0 | 0 | 20 | 3
412 Annex | Classroom |  | 0 | Yes | 20 |  | 0 | 0 | Air Handling Unit
Kitchen Annex | Kitchen |  | 0 | Yes | 20 |  | 0 | 0 | Air Handling Unit
Recceration room | - |  | 0 |  |  | 3780 | 85 | 85 |  | 8 | 30240 | 0 | 1.062 | 0 | 0 | 0 | 0
Health Suite/ 11 rms | - |  | 0 |  |  | 77 | 1 | 1 |  | 8 | 616 | 0 | 1 | 0 | 0 | 0 | 0
Health Suite/ 2 rms | - |  | 0 |  |  | 80 | 1 | 1 |  | 8 | 640 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-14
School: | Grover Washington Jr. Middle School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | CLASSROOM | 288 | 19 |  |  | 700 | 15 | 15 | Fan Coil Unit | 8 | 5600 | 3.0857 | 1 | 3.0857 | 1 | 3.0857 | 1
101 | CLASSROOM | 207 | 13 | Yes | 20 | 700 | 15 | 15 | Fan Coil Unit | 8 | 5600 | 2.2179 | 1 | 2.2179 | 1 | 22.2179 | 3
102 | CLASSROOM | 164 | 10 | Yes | 20 | 698 | 15 | 15 | Fan Coil Unit | 8 | 5584 | 1.7622 | 1 | 1.7622 | 1 | 21.7622 | 3
102A | CLASSROOM | 185 | 12 |  |  | 160 | 3 | 3 | Fan Coil Unit | 8 | 1280 | 8.6719 | 1 | 8.6719 | 2 | 8.6719 | 2
103 | CLASSROOM | 476 | 31 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 4.1608 | 1 | 4.1608 | 2 | 4.1608 | 2
104 | CLASSROOM | 595 | 39 |  |  | 783 | 17 | 17 | Univent | 8 | 6264 | 5.6992 | 1 | 5.6992 | 2 | 5.6992 | 2
105 | CLASSROOM | 935 | 62 |  |  | 726 | 16 | 16 | Univent | 8 | 5808 | 9.6591 | 1 | 9.6591 | 2 | 9.6591 | 2
106 | CLASSROOM | 421 | 28 |  |  | 726 | 16 | 16 | Univent | 8 | 5808 | 4.3492 | 1 | 4.3492 | 2 | 4.3492 | 2
107 | CLASSROOM | 274 | 18 |  |  | 858 | 19 | 18 | Univent | 8 | 6864 | 2.3951 | 1 | 2.3951 | 1 | 2.3951 | 1
108 | CLASSROOM | 395 | 26 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 3.4528 | 1 | 3.4528 | 1 | 3.4528 | 1
109 | CLASSROOM | 573 | 38 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 5.0087 | 1 | 5.0087 | 2 | 5.0087 | 2
110 | CLASSROOM | 310 | 20 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 2.7098 | 1 | 2.7098 | 1 | 2.7098 | 1
112 | CLASSROOM | 377 | 25 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 3.2955 | 1 | 3.2955 | 1 | 3.2955 | 1
113 | CLASSROOM | 392 | 26 |  |  | 312 | 7 | 7 | Univent | 8 | 2496 | 9.4231 | 1 | 9.4231 | 2 | 9.4231 | 2
114 | CLASSROOM | 361 | 24 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 3.1556 | 1 | 3.1556 | 1 | 3.1556 | 1
115 | CLASSROOM | 292 | 19 |  |  | 726 | 16 | 16 | Univent | 8 | 5808 | 3.0165 | 1 | 3.0165 | 1 | 3.0165 | 1
116 | CLASSROOM | 749 | 49 |  |  | 726 | 16 | 16 | Univent | 8 | 5808 | 7.7376 | 1 | 7.7376 | 2 | 7.7376 | 2
117 | CLASSROOM | 763 | 50 |  |  | 726 | 16 | 16 | Univent | 8 | 5808 | 7.8822 | 1 | 7.8822 | 2 | 7.8822 | 2
118 | CLASSROOM | 757 | 50 |  |  | 726 | 16 | 16 | Univent | 8 | 5808 | 7.8202 | 1 | 7.8202 | 2 | 7.8202 | 2
119 | CLASSROOM | 396 | 26 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 3.4615 | 1 | 3.4615 | 1 | 3.4615 | 1
120 | CLASSROOM | 304 | 20 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 2.6573 | 1 | 2.6573 | 1 | 2.6573 | 1
121 | CLASSROOM | 370 | 24 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 3.2343 | 1 | 3.2343 | 1 | 3.2343 | 1
122 | CLASSROOM | 314 | 20 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 2.7448 | 1 | 2.7448 | 1 | 2.7448 | 1
201 | 2ND FLOOR C WING OFFICE | 211 | 14 |  |  | 312 | 7 | 7 | Univent | 8 | 2496 | 5.0721 | 1 | 5.0721 | 2 | 5.0721 | 2
202 | CLASSROOM | 601 | 40 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 5.2535 | 1 | 5.2535 | 2 | 5.2535 | 2
203 | CLASSROOM | 580 | 38 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 5.0699 | 1 | 5.0699 | 2 | 5.0699 | 2
204 | CLASSROOM | 304 | 20 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 2.6573 | 1 | 2.6573 | 1 | 2.6573 | 1
205 | CLASSROOM | 285 | 19 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 2.4913 | 1 | 2.4913 | 1 | 2.4913 | 1
206 | CLASSROOM | 406 | 27 |  |  | 783 | 17 | 17 | Univent | 8 | 6264 | 3.8889 | 1 | 3.8889 | 1 | 3.8889 | 1
207 | CLASSROOM | 456 | 30 |  |  | 726 | 16 | 16 | Univent | 8 | 5808 | 4.7107 | 1 | 4.7107 | 2 | 4.7107 | 2
208 | CLASSROOM | 561 | 37 |  |  | 1584 | 36 | 36 | Univent | 8 | 12672 | 2.6562 | 1 | 2.6562 | 1 | 2.6562 | 1
209 | CLASSROOM | 320 | 21 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 2.7972 | 1 | 2.7972 | 1 | 2.7972 | 1
210 | CLASSROOM | 388 | 25 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 3.3916 | 1 | 3.3916 | 1 | 3.3916 | 1
211 | CLASSROOM | 348 | 23 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 3.042 | 1 | 3.042 | 1 | 3.042 | 1
212 | CLASSROOM | 318 | 21 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 2.7797 | 1 | 2.7797 | 1 | 2.7797 | 1
213 | CLASSROOM | 307 | 20 |  |  | 1248 | 28 | 20 | Univent | 8 | 9984 | 1.845 | 1 | 1.845 | 1 | 1.845 | 1
214 | CLASSROOM | 286 | 19 | Yes | 20 | 1144 | 26 | 26 | Univent | 8 | 9152 | 1.875 | 1 | 1.875 | 1 | 21.875 | 3
215 | CLASSROOM | 693 | 46 |  |  | 1170 | 26 | 26 | Univent | 8 | 9360 | 4.4423 | 1 | 4.4423 | 2 | 4.4423 | 2
216 | CLASSROOM | 370 | 24 |  |  | 783 | 17 | 17 | Univent | 8 | 6264 | 3.5441 | 1 | 3.5441 | 1 | 3.5441 | 1
217 | CLASSROOM | 306 | 20 |  |  | 726 | 16 | 16 | Univent | 8 | 5808 | 3.1612 | 1 | 3.1612 | 1 | 3.1612 | 1
218 | CLASSROOM | 314 | 20 |  |  | 783 | 17 | 17 | Univent | 8 | 6264 | 3.0077 | 1 | 3.0077 | 1 | 3.0077 | 1
219 | CLASSROOM | 332 | 22 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 2.9021 | 1 | 2.9021 | 1 | 2.9021 | 1
220 | CLASSROOM | 407 | 27 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 3.5577 | 1 | 3.5577 | 1 | 3.5577 | 1
221 | 2ND FLOOR D WING OFFICE | 181 | 12 |  |  | 312 | 7 | 7 | Univent | 8 | 2496 | 4.351 | 1 | 4.351 | 2 | 4.351 | 2
301 | CLASSROOM | 112 | 7 | Yes | 20 | 858 | 19 | 19 | Fan Coil Unit | 8 | 6864 | 0.97902 | 1 | 0.97902 | 0 | 20.979 | 3
302 | CLASSROOM | 339 | 22 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 2.9633 | 1 | 2.9633 | 1 | 2.9633 | 1
303 | CLASSROOM | 0 | 0 | Yes | 20 | 858 | 19 | 19 | Univent | 8 | 6864 | 0 | 1 | 0 | 0 | 20 | 3
304 | CLASSROOM | 231 | 15 |  |  | 858 | 19 | 15 | Univent | 8 | 6864 | 2.0192 | 1 | 2.0192 | 1 | 2.0192 | 1
305 | CLASSROOM | 385 | 25 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 3.3654 | 1 | 3.3654 | 1 | 3.3654 | 1
306 | CLASSROOM | 353 | 23 |  |  | 783 | 17 | 17 | Univent | 8 | 6264 | 3.3812 | 1 | 3.3812 | 1 | 3.3812 | 1
307 | CLASSROOM | 316 | 21 |  |  | 726 | 16 | 16 | Univent | 8 | 5808 | 3.2645 | 1 | 3.2645 | 1 | 3.2645 | 1
308 | CLASSROOM | 306 | 20 |  |  | 1584 | 36 | 20 | Univent | 8 | 12672 | 1.4489 | 1 | 1.4489 | 1 | 1.4489 | 1
309 | CLASSROOM | 486 | 32 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 4.2483 | 1 | 4.2483 | 2 | 4.2483 | 2
310 | CLASSROOM | 283 | 18 |  |  | 858 | 19 | 18 | Univent | 8 | 6864 | 2.4738 | 1 | 2.4738 | 1 | 2.4738 | 1
311 | CLASSROOM | 265 | 17 |  |  | 858 | 19 | 17 | Univent | 8 | 6864 | 2.3164 | 1 | 2.3164 | 1 | 2.3164 | 1
312 | CLASSROOM | 389 | 25 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 3.4003 | 1 | 3.4003 | 1 | 3.4003 | 1
313 | CLASSROOM | 355 | 23 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 3.1031 | 1 | 3.1031 | 1 | 3.1031 | 1
314 | CLASSROOM | 305 | 20 | Yes | 20 | 1144 | 26 | 26 | Univent | 8 | 9152 | 1.9996 | 1 | 1.9996 | 1 | 21.9996 | 3
315 | CLASSROOM | 1003 | 66 |  |  | 1170 | 26 | 26 | Univent | 8 | 9360 | 6.4295 | 1 | 6.4295 | 2 | 6.4295 | 2
316 | CLASSROOM | 363 | 24 |  |  | 783 | 17 | 17 | Univent | 8 | 6264 | 3.477 | 1 | 3.477 | 1 | 3.477 | 1
317 | CLASSROOM | 81 | 5 | Yes | 20 | 858 | 19 | 19 | Univent | 8 | 6864 | 0.70804 | 1 | 0.70804 | 0 | 20.708 | 3
318 | CLASSROOM | 510 | 34 | Yes | 20 | 858 | 19 | 19 | Univent | 8 | 6864 | 4.458 | 1 | 4.458 | 2 | 24.458 | 4
319 | CLASSROOM | 463 | 30 |  |  | 858 | 19 | 19 | Univent | 8 | 6864 | 4.0472 | 1 | 4.0472 | 2 | 4.0472 | 2
320 | CLASSROOM | 0 | 0 | Yes | 20 | 858 | 19 | 19 | Univent | 8 | 6864 | 0 | 1 | 0 | 0 | 20 | 3
- | GYMNASIUM | 900 | 60 |  |  | 6370 | 144 | 60 | Rooftop Unit | 8 | 50960 | 1.0597 | 1.4912 | 1.5801 | 1 | 1.5801 | 1
- | CAFETERIA | 3339 | 222 |  |  | 5160 | 117 | 117 | Rooftop Unit | 8 | 41280 | 4.8532 | 1.062 | 5.1543 | 2 | 5.1543 | 2
- | AUDITORIUM | 2146 | 143 |  |  | 7008 | 159 | 143 | Rooftop Unit | 8 | 56064 | 2.2967 | 1.4912 | 3.4247 | 1 | 3.4247 | 1
- | KITCHEN HOOD | 8665 | 577 |  |  | 1584 | 36 | 36 | Rooftop Unit | 8 | 12672 | 41.0275 | 1 | 41.0275 | 4 | 41.0275 | 4
- | 1ST FLOOR BACK CORR. | 255 | 17 |  |  | 800 | 18 | 17 | Fan Coil Unit | 8 | 6400 | 2.3906 | 1 | 2.3906 | 1 | 2.3906 | 1
- | 1ST FLOOR CIRCLE HALL | 220 | 14 |  |  | 1246 | 28 | 14 | Fan Coil Unit | 8 | 9968 | 1.3242 | 1 | 1.3242 | 1 | 1.3242 | 1
- | 1ST FLOOR CORR INFRONT OF CAFÉ | 209 | 13 |  |  | 1008 | 22 | 13 | Fan Coil Unit | 8 | 8064 | 1.5551 | 1 | 1.5551 | 1 | 1.5551 | 1
- | 1ST FLOOR D WING OFFICE | 149 | 9 |  |  | 312 | 7 | 7 | Fan Coil Unit | 8 | 2496 | 3.5817 | 1 | 3.5817 | 1 | 3.5817 | 1
- | 1ST FLOOR ENTRANCE CORR. | 360 | 24 |  |  | 1053 | 23 | 23 | Fan Coil Unit | 8 | 8424 | 2.5641 | 1 | 2.5641 | 1 | 2.5641 | 1
- | 1ST FLOOR FRONT CORR. | 1074 | 71 |  |  | 1008 | 22 | 22 | Fan Coil Unit | 8 | 8064 | 7.9911 | 1 | 7.9911 | 2 | 7.9911 | 2
- | 1ST FLOOR FRONT HALL | 562 | 37 |  |  | 1540 | 35 | 35 | Fan Coil Unit | 8 | 12320 | 2.737 | 1 | 2.737 | 1 | 2.737 | 1
- | 1ST FLOOR OFFICES | 493 | 32 |  |  | 1888 | 42 | 32 | Fan Coil Unit | 8 | 15104 | 1.9584 | 1 | 1.9584 | 1 | 1.9584 | 1
- | 2ND / 1ST FLOOR D WING CORR | 380 | 25 |  |  | 1616 | 36 | 25 | Fan Coil Unit | 8 | 12928 | 1.7636 | 1 | 1.7636 | 1 | 1.7636 | 1
- | 2ND FLOOR C WING CLUSTER OFFICE | 1861 | 124 |  |  | 888 | 20 | 20 | Fan Coil Unit | 8 | 7104 | 15.7179 | 1 | 15.7179 | 3 | 15.7179 | 3
- | 2ND FLOOR C WING CONF. ROOM | 107 | 7 |  |  | 810 | 18 | 7 | Fan Coil Unit | 8 | 6480 | 0.99074 | 1 | 0.99074 | 0 | 0.99074 | 0
- | 2ND FLOOR CIRCLE HALL | 136 | 9 |  |  | 1246 | 28 | 9 | Fan Coil Unit | 8 | 9968 | 0.81862 | 1 | 0.81862 | 0 | 0.81862 | 0
- | 2ND FLOOR D WING SHOP | 97 | 6 |  |  | 408 | 9 | 6 | Fan Coil Unit | 8 | 3264 | 1.7831 | 1 | 1.7831 | 1 | 1.7831 | 1
- | 3RD FLOOR C WING CORR. | 660 | 44 |  |  | 1616 | 36 | 36 | Fan Coil Unit | 8 | 12928 | 3.0631 | 1 | 3.0631 | 1 | 3.0631 | 1
- | 3RD FLOOR CIRCLE HALL | 137 | 9 |  |  | 1246 | 28 | 9 | Fan Coil Unit | 8 | 9968 | 0.82464 | 1 | 0.82464 | 0 | 0.82464 | 0
- | 3RD FLOOR D WING CORR. | 501 | 33 |  |  | 1616 | 36 | 33 | Fan Coil Unit | 8 | 12928 | 2.3252 | 1 | 2.3252 | 1 | 2.3252 | 1
- | 3RD FLOOR D WING OFFICE | 167 | 11 |  |  | 312 | 7 | 7 | Fan Coil Unit | 8 | 2496 | 4.0144 | 1 | 4.0144 | 2 | 4.0144 | 2
- | 3RD FLOOR SHOP | 81 | 5 |  |  | 408 | 9 | 5 | Fan Coil Unit | 8 | 3264 | 1.489 | 1 | 1.489 | 1 | 1.489 | 1
- | BUILDING ENGINEER | 79 | 5 |  |  | 156 | 3 | 3 | Fan Coil Unit | 8 | 1248 | 3.7981 | 1 | 3.7981 | 1 | 3.7981 | 1
- | FACULTY BREAK ROOM | 188 | 12 |  |  | 648 | 14 | 12 | Fan Coil Unit | 8 | 5184 | 2.1759 | 1 | 2.1759 | 1 | 2.1759 | 1
- | GYM LOCKER ROOMS | 254 | 16 |  |  | 532 | 12 | 12 | Fan Coil Unit | 8 | 4256 | 3.5808 | 1 | 3.5808 | 1 | 3.5808 | 1
- | GYM TEACHER | 144 | 9 |  |  | 280 | 6 | 6 | Fan Coil Unit | 8 | 2240 | 3.8571 | 1 | 3.8571 | 1 | 3.8571 | 1
- | INSTRUMENT MUSIC | 0 | 0 | Yes | 20 | 1147 | 26 | 26 | Fan Coil Unit | 8 | 9176 | 0 | 1 | 0 | 0 | 20 | 3
- | IT Room | 268 | 17 |  |  | 396 | 9 | 9 | Fan Coil Unit | 8 | 3168 | 5.0758 | 1 | 5.0758 | 2 | 5.0758 | 2
- | KITCHEN OFFICE | 164 | 10 |  |  | 156 | 3 | 3 | Fan Coil Unit | 8 | 1248 | 7.8846 | 1 | 7.8846 | 2 | 7.8846 | 2
- | LIBRARY | 769 | 51 |  |  | 3864 | 87 | 51 | Fan Coil Unit | 8 | 30912 | 1.4926 | 1.062 | 1.5852 | 1 | 1.5852 | 1
- | LIBRARY STORAGE | 184 | 12 |  |  | 396 | 9 | 9 | Fan Coil Unit | 8 | 3168 | 3.4848 | 1 | 3.4848 | 1 | 3.4848 | 1
- | MUSIC PRACTICE B | 174 | 11 |  |  | 135 | 3 | 3 | Fan Coil Unit | 8 | 1080 | 9.6667 | 1 | 9.6667 | 2 | 9.6667 | 2
- | MUSIC PRACTICE C | 272 | 18 |  |  | 135 | 3 | 3 | Fan Coil Unit | 8 | 1080 | 15.1111 | 1 | 15.1111 | 3 | 15.1111 | 3
- | MUSIC PRATICE A | 126 | 8 |  |  | 135 | 3 | 3 | Fan Coil Unit | 8 | 1080 | 7 | 1 | 7 | 2 | 7 | 2
- | VOCAL MUSIC | 0 | 0 | Yes | 20 | 1221 | 27 | 27 | Fan Coil Unit | 8 | 9768 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-03-22
School: | Martha Washington Elementary-Middle School
Vendor: | Meehan
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 808 | 53 |  |  | 782 | 17 | 17 | House Fan | 8 | 6256 | 7.7494 | 1 | 7.7494 | 2 | 7.7494 | 2
102 | Classroom | 1564 | 104 |  |  | 920 | 20 | 20 | House Fan | 8 | 7360 | 12.75 | 1 | 12.75 | 3 | 12.75 | 3
103 | Classroom | 540 | 36 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 6.072 | 1 | 6.072 | 2 | 6.072 | 2
104 | Classroom | 250 | 16 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 2.8111 | 1 | 2.8111 | 1 | 2.8111 | 1
106 | Classroom | 529 | 35 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 5.9483 | 1 | 5.9483 | 2 | 5.9483 | 2
107 | Classroom | 370 | 24 |  |  | 690 | 15 | 15 | House Fan | 8 | 5520 | 4.0217 | 1 | 4.0217 | 2 | 4.0217 | 2
108 | Classroom | 279 | 18 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 3.1372 | 1 | 3.1372 | 1 | 3.1372 | 1
109 | Classroom | 525 | 35 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 5.9033 | 1 | 5.9033 | 2 | 5.9033 | 2
110 | - |  | 0 |  |  | 667 | 15 | 0 | Univent | 8 | 5336 | 0 | 1 | 0 | 0 | 0 | 0
111 | - |  | 0 | Yes | 20 | 667 | 15 | 15 | Univent | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
112 | - |  | 0 | Yes | 20 | 667 | 15 | 15 | Univent | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
113 | Classroom |  | 0 | Yes | 20 | 667 | 15 | 15 | Univent | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
201 | Classroom | 1290 | 86 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 14.5052 | 1 | 14.5052 | 3 | 14.5052 | 3
202 | Classroom | 990 | 66 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 11.1319 | 1 | 11.1319 | 3 | 11.1319 | 3
203 | Classroom | 425 | 28 |  |  | 759 | 17 | 17 | House Fan | 8 | 6072 | 4.1996 | 1 | 4.1996 | 2 | 4.1996 | 2
204 | Classroom | 442 | 29 |  |  | 713 | 16 | 16 | House Fan | 8 | 5704 | 4.6494 | 1 | 4.6494 | 2 | 4.6494 | 2
205 | Classroom | 345 | 23 |  |  | 621 | 14 | 14 | House Fan | 8 | 4968 | 4.1667 | 1 | 4.1667 | 2 | 4.1667 | 2
206 | Classroom | 829 | 55 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 9.3216 | 1 | 9.3216 | 2 | 9.3216 | 2
207 | Classroom | 479 | 31 |  |  | 660 | 15 | 15 | House Fan | 8 | 5280 | 5.4432 | 1 | 5.4432 | 2 | 5.4432 | 2
208 | Classroom | 489 | 32 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 5.4985 | 1 | 5.4985 | 2 | 5.4985 | 2
209 | Classroom | 394 | 26 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 4.4303 | 1 | 4.4303 | 2 | 4.4303 | 2
211 | - |  | 0 | Yes | 20 | 667 | 15 | 15 | Univent | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
212 | - |  | 0 | Yes | 20 | 667 | 15 | 15 | Univent | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 551 | 36 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 6.1957 | 1 | 6.1957 | 2 | 6.1957 | 2
302 | Classroom | 850 | 56 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 9.5577 | 1 | 9.5577 | 2 | 9.5577 | 2
303 | Classroom | 453 | 30 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 5.0937 | 1 | 5.0937 | 2 | 5.0937 | 2
304 | Classroom | 236 | 15 |  |  | 1215 | 27 | 15 | House Fan | 8 | 9720 | 1.4568 | 1 | 1.4568 | 1 | 1.4568 | 1
305 | Classroom | 62 | 4 |  |  | 644 | 14 | 4 | House Fan | 8 | 5152 | 0.72205 | 1 | 0.72205 | 0 | 0.72205 | 0
306 | Classroom | 807 | 53 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 9.0742 | 1 | 9.0742 | 2 | 9.0742 | 2
307 | Classroom | 649 | 43 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 7.2976 | 1 | 7.2976 | 2 | 7.2976 | 2
308 | Classroom | 506 | 33 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 5.6897 | 1 | 5.6897 | 2 | 5.6897 | 2
309 | Classroom | 826 | 55 |  |  | 667 | 15 | 15 | House Fan | 8 | 5336 | 9.2879 | 1 | 9.2879 | 2 | 9.2879 | 2
310 | Classroom | 139 | 9 |  |  | 667 | 15 | 9 | House Fan | 8 | 5336 | 1.563 | 1 | 1.563 | 1 | 1.563 | 1
- | Main Office |  | 0 | Yes | 20 | 420 | 9 | 9 | Radiator | 8 | 3360 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 20 | 234 | 5 | 5 | Radiator | 8 | 1872 | 0 | 1 | 0 | 0 | 20 | 3
- | Nurse's Office |  | 0 | Yes | 20 | 180 | 4 | 4 | Radiator | 8 | 1440 | 0 | 1 | 0 | 0 | 20 | 3
- | BE's Office | 543 | 36 |  |  | 782 | 17 | 17 | House Fan | 8 | 6256 | 5.2078 | 1 | 5.2078 | 2 | 5.2078 | 2
- | Lunch Room A | 1542 | 102 |  |  | 792 | 18 | 18 | House Fan | 8 | 6336 | 14.6023 | 1 | 14.6023 | 3 | 14.6023 | 3
- | Lunch Room B | 1570 | 104 |  |  | 1540 | 35 | 35 | House Fan | 8 | 12320 | 7.6461 | 1 | 7.6461 | 2 | 7.6461 | 2
G2 | - |  | 0 | Yes | 20 | 667 | 15 | 15 | Univent | 8 | 5336 | 0 | 1 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-23
School: | John H. Webster Elementary School
Vendor: | Devine Brothers | Devine Retest
School: | John H. Webster Elementary School- Little School House
Vendor: | Devine Brothers
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Webster Main Building
100 | Classroom | 1169 | 77 |  |  | 656 | 14 | 14 | Univent | 8 | 5248 | 13.3651 | 1 | 13.3651 | 3 | 13.3651 | 3
101 | Classroom | 593 | 39 |  |  | 1263 | 28 | 28 | Univent | 8 | 10104 | 3.5214 | 1 | 3.5214 | 1 | 3.5214 | 1
102 | Classroom | 435 | 29 |  |  | 721 | 16 | 16 | Univent | 8 | 5768 | 4.525 | 1 | 4.525 | 2 | 4.525 | 2
103 | Classroom | 1197 | 79 |  |  | 1062 | 24 | 24 | Univent | 8 | 8496 | 8.4534 | 1 | 8.4534 | 2 | 8.4534 | 2
104 | Classroom | 251 | 16 |  |  | 897 | 20 | 16 | Univent | 8 | 7176 | 2.0987 | 1 | 2.0987 | 1 | 2.0987 | 1
105 | Classroom | 310 | 20 |  |  | 531 | 12 | 12 | Univent | 8 | 4248 | 4.3785 | 1 | 4.3785 | 2 | 4.3785 | 2
106 | Classroom | 477 | 31 |  |  | 949 | 21 | 21 | Univent | 8 | 7592 | 3.7698 | 1 | 3.7698 | 1 | 3.7698 | 1
108 | Office | 49 | 3 |  |  | 226 | 5 | 3 | Air Handling Unit | 8 | 1808 | 1.6261 | 1 | 1.6261 | 1 | 1.6261 | 1
110 | Classroom | 358 | 23 |  |  | 1365 | 31 | 23 | Air Handling Unit | 8 | 10920 | 1.967 | 1 | 1.967 | 1 | 1.967 | 1
111 | Classroom | 312 | 20 |  |  | 1160 | 26 | 20 | Air Handling Unit | 8 | 9280 | 2.0172 | 1 | 2.0172 | 1 | 2.0172 | 1
112 | STS Classroom | 449 | 29 |  |  | 141 | 3 | 3 | Air Handling Unit | 8 | 1128 | 23.883 | 1 | 23.883 | 3 | 23.883 | 3
113 | Classroom | 280 | 18 |  |  | 1157 | 26 | 18 | Air Handling Unit | 8 | 9256 | 1.815 | 1 | 1.815 | 1 | 1.815 | 1
114 | Classroom | 290 | 19 |  |  | 1418 | 32 | 19 | Air Handling Unit | 8 | 11344 | 1.5339 | 1 | 1.5339 | 1 | 1.5339 | 1
200 | Classroom | 503 | 33 |  |  | 761 | 17 | 17 | Univent | 8 | 6088 | 4.9573 | 1 | 4.9573 | 2 | 4.9573 | 2
201 | Classroom | 369 | 24 |  |  | 597 | 13 | 13 | Univent | 8 | 4776 | 4.6357 | 1 | 4.6357 | 2 | 4.6357 | 2
202 | Classroom | 403 | 26 |  |  | 475 | 10 | 10 | Univent | 8 | 3800 | 6.3632 | 1 | 6.3632 | 2 | 6.3632 | 2
203 | Classroom | 444 | 29 |  |  | 772 | 17 | 17 | Univent | 8 | 6176 | 4.3135 | 1 | 4.3135 | 2 | 4.3135 | 2
204 | Classroom | 285 | 19 |  |  | 532 | 12 | 12 | Univent | 8 | 4256 | 4.0179 | 1 | 4.0179 | 2 | 4.0179 | 2
205 | Classroom | 329 | 21 |  |  | 823 | 18 | 18 | Univent | 8 | 6584 | 2.9982 | 1 | 2.9982 | 1 | 2.9982 | 1
206 | Classroom | 438 | 29 |  |  | 480 | 10 | 10 | Univent | 8 | 3840 | 6.8438 | 1 | 6.8438 | 2 | 6.8438 | 2
207 | Classroom | 108 | 7 | Yes | 20 | 648 | 14 | 14 | Univent | 8 | 5184 | 1.25 | 1 | 1.25 | 1 | 21.25 | 3
208 | Classroom | 352 | 23 |  |  | 540 | 12 | 12 | Univent | 8 | 4320 | 4.8889 | 1 | 4.8889 | 2 | 4.8889 | 2
209 | Classroom | 387 | 25 |  |  | 537 | 12 | 12 | Univent | 8 | 4296 | 5.405 | 1 | 5.405 | 2 | 5.405 | 2
300 | Classroom | 161 | 10 |  |  | 789 | 17 | 10 | Univent | 8 | 6312 | 1.5304 | 1 | 1.5304 | 1 | 1.5304 | 1
301 | Classroom | 313 | 20 |  |  | 729 | 16 | 16 | Univent | 8 | 5832 | 3.2202 | 1 | 3.2202 | 1 | 3.2202 | 1
302 | Classroom | 447 | 29 |  |  | 473 | 10 | 10 | Univent | 8 | 3784 | 7.0877 | 1 | 7.0877 | 2 | 7.0877 | 2
303 | Classroom | 137 | 9 | Yes | 20 | 690 | 15 | 15 | Univent | 8 | 5520 | 1.4891 | 1 | 1.4891 | 1 | 21.4891 | 3
304 | Classroom | 324 | 21 |  |  | 667 | 15 | 15 | Univent | 8 | 5336 | 3.6432 | 1 | 3.6432 | 1 | 3.6432 | 1
305 | Classroom | 321 | 21 |  |  | 794 | 18 | 18 | Univent | 8 | 6352 | 3.0321 | 1 | 3.0321 | 1 | 3.0321 | 1
306 | Classroom | 223 | 14 |  |  | 559 | 12 | 12 | Univent | 8 | 4472 | 2.9919 | 1 | 2.9919 | 1 | 2.9919 | 1
307 | Classroom | 171 | 11 |  |  | 790 | 17 | 11 | Univent | 8 | 6320 | 1.6234 | 1 | 1.6234 | 1 | 1.6234 | 1
308 | Classroom | 265 | 17 |  |  | 662 | 15 | 15 | Univent | 8 | 5296 | 3.0023 | 1 | 3.0023 | 1 | 3.0023 | 1
309 | Classroom | 360 | 24 |  |  | 567 | 12 | 12 | Univent | 8 | 4536 | 4.7619 | 1 | 4.7619 | 2 | 4.7619 | 2
311 | Classroom | 0 | 0 | Yes | 20 | 775 | 17 | 17 | Univent | 8 | 6200 | 0 | 1 | 0 | 0 | 20 | 3
312 | Classroom | 397 | 26 |  |  | 573 | 13 | 13 | Univent | 8 | 4584 | 5.1963 | 1 | 5.1963 | 2 | 5.1963 | 2
- | 2nd & 3rd corridors | 251 | 16 |  |  |  | 0 | 0 | Air Handling Unit
- | Administration | 637 | 42 |  |  | 244 | 5 | 5 | Air Handling Unit | 8 | 1952 | 19.5799 | 1 | 19.5799 | 3 | 19.5799 | 3
- | Auditorium | 2708 | 180 |  |  | 3216 | 73 | 73 | Air Handling Unit | 8 | 25728 | 6.3153 | 1.062 | 6.7071 | 2 | 6.7071 | 2
- | Cafeteria | 2800 | 186 |  |  | 3216 | 73 | 73 | Air Handling Unit | 8 | 25728 | 6.5299 | 1.062 | 6.9349 | 2 | 6.9349 | 2
- | Child Care | 1704 | 113 |  |  | 1115 | 25 | 25 | Air Handling Unit | 8 | 8920 | 11.4619 | 1 | 11.4619 | 3 | 11.4619 | 3
- | Conference Office | 98 | 6 |  |  | 236 | 5 | 5 | Air Handling Unit | 8 | 1888 | 3.1144 | 1 | 3.1144 | 1 | 3.1144 | 1
- | Copy Room Office | 44 | 2 |  |  | 178 | 4 | 2 | Air Handling Unit | 8 | 1424 | 1.8539 | 1 | 1.8539 | 1 | 1.8539 | 1
- | Gym | 0 | 0 |  |  | 4403 | 100 | 0 | Air Handling Unit | 8 | 35224 | 0 | 1.062 | 0 | 0 | 0 | 0
- | IMC |  | 0 | Yes | 20 | 1363 | 30 | 30 | Univent | 8 | 10904 | 0 | 1 | 0 | 0 | 20 | 3
- | Kitchen Make Up | 1547 | 103 |  |  | 352 | 8 | 8 | Air Handling Unit | 8 | 2816 | 32.9616 | 1 | 32.9616 | 4 | 32.9616 | 4
- | Main Office | 201 | 13 |  |  | 244 | 5 | 5 | Air Handling Unit | 8 | 1952 | 6.1783 | 1 | 6.1783 | 2 | 6.1783 | 2
- | Mrs. Freeland's Office | 30 | 2 |  |  | 123 | 2 | 2 | Air Handling Unit | 8 | 984 | 1.8293 | 1 | 1.8293 | 1 | 1.8293 | 1
- | Music Room | 1406 | 93 |  |  | 696 | 15 | 15 | Air Handling Unit | 8 | 5568 | 15.1509 | 1 | 15.1509 | 3 | 15.1509 | 3
- | Nurse's Office | 87 | 5 |  |  | 412 | 9 | 5 | Air Handling Unit | 8 | 3296 | 1.5837 | 1 | 1.5837 | 1 | 1.5837 | 1
- | Principal's Office | 65 | 4 |  |  | 270 | 6 | 4 | Air Handling Unit | 8 | 2160 | 1.8056 | 1 | 1.8056 | 1 | 1.8056 | 1
- | Vice Principal's Office | 54 | 3 |  |  | 130 | 2 | 2 | Air Handling Unit | 8 | 1040 | 3.1154 | 1 | 3.1154 | 1 | 3.1154 | 1
Webster LSH
1 | Classroom | 441 | 29 |  |  | 971 | 22 | 22 | Blower Coil Unit | 8 | 7768 | 3.4063 | 1 | 3.4063 | 1 | 3.4063 | 1
2 | Classroom | 189 | 12 | Yes | 20 | 1012 | 23 | 23 | Blower Coil Unit | 8 | 8096 | 1.4007 | 1 | 1.4007 | 1 | 21.4007 | 3
3 | Classroom | 449 | 29 |  |  | 1016 | 23 | 23 | Blower Coil Unit | 8 | 8128 | 3.3145 | 1 | 3.3145 | 1 | 3.3145 | 1
4 | Classroom | 195 | 13 | Yes | 20 | 1017 | 23 | 23 | Blower Coil Unit | 8 | 8136 | 1.4381 | 1 | 1.4381 | 1 | 21.4381 | 3
5 | Classroom |  | 0 | Yes | 20 | 914 | 20 | 20 | Blower Coil Unit | 8 | 7312 | 0 | 1 | 0 | 0 | 20 | 3
6 | Classroom |  | 0 | Yes | 20 | 1040 | 23 | 23 | Blower Coil Unit | 8 | 8320 | 0 | 1 | 0 | 0 | 20 | 3
7 | Classroom |  | 0 | Yes | 20 | 1003 | 22 | 22 | Blower Coil Unit | 8 | 8024 | 0 | 1 | 0 | 0 | 20 | 3
8 | Classroom |  | 0 | Yes | 20 | 1024 | 23 | 23 | Blower Coil Unit | 8 | 8192 | 0 | 1 | 0 | 0 | 20 | 3
9 | Classroom | 162 | 10 | Yes | 20 | 975 | 22 | 22 | Blower Coil Unit | 8 | 7800 | 1.2462 | 1 | 1.2462 | 1 | 21.2462 | 3
10 | Classroom | 164 | 10 | Yes | 20 | 982 | 22 | 22 | Blower Coil Unit | 8 | 7856 | 1.2525 | 1 | 1.2525 | 1 | 21.2525 | 3
11 | Classroom | 188 | 12 | Yes | 20 | 1012 | 23 | 23 | Blower Coil Unit | 8 | 8096 | 1.3933 | 1 | 1.3933 | 1 | 21.3933 | 3
- | Student Toilets | 171 | 11 |  |  | 292 | 6 | 6 | Blower Coil Unit | 8 | 2336 | 4.3921 | 1 | 4.3921 | 2 | 4.3921 | 2
- | Custodial Closet |  | 0 |  |  | 58 | 1 | 0 | Fan Coil Unit | 8 | 464 | 0 | 1 | 0 | 0 | 0 | 0
- | Faculty Room |  | 0 |  |  | 156 | 3 | 0 | Fan Coil Unit | 8 | 1248 | 0 | 1 | 0 | 0 | 0 | 0
- | Multi Purpose Room | 2361 | 157 |  |  | 1714 | 38 | 38 | Blower Coil Unit | 8 | 13712 | 10.3311 | 1 | 10.3311 | 3 | 10.3311 | 3
- | Office Area | 409 | 27 |  |  | 274 | 6 | 6 | Blower Coil Unit | 8 | 2192 | 11.1953 | 1 | 11.1953 | 3 | 11.1953 | 3
- | Staff Toilets |  | 0 |  |  | 58 | 1 | 0 | Blower Coil Unit | 8 | 464 | 0 | 1 | 0 | 0 | 0 | 0
- | Storage & Closet |  | 0 |  |  | 200 | 4 | 0 | Blower Coil Unit | 8 | 1600 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-13
School: | John Welsh Elementary School
Vendor: | Devine Brothers | Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 573 | 38 |  |  | 1122 | 25 | 25 | Univent | 8 | 8976 | 3.8302 | 1 | 3.8302 | 1 | 3.8302 | 1
102 | Classroom | 641 | 42 |  |  | 1030 | 23 | 23 | Univent | 8 | 8240 | 4.6675 | 1 | 4.6675 | 2 | 4.6675 | 2
103 | Classroom | 311 | 20 |  |  | 650 | 14 | 14 | Univent | 8 | 5200 | 3.5885 | 1 | 3.5885 | 1 | 3.5885 | 1
104 | Faculty Lounge | 774 | 51 |  |  | 750 | 17 | 17 | Univent | 8 | 6000 | 7.74 | 1 | 7.74 | 2 | 7.74 | 2
105 | Classroom | 307 | 20 |  |  | 586 | 13 | 13 | Univent | 8 | 4688 | 3.9292 | 1 | 3.9292 | 1 | 3.9292 | 1
106 | Classroom | 674 | 44 |  |  | 760 | 17 | 17 | Univent | 8 | 6080 | 6.6513 | 1 | 6.6513 | 2 | 6.6513 | 2
200 | Classroom | 301 | 20 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 2.7364 | 1 | 2.7364 | 1 | 2.7364 | 1
201 | Classroom | 336 | 22 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 3.0545 | 1 | 3.0545 | 1 | 3.0545 | 1
202 | Classroom | 333 | 22 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 3.0273 | 1 | 3.0273 | 1 | 3.0273 | 1
203 | Classroom | 574 | 38 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 5.2182 | 1 | 5.2182 | 2 | 5.2182 | 2
204 | Classroom | 356 | 23 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 3.2364 | 1 | 3.2364 | 1 | 3.2364 | 1
205 | Classroom | 380 | 25 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 3.4545 | 1 | 3.4545 | 1 | 3.4545 | 1
206 | Classroom | 405 | 27 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 3.6818 | 1 | 3.6818 | 1 | 3.6818 | 1
209 | Classroom | 330 | 22 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 3 | 1 | 3 | 1 | 3 | 1
210 | Library | 642 | 42 |  |  | 1218 | 27 | 27 | Univent | 8 | 9744 | 3.9532 | 1 | 3.9532 | 1 | 3.9532 | 1
211 | Classroom | 320 | 21 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 2.9091 | 1 | 2.9091 | 1 | 2.9091 | 1
212 | Classroom | 610 | 40 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 5.5455 | 1 | 5.5455 | 2 | 5.5455 | 2
300 | Classroom | 858 | 57 |  |  | 830 | 18 | 18 | Univent | 8 | 6640 | 7.753 | 1 | 7.753 | 2 | 7.753 | 2
301A | Classroom | 341 | 22 |  |  | 393 | 8 | 8 | Univent | 8 | 3144 | 6.5076 | 1 | 6.5076 | 2 | 6.5076 | 2
301B | Classroom |  | 0 | Yes | 20 | 393 | 8 | 8 | Univent | 8 | 3144 | 0 | 1 | 0 | 0 | 20 | 3
302 | Classroom | 887 | 59 |  |  | 830 | 18 | 18 | Univent | 8 | 6640 | 8.0151 | 1 | 8.0151 | 2 | 8.0151 | 2
303 | Classroom | 341 | 22 |  |  | 830 | 18 | 18 | Univent | 8 | 6640 | 3.0813 | 1 | 3.0813 | 1 | 3.0813 | 1
304 | Classroom | 790 | 52 |  |  | 830 | 18 | 18 | Univent | 8 | 6640 | 7.1386 | 1 | 7.1386 | 2 | 7.1386 | 2
305 | Classroom | 885 | 59 |  |  | 830 | 18 | 18 | Univent | 8 | 6640 | 7.997 | 1 | 7.997 | 2 | 7.997 | 2
306 | Classroom | 590 | 39 |  |  | 423 | 9 | 9 | Univent | 8 | 3384 | 10.461 | 1 | 10.461 | 3 | 10.461 | 3
308 | Classroom | 420 | 28 |  |  | 411 | 9 | 9 | Univent | 8 | 3288 | 7.6642 | 1 | 7.6642 | 2 | 7.6642 | 2
309 | Classroom | 454 | 30 |  |  | 830 | 18 | 18 | Univent | 8 | 6640 | 4.1024 | 1 | 4.1024 | 2 | 4.1024 | 2
310 | Classroom | 705 | 47 |  |  | 830 | 18 | 18 | Univent | 8 | 6640 | 6.3705 | 1 | 6.3705 | 2 | 6.3705 | 2
311 | Classroom | 890 | 59 |  |  | 830 | 18 | 18 | Univent | 8 | 6640 | 8.0422 | 1 | 8.0422 | 2 | 8.0422 | 2
312 | Classroom | 798 | 53 |  |  | 830 | 18 | 18 | Univent | 8 | 6640 | 7.2108 | 1 | 7.2108 | 2 | 7.2108 | 2
400 | Classroom | 346 | 23 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 3.1455 | 1 | 3.1455 | 1 | 3.1455 | 1
401 | Classroom | 874 | 58 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 7.9455 | 1 | 7.9455 | 2 | 7.9455 | 2
402 | Classroom | 801 | 53 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 7.2818 | 1 | 7.2818 | 2 | 7.2818 | 2
403 | Classroom | 852 | 56 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 7.7455 | 1 | 7.7455 | 2 | 7.7455 | 2
404 | Classroom | 368 | 24 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 3.3455 | 1 | 3.3455 | 1 | 3.3455 | 1
405 | Classroom | 820 | 54 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 7.4545 | 1 | 7.4545 | 2 | 7.4545 | 2
406 | Classroom | 328 | 21 |  |  | 425 | 9 | 9 | Univent | 8 | 3400 | 5.7882 | 1 | 5.7882 | 2 | 5.7882 | 2
408 | Classroom | 426 | 28 |  |  | 410 | 9 | 9 | Univent | 8 | 3280 | 7.7927 | 1 | 7.7927 | 2 | 7.7927 | 2
409 | Classroom | 417 | 27 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 3.7909 | 1 | 3.7909 | 1 | 3.7909 | 1
410 | Classroom | 558 | 37 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 5.0727 | 1 | 5.0727 | 2 | 5.0727 | 2
411 | Classroom | 897 | 59 |  |  | 825 | 18 | 18 | Univent | 8 | 6600 | 8.1545 | 1 | 8.1545 | 2 | 8.1545 | 2
412 | Classroom | 0 | 0 |  |  | 403 | 9 | 0 | Univent | 8 | 3224 | 0 | 1 | 0 | 0 | 0 | 0
412A | Classroom | 820 | 54 |  |  | 403 | 9 | 9 | Univent | 8 | 3224 | 15.2605 | 1 | 15.2605 | 3 | 15.2605 | 3
- | Main Office | 438 | 29 |  |  | 1038 | 23 | 23 | Univent | 8 | 8304 | 3.1647 | 1 | 3.1647 | 1 | 3.1647 | 1
- | Auditorium | 0 | 0 |  |  | 3868 | 87 | 0 | Air Handling Unit | 8 | 30944 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Gym | 4931 | 328 |  |  | 3509 | 79 | 79 | Air Handling Unit | 8 | 28072 | 10.5393 | 1.062 | 11.1931 | 3 | 11.1931 | 3
Sheet Last Modified: | 2021-04-30
School: | New West Philadelphia High School
Vendor: | Chadwick
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
107 | Nurse Office |  | 0 |  |  | 264 | 6 | 0 | Air Handing Unit | 8 | 2112 | 0 | 1 | 0 | 0 | 0 | 0
107A | Nurse Exam Room |  | 0 |  |  | 149 | 3 | 0 | Air Handing Unit | 8 | 1192 | 0 | 1 | 0 | 0 | 0 | 0
107B | Nurse Suite |  | 0 |  |  | 100 | 2 | 0 | Air Handing Unit | 8 | 800 | 0 | 1 | 0 | 0 | 0 | 0
107C | Nurse Suite |  | 0 |  |  | 110 | 2 | 0 | Air Handing Unit | 8 | 880 | 0 | 1 | 0 | 0 | 0 | 0
101C | Maker Room |  | 0 | Yes | 20 | 1268 | 28 | 28 | Air Handing Unit | 8 | 10144 | 0 | 1 | 0 | 0 | 20 | 3
200 | - | 145 | 9 |  |  | 875 | 19 | 9 | Univent | 8 | 7000 | 1.2429 | 1 | 1.2429 | 1 | 1.2429 | 1
201 | Classroom | 190 | 12 |  |  | 539 | 12 | 12 | Univent | 8 | 4312 | 2.6438 | 1 | 2.6438 | 1 | 2.6438 | 1
202 | - | 308 | 20 |  |  | 895 | 20 | 20 | Univent | 8 | 7160 | 2.581 | 1 | 2.581 | 1 | 2.581 | 1
203 | - | 165 | 11 |  |  | 899 | 20 | 11 | Univent | 8 | 7192 | 1.3765 | 1 | 1.3765 | 1 | 1.3765 | 1
204 | - | 398 | 26 |  |  | 900 | 20 | 20 | Univent | 8 | 7200 | 3.3167 | 1 | 3.3167 | 1 | 3.3167 | 1
205 | - | 105 | 7 |  |  | 877 | 19 | 7 | Univent | 8 | 7016 | 0.89795 | 1 | 0.89795 | 0 | 0.89795 | 0
206 | - | 344 | 22 |  |  | 898 | 20 | 20 | Univent | 8 | 7184 | 2.8731 | 1 | 2.8731 | 1 | 2.8731 | 1
207 | - | 315 | 21 |  |  | 877 | 19 | 19 | Univent | 8 | 7016 | 2.6938 | 1 | 2.6938 | 1 | 2.6938 | 1
208 | - | 281 | 18 |  |  | 937 | 21 | 18 | Univent | 8 | 7496 | 2.2492 | 1 | 2.2492 | 1 | 2.2492 | 1
216 | - | 176 | 11 |  |  | 1330 | 30 | 11 | Univent | 8 | 10640 | 0.99248 | 1 | 0.99248 | 0 | 0.99248 | 0
300 | - | 210 | 14 |  |  | 878 | 19 | 14 | Univent | 8 | 7024 | 1.7938 | 1 | 1.7938 | 1 | 1.7938 | 1
301 | - | 0 | 0 |  |  | 544 | 12 | 0 | Univent | 8 | 4352 | 0 | 1 | 0 | 0 | 0 | 0
302 | - | 470 | 31 |  |  | 898 | 20 | 20 | Univent | 8 | 7184 | 3.9254 | 1 | 3.9254 | 1 | 3.9254 | 1
303 | - | 205 | 13 |  |  | 900 | 20 | 13 | Univent | 8 | 7200 | 1.7083 | 1 | 1.7083 | 1 | 1.7083 | 1
304 | - | 235 | 15 |  |  | 900 | 20 | 15 | Univent | 8 | 7200 | 1.9583 | 1 | 1.9583 | 1 | 1.9583 | 1
305 | - |  | 0 |  |  | 874 | 19 | 0 | Univent | 8 | 6992 | 0 | 1 | 0 | 0 | 0 | 0
306 | - | 190 | 12 |  |  | 896 | 20 | 12 | Univent | 8 | 7168 | 1.5904 | 1 | 1.5904 | 1 | 1.5904 | 1
307 | Classroom |  | 0 | Yes | 20 | 1387 | 31 | 31 | Univent | 8 | 11096 | 0 | 1 | 0 | 0 | 20 | 3
308 | - | 230 | 15 |  |  | 897 | 20 | 15 | Univent | 8 | 7176 | 1.9231 | 1 | 1.9231 | 1 | 1.9231 | 1
309 | Classroom |  | 0 | Yes | 20 | 1357 | 30 | 30 | Univent | 8 | 10856 | 0 | 1 | 0 | 0 | 20 | 3
310 | - | 115 | 7 |  |  | 898 | 20 | 7 | Univent | 8 | 7184 | 0.96047 | 1 | 0.96047 | 0 | 0.96047 | 0
311 | - |  | 0 |  |  | 900 | 20 | 0 | Univent | 8 | 7200 | 0 | 1 | 0 | 0 | 0 | 0
312 | - | 625 | 41 |  |  | 872 | 19 | 19 | Univent | 8 | 6976 | 5.3756 | 1 | 5.3756 | 2 | 5.3756 | 2
313 | - |  | 0 |  |  | 877 | 19 | 0 | Univent | 8 | 7016 | 0 | 1 | 0 | 0 | 0 | 0
315 | - | 425 | 28 |  |  | 876 | 19 | 19 | Univent | 8 | 7008 | 3.6387 | 1 | 3.6387 | 1 | 3.6387 | 1
316 | - | 190 | 12 |  |  | 399 | 9 | 9 | Univent | 8 | 3192 | 3.5714 | 1 | 3.5714 | 1 | 3.5714 | 1
317 | - | 205 | 13 |  |  | 902 | 20 | 13 | Univent | 8 | 7216 | 1.7045 | 1 | 1.7045 | 1 | 1.7045 | 1
318 | - | 365 | 24 |  |  | 1274 | 28 | 24 | Univent | 8 | 10192 | 2.1487 | 1 | 2.1487 | 1 | 2.1487 | 1
319 | - | 195 | 13 |  |  | 899 | 20 | 13 | Univent | 8 | 7192 | 1.6268 | 1 | 1.6268 | 1 | 1.6268 | 1
320 | - |  | 0 |  |  | 876 | 19 | 0 | Univent | 8 | 7008 | 0 | 1 | 0 | 0 | 0 | 0
321 | - | 425 | 28 |  |  | 894 | 20 | 20 | Univent | 8 | 7152 | 3.5654 | 1 | 3.5654 | 1 | 3.5654 | 1
Gymnasium | Gymnasium | 0 | 0 |  |  | 6370 | 144 | 0 | Univent | 8 | 50960 | 0 | 1.4912 | 0 | 0 | 0 | 0
Gymnasium | Gymnasium | 0 | 0 | Yes | 20 | 10648 | 242 | 242 | Univent | 8 | 85184 | 0 | 1.4912 | 0 | 0 | 20 | 3
Sheet Last Modified: | 2021-04-13
School: | Widener Memorial Elementary School
Vendor: | EMCOR
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
2 | - | 1283 | 85 |  |  | 2800 | 63 | 63 | Carrier / Perimeter Heater | 8 | 22400 | 3.4366 | 1.062 | 3.6498 | 1 | 3.6498 | 1
3 | - | 500 | 33 |  |  | 1344 | 30 | 30 | Carrier / Perimeter Heater | 8 | 10752 | 2.7902 | 1 | 2.7902 | 1 | 2.7902 | 1
4 | - | 70 | 4 |  |  | 1332 | 30 | 4 | Carrier / Perimeter Heater | 8 | 10656 | 0.39414 | 1 | 0.39414 | 0 | 0.39414 | 0
5 | - | 146 | 9 |  |  | 527 | 11 | 9 | Carrier / Perimeter Heater | 8 | 4216 | 2.0778 | 1 | 2.0778 | 1 | 2.0778 | 1
6 | - | 38 | 2 |  |  | 744 | 16 | 2 | Carrier / Perimeter Heater | 8 | 5952 | 0.38306 | 1 | 0.38306 | 0 | 0.38306 | 0
7 | - | 70 | 4 |  |  | 912 | 20 | 4 | Carrier / Perimeter Heater | 8 | 7296 | 0.57566 | 1 | 0.57566 | 0 | 0.57566 | 0
8 | - | 317 | 21 |  |  | 460 | 10 | 10 | Carrier / Perimeter Heater | 8 | 3680 | 5.1685 | 1 | 5.1685 | 2 | 5.1685 | 2
9 | - | 311 | 20 |  |  | 480 | 10 | 10 | Carrier / Perimeter Heater | 8 | 3840 | 4.8594 | 1 | 4.8594 | 2 | 4.8594 | 2
10 | - | 291 | 19 |  |  | 504 | 11 | 11 | Carrier / Perimeter Heater | 8 | 4032 | 4.3304 | 1 | 4.3304 | 2 | 4.3304 | 2
11 | - | 290 | 19 |  |  | 504 | 11 | 11 | Carrier / Perimeter Heater | 8 | 4032 | 4.3155 | 1 | 4.3155 | 2 | 4.3155 | 2
12 | - | 292 | 19 |  |  | 744 | 16 | 16 | Carrier / Perimeter Heater | 8 | 5952 | 2.9435 | 1 | 2.9435 | 1 | 2.9435 | 1
13 | - | 210 | 14 |  |  | 759.5 | 17 | 14 | Carrier / Perimeter Heater | 8 | 6076 | 2.0737 | 1 | 2.0737 | 1 | 2.0737 | 1
14 | - | 244 | 16 |  |  | 759.5 | 17 | 16 | Carrier / Perimeter Heater | 8 | 6076 | 2.4095 | 1 | 2.4095 | 1 | 2.4095 | 1
15 | - | 224 | 14 |  |  | 759.5 | 17 | 14 | Carrier / Perimeter Heater | 8 | 6076 | 2.212 | 1 | 2.212 | 1 | 2.212 | 1
16 | - | 225 | 15 |  |  | 759.5 | 17 | 15 | Carrier / Perimeter Heater | 8 | 6076 | 2.2219 | 1 | 2.2219 | 1 | 2.2219 | 1
17 | - | 260 | 17 |  |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6076 | 2.5675 | 1 | 2.5675 | 1 | 2.5675 | 1
18 | - | 304 | 20 |  |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6076 | 3.002 | 1 | 3.002 | 1 | 3.002 | 1
19 | - | 0 | 0 | Yes | 20 | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6076 | 0 | 1 | 0 | 0 | 20 | 3
20 | - | 356 | 23 |  |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6076 | 3.5155 | 1 | 3.5155 | 1 | 3.5155 | 1
21 | - | 271 | 18 |  |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6076 | 2.6761 | 1 | 2.6761 | 1 | 2.6761 | 1
22 | - | 282 | 18 |  |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6076 | 2.7847 | 1 | 2.7847 | 1 | 2.7847 | 1
23 | - | 275 | 18 |  |  | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6076 | 2.7156 | 1 | 2.7156 | 1 | 2.7156 | 1
24 | - | 0 | 0 | Yes | 20 | 759.5 | 17 | 17 | Carrier / Perimeter Heater | 8 | 6076 | 0 | 1 | 0 | 0 | 20 | 3
25 | - | 192 | 12 |  |  | 1014 | 23 | 12 | Carrier / Perimeter Heater | 8 | 8112 | 1.4201 | 1 | 1.4201 | 1 | 1.4201 | 1
26 | - | 2008 | 133 |  |  | 891 | 20 | 20 | Air Handling Unit | 8 | 7128 | 16.9024 | 1 | 16.9024 | 3 | 16.9024 | 3
27 | - | 416 | 27 |  |  | 619.5 | 14 | 14 | Air Handling Unit | 8 | 4956 | 5.0363 | 1 | 5.0363 | 2 | 5.0363 | 2
28 | - | 416 | 27 |  |  | 925 | 21 | 21 | Air Handling Unit | 8 | 7400 | 3.373 | 1 | 3.373 | 1 | 3.373 | 1
31A | - | 0 | 0 | Yes | 20 | 190 | 4 | 4 | Carrier / Perimeter Heater | 8 | 1520 | 0 | 1 | 0 | 0 | 20 | 3
31B | Nurse's Office | 0 | 0 | Yes | 20 | 196 | 4 | 4 | Carrier / Perimeter Heater | 8 | 1568 | 0 | 1 | 0 | 0 | 20 | 3
32 | - | 0 | 0 |  |  | 272 | 6 | 0 | Carrier / Perimeter Heater | 8 | 2176 | 0 | 1 | 0 | 0 | 0 | 0
33 | - | 396 | 26 |  |  | 1271 | 28 | 26 | Carrier / Perimeter Heater | 8 | 10168 | 2.3367 | 1 | 2.3367 | 1 | 2.3367 | 1
34 | - | 622 | 41 |  |  | 1470 | 33 | 33 | Carrier / Perimeter Heater | 8 | 11760 | 3.1735 | 1 | 3.1735 | 1 | 3.1735 | 1
35A | - | 265 | 17 |  |  | 720 | 16 | 16 | Carrier / Perimeter Heater | 8 | 5760 | 2.7604 | 1 | 2.7604 | 1 | 2.7604 | 1
35B | - | 222 | 14 |  |  | 1107 | 25 | 14 | Carrier / Perimeter Heater | 8 | 8856 | 1.5041 | 1 | 1.5041 | 1 | 1.5041 | 1
35C | - | 0 | 0 | Yes | 20 | 364 | 8 | 8 | Carrier / Perimeter Heater | 8 | 2912 | 0 | 1 | 0 | 0 | 20 | 3
36 | - | 0 | 0 |  |  | 1288 | 29 | 0 | Carrier / Perimeter Heater | 8 | 10304 | 0 | 1 | 0 | 0 | 0 | 0
37 | - | 235 | 15 |  |  | 600 | 13 | 13 | Carrier / Perimeter Heater | 8 | 4800 | 2.9375 | 1 | 2.9375 | 1 | 2.9375 | 1
38 | - | 257 | 17 |  |  | 600 | 13 | 13 | Carrier / Perimeter Heater | 8 | 4800 | 3.2125 | 1 | 3.2125 | 1 | 3.2125 | 1
39 | - | 88 | 5 |  |  | 462 | 10 | 5 | Carrier / Perimeter Heater | 8 | 3696 | 1.4286 | 1 | 1.4286 | 1 | 1.4286 | 1
40 | - | 115 | 7 |  |  | 472 | 10 | 7 | Carrier / Perimeter Heater | 8 | 3776 | 1.8273 | 1 | 1.8273 | 1 | 1.8273 | 1
41 | - | 235 | 15 |  |  | 702 | 15 | 15 | Carrier / Perimeter Heater | 8 | 5616 | 2.5107 | 1 | 2.5107 | 1 | 2.5107 | 1
46 | Small Cafeteria | 182 | 12 |  |  | 1347 | 30 | 12 | Carrier / Perimeter Heater | 8 | 10776 | 1.0134 | 1 | 1.0134 | 1 | 1.0134 | 1
47 | - | 75 | 5 | Yes | 20 | 315 | 7 | 7 | Carrier / Perimeter Heater | 8 | 2520 | 1.7857 | 1 | 1.7857 | 1 | 21.7857 | 3
48 | - | 90 | 6 |  |  | 817 | 18 | 6 | Carrier / Perimeter Heater | 8 | 6536 | 0.82619 | 1 | 0.82619 | 0 | 0.82619 | 0
103 | - | 290 | 19 |  |  | 840 | 19 | 19 | Carrier / Perimeter Heater | 8 | 6720 | 2.5893 | 1 | 2.5893 | 1 | 2.5893 | 1
104 | - | 310 | 20 |  |  | 840 | 19 | 19 | Carrier / Perimeter Heater | 8 | 6720 | 2.7679 | 1 | 2.7679 | 1 | 2.7679 | 1
105 | - | 410 | 27 |  |  | 810 | 18 | 18 | Carrier / Perimeter Heater | 8 | 6480 | 3.7963 | 1 | 3.7963 | 1 | 3.7963 | 1
106 | - | 300 | 20 |  |  | 868 | 19 | 19 | Carrier / Perimeter Heater | 8 | 6944 | 2.5922 | 1 | 2.5922 | 1 | 2.5922 | 1
107 | - | 530 | 35 |  |  | 850 | 19 | 19 | Carrier / Perimeter Heater | 8 | 6800 | 4.6765 | 1 | 4.6765 | 2 | 4.6765 | 2
108 | - | 489 | 32 |  |  | 840 | 19 | 19 | Carrier / Perimeter Heater | 8 | 6720 | 4.3661 | 1 | 4.3661 | 2 | 4.3661 | 2
109 | - | 40 | 2 | Yes | 20 | 840 | 19 | 19 | Carrier / Perimeter Heater | 8 | 6720 | 0.35714 | 1 | 0.35714 | 0 | 20.3571 | 3
110 | - | 550 | 36 |  |  | 840 | 19 | 19 | Carrier / Perimeter Heater | 8 | 6720 | 4.9107 | 1 | 4.9107 | 2 | 4.9107 | 2
101 | - | 430 | 28 |  |  | 1271 | 28 | 28 | Carrier / Perimeter Heater | 8 | 10168 | 2.5374 | 1 | 2.5374 | 1 | 2.5374 | 1
102A | - | 124 | 8 |  |  | 140 | 3 | 3 | Carrier / Perimeter Heater | 8 | 1120 | 6.6429 | 1 | 6.6429 | 2 | 6.6429 | 2
102B | - | 165 | 11 |  |  | 140 | 3 | 3 | Carrier / Perimeter Heater | 8 | 1120 | 8.8393 | 1 | 8.8393 | 2 | 8.8393 | 2
111A | - | 98 | 6 |  |  | 140 | 3 | 3 | Carrier / Perimeter Heater | 8 | 1120 | 5.25 | 1 | 5.25 | 2 | 5.25 | 2
111B | - | 110 | 7 |  |  | 140 | 3 | 3 | Carrier / Perimeter Heater | 8 | 1120 | 5.8929 | 1 | 5.8929 | 2 | 5.8929 | 2
112 | - | 905 | 60 |  |  | 1271 | 28 | 28 | Carrier / Perimeter Heater | 8 | 10168 | 5.3403 | 1 | 5.3403 | 2 | 5.3403 | 2
- | Auditorium | 1042 | 69 |  |  | 4087 | 92 | 69 | Air Handling Unit | 8 | 32696 | 1.9122 | 1.062 | 2.0308 | 1 | 2.0308 | 1
- | Cafeteria | 918 | 61 |  |  | 2720 | 61 | 61 | Carrier / Perimeter Heater | 8 | 21760 | 2.5312 | 1.062 | 2.6883 | 1 | 2.6883 | 1
- | Computer Lab | 320 | 21 | Yes | 20 | 943 | 21 | 21 | Air Handling Unit | 8 | 7544 | 2.5451 | 1 | 2.5451 | 1 | 22.5451 | 3
- | Food Service "A & B" | 0 | 0 |  |  | 1320 | 30 | 0 | Carrier / Perimeter Heater | 8 | 10560 | 0 | 1 | 0 | 0 | 0 | 0
- | Game Room | 577 | 38 |  |  | 675 | 15 | 15 | Carrier / Perimeter Heater | 8 | 5400 | 6.4111 | 1 | 6.4111 | 2 | 6.4111 | 2
- | GYM | 174 | 11 |  |  | 3721 | 84 | 11 | Air Handling Unit | 8 | 29768 | 0.35071 | 1.062 | 0.37247 | 0 | 0.37247 | 0
- | Kitchen | 3011 | 200 |  |  | 1191 | 27 | 27 | Make-Up Air Unit | 8 | 9528 | 18.961 | 1 | 18.961 | 3 | 18.961 | 3
- | Music Room | 2765 | 184 |  |  | 2040 | 46 | 46 | Air Handling Unit | 8 | 16320 | 10.1654 | 1 | 10.1654 | 3 | 10.1654 | 3
- | Pool | 0 | 0 |  |  | 7467 | 169 | 0 | Air Handling Unit | 8 | 59736 | 0 | 1.4912 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30
School: | Frances E. Willard Elementary School
Vendor: | Devine | Main Building Retest
School: | Willard Annex
Vendor: | EMCOR Fluidics | EMCOR Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
Willard Main Building
100A | OFFICE | 39 | 2 |  |  | 181 | 4 | 2 | Air Handling Unit | 8 | 1448 | 1.616 | 1 | 1.616 | 1 | 1.616 | 1
100B | OFFICE | 31 | 2 |  |  | 121 | 2 | 2 | Air Handling Unit | 8 | 968 | 1.9215 | 1 | 1.9215 | 1 | 1.9215 | 1
100C | OFFICE | 39 | 2 |  |  | 43 | 0 | 0 | Air Handling Unit | 8 | 344 | 6.8023 | 1 | 6.8023 | 2 | 6.8023 | 2
100D | OFFICE | 37 | 2 |  |  | 121 | 2 | 2 | Air Handling Unit | 8 | 968 | 2.2934 | 1 | 2.2934 | 1 | 2.2934 | 1
100E | OFFICE | 35 | 2 |  |  | 120 | 2 | 2 | Air Handling Unit | 8 | 960 | 2.1875 | 1 | 2.1875 | 1 | 2.1875 | 1
100F | OFFICE | 51 | 3 |  |  | 345 | 7 | 3 | Air Handling Unit | 8 | 2760 | 1.1087 | 1 | 1.1087 | 1 | 1.1087 | 1
100G | Conference | 85 | 5 |  |  | 279 | 6 | 5 | Air Handling Unit | 8 | 2232 | 2.2849 | 1 | 2.2849 | 1 | 2.2849 | 1
100H | BREAK ROOM | 70 | 4 |  |  | 145 | 3 | 3 | Air Handling Unit | 8 | 1160 | 3.6207 | 1 | 3.6207 | 1 | 3.6207 | 1
100I | OFFICE | 76 | 5 |  |  | 210 | 4 | 4 | Air Handling Unit | 8 | 1680 | 2.7143 | 1 | 2.7143 | 1 | 2.7143 | 1
101 | Classroom | 310 | 20 |  |  | 984 | 22 | 20 | Univent and Air Handling Unit | 8 | 7872 | 2.3628 | 1 | 2.3628 | 1 | 2.3628 | 1
102 | Classroom | 304 | 20 |  |  | 1059 | 24 | 20 | Univent and Air Handling Unit | 8 | 8472 | 2.153 | 1 | 2.153 | 1 | 2.153 | 1
103 | Classroom | 321 | 21 |  |  | 889 | 20 | 20 | Univent and Air Handling Unit | 8 | 7112 | 2.7081 | 1 | 2.7081 | 1 | 2.7081 | 1
104 | Classroom | 282 | 18 |  |  | 1086 | 24 | 18 | Univent and Air Handling Unit | 8 | 8688 | 1.9475 | 1 | 1.9475 | 1 | 1.9475 | 1
105 | Classroom | 295 | 19 |  |  | 677 | 15 | 15 | Univent and Air Handling Unit | 8 | 5416 | 3.2681 | 1 | 3.2681 | 1 | 3.2681 | 1
106 | Classroom | 331 | 22 |  |  | 800 | 18 | 18 | Univent and Air Handling Unit | 8 | 6400 | 3.1031 | 1 | 3.1031 | 1 | 3.1031 | 1
107 | Nurse OFFICE | 35 | 2 |  |  | 277 | 6 | 2 | Fan Coil | 8 | 2216 | 0.94765 | 1 | 0.94765 | 0 | 0.94765 | 0
107A | OFFICE | 45 | 3 |  |  | 161 | 3 | 3 | Fan Coil | 8 | 1288 | 2.0963 | 1 | 2.0963 | 1 | 2.0963 | 1
107C | OFFICE | 14 | 0 |  |  | 150 | 3 | 0 | Air Handling Unit | 8 | 1200 | 0.7 | 1 | 0.7 | 0 | 0.7 | 0
107D | OFFICE | 26 | 1 |  |  | 103 | 2 | 1 | Air Handling Unit | 8 | 824 | 1.8932 | 1 | 1.8932 | 1 | 1.8932 | 1
107G | COMPUTER LAB | 298 | 19 |  |  | 1033 | 23 | 19 | Univent | 8 | 8264 | 2.1636 | 1 | 2.1636 | 1 | 2.1636 | 1
109 | Classroom | 282 | 18 |  |  | 802 | 18 | 18 | Univent and Air Handling Unit | 8 | 6416 | 2.6372 | 1 | 2.6372 | 1 | 2.6372 | 1
110 | Classroom | 282 | 18 |  |  | 818 | 18 | 18 | Univent and Air Handling Unit | 8 | 6544 | 2.5856 | 1 | 2.5856 | 1 | 2.5856 | 1
111 | Classroom | 295 | 19 |  |  | 818 | 18 | 18 | Univent and Air Handling Unit | 8 | 6544 | 2.7048 | 1 | 2.7048 | 1 | 2.7048 | 1
112 | Classroom | 306 | 20 |  |  | 813 | 18 | 18 | Univent and Air Handling Unit | 8 | 6504 | 2.8229 | 1 | 2.8229 | 1 | 2.8229 | 1
113 | Classroom | 305 | 20 |  |  | 813 | 18 | 18 | Univent and Air Handling Unit | 8 | 6504 | 2.8137 | 1 | 2.8137 | 1 | 2.8137 | 1
114 | Classroom | 280 | 18 |  |  | 815 | 18 | 18 | Univent and Air Handling Unit | 8 | 6520 | 2.5767 | 1 | 2.5767 | 1 | 2.5767 | 1
115 | Classroom | 293 | 19 |  |  | 815 | 18 | 18 | Univent and Air Handling Unit | 8 | 6520 | 2.6963 | 1 | 2.6963 | 1 | 2.6963 | 1
116 | Classroom | 302 | 20 |  |  | 813 | 18 | 18 | Univent and Air Handling Unit | 8 | 6504 | 2.786 | 1 | 2.786 | 1 | 2.786 | 1
117 | Classroom | 295 | 19 |  |  | 813 | 18 | 18 | Univent and Air Handling Unit | 8 | 6504 | 2.7214 | 1 | 2.7214 | 1 | 2.7214 | 1
121 | Classroom | 381 | 25 |  |  | 1059 | 24 | 24 | Univent and Air Handling Unit | 8 | 8472 | 2.6983 | 1 | 2.6983 | 1 | 2.6983 | 1
122 | Music Room | 328 | 21 |  |  | 1189 | 27 | 21 | Univent | 8 | 9512 | 2.069 | 1 | 2.069 | 1 | 2.069 | 1
123 | Classroom | 392 | 26 |  |  | 1061 | 24 | 24 | Univent and Air Handling Unit | 8 | 8488 | 2.771 | 1 | 2.771 | 1 | 2.771 | 1
126 | Staff Lounge | 397 | 26 |  |  | 419 | 9 | 9 | Univent and Air Handling Unit | 8 | 3352 | 7.1062 | 1 | 7.1062 | 2 | 7.1062 | 2
128 | Workroom | 154 | 10 |  |  | 285 | 6 | 6 | Air Handling Unit | 8 | 2280 | 4.0526 | 1 | 4.0526 | 2 | 4.0526 | 2
132 | BE Office | 78 | 5 |  |  | 135 | 3 | 3 | Air Handling Unit | 8 | 1080 | 4.3333 | 1 | 4.3333 | 2 | 4.3333 | 2
200E | IMC | 60 | 4 |  |  | 80 | 1 | 1 | Air Handling Unit | 8 | 640 | 5.625 | 1 | 5.625 | 2 | 5.625 | 2
200F | CONF ROOM | 325 | 21 |  |  | 352 | 8 | 8 | Univent | 8 | 2816 | 6.9247 | 1 | 6.9247 | 2 | 6.9247 | 2
201 | Classsroom | 425 | 28 |  |  | 814 | 18 | 18 | Univent and Air Handling Unit | 8 | 6512 | 3.9158 | 1 | 3.9158 | 1 | 3.9158 | 1
202 | Classsroom | 530 | 35 |  |  | 814 | 18 | 18 | Univent and Air Handling Unit | 8 | 6512 | 4.8833 | 1 | 4.8833 | 2 | 4.8833 | 2
203 | Classsroom | 394 | 26 |  |  | 814 | 18 | 18 | Univent and Air Handling Unit | 8 | 6512 | 3.6302 | 1 | 3.6302 | 1 | 3.6302 | 1
204 | Classsroom | 517 | 34 |  |  | 814 | 18 | 18 | Univent and Air Handling Unit | 8 | 6512 | 4.7635 | 1 | 4.7635 | 2 | 4.7635 | 2
205 | Classsroom | 432 | 28 |  |  | 810 | 18 | 18 | Univent and Air Handling Unit | 8 | 6480 | 4 | 1 | 4 | 1 | 4 | 1
206 | Classsroom | 407 | 27 |  |  | 812 | 18 | 18 | Univent and Air Handling Unit | 8 | 6496 | 3.7592 | 1 | 3.7592 | 1 | 3.7592 | 1
207 | Classsroom | 368 | 24 |  |  | 685 | 15 | 15 | Univent and Air Handling Unit | 8 | 5480 | 4.0292 | 1 | 4.0292 | 2 | 4.0292 | 2
208 | ART | 479 | 31 |  |  | 1059 | 24 | 24 | Univent | 8 | 8472 | 3.3924 | 1 | 3.3924 | 1 | 3.3924 | 1
209 | Classsroom | 379 | 25 |  |  | 807 | 18 | 18 | Univent and Air Handling Unit | 8 | 6456 | 3.5223 | 1 | 3.5223 | 1 | 3.5223 | 1
210 | Classsroom | 382 | 25 |  |  | 820 | 18 | 18 | Univent and Air Handling Unit | 8 | 6560 | 3.4939 | 1 | 3.4939 | 1 | 3.4939 | 1
211 | Classsroom | 389 | 25 |  |  | 821 | 18 | 18 | Univent and Air Handling Unit | 8 | 6568 | 3.5536 | 1 | 3.5536 | 1 | 3.5536 | 1
212 | Classsroom | 375 | 25 |  |  | 814 | 18 | 18 | Univent and Air Handling Unit | 8 | 6512 | 3.4552 | 1 | 3.4552 | 1 | 3.4552 | 1
213 | Classsroom | 392 | 26 |  |  | 814 | 18 | 18 | Univent and Air Handling Unit | 8 | 6512 | 3.6118 | 1 | 3.6118 | 1 | 3.6118 | 1
214 | Classsroom | 382 | 25 |  |  | 811 | 18 | 18 | Univent and Air Handling Unit | 8 | 6488 | 3.5327 | 1 | 3.5327 | 1 | 3.5327 | 1
215 | Classsroom | 420 | 28 |  |  | 811 | 18 | 18 | Univent and Air Handling Unit | 8 | 6488 | 3.8841 | 1 | 3.8841 | 1 | 3.8841 | 1
216 | Classsroom | 301 | 20 |  |  | 811 | 18 | 18 | Univent and Air Handling Unit | 8 | 6488 | 2.7836 | 1 | 2.7836 | 1 | 2.7836 | 1
217 | Classsroom | 411 | 27 |  |  | 811 | 18 | 18 | Univent and Air Handling Unit | 8 | 6488 | 3.8009 | 1 | 3.8009 | 1 | 3.8009 | 1
221 | Classroom | 301 | 20 |  |  | 658 | 14 | 14 | Univent | 8 | 5264 | 3.4309 | 1 | 3.4309 | 1 | 3.4309 | 1
223 | Classroom | 357 | 23 |  |  | 887 | 20 | 20 | Univent and Air Handling Unit | 8 | 7096 | 3.0186 | 1 | 3.0186 | 1 | 3.0186 | 1
224 | Classroom | 585 | 39 |  |  | 1410 | 32 | 32 | Univent and Air Handling Unit | 8 | 11280 | 3.1117 | 1 | 3.1117 | 1 | 3.1117 | 1
225 | Classroom | 175 | 11 |  |  | 1267 | 28 | 11 | Univent and Air Handling Unit | 8 | 10136 | 1.0359 | 1 | 1.0359 | 1 | 1.0359 | 1
- | Auditorium | 3411 | 227 |  |  | 2755 | 62 | 62 | Air Handling Unit | 8 | 22040 | 9.2858 | 1.062 | 9.8619 | 2 | 9.8619 | 2
- | Cafeteria | 2559 | 170 |  |  | 5041 | 114 | 114 | Air Handling Unit | 8 | 40328 | 3.8073 | 1.062 | 4.0435 | 2 | 4.0435 | 2
- | Gym | 2627 | 175 |  |  | 5960 | 135 | 135 | Air Handling Unit | 8 | 47680 | 3.3058 | 1.062 | 3.5109 | 1 | 3.5109 | 1
- | LIBRARY | 514 | 34 |  |  | 2639 | 59 | 34 | Air Handling Unit | 8 | 21112 | 1.4608 | 1.062 | 1.5514 | 1 | 1.5514 | 1
- | Lobby | 1166 | 77 |  |  | 3402 | 77 | 77 | Air Handling Unit | 8 | 27216 | 2.5705 | 1.062 | 2.73 | 1 | 2.73 | 1
- | Main Office | 236 | 15 |  |  | 1165 | 26 | 15 | Air Handling Unit | 8 | 9320 | 1.5193 | 1 | 1.5193 | 1 | 1.5193 | 1
Willard Annex
#1 | Classroom | 334 | 22 |  |  | 828 | 18 | 18 | Rooftop Unit | 8 | 6624 | 3.0254 | 1 | 3.0254 | 1 | 3.0254 | 1
#2 | Classroom | 534 | 35 |  |  | 828 | 18 | 18 | Rooftop Unit | 8 | 6624 | 4.837 | 1 | 4.837 | 2 | 4.837 | 2
#3 | Classroom | 667 | 44 |  |  | 828 | 18 | 18 | Rooftop Unit | 8 | 6624 | 6.0417 | 1 | 6.0417 | 2 | 6.0417 | 2
#4 | Classroom | 595 | 39 |  |  | 828 | 18 | 18 | Rooftop Unit | 8 | 6624 | 5.3895 | 1 | 5.3895 | 2 | 5.3895 | 2
#5 | Classroom | 453 | 30 |  |  | 828 | 18 | 18 | Rooftop Unit | 8 | 6624 | 4.1033 | 1 | 4.1033 | 2 | 4.1033 | 2
#6 | Classroom | 1118 | 74 |  |  | 828 | 18 | 18 | Rooftop Unit | 8 | 6624 | 10.1268 | 1 | 10.1268 | 3 | 10.1268 | 3
- | Admin Desk/Office | 402 | 26 |  |  | 180 | 4 | 4 | Rooftop Unit | 8 | 1440 | 16.75 | 1 | 16.75 | 3 | 16.75 | 3
- | Entrance Hallway | 93 | 6 |  |  | N/A | 0 | 0 | Rooftop Unit
- | Kitchen | 123 | 8 |  |  | 180 | 4 | 4 | Rooftop Unit | 8 | 1440 | 5.125 | 1 | 5.125 | 2 | 5.125 | 2
- | Office Space | 29 | 1 |  |  | 200 | 4 | 1 | Rooftop Unit | 8 | 1600 | 1.0875 | 1 | 1.0875 | 1 | 1.0875 | 1
- | Play Area | 2452 | 163 |  |  | 1228 | 27 | 27 | Rooftop Unit | 8 | 9824 | 14.9756 | 1 | 14.9756 | 3 | 14.9756 | 3
- | Principals Office | 257 | 17 |  |  | 120 | 2 | 2 | Rooftop Unit | 8 | 960 | 16.0625 | 1 | 16.0625 | 3 | 16.0625 | 3
- | BE Office | 362 | 24 |  |  | 195 | 4 | 4 | Rooftop Unit | 8 | 1560 | 13.9231 | 1 | 13.9231 | 3 | 13.9231 | 3
- | Health/Teachers Lounge | 0 | 0 |  |  | 240 | 5 | 0 | Univent | 8 | 1920 | 0 | 1 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-04-30
School: | Woodrow Wilson Middle School
Vendor: | Capital
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Classroom | 693 | 46 |  |  | 1080 | 24 | 24 | Air Handling Unit | 8 | 8640 | 4.8125 | 1 | 4.8125 | 2 | 4.8125 | 2
102 | Classroom | 429 | 28 |  |  | 853 | 19 | 19 | Air Handling Unit | 8 | 6824 | 3.772 | 1 | 3.772 | 1 | 3.772 | 1
103 | Classroom | 962 | 64 |  |  | 672 | 15 | 15 | Air Handling Unit | 8 | 5376 | 10.7366 | 1 | 10.7366 | 3 | 10.7366 | 3
104 | Room |  | 0 |  |  | 616 | 14 | 0 | Air Handling Unit | 8 | 4928 | 0 | 1 | 0 | 0 | 0 | 0
105 | Classroom | 540 | 36 |  |  | 1038 | 23 | 23 | Air Handling Unit | 8 | 8304 | 3.9017 | 1 | 3.9017 | 1 | 3.9017 | 1
107 | Classroom | 882 | 58 |  |  | 968 | 22 | 22 | Air Handling Unit | 8 | 7744 | 6.8337 | 1 | 6.8337 | 2 | 6.8337 | 2
108 | Room |  | 0 |  |  | 352 | 8 | 0 | Air Handling Unit | 8 | 2816 | 0 | 1 | 0 | 0 | 0 | 0
109 | Classroom | 506 | 33 |  |  | 374 | 8 | 8 | Air Handling Unit | 8 | 2992 | 10.1471 | 1 | 10.1471 | 3 | 10.1471 | 3
110 | Room |  | 0 |  |  | 660 | 15 | 0 | Air Handling Unit | 8 | 5280 | 0 | 1 | 0 | 0 | 0 | 0
111 | Classroom | 277 | 18 |  |  | 812 | 18 | 18 | Air Handling Unit | 8 | 6496 | 2.5585 | 1 | 2.5585 | 1 | 2.5585 | 1
112 | Classroom | 271 | 18 |  |  | 954 | 21 | 18 | Air Handling Unit | 8 | 7632 | 2.1305 | 1 | 2.1305 | 1 | 2.1305 | 1
116 | Classroom | 143 | 9 |  |  | 697 | 15 | 9 | Air Handling Unit | 8 | 5576 | 1.5387 | 1 | 1.5387 | 1 | 1.5387 | 1
117 | Classroom | 191 | 12 |  |  | 697 | 15 | 12 | Air Handling Unit | 8 | 5576 | 2.0552 | 1 | 2.0552 | 1 | 2.0552 | 1
118 | Classroom | 146 | 9 |  |  | 697 | 15 | 9 | Air Handling Unit | 8 | 5576 | 1.571 | 1 | 1.571 | 1 | 1.571 | 1
119 | Classroom | 98 | 6 |  |  | 349 | 7 | 6 | Air Handling Unit | 8 | 2792 | 2.106 | 1 | 2.106 | 1 | 2.106 | 1
201 | Classroom | 0 | 0 | Yes | 20 | 727 | 16 | 16 | Air Handling Unit | 8 | 5816 | 0 | 1 | 0 | 0 | 20 | 3
202 | Classroom | 338 | 22 |  |  | 687 | 15 | 15 | Air Handling Unit | 8 | 5496 | 3.69 | 1 | 3.69 | 1 | 3.69 | 1
203 | Classroom | 451 | 30 |  |  | 726 | 16 | 16 | Air Handling Unit | 8 | 5808 | 4.6591 | 1 | 4.6591 | 2 | 4.6591 | 2
204 | Office |  | 0 | Yes | 20 | 160 | 3 | 3 | Air Handling Unit | 8 | 1280 | 0 | 1 | 0 | 0 | 20 | 3
205 | Classroom | 311 | 20 |  |  | 348 | 7 | 7 | Air Handling Unit | 8 | 2784 | 6.7026 | 1 | 6.7026 | 2 | 6.7026 | 2
206 | Classroom | 452 | 30 |  |  | 324 | 7 | 7 | Air Handling Unit | 8 | 2592 | 10.463 | 1 | 10.463 | 3 | 10.463 | 3
207 | Room |  | 0 |  |  | 308 | 7 | 0 | Air Handling Unit | 8 | 2464 | 0 | 1 | 0 | 0 | 0 | 0
208-C | Main Office |  | 0 |  |  | 572 | 13 | 0 | Air Handling Unit | 8 | 4576 | 0 | 1 | 0 | 0 | 0 | 0
209 | Classroom | 765 | 51 |  |  | 901 | 20 | 20 | Air Handling Unit | 8 | 7208 | 6.3679 | 1 | 6.3679 | 2 | 6.3679 | 2
210 | Classroom | 394 | 26 |  |  | 1034 | 23 | 23 | Air Handling Unit | 8 | 8272 | 2.8578 | 1 | 2.8578 | 1 | 2.8578 | 1
211 | Classroom | 356 | 23 |  |  | 849 | 19 | 19 | Air Handling Unit | 8 | 6792 | 3.1449 | 1 | 3.1449 | 1 | 3.1449 | 1
212 | Classroom | 318 | 21 |  |  | 867 | 19 | 19 | Air Handling Unit | 8 | 6936 | 2.7509 | 1 | 2.7509 | 1 | 2.7509 | 1
213 | Classroom | 213 | 14 |  |  | 687 | 15 | 14 | Air Handling Unit | 8 | 5496 | 2.3253 | 1 | 2.3253 | 1 | 2.3253 | 1
214 | Classroom | 596 | 39 |  |  | 727 | 16 | 16 | Air Handling Unit | 8 | 5816 | 6.1486 | 1 | 6.1486 | 2 | 6.1486 | 2
215 | Classroom | 1059 | 70 |  |  | 668 | 15 | 15 | Air Handling Unit | 8 | 5344 | 11.89 | 1 | 11.89 | 3 | 11.89 | 3
216 | Classroom | 1311 | 87 |  |  | 791 | 17 | 17 | Air Handling Unit | 8 | 6328 | 12.4305 | 1 | 12.4305 | 3 | 12.4305 | 3
217 | Classroom | 1097 | 73 |  |  | 682 | 15 | 15 | Air Handling Unit | 8 | 5456 | 12.0638 | 1 | 12.0638 | 3 | 12.0638 | 3
218 | Classroom | 810 | 54 |  |  | 702 | 15 | 15 | Air Handling Unit | 8 | 5616 | 8.6538 | 1 | 8.6538 | 2 | 8.6538 | 2
219 | Classroom | 1352 | 90 |  |  | 700 | 15 | 15 | Air Handling Unit | 8 | 5600 | 14.4857 | 1 | 14.4857 | 3 | 14.4857 | 3
220 | Classroom | 1207 | 80 |  |  | 682 | 15 | 15 | Air Handling Unit | 8 | 5456 | 13.2735 | 1 | 13.2735 | 3 | 13.2735 | 3
221 | Classroom | 897 | 59 |  |  | 791 | 17 | 17 | Air Handling Unit | 8 | 6328 | 8.5051 | 1 | 8.5051 | 2 | 8.5051 | 2
222 | Classroom | 608 | 40 |  |  | 668 | 15 | 15 | Air Handling Unit | 8 | 5344 | 6.8263 | 1 | 6.8263 | 2 | 6.8263 | 2
223 | Classroom | 305 | 20 |  |  | 347 | 7 | 7 | Air Handling Unit | 8 | 2776 | 6.5922 | 1 | 6.5922 | 2 | 6.5922 | 2
224 | Room |  | 0 |  |  | 308 | 7 | 0 | Air Handling Unit | 8 | 2464 | 0 | 1 | 0 | 0 | 0 | 0
226 | Classroom | 86 | 5 |  |  | 216 | 4 | 4 | Air Handling Unit | 8 | 1728 | 2.9861 | 1 | 2.9861 | 1 | 2.9861 | 1
227 | Classroom | 163 | 10 |  |  | 347 | 7 | 7 | Air Handling Unit | 8 | 2776 | 3.5231 | 1 | 3.5231 | 1 | 3.5231 | 1
228 | Classroom | 208 | 13 |  |  | 694 | 15 | 13 | Air Handling Unit | 8 | 5552 | 2.2478 | 1 | 2.2478 | 1 | 2.2478 | 1
245 | Room |  | 0 | Yes | 20 | 87 | 1 | 1 | Air Handling Unit | 8 | 696 | 0 | 1 | 0 | 0 | 20 | 3
246 | Room |  | 0 | Yes | 20 | 82 | 1 | 1 | Air Handling Unit | 8 | 656 | 0 | 1 | 0 | 0 | 20 | 3
247 | Room |  | 0 | Yes | 20 | 110 | 2 | 2 | Air Handling Unit | 8 | 880 | 0 | 1 | 0 | 0 | 20 | 3
301 | Classroom | 813 | 54 |  |  | 727 | 16 | 16 | Air Handling Unit | 8 | 5816 | 8.3872 | 1 | 8.3872 | 2 | 8.3872 | 2
302 | Classroom | 439 | 29 |  |  | 684 | 15 | 15 | Air Handling Unit | 8 | 5472 | 4.8136 | 1 | 4.8136 | 2 | 4.8136 | 2
303 | Classroom | 605 | 40 |  |  | 697 | 15 | 15 | Air Handling Unit | 8 | 5576 | 6.51 | 1 | 6.51 | 2 | 6.51 | 2
304 | Classroom | 552 | 36 |  |  | 972 | 22 | 22 | Air Handling Unit | 8 | 7776 | 4.2593 | 1 | 4.2593 | 2 | 4.2593 | 2
305 | Classroom | 518 | 34 |  |  | 914 | 20 | 20 | Air Handling Unit | 8 | 7312 | 4.2505 | 1 | 4.2505 | 2 | 4.2505 | 2
306 | Classroom | 497 | 33 |  |  | 898 | 20 | 20 | Air Handling Unit | 8 | 7184 | 4.1509 | 1 | 4.1509 | 2 | 4.1509 | 2
307 | Classroom | 781 | 52 |  |  | 965 | 21 | 21 | Air Handling Unit | 8 | 7720 | 6.0699 | 1 | 6.0699 | 2 | 6.0699 | 2
308 | Classroom | 466 | 31 |  |  | 833 | 18 | 18 | Air Handling Unit | 8 | 6664 | 4.1957 | 1 | 4.1957 | 2 | 4.1957 | 2
309 | Classroom | 735 | 49 |  |  | 894 | 20 | 20 | Air Handling Unit | 8 | 7152 | 6.1661 | 1 | 6.1661 | 2 | 6.1661 | 2
309-A | Room |  | 0 |  |  | 220 | 5 | 0 | Air Handling Unit | 8 | 1760 | 0 | 1 | 0 | 0 | 0 | 0
310 | Classroom | 765 | 51 |  |  | 924 | 21 | 21 | Air Handling Unit | 8 | 7392 | 6.2094 | 1 | 6.2094 | 2 | 6.2094 | 2
311 | Classroom | 1322 | 88 |  |  | 958 | 21 | 21 | Air Handling Unit | 8 | 7664 | 10.3497 | 1 | 10.3497 | 3 | 10.3497 | 3
312 | Classroom | 660 | 44 |  |  | 728 | 16 | 16 | Air Handling Unit | 8 | 5824 | 6.7995 | 1 | 6.7995 | 2 | 6.7995 | 2
313 | Classroom | 403 | 26 |  |  | 313 | 7 | 7 | Air Handling Unit | 8 | 2504 | 9.6565 | 1 | 9.6565 | 2 | 9.6565 | 2
2021-11-09 | Classroom | 1020 | 68 |  |  | 314 | 7 | 7 | Air Handling Unit | 8 | 2512 | 24.3631 | 1 | 24.3631 | 4 | 24.3631 | 4
315 | Classroom | 1082 | 72 |  |  | 668 | 15 | 15 | Air Handling Unit | 8 | 5344 | 12.1482 | 1 | 12.1482 | 3 | 12.1482 | 3
316 | Classroom | 1750 | 116 |  |  | 791 | 17 | 17 | Air Handling Unit | 8 | 6328 | 16.5929 | 1 | 16.5929 | 3 | 16.5929 | 3
317 | Classroom | 2057 | 137 |  |  | 685 | 15 | 15 | Air Handling Unit | 8 | 5480 | 22.5219 | 1 | 22.5219 | 3 | 22.5219 | 3
318 | Classroom | 1824 | 121 |  |  | 699 | 15 | 15 | Air Handling Unit | 8 | 5592 | 19.5708 | 1 | 19.5708 | 3 | 19.5708 | 3
319 | Classroom | 1263 | 84 |  |  | 699 | 15 | 15 | Air Handling Unit | 8 | 5592 | 13.5515 | 1 | 13.5515 | 3 | 13.5515 | 3
320 | Classroom | 642 | 42 |  |  | 684 | 15 | 15 | Air Handling Unit | 8 | 5472 | 7.0395 | 1 | 7.0395 | 2 | 7.0395 | 2
321 | Classroom | 658 | 43 |  |  | 791 | 17 | 17 | Air Handling Unit | 8 | 6328 | 6.2389 | 1 | 6.2389 | 2 | 6.2389 | 2
322 | Classroom | 508 | 33 |  |  | 668 | 15 | 15 | Air Handling Unit | 8 | 5344 | 5.7036 | 1 | 5.7036 | 2 | 5.7036 | 2
323 | Classroom | 282 | 18 |  |  | 347 | 7 | 7 | Air Handling Unit | 8 | 2776 | 6.0951 | 1 | 6.0951 | 2 | 6.0951 | 2
324 | Classroom | 127 | 8 |  |  | 694 | 15 | 8 | Air Handling Unit | 8 | 5552 | 1.3725 | 1 | 1.3725 | 1 | 1.3725 | 1
327 | Room |  | 0 |  |  | 264 | 6 | 0 | Air Handling Unit | 8 | 2112 | 0 | 1 | 0 | 0 | 0 | 0
328 | Classroom | 107 | 7 |  |  | 694 | 15 | 7 | Air Handling Unit | 8 | 5552 | 1.1563 | 1 | 1.1563 | 1 | 1.1563 | 1
401 | Room |  | 0 |  |  | 264 | 6 | 0 | Rooftop Unit | 8 | 2112 | 0 | 1 | 0 | 0 | 0 | 0
401A | Room |  | 0 |  |  | 572 | 13 | 0 | Rooftop Unit | 8 | 4576 | 0 | 1 | 0 | 0 | 0 | 0
402 | Room |  | 0 |  |  | 836 | 19 | 0 | Rooftop Unit | 8 | 6688 | 0 | 1 | 0 | 0 | 0 | 0
403 | Room |  | 0 |  |  | 1056 | 24 | 0 | Rooftop Unit | 8 | 8448 | 0 | 1 | 0 | 0 | 0 | 0
404 | Room |  | 0 |  |  | 1188 | 27 | 0 | Rooftop Unit | 8 | 9504 | 0 | 1 | 0 | 0 | 0 | 0
406 | Room |  | 0 |  |  | 44 | 1 | 0 | Rooftop Unit | 8 | 352 | 0 | 1 | 0 | 0 | 0 | 0
407 | Room |  | 0 |  |  | 44 | 1 | 0 | Rooftop Unit | 8 | 352 | 0 | 1 | 0 | 0 | 0 | 0
408 | Room |  | 0 |  |  | 44 | 1 | 0 | Rooftop Unit | 8 | 352 | 0 | 1 | 0 | 0 | 0 | 0
409 | Room |  | 0 |  |  | 132 | 3 | 0 | Rooftop Unit | 8 | 1056 | 0 | 1 | 0 | 0 | 0 | 0
410 | Counselor's Office |  | 0 | Yes | 20 | 165 | 3 | 3 | Rooftop Unit | 8 | 1320 | 0 | 1 | 0 | 0 | 20 | 3
- | Auditorium |  | 0 |  |  | 3740 | 85 | 0 | Air Handling Unit | 8 | 29920 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Gym 1 |  | 0 |  |  | 2816 | 64 | 0 | Air Handling Unit | 8 | 22528 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Gym 2 |  | 0 |  |  | 2816 | 64 | 0 | Air Handling Unit | 8 | 22528 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Lunchroom 1 |  | 0 |  |  | 2640 | 60 | 0 | Air Handling Unit | 8 | 21120 | 0 | 1.062 | 0 | 0 | 0 | 0
- | Lunchroom 2 |  | 0 |  |  | 2596 | 59 | 0 | Air Handling Unit | 8 | 20768 | 0 | 1.062 | 0 | 0 | 0 | 0
Sheet Last Modified: | 2021-03-29
School: | Wister Elementary School
Vendor: | Mastery Charter Property Management
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Classroom | 307 | 20 |  |  |  | 0 | 0 | Unit Ventilator
101 | Classroom | 319 | 21 |  |  |  | 0 | 0 | Unit Ventilator
103 | Classroom | 148 | 9 |  |  |  | 0 | 0 | Unit Ventilator
106 | Lounge | 202 | 13 |  |  |  | 0 | 0 | Unit Ventilator
107A | Main Office | 0 | 0 |  |  |  | 0 | 0 | Unit Ventilator
108 | Classroom | 316 | 21 |  |  | 1134 | 25 | 21 | Unit Ventilator | 8 | 9072 | 2.0899 | 1 | 2.0899 | 1 | 2.0899 | 1
109 | Classroom | 313 | 20 |  |  | 1094 | 24 | 20 | Unit Ventilator | 8 | 8752 | 2.1458 | 1 | 2.1458 | 1 | 2.1458 | 1
110 | Storage | 215 | 14 |  |  |  | 0 | 0 | Unit Ventilator
111 | Classroom | 339 | 22 |  |  | 1414 | 32 | 22 | Unit Ventilator | 8 | 11312 | 1.7981 | 1 | 1.7981 | 1 | 1.7981 | 1
200 | Classroom | 309 | 20 |  |  |  | 0 | 0 | Unit Ventilator
201 | Office | 162 | 10 |  |  |  | 0 | 0 | Unit Ventilator
202 | Classroom | 138 | 9 |  |  |  | 0 | 0 | Unit Ventilator
203 | Classroom | 311 | 20 |  |  |  | 0 | 0 | Unit Ventilator
204 | Classroom | 271 | 18 |  |  |  | 0 | 0 | Unit Ventilator
205 | Classroom | 144 | 9 |  |  |  | 0 | 0 | Unit Ventilator
206 | Classroom | 304 | 20 |  |  |  | 0 | 0 | Unit Ventilator
207 | Classroom | 304 | 20 |  |  |  | 0 | 0 | Unit Ventilator
208 | Classroom | 308 | 20 |  |  |  | 0 | 0 | Unit Ventilator
209C | Classroom | 337 | 22 |  |  |  | 0 | 0 | Unit Ventilator
210 | Classroom | 319 | 21 |  |  |  | 0 | 0 | Unit Ventilator
211 | Classroom | 302 | 20 |  |  |  | 0 | 0 | Unit Ventilator
212 | Classroom | 313 | 20 |  |  |  | 0 | 0 | Unit Ventilator
213 | Classroom | 331 | 22 |  |  |  | 0 | 0 | Unit Ventilator
214 | Classroom | 349 | 23 |  |  |  | 0 | 0 | Unit Ventilator
300 | Classroom | 299 | 19 |  |  |  | 0 | 0 | Unit Ventilator
301 | Office | 129 | 8 |  |  |  | 0 | 0 | Unit Ventilator
302 | Classroom | 153 | 10 |  |  |  | 0 | 0 | Unit Ventilator
303 | Classroom | 308 | 20 |  |  |  | 0 | 0 | Unit Ventilator
304 | Classroom | 330 | 22 |  |  |  | 0 | 0 | Unit Ventilator
305 | Classroom | 332 | 22 |  |  |  | 0 | 0 | Unit Ventilator
306 | Classroom | 311 | 20 |  |  |  | 0 | 0 | Unit Ventilator
307 | Classroom | 312 | 20 |  |  |  | 0 | 0 | Unit Ventilator
- | Auditorium | 2036 | 135 |  |  |  | 0 | 0 | AHU
- | Gym | 1544 | 102 |  |  |  | 0 | 0 | AHU
Sheet Last Modified: | 2021-03-17
School: | Sustainability Workshop School
Vendor: | Goldner
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
101 | Corridor | 7 | 0 |  |  | 533 | 12 | 0 | VAV | 8 | 4264 | 0.098499 | 1 | 0.098499 | 0 | 0.098499 | 0
102 | Closet | 6 | 0 |  |  | 45 | 1 | 0 | VAV | 8 | 360 | 1 | 1 | 1 | 0 | 1 | 0
105 | Nurses Office / Classroom |  | 0 |  |  | 150 | 3 | 0 | HU | 8 | 1200 | 0 | 1 | 0 | 0 | 0 | 0
106 | Woodshop | 43 | 2 |  |  | 1003 | 22 | 2 | HU | 8 | 8024 | 0.32154 | 1 | 0.32154 | 0 | 0.32154 | 0
110 | Classroom | 23 | 1 |  |  | 884 | 20 | 1 | VAV | 8 | 7072 | 0.19514 | 1 | 0.19514 | 0 | 0.19514 | 0
111 | Auto Service | 0 | 0 |  |  | 1761 | 40 | 0 | HU and Univent | 8 | 14088 | 0 | 1 | 0 | 0 | 0 | 0
111 | Classroom |  | 0 |  |  | 756 | 17 | 0 | Univent | 8 | 6048 | 0 | 1 | 0 | 0 | 0 | 0
112 | Training Classroom | 0 | 0 |  |  | 459 | 10 | 0 | HU and Univent | 8 | 3672 | 0 | 1 | 0 | 0 | 0 | 0
114 | Tool Storage | 0 | 0 |  |  | 450 | 10 | 0 | HU and Univent | 8 | 3600 | 0 | 1 | 0 | 0 | 0 | 0
117 | Body Shop | 0 | 0 |  |  | 2944 | 66 | 0 | HU | 8 | 23552 | 0 | 1.062 | 0 | 0 | 0 | 0
121 | Classroom |  | 0 |  |  | 729 | 16 | 0 | Univent | 8 | 5832 | 0 | 1 | 0 | 0 | 0 | 0
200 | Corridor | 33 | 2 |  |  | 1868 | 42 | 2 | VAV | 8 | 14944 | 0.13249 | 1 | 0.13249 | 0 | 0.13249 | 0
201 | Classroom | 42 | 2 |  |  | 740 | 16 | 2 | VAV | 8 | 5920 | 0.42568 | 1 | 0.42568 | 0 | 0.42568 | 0
206 | Main Office | 7 | 0 |  |  | 234 | 5 | 0 | VAV | 8 | 1872 | 0.22436 | 1 | 0.22436 | 0 | 0.22436 | 0
207 | Office | 6 | 0 |  |  | 192 | 4 | 0 | VAV | 8 | 1536 | 0.23438 | 1 | 0.23438 | 0 | 0.23438 | 0
208 | Principle Office | 5 | 0 |  |  | 80 | 1 | 0 | VAV | 8 | 640 | 0.46875 | 1 | 0.46875 | 0 | 0.46875 | 0
209 | Copy Room | 12 | 0 |  |  | 132 | 3 | 0 | VAV | 8 | 1056 | 0.68182 | 1 | 0.68182 | 0 | 0.68182 | 0
210 | Classroom | 25 | 1 |  |  | 748 | 17 | 1 | VAV | 8 | 5984 | 0.25067 | 1 | 0.25067 | 0 | 0.25067 | 0
210-C | Counselors office in front of classroom 210 | 2 | 0 |  |  | NA | 0 | 0 | VAV
212 | Mechanical room |  | 0 |  |  | 620 | 14 | 0 | AHU | 8 | 4960 | 0 | 1 | 0 | 0 | 0 | 0
212 | Classroom | 366 | 24 |  |  | 720 | 16 | 16 | VAV | 8 | 5760 | 3.8125 | 1 | 3.8125 | 1 | 3.8125 | 1
213 | Classroom | 1829 | 121 |  |  | 691 | 15 | 15 | VAV | 8 | 5528 | 19.8517 | 1 | 19.8517 | 3 | 19.8517 | 3
214 | Classroom | 837 | 55 |  |  | 761 | 17 | 17 | VAV | 8 | 6088 | 8.249 | 1 | 8.249 | 2 | 8.249 | 2
215 | Classroom | 839 | 55 |  |  | 961 | 21 | 21 | VAV | 8 | 7688 | 6.5479 | 1 | 6.5479 | 2 | 6.5479 | 2
215A | Classroom | 96 | 6 |  |  | NA | 0 | 0 | VAV
216 | Classroom | 655 | 43 |  |  | 1012 | 23 | 23 | VAV | 8 | 8096 | 4.8542 | 1 | 4.8542 | 2 | 4.8542 | 2
219 | Corridor Bathroom | 40 | 2 |  |  | 48 | 1 | 1 | VAV | 8 | 384 | 6.25 | 1 | 6.25 | 2 | 6.25 | 2
- | Automotive Classroom | 0 | 0 |  |  | NA | 0 | 0 | HU and Univent
- | Body Shop Classroom | 0 | 0 |  |  | NA | 0 | 0 | Univent
- | Cafeteria Bathroom | 41 | 2 |  |  | 49 | 1 | 1 | VAV | 8 | 392 | 6.2755 | 1 | 6.2755 | 2 | 6.2755 | 2
- | Cafeteria | 402 | 26 |  |  | 2550 | 57 | 26 | RTU | 8 | 20400 | 1.1824 | 1.062 | 1.2557 | 1 | 1.2557 | 1
- | Computer Lab | 60 | 4 |  |  | 312 | 7 | 4 | HU | 8 | 2496 | 1.4423 | 1 | 1.4423 | 1 | 1.4423 | 1
- | Kitchen | 0 | 0 |  |  | 504 | 11 | 0 | MUA | 8 | 4032 | 0 | 1 | 0 | 0 | 0 | 0
- | Mr. Boyd Office | 185 | 12 |  |  | 152 | 3 | 3 | VAV and RETURN DUCT | 8 | 1216 | 9.1283 | 1 | 9.1283 | 2 | 9.1283 | 2
- | Mr. Tobias Office | 185 | 12 |  |  | 80 | 1 | 1 | VAV | 8 | 640 | 17.3438 | 1 | 17.3438 | 3 | 17.3438 | 3
- | Mrs. Walker Office | 138 | 9 |  |  | 80 | 1 | 1 | VAV | 8 | 640 | 12.9375 | 1 | 12.9375 | 3 | 12.9375 | 3
- | Ms. Phoebe Office | 188 | 12 |  |  | 91 | 2 | 2 | VAV | 8 | 728 | 15.4945 | 1 | 15.4945 | 3 | 15.4945 | 3
- | Nurse Room | 0 | 0 |  |  | NA | 0 | 0 | HU and Univent
- | Storage / Office | 15 | 1 |  |  | 120 | 2 | 1 | RTU | 8 | 960 | 0.9375 | 1 | 0.9375 | 0 | 0.9375 | 0
- | Woodshop Office | 43 | 2 |  |  | NA | 0 | 0 | HU
- | Woodshop Saw | 24 | 1 |  |  | NA | 0 | 0 | HU
Sheet Last Modified: | 2021-04-30
School: | Richard R. Wright Elementary School
Vendor: | Goldner | Goldner Retest
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
100 | Art Room | 280 | 18 | Yes | 20 | 1400 | 31 | 31 | Unit Ventilator | 8 | 11200 | 1.5 | 1 | 1.5 | 1 | 21.5 | 3
108-A | 1st Floor Gymnasium Office | 5 | 0 |  |  | 100 | 2 | 0 | Air Handling Unit | 8 | 800 | 0.375 | 1 | 0.375 | 0 | 0.375 | 0
112-A | 1st Floor Music Practice | 10 | 0 |  |  | 100 | 2 | 0 | Air Handling Unit | 8 | 800 | 0.75 | 1 | 0.75 | 0 | 0.75 | 0
112-B | 1st Floor Music Practice | 19 | 1 |  |  | 100 | 2 | 1 | Air Handling Unit | 8 | 800 | 1.425 | 1 | 1.425 | 1 | 1.425 | 1
114 | Classroom | 334 | 22 | Yes | 20 | 1360 | 30 | 30 | Unit Ventilator | 8 | 10880 | 1.8419 | 1 | 1.8419 | 1 | 21.8419 | 3
115 | Classroom | 358 | 23 | Yes | 20 | 1360 | 30 | 30 | Unit Ventilator | 8 | 10880 | 1.9743 | 1 | 1.9743 | 1 | 21.9743 | 3
118 | Nurse area | 0 | 0 | Yes | 20 | 378 | 8 | 8 | Unit Ventilator | 8 | 3024 | 0 | 1 | 0 | 0 | 20 | 3
119 | Nurse area | 0 | 0 | Yes | 20 | 216 | 4 | 4 | Unit Ventilator | 8 | 1728 | 0 | 1 | 0 | 0 | 20 | 3
120 | Classroom | 273 | 18 | Yes | 20 | 1360 | 30 | 30 | Unit Ventilator | 8 | 10880 | 1.5055 | 1 | 1.5055 | 1 | 21.5055 | 3
121 | Classroom | 435 | 29 |  |  | 1360 | 30 | 29 | Unit Ventilator | 8 | 10880 | 2.3989 | 1 | 2.3989 | 1 | 2.3989 | 1
122 | Classroom | 273 | 18 | Yes | 20 | 1360 | 30 | 30 | Unit Ventilator | 8 | 10880 | 1.5055 | 1 | 1.5055 | 1 | 21.5055 | 3
201 | Classroom | 342 | 22 | Yes | 20 | 1610 | 36 | 36 | Unit Ventilator | 8 | 12880 | 1.5932 | 1 | 1.5932 | 1 | 21.5932 | 3
202 | Classroom | 634 | 42 |  |  | 1702 | 38 | 38 | Unit Ventilator | 8 | 13616 | 2.7938 | 1 | 2.7938 | 1 | 2.7938 | 1
203 | Classroom | 349 | 23 | Yes | 20 | 1120 | 25 | 25 | Unit Ventilator | 8 | 8960 | 2.3371 | 1 | 2.3371 | 1 | 22.3371 | 3
204 | Classroom | 358 | 23 |  |  |  | 0 | 0 | Unit Ventilator
205 | Classroom | 482 | 32 |  |  | 870 | 19 | 19 | Unit Ventilator | 8 | 6960 | 4.1552 | 1 | 4.1552 | 2 | 4.1552 | 2
206 | Classroom | 499 | 33 |  |  | 812 | 18 | 18 | Unit Ventilator | 8 | 6496 | 4.609 | 1 | 4.609 | 2 | 4.609 | 2
207 | Classroom | 460 | 30 |  |  | 870 | 19 | 19 | Unit Ventilator | 8 | 6960 | 3.9655 | 1 | 3.9655 | 1 | 3.9655 | 1
208 | Classroom | 232 | 15 | Yes | 20 | 841 | 19 | 19 | Unit Ventilator | 8 | 6728 | 2.069 | 1 | 2.069 | 1 | 22.069 | 3
209 | Classroom | 341 | 22 |  |  |  | 0 | 0 | Unit Ventilator
210 | Classroom | 413 | 27 |  |  | 899 | 20 | 20 | Unit Ventilator | 8 | 7192 | 3.4455 | 1 | 3.4455 | 1 | 3.4455 | 1
211 | Classroom | 270 | 18 | Yes | 20 | 1715 | 38 | 38 | Unit Ventilator | 8 | 13720 | 1.1808 | 1 | 1.1808 | 1 | 21.1808 | 3
212 | Classroom | 434 | 28 | Yes | 20 | 1911 | 43 | 43 | Unit Ventilator | 8 | 15288 | 1.7033 | 1 | 1.7033 | 1 | 21.7033 | 3
213 | Classroom | 310 | 20 | Yes | 20 | 1715 | 38 | 38 | Unit Ventilator | 8 | 13720 | 1.3557 | 1 | 1.3557 | 1 | 21.3557 | 3
214 | Classroom | 799 | 53 |  |  | 1786 | 40 | 40 | Unit Ventilator | 8 | 14288 | 3.3553 | 1 | 3.3553 | 1 | 3.3553 | 1
215 | Classroom | 325 | 21 |  |  | 870 | 19 | 19 | Unit Ventilator | 8 | 6960 | 2.8017 | 1 | 2.8017 | 1 | 2.8017 | 1
216 | Classroom | 296 | 19 | Yes | 20 | 930 | 21 | 21 | Unit Ventilator | 8 | 7440 | 2.3871 | 1 | 2.3871 | 1 | 22.3871 | 3
217 | Classroom | 568 | 37 |  |  | 870 | 19 | 19 | Unit Ventilator | 8 | 6960 | 4.8966 | 1 | 4.8966 | 2 | 4.8966 | 2
218 | Classroom | 415 | 27 |  |  | 870 | 19 | 19 | Unit Ventilator | 8 | 6960 | 3.5776 | 1 | 3.5776 | 1 | 3.5776 | 1
219 | Classroom | 289 | 19 |  |  | 870 | 19 | 19 | Unit Ventilator | 8 | 6960 | 2.4914 | 1 | 2.4914 | 1 | 2.4914 | 1
220 | Classroom | 278 | 18 |  |  | 870 | 19 | 18 | Unit Ventilator | 8 | 6960 | 2.3966 | 1 | 2.3966 | 1 | 2.3966 | 1
221 | Classroom | 339 | 22 |  |  | 899 | 20 | 20 | Unit Ventilator | 8 | 7192 | 2.8281 | 1 | 2.8281 | 1 | 2.8281 | 1
222 | Classroom | 372 | 24 |  |  | 784 | 17 | 17 | Unit Ventilator | 8 | 6272 | 3.5587 | 1 | 3.5587 | 1 | 3.5587 | 1
223 | Classroom | 369 | 24 | Yes | 20 | 1739 | 39 | 39 | Unit Ventilator | 8 | 13912 | 1.5914 | 1 | 1.5914 | 1 | 21.5914 | 3
224 | Classroom | 284 | 18 | Yes | 20 | 1739 | 39 | 39 | Unit Ventilator | 8 | 13912 | 1.2248 | 1 | 1.2248 | 1 | 21.2248 | 3
225 | Room | 211 | 14 |  |  | 196 | 4 | 4 | Air Handling Unit | 8 | 1568 | 8.074 | 1 | 8.074 | 2 | 8.074 | 2
227 | Room | 119 | 7 |  |  | 196 | 4 | 4 | Air Handling Unit | 8 | 1568 | 4.5536 | 1 | 4.5536 | 2 | 4.5536 | 2
- | 1st Floor Conference Room | 89 | 5 |  |  | 108 | 2 |  | Air Handling Unit | 8 | 864 | 6.1806 | 1 | 6.1806 | 2 | 6.1806 | 2
- | 1st Floor Counselor's Office | 17 | 1 |  |  | 100 | 2 |  | Air Handling Unit | 8 | 800 | 1.275 | 1 | 1.275 | 1 | 1.275 | 1
- | 1st Floor Engineer's Office | 30 | 2 |  |  | 36 | 0 |  | Air Handling Unit | 8 | 288 | 6.25 | 1 | 6.25 | 2 | 6.25 | 2
- | 1st Floor Entry Hallway | 79 | 5 |  |  | 140 | 3 |  | Air Handling Unit | 8 | 1120 | 4.2321 | 1 | 4.2321 | 2 | 4.2321 | 2
- | 1st Floor CSC Office | 4 | 0 |  |  | 100 | 2 |  | Air Handling Unit | 8 | 800 | 0.3 | 1 | 0.3 | 0 | 0.3 | 0
- | 1st Floor IT Room | 10 | 0 |  |  | 100 | 2 |  | Air Handling Unit | 8 | 800 | 0.75 | 1 | 0.75 | 0 | 0.75 | 0
- | 1st Floor Main Office | 98 | 6 |  |  | 144 | 3 |  | Air Handling Unit | 8 | 1152 | 5.1042 | 1 | 5.1042 | 2 | 5.1042 | 2
- | 1st Floor Office Storage | 0 | 0 |  |  | 160 | 3 |  | Air Handling Unit | 8 | 1280 | 0 | 1 | 0 | 0 | 0 | 0
- | 1st Floor Prinicpal's Office | 23 | 1 |  |  | 140 | 3 |  | Air Handling Unit | 8 | 1120 | 1.2321 | 1 | 1.2321 | 1 | 1.2321 | 1
- | 1st Floor Psychologist's Office | 14 | 0 |  |  | 140 | 3 |  | Air Handling Unit | 8 | 1120 | 0.75 | 1 | 0.75 | 0 | 0.75 | 0
- | 1st Floor Small Kitchen | 56 | 3 |  |  | 84 | 1 |  | Air Handling Unit | 8 | 672 | 5 | 1 | 5 | 2 | 5 | 2
- | 1st Floor Staff Lounge | 447 | 29 |  |  | 1556 | 35 | 29 | Unit Ventilator | 8 | 12448 | 2.1546 | 1 | 2.1546 | 1 | 2.1546 | 1
- | 2nd Floor Computer Storage | 44 | 2 |  |  | 196 | 4 | 2 | Air Handling Unit | 8 | 1568 | 1.6837 | 1 | 1.6837 | 1 | 1.6837 | 1
- | 2nd Floor Library | 2489 | 165 |  |  | 556 | 12 | 12 | Air Handling Unit | 8 | 4448 | 33.5746 | 1 | 33.5746 | 4 | 33.5746 | 4
- | 2nd Floor Library Lounge | 131 | 8 |  |  | 192 | 4 | 4 | Air Handling Unit | 8 | 1536 | 5.1172 | 1 | 5.1172 | 2 | 5.1172 | 2
- | 2nd Floor Library Storage | 109 | 7 |  |  | 336 | 7 | 7 | Air Handling Unit | 8 | 2688 | 2.433 | 1 | 2.433 | 1 | 2.433 | 1
- | 2nd Floor Office space | 250 | 16 |  |  | 216 | 4 | 4 | Unit Ventilator | 8 | 1728 | 8.6806 | 1 | 8.6806 | 2 | 8.6806 | 2
- | 2nd Floor Storage space | 358 | 23 |  |  | 432 | 9 | 9 | Unit Ventilator | 8 | 3456 | 6.2153 | 1 | 6.2153 | 2 | 6.2153 | 2
- | Cafetorium | 4622 | 308 |  |  | 4730 | 107 | 107 | Air Handling Unit | 8 | 37840 | 7.3288 | 1.062 | 7.7834 | 2 | 7.7834 | 2
- | Gym | 890 | 59 |  |  | 5644 | 128 | 59 | Air Handling Unit | 8 | 45152 | 1.1827 | 1.062 | 1.256 | 1 | 1.256 | 1
Sheet Last Modified: | 2021-05-03
School: | William H. Ziegler Elementary School
Vendor: | Chadwick | Chadwick Part 2 | Chadwick Part 3
Please visit https://bit.ly/3mA7rMY for more information on how to read this report.
Classroom ID / Area ID Number | Classroom / Area Type supplied | Actual Mechanical System Outside Air CFM (OA) | Mechanical System Occupancy (OA CFM / 15) | Active Pure Unit Installed |  | Classroom / Area Square Footage | Square Footage Occupancy (SqFt / 44) | Maximum Occupancy per Room | Type of Unit
102 | Classroom | 147 | 9 |  |  | 140 | 3 | 3 | Unit Ventilator | 8 | 1120 | 7.875 | 1 | 7.875 | 2 | 7.875 | 2
103 | Classroom | 309 | 20 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 2.7721 | 1 | 2.7721 | 1 | 2.7721 | 1
104 | Classroom | 346 | 23 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 3.1041 | 1 | 3.1041 | 1 | 3.1041 | 1
105 | Classroom | 296 | 19 |  |  | 836 | 19 | 19 | Unit Ventilator | 8 | 6688 | 2.6555 | 1 | 2.6555 | 1 | 2.6555 | 1
106 | Office/Classroom |  | 0 | Yes | 20 | 322 | 7 | 7 | Unit Ventilator | 8 | 2576 | 0 | 1 | 0 | 0 | 20 | 3
107 | Classroom | 161 | 10 | Yes | 20 | 638 | 14 | 14 | Unit Ventilator | 8 | 5104 | 1.8926 | 1 | 1.8926 | 1 | 21.8926 | 3
108 | Nurse |  | 0 | Yes | 20 | 171 | 3 | 3 | Unit Ventilator | 8 | 1368 | 0 | 1 | 0 | 0 | 20 | 3
109 | Classroom |  | 0 | Yes | 20 | 696 | 15 | 15 | Unit Ventilator | 8 | 5568 | 0 | 1 | 0 | 0 | 20 | 3
111 | Classroom | 331 | 22 |  |  | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 3.64 | 1 | 3.64 | 1 | 3.64 | 1
112 | Classroom | 300 | 20 |  |  | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 3.2991 | 1 | 3.2991 | 1 | 3.2991 | 1
113 | Classroom | 338 | 22 |  |  | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 3.717 | 1 | 3.717 | 1 | 3.717 | 1
114 | Classroom | 301 | 20 |  |  | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 3.3101 | 1 | 3.3101 | 1 | 3.3101 | 1
115 | Classroom | 312 | 20 |  |  | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 3.4311 | 1 | 3.4311 | 1 | 3.4311 | 1
116 | Classroom | 318 | 21 |  |  | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 3.4971 | 1 | 3.4971 | 1 | 3.4971 | 1
117 | Classroom | 318 | 21 |  |  | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 3.4971 | 1 | 3.4971 | 1 | 3.4971 | 1
125 | Classroom | 294 | 19 |  |  | 600 | 13 | 13 | Energy Recovery Unit | 8 | 4800 | 3.675 | 1 | 3.675 | 1 | 3.675 | 1
201 | Classroom | 398 | 26 |  |  | 598 | 13 | 13 | Unit Ventilator | 8 | 4784 | 4.9916 | 1 | 4.9916 | 2 | 4.9916 | 2
202 | Classroom | 511 | 34 |  |  | 644 | 14 | 14 | Unit Ventilator | 8 | 5152 | 5.9511 | 1 | 5.9511 | 2 | 5.9511 | 2
203 | Classroom |  | 0 | Yes | 20 | 390 | 8 | 8 | Unit Ventilator | 8 | 3120 | 0 | 1 | 0 | 0 | 20 | 3
204 | Classroom | 417 | 27 |  |  | 780 | 17 | 17 | Unit Ventilator | 8 | 6240 | 4.0096 | 1 | 4.0096 | 2 | 4.0096 | 2
205 | Classroom | 315 | 21 |  |  | 962 | 21 | 21 | Unit Ventilator | 8 | 7696 | 2.4558 | 1 | 2.4558 | 1 | 2.4558 | 1
206 | Classroom | 110 | 7 | Yes | 20 | 644 | 14 | 14 | Unit Ventilator | 8 | 5152 | 1.2811 | 1 | 1.2811 | 1 | 21.2811 | 3
207 | Classroom |  | 0 | Yes | 20 | 243 | 5 | 5 | Unit Ventilator | 8 | 1944 | 0 | 1 | 0 | 0 | 20 | 3
208 | Teacher's Lounge |  | 0 | Yes | 20 | 280 | 6 | 6 | Unit Ventilator | 8 | 2240 | 0 | 1 | 0 | 0 | 20 | 3
210 | Classroom | 147 | 9 | Yes | 20 | 644 | 14 | 14 | Unit Ventilator | 8 | 5152 | 1.712 | 1 | 1.712 | 1 | 21.712 | 3
212 | Classroom | 534 | 35 |  |  | 667 | 15 | 15 | Unit Ventilator | 8 | 5336 | 6.0045 | 1 | 6.0045 | 2 | 6.0045 | 2
213 | Classroom | 332 | 22 |  |  | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 3.651 | 1 | 3.651 | 1 | 3.651 | 1
214 | Classroom | 166 | 11 | Yes | 20 | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 1.8255 | 1 | 1.8255 | 1 | 21.8255 | 3
215 | Classroom | 281 | 18 |  |  | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 3.0902 | 1 | 3.0902 | 1 | 3.0902 | 1
216 | Classroom | 265 | 17 |  |  | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 2.9142 | 1 | 2.9142 | 1 | 2.9142 | 1
217 | Classroom | 261 | 17 |  |  | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 2.8702 | 1 | 2.8702 | 1 | 2.8702 | 1
218 | Classroom | 275 | 18 |  |  | 682 | 15 | 15 | Energy Recovery Unit | 8 | 5456 | 3.0242 | 1 | 3.0242 | 1 | 3.0242 | 1
220 | Classroom | 269 | 17 |  |  | 748 | 17 | 17 | Energy Recovery Unit | 8 | 5984 | 2.6972 | 1 | 2.6972 | 1 | 2.6972 | 1
- | Cafeteria | 2750 | 183 |  |  | 2736 | 62 | 62 | Air Handling Unit | 8 | 21888 | 7.5384 | 1.062 | 8.006 | 2 | 8.006 | 2
- | Gymasium | 1073 | 71 |  |  | 3498 | 79 | 71 | Air Handling Unit | 8 | 27984 | 2.3006 | 1.062 | 2.4433 | 1 | 2.4433 | 1
- | Hallway | 105 | 7 |  |  |  | 0 | 0 | Air Handling Unit
- | Library/IMC | 983 | 65 |  |  | 1953 | 44 | 44 | Air Handling Unit | 8 | 15624 | 3.775 | 1 | 3.775 | 1 | 3.775 | 1
- | Main Office |  | 0 | Yes | 20 | 456 | 10 | 10 | Unit Ventilator | 8 | 3648 | 0 | 1 | 0 | 0 | 20 | 3
- | Principal's Office |  | 0 | Yes | 20 | 198 | 4 | 4 | Unit Ventilator | 8 | 1584 | 0 | 1 | 0 | 0 | 20 | 3
- | Science Lab | 228 | 15 |  |  | 968 | 22 | 15 | Energy Recovery Unit | 8 | 7744 | 1.7665 | 1 | 1.7665 | 1 | 1.7665 | 1

## Macro What If
Num PCO Units | eAUC / PCO | Total cu-ft | Total HVAC CFM | Total HVAC AUC | Total eAUC | Total AUC | Rooms | AUC | Level | Cost | PCO / Room | Comments
0 | 20 | 92871681.264 | 4337033 | 38324.1182 | 0 | 38324.1182 | 12842 | 2.9843 | 1
2503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 50060 | 88384.1182 | 12842 | 6.8824 | 2 | 3754500 | 0.19491
4503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 90060 | 128384.1182 | 12842 | 9.9972 | 2 | 6754500 | 0.35065 | From site survey
6503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 130060 | 168384.1182 | 12842 | 13.112 | 3 | 9754500 | 0.50639
8503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 170060 | 208384.1182 | 12842 | 16.2268 | 3 | 12754500 | 0.66212
10503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 210060 | 248384.1182 | 12842 | 19.3415 | 3 | 15754500 | 0.81786
12503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 250060 | 288384.1182 | 12842 | 22.4563 | 3 | 18754500 | 0.9736
14503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 290060 | 328384.1182 | 12842 | 25.5711 | 4 | 21754500 | 1.1293
16503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 330060 | 368384.1182 | 12842 | 28.6859 | 4 | 24754500 | 1.2851 | Eventually HVAC system becomes irrelevant
18503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 370060 | 408384.1182 | 12842 | 31.8007 | 4 | 27754500 | 1.4408
20503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 410060 | 448384.1182 | 12842 | 34.9154 | 4 | 30754500 | 1.5966
22503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 450060 | 488384.1182 | 12842 | 38.0302 | 4 | 33754500 | 1.7523
24503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 490060 | 528384.1182 | 12842 | 41.145 | 4 | 36754500 | 1.908
26503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 530060 | 568384.1182 | 12842 | 44.2598 | 4 | 39754500 | 2.0638
28503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 570060 | 608384.1182 | 12842 | 47.3746 | 4 | 42754500 | 2.2195
30503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 610060 | 648384.1182 | 12842 | 50.4893 | 5 | 45754500 | 2.3753
32503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 650060 | 688384.1182 | 12842 | 53.6041 | 5 | 48754500 | 2.531
34503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 690060 | 728384.1182 | 12842 | 56.7189 | 5 | 51754500 | 2.6867
36503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 730060 | 768384.1182 | 12842 | 59.8337 | 5 | 54754500 | 2.8425
38503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 770060 | 808384.1182 | 12842 | 62.9485 | 5 | 57754500 | 2.9982
40503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 810060 | 848384.1182 | 12842 | 66.0632 | 5 | 60754500 | 3.1539
42503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 850060 | 888384.1182 | 12842 | 69.178 | 5 | 63754500 | 3.3097
44503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 890060 | 928384.1182 | 12842 | 72.2928 | 5 | 66754500 | 3.4654
46503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 930060 | 968384.1182 | 12842 | 75.4076 | 5 | 69754500 | 3.6212
48503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 970060 | 1008384.1182 | 12842 | 78.5224 | 5 | 72754500 | 3.7769
50503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1010060 | 1048384.1182 | 12842 | 81.6371 | 5 | 75754500 | 3.9326
52503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1050060 | 1088384.1182 | 12842 | 84.7519 | 5 | 78754500 | 4.0884
54503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1090060 | 1128384.1182 | 12842 | 87.8667 | 5 | 81754500 | 4.2441
56503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1130060 | 1168384.1182 | 12842 | 90.9815 | 5 | 84754500 | 4.3999
58503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1170060 | 1208384.1182 | 12842 | 94.0963 | 5 | 87754500 | 4.5556
60503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1210060 | 1248384.1182 | 12842 | 97.211 | 5 | 90754500 | 4.7113
62503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1250060 | 1288384.1182 | 12842 | 100.3258 | 5 | 93754500 | 4.8671
64503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1290060 | 1328384.1182 | 12842 | 103.4406 | 5 | 96754500 | 5.0228
66503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1330060 | 1368384.1182 | 12842 | 106.5554 | 5 | 99754500 | 5.1786
68503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1370060 | 1408384.1182 | 12842 | 109.6702 | 5 | 102754500 | 5.3343
70503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1410060 | 1448384.1182 | 12842 | 112.7849 | 5 | 105754500 | 5.49
72503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1450060 | 1488384.1182 | 12842 | 115.8997 | 5 | 108754500 | 5.6458
74503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1490060 | 1528384.1182 | 12842 | 119.0145 | 5 | 111754500 | 5.8015
76503 | 20 | 92871681.264 | 4337033 | 38324.1182 | 1530060 | 1568384.1182 | 12842 | 122.1293 | 6 | 114754500 | 5.9572